## 02_Raw_Data_Table
Plant Name | EIA Plant Code | Unit No. | RunNumber | CoalFlowRate | HHV | pctSulphur | pctMoisture | pctAsh | Chlorine | Hg | CoalAnalysisMethod | FuelType | Inlet Flow Rate | temp_GasIn | pct_StackGasMoistureIn | pct_StackGasO2In | Hg_ParticleBoundIn | Hg_OxidizedIn | Hg_ElementalIn | Outlet Flow Rate | temp_GasOut | pct_StackGasMoistureOut | pct_StackGasO2Out | Hg_ParticleBoundOut | Hg_OxidizedOut | Hg_ElementalOut
| & ORIS Code |  |  | (kg/hr), dry | Btu/lb | % | % | % | mg/kg or ppm | mg/kg or ppm |  |  | dscm/hr | Deg C | % | % | ug/dscm | ug/dscm | ug/dscm | dscm/hr | Deg C | % | % | ug/dscm | ug/dscm | ug/dscm
AES Cayuga (NY) (formerly NYSEG Milliken) | 0135110000-02535 | 2 | 1 | 50040.956 | 13731 | 2.51 | 4.81 | 9.41 | 840 | 0.10505 | EPA 7471 | Bituminous | 549382.0029 | 134.7778 | 8 | 4.9 | NA | 5.25 | 1.91 | 609379.1783 | 49.8889 | 14.2 | 5.61 | NA | 0.26 | 2.22
AES Cayuga (NY) (formerly NYSEG Milliken) | 0135110000-02535 | 2 | 2 | 51915.1899 | 13791 | 2.55 | 5.77 | 9.01 | 955 | 0.11249 | EPA 7471 | Bituminous | 563471.9011 | 137 | 8.1 | 5.28 | 0.72 | 5.59 | 2.10 | 609569.4676 | 50.4444 | 14.4 | 5.31 | 0.013 | 0.14 | 2.19
AES Cayuga (NY) (formerly NYSEG Milliken) | 0135110000-02535 | 2 | 3 | 52215.0128 | 13661 | 2.33 | 5.93 | 9.69 | 850 | 0.10205 | EPA 7471 | Bituminous | 560811.2499 | 140.3333 | 8.1 | 5.16 | 1.62 | 4.88 | 2.42 | 616217.6976 | 49.9444 | 14 | 5.32 | 0.02 | 0.13 | 2.50
AES Hawaii, Inc. | 10673 | AB | 1 | 32884 | 12742 | 0.67 | 12.72 | 8.17 | 60 | 0.03 | D3684-94 - FICVAA | Subbituminous | 415320 | 137.2 | 8.7 | 8.0 | 0.19 | ND(0.056) | 0.79 | 399840 | 133.7 | 7.7 | 8.0 | ND(0.003) | ND(0.03) | 0.42
AES Hawaii, Inc. | 10673 | AB | 2 | 33360 | 12743 | 0.65 | 12.79 | 8.04 | ND(50) | 0.03 | D3684-94 - FICVAA | Subbituminous | 427620 | 135.2 | 8.1 | 8.0 | 0.25 | 0.12 | 0.94 | 411360 | 133.2 | 7.5 | 8.0 | ND(0.002) | ND(0.03) | 0.59
AES Hawaii, Inc. | 10673 | AB | 3 | 33485 | 12625 | 0.66 | 13 | 8.85 | 52 | 0.02 | D3684-94 - FICVAA | Subbituminous | 423900 | 137.2 | 9.4 | XB | 0.26 | 0.077 | 0.72 | 406560 | 133.7 | 8.2 | 8.0 | ND(0.002) | ND(0.03) | 0.33
Antelope Valley Station | 0013070000-06469 | B1 | 1 | 433349 | 10180 | 1.09 | 37.64 | 15.3 | 140 | 0.06 | EPA 7471 | Lignite | 2166565 | 154 | 15.4 | 5.4 | ND(0.13) | 0.33 | 6.76 | 1915792 | 86 | 18.9 | 6 | ND(0.01) | 0.21 | 0.16
Antelope Valley Station | 0013070000-06469 | B1 | 2 | 419526 | 10280 | 1.24 | 35.95 | 15.93 | 84 | 0.071 | EPA 7471 | Lignite | 2143628 | 151 | 15 | 5.4 | ND(0.18) | 0.36 | 6.94 | 1932952 | 82 | 18.4 | 6 | 0.02 | 0.66 | 6.8
Antelope Valley Station | 0013070000-06469 | B1 | 3 | 413661 | 10400 | 1.05 | 36.67 | 14.39 | 97 | 0.055 | EPA 7471 | Lignite | 2100474 | 154 | 14.8 | 5.4 | 0.14 | 0.14 | 6.81 | 1873657 | 84 | 18.4 | 5.6 | 0.02 | 0.27 | 5.96
Bailly | 0137560000-00995 | 7 and 8 | 1 | 177627 | 12725 | 3.16 | 14.25 | 8.87 | 713 | 0.07 | ASTM 3684 | Bituminous/Petroleum Coke | 2404954 | 176.3 | 8.63 | 5.63 | 0.036 | 2.92 | 2.41 | 2083127 | 54.5 | 15.5 | 7.0 | ND(0.002) | 0.28 | 2.22
Bailly | 0137560000-00995 | 7 and 8 | 2 | 179853 | 12735 | 3.12 | 14.78 | 8.88 | 459 | 0.08 | ASTM 3684 | Bituminous/Petroleum Coke | 2433488 | 167.3 | 8.22 | 5.7 | 0.05 | 1.95 | 2.65 | 2107800 | 53.9 | 14.5 | 7.0 | ND(0.002) | 0.24 | 2.04
Bailly | 0137560000-00995 | 7 and 8 | 3 | 175369 | 12813 | 2.5 | 15.0 | 9.86 | 766 | 0.06 | ASTM 3684 | Bituminous/Petroleum Coke | 2396825 | 175.1 | 8.19 | 6.28 | 0.06 | 2.76 | 2.22 | 2086775 | 54.2 | 15.06 | 7.0 | 0.003 | 0.3 | 2.16
Bay Front Plant Generating | 0137810000-03982 | 5 | 1 | 3911 | 12790 | 0.65 | 13.77 | 7.57 | 110 | 0.06 | ASTM 3684 | Bituminous | 232291 | 136 | 9.82 | 8.7 | 0.52 | 0.53 | 1.48 | 95812 | 135 | 8.10 | 9.0 | 0.79 | 0.4 | 1.27
Bay Front Plant Generating | 0137810000-03982 | 5 | 2 | 3913 | 12635 | 0.65 | 13.73 | 7.51 | 119 | 0.06 | ASTM 3684 | Bituminous | 195145 | 132 | 7.18 | 8.3 | 0.76 | 0.47 | 1.37 | 110435 | 132 | 7.15 | 9.0 | 0.57 | 1.83 | 1.2
Bay Front Plant Generating | 0137810000-03982 | 5 | 3 | 3934 | 12597 | 0.66 | 13.26 | 7.56 | 152 | 0.06 | ASTM 3684 | Bituminous | 191081 | 134 | 7.12 | 9.0 | 0.06 | 0.51 | 1.16 | 105389 | 134 | 7.17 | 9.1 | 0.32 | 2.36 | 1.18
Big Bend | 0184540000-00645 | BB03 | 1 | 133914 | 12730 | 3.15 | 9.55 | 11 | 1800 | 0.177 | EPA 7471 | Bituminous | 1440752 | 155 | 9.1 | 4.1 | XB | 4.56 | 2.25 | 1904069 | 52 | 13 | 7.3 | XB | 0.16 | 1.66
Big Bend | 0184540000-00645 | BB03 | 2 | 132229 | 12790 | 3.22 | 9.58 | 10.6 | 1800 | 0.113 | EPA 7471 | Bituminous | 1440242 | 155 | 9 | 4.4 | XB | 4.54 | 2.13 | 1907467 | 52 | 9.9 | 7.2 | XB | 0.09 | 1.34
Big Bend | 0184540000-00645 | BB03 | 3 | 132805 | 12980 | 3.08 | 9.69 | 10.2 | 1700 | 0.125 | EPA 7471 | Bituminous | 1421383 | 156 | 9 | 3.5 | XB | 4.14 | 2.07 | 1892516 | 52 | 12.4 | 7.1 | XB | 0.18 | 1.58
Big Brown | 0443720000-03497 | 1 | 1 | 310664 | 8690 | 1.01 | 25 | 23.7 | 100 | 0.287 | ASTM 6414 | Lignite | 2049164 | 183 | 14.67 | 5.6 | 2.22 | 7.14 | 26.73 | 2351953 | 167 | 12.4 | 6 | 0.08 | 13.82 | 21
Big Brown | 0443720000-03497 | 1 | 2 | 312513 | 8720 | 1.03 | 25.5 | 23 | 100 | 0.29 | ASTM 6414 | Lignite | 2067102 | 186 | 13.53 | 5.2 | 0.47 | 9.1 | 23.97 | 2345298 | 171 | 12.78 | 6.8 | 0.03 | 13.93 | 20.09
Big Brown | 0443720000-03497 | 1 | 3 | 298538 | 9050 | 1 | 26.1 | 21 | 200 | 0.287 | ASTM 6414 | Lignite | 2108492 | 185 | 13.79 | 5.2 | 0.2 | 12.41 | 19.25 | 2332550 | 164 | 13.47 | 6.4 | 0.03 | 15 | 17.94
Brayton Point | 0134330000-01619 | 1 | 1 | 76292 | 13684 | 0.83 | 6.56 | 7.6 | 300 | 0.08 | ASTM 3684 | Bituminous | 1219061 | 155 | 7.55 | 6.68 | 1.6 | 2.66 | 0.401 | 1031980 | 144 | 6.7 | 7.2 | 0.59 | 2.94 | 0.252
Brayton Point | 0134330000-01619 | 1 | 2 | 75446 | 13756 | 0.73 | 6.03 | 7.6 | 700 | 0.05 | ASTM 3684 | Bituminous | 1228778 | 153 | 7.7 | 6.8 | 2.06 | 2.88 | 0.318 | 1028595 | 144 | 7.4 | 7.1 | 0.58 | 2.46 | 0.279
Brayton Point | 0134330000-01619 | 1 | 3 | 76493 | 13754 | 0.76 | 6 | 7.43 | 700 | 0.06 | ASTM 3684 | Bituminous | 1237069 | 153 | 8.05 | 7.0 | 1.65 | 2.71 | 0.305 | 1056892 | 141 | 7.4 | 7.4 | 0.58 | 2.28 | 0.261
Brayton Point | 0134330000-01619 | 3 | 1 | 163357 | 13521 | 0.82 | 5.97 | 10.56 | 900 | 0.1 | ASTM 3684 | Bituminous | 2836137 | 123 | 8.9 | 8.1 | 2.11 | 2.75 | 0.39 | 2547085 | 127 | 8.3 | 8.6 | 0.54 | 2.19 | 0.508
Brayton Point | 0134330000-01619 | 3 | 2 | 157296 | 13583 | 0.76 | 6.48 | 10 | 1100 | 0.07 | ASTM 3684 | Bituminous | 2907989 | 123 | 9.3 | 7.25 | 1.46 | 2.41 | 0.379 | 2520381 | 126 | 7.6 | 9.4 | 0.62 | 1.59 | 0.376
Brayton Point | 0134330000-01619 | 3 | 3 | 178153 | 13875 | 0.77 | 6.04 | 8.14 | 900 | 0.07 | ASTM 3684 | Bituminous | 3025158 | 119 | 7.45 | 6.85 | 1.05 | 2.55 | 2.39 | 2493881 | 121 | 7.0 | 8.0 | XB | 2.48 | 2.37
Bruce Mansfield | 0147160000-06094 | 1 | 1 | 277790 | 13163 | 4.29 | 5.49 | 12.1 | 800 | 0.096 | ASTM 6414 | Bituminous | 3160872 | 137 | 7.3 | 7.1 | 0.33 | 6.68 | 1.22 | 3050116 | 52 | 15.37 | 7.4 | 0.14 | 1.43 | 5.3
Bruce Mansfield | 0147160000-06094 | 1 | 2 | 279761 | 13678 | 4.54 | 5.98 | 8.57 | 700 | 0.079 | ASTM 6414 | Bituminous | 3183792 | 144 | 6.69 | 7 | 0.57 | 7.65 | 1.62 | 3041448 | 53 | 14.75 | 7.1 | 0.14 | 2.11 | 6.15
Bruce Mansfield | 0147160000-06094 | 1 | 3 | 270273 | 13237 | 4.6 | 5.42 | 11.2 | 800 | 0.103 | ASTM 6414 | Bituminous | 2883648 | 141 | 6.66 | 6.3 | 0.34 | 6.81 | 1.39 | 2986566 | 52 | 12.76 | 6.8 | 0.13 | 0.96 | 6.54
Charles R. Lowman | 0001890000-00056 | 2 | 1 | 77844 | 13352 | 0.53 | 12 | 4.65 | 400 | 0.084 | ASTM 6414 | Bituminous | 338513 | 146 | 7.02 | 6.2 | XB | 2.74 | 1.72 | 961444 | 122 | 8.46 | 6.6 | 0.03 | 1.34 | 2.71
Charles R. Lowman | 0001890000-00056 | 2 | 2 | 76370 | 13356 | 0.52 | 12.1 | 5.29 | 400 | 0.077 | ASTM 6414 | Bituminous | 344092 | 146 | 6.45 | 6.7 | 1.23 | 3.16 | 1.72 | 955671 | 121 | 7.41 | 6.4 | 0.05 | 1.51 | 2.84
Charles R. Lowman | 0001890000-00056 | 2 | 3 | 77844 | 13352 | 0.53 | 12 | 4.93 | 300 | 0.08 | ASTM 6414 | Bituminous | 329689 | 147 | 7.48 | 6.8 | 2.72 | 2.8 | 1.59 | 963479 | 123 | 8.43 | 6.4 | 0.02 | 1.67 | 2.59
Cholla | 0008030000-00113 | 2 | 1 | 125445.6 | 11222 | 0.495 | 5.68 | 18.8 | ND(100) | 0.045 | EPA 7471 | Subbituminous | 943921 | 136 | 8.8 | 4.7 | XB | 0.61 | 4.24 | 986504 | 86.7 | 13.4 | 5.7 | XB | 0.18 | 3.34
Cholla | 0008030000-00113 | 2 | 2 | 123908.4 | 10955 | 0.51 | 6.13 | 20.49 | ND(100) | 0.04 | EPA 7471 | Subbituminous | 814490 | 137 | 9.2 | 3.8 | 0.95 | NA | 2.5 | 978703 | 86.7 | 13.5 | 5.9 | XB | 0.12 | 3.92
Cholla | 0008030000-00113 | 2 | 3 | 127224 | 11134 | 0.525 | 5.76 | 19.44 | ND(100) | 0.035 | EPA 7471 | Subbituminous | 915890 | 137 | 8.7 | 3.8 | XB | 1.21 | 2.86 | 990517 | 86.6 | 13.6 | 5.1 | XB | 0.12 | 3.73
Cholla | 0008030000-00113 | 3 | 1 | 116562.6 | 11863 | 0.43 | 7.49 | 11.94 | ND(100) | 0.04 | ASTM 3684 | Subbituminous | 938720 | 362 | 9.7 | 3.8 | XB | ND(0.08) | 1.84 | 1101701 | 159 | 8.5 | 6.2 | XB | 0.42 | 1.54
Cholla | 0008030000-00113 | 3 | 2 | 120860.6 | 12172 | 0.42 | 7.74 | 9.06 | ND(100) | 0.04 | ASTM 3684 | Subbituminous | 962341 | 358 | 9.5 | 3.9 | XB | 0.3 | 0.44 | 1085343 | 155 | 8.7 | 5.5 | XB | NA | 0.86
Cholla | 0008030000-00113 | 3 | 3 | 121240.5 | 12135 | 0.42 | 7.46 | 9.91 | ND(100) | 0.03 | ASTM 3684 | Subbituminous | 934887 | 357 | 9.3 | 3.7 | XB | 0.41 | 0.59 | 1077618 | 159 | 8.6 | 5.7 | XB | 0.33 | 1.08
Clay Boswell | 0126470000-01893 | 2 | 1 | 21481 | 12158 | 0.62 | 26.6 | 7.31 | ND(100) | 0.078 | ASTM 6414 | Subbituminous | 240607 | 179 | 10.5 | 6.0 | 2.29 | 1.51 | 1.33 | 252527 | 169 | 10.4 | 6.6 | 0.059 | 1.01 | 0.11
Clay Boswell | 0126470000-01893 | 2 | 2 | 21590 | 12087 | 0.62 | 26.5 | 7.97 | ND(100) | 0.043 | ASTM 6414 | Subbituminous | 268405 | 173 | 10.4 | 6.7 | 1.58 | 1 | 1.16 | 243054 | 166 | 10.5 | 7.2 | 0.003 | 0.27 | 0.18
Clay Boswell | 0126470000-01893 | 2 | 3 | 21620 | 12100 | 0.68 | 26.4 | 8.12 | ND(100) | 0.049 | ASTM 6414 | Subbituminous | 251138 | 175 | 11.4 | 6.4 | 0.67 | 0.93 | 2.02 | 238502 | 168 | 11.3 | 7.1 | ND(0.01) | 0.45 | 0.09
Clay Boswell | 0126470000-01893 | 3 | 1 | 125453 | 12072 | 0.61 | 26.1 | 7.67 | ND(100) | 0.054 | ASTM 6414 | Subbituminous | 1564633 | 139 | 10.8 | 5.4 | 0.01 | 0.22 | 5.25 | 1627639 | 51 | 13.3 | 6.0 | 0.002 | 0.04 | 4.85
Clay Boswell | 0126470000-01893 | 3 | 2 | 119812 | 12052 | 0.75 | 28.3 | 7.13 | ND(100) | 0.072 | ASTM 6414 | Subbituminous | 1560844 | 148 | 12.5 | 5.4 | ND(0.02) | 0.27 | 5.2 | 1668489 | 51 | 13.8 | 6.4 | ND(0.001) | 0.05 | 4.37
Clay Boswell | 0126470000-01893 | 3 | 3 | 120910 | 11972 | 0.68 | 27.8 | 8.54 | ND(100) | 0.063 | ASTM 6414 | Subbituminous | 1528607 | 144 | 11.4 | 5.5 | 0.05 | 0.53 | 4.49 | 1657786 | 51 | 13.6 | 6.7 | 0.002 | 0.05 | 4.38
Clay Boswell | 0126470000-01893 | 4 | 1 | 195911 | 12075 | 0.54 | 26.7 | 7.27 | ND(100) | 0.065 | ASTM 6414 | Subbituminous | 2133642 | 154 | 10.4 | 5.6 | 0.09 | 0.28 | 4.32 | 2191238 | 67 | 13.8 | 5.2 | 0.02 | 0.09 | 4.85
Clay Boswell | 0126470000-01893 | 4 | 2 | 197038 | 12197 | 0.57 | 26.3 | 7.44 | ND(100) | 0.063 | ASTM 6414 | Subbituminous | 2104866 | 141 | 11.5 | 5.2 | 2.62 | 0.94 | 1.29 | 2182773 | 68 | 14.0 | 5.6 | 0.17 | 0.38 | 5.04
Clay Boswell | 0126470000-01893 | 4 | 3 | 200509 | 11888 | 0.6 | 25 | 8.62 | ND(100) | 0.07 | ASTM 6414 | Subbituminous | 2015790 | 136 | 10.7 | 5.2 | 2.41 | 0.48 | 1.02 | 2151376 | 69 | 14.3 | 6.0 | 0.23 | 0.49 | 4.64
Cliffside | 0054160000-02721 | 1 | 1 | 15852 | 13803 | 0.85 | 7.34 | 9.16 | 1400 | 0.07 | ASTM 3684 | Bituminous | 220456 | 343.9 | 8.71 | 4.3 | 0.16 | 3.45 | 3.07 | 220456 | 195.1 | 8.05 | 6.4 | 0.33 | 2.26 | 3.2
Cliffside | 0054160000-02721 | 1 | 2 | 15818 | 13181 | 0.77 | 7.83 | 8.31 | 1400 | 0.05 | ASTM 3684 | Bituminous | 221841 | 342.6 | 8.61 | 4.3 | 0.08 | 3.28 | 4.31 | 221841 | 196.6 | 8.46 | 6.3 | 0.08 | 1.85 | 1.59
Cliffside | 0054160000-02721 | 1 | 3 | 15838 | 13804 | 0.85 | 7.26 | 8.44 | 1400 | 0.06 | ASTM 3684 | Bituminous | 214583 | 340.8 | 9.01 | 4.4 | 0.07 | 3.83 | 6.7 | 214583 | 191.7 | 7.95 | 6.1 | 0.08 | 3.29 | 2.1
Clifty Creek | 0092690000-00983 | 6 | 1 | 71060 | 12494 | 0.86 | 22.69 | 8.08 | 430 | 0.08 | ASTM 3684 | Subbituminous/Bituminous | 746218 | 382 | 12.01 | 3.9 | 0.38 | 2.23 | 10.61 | 989499 | 170 | 9.91 | 6.0 | 0.58 | 3 | 3.89
Clifty Creek | 0092690000-00983 | 6 | 2 | 69626 | 12578 | 0.86 | 22.74 | 8.66 | 374 | 0.08 | ASTM 3684 | Subbituminous/Bituminous | 760863 | 385 | 11.62 | 3.8 | 0.02 | 3.42 | 10.64 | 880430 | 166 | 8.64 | 6.0 | ND(0.01) | 4.2 | 4.45
Clifty Creek | 0092690000-00983 | 6 | 3 | 74180 | 12632 | 0.99 | 21.52 | 8.98 | 519 | 0.08 | ASTM 3684 | Subbituminous/Bituminous | 760318 | 382 | 11.42 | 3.7 | ND(0.01) | 3.28 | 11.01 | 947181 | 166 | 8.02 | 6.0 | 0.06 | 4.58 | 3.17
Clover Power Station | 0198760000-07213 | 2 | 1 | 143480 | 13089.3884 | NA | 4.35 | NA | 418.1913 | 0.115 | EPA 7471 | Bituminous | 694552 | 139 | 6 | 4.5 | 0.05 | 0.86 | 0.96 | 1636723 | 50.6 | 11.9 | 6.7 | 0.04 | 0.33 | 0.25
Clover Power Station | 0198760000-07213 | 2 | 2 | 143553 | 13605.3013 | NA | 3.42 | NA | 517.7055 | 0.16567 | EPA 7471 | Bituminous | 705133 | 139 | 6.15 | 4.7 | 0.03 | 0.94 | 1.09 | 1651090 | 50 | 12.3 | 6.5 | ND(0.02) | 0.27 | 0.12
Clover Power Station | 0198760000-07213 | 2 | 3 | 142146 | 13568.3094 | NA | 3.82 | NA | 623.8303 | 0.19755 | EPA 7471 | Bituminous | 696696 | 139 | 6.15 | 4.75 | 0.07 | 1.02 | 0.54 | 1659892 | 50 | 12.1 | 6.4 | 0.03 | ND(0.08) | 0.09
Colstrip | 0128250000-06076 | 3 | 1 | 370938 | 10779 | 0.72 | 11.4 | 16.8 | ND(100) | 0.063 | ASTM 6414 | Subbituminous | 3362880 | 140 | 9.58 | 4.6 | 1.62 | 2.09 | 0.98 | 3143106 | 89 | 15.6 | 6.2 | 0.114 | ND(0.69) | 7.51
Colstrip | 0128250000-06076 | 3 | 2 | 373615 | 10568 | 0.74 | 12 | 18 | ND(100) | 0.066 | ASTM 6414 | Subbituminous | 3391696 | 142 | 9.54 | 4.6 | 1.77 | 2.16 | 5.8 | 3124774 | 89 | 15.91 | 6.2 | 0.112 | ND(0.75) | 9.07
Colstrip | 0128250000-06076 | 3 | 3 | 366517 | 10688 | 0.76 | 11.4 | 17.3 | 100 | 0.067 | ASTM 6414 | Subbituminous | 3441304 | 136 | 10.71 | 4.8 | 1.47 | 2.57 | 4.85 | 3157213 | 89 | 15.61 | 6.2 | 0.074 | ND(0.64) | 1.75
Columbia | 0208560000-08023 | 1 | 1 | 205968 | 12261 | 0.43 | 30.43 | 6.49 | 292 | 0.1 | ASTM 3684 | Subbituminous | 2188995 | 406 | 13.48 | 3.8 | 0.02 | 0.89 | 13.64 | 2188995 | 149 | 11.7 | 6 | 0.004 | 2.28 | 9.76
Columbia | 0208560000-08023 | 1 | 2 | 210060 | 12120 | 0.43 | 29.09 | 6.2 | 347 | 0.1 | ASTM 3684 | Subbituminous | 2159390 | 403 | 13.91 | 4 | 0.03 | 5.5 | 12.66 | 2159390 | 156 | 11.85 | 5.8 | 0.004 | 1.82 | 9.98
Columbia | 0208560000-08023 | 1 | 3 | 208610 | 12182 | 0.42 | 29.77 | 5.38 | 303 | 0.1 | ASTM 3684 | Subbituminous | 2158955 | 409 | 11.85 | 4.2 | 0.04 | 0.43 | 13.67 | 2158955 | 157 | 11.88 | 6 | 0.004 | 2.21 | 9.99
Comanche | 0154660000-00470 | 2 | 1 | 133163 | 11891.6324 | 0.42524 | 27.1 | 6.4472 | ND(100) | 0.094047 | EPA 1631 | Subbituminous | 1246033 | 142.7778 | 10 | 5.4 | 1.70 | 2.95 | 4.61 | 1262340 | 149.4444 | 10.8 | 4.5 | 0.043 | 2.80 | 0.232
Comanche | 0154660000-00470 | 2 | 2 | 130385 | 11891.6324 | 0.42524 | 27.1 | 6.4472 | ND(100) | 0.096337 | EPA 1631 | Subbituminous | 1252037 | 150 | 9.4 | 6.5 | 2.15 | 0.87 | 4.27 | 1253400 | 157.7778 | 11.1 | 4.5 | ND(0.025) | 3.38 | 0.537
Comanche | 0154660000-00470 | 2 | 3 | 135158 | 11891.6324 | 0.42524 | 27.1 | 6.4472 | ND(100) | 0.086228 | EPA 1631 | Subbituminous | 1270674 | 141.6667 | 10.6 | 5.2 | 4.69 | 0.69 | 3.01 | 1290710 | 147.2222 | 11.6 | 4.5 | ND(0.038) | 2.70 | 0.214
Coronado | 0615720000-06177 | U1B | 1 | 159600 | 11187 | 0.53 | 13.26 | 17.76 | 100 | 0.035 | EPA 7371/1631 | Subbituminous | 1405808 | 136 | 10.05 | 4.94 | ND(0.05) | 0.88 | 1.95 | 1385518 | 48 | 13.7 | 5.71 | ND(0.026) | 0.037 | 3.02
Coronado | 0615720000-06177 | U1B | 2 | 158800 | 11439 | 0.49 | 13.62 | 17.08 | ND(100) | 0.039 | EPA 7371/1631 | Subbituminous | 1398779 | 135 | 9.58 | 4.27 | ND(0.05) | 0.76 | 1.73 | 1380391 | 47 | 12.9 | 5.42 | 0.073 | ND(0.061) | 2.74
Coronado | 0615720000-06177 | U1B | 3 | 162900 | 11262 | 0.51 | 13.53 | 18.25 | 200 | 0.031 | EPA 7371/1631 | Subbituminous | 1392035 | 143 | 10.27 | 3.97 | ND(0.05) | 1.03 | 1.77 | 1363637 | 49 | 13.8 | 5.39 | 0.097 | 0.115 | 2.67
Coyote | 0128190000-08222 | 1 | 1 | 180563 | 11080 | 1.33 | 35.23 | 11.1 | ND(200) | 0.088 | EPA 3050/7471 | Lignite | 2126971 | 163 | 13.8 | 8.2 | 0.49 | 1.15 | 9.73 | 2126971 | 109 | 15.2 | 9.8 | 0.052 | ND(0.017) | 8.695
Coyote | 0128190000-08222 | 1 | 2 | 184283 | 106.73 | 2.07 | 35.12 | 13.26 | ND(200) | 0.15 | EPA 3050/7471 | Lignite | 2111511 | 176 | 13.7 | 8.3 | 0.83 | 2.1 | 9.81 | 2111511 | 96 | 16.8 | 9.7 | 0.09 | 0.152 | ND(0.14)
Coyote | 0128190000-08222 | 1 | 3 | 179437 | 10904 | 1.76 | 35.11 | 12.68 | ND(200) | 0.094 | EPA 3050/7471 | Lignite | 2083307 | 177 | 14 | 8.2 | 1.2 | 2.18 | 10.6 | 2083307 | 102 | 16.7 | 9.7 | 0.049 | 0.279 | 11.338
Craig | 0301510000-06021 | C1 | 1 | 155754 | 12322 | 0.52 | 15.84 | 8.02 | 400 | 0.022 | EPA 1631/7371 | Subbituminous | 1842363 | 121 | 8.43 | 7.32 | ND(0.06) | 0.25 | 2.74 | 1741594 | 64 | 10.91 | 7.16 | ND(0.006) | 0.097 | 1.69
Craig | 0301510000-06021 | C1 | 2 | 159979 | 12447 | 0.52 | 14.81 | 8.17 | 200 | 0.025 | EPA 1631/7371 | Subbituminous | 1875084 | 124 | 8.33 | 7.24 | ND(0.06) | 0.22 | 1.93 | 1711326 | 64 | 13.04 | 7.11 | ND(0.005) | 0.083 | 1.61
Craig | 0301510000-06021 | C1 | 3 | 155324 | 12451 | 0.58 | 18.08 | 6.37 | 200 | 0.021 | EPA 1631/7371 | Subbituminous | 1919707 | 118 | 7.98 | 7.69 | ND(0.06) | 0.12 | 1.47 | 1767065 | 58 | 11.48 | 7.18 | 0.009 | 0.072 | 1.56
Craig | 0301510000-06021 | C3 | 1 | 157201 | 12549 | 0.47 | 17.09 | 6.63 | 100 | 0.011 | EPA 1631/7371 | Subbituminous | 1650793 | 138 | 9.74 | 6.57 | 0.46 | 0.52 | 0.24 | 1897089 | 80.6 | 10.38 | 8.43 | ND(0.005) | ND(0.05) | 0.7
Craig | 0301510000-06021 | C3 | 2 | 156035 | 12624 | 0.44 | 17.11 | 5.96 | ND(100) | 0.01 | EPA 1631/7371 | Subbituminous | 1651990 | 146 | 9.13 | 6.36 | 0.75 | 0.41 | 0.23 | 1902028 | 85.6 | 10.3 | 8.27 | ND(0.005) | ND(0.05) | 0.7
Craig | 0301510000-06021 | C3 | 3 | 153356 | 12562 | 0.49 | 17.94 | 6.4 | 200 | 0.009 | EPA 1631/7371 | Subbituminous | 1654007 | 133 | 8.66 | 6.36 | 0.73 | 0.19 | 0.18 | 1868838 | 79.4 | 10.36 | 8.03 | ND(0.005) | ND(0.05) | 0.66
Dunkirk | 0135730000-02554 | 2 | 1 | 32714 | 13907 | 2.31 | 5.76 | 7.4 | 811 | 0.13 | ASTM 3684 | Bituminous | 478725 | 303.4 | 8.0 | 5.1 | 0.16 | 7.56 | 2.49 | 481326 | 293.4 | 7.50 | 5.9 | 0.35 | 5.78 | 3.08
Dunkirk | 0135730000-02554 | 2 | 2 | 32650 | 14022 | 2.23 | 5.1 | 7.8 | 925 | 0.13 | ASTM 3684 | Bituminous | 460709 | 304.5 | 8.83 | 4.9 | .25 | 7.97 | 1.28 | 464347 | 295.2 | 8.11 | 5.8 | .13 | 3.86 | 2.08
Dunkirk | 0135730000-02554 | 2 | 3 | 31910 | 13819 | 2.25 | 6.6 | 8.92 | 880 | 0.13 | ASTM 3684 | Bituminous | 466192 | 306.4 | 8.47 | 4.4 | .32 | 8.43 | 2.91 | 469910 | 295.8 | 7.74 | 5.7 | 0.05 | 5.44 | 3.23
Dwayne Collier Battle Cogeneration Facility | 10384 | 2B | 1 | 12432 | 13820 | 0.73 | 4.5 | 7.16 | 1500 | ND(0.06) | EPA 7471 | Bituminous | 124965 | 167 | 7.4 | 4.3 | 2.03 | ND(0.05) | ND(0.17) | 135128 | 85 | 11.6 | 5 | 0.05 | ND(0.04) | ND(0.15)
Dwayne Collier Battle Cogeneration Facility | 10384 | 2B | 2 | 12391 | 13900 | 0.76 | 4.37 | 6.94 | 1800 | ND(0.06) | EPA 7471 | Bituminous | 120578 | 167 | 8 | 4.3 | 1.93 | 0.17 | 0.39 | 132796 | 86 | 11.6 | 5.1 | 0.026 | ND(0.05) | ND(0.166)
Dwayne Collier Battle Cogeneration Facility | 10384 | 2B | 3 | 11888 | 13930 | 0.77 | 4.43 | 6.42 | 1800 | ND(0.06) | EPA 7471 | Bituminous | 122308 | 169 | 7.8 | 4.3 | 1.85 | ND(0.06) | ND(0.20) | 132687 | 86 | 12.1 | 5.3 | ND(0.014) | ND(0.05) | ND(0.17)
Gaston | 0001950000-00026 | 1 | 1 | 82264 | 13560 | 0.8 | 6.97 | 13.2 | 300 | 0.054 | EPA 7471 | Bituminous | 914665 | 336 | 7.9 | 4.2 | 3.99 | 0.8 | 2.46 | 938079 | 128 | 6.3 | 7.1 | 0.57 | 3.63 | 1.81
Gaston | 0001950000-00026 | 1 | 2 | 78015 | 13300 | 1.03 | 6.58 | 13.8 | 300 | 0.067 | EPA 7471 | Bituminous | 893577 | 334 | 8.7 | 4.2 | 2.4 | 0.66 | 3.32 | 973011 | 124 | 7.0 | 6.9 | 0.31 | 4.54 | 2.72
Gaston | 0001950000-00026 | 1 | 3 | 72147 | 13640 | 0.83 | 7.33 | 12.1 | 400 | 0.057 | EPA 7471 | Bituminous | 931343 | 339 | 7.5 | 4.1 | 0.4 | 3.7 | 2.66 | 980478 | 128 | 6.1 | 6.5 | 0.93 | 3.81 | 1.64
George Neal south | 0123410000-07343 | 4 | 1 | 312422 | 12003 | 0.42 | 27.89 | 7.6 | 200 | 0.09 | ASTM 3684 | Subbituminous | 2633333 | 149 | 12.94 | 5.5 | 0.147 | 4.11 | 5.4 | 2630138 | 138 | 11.07 | 6.8 | 0.024 | 3.21 | 4.32
George Neal south | 0123410000-07343 | 4 | 2 | 305364 | 12014 | 0.44 | 28.31 | 7.61 | 100 | 0.08 | ASTM 3684 | Subbituminous | 2709436 | 153 | 13.04 | 6.2 | 0.058 | 3.57 | 6.78 | 2671453 | 142 | 11.65 | 7 | 0.048 | 3.58 | 5.34
George Neal south | 0123410000-07343 | 4 | 3 | 312314 | 11901 | 0.44 | 30.03 | 8.64 | 273 | 0.1 | ASTM 3684 | Subbituminous | 2688240 | 154 | 12.7 | 6.8 | ND(0.03) | 2.79 | 2.97 | 2660146 | 144 | 10.88 | 8.6 | 0.023 | 3.26 | 4.40
Gibson Generating Station (10/99 testing) | 0154700000-06113 | 3 | 1 | 209510 | 12530 | 1.71 | 13.6 | 13.1 | 1900 | 0.134 | ASTM 6414 | Bituminous | 2343261 | 158 | 7.92 | 5.6 | 4.77 | 8.84 | 2.15 | 2587937 | 171 | 6.60 | 5.9 | ND(0.04) | 5.08 | 4.34
Gibson Generating Station (10/99 testing) | 0154700000-06113 | 3 | 2 | 216693 | 12570 | 1.74 | 12.6 | 12.9 | 2200 | 0.142 | ASTM 6414 | Bituminous | 2353191 | 162 | 4.63 | 5.4 | 23.92 | 3.28 | 1.31 | 2952993 | 171 | 5.69 | 6.0 | ND(0.08) | 7.01 | 4.33
Gibson Generating Station (10/99 testing) | 0154700000-06113 | 3 | 3 | 215173 | 12570 | 1.71 | 12.8 | 13.1 | 2200 | 0.141 | ASTM 6414 | Bituminous | 2371609 | 163 | 8.20 | 5.2 | 4.09 | 9.67 | 1.62 | 3508960 | 173 | 7.26 | 5.8 | ND(0.04) | 9.31 | 4.02
Gibson Generating Station (03/00 testing) | 0154700000-06113 | 3 | 1 | 248127 | 11640 | 1.45 | 7.38 | 12.2 | 1700 | 0.117 | ASTM 6414 | Bituminous | 2544538 | 156 | 7.21 | 6.0 | 1.62 | 26.45 | 3.66 | 3195060 | 154 | 6.30 | 9.2 | 0.006 | 21 | 4.93
Gibson Generating Station (03/00 testing) | 0154700000-06113 | 3 | 2 | 240702 | 11630 | 1.45 | 7.81 | 12.9 | 1700 | 0.115 | ASTM 6414 | Bituminous | 2525292 | 157 | 7.92 | 6.2 | 1.03 | 31.29 | 2.4 | 3152365 | 154 | 7.11 | 8.8 | 0.007 | 21.83 | 3.93
Gibson Generating Station (03/00 testing) | 0154700000-06113 | 3 | 3 | 230739 | 11550 | 1.57 | 8.19 | 13.9 | 2200 | 0.123 | ASTM 6414 | Bituminous | 2551178 | 155 | 7.48 | 6.2 | 1.44 | 36.54 | 1.36 | 3189981 | 157 | 5.90 | 9.1 | 0.006 | 26.23 | 2.55
GRDA | 0074900000-00165 | 2 | 1 | 192022 | 12091 | 0.71 | 24.16 | 8.11 | 379 | 0.1 | ASTM 3684 | Subbituminous/Bituminous | 1795109 | 154.8 | 12.59 | 5.4 | 0.22 | 3.83 | 6.73 | 1974682 | 84.0 | 15.81 | 6.1 | 0.01 | 1.28 | 9.241
GRDA | 0074900000-00165 | 2 | 2 | 184341 | 12186 | 0.73 | 24.9 | 8.04 | 386 | 0.1 | ASTM 3684 | Subbituminous/Bituminous | 1814982 | 156.6 | 11.67 | 5.6 | 0.45 | 2.54 | 5.56 | 2007962 | 84.2 | 15.77 | 6.4 | 0.02 | 1.04 | 9.02
GRDA | 0074900000-00165 | 2 | 3 | 211706 | 12096 | 0.88 | 24.25 | 8.46 | 431 | 0.1 | ASTM 3684 | Subbituminous/Bituminous | 1808161 | 155.8 | 12.53 | 5.2 | 1.0 | 7.71 | 3.26 | 1970052 | 84.2 | 15.68 | 6.3 | 0.01 | 0.28 | 8.825
Intermountain | 0112080000-06481 | 2SGA | 1 | 281058 | 12986 | 0.68 | 7.52 | 9.16 | 300 | 0.02 | ASTM 3684 | Bituminous | 3312000 | 152 | 7.2 | 4.5 | ND(0.018) | 0.94 | 0.125 | 3312000 | 49 | 11.5 | 4.5 | 0.012 | ND(0.041) | 0.139
Intermountain | 0112080000-06481 | 2SGA | 2 | 279461 | 13022 | 0.67 | 7.77 | 9.36 | 200 | 0.02 | ASTM 3684 | Bituminous | 3336000 | 152 | 6.7 | 4.4 | ND(0.016) | 1.05 | 0.127 | 3336000 | 49 | 11.5 | 4.4 | 0.0065 | 0.077 | 0.325
Intermountain | 0112080000-06481 | 2SGA | 3 | 284219 | 12949 | 0.63 | 7.31 | 9.36 | 100 | 0.03 | ASTM 3684 | Bituminous | 3372000 | 149 | 6.6 | 5.1 | ND(0.017) | 1.21 | 0.145 | 3372000 | 48 | 11.5 | 5.1 | 0.0092 | 0.076 | 0.269
Jack Watson | 0126860000-02049 | 4 | 1 | 80122 | 13080 | 1.02 | 4 | 6.84 | 833 | 0.05 | EPA 7471 | Bituminous | 1072801 | 155 | 9.1 | 6.7 | 2.86 | 0.97 | 0.73 | 1043609 | 157 | 8.9 | 6.3 | 0.02 | 2.1 | 1.53
Jack Watson | 0126860000-02049 | 4 | 2 | 80893 | 13080 | 1.06 | 3.4 | 6.97 | 725 | 0.052 | EPA 7471 | Bituminous | 934375 | 148 | 8.4 | 6.7 | 3.9 | 0.92 | 0.2 | 961264 | 150 | 8.3 | 7.1 | 0.04 | 2.31 | 0.69
Jack Watson | 0126860000-02049 | 4 | 3 | 81111 | 13070 | 1.03 | 3.34 | 7.12 | 724 | 0.059 | EPA 7471 | Bituminous | 978658 | 146 | 7.9 | 6.8 | 3.66 | 0.47 | ND(0.15) | 971814 | 150 | 8.0 | 6.7 | ND(0.05) | 2.32 | 0.71
Jim Bridger | 0143540000-08066 | BW 74 | 1 | NA | 11821 | 0.71 | 19.03 | 11.83 | ND(100) | 0.08 | Other | Subbituminous | 2833202 | 147 | 9.6 | 5.8 | 0.04 | 2.1 | 4.4 | 2187085 | 54 | 12.8 | 5.8 | 0.053 | 0.212 | 5.6
Jim Bridger | 0143540000-08066 | BW 74 | 2 | NA | 11963 | 0.64 | 19.51 | 11.45 | ND(100) | 0.08 | Other | Subbituminous | 2701314 | 146 | 9.0 | 6.0 | 0.37 | 1.7 | 4.55 | 2133973 | 53 | 14.1 | 5.8 | 0.039 | 0.248 | 5.38
Jim Bridger | 0143540000-08066 | BW 74 | 3 | NA | 11973 | 0.69 | 19.55 | 10.85 | ND(100) | 0.06 | Other | Subbituminous | 2729912 | 145 | 9.1 | 5.8 | 0.06 | 1.5 | 3.66 | 2159407 | 54 | 13.4 | 5.8 | 0.028 | 0.168 | 4.87
Kline Township Cogen Facility | 50039 | GEN1 | 1 | 165225.691 | 5110 | 0.43 | 9.51 | 58.3 | 300 | 0.3 | EPA 7471 | Waste Anthracite | 322630 | 188 | 6.4 | 2.4 | 46.02 | ND(0.12) | 0.47 | 285771 | 173 | 6.9 | 5.2 | ND(0.006) | ND(0.05) | 0.07
Kline Township Cogen Facility | 50039 | GEN1 | 2 | 171535.0592 | 5050 | 0.44 | 8.54 | 58.7 | 200 | 0.4 | EPA 7471 | Waste Anthracite | 311820 | 186 | 7.4 | 2.4 | 44.56 | ND(0.06) | 0.41 | 278346 | 174 | 6.9 | 5.2 | ND(0.006) | ND(0.05) | 0.07
Kline Township Cogen Facility | 50039 | GEN1 | 3 | 176051.8616 | 4930 | 0.38 | 7.94 | 61 | 300 | 0.3 | EPA 7471 | Waste Anthracite | 327118 | 189 | 6.4 | 2.1 | 47.22 | ND(0.06) | 0.36 | 276877 | 174 | 6.1 | 5.2 | ND(0.006) | 0.063 | ND(0.075)
La Cygne | 0100000000-01241 | 1 | 1 | 290481 | 11800 | 1.22 | 25.5 | 11.4 | 300 | 0.11 | ASTM 6414 | Subbituminous | NA | 144 | 10.74 | 5.4 | 5.81 | 3.46 | 1.13 | 2871424 | 72 | 13.98 | 7.4 | 0.13 | ND(0.67) | 6.6
La Cygne | 0100000000-01241 | 1 | 2 | 277548 | 11740 | 1.31 | 24.7 | 11.7 | 300 | 0.102 | ASTM 6414 | Subbituminous | NA | 144 | 10.78 | 5.3 | 5.69 | 2.91 | ND(1.04) | 2856858 | 72 | 14.65 | 7.2 | 0.1 | ND(0.66) | 5.68
La Cygne | 0100000000-01241 | 1 | 3 | 284632 | 11800 | 1.2 | 23.4 | 10.8 | 300 | 0.098 | ASTM 6414 | Subbituminous | NA | 144 | 10.93 | 5.6 | 5.12 | ND(1.01) | ND(1.04) | 2897940 | 74 | 13.6 | 6.8 | 0.16 | ND(0.64) | 4.02
Laramie River Station | 0013070000-06204 | 1 | 1 | 207045 | 11860 | 0.52 | 31.05 | 7.84 | 87 | 0.103 | EPA 3051/3052/7471 | Subbituminous | 2330443 | 141.1 | 12.8 | 10 | 0.154 | 1.921 | 4.593 | 2376027 | 64.4 | 15.2 | 10.5 | XB | 0.171 | 2.835
Laramie River Station | 0013070000-06204 | 1 | 2 | 197203 | 11940 | 0.52 | 31.21 | 7.63 | 78 | 0.111 | EPA 3051/3052/7471 | Subbituminous | 2278573 | 138.3 | 11.9 | 10.1 | 0.023 | 1.3058 | 5.055 | 2295053 | 63.3 | 14.9 | 10.0 | XB | 0.072 | 3.501
Laramie River Station | 0013070000-06204 | 1 | 3 | 195728 | 11890 | 0.54 | 31.29 | 8.1 | 57 | 0.144 | EPA 3051/3052/7471 | Subbituminous | 2298553 | 136.1 | 11.6 | 10.1 | ND(0.02) | 1.866 | 4.562 | 2334062 | 63.3 | 15.7 | 7.8 | XB | ND(0.042) | 3.286
Laramie River Station | 0013070000-06204 | 3 | 1 | 208000 | 11820 | 0.49 | 30.8 | 7.4 | 86 | 0.118 | EPA 3051/3052/7471 | Subbituminous | 2648783 | 137.7 | 10.4 | 9.9 | ND(0.032) | 0.1368 | 0.3886 | 2648783 | 77.7 | 15.3 | 10.0 | 0.0158 | 0.0592 | 2.368
Laramie River Station | 0013070000-06204 | 3 | 2 | 213000 | 11990 | 0.49 | 30.83 | 7.51 | 66 | 0.142 | EPA 3051/3052/7471 | Subbituminous | 2776514 | 140.6 | 10.6 | 9.9 | 1.0417 | 0.3235 | 5.263 | 2776514 | 78.9 | 14.8 | 10 | 0.0173 | ND(0.046) | 2.7609
Laramie River Station | 0013070000-06204 | 3 | 3 | 210000 | 12070 | 0.47 | 30.98 | 7.06 | 79 | 0.114 | EPA 3051/3052/7471 | Subbituminous | 2645760 | 136.1 | 10.6 | 10.1 | 2.7544 | 0.2642 | 5.6211 | 2647467 | 78.9 | 14.9 | 9.8 | 0.0206 | ND(0.048) | 3.2811
Lawrence | 0002250000-01250 | 4 | 1 | 36186 | 12280 | 0.58 | 16.9 | 8.62 | 400 | 0.052 | ASTM 6414 | Subbituminous | 376788 | 172 | 8.82 | 6.6 | 0.18 | 1.32 | 3.99 | 401504 | 68 | 16.94 | 7.2 | 0.09 | ND(0.75) | 4.88
Lawrence | 0002250000-01250 | 4 | 2 | 38541 | 12260 | 0.45 | 18.3 | 7.03 | 200 | 0.044 | ASTM 6414 | Subbituminous | 382234 | 157 | 9.43 | 6.4 | 0.43 | ND(1.03) | 3.58 | 413938 | 66 | 15.09 | 7.8 | 0.17 | ND(0.77) | 4.92
Lawrence | 0002250000-01250 | 4 | 3 | 38095 | 12340 | 0.44 | 17.5 | 6.68 | 200 | 0.047 | ASTM 6414 | Subbituminous | 381990 | 169 | 9.19 | 7 | 0.19 | ND(1.13) | 3.86 | 425946 | 68 | 15.23 | 7.7 | 0.16 | ND(0.76) | 4.58
Leland Olds Station | 0013070000-02817 | 2 | 1 | 229813 | 10500 | 0.8 | 36.03 | 11.27 | 91 | ND(0.05) | EPA 7471 | Lignite | 1830157 | 199 | 12.1 | 5.3 | 0.49 | 0.2 | 2.74 | 1818264 | 182 | 12.9 | 5.8 | ND(0.004) | 0.69 | 3.41
Leland Olds Station | 0013070000-02817 | 2 | 2 | 187931 | 10700 | 1.07 | 36.26 | 10.73 | 104 | 0.056 | EPA 7471 | Lignite | 1895399 | 201 | 14.4 | 5.6 | 0.22 | 0.39 | 7.53 | 1879428 | 182 | 13.1 | 5.8 | ND(0.004) | 0.92 | 4.44
Leland Olds Station | 0013070000-02817 | 2 | 3 | 315756 | 10890 | 0.91 | 36.37 | 9.46 | 77 | ND(0.05) | EPA 7471 | Lignite | 1826759 | 205 | 14.8 | 5.6 | LS | LS | LS | 1818434 | 185 | 14 | 5.8 | LS | LS | LS
Lewis & Clark | 0128190000-06089 | B1 | 1 | 28727 | 10427 | 0.89 | 37.42 | 15.29 | ND(200) | 0.107 | 7471A | Lignite | 207448 | 195 | 14.6 | 4.5 | 1.05 | 15.1 | 10.68 | 197084 | 60 | 20.4 | 4.8 | 0.054 | 0.45 | 12.47
Lewis & Clark | 0128190000-06089 | B1 | 2 | 27281 | 10435 | 0.7 | 37.35 | 15.18 | ND(200) | 0.121 | 7471A | Lignite | 214924 | 198 | 14.5 | 4.4 | 1.55 | 12.58 | 7.77 | 186890 | 60 | 20.9 | 4.7 | ND(0.008) | 0.32 | 12.85
Lewis & Clark | 0128190000-06089 | B1 | 3 | 25593 | 10391 | 0.87 | 37.03 | 15.91 | ND(200) | 0.13 | 7471A | Lignite | 214924 | 203 | 14.5 | 4.4 | 1.3 | 5.79 | 9.41 | 185531 | 60 | 21.0 | 4.7 | ND(0.008) | 0.45 | 14.32
Limestone | 0089010000-00298 | LIM1 | 1 | 332740.499 | 10422 | 1.37 | 31.62 | 18.95 | ND(100) | 0.121 | ASTM 3684 | Lignite | 4920304 | 156 | 13.2 | 6.5 | 0.01 | 18.97 | 10.78 | 3452368 | 59 | 18.5 | 8 | 0.03 | 1.94 | 11.53
Limestone | 0089010000-00298 | LIM1 | 2 | 336256.8833 | 10700 | 1.52 | 31.79 | 17.44 | ND(100) | 0.171 | ASTM 3684 | Lignite | 4845548 | 162 | 13.6 | 6.5 | 0.01 | 19.78 | 10.56 | 3479552 | 61 | 19.5 | 8 | 0.24 | 2.3 | 11.72
Limestone | 0089010000-00298 | LIM1 | 3 | 344827.2384 | 10574 | 1.54 | 31.66 | 18.48 | ND(100) | 0.125 | ASTM 3684 | Lignite | 4818364 | 167 | 13.6 | 6.5 | 0.02 | 22.68 | 11.37 | 3330040 | 59 | 18.7 | 8 | 0.09 | 0.92 | 12.41
Logan Generating Plant | 10043 | Gen 1 | 1 | 75400 | 13758 | 1.13 | 1.08 | 10.21 | 1500 | 0.19 | ASTM 3684 | Bituminous | 769254 | 145 | 9.6 | 3.7 | 12.3 | 4.85 | 0.89 | 824752 | 86.7 | 12.9 | 5.3 | 0.0178 | 0.032 | 0.099
Logan Generating Plant | 10043 | Gen 1 | 2 | 75526 | 13767 | 1.08 | 1.02 | 10.06 | 1500 | 0.18 | ASTM 3684 | Bituminous | 759560 | 149 | 9.4 | 3.5 | 12.39 | 3.58 | 0.32 | 835164 | 87 | 12.6 | 5.2 | 0.0162 | 0.052 | 0.080
Logan Generating Plant | 10043 | Gen 1 | 3 | 75351 | 13757 | 1.08 | 1.12 | 9.95 | 1500 | 0.17 | ASTM 3684 | Bituminous | 763218 | 148 | 10 | 3.8 | 11.9 | 1.92 | 0.55 | 815007 | 87.2 | 13.4 | 5 | 0.0131 | 0.016 | 0.71
Mecklenburg Cogeneration Facility | 52007 | GEN 1 | 1 | 25138 | 14042 | 1.25 | 5.43 | 6.97 | 1901 | 0.09 | ASTM 3684 | Bituminous | 225117 | 149.4 | 9.08 | 4.4 | 10.46 | 3.14 | 6.24 | 271499 | 75.5 | 13.15 | 4.8 | ND(0.027) | 0.066 | ND(0.137)
Mecklenburg Cogeneration Facility | 52007 | GEN 1 | 2 | 26151 | 13877 | 1.55 | 5.64 | 7.73 | 1852 | 0.11 | ASTM 3684 | Bituminous | 243126 | 147.2 | 9.54 | 4.0 | 5.35 | 3.98 | ND(0.171) | 275747 | 74.4 | 13.59 | 4.4 | ND(0.026) | 0.065 | ND(0.134)
Mecklenburg Cogeneration Facility | 52007 | GEN 1 | 3 | 25488 | 13867 | 1.38 | 7.12 | 7.7 | 1925 | 0.09 | ASTM 3684 | Bituminous | 227410 | 147.2 | 9.81 | 4.0 | 6.52 | 2.87 | ND(0.175) | 272009 | 73.9 | 14.09 | 4.8 | ND(0.027) | ND(0.055) | ND(0.138)
Meramec | 0194360000-02104 | 4 | 1 | 126826 | 13254 | 0.89 | 14.09 | 7.75 | 3200 | 0.085 | ASTM 3684 | Subbituminous/Bituminous | 1610937 | 169 | 10.92 | 6.61 | 6.08 | 0.39 | 0.20 | 1670346 | 162 | 9.02 | 7.27 | ND(0.004) | 0.58 | 0.61
Meramec | 0194360000-02104 | 4 | 2 | 112566 | 13499 | 1.29 | 10.55 | 8.18 | 3860 | 0.12 | ASTM 3684 | Subbituminous/Bituminous | 1405042 | 172 | 10.29 | 6.82 | 7.36 | 1.07 | 0.35 | 1579124 | 163 | 8.91 | 7.20 | 0.006 | 1.69 | 0.87
Meramec | 0194360000-02104 | 4 | 3 | 105878 | 13415 | 1.27 | 11.95 | 7.85 | 3800 | 0.068 | ASTM 3684 | Subbituminous/Bituminous | 1278496 | 168 | 10.84 | 6.43 | 4.57 | 1.56 | 0.5 | 1448087 | 150 | 9.25 | 6.17 | ND(0.004) | 1.24 | 0.65
Monticello | 0443720000-06147 | 1 | 1 | 314734 | 8220 | 0.58 | 22.8 | 21.2 | 200 | 0.318 | ASTM 6414 | Lignite | 1925000 | 178 | 14.78 | 3.6 | 15.44 | 21.79 | 8.53 | 3171600 | 166 | 12.73 | 10.4 | 0.1 | 18.85 | 0.93
Monticello | 0443720000-06147 | 1 | 2 | 319432 | 8340 | 0.64 | 22.9 | 19.5 | 100 | 0.325 | ASTM 6414 | Lignite | 2214400 | 183 | 14.55 | 5.4 | 0.32 | 12.84 | 40.12 | 3613000 | 166 | 13.01 | 11.4 | 0.06 | 41.64 | 7.98
Monticello | 0443720000-06147 | 1 | 3 | 315757 | 7740 | 1.55 | 23.3 | 27.5 | 200 | 0.472 | ASTM 6414 | Lignite | 2330200 | 182 | 14.50 | 7.4 | 6.02 | 17.18 | 33.39 | 3615900 | 164 | 13.59 | 12.2 | 0.04 | 42.48 | 9.09
Monticello | 0443720000-06147 | 3 | 1 | 430100 | 8680 | 0.66 | 22.4 | 19.8 | 100 | 0.388 | ASTM 6414 | Lignite | 4179262 | 179 | 10.17 | 9.4 | 0.12 | 10.63 | 18.94 | 3664245 | 90 | 19.91 | 10.4 | 0.18 | 3.83 | 17.34
Monticello | 0443720000-06147 | 3 | 2 | 447000 | 8250 | 0.57 | 25 | 25.2 | 200 | 0.375 | ASTM 6414 | Lignite | 4120503 | 175 | 11.90 | 9.4 | 0.07 | 12.74 | 18.14 | 3735714 | 89 | 17.3 | 8.0 | 0.13 | 0.32 | 18.43
Monticello | 0443720000-06147 | 3 | 3 | 434600 | 8740 | 0.63 | 24.8 | 22.1 | 100 | 0.482 | ASTM 6414 | Lignite | 4322378 | 175 | 11.49 | 9.6 | 0.08 | 16.36 | 17.23 | 3764935 | 89 | 17.17 | 8.2 | 0.17 | 5.16 | 16.43
Montrose | 0100000000-02080 | 1 | 1 | 69976 | 10440 | 0.2 | 16.6 | 4.81 | 200 | 0.089 | ASTM 6414 | Subbituminous | 158080 | 155.5 | 11.05 | 5.2 | 1.69 | 1.62 | 5.23 | 665841 | 166.1 | 10.41 | 6.8 | 0.0052 | 2.03 | 4.29
Montrose | 0100000000-02080 | 1 | 2 | 70645 | 10300 | 0.2 | 15.7 | 5.72 | 100 | 0.107 | ASTM 6414 | Subbituminous | 159491 | 157.8 | 11.29 | 4.6 | 0.82 | 2.3 | 4.45 | 692741 | 167.8 | 10.74 | 6.6 | ND(0.005) | 2.08 | 4.72
Montrose | 0100000000-02080 | 1 | 3 | 68841 | 10500 | 0.21 | 17.4 | 5 | 100 | 0.103 | ASTM 6414 | Subbituminous | 158977 | 161.7 | 11.37 | 4.2 | 1.51 | 2.66 | 4.33 | 673398 | 167.8 | 11.17 | 6.0 | ND(0.003) | 1.92 | 4.70
Navajo | 0165720000-04941 | 3 | 1 | 277000 | 12771 | 0.53 | 11.53 | 7.8 | 200 | 0.040 | EPA 7371/1631 | Bituminous | 3055474 | 157 | 8.89 | 6.23 | ND(0.05) | 2.39 | 2.91 | 3000253 | 49 | 13.8 | 5.96 | 0.045 | ND(0.06) | 3.07
Navajo | 0165720000-04941 | 3 | 2 | 277300 | 12700 | 0.57 | 12.13 | 7.74 | 200 | 0.024 | EPA 7371/1631 | Bituminous | 3004856 | 152 | 8.53 | 5.88 | ND(0.05) | 0.38 | 3.3 | 2992900 | 49 | 13.8 | 5.82 | 0.019 | ND(0.06) | 3.2
Navajo | 0165720000-04941 | 3 | 3 | 278500 | 12850 | 0.56 | 12.35 | 7.11 | ND(100) | 0.027 | EPA 7371/1631 | Bituminous | 3077836 | 156. | 8.76 | 6.00 | ND(0.045) | 0.52 | 2.92 | 3047161 | 49 | 14.1 | 5.85 | 0.011 | ND(0.06) | 3.17
Nelson Dewey | 0208560000-04054 | 1 | 1 | 39446 | 13006 | 1.48 | 22.4 | 5.04 | 141 | 0.06 | ASTM 3684 | Subbituminous/Petroleum Coke | 387802 | 254 | 10.75 | 4.4 | 0.0224 | 0.45 | 2.95 | 365757 | 258 | 11.1 | 4.2 | ND(0.092) | 0.24 | 3.11
Nelson Dewey | 0208560000-04054 | 1 | 2 | 37930 | 13052 | 1.37 | 21.52 | 4.83 | 151 | 0.06 | ASTM 3684 | Subbituminous/Petroleum Coke | 379100 | 257 | 10.34 | 4.3 | 0.0167 | 0.22 | 2.03 | 364242 | 258 | 10.78 | 4.2 | ND(0.036) | 0.15 | 2.24
Nelson Dewey | 0208560000-04054 | 1 | 3 | 37886 | 12984 | 1.35 | 23.56 | 4.93 | 95 | 0.06 | ASTM 3684 | Subbituminous/Petroleum Coke | 390626 | 260 | 10.29 | 3.8 | 0.0191 | 0.11 | 1.97 | 371406 | 264 | 10.91 | 3.8 | ND(0.035) | 0.24 | 2.33
Newton | 0032530000-06017 | 2 | 1 | 206681 | 11025 | 0.44 | 24.31 | 9.15 | 178 | 0.074 | EPA 7473 | Subbituminous | 1882980 | 169 | 14.98 | 4.0 | ND(0.08) | 0.55 | 9.16 | 2113031 | 169 | 13.51 | 5.84 | ND(0.007) | 1.9 | 6.8
Newton | 0032530000-06017 | 2 | 2 | 204152.1624 | 11105 | 0.4 | 27.64 | 7.36 | ND(50) | 0.068 | EPA 7473 | Subbituminous | 1830477 | 150 | 14.15 | 4.05 | ND(0.07) | 0.59 | 9.28 | 2050761 | 163 | 11.7 | 5.86 | ND(0.005) | 1.4 | 6
Newton | 0032530000-06017 | 2 | 3 | 202528.828 | 11019 | 0.38 | 28.56 | 7.73 | ND(50) | 0.070 | EPA 7473 | Subbituminous | 1901994 | 164 | 13.82 | 3.96 | ND(0.16) | 1.56 | 8.77 | 2036644 | 170 | 14.94 | 5.08 | ND(0.005) | 1.8 | 7.1
Northern States Power - Sherburne County Generating Plant | 0137810000-06090 | #3 | 1 | 331255 | 11770 | 0.81 | 26.67 | 11.31 | 85 | 0.08 | ASTM 3684 | Subbituminous | 3344159 | 145 | 11.67 | 3.8 | ND(0.01) | 0.51 | 10.43 | 3451947 | 80 | 11.49 | 6.3 | 0.1 | 0.16 | 6.88
Northern States Power - Sherburne County Generating Plant | 0137810000-06090 | #3 | 2 | 336080 | 11670 | 0.68 | 25.5 | 10.99 | 93 | 0.08 | ASTM 3684 | Subbituminous | 3362593 | 147 | 12.02 | 3.6 | ND(0.01) | 0.22 | 10.56 | 3222806 | 80 | 17.86 | 6.6 | 0.11 | 0.14 | 9.67
Northern States Power - Sherburne County Generating Plant | 0137810000-06090 | #3 | 3 | 341562 | 11541 | 0.78 | 25.46 | 12.23 | 128 | 0.07 | ASTM 3684 | Subbituminous | 3315734 | 150 | 12.03 | 4.2 | ND(0.01) | 0.18 | 9.56 | 3359506 | 81 | 15.02 | 6.5 | 0.22 | 0.19 | 7.93
Platte | 0406060000-00059 | 1 | 1 | 35418 | 12230 | 0.45 | 31.68 | 7.63 | 177 | 0.11 | ASTM 3684 | Subbituminous | 382795 | 411.8 | 12.38 | 4.5 | 0.03 | 3.8 | 9 | 403992 | 153.4 | 12.15 | 5.9 | 0.022 | 1.22 | 7.35
Platte | 0406060000-00059 | 1 | 2 | 37782 | 12211 | 0.43 | 29.14 | 6.94 | 174 | 0.09 | ASTM 3684 | Subbituminous | 377498 | 413.2 | 13.61 | 4.2 | 0.03 | 1.79 | 10.56 | 392228 | 158.0 | 14.24 | 5.7 | 0.023 | 0.66 | 14.33
Platte | 0406060000-00059 | 1 | 3 | 33011 | 12284 | 0.42 | 31.22 | 7.11 | 191 | 0.07 | ASTM 3684 | Subbituminous | 379912 | 415.9 | 15.08 | 2.9 | 0.03 | 4.41 | 11.69 | 402733 | 152.9 | 13.42 | 5.9 | 0.019 | 1.27 | 12.5
Polk Power | 0184540000-07242 | 1 | 1 | 91456 | 11965 | 3.11 | 9.99 | 13.1 | 1100 | ND(0.1) | EPA 7471 | Bituminous | [7 empty] | 1430191 | 171 | 7.1 | 12.2 | ND(0.01) | 0.39 | 3.55
Polk Power | 0184540000-07242 | 1 | 2 | 88709 | 12934 | 3.12 | 10.7 | 10.1 | 1000 | ND(0.1) | EPA 7471 | Bituminous | [7 empty] | 1453617 | 172 | 6.9 | 11.6 | ND(0.01) | 0.31 | 3.55
Polk Power | 0184540000-07242 | 1 | 3 | 71375 | 12958 | 3.36 | 11.1 | 9.67 | 1100 | ND(0.1) | EPA 7471 | Bituminous | [7 empty] | 1414052 | 171 | 6.9 | 11.9 | ND(0.01) | 0.13 | 3.55
Port Washington | 0208470000-04040 | 4 | 1 | 29740 | 14025 | 1.49 | 2.43 | 7.4 | 1148 | 0.09 | ASTM 3684 EPA 7473 and 7471A | Bituminous | 344842 | 403.8 | 7.38 | 4.3 | ND(0.008) | 4.02 | 10.79 | 344842 | 204.5 | 6.9 | 6.0 | ND(0.0066) | 5.34 | 2.55
Port Washington | 0208470000-04040 | 4 | 2 | 30173 | 13947 | 1.55 | 2.46 | 7.42 | 1241 | 0.09 | ASTM 3684 EPA 7473 and 7471A | Bituminous | 340791 | 406.7 | 8.2 | 4.3 | ND(0.02) | 7.19 | 10.22 | 340791 | 206.3 | 6.89 | 6.0 | ND(0.0065) | 4.87 | 2.54
Port Washington | 0208470000-04040 | 4 | 3 | 29648 | 13982 | 1.5 | 2.15 | 7.44 | 1257 | 0.09 | ASTM 3684 EPA 7473 and 7471A | Bituminous | 339646 | 406.4 | 7.41 | 4.5 | ND(0.009) | 5.87 | 9.12 | 339646 | 206.8 | 7.04 | 6.0 | ND(0.0635) | 5.43 | 2.53
Presque Isle | 0208470000-01769 | 5 | 1 | 31232 | 12771.6186 | 1.0136 | 5.29 | 9.7983 | 180.5512 | 0.045402 | Proposed ASTM Method | Bituminous/Petroleum Coke | 407436.4299 | 170 | 9.5 | 5.5 | 3.923 | 0.41 | 0.12114 | 308484.3302 | 171.1111 | 9.2 | 5.4 | 0.0093182 | 0.62432 | 0.9225
Presque Isle | 0208470000-01769 | 5 | 2 | 30874 | 12798.9045 | 1.0218 | 5.07 | 9.9442 | 220.1622 | 0.040029 | Proposed ASTM Method | Bituminous/Petroleum Coke | 421072.6922 | 172.2222 | 9.4 | 5 | 3.1961 | 0.58705 | 0.050318 | 321648.2675 | 172.7778 | 9.2 | 5 | 0.0037273 | 0.72682 | 0.090386
Presque Isle | 0208470000-01769 | 5 | 3 | 31922 | 12765.62 | 1.0361 | 5.41 | 10.3816 | 170.2083 | 0.043345 | Proposed ASTM Method | Bituminous/Petroleum Coke | 416619.5843 | 174.4444 | 9.4 | 4.9 | 4.5286 | 0.40068 | 0.21 | 337525.5253 | 171.6667 | 9.3 | 5.2 | 0.041909 | 0.62432 | 0.80136
Presque Isle | 0208470000-01769 | 6 | 1 | 36121 | 12765.62 | 0.40707 | 21.39 | 7.022 | 209.897 | 0.068694 | Proposed ASTM Method | Bituminous/Petroleum Coke | 304913.0091 | 375.5556 | 14.8 | 2.1 | 0.046591 | 0.014909 | 7.0352 | 329268.3318 | 195 | 14.4 | 4 | 0.0027955 | 0.54045 | 5.9543
Presque Isle | 0208470000-01769 | 6 | 2 | 36399 | 12026.4597 | 0.41536 | 20.55 | 6.9855 | 250.472 | 0.06545 | Proposed ASTM Method | Bituminous/Petroleum Coke | 318501.6991 | 381.6667 | 14.1 | 2 | ND(0.02) | 0.14909 | 7.2775 | 328624.4066 | 195.5556 | 13.7 | 3.8 | ND(0.005) | 0.64295 | 6.4389
Presque Isle | 0208470000-01769 | 6 | 3 | 36525 | 12066.7086 | 0.41515 | 20.51 | 7.0827 | 210.0893 | 0.070449 | Proposed ASTM Method | Bituminous/Petroleum Coke | 311204.4469 | 387.7778 | 13.8 | 2.1 | ND(0.03) | 0.1025 | 6.7557 | 331716.6066 | 196.6667 | 13.7 | 3.6 | ND(0.004) | 0.52182 | 6.1686
Presque Isle | 0208470000-01769 | 9 | 1 | 27400 | 12051.8304 | 1.0229 | 5.17 | 10.2816 | 200.3585 | 0.026363 | Proposed ASTM Method | Subbituminous | 371896.5178 | 153.8889 | 10.1 | 4.9 | 2.4414 | 0.55909 | 1.4909 | 299943.4019 | 151.6667 | 9.5 | 6.1 | 0.048455 | 0.69886 | 0.57773
Presque Isle | 0208470000-01769 | 9 | 2 | 27636 | 12694.2951 | 1.0432 | 5.1 | 10.0527 | 209.6944 | 0.048472 | Proposed ASTM Method | Subbituminous | 363848.3027 | 152.7778 | 9.7 | 4.9 | 2.6557 | 0.64295 | 0.22364 | 312538.1705 | 151.1111 | 9.5 | 5.8 | 0.022364 | 0.84795 | 0.78273
Presque Isle | 0208470000-01769 | 9 | 3 | 27550 | 12772.392 | 1.0432 | 5.1 | 9.9895 | 180.1897 | 0.043203 | Proposed ASTM Method | Subbituminous | 370661.3368 | 153.3333 | 9.8 | 5.2 | 2.5998 | 0.54045 | 0.14909 | 296973.5307 | 152.2222 | 9.4 | 5.9 | ND(0.004) | 0.615 | 0.68023
R. D. Morrow Sr. Generating plant | 0175680000-06061 | 2 | 1 | 71013 | 13145 | 1.11 | 1.41 | 10.1 | 900 | ND(0.1) | EPA 7471 | Bituminous | 850873 | 166 | 7.9 | 7.3 | 0.044 | 8.22 | 3.36 | 869922 | 83 | 12.8 | 7.6 | ND(0.041) | 1.53 | 3.72
R. D. Morrow Sr. Generating plant | 0175680000-06061 | 2 | 2 | 73853 | 12982 | 1.11 | 1.71 | 11 | 900 | ND(0.1) | EPA 7471 | Bituminous | 869922 | 166 | 7.5 | 6.9 | ND(0.013) | 6.51 | 3.21 | 888834 | 88 | 11.8 | 7.2 | ND(0.024) | 1.37 | 3.45
R. D. Morrow Sr. Generating plant | 0175680000-06061 | 2 | 3 | 68743 | 12876 | 1.05 | 1.83 | 11.6 | 700 | ND(0.1) | EPA 7471 | Bituminous | 808602 | 167 | 7.2 | 6.8 | ND(0.015) | 5.51 | 2.62 | 823039 | 88 | 12.8 | 7.2 | ND(0.026) | 0.86 | 3.49
R.M. Heskett Station | 0128190000-02790 | B2 | 1 | 36399 | 10828 | 1.63 | 34.77 | 11.85 | ND(200) | 0.098 | EPA 7471A | Lignite | 381222 | 164 | 14 | 8.6 | 3.26 | 3.71 | 2.27 | 356994 | 159 | 14.7 | 7.9 | 0.077 | 1.049 | 3.23
R.M. Heskett Station | 0128190000-02790 | B2 | 2 | 35751 | 10887 | 1.14 | 34.96 | 10.24 | ND(200) | 0.088 | EPA 7471A | Lignite | 360188 | 157 | 14.7 | 8.6 | 2.02 | 0.66 | 1.8 | 340717 | 153 | 14.6 | 8 | 0.051 | 0.293 | 3.832
R.M. Heskett Station | 0128190000-02790 | B2 | 3 | 36658 | 10666 | 1.19 | 34.49 | 12.03 | ND(200) | 0.073 | EPA 7471A | Lignite | 338645 | 166 | 15 | 8.2 | 5.28 | 0.31 | 1.98 | 333208 | 161 | 14.6 | 8.2 | 0.038 | 0.131 | 3.266
Rawhide | 0151430000-06761 | 101 | 1 | 111122 | 11867 | 0.31 | 20.51 | 7.26 | 133 | 0.07 | ASTM 3684 | Subbituminous | 1088760 | 171.2 | 12.65 | 5.1 | 0.22 | 1.22 | 11.01 | 1088760 | 103.8 | 12.78 | 6.0 | 0.20 | 0.63 | 9
Rawhide | 0151430000-06761 | 101 | 2 | 103104 | 12003 | 0.3 | 25.55 | 7.31 | 118 | 0.07 | ASTM 3684 | Subbituminous | 1055239 | 170.5 | 12.86 | 4.2 | 1.79 | 0.77 | 11.99 | 1055239 | 104.9 | 16.27 | 5.5 | ND(0.01) | 0.59 | 8.53
Rawhide | 0151430000-06761 | 101 | 3 | 105518 | 11932 | 0.3 | 23.44 | 7.48 | 129 | 0.08 | ASTM 3684 | Subbituminous | 1068097 | 171.1 | 12.27 | 5.6 | 3.22 | 0.39 | 12.65 | 1068097 | 103.3 | 16.19 | 6.0 | 0.05 | 0.82 | 7.5
Salem Harbor | 0134330000-01626 | 3 | 1 | 49538 | 13889 | 0.7 | 9.59 | 5.42 | 100 | 0.03 | ASTM 3684 | Bituminous | 705491 | 124 | 8.2 | 8.8 | 2.81 | 0.22 | 0.34 | 730321 | 128 | 8.0 | 9.6 | 0.0419 | 0.1756 | 0.24
Salem Harbor | 0134330000-01626 | 3 | 2 | 48150 | 13850 | 0.69 | 9.64 | 5.72 | 100 | 0.02 | ASTM 3684 | Bituminous | 672460 | 126 | 8.3 | 8.5 | 2.83 | 0.034 | 0.14 | 701425 | 128 | 8.2 | 8.3 | 0.0692 | 0.0491 | 0.11
Salem Harbor | 0134330000-01626 | 3 | 3 | 48689 | 13707 | 0.74 | 8.63 | 6.53 | 100 | 0.03 | ASTM 3684 | Bituminous | 677049 | 127 | 8.8 | 8.0 | 2.85 | 0.042 | 0.14 | 711038 | 130 | 7.9 | 8.4 | 0.0527 | 0.0527 | 0.14
Sam Seymour | 0112690000-06179 | 3 | 1 | 136862 | 11773.309 | 0.53539 | 23.42 | 7.2473 | 22 | 0.139 | EPA 7471A | Subbituminous | 742598 | 152 | 9.9 | 4.5 | 0.02 | 2.02 | 6.12 | 707687 | 57.1 | 17.6 | 8 | 0.04 | 0.16 | 8.25
Sam Seymour | 0112690000-06179 | 3 | 2 | 136755 | 11897.5431 | 0.47047 | 23.48 | 6.9132 | 19 | 0.115 | EPA 7471A | Subbituminous | 771746 | 150 | 13.3 | 4.7 | ND(0.01) | 3.07 | 4.83 | 727462 | 53.9 | 20.1 | 8 | 0.07 | 0.20 | 8.97
Sam Seymour | 0112690000-06179 | 3 | 3 | 138096 | 11964.5399 | 0.4659 | 22.73 | 7.8556 | 19 | 0.114 | EPA 7471A | Subbituminous | 664148 | 147 | 7 | 4.75 | ND(0.01) | 3.9 | 8.66 | 656564 | 56.1 | 18.1 | 8 | 0.04 | 0.23 | 8.07
San Juan | 0154730000-02451 | 2 | 1 | 157925 | 9976 | 0.67 | 5.71 | 29.97 | 200 | 0.045 | EPA 7371/1631 | Subbituminous | 1046292 | 145.5 | 8.96 | 5.61 | ND(0.03) | 5.34 | 4.97 | 1046292 | 47.7 | 14.42 | 5.8 | 0.041 | 0.38 | 6.03
San Juan | 0154730000-02451 | 2 | 2 | 142879 | 10946 | 0.73 | 5.35 | 23.78 | 100 | 0.051 | EPA 7371/1631 | Subbituminous | 962604 | 136.6 | 8.37 | 5.32 | 0.07 | 2.88 | 3.71 | 962604 | 47.7 | 13.73 | 5.7 | 0.071 | 0.32 | 4.07
San Juan | 0154730000-02451 | 2 | 3 | 148399 | 10354 | 0.82 | 5.17 | 27.55 | 200 | 0.065 | EPA 7371/1631 | Subbituminous | 964490 | 146.6 | 9.41 | 4.63 | ND(0.05) | 4.61 | 3.29 | 964490 | 48.3 | 14.54 | 5.16 | 0.048 | 0.27 | 4.1
Scrubgrass Generating Company L. P. | 50974 | GEN1 | 1 | 59438 | 8509 | 1.49 | 10.47 | 39.74 | 600 | 0.55 | ASTM 3684 | Waste Bituminous | 217768 | 159 | 8.7 | 7.2 | 141.1 | 0.52 | ND(0.12) | 233086 | 156 | 8.4 | 7.3 | ND(0.0043) | 0.0495 | ND(0.1205)
Scrubgrass Generating Company L. P. | 50974 | GEN1 | 2 | 59438 | 8520 | 1.52 | 11.21 | 37 | 600 | 0.52 | ASTM 3684 | Waste Bituminous | 222024 | 161 | 8.8 | 6.7 | 98.6 | 0.33 | ND(0.10) | 246691 | 157 | 8.5 | 7.0 | ND(0.0043) | 0.0373 | ND(0.1196)
Scrubgrass Generating Company L. P. | 50974 | GEN1 | 3 | 61826 | 7996 | 1.4 | 9.06 | 43.05 | 600 | 0.51 | ASTM 3684 | Waste Bituminous | 213797 | 163 | 8.6 | 6.3 | 62.62 | 0.18 | ND(0.12) | 248881 | 158 | 8.3 | 7 | ND(0.0041) | 0.0313 | ND(0.1141)
SEI - Birchwood Power Facility | 54304 | 1 | 1 | 76807 | 12650 | 0.77 | 5.77 | 13.3 | 846 | 0.11 | EPA 7471 | Bituminous | 776654 | 134 | 8.7 | 5.9 | 11.31 | 0.25 | 0.19 | 849391 | 90 | 12.6 | 6 | 0.009 | 0.29 | 0.18
SEI - Birchwood Power Facility | 54304 | 1 | 2 | 75641 | 12570 | 0.79 | 6.05 | 13.8 | 954 | 0.11 | EPA 7471 | Bituminous | 763255 | 132 | 8.9 | 5.8 | 8 | 0.21 | 0.15 | 847458 | 90 | 13 | 6.2 | 0.01 | ND(0.14) | 0.1
SEI - Birchwood Power Facility | 54304 | 1 | 3 | 76065 | 12440 | 0.83 | 5.47 | 14.7 | 952 | 0.11 | EPA 7471 | Bituminous | 747652 | 136 | 9.4 | 5.7 | 10.21 | 0.21 | ND(0.27) | 867496 | 90 | 12.7 | 5.9 | 0.013 | ND(0.13) | ND(0.18)
Shawnee Fossil Plant | 0186420000-01379 | 3 | 1 | 46649 | 12882 | 0.48 | 12.2 | 8.78 | 200 | 0.022 | ASTM 6414 | Bituminous/Subbituminous | 603793 | 159 | 6.97 | 8.2 | 2.26 | ND(0.82) | ND(1.03) | 633712 | 152 | 6.28 | 8.8 | 0.05 | ND(0.86) | 0.57
Shawnee Fossil Plant | 0186420000-01379 | 3 | 2 | 48001 | 12714 | 0.5 | 13.4 | 9.69 | 200 | 0.039 | ASTM 6414 | Bituminous/Subbituminous | 613149 | 157 | 6.74 | 8.2 | 2.14 | 0.7 | ND(0.94) | 654382 | 149 | 7.39 | 9 | 0.08 | ND(0.81) | ND(1.01)
Shawnee Fossil Plant | 0186420000-01379 | 3 | 3 | 47095 | 12777 | 0.49 | 12.5 | 9.68 | 100 | 0.024 | ASTM 6414 | Bituminous/Subbituminous | 616736 | 157 | 6.68 | 8.6 | 2.37 | ND(0.79) | ND(0.92) | 645238 | 153 | 6.75 | 9 | ND(0.09) | ND(0.80) | ND(0.91)
St Clair Power Plant | 0051090000-01743 | 4 | 1 | 65723 | 12430 | 0.94 | 22.6 | 7.4 | 400 | 0.06 | ASTM 6414 | Subbituminous/Bituminous | 707478 | 138 | 8.23 | 7.4 | 1.91 | 1.73 | 1.49 | 638440 | 137 | 7.43 | 7.8 | ND(0.177) | 0.99 | 2.21
St Clair Power Plant | 0051090000-01743 | 4 | 2 | 65129 | 12670 | 0.96 | 23.3 | 6.36 | 300 | 0.055 | ASTM 6414 | Subbituminous/Bituminous | 717298 | 140 | 8.57 | 7.2 | 2.2 | 1.63 | 1.07 | 686046 | 142 | 8.25 | 8.4 | ND(0.061) | 0.97 | 2.62
St Clair Power Plant | 0051090000-01743 | 4 | 3 | 64469 | 12580 | 0.96 | 22.9 | 6.24 | 300 | 0.069 | ASTM 6414 | Subbituminous/Bituminous | 778622 | 141 | 7.70 | 8.0 | 0.71 | 1.4 | 3.09 | 670801 | 141 | 7.47 | 8.8 | ND(0.113) | 0.9 | 3.55
Stanton Station | 0195140000-02824 | 1 | 1 | 91172 | 10674 | 1.21 | 36.3 | 9.79 | ND(70) | 0.086 | EPA 3051/7471 | Lignite | 317712 | 173.3 | 12.89 | 6.9 | ND(0.21) | 0.099 | 7.34 | 317712 | 191.1 | 13.36 | 6.4 | ND(0.026) | 0.28 | 7.35
Stanton Station | 0195140000-02824 | 1 | 2 | 91172 | 10749 | 1.68 | 37.5 | 10.95 | ND(70) | 0.105 | EPA 3051/7471 | Lignite | 292227 | 157.2 | 12.22 | 6.7 | ND(0.083) | 0.08 | 6.83 | 292227 | 150.0 | 13.77 | 6.9 | ND(0.014) | 0.27 | 7.17
Stanton Station | 0195140000-02824 | 1 | 3 | 91625 | 10703 | 1.01 | 37.3 | 10.03 | 81 | 0.056 | EPA 3051/7471 | Lignite | 319411 | 164.4 | 13.35 | 6.5 | 0.054 | 0.039 | 7.56 | 319411 | 158.3 | 14.03 | 6.7 | ND(0.003) | 0.28 | 7.56
Stanton Station | 0195140000-02824 | 10 | 1 | 22582 | 10621 | 1.33 | 36.9 | 10.49 | ND(60) | 0.0865 | EPA 3051/7471 | Lignite | 280334 | 169.1 | 14.29 | 5.5 | ND(0.01) | 0.18 | 7.59 | 280334 | 91.1 | 20.44 | 6.5 | ND(0.01) | 0.25 | 6.58
Stanton Station | 0195140000-02824 | 10 | 2 | 22877 | 10448 | 1.26 | 36.4 | 11.49 | ND(60) | 0.101 | EPA 3051/7471 | Lignite | 275237 | 172.2 | 14.94 | 5.7 | ND(0.004) | 0.26 | 7.13 | 275237 | 95.0 | 19.17 | 6.4 | ND(0.01) | 0.11 | 6.96
Stanton Station | 0195140000-02824 | 10 | 3 | 22762 | 10529 | 1.31 | 36.8 | 12.37 | ND(50) | 0.063 | EPA 3051/7471 | Lignite | 275237 | 186.7 | 14.98 | 5.4 | NC(0.004) | 0.52 | 7.10 | 275237 | 93.9 | 19.75 | 6.4 | ND(0.01) | ND(0.2) | 7.12
Stockton Cogen Company | 10640 | GEN1 | 1 | 17000 | 12334 | 0.64 | 6.12 | 13.07 | 668 | 0.026 | ASTM 3684 | Bituminous/Petroleum Coke | 274312 | 150 | 5.9 | 3.7 | 2.737 | ND(0.136) | ND(0.134) | 266684 | 147 | 5.7 | 5.07 | ND(0.129) | ND(0.084) | ND(0.086)
Stockton Cogen Company | 10640 | GEN1 | 2 | 13746 | 12935 | 0.59 | 3.87 | 9.71 | 612 | 0.026 | ASTM 3684 | Bituminous/Petroleum Coke | 268688 | 148 | 6 | 4.36 | ND(3.012) | ND(0.141) | ND(0.139) | 266466 | 146 | 5.5 | 5.22 | ND(0.146) | ND(0.097) | ND(0.102)
Stockton Cogen Company | 10640 | GEN1 | 3 | 14990 | 12254 | 0.56 | 1.16 | 12.78 | 470 | 0.029 | ASTM 3684 | Bituminous/Petroleum Coke | 275359 | 147 | 6 | 3.87 | 2.1 | ND(0.131) | ND(0.148) | 275668 | 145 | 5.7 | 5.15 | ND(0.136) | ND(0.089) | ND(0.100)
TNP-One | 0400510000-07030 | U2 | 1 | 75449 | 9520 | 1.27 | 29.4 | 26.1 | 300 | 0.222 | ASTM 6414 | Lignite | 555305 | 184 | 15.31 | 5.2 | 19 | 7.62 | 6.51 | 585120 | 177 | 13.33 | 6 | 0.06 | 10.11 | 3.95
TNP-One | 0400510000-07030 | U2 | 2 | 72195 | 9810 | 1.26 | 28.5 | 23.1 | ND(100) | 0.18 | ASTM 6414 | Lignite | 584340 | 181 | 13.16 | 5.4 | 9.23 | 3.91 | 5.28 | 584340 | 178 | 11.99 | 5.4 | 0.05 | 5.88 | 2.55
TNP-One | 0400510000-07030 | U2 | 3 | 78013 | 9000 | 1.43 | 30.2 | 30.7 | ND(100) | 0.362 | ASTM 6414 | Lignite | 573407 | 177 | 15.08 | 4.4 | 25.93 | 12.71 | 6.49 | 587654 | 171 | 13.54 | 4.8 | 0.04 | 12.19 | 4.56
Valley | 0208470000-04042 | 2 | 1 | 27746 | 13318 | 0.85 | 8.7 | 7.88 | 124 | 0.0092 | ASTM 3684 EPA 7473 and 7471 | Bituminous/Petroleum Coke | 334586 | 157.0 | 7.63 | 6.6 | 0.03 | 1.15 | 0.97 | 361271 | 157.8 | 7.02 | 6.8 | 0.09 | 1.59 | 0.32
Valley | 0208470000-04042 | 2 | 2 | 27687 | 13269 | 0.85 | 8.35 | 7.82 | 134 | 0.013 | ASTM 3684 EPA 7473 and 7471 | Bituminous/Petroleum Coke | 339094 | 156.6 | 7.35 | 6.6 | 0.04 | 1.19 | 0.36 | 372104 | 158.7 | 7.00 | 6.7 | 0.03 | 1.23 | 0.33
Valley | 0208470000-04042 | 2 | 3 | 27022 | 13456 | 0.92 | 8.91 | 7.14 | 125 | 0.015 | ASTM 3684 EPA 7473 and 7471 | Bituminous/Petroleum Coke | 331724 | 156.4 | 7.52 | 6.5 | 0.03 | 0.98 | 0.54 | 377717 | 158.8 | 7.11 | 6.7 | ND(0.008) | 1.5 | 0.41
Valmont | 0154660000-00477 | 5 | 1 | 59355 | 12299 | 0.29 | 16.1 | 8 | ND(50) | 0.01 | MODIFIED EPA 3051/7471A | Bituminous | 858556 | 142 | 11.7 | 5.4 | 0.8 | 0.1 | 0.16 | 692863 | 134 | 8.27 | 5.4 | ND(0.01) | 0.105 | 0.032
Valmont | 0154660000-00477 | 5 | 2 | 58814 | 12243 | 0.3 | 16.3 | 8.25 | 66 | 0.0055 | MODIFIED EPA 3051/7471A | Bituminous | 844486 | 143 | 8.57 | 5.3 | 0.8 | 0.06 | 0.12 | 667242 | 138 | 8.51 | 5.4 | ND(0.01) | 0.084 | 0.017
Valmont | 0154660000-00477 | 5 | 3 | 55471 | 11607 | 0.49 | 12.1 | 8.76 | ND(50) | 0.0083 | MODIFIED EPA 3051/7471A | Bituminous | 849780 | 156 | 7.37 | 5.5 | 1.06 | 0.09 | 0.15 | 648289 | 148 | 7.57 | 5.5 | ND(0.01) | 0.178 | 0.027
W. H. Sammis | 0139980000-02866 | 1 | 1 | 50494 | 12202 | 0.91 | 5.34 | 17.3 | 1300 | 0.081 | ASTM 6414 | Bituminous | 739403 | 161 | 6.13 | 6 | 9.814 | ND(0.80) | ND(0.99) | 742450 | 153 | 6.64 | 7.1 | 0.03 | ND(0.76) | ND(0.93)
W. H. Sammis | 0139980000-02866 | 1 | 2 | 48308 | 13594 | 1.51 | 4.74 | 9.3 | 1200 | 0.12 | ASTM 6414 | Bituminous | 729449 | 157 | 6.7 | 6 | 12.788 | ND(0.83) | ND(0.90) | 716614 | 149 | 7.54 | 6.8 | 0.05 | ND(0.93) | ND(0.87)
W. H. Sammis | 0139980000-02866 | 1 | 3 | 48049 | 13531 | 1.43 | 4.74 | 9.84 | 1200 | 0.117 | ASTM 6414 | Bituminous | 706103 | 156 | 6.95 | 6 | 12.186 | ND(0.85) | ND(0.86) | 699740 | 150 | 8.25 | 7 | 0.04 | ND(0.79) | ND(0.88)
Wabash River Generating Station | 0154700000-01010 | 1 + 1A | 1 | 90663 | 12350 | 2.72 | 14.8 | 13 | 600 | 0.064 | ASTM 6414 | Bituminous | [7 empty] | 1372064 | 181.7 | 14.47 | 13.6 | ND(0.05) | ND(0.84) | 2.58
Wabash River Generating Station | 0154700000-01010 | 1 + 1A | 2 | 89629 | 12530 | 2.75 | 15.7 | 12.7 | 600 | 0.068 | ASTM 6414 | Bituminous | [7 empty] | 1385884 | 168.3 | 14.46 | 14.0 | ND(0.05) | ND(0.089) | 2.6
Wabash River Generating Station | 0154700000-01010 | 1 + 1A | 3 | 89493 | 12540 | 2.89 | 15.9 | 13.1 | 600 | 0.07 | ASTM 6414 | Bituminous | [7 empty] | 1352458 | 178.3 | 13.79 | 13.6 | 0.03 | ND(0.90) | 2.77
Widows Creek Fossil Plant | 0186420000-00050 | 6 | 1 | 41312 | 12633 | 0.59 | 8.89 | 11.4 | 400 | 0.029 | ASTM 6414 | Bituminous | 438532 | 160 | 7.73 | 5.2 | 2.95 | ND(0.78) | ND(0.94) | 496976 | 162 | 6.95 | 8.2 | 0.1 | 1.05 | ND(1.15)
Widows Creek Fossil Plant | 0186420000-00050 | 6 | 2 | 41520 | 12744 | 0.51 | 9.45 | 10.4 | 300 | 0.024 | ASTM 6414 | Bituminous | 436101 | 162 | 7.29 | 5.6 | 2.55 | ND(0.77) | ND(0.87) | 500143 | 158 | 6.53 | 7.2 | 0.04 | 0.98 | ND(1.04)
Widows Creek Fossil Plant | 0186420000-00050 | 6 | 3 | 40552 | 12769 | 0.53 | 9.23 | 10.2 | 300 | 0.021 | ASTM 6414 | Bituminous | 445789 | 159 | 7.6 | 5 | 2.55 | ND(0.83) | ND(0.88) | 500532 | 151 | 6.79 | 7.6 | 0.06 | ND(0.97) | ND(1.00)
Wyodak | 0143540000-06101 | BW 91 | 1 | 145472 | 11550 | 0.87 | 29.67 | 10.04 | ND(50) | 0.03 | ASTM 3684 | Subbituminous | 1928365 | 162 | 9.3 | 8 | 1.8 | 2.8 | 8.2 | 1906278 | 82 | 13.7 | 8 | ND(0.025) | 0.048 | 7.03
Wyodak | 0143540000-06101 | BW 91 | 2 | 145265 | 11677 | 0.84 | 29.77 | 9.4 | ND(50) | 0.04 | ASTM 3684 | Subbituminous | 1789047 | 158 | 9.9 | 8 | 2.2 | 3.4 | 6.8 | 1913074 | 82 | 13.7 | 8 | ND(0.029) | 0.12 | 6.98
Wyodak | 0143540000-06101 | BW 91 | 3 | 147351 | 11640 | 0.81 | 30.29 | 9.7 | ND(50) | 0.05 | ASTM 3684 | Subbituminous | 1712592 | 160 | 9.8 | 7.4 | 1.7 | 2.7 | 8.7 | 1952151 | 81 | 13.2 | 8 | ND(0.028) | 0.18 | 6.95
XB = Excessive reagent blank caused the data to be unreliable
NA = Data was not included in report
LS = Test sample was broken, damaged, or lost during testing or in transport

## 03_Data_Bin_Table
Speciated Hg split in stack (fraction) 3
Plant ID | EIA Plant Code & ORIS Plant Code or just ORIS Plant Code | Unit No. | Run Number | Emission Modification Factor (fractional Hg retention across testing locations) | Testing locations | Primary Fuel/ Secondary Fuel | Boiler/furnace type 1 | PM Control | SO2 Control | External NOX Control 2 | Particle-bound Hg | Oxidized Hg | Elemental Hg
Emission control device type Bin 0
Polk Power | 0184540000-07242 | 1 | 1 (4) | 1.2338 | coal to stack | Bituminous/None | COAL GAS | COAL GAS 5 | COAL GAS 5 | NONE | 0.00127 | 0.09886 | 0.89987
Polk Power | 0184540000-07242 | 1 | 2 (4) | 1.2667 | coal to stack | Bituminous/None | COAL GAS | COAL GAS 5 | COAL GAS 5 | NONE | 0.00129 | 0.08021 | 0.9185
Polk Power | 0184540000-07242 | 1 | 3 (4) | 1.4601 | coal to stack | Bituminous/None | COAL GAS | COAL GAS 5 | COAL GAS 5 | NONE | 0.00136 | 0.03528 | 0.96337
Wabash River Generating Station | 0154700000-01010 | 1 + 1A | 1 | 0.7153 | coal to stack | Bituminous/None | COAL GAS | COAL GAS 5 | COAL GAS 5 | NONE | 0.00826 | 0.13884 | 0.85289
Wabash River Generating Station | 0154700000-01010 | 1 + 1A | 2 | 0.60701 | coal to stack | Bituminous/None | COAL GAS | COAL GAS 5 | COAL GAS 5 | NONE | 0.00937 | 0.01667 | 0.97397
Wabash River Generating Station | 0154700000-01010 | 1 + 1A | 3 | 0.70165 | coal to stack | Bituminous/None | COAL GAS | COAL GAS 5 | COAL GAS 5 | NONE | 0.00923 | 0.13846 | 0.85231
|  |  | Average emission modification factor | 0.99743 | [5 empty] | Average speciated Hg fraction | 0.00513 | 0.08472 | 0.91015
Emission control device type Bin 1
Brayton Point | 0134330000-01619 | 1 | 1 | 0.84199 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.156 | 0.77737 | 0.06663
Brayton Point | 0134330000-01619 | 1 | 2 | 0.64485 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.17475 | 0.74119 | 0.08406
Brayton Point | 0134330000-01619 | 1 | 3 | 0.6887 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.18584 | 0.73054 | 0.08363
Brayton Point | 0134330000-01619 | 3 | 1 | 0.64163 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.16677 | 0.67634 | 0.15689
Brayton Point | 0134330000-01619 | 3 | 2 | 0.72142 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.23975 | 0.61485 | 0.1454
Brayton Point | 0134330000-01619 | 3 | 3 | 0.88131 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0 | 0.51134 | 0.48866
Gibson Generating Station (03/00 testing) | 0154700000-06113 | 3 | 1 | 1.0391 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00023 | 0.80969 | 0.19008
Gibson Generating Station (03/00 testing) | 0154700000-06113 | 3 | 2 | 0.9003 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00027 | 0.84721 | 0.15252
Gibson Generating Station (03/00 testing) | 0154700000-06113 | 3 | 3 | 0.91004 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00021 | 0.91121 | 0.08858
Gibson Generating Station (10/99 testing) | 0154700000-06113 | 3 | 1 | 0.61089 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00212 | 0.53814 | 0.45975
Gibson Generating Station (10/99 testing) | 0154700000-06113 | 3 | 2 | 0.41512 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00351 | 0.61599 | 0.38049
Gibson Generating Station (10/99 testing) | 0154700000-06113 | 3 | 3 | 0.90227 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.0015 | 0.69738 | 0.30112
Jack Watson | 0126860000-02049 | 4 | 1 | 0.77866 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00548 | 0.57534 | 0.41918
Jack Watson | 0126860000-02049 | 4 | 2 | 0.623 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.01316 | 0.75987 | 0.22697
Jack Watson | 0126860000-02049 | 4 | 3 | 0.72144 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00818 | 0.75941 | 0.23241
Widows Creek Fossil Plant | 0186420000-00050 | 6 | 1 | 0.55887 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | NONE | 0.05797 | 0.6087 | 0.33333
Widows Creek Fossil Plant | 0186420000-00050 | 6 | 2 | 0.50996 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | NONE | 0.02597 | 0.63636 | 0.33766
Widows Creek Fossil Plant | 0186420000-00050 | 6 | 3 | 0.36645 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | NONE | 0.05742 | 0.46411 | 0.47847
|  |  | Average emission modification factor | 0.70866 | [5 empty] | Average speciated Hg fraction | 0.06106 | 0.68195 | 0.25699
Emission control device type Bin 2
Presque Isle | 0208470000-01769 | 5 | 1 | 0.34713 | across control | Bituminous/Pet Coke | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | NONE | 0.00599 | 0.4012 | 0.59281
Presque Isle | 0208470000-01769 | 5 | 2 | 0.3813 | across control | Bituminous/Pet Coke | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | NONE | 0.00228 | 0.4447 | 0.55302
Presque Isle | 0208470000-01769 | 5 | 3 | 0.28563 | across control | Bituminous/Pet Coke | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | NONE | 0.01035 | 0.43338 | 0.55627
Presque Isle | 0208470000-01769 | 6 | 1 | 0.45459 | across control | Bituminous/Pet Coke | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | NONE | 0.03657 | 0.52743 | 0.43601
Presque Isle | 0208470000-01769 | 6 | 2 | 0.4971 | across control | Bituminous/Pet Coke | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | NONE | 0.01353 | 0.51297 | 0.47351
Presque Isle | 0208470000-01769 | 6 | 3 | 0.41266 | across control | Bituminous/Pet Coke | CONV/PC/NONOX/WET | ESP- CS | COMP COAL | NONE | 0.00154 | 0.47409 | 0.52437
|  |  | Average emission modification factor | 0.3964 | [5 empty] | Average speciated Hg fraction | 0.01171 | 0.46563 | 0.52267
Emission control device type Bin 3
Salem Harbor | 0134330000-01626 | 3 | 1 | 0.14528 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | SNCR | 0.09158 | 0.38383 | 0.52459
Salem Harbor | 0134330000-01626 | 3 | 2 | 0.0748 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | SNCR | 0.30311 | 0.21507 | 0.48182
Salem Harbor | 0134330000-01626 | 3 | 3 | 0.08351 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | SNCR | 0.21475 | 0.21475 | 0.5705
|  |  | Average emission modification factor | 0.1012 | [5 empty] | Average speciated Hg fraction | 0.20315 | 0.27121 | 0.52564
Emission control device type Bin 4
Cliffside | 0054160000-02721 | 1 | 1 | 0.99144 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | NONE | NONE | 0.05699 | 0.39033 | 0.55268
Cliffside | 0054160000-02721 | 1 | 2 | 0.52137 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | NONE | NONE | 0.02273 | 0.52557 | 0.4517
Cliffside | 0054160000-02721 | 1 | 3 | 0.57491 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | NONE | NONE | 0.01463 | 0.60146 | 0.38391
Dunkirk | 0135730000-02554 | 2 | 1 | 0.94985 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | NONE | 0.038 | 0.62758 | 0.33442
Dunkirk | 0135730000-02554 | 2 | 2 | 0.67678 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | NONE | 0.02142 | 0.63591 | 0.34267
Dunkirk | 0135730000-02554 | 2 | 3 | 0.8114 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | NONE | 0.00573 | 0.62385 | 0.37041
Gaston | 0001950000-00026 | 1 | 1 | 1.0019 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | NONE | NONE | 0.09484 | 0.60399 | 0.30116
Gaston | 0001950000-00026 | 1 | 2 | 1.4137 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | NONE | NONE | 0.04095 | 0.59974 | 0.35931
Gaston | 0001950000-00026 | 1 | 3 | 1.1 | across control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | NONE | NONE | 0.14577 | 0.59718 | 0.25705
|  |  | Average emission modification factor | 0.89349 | [5 empty] | Average speciated Hg fraction | 0.04901 | 0.5784 | 0.37259
Emission control device type Bin 5
Bruce Mansfield | 0147160000-06094 | 1 | 1 | 0.85316 | across control | Bituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.02038 | 0.20815 | 0.77147
Bruce Mansfield | 0147160000-06094 | 1 | 2 | 0.8598 | across control | Bituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.01667 | 0.25119 | 0.73214
Bruce Mansfield | 0147160000-06094 | 1 | 3 | 0.9249 | across control | Bituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.01704 | 0.12582 | 0.85714
|  |  | Average emission modification factor | 0.87929 | [5 empty] | Average speciated Hg fraction | 0.01803 | 0.19505 | 0.78692
Emission control device type Bin 6
Port Washington | 0208470000-04040 | 4 | 1 | 0.59321 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- CS | DRY SORBENT | NONE | 0.00042 | 0.67652 | 0.32306
Port Washington | 0208470000-04040 | 4 | 2 | 0.47379 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- CS | DRY SORBENT | NONE | 0.00044 | 0.65693 | 0.34263
Port Washington | 0208470000-04040 | 4 | 3 | 0.58628 | across control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- CS | DRY SORBENT | NONE | 0.00397 | 0.67945 | 0.31658
|  |  | Average emission modification factor | 0.55109 | [5 empty] | Average speciated Hg fraction | 0.00161 | 0.67097 | 0.32742
Emission control device type Bin 7
W. H. Sammis | 0139980000-02866 | 1 | 1 | 0.08817 | across control | Bituminous/None | CONV/PC/NONOX/DRY | BAGHOUSE | NONE | NONE | 0.03429 | 0.43429 | 0.53143
W. H. Sammis | 0139980000-02866 | 1 | 2 | 0.0735 | across control | Bituminous/None | CONV/PC/NONOX/DRY | BAGHOUSE | NONE | NONE | 0.05263 | 0.48947 | 0.45789
W. H. Sammis | 0139980000-02866 | 1 | 3 | 0.07189 | across control | Bituminous/None | CONV/PC/NONOX/DRY | BAGHOUSE | NONE | NONE | 0.04571 | 0.45143 | 0.50286
Valmont | 0154660000-00477 | 5 | 1 | 0.13396 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.03521 | 0.73944 | 0.22535
Valmont | 0154660000-00477 | 5 | 2 | 0.10886 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.04717 | 0.79245 | 0.16038
Valmont | 0154660000-00477 | 5 | 3 | 0.16154 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.02381 | 0.84762 | 0.12857
|  |  | Average emission modification factor | 0.10632 | [5 empty] | Average speciated Hg fraction | 0.0398 | 0.62578 | 0.33441
Emission control device type Bin 8
Mecklenburg Cogeneration Facility | 52007 | GEN 1 | 1 | 0.00764 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.09122 | 0.44595 | 0.46284
Mecklenburg Cogeneration Facility | 52007 | GEN 1 | 2 | 0.01577 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.08966 | 0.44828 | 0.46207
Mecklenburg Cogeneration Facility | 52007 | GEN 1 | 3 | 0.01218 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.12273 | 0.25 | 0.62727
|  |  | Average emission modification factor | 0.0119 | [5 empty] | Average speciated Hg fraction | 0.1012 | 0.38141 | 0.51739
Emission control device type Bin 9
SEI - Birchwood Power Facility | 54304 | 1 | 1 | 0.04104 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SCR | 0.01879 | 0.60543 | 0.37578
SEI - Birchwood Power Facility | 54304 | 1 | 2 | 0.02211 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SCR | 0.05556 | 0.38889 | 0.55556
SEI - Birchwood Power Facility | 54304 | 1 | 3 | 0.01613 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SCR | 0.07738 | 0.3869 | 0.53571
Logan Generating Plant | 10043 | Gen 1 | 1 | 0.00909 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SCR | 0.11962 | 0.21505 | 0.66532
Logan Generating Plant | 10043 | Gen 1 | 2 | 0.01008 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SCR | 0.10931 | 0.35088 | 0.53981
Logan Generating Plant | 10043 | Gen 1 | 3 | 0.05529 | across control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | SCR | 0.01772 | 0.02165 | 0.96063
|  |  | Average emission modification factor | 0.0256 | [5 empty] | Average speciated Hg fraction | 0.066397 | 0.32813 | 0.60547
Emission control device type Bin 10
Big Bend | 0184540000-00645 | BB03 | 1 | 0.32968 | last control | Bituminous/None | CONV/PC/TURBO/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.08791 | 0.91209
Big Bend | 0184540000-00645 | BB03 | 2 | 0.25789 | last control | Bituminous/None | CONV/PC/TURBO/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.06294 | 0.93706
Big Bend | 0184540000-00645 | BB03 | 3 | 0.35682 | last control | Bituminous/None | CONV/PC/TURBO/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.10227 | 0.89773
AES Cayuga (NY) (formerly NYSEG Milliken) | 0135110000-02535 | 2 | 1 | 0.36235 | last control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.10484 | 0.89516
AES Cayuga (NY) (formerly NYSEG Milliken) | 0135110000-02535 | 2 | 2 | 0.27913 | last control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00555 | 0.05975 | 0.9347
AES Cayuga (NY) (formerly NYSEG Milliken) | 0135110000-02535 | 2 | 3 | 0.30012 | last control | Bituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00755 | 0.04906 | 0.9434
|  |  | Second unit average emission modification factor | 0.31433 | [5 empty] | Average speciated Hg fraction | 0.00218 | 0.07779 | 0.92002
|  |  | First unit average emission modification correction factor | 0.70866
|  |  | Combined emission modification factor 6 | 0.22275
Emission control device type Bin 11
Charles R. Lowman | 0001890000-00056 | 2 | 1 | 0.94021 | last control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00735 | 0.32843 | 0.66422
Charles R. Lowman | 0001890000-00056 | 2 | 2 | 0.70533 | last control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.01136 | 0.34318 | 0.64545
Charles R. Lowman | 0001890000-00056 | 2 | 3 | 0.58548 | last control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00467 | 0.39019 | 0.60514
R. D. Morrow Sr. Generating plant | 0175680000-06061 | 2 | 1 | 0.46357 | last control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00389 | 0.2903 | 0.70582
R. D. Morrow Sr. Generating plant | 0175680000-06061 | 2 | 2 | 0.50759 | last control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00248 | 0.28353 | 0.71399
R. D. Morrow Sr. Generating plant | 0175680000-06061 | 2 | 3 | 0.5517 | last control | Bituminous/None | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00298 | 0.19711 | 0.79991
Navajo | 0165720000-04941 | 3 | 1 | 0.58001 | last control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.01431 | 0.00954 | 0.97615
Navajo | 0165720000-04941 | 3 | 2 | 0.87346 | last control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00585 | 0.00923 | 0.98492
Navajo | 0165720000-04941 | 3 | 3 | 0.91818 | last control | Bituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00343 | 0.00934 | 0.98723
|  |  | Second unit average emission modification factor | 0.68061 | [5 empty] | Average speciated Hg fraction | 0.00626 | 0.20676 | 0.78698
|  |  | First unit average emission modification correction factor | 0.89349
|  |  | Combined emission modification factor | 0.60812
Emission control device type Bin 12
Clover Power Station | 0198760000-07213 | 2 | 1 | 0.38256 | last control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | NONE | 0.06452 | 0.53226 | 0.40323
Clover Power Station | 0198760000-07213 | 2 | 2 | 0.21828 | last control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | NONE | 0.025 | 0.675 | 0.3
Clover Power Station | 0198760000-07213 | 2 | 3 | 0.10925 | last control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | NONE | 0.1875 | 0.25 | 0.5625
Intermountain | 0112080000-06481 | 2SGA | 1 | 0.15968 | last control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | NONE | 0.06997 | 0.11953 | 0.8105
Intermountain | 0112080000-06481 | 2SGA | 2 | 0.34473 | last control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | NONE | 0.01591 | 0.18849 | 0.79559
Intermountain | 0112080000-06481 | 2SGA | 3 | 0.25977 | last control | Bituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | WETSCRUB | NONE | 0.02597 | 0.21457 | 0.75946
|  |  | Second unit average emission modification factor | 0.24571 | [5 empty] | Average speciated Hg fraction | 0.06481 | 0.32998 | 0.60521
|  |  | First unit average emission modification correction factor | 0.10632
|  |  | Combined emission modification factor | 0.02612
Emission control device type Bin 13
Montrose | 0100000000-02080 | 1 | 1 | 0.82411 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00082 | 0.32094 | 0.67824
Montrose | 0100000000-02080 | 1 | 2 | 1.0234 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00037 | 0.30577 | 0.69386
Montrose | 0100000000-02080 | 1 | 3 | 0.87248 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00023 | 0.28996 | 0.70981
George Neal South | 0123410000-07343 | 4 | 1 | 0.85384 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00318 | 0.42494 | 0.57188
George Neal South | 0123410000-07343 | 4 | 2 | 0.91088 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00535 | 0.3992 | 0.59545
George Neal South | 0123410000-07343 | 4 | 3 | 1.5235 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00299 | 0.42431 | 0.57269
Newton | 0032530000-06017 | 2 | 1 | 1.001 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.0004 | 0.2183 | 0.78129
Newton | 0032530000-06017 | 2 | 2 | 0.8367 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00034 | 0.18913 | 0.81054
Newton | 0032530000-06017 | 2 | 3 | 0.91535 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | COMP COAL | NONE | 0.00028 | 0.20219 | 0.79753
|  |  | Average emission modification factor | 0.97348 | [5 empty] | Average speciated Hg fraction | 0.00155 | 0.3083 | 0.69014
Emission control device type Bin 14
Cholla | 0008030000-00113 | 3 | 1 | 1.2116 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- HS | NONE | NONE | 0 | 0.21429 | 0.78571
Cholla | 0008030000-00113 | 3 | 2 | 1.2821 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- HS | NONE | NONE | 0 | 0 | 1
Cholla | 0008030000-00113 | 3 | 3 | 1.5943 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- HS | NONE | NONE | 0 | 0.23404 | 0.76596
Columbia | 0208560000-08023 | 1 | 1 | 0.94917 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | NONE | 0.00033 | 0.18931 | 0.81036
Columbia | 0208560000-08023 | 1 | 2 | 0.72577 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | NONE | 0.00034 | 0.15419 | 0.84548
Columbia | 0208560000-08023 | 1 | 3 | 0.96665 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- HS | COMP COAL | NONE | 0.00033 | 0.18109 | 0.81858
Platte | 0406060000-00059 | 1 | 1 | 0.73177 | across control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00256 | 0.14199 | 0.85545
Platte | 0406060000-00059 | 1 | 2 | 1.3316 | across control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00153 | 0.04396 | 0.95451
Platte | 0406060000-00059 | 1 | 3 | 1.0247 | across control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00138 | 0.0921 | 0.90652
Presque Isle | 0208470000-01769 | 9 | 1 | 0.99901 | across control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00043 | 0.08318 | 0.91639
Presque Isle | 0208470000-01769 | 9 | 2 | 1.0523 | across control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00035 | 0.09076 | 0.90889
Presque Isle | 0208470000-01769 | 9 | 3 | 1.0576 | across control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.0003 | 0.07797 | 0.92173
|  |  | Average emission modification factor | 1.0772 | [5 empty] | Average speciated Hg fraction | 0.00063 | 0.12524 | 0.87413
Emission control device type Bin 15
Clay Boswell | 0126470000-01893 | 2 | 1 | 0.2394 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.05004 | 0.85666 | 0.0933
Clay Boswell | 0126470000-01893 | 2 | 2 | 0.12551 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.00662 | 0.59603 | 0.39735
Clay Boswell | 0126470000-01893 | 2 | 3 | 0.15813 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.00917 | 0.82569 | 0.16514
Comanche | 0154660000-00470 | 2 | 1 | 0.31396 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.01398 | 0.91057 | 0.07545
Comanche | 0154660000-00470 | 2 | 2 | 0.47369 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.00318 | 0.86016 | 0.13666
Comanche | 0154660000-00470 | 2 | 3 | 0.33475 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.00648 | 0.92056 | 0.07296
|  |  | Average emission modification factor | 0.27424 | [5 empty] | Average speciated Hg fraction | 0.01491 | 0.82828 | 0.15681
Emission control device type Bin 16
Clay Boswell | 0126470000-01893 | 3 | 1 | 0.92841 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | COMP COAL | NONE | 0.00041 | 0.00818 | 0.99141
Clay Boswell | 0126470000-01893 | 3 | 2 | 0.86191 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | COMP COAL | NONE | 0.00011 | 0.01131 | 0.98858
Clay Boswell | 0126470000-01893 | 3 | 3 | 0.94752 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | COMP COAL | NONE | 0.00045 | 0.01128 | 0.98827
Clay Boswell | 0126470000-01893 | 4 | 1 | 1.0308 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.00403 | 0.01815 | 0.97782
Clay Boswell | 0126470000-01893 | 4 | 2 | 1.1825 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.03041 | 0.06798 | 0.90161
Clay Boswell | 0126470000-01893 | 4 | 3 | 1.444 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.04291 | 0.09142 | 0.86567
Cholla | 0008030000-00113 | 2 | 1 | 0.77321 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | MECH/PARTSCRUB | NONE | NONE | 0 | 0.05114 | 0.94886
Cholla | 0008030000-00113 | 2 | 2 | 1.3339 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | MECH/PARTSCRUB | NONE | NONE | 0 | 0.0297 | 0.9703
Cholla | 0008030000-00113 | 2 | 3 | 1.0233 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | MECH/PARTSCRUB | NONE | NONE | 0 | 0.03117 | 0.96883
Colstrip | 0128250000-06076 | 3 | 1 | 1.8828 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.01431 | 0.04329 | 0.9424
Colstrip | 0128250000-06076 | 3 | 2 | 1.0884 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.01172 | 0.03924 | 0.94904
Colstrip | 0128250000-06076 | 3 | 3 | 0.26398 | across control | Subbituminous/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.03451 | 0.14925 | 0.81623
Lawrence | 0002250000-01250 | 4 | 1 | 1.0159 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | PARTSCRUB | NONE | NONE | 0.01684 | 0.07016 | 0.913
Lawrence | 0002250000-01250 | 4 | 2 | 1.3383 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | PARTSCRUB | NONE | NONE | 0.03105 | 0.07032 | 0.89863
Lawrence | 0002250000-01250 | 4 | 3 | 1.1678 | across control | Subbituminous/None | CONV/PC/NONOX/DRY | PARTSCRUB | NONE | NONE | 0.03125 | 0.07422 | 0.89453
|  |  | Average emission modification factor | 1.0855 | [5 empty] | Average speciated Hg fraction | 0.01453 | 0.05112 | 0.93435
Emission control device type Bin 17
GRDA | 0074900000-00165 | 2 | 1 | 1.0228 | across control | Subbituminous/Bituminous | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00095 | 0.12155 | 0.8775
GRDA | 0074900000-00165 | 2 | 2 | 1.2435 | across control | Subbituminous/Bituminous | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00198 | 0.10317 | 0.89484
GRDA | 0074900000-00165 | 2 | 3 | 0.81847 | across control | Subbituminous/Bituminous | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.0011 | 0.03072 | 0.96818
Laramie River Station | 0013070000-06204 | 3 | 1 | 4.5534 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00647 | 0.02423 | 0.9693
Laramie River Station | 0013070000-06204 | 3 | 2 | 0.42646 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00618 | 0.00821 | 0.98561
Laramie River Station | 0013070000-06204 | 3 | 3 | 0.37462 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00619 | 0.00722 | 0.98659
Wyodak | 0143540000-06101 | BW 91 | 1 | 0.55395 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00176 | 0.00677 | 0.99147
Wyodak | 0143540000-06101 | BW 91 | 2 | 0.57375 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00204 | 0.01687 | 0.9811
Wyodak | 0143540000-06101 | BW 91 | 3 | 0.57051 | across control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | SDA | NONE | 0.00196 | 0.0252 | 0.97284
|  |  | Average emission modification factor | 1.1264 | [5 empty] | Average speciated Hg fraction | 0.00318 | 0.03821 | 0.9586
Emission control device type Bin 18
Craig | 0301510000-06021 | C3 | 1 | 0.68455 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00344 | 0.03436 | 0.9622
Craig | 0301510000-06021 | C3 | 2 | 0.60191 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00344 | 0.03436 | 0.9622
Craig | 0301510000-06021 | C3 | 3 | 0.70547 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00364 | 0.03636 | 0.96
Rawhide | 0151430000-06761 | 101 | 1 | 0.83693 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.02035 | 0.06409 | 0.91556
Rawhide | 0151430000-06761 | 101 | 2 | 0.67975 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00055 | 0.06466 | 0.93479
Rawhide | 0151430000-06761 | 101 | 3 | 0.52849 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00597 | 0.09797 | 0.89606
Northern States Power - Sherburne County Generating Plant | 0137810000-06090 | #3 | 1 | 0.7633 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.01401 | 0.02241 | 0.96359
Northern States Power - Sherburne County Generating Plant | 0137810000-06090 | #3 | 2 | 1.1114 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.01109 | 0.01411 | 0.9748
Northern States Power - Sherburne County Generating Plant | 0137810000-06090 | #3 | 3 | 0.99157 | across control | Subbituminous/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.02638 | 0.02278 | 0.95084
|  |  | Average emission modification factor | 0.76704 | [5 empty] | Average speciated Hg fraction | 0.00987 | 0.04346 | 0.94667
Emission control device type Bin 19
Jim Bridger | 0143540000-08066 | BW 74 | 1 | 0.89679 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00904 | 0.03615 | 0.95482
Jim Bridger | 0143540000-08066 | BW 74 | 2 | 0.84478 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00688 | 0.04376 | 0.94936
Jim Bridger | 0143540000-08066 | BW 74 | 3 | 0.9705 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00553 | 0.03316 | 0.96131
Laramie River Station | 0013070000-06204 | 1 | 1 | 0.47228 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.05689 | 0.94311
Laramie River Station | 0013070000-06204 | 1 | 2 | 0.55461 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.02015 | 0.97985
Laramie River Station | 0013070000-06204 | 1 | 3 | 0.42417 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- CS | WETSCRUB | NONE | 0 | 0.00635 | 0.99365
Sam Seymour | 0112690000-06179 | 3 | 1 | 1.3143 | last control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00473 | 0.01893 | 0.97633
Sam Seymour | 0112690000-06179 | 3 | 2 | 1.4656 | last control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00758 | 0.02165 | 0.97078
Sam Seymour | 0112690000-06179 | 3 | 3 | 0.82969 | last control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | NONE | 0.0048 | 0.02758 | 0.96763
|  |  | Second unit average emission modification factor | 0.86364 | [5 empty] | Average speciated Hg fraction | 0.00428 | 0.0294 | 0.96631
|  |  | First unit average emission modification correction factor | 0.97348
|  |  | Combined emission modification factor | 0.84073
Emission control device type Bin 20
Coronado | 0615720000-06177 | U1B | 1 | 1.1295 | last control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | WETSCRUB | NONE | 0.00423 | 0.01205 | 0.98371
Coronado | 0615720000-06177 | U1B | 2 | 1.2141 | last control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | WETSCRUB | NONE | 0.02567 | 0.01073 | 0.9636
Coronado | 0615720000-06177 | U1B | 3 | 1.113 | last control | Subbituminous/None | CONV/PC/NOX/WET | ESP- HS | WETSCRUB | NONE | 0.03366 | 0.0399 | 0.92644
Craig | 0301510000-06021 | C1 | 1 | 0.58586 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00168 | 0.05419 | 0.94413
Craig | 0301510000-06021 | C1 | 2 | 0.77047 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00147 | 0.04895 | 0.94957
Craig | 0301510000-06021 | C1 | 3 | 0.97558 | last control | Subbituminous/None | CONV/PC/NOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00548 | 0.04388 | 0.95064
San Juan | 0154730000-02451 | 2 | 1 | 0.6326 | last control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.00636 | 0.05891 | 0.93474
San Juan | 0154730000-02451 | 2 | 2 | 0.68646 | last control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.01592 | 0.07173 | 0.91235
San Juan | 0154730000-02451 | 2 | 3 | 0.57613 | last control | Subbituminous/None | CONV/PC/NONOX/DRY | ESP- HS | WETSCRUB | NONE | 0.01086 | 0.06111 | 0.92802
|  |  | Second unit average emission modification factor | 0.85374 | [5 empty] | Average speciated Hg fraction | 0.0117 | 0.04461 | 0.94369
|  |  | First unit average emission modification correction factor | 1.0772
|  |  | Combined emission modification factor | 0.91966
Emission control device type Bin 21
Stanton Station | 0195140000-02824 | 1 | 1 | 0.97843 | across control | Lignite/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.0017 | 0.03663 | 0.96166
Stanton Station | 0195140000-02824 | 1 | 2 | 1.0865 | across control | Lignite/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00094 | 0.03626 | 0.9628
Stanton Station | 0195140000-02824 | 1 | 3 | 1.039 | across control | Lignite/None | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00019 | 0.03571 | 0.9641
|  |  | Average emission modification factor | 1.0346 | [5 empty] | Average speciated Hg fraction | 0.00094 | 0.0362 | 0.96286
Emission control device type Bin 22
La Cygne | 0100000000-01241 | 1 | 1 | 0.77923 | across control | Subbituminous/None | CYCLONE/NOX/WET | PARTSCRUB | NONE | NONE | 0.0184 | 0.04742 | 0.93418
La Cygne | 0100000000-01241 | 1 | 2 | 0.7622 | across control | Subbituminous/None | CYCLONE/NOX/WET | PARTSCRUB | NONE | NONE | 0.01637 | 0.05401 | 0.92962
La Cygne | 0100000000-01241 | 1 | 3 | 0.79419 | across control | Subbituminous/None | CYCLONE/NOX/WET | PARTSCRUB | NONE | NONE | 0.03556 | 0.07111 | 0.89333
|  |  | Average emission modification factor | 0.77854 | [5 empty] | Average speciated Hg fraction | 0.02344 | 0.05751 | 0.91905
Emission control device type Bin 23
Nelson Dewey | 0208560000-04054 | 1 | 1 | 0.98047 | across control | Subbituminous/Pet Coke | CYCLONE/NOX/WET | ESP- HS | COMP COAL | NONE | 0.01355 | 0.07067 | 0.91578
Nelson Dewey | 0208560000-04054 | 1 | 2 | 1.056 | across control | Subbituminous/Pet Coke | CYCLONE/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00748 | 0.06229 | 0.93023
Nelson Dewey | 0208560000-04054 | 1 | 3 | 1.2327 | across control | Subbituminous/Pet Coke | CYCLONE/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00676 | 0.09275 | 0.90048
|  |  | Average emission modification factor | 1.0897 | [5 empty] | Average speciated Hg fraction | 0.00926 | 0.07524 | 0.9155
Emission control device type Bin 24
Leland Olds Station | 0013070000-02817 | 2 | 1 | 1.2353 | across control | Lignite/None | CYCLONE/NOX/WET | ESP- CS | NONE | NONE | 0.00049 | 0.16821 | 0.8313
Leland Olds Station | 0013070000-02817 | 2 | 2 | 0.66739 | across control | Lignite/None | CYCLONE/NOX/WET | ESP- CS | NONE | NONE | 0.00037 | 0.17158 | 0.82805
|  |  | Average emission modification factor | 0.95132 | [5 empty] | Average speciated Hg fraction | 0.00043 | 0.16989 | 0.82968
Emission control device type Bin 25
Stockton Cogen Company | 10640 | GEN1 | 1 | 0.05653 | across control | Bituminous/Pet Coke | FBC 7 | BAGHOUSE | NONE | SNCR | 0.43144 | 0.28094 | 0.28763
Stockton Cogen Company | 10640 | GEN1 | 2 | 0.11051 | across control | Bituminous/Pet Coke | FBC 7 | BAGHOUSE | NONE | SNCR | 0.42319 | 0.28116 | 0.29565
Stockton Cogen Company | 10640 | GEN1 | 3 | 0.07842 | across control | Bituminous/Pet Coke | FBC 7 | BAGHOUSE | NONE | SNCR | 0.41846 | 0.27385 | 0.30769
|  |  | Average emission modification factor | 0.08182 | [5 empty] | Average speciated Hg fraction | 0.42436 | 0.27865 | 0.29699
Emission control device type Bin 26 - Not Used in Model
Emission control device type Bin 27
Scrubgrass Generating Company L. P. | 50974 | GEN1 | 1 | 0.0008 | across control | Waste Bituminous/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.01921 | 0.44236 | 0.53843
Scrubgrass Generating Company L. P. | 50974 | GEN1 | 2 | 0.00102 | across control | Waste Bituminous/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.02166 | 0.37582 | 0.60252
Scrubgrass Generating Company L. P. | 50974 | GEN1 | 3 | 0.00151 | across control | Waste Bituminous/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.02268 | 0.34624 | 0.63108
|  |  | Average emission modification factor | 0.00111 | [5 empty] | Average speciated Hg fraction | 0.02118 | 0.38814 | 0.59068
Emission control device type Bin 28
R.M. Heskett Station | 0128190000-02790 | B2 | 1 | 0.44624 | across control | Lignite/None | FBC 7 | ESP- CS | NONE | NONE | 0.01768 | 0.24082 | 0.74151
R.M. Heskett Station | 0128190000-02790 | B2 | 2 | 0.88912 | across control | Lignite/None | FBC 7 | ESP- CS | NONE | NONE | 0.01221 | 0.07016 | 0.91762
R.M. Heskett Station | 0128190000-02790 | B2 | 3 | 0.45376 | across control | Lignite/None | FBC 7 | ESP- CS | NONE | NONE | 0.01106 | 0.03814 | 0.9508
|  |  | Average emission modification factor | 0.59637 | [5 empty] | Average speciated Hg fraction | 0.01365 | 0.11637 | 0.86998
Emission control device type Bin 29
TNP-One | 0400510000-07030 | U2 | 1 | 0.44893 | across control | Lignite/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.00425 | 0.71601 | 0.27975
TNP-One | 0400510000-07030 | U2 | 2 | 0.46037 | across control | Lignite/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.0059 | 0.6934 | 0.30071
TNP-One | 0400510000-07030 | U2 | 3 | 0.38122 | across control | Lignite/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.00238 | 0.72603 | 0.27159
|  |  | Average emission modification factor | 0.43017 | [5 empty] | Average speciated Hg fraction | 0.00418 | 0.71181 | 0.28401
Emission control device type Bin 30
Kline Township Cogen Facility | 50039 | GEN1 | 1 | 0.00248 | across control | Waste Anthracite/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.03061 | 0.2551 | 0.71429
Kline Township Cogen Facility | 50039 | GEN1 | 2 | 0.00256 | across control | Waste Anthracite/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.03061 | 0.2551 | 0.71429
Kline Township Cogen Facility | 50039 | GEN1 | 3 | 0.0026 | across control | Waste Anthracite/None | FBC 7 | BAGHOUSE | NONE | NONE | 0.02899 | 0.6087 | 0.36232
|  |  | Average emission modification factor | 0.00255 | [5 empty] | Average speciated Hg fraction | 0.03007 | 0.37297 | 0.59696
Emission control device type Bin 31
Dwayne Collier Battle Cogeneration Facility | 10384 | 2B | 1 | 0.07072 | across control | Bituminous/None | STOKER/NOX/DRY | BAGHOUSE | SDA | NONE | 0.34483 | 0.13793 | 0.51724
Dwayne Collier Battle Cogeneration Facility | 10384 | 2B | 2 | 0.05652 | across control | Bituminous/None | STOKER/NOX/DRY | BAGHOUSE | SDA | NONE | 0.19403 | 0.18657 | 0.6194
Dwayne Collier Battle Cogeneration Facility | 10384 | 2B | 3 | 0.06285 | across control | Bituminous/None | STOKER/NOX/DRY | BAGHOUSE | SDA | NONE | 0.05983 | 0.21368 | 0.7265
|  |  | Average emission modification factor | 0.06337 | [5 empty] | Average speciated Hg fraction | 0.19956 | 0.17939 | 0.62105
Emission control device type Bin 32 - Not Used in Model
Emission control device type Bin 33
Big Brown | 0443720000-03497 | 1 | 1 | 0.99281 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | COMP COAL | NONE | 0.00229 | 0.39599 | 0.60172
Big Brown | 0443720000-03497 | 1 | 2 | 1.1296 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | COMP COAL | NONE | 0.00088 | 0.4091 | 0.59001
Big Brown | 0443720000-03497 | 1 | 3 | 1.1199 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | COMP COAL | NONE | 0.00091 | 0.45496 | 0.54413
Monticello | 0443720000-06147 | 1 | 1 | 0.71314 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | COMP COAL | NONE | 0.00503 | 0.94819 | 0.04678
Monticello | 0443720000-06147 | 1 | 2 | 1.5152 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | COMP COAL | NONE | 0.00121 | 0.83816 | 0.16063
Monticello | 0443720000-06147 | 1 | 3 | 1.4095 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS/BAGHOUSE | COMP COAL | NONE | 0.00078 | 0.8231 | 0.17613
|  |  | Second unit average emission modification factor | 1.1467 | [5 empty] | Average speciated Hg fraction | 0.00185 | 0.64492 | 0.35323
|  |  | First unit average emission modification correction factor | 1.0346
|  |  | Combined emission modification factor | 1.1864
Emission control device type Bin 34
Antelope Valley Station | 0013070000-06469 | B1 | 1 | 0.05451 | across control | Lignite/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.01333 | 0.56 | 0.42667
Antelope Valley Station | 0013070000-06469 | B1 | 2 | 1.0527 | across control | Lignite/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00267 | 0.08824 | 0.90909
Antelope Valley Station | 0013070000-06469 | B1 | 3 | 0.89297 | across control | Lignite/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.0032 | 0.0432 | 0.9536
Stanton Station | 0195140000-02824 | 10 | 1 | 0.93973 | across control | Lignite/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00073 | 0.03658 | 0.96269
Stanton Station | 0195140000-02824 | 10 | 2 | 1.003 | across control | Lignite/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00071 | 0.01555 | 0.98375
Stanton Station | 0195140000-02824 | 10 | 3 | 1.0131 | across control | Lignite/None | CONV/PC/NOX/DRY | BAGHOUSE | SDA | NONE | 0.00069 | 0.01384 | 0.98547
|  |  | Average emission modification factor | 0.826 | [5 empty] | Average speciated Hg fraction | 0.00356 | 0.12623 | 0.87021
Emission control device type Bin 35
Lewis & Clark | 0128190000-06089 | B1 | 1 | 0.49252 | across control | Lignite/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.00416 | 0.03468 | 0.96115
Lewis & Clark | 0128190000-06089 | B1 | 2 | 0.61262 | across control | Lignite/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.0003 | 0.02429 | 0.97541
Lewis & Clark | 0128190000-06089 | B1 | 3 | 0.91187 | across control | Lignite/None | CONV/PC/NOX/DRY | PARTSCRUB | NONE | NONE | 0.00027 | 0.03046 | 0.96927
|  |  | Average emission modification factor | 0.67234 | [5 empty] | Average speciated Hg fraction | 0.00158 | 0.02981 | 0.96861
Emission control device type Bin 36
Monticello | 0443720000-06147 | 3 | 1 | 0.78694 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00843 | 0.17939 | 0.81218
Monticello | 0443720000-06147 | 3 | 2 | 0.54432 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00689 | 0.01695 | 0.97617
Monticello | 0443720000-06147 | 3 | 3 | 0.57559 | last control | Lignite/None | CONV/PC/NONOX/DRY | ESP- CS | WETSCRUB | NONE | 0.00781 | 0.23713 | 0.75506
Limestone | 0089010000-00298 | LIM1 | 1 | 0.50597 | last control | Lignite/None | CONV/PC/NOX/WET | ESP- CS | WETSCRUB | NONE | 0.00222 | 0.1437 | 0.85407
Limestone | 0089010000-00298 | LIM1 | 2 | 0.52407 | last control | Lignite/None | CONV/PC/NOX/WET | ESP- CS | WETSCRUB | NONE | 0.01683 | 0.16129 | 0.82188
Limestone | 0089010000-00298 | LIM1 | 3 | 0.43934 | last control | Lignite/None | CONV/PC/NOX/WET | ESP- CS | WETSCRUB | NONE | 0.00671 | 0.06855 | 0.92474
|  |  | Second unit average emission modification factor | 0.5627 | [5 empty] | Average speciated Hg fraction | 0.00815 | 0.1345 | 0.85735
|  |  | First unit average emission modification correction factor | 1.0346
|  |  | Combined emission modification factor | 0.58219
Emission control device type Bin 37
Bay Front Plant Generating | 0137810000-03982 | 5 | 1 | 0.99664 | across control | Bituminous/None | CYCLONE/NONOX/WET | MECH | NONE | NONE | 0.32114 | 0.1626 | 0.51626
Bay Front Plant Generating | 0137810000-03982 | 5 | 2 | 1.4654 | across control | Bituminous/None | CYCLONE/NONOX/WET | MECH | NONE | NONE | 0.15833 | 0.50833 | 0.33333
Bay Front Plant Generating | 0137810000-03982 | 5 | 3 | 2.25 | across control | Bituminous/None | CYCLONE/NONOX/WET | MECH | NONE | NONE | 0.0829 | 0.6114 | 0.3057
|  |  | Average emission modification factor | 1.5707 | [5 empty] | Average speciated Hg fraction | 0.18746 | 0.42744 | 0.3851
Emission control device type Bin 38
Bailly | 0137560000-00995 | 7 and 8 | 1 | 0.51169 | last control | Bituminous/Pet Coke | CYCLONE/NONOX/WET | ESP- CS | WETSCRUB | NONE | 0.0004 | 0.11196 | 0.88765
Bailly | 0137560000-00995 | 7 and 8 | 2 | 0.53609 | last control | Bituminous/Pet Coke | CYCLONE/NONOX/WET | ESP- CS | WETSCRUB | NONE | 0.00044 | 0.10522 | 0.89434
Bailly | 0137560000-00995 | 7 and 8 | 3 | 0.51382 | last control | Bituminous/Pet Coke | CYCLONE/NONOX/WET | ESP- CS | WETSCRUB | NONE | 0.00122 | 0.1218 | 0.87698
|  |  | Second unit average emission modification factor | 0.52053 | [5 empty] | Average speciated Hg fraction | 0.00069 | 0.11299 | 0.88632
|  |  | First unit average emission modification correction factor | 0.95132
|  |  | Combined emission modification factor | 0.4952
Emission control device type Bin 39
Coyote | 0128190000-08222 | 1 | 1 | 0.88006 | across control | Lignite/None | CYCLONE/NONOX/WET | BAGHOUSE | SDA | NONE | 0.00594 | 0.00097 | 0.99309
Coyote | 0128190000-08222 | 1 | 2 | 0.02752 | across control | Lignite/None | CYCLONE/NONOX/WET | BAGHOUSE | SDA | NONE | 0.28846 | 0.48718 | 0.22436
Coyote | 0128190000-08222 | 1 | 3 | 0.94525 | across control | Lignite/None | CYCLONE/NONOX/WET | BAGHOUSE | SDA | NONE | 0.0042 | 0.02392 | 0.97188
|  |  | Average emission modification factor | 0.61761 | [5 empty] | Average speciated Hg fraction | 0.09953 | 0.17069 | 0.72978
Emission control device type Bin 40
AES Hawaii, Inc. | 10673 | AB | 1 | 0.43304 | across control | Subbituminous/None | FBC 7 | BAGHOUSE | NONE | SNCR | 0.00344 | 0.03436 | 0.9622
AES Hawaii, Inc. | 10673 | AB | 2 | 0.4626 | across control | Subbituminous/None | FBC 7 | BAGHOUSE | NONE | SNCR | 0.00165 | 0.02475 | 0.9736
AES Hawaii, Inc. | 10673 | AB | 3 | 0.52878 | across control | Subbituminous/None | FBC 7 | BAGHOUSE | NONE | SNCR | 0.00289 | 0.04335 | 0.95376
|  |  | Average emission modification factor | 0.4748 | [5 empty] | Average speciated Hg fraction | 0.00266 | 0.03416 | 0.96318
Emission control device type Bin 41
Meramec | 0194360000-02104 | 4 | 1 | 0.1873 | across control | Subbituminous/Bituminous | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00168 | 0.48658 | 0.51175
Meramec | 0194360000-02104 | 4 | 2 | 0.3003 | across control | Subbituminous/Bituminous | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00234 | 0.65861 | 0.33905
Meramec | 0194360000-02104 | 4 | 3 | 0.28037 | across control | Subbituminous/Bituminous | CONV/PC/NOX/DRY | ESP- CS | NONE | NONE | 0.00106 | 0.65539 | 0.34355
St Clair Power Plant | 0051090000-01743 | 4 | 1 | 0.66046 | across control | Subbituminous/Bituminous | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | NONE | 0.02691 | 0.30105 | 0.67204
St Clair Power Plant | 0051090000-01743 | 4 | 2 | 0.80925 | across control | Subbituminous/Bituminous | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | NONE | 0.00842 | 0.26792 | 0.72366
St Clair Power Plant | 0051090000-01743 | 4 | 3 | 0.92346 | across control | Subbituminous/Bituminous | CONV/PC/NONOX/DRY | ESP- CS | COMP COAL | NONE | 0.01254 | 0.19971 | 0.78775
|  |  | Average emission modification factor | 0.52686 | [5 empty] | Average speciated Hg fraction | 0.00882 | 0.42821 | 0.56297
Emission control device type Bin 42
Clifty Creek | 0092690000-00983 | 6 | 1 | 0.64416 | across control | Subbituminous/Bituminous | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.07764 | 0.40161 | 0.52075
Clifty Creek | 0092690000-00983 | 6 | 2 | 0.70486 | across control | Subbituminous/Bituminous | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00058 | 0.48527 | 0.51415
Clifty Creek | 0092690000-00983 | 6 | 3 | 0.63012 | across control | Subbituminous/Bituminous | CONV/PC/NOX/WET | ESP- HS | COMP COAL | NONE | 0.00768 | 0.58643 | 0.40589
|  |  | Average emission modification factor | 0.65971 | [5 empty] | Average speciated Hg fraction | 0.02863 | 0.4911 | 0.48026
Emission control device type Bin 43
Valley | 0208470000-04042 | 2 | 1 | 0.94333 | across control | Bituminous/Pet Coke | CONV/PC/NOX/DRY | BAGHOUSE | NONE | NONE | 0.045 | 0.795 | 0.16
Valley | 0208470000-04042 | 2 | 2 | 1.007 | across control | Bituminous/Pet Coke | CONV/PC/NOX/DRY | BAGHOUSE | NONE | NONE | 0.01887 | 0.77358 | 0.20755
Valley | 0208470000-04042 | 2 | 3 | 1.2521 | across control | Bituminous/Pet Coke | CONV/PC/NOX/DRY | BAGHOUSE | NONE | NONE | 0.00209 | 0.7837 | 0.21421
|  |  | Average emission modification factor | 1.0675 | [5 empty] | Average speciated Hg fraction | 0.02199 | 0.78409 | 0.19392
Emission control device type Bin 44
Shawnee Fossil Plant | 0186420000-01379 | 3 | 1 | 0.34588 | across control | Bituminous/Subbituminous | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.04762 | 0.40952 | 0.54286
Shawnee Fossil Plant | 0186420000-01379 | 3 | 2 | 0.31903 | across control | Bituminous/Subbituminous | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.08081 | 0.40909 | 0.5101
Shawnee Fossil Plant | 0186420000-01379 | 3 | 3 | 0.28837 | across control | Bituminous/Subbituminous | CONV/PC/NOX/DRY | BAGHOUSE | COMP COAL | NONE | 0.05 | 0.44444 | 0.50556
|  |  | Average emission modification factor | 0.31776 | [5 empty] | Average speciated Hg fraction | 0.05948 | 0.42102 | 0.5195
1 Although combustion NOx controls and furnace bottom type are listed in this column, they have no effect on the bin into which the unit was classified.
2 This column addresses external NOx controls only.
3 Speciation was accomplished by analyzing the data in the test reports and computing the total mercury leaving the last control device for each run. Then, within the run, we computed the percentage that each Hg species composed of the total. Then, within the bin, we took the average of each species column. These average percentages were then applied to the units that used the specific bin. A “0" in the data occurred when any speciated Hg outlet number was not provided or was unacceptable (according to the test method). The sum of the fractional splits is 1 except where slight rounding errors exist.
4 All test runs are listed as 1, 2, and 3. This does not mean that during the stack testing that these were the actual 1st, 2nd, or 3rd test runs. However, these were the runs presented in the test reports and date order was maintained.
5 Coal gasification units burn synthetic gas (derived from coal) in a complex process that requires no PM or SO2 control following the process.
6 A different method was used to average fuel type/boiler type/emission control system(s) from all dual-controlled units (units having both a PM and an SO2 control device) than was used for single-controlled units. Since stack test flue-gas speciated Hg was analyzed at the inlet and outlet of the last control device, the effect of the PM control on Hg removal on these dual-controlled units was not clear. Thus: EPA decided that it would be more realistic to add the PM control device removal of Hg to the SO2 control device removal of Hg for dual-controlled units. The PM control device average EMF was taken from the bin of a unit with a similar fuel type/boiler type/PM emission control system to the dual-controlled bin it was modifying. The average EMF of a tested unit with a single PM control device was multiplied by each individual run EMF from a similarly configured dual-controlled unit. These modified EMFs were averaged. This average was used to compute the Hg removal of a dual-controlled unit in the national emissions model.
7 All fluidized bed combustor units tested had limestone injection in their furnaces to reduce SO2.

## 04_Hg_Speciation_Profiles
A LISTING OF TEST BINS WITH HG REMOVALS AND PERCENT SPECIATION
Bin Type | Fuel, Boiler, Emission control device(s) | Hg Removal |  | PERCENT SPECIATION
|  |  | Particulate Hg | Oxidized Hg | Elemental Hg
0 | Bituminous Coal, Coal Gasification | 0.257% | 0.513% | 8.472% | 91.02%
1 | Bituminous Coal, PC Boiler with ESP-CS | 29.13% | 6.106% | 68.19% | 25.7%
2 | Bituminous Coal and Pet. Coke, PC Boiler with ESP-CS | 60.36% | 1.171% | 46.56% | 52.27%
3 | Bituminous Coal, PC Boiler with SNCR and ESP-CS | 89.88% | 20.32% | 27.12% | 52.56%
4 | Bituminous Coal, PC Boiler with ESP-HS | 10.65% | 4.901% | 57.84% | 37.26%
5 | Bituminous Coal, PC Boiler with PM Scrubber | 12.07% | 1.803% | 19.5% | 78.69%
6 | Bituminous Coal, PC Boiler with Dry Sorbent Injection and ESP-CS | 44.89% | 0.161% | 67.1% | 32.74%
7 | Bituminous Coal, PC Boiler with FF Baghouse | 89.37% | 3.98% | 62.58% | 33.44%
8 | Bituminous Coal, PC Boiler with SDA/FF Baghouse | 98.17% | 9.171% | 28.86% | 61.97%
9 | Bituminous Coal, PC Boiler with SCR and SDA/FF Baghouse | 97.36% | 5.058% | 46.04% | 48.9%
10 | Bituminous Coal, PC Boiler with ESP-CS and Wet FGD | 77.72% | 0.218% | 7.779% | 92%
11 | Bituminous Coal, PC Boiler with ESP-HS and Wet FGD | 39.19% | 0.626% | 20.68% | 78.7%
12 | Bituminous Coal, PC Boiler with FF Baghouse and Wet FGD | 97.39% | 6.481% | 33% | 60.52%
13 | Subbituminous Coal, PC Boiler with ESP-CS | 2.652% | 0.155% | 30.83% | 69.01%
14 | Subbituminous Coal, PC Boiler with ESP-HS | 0% | 0.063% | 12.52% | 87.41%
15 | Subbituminous Coal, PC Boiler with FF Baghouse | 72.58% | 1.491% | 82.83% | 15.68%
16 | Subbituminous Coal, PC Boiler with PM Scrubber | 0% | 1.453% | 5.112% | 93.44%
17 | Subbituminous Coal, PC Boiler with SDA/ESP | 0% | 0.318% | 3.821% | 95.86%
18 | Subbituminous Coal, PC Boiler with SDA/FF Baghouse | 23.3% | 0.987% | 4.346% | 94.67%
19 | Subbituminous Coal, PC Boiler with ESP-CS and Wet FGD | 15.93% | 0.428% | 2.94% | 96.63%
20 | Subbituminous Coal, PC Boiler with ESP-HS and Wet FGD | 8.034% | 1.17% | 4.461% | 94.37%
21 | Lignite Coal, PC Boiler with ESP-CS | 0% | 0.094% | 3.62% | 96.29%
22 | Subbituminous Coal, Cyclone Boiler with PM Scrubber | 22.15% | 2.344% | 5.751% | 91.91%
23 | Subbituminous Coal/Pet. Coke, Cyclone Boiler with ESP-HS | 0% | 0.926% | 7.524% | 91.55%
24 | Lignite Coal Coal, Cyclone Boiler with ESP-CS | 4.868% | 0.043% | 16.99% | 82.97%
25 | Bituminous Coal/Pet.Coke, Fludized Bed Combustor with SNCR and FF Baghouse | 91.82% | 42.44% | 27.87% | 29.7%
26 | Not Used
27 | Bituminous Waste, Fludized Bed Combustor with FF Baghouse | 99.89% | 2.118% | 38.81% | 59.07%
28 | Lignite Coal, Fludized Bed Combustor with ESP-CS | 40.36% | 1.365% | 11.64% | 87%
29 | Lignite Coal, Fludized Bed Combustor with FF Baghouse | 56.98% | 0.418% | 71.18% | 28.4%
30 | Antracite Waste, Fludized Bed Combustor with FF Baghouse | 99.74% | 3.007% | 37.3% | 59.7%
31 | Bituminous Coal, Stoker Boiler with SDA/FF Baghouse | 93.66% | 19.96% | 17.94% | 62.1%
32 | Not Used
33 | Lignite Coal, PC Boiler with ESP-CS and FF Baghouse | 0% | 0.185% | 64.49% | 35.32%
34 | Lignite Coal, PC Boiler with SDA/FF Baghouse | 17.4% | 0.356% | 12.62% | 87.02%
35 | Lignite Coal, PC Boiler with PM Scrubber | 32.77% | 0.158% | 2.981% | 96.86%
36 | Lignite Coal, PC Boiler with ESP-CS and Wet FGD | 41.78% | 0.815% | 13.45% | 85.73%
37 | Bituminous Coal, Cyclone Boiler with Mechanical Collector | 0% | 18.75% | 42.74% | 38.51%
38 | Bituminous Coal/Pet. Coke, Cyclone with ESP-CS and Wet FGD | 50.48% | 0.069% | 11.3% | 88.63%
39 | Lignite Coal, Cyclone Boiler with SDA/FF Baghouse | 38.24% | 9.953% | 17.07% | 72.98%
40 | Subbituminous Coal, Fludized Bed Combustor with SNCR and FF Baghouse | 52.52% | 0.266% | 3.416% | 96.32%
41 | Subbituminous Coal/Bituminous Coal, PC Boiler with ESP-CS | 47.31% | 0.882% | 42.82% | 56.3%
42 | Subbituminous Coal/Bituminous Coal, PC Boiler with ESP-HS | 34.03% | 2.863% | 49.11% | 48.03%
43 | Bituminous Coal/Pet. Coke, PC Boiler with FF Baghouse | 0% | 2.199% | 78.41% | 19.39%
44 | Bituminous Coal/Subbituminous Coal, PC Boiler with FF Baghouse | 68.22% | 5.948% | 42.1% | 51.95%