## Sheet1. 1st Quarter
FIELD-SET 3: East F-200 RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Lincoln Water System | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 2 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-12-30 | [5 empty] | 20-min. EBCT Start Date | 1998-12-30 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NE3110926 | Carbon trade name | F200 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Ozone | Typical ozone dose was 1.66 mg/L. | full | 10-min. EBCT Start Time | 9:45 | [5 empty] | 20-min. EBCT Start Time | 9:45 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.5%
Water Industry Data Base Number (optional) | 5592 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.48 | 4 | 4.75 | Filtration | Glass fiber filter (pore size 1.0 micormeter). | bench | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 15
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 13.6 | 6 | 3.35 |  |  |  | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | E-10-1 | N | 1998-12-30 | 9:52 | 0.11667 | 9.6915 | 7.74 | 21.4 | 0.4091 | 0.0034 | 0.83109 | 1.4 | 1.08 | 0.32 | 15 | NA | 16.5 | 36.9 | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | E-20-1 | N | 1998-12-30 | 9:52 | 0.11667 | 4.8748 | 7.91 | 21.4 | 0.3528 | 0.0042 | 1.1905 | 1.4 | 1.12 | 0.28 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.4 | 8 | 2.36 |  |  |  | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | E-10-2 | N | 1998-12-30 | 16:00 | 6.25 | 519.189 | 7.75 | 21.5 | 0.521 | 0.006 | 1.1516 | 1.4 | 1.04 | 0.36 | 15 | NA | 16.5 | NR | BMRL | BMRL | 1.2 | 1 | 2.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | E-20-3 | N | 1998-12-30 | 22:03 | 12.3 | 513.9412 | 7.78 | 21.7 | 0.4705 | 0.0056 | 1.1902 | 1.4 | 1.08 | 0.32 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | NA
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.538 | 10 | 2 |  |  |  | Sampling date | MM/DD/YY | 1998-12-30 | 1999-01-12 | --- | --- |  | Sampling date | MM/DD/YY | 1998-12-30 | 1999-01-12 | --- | --- |  | E-10-3 | N | 1998-12-30 | 22:00 | 12.25 | 1017.6105 | 7.83 | 21.7 | 0.6612 | 0.007 | 1.0587 | 1.4 | 1.06 | 0.34 | 15 | NA | 16.5 | NR | BMRL | BMRL | 2 | 1.5 | 3.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | E-20-12 | N | 1999-01-01 | 7:10 | 45.4167 | 1897.6825 | 7.74 | 21 | 0.5627 | 0.0084 | 1.4928 | 1.4 | 1.06 | 0.34 | 15 | NA | 16.5 | NR | BMRL | BMRL | 2.1 | 1.6 | 3.7 | BMRL | BMRL | BMRL | BMRL | 1.4 | BMRL | NA | NA | NA | 1.4 | 1.4 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 140 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 9:45 | 16:25 | --- | --- |  | Sampling time | hh:mm | 9:45 | 16:25 | --- | --- |  | E-10-4 | N | 1998-12-31 | 7:16 | 21.5167 | 1787.3948 | 7.71 | 20.8 | 0.773 | 0.0108 | 1.3972 | 1.4 | 1.03 | 0.37 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 2.5 | 1.7 | 4.2 | BMRL | 1.2 | BMRL | BMRL | 1.4 | BMRL | NA | NA | NA | 2.6 | 2.6 | E-20-15 | N | 1999-01-01 | 16:10 | 54.4167 | 2273.7371 | 7.82 | 20.5 | 0.6905 | 0.0086 | 1.2455 | 1.4 | 1.02 | 0.38 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 2.8 | 2.2 | 5 | BMRL | 1.5 | BMRL | BMRL | 1.6 | BMRL | NA | NA | NA | 3.1 | 3.1 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 318.6667 | --- | --- |  | Operation time | hh.hh | 0 | 318.6667 | --- | --- |  | E-10-8 | N | 1998-12-31 | 19:15 | 33.5 | 2782.8532 | 7.74 | 20 | 0.8559 | 0.012 | 1.402 | 1.4 | 0.99 | 0.41 | 15 | NA | 16.5 | NR | BMRL | 1.4 | 3.6 | 2.2 | 7.2 | BMRL | 2.9 | BMRL | BMRL | 1.7 | 1.4 | NA | NA | NA | 4.6 | 6 | E-20-17 | N | 1999-01-02 | 7:29 | 69.7333 | 2913.7261 | 7.79 | 21 | 0.8569 | 0.0116 | 1.3537 | 1.4 | 0.99 | 0.41 | 15 | NA | 16.5 | NR | BMRL | 1.3 | 3.9 | 2.9 | 8.1 | BMRL | 2.7 | BMRL | BMRL | 1.8 | 1 | NA | NA | NA | 4.5 | 5.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | NA
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 26471.718 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 13315.1156 | --- | --- |  | E-10-12 | N | 1999-01-01 | 7:10 | 45.4167 | 3772.7736 | 7.74 | 21 | 1.0426 | 0.0136 | 1.3044 | 1.4 | 0.92 | 0.48 | 15 | NA | 16.5 | 48.6 | BMRL | 1.9 | 4.6 | 2.6 | 9.1 | BMRL | 3 | BMRL | BMRL | 2 | 3.4 | NA | NA | NA | 5 | 8.4 | E-20-20 | N | 1999-01-02 | 21:52 | 84.1167 | 3514.717 | 7.8 | 20.4 | 0.8894 | 0.011 | 1.2368 | 1.6 | 1.15 | 0.45 | 15 | NA | 16.5 | BMRL | BMRL | 1.5 | 4.1 | 2.6 | 8.2 | BMRL | 1.8 | BMRL | BMRL | 1.8 | 1.9 | NA | NA | NA | 3.6 | 5.5 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 160 | 170 | 165 | 6.0606 |  | Alkalinity | mg/L as CaCO3 | 160 | 170 | 165 | 6.0606 |  | E-10-14 | N | 1999-01-01 | 12:35 | 50.8333 | 4222.7374 | 7.82 | 20.2 | 1.1147 | 0.0146 | 1.3098 | 1.6 | 1.08 | 0.52 | 15 | NA | 16.5 | 40.7 | BMRL | 2.6 | 5.8 | 3.1 | 11.5 | BMRL | 3.1 | BMRL | BMRL | 2.4 | 4.3 | NA | NA | NA | 5.5 | 9.8 | E-20-22 | N | 1999-01-03 | 11:54 | 98.15 | 4101.0835 | 7.88 | 17.9 | 1.0782 | 0.0102 | 0.94602 | 1.6 | 1.1 | 0.5 | 15 | NA | 16.5 | BMRL | BMRL | 1.8 | 4.9 | 3.1 | 9.8 | BMRL | 1 | BMRL | BMRL | 1.9 | 2.9 | NA | NA | NA | 2.9 | 5.8 | Labor Rate + Fringe ($/work-hour) | 23.08
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 8812.9385 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 201 | 220 | 210.5 | 9.0261 |  | Total hardness | mg/L as CaCO3 | 201 | 220 | 210.5 | 9.0261 |  | E-10-17 | N | 1999-01-02 | 7:25 | 69.6667 | 5787.227 | 7.75 | 21 | 1.234 | 0.0168 | 1.3614 | 1.7 | 1.14 | 0.56 | 15 | NA | 16.5 | 48.1 | 1.1 | 2.8 | 6 | 3.1 | 13 | BMRL | 1.5 | BMRL | BMRL | 3.6 | 3.3 | NA | NA | NA | 5.1 | 8.4 | E-20-25 | N | 1999-01-04 | 7:41 | 117.9333 | 4927.707 | 7.79 | 20.4 | 1.1 | 0.012 | 1.0909 | 1.6 | 1.09 | 0.51 | 15 | NA | 16.5 | 31.4 | BMRL | 2.2 | 5.3 | 3.1 | 10.6 | BMRL | BMRL | BMRL | BMRL | 2.2 | 2.8 | NA | NA | NA | 2.2 | 5 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 17625.877 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 153 | 179 | 166 | 15.6627 |  | Calcium hardness | mg/L as CaCO3 | 153 | 179 | 166 | 15.6627 |  | E-10-20 | N | 1999-01-02 | 21:55 | 84.1667 | 6991.7456 | 7.7 | 20.4 | 1.3359 | 0.0174 | 1.3025 | 1.7 | 0.94 | 0.76 | 15 | NA | 16.5 | NR | 1.3 | 3.3 | 6.5 | 3.2 | 14.3 | BMRL | 1.4 | BMRL | BMRL | 3.4 | 2.4 | NA | NA | NA | 4.8 | 7.2 | E-20-36 | N | 1999-01-08 | 8:05 | 214.3333 | 8955.6688 | 7.74 | 22.9 | 1.3 | 0.014 | 1.0769 | 1.7 | 0.88 | 0.82 | 15 | NA | 16.5 | 42.3 | BMRL | 2.9 | 6.1 | 3.4 | 12.4 | BMRL | BMRL | BMRL | BMRL | 2.4 | 1.5 | NA | NA | NA | 2.4 | 3.9 | Electric Rate ($/kW-h) | 0.0437
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 22913.6401 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | E-10-21 | N | 1999-01-03 | 7:42 | 93.95 | 7804.4495 | 7.79 | 19.8 | 1.4212 | 0.0186 | 1.3088 | 1.7 | 1.01 | 0.69 | 15 | NA | 16.5 | 44.3 | 1.5 | 3.7 | 7.1 | 3.2 | 15.5 | BMRL | 1.4 | BMRL | BMRL | 2.9 | 2.1 | NA | NA | NA | 4.3 | 6.4 | E-20-38 | N | 1999-01-09 | 7:56 | 238.1833 | 9952.2133 | 7.71 | 22.2 | 1.42 | 0.0146 | 1.0282 | 1.7 | 0.92 | 0.78 | 15 | NA | 16.5 | 39.2 | BMRL | 2.8 | 6.1 | 3.2 | 12.1 | BMRL | BMRL | BMRL | BMRL | 2.4 | 1.5 | NA | NA | NA | 2.4 | 3.9 | Fuel Oil Rate ($/gal) | 0.49
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 66 | 84 | 75 | 24 |  | Bromide | mg/L | 66 | 84 | 75 | 24 |  | E-10-24 | N | 1999-01-03 | 19:45 | 106 | 8805.4459 | 7.74 | 20.6 | 1.4996 | 0.0162 | 1.0803 | 1.9 | 1.2 | 0.7 | 15 | NA | 16.5 | 42.2 | 1.4 | 3.8 | 6.8 | 2.9 | 14.9 | BMRL | 1.5 | 1.4 | BMRL | 2.5 | 2.1 | NA | NA | NA | 5.4 | 7.5 | E-20-43 | N | 1999-01-11 | 19:36 | 297.85 | 12445.3154 | NA | 22.4 | 1.55 | 0.018 | 1.1613 | 1.9 | 0.9 | 1 | 15 | NA | 16.5 | 43.2 | 1.4 | 3.7 | 7 | 3.5 | 15.6 | BMRL | 1 | BMRL | BMRL | 2.3 | 1.6 | NA | NA | NA | 3.3 | 4.9 | Natural Gas Rate ($/ft3) | 0.0033
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | E-10-26 | Y | 1999-01-04 | 14:10 | 124.4167 | 10335.3229 | 7.75 | 21 | 1.645 | 0.022 | 1.3374 | 1.9 | 1.175 | 0.725 | 15 | NA | 16.5 | 47.85 | 1.6 | 4.1 | 7.15 | 3 | 15.85 | BMRL | 1.5 | 1.75 | BMRL | 2.4 | 2 | NA | NA | NA | 5.65 | 7.65 | E-20-45 | Y | 1999-01-12 | 13:55 | 316.1667 | 13210.656 | 7.8 | 22.4 | 1.72 | 0.021 | 1.2209 | 1.9 | 0.865 | 1.035 | 15 | NA | 16.5 | 51.1 | 1.9 | 4.55 | 8.15 | 3.85 | 18.45 | BMRL | 1.1 | 1.3 | BMRL | 2.55 | 2 | NA | NA | NA | 4.95 | 6.95 | Current Process Water Rate ($/1000 gal) | 0.17
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.2046e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.0905 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  |  |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 11.6298 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-12-30 | 1999-01-01 | 1999-01-04 | --- | --- | Sampling date | MM/DD/YY | 1998-12-30 | 1999-01-01 | 1999-01-12 | --- | --- |  |  |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | LWS Ashland WTP-Ozone |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 9.2003 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 9:45 | 17:20 | 14:10 | --- | --- | Sampling time | hh:mm | 9:45 | 17:20 | 13:55 | --- | --- |  |  |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | Other/GW |  |  | RSSCT flow rate, QSC (mL/min) | 14.5723 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 55.5833 | 124.4167 | --- | --- | Operation time | hh.hh | 0 | 55.5833 | 316.1667 | --- | --- |  |  |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Ozone |  |  | Estimated total influent volume required, VSCT (L) | 720.6443 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 4617.3211 | 10335.3229 | --- | --- | Bed volumes | (20 minute) | 0 | 2322.4849 | 13210.656 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | ICR455 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.7 | 7.56 | 7.75 | 7.67 | 1.2841 | pH | --- | 7.7 | 7.56 | 7.75 | 7.67 | 1.2841 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NE3110926 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.105 | 0.13 | 0.16 | 0.13167 | 20.9148 | Turbidity | ntu | 0.11 | 0.13 | 0.16 | 0.13333 | 18.8746 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 9.8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 8.4 | 400 | 0.037 |  |  |  | Temperature | oC | 21.4 | 16.2 | 21 | 19.5333 | 14.814 | Temperature | oC | 21.4 | 16.2 | 21 | 19.5333 | 14.814
Historical Average Water Temperature (oC) | 13.4 |  |  | Estimated full-scale run time, tLCT (days) | 133.6629 | [5 empty] | Total organic carbon | mg/L | 2.1794 | 2.19 | 2.0643 | 2.1446 | 3.2508 | Total organic carbon | mg/L | 2.1794 | 2.19 | 2.0643 | 2.1446 | 3.2508 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.72228 | [5 empty] | UV254 | cm-1 | 0.0334 | 0.033 | 0.0322 | 0.032867 | 1.8591 | UV254 | cm-1 | 0.0334 | 0.033 | 0.0322 | 0.032867 | 1.8591 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 11.4931 | [5 empty] | SUVA | L/(mg*m) | 1.5325 | 1.5068 | 1.5599 | 1.5331 | 1.7289 | SUVA | L/(mg*m) | 1.5325 | 1.5068 | 1.5599 | 1.5331 | 1.7289 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 11.0753 | [5 empty] | SDS-Cl2 dose | mg/L | 2.2 | 2.2 | 2.2 | 2.2 | 0 | SDS-Cl2 dose | mg/L | 2.2 | 2.2 | 2.2 | 2.2 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 241.1718 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.2 | 1.23 | 1.04 | 1.1567 | 8.8309 | SDS-Free Cl2 residual | mg/L | 1.2 | 1.23 | 1.04 | 1.1567 | 8.8309 | E-10-26a | Primary | 1999-01-04 | 14:10 | 124.4167 | 10335.3229 | 7.75 | 21 | 1.69 | 0.022 | 1.3018 | 1.9 | 1.19 | 0.71 | 15 | NA | 16.5 | 46.1 | 1.6 | 4.1 | 7.3 | 3.1 | 16.1 | BMRL | 1.5 | 1.8 | BMRL | 2.4 | 2 | NA | NA | NA | 5.7 | 7.7 | E-20-45a | Primary | 1999-01-12 | 13:55 | 316.1667 | 13210.656 | 7.8 | 22.4 | 1.66 | 0.021 | 1.2651 | 1.9 | 0.87 | 1.03 | 15 | NA | 16.5 | 50.9 | 1.9 | 4.5 | 8.1 | 3.8 | 18.3 | BMRL | 1.2 | 1.3 | BMRL | 2.6 | 1.8 | NA | NA | NA | 5.1 | 6.9
|  |  |  | Mass GAC required, mSC (g) | 5.6626 | [5 empty] | SDS-Cl2 demand | mg/L | 1 | 0.97 | 1.16 | 1.0433 | 9.7901 | SDS-Cl2 demand | mg/L | 1 | 0.97 | 1.16 | 1.0433 | 9.7901 | E-10-26b | Duplicate | 1999-01-04 | 14:10 | 124.4167 | 10335.3229 | 7.75 | 21 | 1.6 | 0.022 | 1.375 | 1.9 | 1.16 | 0.74 | 15 | NA | 16.5 | 49.6 | 1.6 | 4.1 | 7 | 2.9 | 15.6 | BMRL | 1.5 | 1.7 | BMRL | 2.4 | 2 | NA | NA | NA | 5.6 | 7.6 | E-20-45b | Duplicate | 1999-01-12 | 13:55 | 316.1667 | 13210.656 | 7.8 | 22.4 | 1.78 | 0.021 | 1.1798 | 1.9 | 0.86 | 1.04 | 15 | NA | 16.5 | 51.3 | 1.9 | 4.6 | 8.2 | 3.9 | 18.6 | BMRL | 1 | 1.3 | BMRL | 2.5 | 2.2 | NA | NA | NA | 4.8 | 7
[11 empty] | SDS-Chlorination temp. | oC | 15 | 15 | 15 | 15 | 0 | SDS-Chlorination temp. | oC | NA | 15 | NA | 15 | #DIV/0! |  | Average | --- | --- | --- | --- | 7.75 | 21 | 1.645 | 0.022 | 1.3384 | 1.9 | 1.175 | 0.725 | 15 | #DIV/0! | 16.5 | 47.85 | 1.6 | 4.1 | 7.15 | 3 | 15.85 | #DIV/0! | 1.5 | 1.75 | #DIV/0! | 2.4 | 2 | #DIV/0! | #DIV/0! | #DIV/0! | 5.65 | 7.65 |  | Average | --- | --- | --- | --- | 7.8 | 22.4 | 1.72 | 0.021 | 1.2224 | 1.9 | 0.865 | 1.035 | 15 | #DIV/0! | 16.5 | 51.1 | 1.9 | 4.55 | 8.15 | 3.85 | 18.45 | #DIV/0! | 1.1 | 1.3 | #DIV/0! | 2.55 | 2 | #DIV/0! | #DIV/0! | #DIV/0! | 4.95 | 6.95
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-Chlorination pH | --- | NA | NA | NA | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | 0 | 0 | 5.4711 | 0 | 5.4711 | 0 | 2.5532 | 4.1379 | 0 | #VALUE! | 0 | 7.3145 | 0 | 0 | 4.1958 | 6.6667 | 3.1546 | #VALUE! | 0 | 5.7143 | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 1.7699 | 1.3072 |  | RPD | --- | --- | --- | --- | 0 | 0 | 6.9767 | 0 | 6.9767 | 0 | 1.1561 | 0.96618 | 0 | #VALUE! | 0 | 0.78278 | 0 | 2.1978 | 1.227 | 2.5974 | 1.626 | #VALUE! | 18.1818 | 0 | #VALUE! | 3.9216 | 20 | #VALUE! | #VALUE! | #VALUE! | 6.0606 | 1.4388
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 16.7 | [5 empty] | SDS-Incubation time | hours | 16.5 | 16.5 | 16.5 | 16.5 | 0 | SDS-Incubation time | hours | NA | 16.5 | NA | 16.5 | #DIV/0! |  | Primary |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Primary |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Estimated full-scale run time, tLCT (days) | 265.7346 | [5 empty] | SDS-TOX | mg Cl- /L | 114 | 159 | 93.5 | 122.1667 | 27.4256 | SDS-TOX | mg Cl- /L | 114 | 159 | 93.5 | 122.1667 | 27.4256 |  | Duplicate |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Duplicate |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.436 | [5 empty] | SDS-CHCl3 | mg/L | 9 | 8.4 | 7.5 | 8.3 | 9.0962 | SDS-CHCl3 | mg/L | 9 | 8.4 | 7.5 | 8.3 | 9.0962 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
|  |  |  | Estimated RSSCT run time, tSCT (days) | 22.8494 | [5 empty] | SDS-BDCM | mg/L | 11.9 | 11.5 | 10.1 | 11.1667 | 8.4641 | SDS-BDCM | mg/L | 11.9 | 11.5 | 10.1 | 11.1667 | 8.4641 |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | RSSCT bed length, lSC (cm) | 22.0188 | [5 empty] | SDS-DBCM | mg/L | 15.5 | 15.3 | 13.3 | 14.7 | 8.2759 | SDS-DBCM | mg/L | 15.5 | 15.3 | 13.3 | 14.7 | 8.2759 |  | Primary |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Primary |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 479.4725 | [5 empty] | SDS-CHBr3 | mg/L | 5.5 | 5.6 | 5.3 | 5.4667 | 2.7943 | SDS-CHBr3 | mg/L | 5.5 | 5.6 | 5.3 | 5.4667 | 2.7943 |  | Duplicate |  |  | -867825.75 | -72090497.3856 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Duplicate |  |  | -867825.75 | -36261088.5053 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Mass GAC required, mSC (g) | 11.2578 | [5 empty] | SDS-THM4 | mg/L | 41.9 | 40.8 | 36.2 | 39.6333 | 7.6294 | SDS-THM4 | mg/L | 41.9 | 40.8 | 36.2 | 39.6333 | 7.6294 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | 6.6 | 6.4 | 3.2 | 5.4 | 35.3311 | SDS-DCAA* | mg/L | 6.6 | 6.4 | 3.2 | 5.4 | 35.3311 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 1.9 | 2.1 | 3.2 | 2.4 | 29.1667 | SDS-TCAA* | mg/L | 1.9 | 2.1 | 3.2 | 2.4 | 29.1667 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.4 | 1.3 | BMRL | 1.35 | 5.2378 | SDS-MBAA* | mg/L | 1.4 | 1.3 | BMRL | 1.35 | 5.2378
[11 empty] | SDS-DBAA* | mg/L | 6 | 5.9 | 2.7 | 4.8667 | 38.5696 | SDS-DBAA* | mg/L | 6 | 5.9 | 2.7 | 4.8667 | 38.5696
[11 empty] | SDS-BCAA* | mg/L | 6.5 | 6.4 | 3.1 | 5.3333 | 36.2769 | SDS-BCAA* | mg/L | 6.5 | 6.4 | 3.1 | 5.3333 | 36.2769
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 15.9 | 15.7 | 9.1 | 13.5667 | 28.5224 | SDS-HAA5 | mg/L | 15.9 | 15.7 | 9.1 | 13.5667 | 28.5224
[11 empty] | SDS-HAA6 | mg/L | 22.4 | 22.1 | 12.2 | 18.9 | 30.7106 | SDS-HAA6 | mg/L | 22.4 | 22.1 | 12.2 | 18.9 | 30.7106
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on E5: Same GAC sample as used for the West Plant F-200 study
Note on H7: Resc was adjusted from 0.5 to match the actual ave. Qsc
Note on H8: The full scale water temp was 13.6C in Dec. 1998
Note on H24: This flow rate is within +- 5% of the average flow rate for the test (13.15) mL/min for the 10 min. column and 13.23 mL/min. for the 20 min. column.
Note on H28: Target EBCT was 10 min. Column was designed using a lit. value of GAC density. EBCT shown represents EBCT calcuated using actual density.
Note on H37: Target EBCT was 20 min. Column was designed using a lit. value of GAC density. EBCT shown represents EBCT calcuated using actual density.
Note on Q3: Reviewer M.H. (12/18/99): Regarding the measurement of instantaneous DBPs, per Consultant: "No instantaneous DBPs (w/o SDS) were determined."
Note on S22: Same influent samples were used for 10 & 20 min. columns since they were fed from same reservoir and run at same time.
Note on U22: Bruce Dvorak: No other influent samples were taken. Note that the date was corrected after a review of our datasheets.
Note on W38: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on W43: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on W53: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on W54: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on Y3: Reviewer M.H. (12/18/99): Regarding the measurement of instantaneous DBPs, per Consultant: "No instantaneous DBPs (w/o SDS) were determined."
Note on AC22: Bruce Dvorak: Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biolical degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors.
Note on AE38: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on AE43: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on AE53: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on AE54: Reviewer M.H. (12/18/99): Per Consultant: "Note that date was corrected after reviewing our datasheets. Also note that this data is correct. The difference in THM4, TOX, and HAA conc. could be a change in the raw water conc during sampling (the influent was collected in 20L glass carboys over the course of 2 hrs at the plant), due to biological degradation (although the samples were kept in a cold rooms @4C until 24 hrs before use), or the difference could be due to lab measurement errors."
Note on AG33: Participation in the treatment studies by the Lincoln Water System was voluntary. Full duplicates were not performed. Partially for cost savings and partially from a mistake in understanding of the study requirements.
Note on AU8: Bruce Dvorak: temp. maintained in an incubator that was maintained (and checked on a daily basis) during the entire treatment study. Inc. had +-0.5C accuracy.
Note on AV8: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV9: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV10: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV11: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV12: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV13: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV14: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV15: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV16: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV17: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV18: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on AV19: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on BP33: Participation in the treatment studies by the Lincoln Water System was voluntary. Full duplicates were not performed. Partially for cost savings and partially from a mistake in understanding of the study requirements.
Note on CD8: Bruce Dvorak: temp. maintained in an incubator that was maintained (and checked on a daily basis) during the entire treatment study. Inc. had +-0.5C accuracy.
Note on CE8: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CZ6: Bruce Dvorak: Ave. value for past 2 years for Lincoln
Note on CZ7: Bruce Dvorak: Typical for Lincoln during past 2 years
Note on CZ8: Reviewer M.H. (2/2/00): Estimated by utility.
Note on CZ9: Reviewer M.H. (2/2/00): Per EPA Treatment Study Coordinator, utility is unable to estimate a value.
Note on CZ14: Reviewer M.H. (2/2/00): Average of $19.11 and $27.05 per hour.
Note on CZ15: Reviewer M.H. (2/2/00): Per EPA Treatment Study Coordinator, utility is unable to estimate a value.
Note on CZ17: Bruce Dvorak: June 1, 1999
Note on CZ19: Bruce Dvorak: June 1, 1999
Note on CZ20: Reviewer M.H. (2/2/00): Estimated by EPA Treatment Studies Coordinator after discussions with utility.

## Sheet2. 2nd Quarter
FIELD-SET 3: East F-400 RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Lincoln Water System | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 2 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1999-01-20 | [5 empty] | 20-min. EBCT Start Date | 1999-01-20 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NE3110926 | Carbon trade name | F400 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Ozone | Typical ozone dose was 1.27 mg/L. | full | 10-min. EBCT Start Time | 10:30 | [5 empty] | 20-min. EBCT Start Time | 10:30 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.5%
Water Industry Data Base Number (optional) | 5592 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.49 | 4 | 4.75 | Filtration | Glass fiber filter (pore size 1.0 micormeter). | bench | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 15
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 11.3 | 6 | 3.35 |  |  |  | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | F-10-1 | N | 1999-01-20 | 10:32 | 0.033333 | 2.3734 | 7.88 | 22.9 | 0.304 | 0.0034 | 1.1184 | 1.4 | 1.05 | 0.35 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | F-20-1 | N | 1999-01-20 | 10:33 | 0.05 | 1.7801 | 7.78 | 22.9 | 0.217 | 0.0024 | 1.106 | 1.4 | 0.95 | 0.45 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.4 | 8 | 2.36 |  |  |  | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | F-10-4 | N | 1999-01-21 | 14:13 | 27.7167 | 1973.5117 | 7.63 | 23.4 | 0.41 | 0.006 | 1.4634 | 1.7 | 1.28 | 0.42 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 1.8 | 1.9 | 3.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | F-20-3 | N | 1999-01-21 | 7:07 | 20.6167 | 733.9849 | 7.85 | 22.9 | 0.28 | 0.0036 | 1.2857 | 1.4 | 1.05 | 0.35 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | BMRL | 1.1 | 1.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | NA
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.457 | 10 | 2 |  |  |  | Sampling date | MM/DD/YY | 1999-01-20 | 1999-02-18 | --- | --- |  | Sampling date | MM/DD/YY | 1999-01-20 | 1999-02-18 | --- | --- |  | F-10-5 | N | 1999-01-21 | 22:30 | 36 | 2563.3104 | 7.9 | 22.9 | 0.51 | 0.0066 | 1.2941 | 1.5 | 1.06 | 0.44 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 2.3 | 2.2 | 4.5 | BMRL | BMRL | BMRL | BMRL | 1.3 | BMRL | NA | NA | NA | 1.3 | 1.3 | F-20-5 | N | 1999-01-21 | 22:30 | 36 | 1281.6552 | 7.85 | 22.9 | 0.46 | 0.0044 | 0.95652 | 1.5 | 1.11 | 0.39 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 1.2 | 1 | 2.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 140 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 10:30 | 19:00 | --- | --- |  | Sampling time | hh:mm | 10:30 | 19:00 | --- | --- |  | F-10-7 | N | 1999-01-22 | 14:46 | 52.2667 | 3721.547 | 7.83 | 22.8 | 0.6 | 0.0088 | 1.4667 | 1.6 | 1.08 | 0.52 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 3.2 | 2.8 | 6 | BMRL | BMRL | BMRL | BMRL | 1.7 | BMRL | NA | NA | NA | 1.7 | 1.7 | F-20-13 | N | 1999-01-24 | 20:46 | 106.2667 | 3783.2563 | 7.81 | 22.6 | 0.57 | 0.0086 | 1.5088 | 1.5 | 1.09 | 0.41 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 2.7 | 3.1 | 5.8 | BMRL | BMRL | BMRL | BMRL | 1.5 | BMRL | NA | NA | NA | 1.5 | 1.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 704.5 | --- | --- |  | Operation time | hh.hh | 0 | 704.5 | --- | --- |  | F-10-8 | N | 1999-01-22 | 21:55 | 59.4167 | 4230.6489 | 7.86 | 23.1 | 0.73 | 0.01 | 1.3699 | 1.6 | 0.99 | 0.61 | 15 | NA | 16.5 | BMRL | BMRL | 1 | 3.8 | 3.7 | 8.5 | BMRL | BMRL | BMRL | BMRL | 2.1 | BMRL | NA | NA | NA | 2.1 | 2.1 | F-20-17 | N | 1999-01-26 | 20:25 | 153.9167 | 5479.6694 | 7.66 | 23.3 | 0.72 | 0.0106 | 1.4722 | 1.6 | 1.08 | 0.52 | 15 | NA | 16.5 | BMRL | BMRL | BMRL | 3.5 | 3.4 | 6.9 | BMRL | BMRL | BMRL | BMRL | 1.7 | BMRL | NA | NA | NA | 1.7 | 1.7 | 1998 ENR Construction Cost Index (CCI base year 1913) | NA
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 50162.5606 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 25081.2803 | --- | --- |  | F-10-11 | N | 1999-01-23 | 22:16 | 83.7667 | 5964.4436 | 8 | 22.5 | 0.9 | 0.0134 | 1.4889 | 1.7 | 1.03 | 0.67 | 15 | NA | 16.5 | BMRL | BMRL | 1.5 | 5.5 | 5 | 12 | BMRL | BMRL | BMRL | BMRL | 2.5 | 1.1 | NA | NA | NA | 2.5 | 3.6 | F-20-20 | N | 1999-01-28 | 9:15 | 190.75 | 6790.9925 | 7.79 | 21.8 | 0.83 | 0.0122 | 1.4699 | 1.6 | 1.17 | 0.43 | 15 | NA | 16.5 | BMRL | BMRL | 1.1 | 4.3 | 4.3 | 9.7 | BMRL | BMRL | BMRL | BMRL | 2.1 | BMRL | NA | NA | NA | 2.1 | 2.1 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 178 | 194 | 186 | 8.6022 |  | Alkalinity | mg/L as CaCO3 | 178 | 194 | 186 | 8.6022 |  | F-10-17 | N | 1999-01-26 | 20:25 | 153.9167 | 10959.3387 | 7.8 | 23.3 | 1.05 | 0.016 | 1.5238 | 1.8 | 1.18 | 0.62 | 15 | NA | 16.5 | 27.6 | BMRL | 1.8 | 5.7 | 4.8 | 12.3 | BMRL | BMRL | BMRL | BMRL | 2.3 | 1.1 | NA | NA | NA | 2.3 | 3.4 | F-20-24 | N | 1999-01-30 | 9:37 | 239.1167 | 8512.92 | 7.6 | 21.8 | 1.015 | 0.0132 | 1.3005 | 1.7 | 1.04 | 0.66 | 15 | NA | 16.5 | 54.5 | BMRL | 1.7 | 5.6 | 5.7 | 13 | BMRL | BMRL | BMRL | BMRL | 2.2 | BMRL | NA | NA | NA | 2.2 | 2.2 | Labor Rate + Fringe ($/work-hour) | 23.08
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 8812.9385 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 224 | 227 | 225.5 | 1.3304 |  | Total hardness | mg/L as CaCO3 | 224 | 227 | 225.5 | 1.3304 |  | F-10-19 | N | 1999-01-27 | 20:15 | 177.75 | 12656.3451 | 7.89 | 22.4 | 1.14 | 0.0162 | 1.4211 | 1.8 | 1.2 | 0.6 | 15 | NA | 16.5 | 34.3 | BMRL | 2.1 | 6.4 | 5.5 | 14 | BMRL | BMRL | BMRL | BMRL | 2.5 | 1.1 | NA | NA | NA | 2.5 | 3.6 | F-20-27 | N | 1999-01-31 | 20:45 | 274.25 | 9763.7205 | 7.76 | 22.5 | 1.098 | 0.015 | 1.3661 | 1.7 | 1.15 | 0.55 | 15 | NA | 16.5 | NA | BMRL | 1.8 | 5.7 | 5.3 | 12.8 | BMRL | BMRL | BMRL | BMRL | 2.2 | 1 | NA | NA | NA | 2.2 | 3.2 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 17625.877 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 172 | 188 | 180 | 8.8889 |  | Calcium hardness | mg/L as CaCO3 | 172 | 188 | 180 | 8.8889 |  | F-10-20 | N | 1999-01-28 | 9:15 | 190.75 | 13581.985 | 7.68 | 21.8 | 1.24 | 0.018 | 1.4516 | 1.9 | 1.24 | 0.66 | 15 | NA | 16.5 | 34.3 | BMRL | 2.7 | 7.2 | 5.2 | 15.1 | BMRL | BMRL | BMRL | BMRL | 2.8 | 1.5 | NA | NA | NA | 2.8 | 4.3 | F-20-32 | N | 1999-02-03 | 9:24 | 334.9 | 11922.9535 | 7.49 | 19.8 | 1.21 | 0.0156 | 1.2893 | 1.8 | 0.92 | 0.88 | 15 | NA | 16.5 | 65.5 | BMRL | 2.8 | 7.4 | 5.7 | 15.9 | BMRL | BMRL | BMRL | BMRL | 2.7 | 1.5 | NA | NA | NA | 2.7 | 4.2 | Electric Rate ($/kW-h) | 0.0437
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 22913.6401 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | F-10-22 | N | 1999-01-29 | 8:30 | 214 | 15237.4563 | 7.82 | 21.5 | 1.34 | 0.0186 | 1.3881 | 1.9 | 1.15 | 0.75 | 15 | NA | 16.5 | 36.6 | BMRL | 3 | 7.7 | 5.7 | 16.4 | BMRL | BMRL | BMRL | BMRL | 2.8 | 1.6 | NA | NA | NA | 2.8 | 4.4 | F-20-36 | N | 1999-02-06 | 9:15 | 406.75 | 14480.9237 | 7.8 | 22.1 | 1.32 | 0.0204 | 1.5455 | 1.8 | 1.05 | 0.75 | 15 | NA | 16.5 | 51.2 | BMRL | 3.2 | 8.6 | 6.8 | 18.6 | BMRL | BMRL | BMRL | BMRL | 2.9 | 1.5 | NA | NA | NA | 2.9 | 4.4 | Fuel Oil Rate ($/gal) | 0.49
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 113 | 120 | 116.5 | 6.0086 |  | Bromide | mg/L | 113 | 120 | 116.5 | 6.0086 |  | F-10-25 | N | 1999-01-30 | 20:28 | 249.9667 | 17798.3933 | 7.69 | 22.4 | 1.47 | 0.022 | 1.4966 | 2 | 1.14 | 0.86 | 15 | NA | 16.5 | 46.6 | 1.2 | 3.8 | 9 | 5.9 | 19.9 | BMRL | BMRL | BMRL | BMRL | 2.9 | 1.8 | NA | NA | NA | 2.9 | 4.7 | F-20-43 | N | 1999-02-13 | 10:25 | 575.9167 | 20503.5165 | 7.88 | 21.9 | 1.39 | 0.0204 | 1.4676 | 2 | 1.15 | 0.85 | 15 | NA | 16.5 | 43.3 | 1.6 | 4.8 | 10 | 5.9 | 22.3 | BMRL | 1.3 | BMRL | BMRL | 3.7 | 2.4 | NA | NA | NA | 5 | 7.4 | Natural Gas Rate ($/ft3) | 0.0033
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | F-10-30 | Y | 1999-02-02 | 9:00 | 310.5 | 22108.5523 | 7.81 | 22 | 1.65 | 0.024 | 1.4545 | 2 | 1.035 | 0.965 | 15 | NA | 16.5 | 48.85 | 1.5 | 4.65 | 10.15 | 6.3 | 22.6 | BMRL | 1.3 | BMRL | BMRL | 3.25 | 2.1 | NA | NA | NA | 4.55 | 6.65 | F-20-47 | Y | 1999-02-18 | 16:40 | 702.1667 | 24998.2101 | 7.795 | 23.2 | 1.54 | 0.02 | 1.2987 | 2 | 1.09 | 0.91 | 15 | NA | 16.5 | 52.75 | 1.9 | 5.45 | 11.65 | 6.35 | 25.35 | BMRL | 1.4 | BMRL | BMRL | 4 | 2.6 | NA | NA | NA | 5.4 | 8 | Current Process Water Rate ($/1000 gal) | 0.17
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.2781e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.0905 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  |  |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 11.6298 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-27 | 1999-02-18 | --- | --- | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-27 | 1999-02-18 | --- | --- |  |  |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | LWS Ashland WTP-Ozone |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 9.9649 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 10:30 | 20:05 | 19:00 | --- | --- | Sampling time | hh:mm | 10:30 | 20:05 | 19:00 | --- | --- |  |  |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | Other/GW |  |  | RSSCT flow rate, QSC (mL/min) | 15.7833 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 177.5833 | 704.5 | --- | --- | Operation time | hh.hh | 0 | 177.5833 | 704.5 | --- | --- |  |  |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Ozone |  |  | Estimated total influent volume required, VSCT (L) | 914.2532 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 12644.478 | 50162.5606 | --- | --- | Bed volumes | (20 minute) | 0 | 6322.239 | 25081.2803 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | ICR455 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.37 | 7.89 | 7.5 | 7.5867 | 3.567 | pH | --- | 7.37 | 7.89 | 7.5 | 7.5867 | 3.567 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NE3110926 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.16 | 0.105 | 0.135 | 0.13333 | 20.6534 | Turbidity | ntu | 0.16 | 0.11 | 0.14 | 0.13667 | 18.4142 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 9.8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 9.8 | 400 | 0.037 |  |  |  | Temperature | oC | 22.4 | 19.2 | 21 | 20.8667 | 7.6877 | Temperature | oC | 22.4 | 19.2 | 21 | 20.8667 | 7.6877
Historical Average Water Temperature (oC) | 13.4 |  |  | Estimated full-scale run time, tLCT (days) | 155.9401 | [5 empty] | Total organic carbon | mg/L | 2.11 | 2.04 | 2.04 | 2.0633 | 1.9587 | Total organic carbon | mg/L | 2.11 | 2.04 | 2.04 | 2.0633 | 1.9587 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.84266 | [5 empty] | UV254 | cm-1 | 0.035 | 0.034 | 0.033 | 0.034 | 2.9412 | UV254 | cm-1 | 0.035 | 0.034 | 0.033 | 0.034 | 2.9412 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 13.4086 | [5 empty] | SUVA | L/(mg*m) | 1.6588 | 1.6667 | 1.6176 | 1.6477 | 1.5973 | SUVA | L/(mg*m) | 1.6588 | 1.6667 | 1.6176 | 1.6477 | 1.5973 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.9951 | [5 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.3 | 2.3 | 2.3667 | 4.879 | SDS-Cl2 dose | mg/L | 2.5 | 2.3 | 2.3 | 2.3667 | 4.879 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 304.7511 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.16 | 1.19 | 1.04 | 1.13 | 7.0241 | SDS-Free Cl2 residual | mg/L | 1.16 | 1.19 | 1.04 | 1.13 | 7.0241 | F-10-30a | Primary | 1999-02-02 | 9:00 | 310.5 | 22108.5523 | 7.81 | 22 | 1.61 | 0.024 | 1.4907 | 2 | 0.91 | 1.09 | 15 | NA | 16.5 | 46.2 | 1.5 | 4.7 | 10 | 6.2 | 22.4 | BMRL | 1.2 | BMRL | BMRL | 3 | 2 | NA | NA | NA | 4.2 | 6.2 | F-20-47a | Primary | 1999-02-18 | 16:40 | 702.1667 | 24998.2101 | 7.79 | 23.2 | 1.53 | 0.02 | 1.3072 | 2 | 1.08 | 0.92 | 15 | NA | 16.5 | 58.3 | 2 | 5.6 | 11.6 | 5.8 | 25 | BMRL | 1.5 | BMRL | BMRL | 4 | 2.7 | NA | NA | NA | 5.5 | 8.2
|  |  |  | Mass GAC required, mSC (g) | 6.0781 | [5 empty] | SDS-Cl2 demand | mg/L | 1.34 | 1.11 | 1.26 | 1.2367 | 9.4417 | SDS-Cl2 demand | mg/L | 1.34 | 1.11 | 1.26 | 1.2367 | 9.4417 | F-10-30b | Duplicate | 1999-02-02 | 9:00 | 310.5 | 22108.5523 | 7.81 | 22 | 1.69 | 0.024 | 1.4201 | 2 | 1.16 | 0.84 | 15 | NA | 16.5 | 51.5 | 1.5 | 4.6 | 10.3 | 6.4 | 22.8 | BMRL | 1.4 | BMRL | BMRL | 3.5 | 2.2 | NA | NA | NA | 4.9 | 7.1 | F-20-47b | Duplicate | 1999-02-18 | 16:40 | 702.1667 | 24998.2101 | 7.8 | 23.2 | 1.55 | 0.02 | 1.2903 | 2 | 1.1 | 0.9 | 15 | NA | 16.5 | 47.2 | 1.8 | 5.3 | 11.7 | 6.9 | 25.7 | BMRL | 1.3 | BMRL | BMRL | 4 | 2.5 | NA | NA | NA | 5.3 | 7.8
[11 empty] | SDS-Chlorination temp. | oC | 15 | 15 | 15 | 15 | 0 | SDS-Chlorination temp. | oC | 15 | 15 | 15 | 15 | 0 |  | Average | --- | --- | --- | --- | 7.81 | 22 | 1.65 | 0.024 | 1.4554 | 2 | 1.035 | 0.965 | 15 | #DIV/0! | 16.5 | 48.85 | 1.5 | 4.65 | 10.15 | 6.3 | 22.6 | #DIV/0! | 1.3 | #DIV/0! | #DIV/0! | 3.25 | 2.1 | #DIV/0! | #DIV/0! | #DIV/0! | 4.55 | 6.65 |  | Average | --- | --- | --- | --- | 7.795 | 23.2 | 1.54 | 0.02 | 1.2988 | 2 | 1.09 | 0.91 | 15 | #DIV/0! | 16.5 | 52.75 | 1.9 | 5.45 | 11.65 | 6.35 | 25.35 | #DIV/0! | 1.4 | #DIV/0! | #DIV/0! | 4 | 2.6 | #DIV/0! | #DIV/0! | #DIV/0! | 5.4 | 8
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-Chlorination pH | --- | NA | NA | NA | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | 0 | 0 | 4.8485 | 0 | 4.8485 | 0 | 24.1546 | 25.9067 | 0 | #VALUE! | 0 | 10.8495 | 0 | 2.1505 | 2.9557 | 3.1746 | 1.7699 | #VALUE! | 15.3846 | #VALUE! | #VALUE! | 15.3846 | 9.5238 | #VALUE! | #VALUE! | #VALUE! | 15.3846 | 13.5338 |  | RPD | --- | --- | --- | --- | 0.12829 | 0 | 1.2987 | 0 | 1.2987 | 0 | 1.8349 | 2.1978 | 0 | #VALUE! | 0 | 21.0427 | 10.5263 | 5.5046 | 0.85837 | 17.3228 | 2.7613 | #VALUE! | 14.2857 | #VALUE! | #VALUE! | 0 | 7.6923 | #VALUE! | #VALUE! | #VALUE! | 3.7037 | 5
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 19.6 | [5 empty] | SDS-Incubation time | hours | 16.5 | 16.5 | 16.5 | 16.5 | 0 | SDS-Incubation time | hours | 16.5 | 16.5 | 16.5 | 16.5 | 0 |  | Primary |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Primary |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Estimated full-scale run time, tLCT (days) | 311.8801 | [5 empty] | SDS-TOX | mg Cl- /L | 75.3 | 80.3 | 84.5 | 80.0333 | 5.7548 | SDS-TOX | mg Cl- /L | 75.3 | 80.3 | 84.5 | 80.0333 | 5.7548 |  | Duplicate |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Duplicate |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.6853 | [5 empty] | SDS-CHCl3 | mg/L | 5.3 | 5.3 | 5.3 | 5.3 | 0 | SDS-CHCl3 | mg/L | 5.3 | 5.3 | 5.3 | 5.3 | 0 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
|  |  |  | Estimated RSSCT run time, tSCT (days) | 26.8172 | [5 empty] | SDS-BDCM | mg/L | 10.1 | 9.8 | 9.2 | 9.7 | 4.7243 | SDS-BDCM | mg/L | 10.1 | 9.8 | 9.2 | 9.7 | 4.7243 |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | RSSCT bed length, lSC (cm) | 27.9902 | [5 empty] | SDS-DBCM | mg/L | 13.6 | 13.8 | 12.8 | 13.4 | 3.9489 | SDS-DBCM | mg/L | 13.6 | 13.8 | 12.8 | 13.4 | 3.9489 |  | Primary |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Primary |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 609.5021 | [5 empty] | SDS-CHBr3 | mg/L | 4.7 | 5.4 | 5.2 | 5.1 | 7.0697 | SDS-CHBr3 | mg/L | 4.7 | 5.4 | 5.2 | 5.1 | 7.0697 |  | Duplicate |  |  | -868330.5 | -61827794.6499 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  | Duplicate |  |  | -868330.5 | -30913897.325 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Mass GAC required, mSC (g) | 12.1562 | [5 empty] | SDS-THM4 | mg/L | 33.7 | 34.3 | 32.5 | 33.5 | 2.7359 | SDS-THM4 | mg/L | 33.7 | 34.3 | 32.5 | 33.5 | 2.7359 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | 2.8 | 2.9 | 3 | 2.9 | 3.4483 | SDS-DCAA* | mg/L | 2.8 | 2.9 | 3 | 2.9 | 3.4483 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 1.2 | 1.3 | 1.3 | 1.2667 | 4.558 | SDS-TCAA* | mg/L | 1.2 | 1.3 | 1.3 | 1.2667 | 4.558 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 3.5 | 4 | 4.2 | 3.9 | 9.245 | SDS-DBAA* | mg/L | 3.5 | 4 | 4.2 | 3.9 | 9.245
[11 empty] | SDS-BCAA* | mg/L | 3.5 | 3.8 | 3.9 | 3.7333 | 5.5759 | SDS-BCAA* | mg/L | 3.5 | 3.8 | 3.9 | 3.7333 | 5.5759
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 7.5 | 8.2 | 8.5 | 8.0667 | 6.3615 | SDS-HAA5 | mg/L | 7.5 | 8.2 | 8.5 | 8.0667 | 6.3615
[11 empty] | SDS-HAA6 | mg/L | 11 | 12 | 12.4 | 11.8 | 6.1111 | SDS-HAA6 | mg/L | 11 | 12 | 12.4 | 11.8 | 6.1111
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on E5: Samp GAC sample as used for West Plant F-400 study
Note on H7: Resc was adjusted from 0.5 to match the actual ave. Qsc
Note on H8: Bruce Dvorak: Full-scale water temp was 11.3C for Jan. Note that Lincoln's water temp on the full scale varies through the year from a high around 14.3C to a low of 11.3C.
Note on H24: Bruce Dvorak: Actual ave. flow rate for 10 min column: 13.20 mL/min (0.9% diff. From model value). Actual ave. flow rate for 20 min. column = 13.25 mL (0.5% diff from model value).
Note on H28: Target EBCT was 10 min. Column was designed using a lit. value of GAC density. EBCT shown represents EBCT calcuated using experimentally measured density
Note on H37: Target EBCT was 20 min. Column was designed using a lit. value of GAC density. EBCT shown represents EBCT calcuated using experimentally measured density
Note on Q3: Reviewer M.H. (12/18/99): Regarding the measurement of instantaneous DBPs, per Consultant: "No instantaneous DBPs (w/o SDS) were determined."
Note on S10: Bruce Dvorak: Samples A
Note on S11: M.H. (8/18/99): Reviewer changed sample time from 9:15 to 10:30 so data would appear correctly on plots.
Note on S22: Same influent samples are reported for 10 & 20 min. columns since they were run at same time using same influent reservoir.
Note on S23: M.H. (8/18/99): Reviewer changed sample time from 9:15 to 10:30 so data would appear correctly on plots.
Note on T11: Bruce Dvorak: Samples A-2 10 and A2-20 are the same. Our mistake. Sorry
Note on Y3: Reviewer M.H. (12/18/99): Regarding the measurement of instantaneous DBPs, per Consultant: "No instantaneous DBPs (w/o SDS) were determined."
Note on AA11: M.H. (8/18/99): Reviewer changed sample time from 9:15 to 10:30 so data would appear correctly on plots.
Note on AA23: M.H. (8/18/99): Reviewer changed sample time from 9:15 to 10:30 so data would appear correctly on plots.
Note on AB10: Bruce Dvorak: Same sample as A2-10
Note on AG33: Participation in the treatment studies by the Lincoln Water System was voluntary. Full duplicates were not performed. Partially for cost savings and partially from a mistake in understanding of the study requirements.
Note on AU8: Bruce Dvorak: temp. maintained in an incubator that was maintained (and checked on a daily basis) during the entire treatment study. Inc. had +-0.5C accuracy.
Note on AV8: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on BP33: Participation in the treatment studies by the Lincoln Water System was voluntary. Full duplicates were not performed. Partially for cost savings and partially from a mistake in understanding of the study requirements.
Note on CD8: Bruce Dvorak: temp. maintained in an incubator that was maintained (and checked on a daily basis) during the entire treatment study. Inc. had +-0.5C accuracy.
Note on CE8: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE9: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE10: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE11: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE12: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE13: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE14: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE15: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE16: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE17: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE18: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CE19: Assumed to be near 7.9 given our lab data, near the dist. System pH.
Note on CZ6: Bruce Dvorak: Ave. value for past 2 years for Lincoln
Note on CZ7: Bruce Dvorak: Typical for Lincoln during past 2 years
Note on CZ8: Reviewer M.H. (2/2/00): Estimated by utility.
Note on CZ9: Reviewer M.H. (2/2/00): Per EPA Treatment Study Coordinator, utility is unable to estimate a value.
Note on CZ14: Reviewer M.H. (2/2/00): Average of $19.11 and $27.05 per hour.
Note on CZ15: Reviewer M.H. (2/2/00): Per EPA Treatment Study Coordinator, utility is unable to estimate a value.
Note on CZ17: Bruce Dvorak: June 1, 1999
Note on CZ19: Bruce Dvorak: June 1, 1999
Note on CZ20: Reviewer M.H. (2/2/00): Estimated by EPA Treatment Studies Coordinator after discussions with utility.