## ESNA 1st Quarter
FIELD-SET 1: 1st QUARTER SEBST RESULTS (FILE: sebst-2.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: SEBST Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 1-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 1-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 1-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 1-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.72 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.76 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | ESNA | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.10417 | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSP | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.99 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.93 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.94 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.93 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.93 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | ESNA-4040 |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-01-11 | 12:38 | 47.7 | 5.4 | 89 | 84 | 0 | 3.8 | 0.68 | 0.26 |  | 0.94 | 4.74 | 0.70023 | 0.7234 | 4.0426 | 11.52 | 15.2999 | 10 | 76.5 | 0.2 | 8.17 | 7.26 | 6.94 | 10 | NR | 1200 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.79 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.73 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.97 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.71 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.71 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200-300 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-01-12 | 11:00 | 70.1 | 5.6 | 90 | 85 | 0 | 3.9 | 0.66 | 0.3 |  | 0.96 | 4.86 | 0.72092 | 0.6875 | 4.0625 | 11.1812 | 14.7624 | 10 | 77.5 | 0.19048 | 6.62 | 7.47 | 6.92 | 10 | NR | 980 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-01-13 | 10:05 | 93.1 | 5.2 | 90 | 85 | 0 | 3.9 | 0.69 | 0.21 |  | 0.9 | 4.8 | 0.70898 | 0.76667 | 4.3333 | 11.6894 | 15.617 | 10 | 77.5 | 0.20151 | 9.13 | 8.62 | 9.07 | 10 | NR | 850 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Composite | Design flux, FW (gfd) | 12 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-01-14 | 11:25 | 118.35 | 5.5 | 92 | 86 | 0 | 3.82 | 0.72 | 0.29 |  | 1.01 | 4.83 | 0.71137 | 0.71287 | 3.7822 | 12.1976 | 16.1521 | 10 | 79 | 0.20446 | 5.44 | 7.65 | 6.69 | 10 | NR | 770 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate, Qp (gpm) | 0.70833 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-01-15 | 10:50 | 140.95 | 6.5 | 85 | 80 | 0 | 3.82 | 0.68 | 0.31 |  | 0.99 | 4.81 | 0.71137 | 0.68687 | 3.8586 | 11.52 | 14.8105 | 10 | 72.5 | 0.20428 | 5.06 | 5.48 | 5.98 | 10 | NR | 970 | [21 empty] | Sampling date | MM/DD/YY | 1998-01-18 | 1998-01-18 | 1998-01-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-01-25 | 1998-01-25 | 1998-01-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-01 | 1998-02-01 | 1998-02-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-09 | 1998-02-09 | 1998-02-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-09 | 1998-02-09 | 1998-02-09 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negavite | Feed flow rate, QF (gpm) | 0.94444 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-01-16 | 9:20 | 151.85 | 6.9 | 81 | 75 | 0 | 3.78 | 0.68 | 0.25 |  | 0.93 | 4.71 | 0.69546 | 0.73118 | 4.0645 | 11.52 | 14.6364 | 10 | 68 | 0.21524 | 5.83 | 5.01 | 6.48 | 20 | NR | 920 | [21 empty] | Sampling time | hh:mm | 12:30 | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:48 | 10:48 | 10:48 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:04 | 11:04 | 11:04 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:15 | 10:15 | 10:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:15 | 10:15 | 10:15 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.23611 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-01-17 | 12:35 | 155.5 | 6.3 | 90 | 88 | 0 | 3.8 | 0.74 | 0.27 |  | 1.01 | 4.81 | 0.7066 | 0.73267 | 3.7624 | 12.5365 | 16.2128 | 10 | 79 | 0.20523 | 6 | 6.14 | 6.02 | 10 | NR | 830 | [21 empty] | Operation time | hh.hh | 179 | 179 | 179 | --- | --- | --- | --- | --- | Operation time | hh.hh | 345.7 | 345.7 | 345.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 504.1 | 504.1 | 504.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 654.9 | 654.9 | 654.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 654.9 | 654.9 | 654.9 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-01-18 | 12:00 | 179 | 6.6 | 90 | 85 | 0 | 3.8 | 0.71 | 0.28 |  | 0.99 | 4.79 | 0.7058 | 0.71717 | 3.8384 | 12.0282 | 15.4182 | 10 | 77.5 | 0.19894 | 6.64 | 6.94 | 6.24 | 20 | NR | 940 | [21 empty] | pH | --- | 6.64 | 6.94 | 6.24 | --- | --- | --- | --- | --- | pH | --- | 6.2 | 5.99 | 6.53 | --- | --- | --- | --- | --- | pH | --- | 6.21 | 5.25 | 6.38 | --- | --- | --- | --- | --- | pH | --- | 6.45 | 6.67 | 7.1 | --- | --- | --- | --- | --- | pH | --- | NA | NA | 7.1 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 3.94" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 51.5 |  |  |  | 1998-01-19 | 9:35 | 200.6 | 5.8 | 95 | 90 | 0 | 3.8 | 0.71 | 0.22 |  | 0.93 | 4.73 | 0.69625 | 0.76344 | 4.086 | 12.0282 | 15.7872 | 10 | 82.5 | 0.19136 | 6.91 | 5.91 | 6.14 | 10 | NR | 1140 | [21 empty] | Temperature | oC | 6.6 | 6.6 | 6.6 | --- | --- | --- | --- | --- | Temperature | oC | 7 | 7 | 7 | --- | --- | --- | --- | --- | Temperature | oC | 7.7 | 7.7 | 7.7 | --- | --- | --- | --- | --- | Temperature | oC | 6.9 | 6.9 | 6.9 | --- | --- | --- | --- | --- | Temperature | oC | 6.9 | 6.9 | 6.9 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Design influent flow rate2, QI (gpm) | 4.8 | Barium (mg/L) | 0.016 |  |  |  | 1998-01-20 | 8:37 | 223.6 | 5.8 | 93 | 88 | 0 | 3.8 | 0.71 | 0.22 |  | 0.93 | 4.73 | 0.69625 | 0.76344 | 4.086 | 12.0282 | 15.7872 | 10 | 80.5 | 0.19611 | 6.65 | 6.27 | 6.32 | 20 | NR | 1120 | [21 empty] | Alkalinity | mg/L as CaCO3 | 8 | 19 | NA | 47.2857 | #VALUE! | 57.8947 | 44.3627 | 81.9668 | Alkalinity | mg/L as CaCO3 | 7 | 18 | NA | 51 | #VALUE! | 61.1111 | 47.7558 | 85.3421 | Alkalinity | mg/L as CaCO3 | 11 | 28 | NA | 81.8333 | #VALUE! | 60.7143 | 76.7425 | 85.6663 | Alkalinity | mg/L as CaCO3 | 9.5 | 19.3 | NA | 45.7963 | #VALUE! | 50.7772 | 43.1804 | 77.9993 | Alkalinity | mg/L as CaCO3 | 9.2 | 19.3 | NA | 46.6074 | #VALUE! | 52.3316 | 43.9115 | 79.0487 | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | 12 | Design recycle flow rate, QR (gpm) | 3.8556 | Strontium (mg/L) | 0.247 |  |  |  | 1998-01-21 | 9:30 | 248.6 | 6.4 | 105 | 100 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.69705 | 0.75269 | 4.086 | 11.8588 | 15.2912 | 10 | 92.5 | 0.16531 | 9.7 | 8.5 | 8.97 | 30 | NR | 1380 | [21 empty] | Total dissolved solids | mg/L | 17 | NR | 940 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 20 | NR | 1580 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 60 | NR | 1380 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 38.4 | NR | 1056 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 38.4 | NR | 1056 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Recycle ratio, r | 4.0824 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-01-22 | 8:54 | 271.8 | 6.5 | 105 | 99 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 15.4639 | 10 | 92 | 0.16809 | 7.32 | 6.25 | 6.71 | 20 | NR | 1380 | [21 empty] | Total hardness | mg/L as CaCO3 | 1.4 | 145 | NA | 514.2571 | #VALUE! | 99.0345 | 476.098 | 99.7059 | Total hardness | mg/L as CaCO3 | BMRL | 181 | NA | #VALUE! | #VALUE! | 100 | #VALUE! | 100 | Total hardness | mg/L as CaCO3 | BMRL | 182 | NA | #VALUE! | #VALUE! | 100 | #VALUE! | 100 | Total hardness | mg/L as CaCO3 | 4.33 | 184 | NA | 669.7744 | #VALUE! | 97.6467 | 621.8158 | 99.3037 | Total hardness | mg/L as CaCO3 | 4.22 | 184 | NA | 670.0719 | #VALUE! | 97.7065 | 622.0839 | 99.3216 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.14 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-01-23 | 9:10 | 296.1 | 6.6 | 104 | 99 | 0 | 3.8 | 0.73 | 0.21 |  | 0.94 | 4.74 | 0.69625 | 0.7766 | 4.0426 | 12.3671 | 15.8525 | 10 | 91.5 | 0.17325 | 7.74 | 7.18 | 8.03 | 40 | NR | 1210 | [21 empty] | Calcium hardness | mg/L as CaCO3 | 1.5 | 109 | NA | 385.4286 | #VALUE! | 98.6239 | 356.8624 | 99.5797 | Calcium hardness | mg/L as CaCO3 | BMRL | 131 | NA | #VALUE! | #VALUE! | 100 | #VALUE! | 100 | Calcium hardness | mg/L as CaCO3 | BMRL | 115.3 | NA | #VALUE! | #VALUE! | 100 | #VALUE! | 100 | Calcium hardness | mg/L as CaCO3 | 3.45 | 141 | NA | 512.8944 | #VALUE! | 97.5532 | 476.1788 | 99.2755 | Calcium hardness | mg/L as CaCO3 | 3.37 | 141 | NA | 513.1107 | #VALUE! | 97.6099 | 476.3737 | 99.2926 | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-01-24 | 11:55 | 322.9 | 5.9 | 104 | 99 | 0 | 3.8 | 0.74 | 0.23 |  | 0.97 | 4.77 | 0.70023 | 0.76289 | 3.9175 | 12.5365 | 16.4057 | 10 | 91.5 | 0.1793 | 6.74 | 5.61 | 6.45 | 10 | NR | 1080 | [21 empty] | Turbidity | ntu | 0.05 | 0.35 | NA | 1.1214 | #VALUE! | 85.7143 | 1.0417 | 95.2002 | Turbidity | ntu | 0.05 | 0.2 | NA | 0.65 | #VALUE! | 75 | 0.60576 | 91.7459 | Turbidity | ntu | 0 | 3.3 | NA | 13.75 | #VALUE! | 100 | 12.7618 | 100 | Turbidity | ntu | 0.05 | 2 | NA | 7.2722 | #VALUE! | 97.5 | 6.7517 | 99.2594 | Turbidity | ntu | 0.05 | 2 | NA | 7.2722 | #VALUE! | 97.5 | 6.7517 | 99.2594 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-01-25 | 10:48 | 345.7 | 7 | 104 | 100 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.69705 | 0.75269 | 4.086 | 11.8588 | 15.0224 | 10 | 92 | 0.16329 | 6.2 | 5.99 | 6.53 | 20 | NR | 1580 | [21 empty] | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-01-26 | 8:36 | 367.6 | 6.8 | 107 | 100 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 15.3274 | 10 | 93.5 | 0.16393 | 7.26 | 5.97 | 6.73 | 10 | NR | 1180 | [21 empty] | Total organic carbon | mg/L | 0.07 | 2.04 | NA | 7.1057 | #VALUE! | 96.5686 | 6.5822 | 98.9365 | Total organic carbon | mg/L | 0.32 | 1.94 | NA | 6.8 | #VALUE! | 83.5052 | 6.3222 | 94.9385 | Total organic carbon | mg/L | 0.33 | 2.1 | NA | 7.705 | #VALUE! | 84.2857 | 7.1749 | 95.4007 | Total organic carbon | mg/L | 0.4 | 1.82 | NA | 5.6593 | #VALUE! | 78.022 | 5.2802 | 92.4246 | Total organic carbon | mg/L | 0.46 | 1.99 | NA | 6.1267 | #VALUE! | 76.8844 | 5.7183 | 91.9556
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 14 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-01-27 | 12:04 | 385.9 | 7.5 | 110 | 104 | 0 | 3.8 | 0.74 | 0.23 |  | 0.97 | 4.77 | 0.70023 | 0.76289 | 3.9175 | 12.5365 | 15.6478 | 10 | 97 | 0.16132 | 8.01 | 7.4 | 7.48 | 70 | NR | 1950 | [21 empty] | UV254 | cm-1 | 0.03 | 0.046 | NA | 0.087143 | #VALUE! | 34.7826 | 0.082891 | 63.808 | UV254 | cm-1 | 0.003 | 0.033 | NA | 0.123 | #VALUE! | 90.9091 | 0.11415 | 97.3719 | UV254 | cm-1 | 0.017 | 0.047 | NA | 0.142 | #VALUE! | 63.8298 | 0.13302 | 87.2196 | UV254 | cm-1 | 0.022 | 0.048 | NA | 0.1183 | #VALUE! | 54.1667 | 0.11136 | 80.2436 | UV254 | cm-1 | 0.022 | 0.048 | NA | 0.1183 | #VALUE! | 54.1667 | 0.11136 | 80.2436
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.001 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-01-28 | 12:45 | 410.5 | 7.3 | 110 | 103 | 0 | 3.75 | 0.72 | 0.32 |  | 1.04 | 4.79 | 0.70501 | 0.69231 | 3.6058 | 12.1976 | 15.3152 | 10 | 96.5 | 0.15871 | 9.28 | 8.2 | 8.84 | 10 | NR | 1540 | [21 empty] | SUVA | L/(mg*m) | 42.8571 | 2.2549 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 0.9375 | 1.701 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.1515 | 2.2381 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.5 | 2.6374 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.7826 | 2.4121 | NA | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.85 | [5 empty] | 1998-01-29 | 9:00 | 430.7 | 7 | 106 | 100 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 15.4516 | 10 | 93 | 0.16615 | 10.09 | 8.64 | 9.37 | 20 | NR | 1050 | [21 empty] | Bromide | mg/L | BMRL | 45 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 60 | 110 | --- | 268.3333 | --- | 45.4545 | 253.3602 | 76.3183 | Bromide | mg/L | BMRL | 90 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 90 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | 950 | Feed TDS, TDSF (mg/L) | 1000 | [5 empty] | 1998-01-30 | 13:00 | 458.3 | 7.2 | 106 | 100 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 15.1472 | 10 | 93 | 0.16287 | 8.88 | 7.9 | 8.4 | 40 | NR | 1070 | [21 empty] | SDS-Cl2 dose | mg/L | 1 | 2.4 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 1.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.6 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | 2872.9916 | [5 empty] | 1998-01-31 | 12:00 | 482.3 | 7 | 107 | 101 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.69705 | 0.75269 | 4.086 | 11.8588 | 15.0224 | 10 | 94 | 0.15981 | 8.02 | 7.48 | 7.69 | 60 | NR | 1200 | [21 empty] | SDS-Free Cl2 residual | mg/L | 0.9 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.6 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.6 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | 375.6695 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-02-01 | 11:04 | 504.1 | 7.7 | 115 | 110 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 14.925 | 10 | 102.5 | 0.14561 | 6.55 | 6.17 | 6.38 | 60 | NR | 1380 | [21 empty] | SDS-Cl2 demand | mg/L | 0.1 | 1.9 | --- | 6.5286 | --- | 94.7368 | 6.0503 | 98.3472 | SDS-Cl2 demand | mg/L | 0.7 | 1.7 | --- | 4.7 | --- | 58.8235 | 4.4051 | 84.1092 | SDS-Cl2 demand | mg/L | 0.4 | 1.15 | --- | 3.525 | --- | 65.2174 | 3.3004 | 87.8803 | SDS-Cl2 demand | mg/L | 0.7 | 1.9 | --- | 5.1444 | --- | 63.1579 | 4.8241 | 85.4896 | SDS-Cl2 demand | mg/L | 0.7 | 1.9 | --- | 5.1444 | --- | 63.1579 | 4.8241 | 85.4896
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | 0.6-1.0 | Influent TDS, TDSI (mg/L) | 2504.4631 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-02-02 | 10:08 | 527.7 | 7.3 | 115 | 110 | 0 | 3.8 | 0.76 | 0.23 |  | 0.99 | 4.79 | 0.70182 | 0.76768 | 3.8384 | 12.8753 | 16.166 | 10 | 102.5 | 0.15772 | 6.99 | 7.02 | 7.15 | 60 | NR | 1200 | [21 empty] | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | Dependant upon array and feedwater | Osmotic pressure gradient, Dp (psi) | 23.1306 | [5 empty] | 1998-02-03 | 12:26 | 544.1 | 6.4 | 100 | 95 | 0 | 3.8 | 0.74 | 0.23 |  | 0.97 | 4.77 | 0.70023 | 0.76289 | 3.9175 | 12.5365 | 16.165 | 10 | 87.5 | 0.18474 | 7.52 | 7.81 | 7.56 | 50 | NR | 990 | [21 empty] | SDS-Chlorination pH | --- | 7.14 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.4 | 7.32 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.54 | 7.38 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.85 | 7.87 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.85 | 7.87 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 1998-02-04 | 12:00 | 567.5 | 7 | 116 | 110 | 0 | 3.92 | 0.7 | 0.4 |  | 1.1 | 5.02 | 0.7432 | 0.63636 | 3.5636 | 11.8588 | 15.0224 | 10 | 103 | 0.14585 | 6.21 | 5.25 | 6.5 | 20 | NR | 1290 | [21 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 1998-02-07 | 13:00 | 611.8 | 6.2 | 105 | 100 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 15.6016 | 10 | 92.5 | 0.16867 | 7.08 | 6.68 | 7.16 | 40 | NR | 860 | [21 empty] | SDS-TOX | mg Cl- /L | BMRL | 47 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 68 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 79.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 63 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 50 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | 85-95%; 500 mg/L NaCl | Estimated system pressure losses, DPloss (psi) | 4 | [5 empty] | 1998-02-08 | 12:21 | 633 | 6.5 | 129 | 124 | 0 | 3.8 | 0.74 | 0.23 | X | 0.97 | 4.77 | 0.70023 | 0.76289 | 3.9175 | 12.5365 | 16.1173 | 10 | 116.5 | 0.13835 | 7.95 | 7.98 | 7.95 | 41 | NR | 947 | [21 empty] | SDS-CHCl3 | mg/L | BMRL | 5.89 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 1.35 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 8.31 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.09 | 7.83 | --- | 26.053 | --- | 86.0792 | 24.2539 | 95.5059 | SDS-CHCl3 | mg/L | 1.09 | 10.28 | --- | 35.127 | --- | 89.3969 | 32.674 | 96.664
|  | (e.g., solute type and concentration) |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-02-19 | 16:28 | 698.2 | 7.3 | 91 | 86 | 0 | 3.8 | 0.73 | 0.23 |  | 0.96 | 4.76 | 0.69944 | 0.76042 | 3.9583 | 12.3671 | 15.5279 | 10 | 78.5 | 0.19781 | 6.56 | 6.52 | 6.96 | 29 | NR | 1005 | [21 empty] | SDS-BDCM | mg/L | BMRL | 2.77 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 6.95 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 8.34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 8.99 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 9.45 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | 85-95% | Required influent pressure, PI (psi) | 142.3234 | [5 empty] | 1998-02-20 | 8:15 | 706 | 7.5 | 91 | 86 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.69705 | 0.75269 | 4.086 | 11.8588 | 14.802 | 10 | 78.5 | 0.18856 | 8.5 | 7.12 | 7.53 | 35 | NR | 1004 | [21 empty] | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 5.79 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 5.78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 1.5 | 8.27 | --- | 26.5741 | --- | 81.8622 | 24.767 | 93.9435 | SDS-DBCM | mg/L | 1.5 | 8.71 | --- | 28.2037 | --- | 82.7784 | 26.2792 | 94.2921
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-02-21 | 12:29 | 734.2 | 7.8 | 92 | 87 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 14.8809 | 10 | 79.5 | 0.18718 | 6.34 | 5.75 | 6.91 | 29 | NR | 1011 | [21 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | 1.16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | 1.46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 6.5-7.0 | [7 empty] | 1998-02-22 | 11:59 | 757.7 | 7.8 | 92 | 87 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.69705 | 0.75269 | 4.086 | 11.8588 | 14.6713 | 10 | 79.5 | 0.18455 | 6.37 | 5.75 | 6.87 | 31 | NR | 998 | [21 empty] | SDS-THM4 | mg/L | 0 | 8.66 | --- | 30.9286 | --- | 100 | 28.6273 | 100 | SDS-THM4 | mg/L | 0 | 14.09 | --- | 56.36 | --- | 100 | 52.2045 | 100 | SDS-THM4 | mg/L | 0 | 22.43 | --- | 93.4583 | --- | 100 | 86.7414 | 100 | SDS-THM4 | mg/L | 2.59 | 26.25 | --- | 90.2196 | --- | 90.1333 | 83.9042 | 96.9131 | SDS-THM4 | mg/L | 2.59 | 29.9 | --- | 103.7381 | --- | 91.3378 | 96.4484 | 97.3146
|  | Acceptable range of operating pressures | less than or equal to 400 psi | [7 empty] | 1998-02-23 | 8:24 | 778.1 | 8 | 92 | 87 | 0 | 3.8 | 0.73 | 0.23 |  | 0.96 | 4.76 | 0.69944 | 0.76042 | 3.9583 | 12.3671 | 15.2099 | 10 | 79.5 | 0.19132 | 6.99 | 6.66 | 7.38 | 42 | NR | 1069 | [21 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3.0-10.0 | [7 empty] | 1998-02-24 | 8:23 | 802.1 | 8.4 | 92 | 87 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.69705 | 0.75269 | 4.086 | 11.8588 | 14.4134 | 10 | 79.5 | 0.1813 | 6.4 | 5.81 | 6.91 | 39 | NR | 1030 | [21 empty] | SDS-DCAA* | mg/L | BMRL | 5.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 5.25 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 4.55 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 12 psi max | [7 empty] | 1998-02-25 | 8:52 | 826.8 | 9.5 | 92 | 87 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.69784 | 0.75532 | 4.0426 | 12.0282 | 14.1516 | 10 | 79.5 | 0.17801 | 6.32 | 5.68 | 6.8 | 36 | NR | 1030 | [21 empty] | SDS-TCAA* | mg/L | BMRL | 1.35 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 4.17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 5.12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 1.98 | 6.49 | --- | 18.6837 | --- | 69.4915 | 17.4799 | 88.6727 | SDS-TCAA* | mg/L | 2.12 | 6.39 | --- | 17.9348 | --- | 66.8232 | 16.795 | 87.3772
|  | Maximum permissible SDI | 4 | [55 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | 5.03 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | 4.84 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [55 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 0.84 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.02 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 3.38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 3.11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0.0 mg/L | [55 empty] | SDS-BCAA* | mg/L | BMRL | 1.94 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.71 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.82 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 1.11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | 100 | SDS-BCAA* | mg/L | BMRL | 5.49 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [56 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | 1.24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | 1.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [56 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.58 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 2.47 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 4.76 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5 | mg/L | 0 | 6.58 | --- | 23.5 | --- | 100 | 21.7515 | 100 | SDS-HAA5 | mg/L | 0 | 10.26 | --- | 41.04 | --- | 100 | 38.0141 | 100 | SDS-HAA5 | mg/L | 0 | 10.69 | --- | 44.5417 | --- | 100 | 41.3404 | 100 | SDS-HAA5 | mg/L | 1.98 | 14.9 | --- | 49.8319 | --- | 86.7114 | 46.3832 | 95.7312 | SDS-HAA5 | mg/L | 2.12 | 14.34 | --- | 47.3793 | --- | 85.2162 | 44.1174 | 95.1946
[59 empty] | SDS-HAA6 | mg/L | 0 | 8.52 | --- | 30.4286 | --- | 100 | 28.1645 | 100 | SDS-HAA6 | mg/L | 0 | 12.97 | --- | 51.88 | --- | 100 | 48.0548 | 100 | SDS-HAA6 | mg/L | 0 | 13.51 | --- | 56.2917 | --- | 100 | 52.2459 | 100 | SDS-HAA6 | mg/L | 1.98 | 16.01 | --- | 53.943 | --- | 87.6327 | 50.198 | 96.0556 | SDS-HAA6 | mg/L | 2.12 | 19.83 | --- | 67.7126 | --- | 89.3091 | 62.9853 | 96.6341
[59 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[59 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[59 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[60 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[60 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[59 empty] | Qp/QT (THM4), % | -731.4088 | -315.7044 |  | Qp/QT (HAA5), % | -720.6687 | -310.3343 |  |  |  | Qp/QT (THM4), % | -411.0007 | -155.5004 |  | Qp/QT (HAA5), % | -426.3158 | -163.1579 |  |  |  | Qp/QT (THM4), % | -220.9987 | -60.4993 |  | Qp/QT (HAA5), % | -405.145 | -152.5725 |  |  |  | Qp/QT (THM4), % | -193.3643 | -41.2088 |  | Qp/QT (HAA5), % | -302.6316 | -93.6533 |  |  |  | Qp/QT (THM4), % | -154.156 | -22.3361 |  | Qp/QT (HAA5), % | -324.5499 | -103.6007
[59 empty] | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA
[59 empty] | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA
[59 empty] | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA
[59 empty] | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA
[59 empty] | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA
[59 empty] | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA
[59 empty] | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA
[59 empty] | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA
[59 empty] | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA
[59 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA
[59 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[59 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[59 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[59 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[59 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[59 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[59 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[59 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[59 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[59 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on AA13: Carollo Engineers: Low pH alarm shut off pilot plant.
Note on AA23: Carollo Engineers: Low pH alarm shut off pilot plant.
Note on AA26: Carollo Engineers: Replaced Cartridge filter.
Note on AA30: Carollo Engineers: Low pH alarm shut off pilot plant.
Note on AA31: Carollo Engineers: Blown fuse shut down pilot plant.
Note on AA33: Carollo Engineers: Low pH alarm shut off pilot plant.
Note on AI5: Carollo Engineers: Estimated Osmotic Pressure. Based on average permeate TDS concentration of 30 mg/L and estimated bulk concentration of 1100 mg/L (which was measured but not reported.
Note on AM6: Carollo Engineers: pH was controlled by a metering pump manually. Daily variations in alkalinity caused fluctuations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of erratic permeate TDS concentrations.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BP23: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on BQ25: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on BQ37: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on BQ47: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CB25: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on CB37: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on CB47: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CL25: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on CM25: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on CM37: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on CM47: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CX37: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on CX47: Carollo Engineers: THM and HAA Concentrations are noted to increase in both the feed and permeate concentrations over the four weeks of testing. It is speculated that this may be due to variations in the quality of NOM present in the NF feed waters. As this experiment proceeds from January to late February, the feed water temperature changes by approximately 5 degrees centigrate which may also indicate that some run off may be occuring. NF feed water TOC is the result of lime softening pretreatment which may not be selective to the "type" of TOC it is treating. In a paper titled "Chlorination of Humic Materials: By-product Formation and Chemical Interpretations", Reckhow, Singer and Malcolm (1990) have shown why SUVA may not be used as an idicator for THMFP since the functionalization of humic TOC in water may impact THM formation potential and is not always related to the carbon carbon double or triple bonds which are measured as UV254. In summary the increase in THM and HAA formation may rather be more a relation to the quality of TOC present as run off in the Missouri River begins.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.

## ESNA 2nd Quarter
FIELD-SET 2: 2nd QUARTER SEBST RESULTS (FILE: sebst-2.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: SEBST Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 2-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 2-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 2-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 2-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Osmonics | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | MS | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.74409 | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.99 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.07 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.2 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.17 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.17 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | S4040 |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-02-27 | 9:23 | 873 | 11.3 | 192 | 188 | 0 | 3.8 | 0.71 | 0.24 |  | 0.95 | 4.75 | 0.29673 | 0.74737 | 4 | 12.0282 | 13.4184 | 10 | 180 | 0.074546 | 6.18 | 5.75 | 6.89 | 3.84 | NR | 1146 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.79 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.87 | [8 empty] | Influent flow rate during sample collection (gpm) | 5 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.97 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.97 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | < 300 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-02-28 | 12:07 | 899.7 | 10.8 | 191 | 187 | 0 | 3.8 | 0.73 | 0.24 |  | 0.97 | 4.77 | 0.29741 | 0.75258 | 3.9175 | 12.3671 | 14.0018 | 10 | 179 | 0.078222 | 6.25 | 5.83 | 6.93 | 4.48 | NR | 890 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polysulfone with a Polyamide active layer | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 2/29/98 | 12:02 | 923.6 | 10.6 | 196 | 192 | 0 | 3.8 | 0.76 | 0.24 |  | 1 | 4.8 | 0.29842 | 0.76 | 3.8 | 12.8753 | 14.6636 | 10 | 184 | 0.079694 | 6.1 | 5.86 | 7.04 | 5.12 | NR | 1203 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin film composite | Design flux, FW (gfd) | 12 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-03-02 | 11:10 | 946.7 | 9.8 | 197 | 192 | 0 | 3.8 | 0.7 | 0.31 |  | 1.01 | 4.81 | 0.30112 | 0.69307 | 3.7624 | 11.8588 | 13.8291 | 10 | 184.5 | 0.074955 | 6.09 | 5.84 | 6.85 | 1.28 | NR | 858 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate, Qp (gpm) | 0.70833 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-03-03 | 11:10 | 970.7 | 8.9 | 197 | 192 | 0 | 3.8 | 0.71 | 0.25 |  | 0.96 | 4.76 | 0.29741 | 0.73958 | 3.9583 | 12.0282 | 14.4049 | 10 | 184.5 | 0.078075 | 7.02 | 6.43 | 7.13 | 1.28 | NR | 864 | [21 empty] | Sampling date | MM/DD/YY | 1998-03-06 | 1998-03-06 | 1998-03-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-11 | 1998-03-11 | 1998-03-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-29 | 1998-03-29 | 1998-03-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-02 | 1998-04-02 | 1998-04-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-02 | 1998-04-02 | 1998-04-02 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Neutral | Feed flow rate, QF (gpm) | 0.94444 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-03-04 | 10:20 | 993.8 | 9.1 | 197 | 192 | 0 | 3.8 | 0.68 | 0.25 |  | 0.93 | 4.73 | 0.29639 | 0.73118 | 4.086 | 11.52 | 13.7149 | 10 | 184.5 | 0.074335 | 6.55 | 6.66 | 7.3 | 0.64 | NR | 877 | [21 empty] | Sampling time | hh:mm | 8:58 | 8:58 | 8:58 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:31 | 9:31 | 9:31 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:06 | 11:06 | 11:06 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:08 | 9:08 | 9:08 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:08 | 9:08 | 9:08 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.23611 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-03-06 | 8:58 | 1017.3 | 7.7 | 200 | 205 | 0 | 3.8 | 0.74 | 0.25 |  | 0.99 | 4.79 | 0.29842 | 0.74747 | 3.8384 | 12.5365 | 15.5556 | 10 | 192.5 | 0.080808 | 7.4 | 7.62 | 6.81 | 2.56 | NR | 768 | [21 empty] | Operation time | hh.hh | 1044.5 | 1044.5 | 1044.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1136.2 | 1136.2 | 1136.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1472 | 1472 | 1472 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1566 | 1566 | 1566 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1566 | 1566 | 1566 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | NA | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-03-07 | 12:11 | 1044.5 | 7.9 | 215 | 210 | 0 | 3.8 | 0.79 | 0.32 |  | 1.11 | 4.91 | 0.30483 | 0.71171 | 3.4234 | 13.3835 | 16.5088 | 10 | 202.5 | 0.081525 | 6.23 | 6.69 | 6.75 | 3.2 | NR | 896 | [21 empty] | pH | --- | 7.4 | 7.62 | 6.81 | --- | --- | --- | --- | --- | pH | --- | 7.1 | 7.02 | 6.71 | --- | --- | --- | --- | --- | pH | --- | 9.14 | 8.28 | 8.77 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 5.93 | 6.73 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 5.93 | 6.73 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 3.9" x 40" | Maximum influent flow rate, QI, max (gpm) | 15 | Calcium (mg/L) | 51.5 |  |  |  | 1998-03-08 | 12:04 | 1068.4 | 7.9 | 215 | 210 | 0 | 3.8 | 0.74 | 0.29 |  | 1.03 | 4.83 | 0.30112 | 0.71845 | 3.6893 | 12.5365 | 15.4639 | 10 | 202.5 | 0.076365 | 5.58 | 5.87 | 6.41 | 3.84 | NR | 992 | [21 empty] | Temperature | oC | 7.7 | 7.7 | 7.7 | --- | --- | --- | --- | --- | Temperature | oC | 7 | 7 | 7 | --- | --- | --- | --- | --- | Temperature | oC | 15.7 | 15.7 | 15.7 | --- | --- | --- | --- | --- | Temperature | oC | 14.1 | 14.1 | 14.1 | --- | --- | --- | --- | --- | Temperature | oC | 14.1 | 14.1 | 14.1 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Design influent flow rate2, QI (gpm) | 4.8 | Barium (mg/L) | 0.016 |  |  |  | 1998-03-09 | 10:25 | 1090.7 | 7.1 | 231 | 228 | 0 | 3.8 | 0.76 | 0.29 |  | 1.05 | 4.85 | 0.30179 | 0.72381 | 3.619 | 12.8753 | 16.2619 | 10 | 219.5 | 0.074086 | 5.76 | 5.85 | 6.54 | 3.84 | NR | 986 | [21 empty] | Alkalinity | mg/L as CaCO3 | BMRL | 21 | 104 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 5 | 35 | 137 | 105 | 23.3577 | 85.7143 | 96.7606 | 94.8326 | Alkalinity | mg/L as CaCO3 | BMRL | 34 | 122 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | 22 | Design recycle flow rate, QR (gpm) | 3.8556 | Strontium (mg/L) | 0.247 |  |  |  | 1998-03-10 | 9:33 | 1112.3 | 5.9 | 225 | 221 | 0 | 3.8 | 0.78 | 0.29 |  | 1.07 | 4.87 | 0.30247 | 0.72897 | 3.5514 | 13.2141 | 17.2925 | 10 | 213 | 0.081185 | 6.03 | 6.29 | 6.71 | 2.56 | NR | 966 | [21 empty] | Total dissolved solids | mg/L | 2.56 | NR | 760 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 3.2 | NR | 979 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 7.04 | NR | 819 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 3.84 | NR | 512 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 3.84 | NR | 512 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 220 | Recycle ratio, r | 4.0824 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-03-11 | 9:31 | 1136.2 | 7 | 228 | 224 | 0 | 3.8 | 0.78 | 0.29 |  | 1.07 | 4.87 | 0.30247 | 0.72897 | 3.5514 | 13.2141 | 16.7392 | 10 | 216 | 0.077497 | 7.1 | 7.02 | 6.71 | 3.2 | NR | 979 | [21 empty] | Total hardness | mg/L as CaCO3 | BMRL | 193 | 504 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 6.94 | 321 | 629 | 1170.1252 | -86.0294 | 97.838 | 1076.8435 | 99.3555 | Total hardness | mg/L as CaCO3 | BMRL | 186 | 424 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | BMRL | 200 | 447 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | BMRL | 204 | 445 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 1 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-03-12 | 9:52 | 1160.6 | 6.6 | 229 | 225 | 0 | 3.8 | 0.76 | 0.29 |  | 1.05 | 4.85 | 0.30179 | 0.72381 | 3.619 | 12.8753 | 16.504 | 10 | 217 | 0.076055 | 8.2 | 7.76 | 7.76 | 3.84 | NR | 922 | [21 empty] | Calcium hardness | mg/L as CaCO3 | BMRL | 142 | 357 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 4.02 | 257 | 537 | 940.983 | -75.2296 | 98.4358 | 865.8432 | 99.5357 | Calcium hardness | mg/L as CaCO3 | BMRL | 137 | 317 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 171 | 385 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 176 | 380 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-03-13 | 9:10 | 1183.7 | 7.3 | 221 | 216 | 0 | 3.8 | 0.76 | 0.32 |  | 1.08 | 4.88 | 0.30382 | 0.7037 | 3.5185 | 12.8753 | 16.166 | 10 | 208.5 | 0.077535 | 7 | 6.39 | 6.51 | 2.56 | NR | 896 | [21 empty] | Turbidity | ntu | 0.1 | 0.9 | NA | 3.3 | #VALUE! | 88.8889 | 3.052 | 96.7234 | Turbidity | ntu | 0.05 | 1.2 | NA | 4.3093 | #VALUE! | 95.8333 | 3.9677 | 98.7398 | Turbidity | ntu | 0.03 | 1.38 | NA | 4.53 | #VALUE! | 97.8261 | 4.152 | 99.2775 | Turbidity | ntu | 0.05 | 1.9 | NA | 6.2167 | #VALUE! | 97.3684 | 5.7086 | 99.1241 | Turbidity | ntu | 0.05 | 1.9 | NA | 6.2167 | #VALUE! | 97.3684 | 5.7086 | 99.1241 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 15 | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-03-14 | 11:12 | 1210.2 | 8.1 | 222 | 217 | 0 | 3.8 | 0.7 | 0.32 |  | 1.02 | 4.82 | 0.30179 | 0.68627 | 3.7255 | 11.8588 | 14.5418 | 10 | 209.5 | 0.069412 | 7.1 | 6.74 | 6.67 | 2.56 | NR | 755 | [21 empty] | Ammonia | mg NH3-N / L | 0.039 | 0.068 | 0.193 | 0.155 | 19.6891 | 42.6471 | 0.14601 | 73.2894 | Ammonia | mg NH3-N / L | 0.044 | 0.123 | 0.097 | 0.33659 | -247.0027 | 64.2276 | 0.31313 | 85.9482 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.038 | 0.125 | 0.204 | 0.328 | -60.7843 | 69.6 | 0.30411 | 87.5043 | Ammonia | mg NH3-N / L | 0.029 | 0.145 | 0.2 | 0.41567 | -107.8333 | 80 | 0.38381 | 92.4441
|  | Minimum flow rate to the element, QI, min (gpm) | NA | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-03-15 | 11:52 | 1234.4 | 8 | 223 | 218 | 0 | 3.8 | 0.67 | 0.3 |  | 0.97 | 4.77 | 0.29943 | 0.69072 | 3.9175 | 11.3506 | 13.9598 | 10 | 210.5 | 0.066317 | 6.03 | 5.49 | 6.36 | 4.48 | NR | 1062 | [21 empty] | Total organic carbon | mg/L | 0.26 | 2.16 | 6.35 | 7.86 | -23.7795 | 87.963 | 7.271 | 96.4241 | Total organic carbon | mg/L | 0.45 | 2.22 | 3.12 | 7.0056 | -124.537 | 79.7297 | 6.4798 | 93.0554 | Total organic carbon | mg/L | 0.52 | 2.48 | 28.8 | 7.0533 | 75.5093 | 79.0323 | 6.5045 | 92.0056 | Total organic carbon | mg/L | 0.44 | 2.83 | 6.08 | 8.4067 | -38.2675 | 84.4523 | 7.7503 | 94.3228 | Total organic carbon | mg/L | 0.35 | 3.02 | 6.1 | 9.25 | -51.6393 | 88.4106 | 8.5167 | 95.8904
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 16.5 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-03-16 | 9:08 | 1255.6 | 8.7 | 221 | 216 | 0 | 3.8 | 0.68 | 0.25 |  | 0.93 | 4.73 | 0.29639 | 0.73118 | 4.086 | 11.52 | 13.878 | 10 | 208.5 | 0.066561 | 5.92 | 5.82 | 6.41 | 3.84 | NR | 1126 | [21 empty] | UV254 | cm-1 | 0.018 | 0.049 | 0.121 | 0.142 | -17.3554 | 63.2653 | 0.13239 | 86.4037 | UV254 | cm-1 | 0.023 | 0.047 | 0.065 | 0.11189 | -72.1368 | 51.0638 | 0.10476 | 78.0451 | UV254 | cm-1 | 0.016 | 0.053 | 0.133 | 0.13933 | -4.7619 | 69.8113 | 0.12897 | 87.5943 | UV254 | cm-1 | 0.016 | 0.071 | 0.137 | 0.19933 | -45.4988 | 77.4648 | 0.18423 | 91.3151 | UV254 | cm-1 | 0.015 | 0.069 | 0.141 | 0.195 | -38.2979 | 78.2609 | 0.18017 | 91.6745
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.002 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-03-17 | 10:45 | 1281.2 | 8.3 | 222 | 217 | 0 | 3.8 | 0.69 | 0.3 |  | 0.99 | 4.79 | 0.30011 | 0.69697 | 3.8384 | 11.6894 | 14.2496 | 10 | 209.5 | 0.068017 | 6.32 | 6.64 | 6.89 | 3.2 | NR | 928 | [21 empty] | SUVA | L/(mg*m) | 6.9231 | 2.2685 | 1.9055 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.1111 | 2.1171 | 2.0833 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.0769 | 2.1371 | 0.46181 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.6364 | 2.5088 | 2.2533 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.2857 | 2.2848 | 2.3115 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | NA | Manufacturer reported TDS rejection, RejTDS (decimal) | NA | [5 empty] | 1998-03-18 | 8:25 | 1303 | 8.6 | 234 | 229 | 0 | 3.8 | 0.84 | 0.28 |  | 1.12 | 4.92 | 0.30382 | 0.75 | 3.3929 | 14.2306 | 17.1942 | 10 | 221.5 | 0.077626 | 6.85 | 7.01 | 6.85 | 0.64 | NR | 1018 | [21 empty] | Bromide | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 60 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 50 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | NA | Feed TDS, TDSF (mg/L) | NA | [5 empty] | 1998-03-19 | 12:05 | 1330.6 | 9 | 234 | 229 | 0 | 3.8 | 0.74 | 0.21 |  | 0.95 | 4.75 | 0.29572 | 0.77895 | 4 | 12.5365 | 14.9692 | 10 | 221.5 | 0.067581 | 7.18 | 6.35 | 6.66 | 1.29 | NR | 1171 | [21 empty] | SDS-Cl2 dose | mg/L | 1 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 3 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | #VALUE! | [5 empty] | 1998-03-20 | 12:35 | 1355.1 | 9.5 | 234 | 229 | 0 | 3.8 | 0.73 | 0.19 |  | 0.92 | 4.72 | 0.29403 | 0.79348 | 4.1304 | 12.3671 | 14.5503 | 10 | 221.5 | 0.06569 | 6.39 | 6.37 | 6.75 | 1.28 | NR | 1075 | [21 empty] | SDS-Free Cl2 residual | mg/L | 0.8 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.6 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.6 | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.7 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.7 | 0.5 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | #VALUE! | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-03-25 | 8:36 | 1374.4 | 9.4 | 210 | 205 | 0 | 3.8 | 0.79 | 0.28 |  | 1.07 | 4.87 | 0.30213 | 0.73832 | 3.5514 | 13.3835 | 15.7928 | 10 | 197.5 | 0.079964 | 6.21 | 5.94 | 6.8 | 3.84 | NR | 947 | [21 empty] | SDS-Cl2 demand | mg/L | 0.2 | 1.85 | --- | 6.8 | --- | 89.1892 | 6.2885 | 96.8196 | SDS-Cl2 demand | mg/L | 0.5 | 1.9 | --- | 5.6852 | --- | 73.6842 | 5.2694 | 90.5112 | SDS-Cl2 demand | mg/L | 0.4 | 1.5 | --- | 4.0667 | --- | 73.3333 | 3.7587 | 89.3579 | SDS-Cl2 demand | mg/L | 0.3 | 2.5 | --- | 7.6333 | --- | 88 | 7.0291 | 95.732 | SDS-Cl2 demand | mg/L | 0.3 | 2.5 | --- | 7.6333 | --- | 88 | 7.0291 | 95.732
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | NA | Influent TDS, TDSI (mg/L) | #VALUE! | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-03-26 | 8:22 | 1398.1 | 11.2 | 210 | 205 | 0 | 3.8 | 0.79 | 0.32 |  | 1.11 | 4.91 | 0.30483 | 0.71171 | 3.4234 | 13.3835 | 14.9745 | 10 | 197.5 | 0.07582 | 7.25 | 6.37 | 6.83 | 5.12 | NR | 1312 | [21 empty] | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | 6 | Osmotic pressure gradient, Dp (psi) | #VALUE! | [5 empty] | 1998-03-27 | 9:28 | 1423.2 | 11.8 | 208 | 203 | 0 | 3.8 | 0.75 | 0.26 |  | 1.01 | 4.81 | 0.29943 | 0.74257 | 3.7624 | 12.7059 | 13.9664 | 10 | 195.5 | 0.071439 | 6.8 | 5.54 | 6.26 | 5.12 | NR | 890 | [21 empty] | SDS-Chlorination pH | --- | 7.07 | 7.01 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.06 | 7.06 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.27 | 7.38 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.25 | 7.13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.25 | 7.13 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NA | [7 empty] | 1998-03-28 | 11:03 | 1448.2 | 12.7 | 205 | 200 | 0 | 3.8 | 0.79 | 0.32 |  | 1.11 | 4.91 | 0.30483 | 0.71171 | 3.4234 | 13.3835 | 14.3251 | 10 | 192.5 | 0.074416 | 5.98 | 5.45 | 6.34 | 5.76 | NR | 1024 | [21 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) |  | Estimate the Required Influent Pressure | [6 empty] | 1998-03-29 | 11:06 | 1472 | 13.1 | 192 | 187 | 0 | 3.8 | 0.84 | 0.36 | X | 1.2 | 5 | 0.30922 | 0.7 | 3.1667 | 14.2306 | 15.0527 | 10 | 179.5 | 0.083859 | 9.14 | 8.28 | 8.77 | 7.04 | NR | 819 | [21 empty] | SDS-TOX | mg Cl- /L | BMRL | 81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 50 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 99 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 122 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | 1500 mg/L NaCl | Estimated system pressure losses, DPloss (psi) | NA | [5 empty] | 1998-03-30 | 11:30 | 1496.5 | 15.7 | 195 | 190 | 0 | 3.8 | 0.6 | 0.23 |  | 0.83 | 4.63 | 0.29234 | 0.72289 | 4.5783 | 10.1647 | 9.9565 | 10 | 182.5 | 0.054556 | 7.86 | 7.92 | 8.36 | 3.2 | NR | 954 | [21 empty] | SDS-CHCl3 | mg/L | BMRL | 10.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 8.59 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) |  | Design permeate pressure, Pp (psi) | NA | [5 empty] | 1998-03-31 | 10:55 | 1519.7 | 14.5 | 195 | 189 | 0 | 3.8 | 0.8 | 0.3 |  | 1.1 | 4.9 | 0.30382 | 0.72727 | 3.4545 | 13.5529 | 13.7547 | 10 | 182 | 0.075575 | 5.45 | 5.88 | 7.03 | 2.56 | NR | 1062 | [21 empty] | SDS-BDCM | mg/L | BMRL | 7.24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 7.16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | 32 | Required influent pressure, PI (psi) | #VALUE! | [5 empty] | 1998-04-01 | 19:32 | 1552.4 | 14.9 | 200 | 196 | 0 | 3.8 | 0.81 | 0.3 |  | 1.11 | 4.91 | 0.30416 | 0.72973 | 3.4234 | 13.7224 | 13.763 | 10 | 188 | 0.073207 | 6.02 | 5.56 | 6.45 | 4.48 | NR | 736 | [21 empty] | SDS-DBCM | mg/L | BMRL | 4.45 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 5.18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-04-02 | 9:08 | 1566 | 14.1 | 228 | 223 | 0 | 3.8 | 0.81 | 0.355 |  | 1.165 | 4.965 | 0.30787 | 0.69528 | 3.2618 | 13.7224 | 14.0923 | 10 | 215.5 | 0.065394 | 6.16 | 5.93 | 6.73 | 3.84 | NR | 512 | [21 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7 | [7 empty] | 1998-04-03 | 8:13 | 1589.1 | 13.6 | 229 | 224 | 0 | 3.8 | 0.8 | 0.35 |  | 1.15 | 4.95 | 0.3072 | 0.69565 | 3.3043 | 13.5529 | 14.1256 | 10 | 216.5 | 0.065245 | 7.57 | 7.24 | 7.14 | 2.56 | NR | 531 | [21 empty] | SDS-THM4 | mg/L | 0 | 22.29 | --- | 89.16 | --- | 100 | 82.2496 | 100 | SDS-THM4 | mg/L | 0 | 20.93 | --- | 77.5185 | --- | 100 | 71.3019 | 100 | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 250 max | [7 empty] | 1998-04-04 | 9:23 | 1614.2 | 13.4 | 230 | 225 | 0 | 3.8 | 0.8 | 0.35 |  | 1.15 | 4.95 | 0.3072 | 0.69565 | 3.3043 | 13.5529 | 14.2093 | 10 | 217.5 | 0.06533 | 6.97 | 6.16 | 7.44 | 3.2 | NR | 602 | [21 empty] | SDS-MCAA* | mg/L | BMRL | 3.02 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | 3.32 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 35896 | [7 empty] | 1998-04-05 | 10:46 | 1638.7 | 13.5 | 235 | 230 | 0 | 3.8 | 0.43 | 0.31 |  | 0.74 | 4.54 | 0.292 | 0.58108 | 5.1351 | 7.2847 | 7.615 | 10 | 222.5 | 0.034225 | 8.85 | 7.5 | 8.23 | 3.2 | NR | 627 | [21 empty] | SDS-DCAA* | mg/L | 1.42 | 9.71 | --- | 34.58 | --- | 85.3759 | 32.0099 | 95.5639 | SDS-DCAA* | mg/L | 1.74 | 7.31 | --- | 22.3696 | --- | 76.197 | 20.7152 | 91.6004 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | [8 empty] | 1998-04-06 | 8:41 | 1660.4 | 11.8 | 201 | 197 | 0 | 3.8 | 0.82 | 0.35 | X | 1.17 | 4.97 | 0.30787 | 0.70085 | 3.2479 | 13.8918 | 15.2699 | 10 | 189 | 0.080793 | 6.1 | 5.59 | 6.58 | 4.4 | NR | 557 | [21 empty] | SDS-TCAA* | mg/L | BMRL | 6.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 5.24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [55 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [55 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0.1 | [55 empty] | SDS-BCAA* | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [56 empty] | SDS-TBAA | mg/L | BMRL | 6.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [56 empty] | SDS-CDBAA | mg/L | BMRL | 1.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.04 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-DCBAA | mg/L | BMRL | 4.89 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 4.25 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5 | mg/L | 1.42 | 18.96 | --- | 71.58 | --- | 92.5105 | 66.1422 | 97.8531 | SDS-HAA5 | mg/L | 5.06 | 12.55 | --- | 32.8007 | --- | 59.6813 | 30.5761 | 83.4511 | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA6 | mg/L | 1.42 | 22.16 | --- | 84.38 | --- | 93.5921 | 77.9502 | 98.1783 | SDS-HAA6 | mg/L | 5.06 | 15.33 | --- | 43.097 | --- | 66.9928 | 40.0467 | 87.3647 | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[59 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[59 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[60 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[60 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[59 empty] | Qp/QT (THM4), % | -223.0148 | -61.5074 |  | Qp/QT (HAA5), % | -199.7719 | -45.8381 |  |  |  | Qp/QT (THM4), % | -244.0038 | -72.0019 |  | Qp/QT (HAA5), % | -553.4045 | -192.9239 |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
[59 empty] | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
[59 empty] | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
[59 empty] | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
[59 empty] | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[59 empty] | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[59 empty] | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[59 empty] | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[59 empty] | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[59 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[59 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[59 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[59 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[59 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[59 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[59 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[59 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[59 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[59 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[59 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on AA12: Carollo Engineers: Low pressure alarm shut down pilot plant.
Note on AA27: Carollo Engineers: Electrical maintenance was performed to the building housing the pilot plants. Power outage required pilot plant shut down.
Note on AI5: Carollo Engineers: Estimated Osmotic Pressure. Based on average permeate TDS concentration of 30 mg/L and estimated bulk concentration of 1100 mg/L (which was measured but not reported.
Note on AM6: Carollo Engineers: pH was controlled by a metering pump manually. Daily variations in alkalinity caused fluctuations in pH.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BQ25: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CB18: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on CB19: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CC22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CE22: Carollo Engineers: Data verified 8/6/99 by Carollo.
Note on CE23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CJ37: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CJ47: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CP22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CU37: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CU47: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CX25: Carollo Engineers: Data verified by Carollo 8/5/99.
Note on DA22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DA23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DF37: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on DF47: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.

## ESNA 3rd Quarter
FIELD-SET 3: 3rd QUARTER SEBST RESULTS (FILE: sebst-2.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: SEBST Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 3-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 3-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 3-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 3-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.72 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | ESNA | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.10417 | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSP | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1.06 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.98 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.01 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.03 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.03 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | ESNA-4040 |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-04-11 | 10:45 | 1708.8 | 11.3 | 90 | 84 | 0 | 3.8 | 0.79 | 0.24 |  | 1.03 | 4.83 | 0.7058 | 0.76699 | 3.6893 | 13.3835 | 14.9303 | 10 | 77 | 0.1939 | 8.4 | 8.34 | 8.99 | 64 | NR | 768 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.86 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.78 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.81 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200-300 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-04-13 | 13:35 | 1715.4 | 12.7 | 80 | 75 | 0 | 3.8 | 0.73 | 0.3 |  | 1.03 | 4.83 | 0.71058 | 0.70874 | 3.6893 | 12.3671 | 13.2371 | 10 | 67.5 | 0.1961 | 6.85 | 6.98 | 6.8 | 51 | NR | 736 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-04-14 | 8:25 | 1734.3 | 13 | 80 | 75 | 0 | 3.8 | 0.73 | 0.3 |  | 1.03 | 4.83 | 0.71058 | 0.70874 | 3.6893 | 12.3671 | 13.1202 | 10 | 67.5 | 0.19437 | 6.8 | 6.39 | 6.78 | 77 | NR | 858 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Composite | Design flux, FW (gfd) | 12 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-04-15 | 8:43 | 1758.6 | 14.7 | 80 | 75 | 0 | 3.8 | 0.74 | 0.3 |  | 1.04 | 4.84 | 0.71137 | 0.71154 | 3.6538 | 12.5365 | 12.6481 | 10 | 67.5 | 0.18738 | 6.12 | 5.51 | 6.52 | 58 | NR | 870 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate, Qp (gpm) | 0.70833 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-04-16 | 9:34 | 1783.4 | 14.6 | 80 | 75 | 0 | 3.8 | 0.73 | 0.3 |  | 1.03 | 4.83 | 0.71058 | 0.70874 | 3.6893 | 12.3671 | 12.5141 | 10 | 67.5 | 0.18539 | 6.47 | 5.83 | 6.68 | 77 | NR | 890 | [21 empty] | Sampling date | MM/DD/YY | 1998-04-17 | 1998-04-17 | 1998-04-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-30 | 1998-04-30 | 1998-04-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-05 | 1998-05-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-05 | 1998-05-05 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negavite | Feed flow rate, QF (gpm) | 0.94444 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-04-17 | 8:37 | 1803.6 | 13.8 | 80 | 75 | 0 | 3.8 | 0.76 | 0.3 |  | 1.06 | 4.86 | 0.71296 | 0.71698 | 3.5849 | 12.8753 | 13.3402 | 10 | 67.5 | 0.19763 | 6.72 | 6.63 | 6.91 | 70 | NR | 774 | [21 empty] | Sampling time | hh:mm | 8:37 | 8:37 | 8:37 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:35 | 8:35 | 8:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:31 | 9:31 | 9:31 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:12 | 9:12 | 9:12 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:12 | 9:12 | 9:12 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.23611 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-04-18 | 11:40 | 1806.6 | 14.3 | 80 | 75 | 0 | 3.8 | 0.76 | 0.25 |  | 1.01 | 4.81 | 0.70501 | 0.75248 | 3.7624 | 12.8753 | 13.1445 | 10 | 67.5 | 0.19473 | 6.66 | 7.2 | 7.05 | 58 | NR | 928 | [21 empty] | Operation time | hh.hh | 1803.6 | 1803.6 | 1803.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1885.8 | 1885.8 | 1885.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2078.7 | 2078.7 | 2078.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2198 | 2198 | 2198 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2198 | 2198 | 2198 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-04-19 | 12:28 | 1831.4 | 13.9 | 80 | 75 | 0 | 3.8 | 0.73 | 0.25 |  | 0.98 | 4.78 | 0.70262 | 0.7449 | 3.8776 | 12.3671 | 12.7758 | 10 | 67.5 | 0.18927 | 6.02 | 5.29 | 6.4 | 64 | NR | 966 | [21 empty] | pH | --- | 6.72 | 6.63 | 6.91 | --- | --- | --- | --- | --- | pH | --- | 6.32 | 5.59 | 6.79 | --- | --- | --- | --- | --- | pH | --- | 7.66 | 6.65 | 7.3 | --- | --- | --- | --- | --- | pH | --- | 7.72 | 7.03 | 7.73 | --- | --- | --- | --- | --- | pH | --- | 7.72 | 7.03 | 7.73 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 3.94" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 51.5 |  |  |  | 1998-04-20 | 8:55 | 1838.1 | 14.1 | 81 | 76 | 0 | 3.8 | 0.73 | 0.23 |  | 0.96 | 4.76 | 0.69944 | 0.76042 | 3.9583 | 12.3671 | 12.7005 | 10 | 68.5 | 0.18541 | 7.24 | 6.16 | 6.58 | 77 | NR | 992 | [21 empty] | Temperature | oC | 13.8 | 13.8 | 13.8 | --- | --- | --- | --- | --- | Temperature | oC | 13.7 | 13.7 | 13.7 | --- | --- | --- | --- | --- | Temperature | oC | 15.4 | 15.4 | 15.4 | --- | --- | --- | --- | --- | Temperature | oC | 19.9 | 19.9 | 19.9 | --- | --- | --- | --- | --- | Temperature | oC | 19.9 | 19.9 | 19.9 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Design influent flow rate2, QI (gpm) | 4.8 | Barium (mg/L) | 0.016 |  |  |  | 1998-04-21 | 9:12 | 1862.4 | 13.6 | 95 | 90 | 0 | 3.8 | 0.73 | 0.23 |  | 0.96 | 4.76 | 0.69944 | 0.76042 | 3.9583 | 12.3671 | 12.8896 | 10 | 82.5 | 0.15624 | 6.44 | 5.71 | 6.72 | 51.2 | NR | 928 | [21 empty] | Alkalinity | mg/L as CaCO3 | 9 | 25 | 72 | 66.1429 | 8.1349 | 64 | 61.6561 | 85.4029 | Alkalinity | mg/L as CaCO3 | 7 | 25 | 56 | 76.2308 | -36.1264 | 72 | 70.9791 | 90.1379 | Alkalinity | mg/L as CaCO3 | 8 | 25 | 98 | 64.6667 | 34.0136 | 68 | 60.5021 | 86.7773 | Alkalinity | mg/L as CaCO3 | 11 | 58 | 114 | 173.069 | -51.8149 | 81.0345 | 160.7997 | 93.1592 | Alkalinity | mg/L as CaCO3 | 10 | 57 | 109 | 172.069 | -57.8614 | 82.4561 | 159.7997 | 93.7422 | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | 12 | Design recycle flow rate, QR (gpm) | 3.8556 | Strontium (mg/L) | 0.247 |  |  |  | 1998-04-22 | 8:35 | 1885.8 | 13.7 | 95 | 90 | 0 | 3.8 | 0.73 | 0.25 |  | 0.98 | 4.78 | 0.70262 | 0.7449 | 3.8776 | 12.3671 | 12.8515 | 10 | 82.5 | 0.15578 | 6.32 | 5.59 | 6.79 | 70.4 | NR | 934.4 | [21 empty] | Total dissolved solids | mg/L | 70 | NR | 774 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 70.4 | NR | 934.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 57.6 | NR | 966.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 76.8 | NR | 844.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 76.8 | NR | 844.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Recycle ratio, r | 4.0824 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-04-23 | 9:50 | 1910 | 14.3 | 90 | 85 | 0 | 3.8 | 0.74 | 0.25 |  | 0.99 | 4.79 | 0.70341 | 0.74747 | 3.8384 | 12.5365 | 12.7986 | 10 | 77.5 | 0.16514 | 7.09 | 6.63 | 7.19 | 70.4 | NR | 953.6 | [21 empty] | Total hardness | mg/L as CaCO3 | 4.57 | 171 | 407 | 598.9629 | -47.1653 | 97.3275 | 552.292 | 99.1725 | Total hardness | mg/L as CaCO3 | 2.17 | 198 | 532 | 755.3623 | -41.9854 | 98.904 | 698.2268 | 99.6892 | Total hardness | mg/L as CaCO3 | 2.87 | 176 | 500 | 579.97 | -15.994 | 98.3693 | 537.5573 | 99.4661 | Total hardness | mg/L as CaCO3 | BMRL | 205 | 498 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | BMRL | 203 | 504 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.14 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-04-24 | 9:00 | 1934.2 | 14.8 | 90 | 85 | 0 | 3.8 | 0.74 | 0.3 |  | 1.04 | 4.84 | 0.71137 | 0.71154 | 3.6538 | 12.5365 | 12.6108 | 10 | 77.5 | 0.16272 | 8.26 | 7.35 | 7.96 | 57.6 | NR | 966.4 | [21 empty] | Calcium hardness | mg/L as CaCO3 | 3.95 | 139 | 330 | 486.2714 | -47.355 | 97.1583 | 448.4003 | 99.1191 | Calcium hardness | mg/L as CaCO3 | 2.17 | 175 | 464 | 666.9008 | -43.7286 | 98.76 | 616.4758 | 99.648 | Calcium hardness | mg/L as CaCO3 | 2.87 | 158 | 447 | 519.97 | -16.3244 | 98.1835 | 481.9669 | 99.4045 | Calcium hardness | mg/L as CaCO3 | BMRL | 197 | 477 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 195 | 482 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-04-25 | 11:35 | 1960.7 | 15 | 89 | 84 | 0 | 3.8 | 0.74 | 0.25 |  | 0.99 | 4.79 | 0.70341 | 0.74747 | 3.8384 | 12.5365 | 12.5365 | 10 | 76.5 | 0.16388 | 6.93 | 6.01 | 7.19 | 64 | NR | 1024 | [21 empty] | Turbidity | ntu | 0.05 | 0.4 | NA | 1.3 | #VALUE! | 87.5 | 1.2019 | 95.8398 | Turbidity | ntu | 0.05 | 0.95 | 0.5 | 3.5115 | -602.3077 | 94.7368 | 3.249 | 98.461 | Turbidity | ntu | 0.05 | 0.75 | 0.45 | 2.3833 | -429.6296 | 93.3333 | 2.2119 | 97.7394 | Turbidity | ntu | 0.05 | 0.35 | 1.15 | 1.0845 | 5.6972 | 85.7143 | 1.0062 | 95.0307 | Turbidity | ntu | 0.05 | 0.33 | 1.15 | 1.0155 | 11.6942 | 84.8485 | 0.94242 | 94.6945 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-04-26 | 11:51 | 1984 | 16.6 | 82 | 77 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 11.6342 | 10 | 69.5 | 0.1674 | 6.19 | 5.66 | 6.8 | 71.39 | NR | 1171.2 | [21 empty] | Ammonia | mg NH3-N / L | 0.044 | 0.061 | 0.102 | 0.10471 | -2.6611 | 27.8689 | 0.099947 | 55.9767 | Ammonia | mg NH3-N / L | BMRL | 0.058 | 0.131 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.025 | 0.05 | 0.15 | 0.10833 | 27.7778 | 50 | 0.10221 | 75.5403 | Ammonia | mg NH3-N / L | 0.039 | 0.049 | 0.109 | 0.073483 | 32.5846 | 20.4082 | 0.070872 | 44.9714 | Ammonia | mg NH3-N / L | 0.038 | 0.05 | 0.109 | 0.079379 | 27.1749 | 24 | 0.076247 | 50.1618
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-04-27 | 15:35 | 2012.8 | 16.6 | 82 | 77 | 0 | 3.8 | 0.68 | 0.27 |  | 0.95 | 4.75 | 0.70182 | 0.71579 | 4 | 11.52 | 10.9879 | 10 | 69.5 | 0.1581 | 7.44 | 6.51 | 7.3 | 30.72 | NR | 1068.8 | [21 empty] | Total organic carbon | mg/L | 0.43 | 2.56 | 5.7 | 8.0371 | -41.0025 | 83.2031 | 7.4398 | 94.2203 | Total organic carbon | mg/L | 0.41 | 3.19 | 6.4 | 11.1023 | -73.4736 | 87.1473 | 10.2912 | 96.016 | Total organic carbon | mg/L | 0.36 | 2.59 | 5.68 | 7.7933 | -37.2066 | 86.1004 | 7.247 | 95.0325 | Total organic carbon | mg/L | 0.52 | 2.32 | 5.76 | 6.7269 | -16.7864 | 77.5862 | 6.257 | 91.6893 | Total organic carbon | mg/L | 0.28 | 2.26 | 5.23 | 7.1076 | -35.9003 | 87.6106 | 6.5907 | 95.7516
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 14 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-04-28 | 10:55 | 2032.1 | 15.8 | 84 | 78 | 0 | 3.8 | 0.6 | 0.25 |  | 0.85 | 4.65 | 0.69227 | 0.70588 | 4.4706 | 10.1647 | 9.9272 | 10 | 71 | 0.13982 | 6.16 | 5.71 | 6.78 | 22.4 | NR | 1017.6 | [21 empty] | UV254 | cm-1 | 0.018 | 0.055 | 0.118 | 0.15014 | -27.2397 | 67.2727 | 0.13977 | 87.1214 | UV254 | cm-1 | 0.033 | 0.068 | 0.1 | 0.16762 | -67.6154 | 51.4706 | 0.1574 | 79.0348 | UV254 | cm-1 | 0.02 | 0.061 | 0.117 | 0.15667 | -33.9031 | 67.2131 | 0.14662 | 86.3595 | UV254 | cm-1 | 0.022 | 0.055 | 0.111 | 0.13579 | -22.3361 | 60 | 0.12718 | 82.7015 | UV254 | cm-1 | 0.017 | 0.056 | 0.118 | 0.15148 | -28.3752 | 69.6429 | 0.1413 | 87.969
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.001 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-04-29 | 18:35 | 2063.9 | 15.3 | 106 | 101 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 12.09 | 10 | 93.5 | 0.1293 | 6.24 | 5.93 | 6.82 | 57.6 | NR | 972.8 | [21 empty] | SUVA | L/(mg*m) | 4.186 | 2.1484 | 2.0702 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 8.0488 | 2.1317 | 1.5625 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.5556 | 2.3552 | 2.0599 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.2308 | 2.3707 | 1.9271 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 6.0714 | 2.4779 | 2.2562 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.85 | [5 empty] | 1998-04-30 | 9:31 | 2078.7 | 15.4 | 112 | 107 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.70898 | 0.70297 | 3.7624 | 12.0282 | 11.8869 | 10 | 99.5 | 0.11947 | 7.66 | 6.65 | 7.3 | 57.6 | NR | 966.4 | [21 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 80 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 90 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 90 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 100 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | 950 | Feed TDS, TDSF (mg/L) | 1000 | [5 empty] | 1998-05-01 | 9:25 | 2102.7 | 15.7 | 160 | 155 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.70898 | 0.70297 | 3.7624 | 12.0282 | 11.7819 | 10 | 147.5 | 0.079877 | 7 | 6.98 | 7.24 | 51.2 | NR | 960 | [21 empty] | SDS-Cl2 dose | mg/L | 1 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | 2872.9916 | [5 empty] | 1998-05-02 | 12:02 | 2129.1 | 14.8 | 80 | 75 | 0 | 3.8 | 0.72 | 0.3 | X | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 12.27 | 10 | 67.5 | 0.18178 | 6.71 | 5.67 | 6.42 | 44.8 | NR | 1056 | [21 empty] | SDS-Free Cl2 residual | mg/L | 0.5 | 0.9 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.55 | 0.7 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.65 | 0.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | 375.6695 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-05-03 | 11:53 | 2152.9 | 15.6 | 97 | 92 | 0 | 3.8 | 0.74 | 0.23 |  | 0.97 | 4.77 | 0.70023 | 0.76289 | 3.9175 | 12.5365 | 12.3161 | 10 | 84.5 | 0.14575 | 7.31 | 7.31 | 7.97 | 76.8 | NR | 1043.2 | [21 empty] | SDS-Cl2 demand | mg/L | 0.5 | 2.1 | --- | 6.2143 | --- | 76.1905 | 5.7656 | 91.3279 | SDS-Cl2 demand | mg/L | 0.45 | 1.8 | --- | 5.6423 | --- | 75 | 5.2484 | 91.426 | SDS-Cl2 demand | mg/L | 0.55 | 2.2 | --- | 6.05 | --- | 75 | 5.6458 | 90.2582 | SDS-Cl2 demand | mg/L | 0.7 | 2.3 | --- | 6.2172 | --- | 69.5652 | 5.7996 | 87.9301 | SDS-Cl2 demand | mg/L | 0.7 | 2.3 | --- | 6.2172 | --- | 69.5652 | 5.7996 | 87.9301
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | 0.6-1.0 | Influent TDS, TDSI (mg/L) | 2504.4631 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-05-04 | 8:55 | 2174 | 16.3 | 115 | 110 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 11.7378 | 10 | 102.5 | 0.11452 | 7.22 | 6.75 | 7.7 | 57.6 | NR | 1004.8 | [21 empty] | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | Dependant upon array and feedwater | Osmotic pressure gradient, Dp (psi) | 23.1306 | [5 empty] | 1998-05-05 | 9:12 | 2198 | 19.9 | 80 | 75 | 0 | 3.8 | 0.72 | 0.3 | X | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 10.5529 | 10 | 67.5 | 0.15634 | 7.72 | 7.03 | 7.73 | 51.2 | NR | 902.4 | [21 empty] | SDS-Chlorination pH | --- | 7.36 | 7.26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.35 | 7.27 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.34 | 7.23 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.34 | 7.21 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.34 | 7.21 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 1998-05-06 | 8:40 | 2221.5 | 18.1 | 89 | 84 | 0 | 3.8 | 0.73 | 0.3 |  | 1.03 | 4.83 | 0.71058 | 0.70874 | 3.6893 | 12.3671 | 11.2842 | 10 | 76.5 | 0.14751 | 8.19 | 7.35 | 7.82 | 76.8 | NR | 844.8 | [21 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 1998-05-07 | 8:42 | 2245.5 | 18.4 | 99 | 94 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 11.0314 | 10 | 86.5 | 0.12753 | 6.91 | 7.21 | 7.53 | 57.6 | NR | 864 | [21 empty] | SDS-TOX | mg Cl- /L | BMRL | 128 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 141 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 107 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 133 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | 85-95%; 500 mg/L NaCl | Estimated system pressure losses, DPloss (psi) | 4 | [5 empty] | 1998-05-08 | 8:50 | 2269.2 | 19.3 | 98 | 93 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.70819 | 0.7 | 3.8 | 11.8588 | 10.4434 | 10 | 85.5 | 0.12214 | 7.55 | 6.06 | 7.11 | 153.6 | NR | 844.8 | [21 empty] | SDS-CHCl3 | mg/L | 1.22 | 28.4 | --- | 98.2914 | --- | 95.7042 | 90.6695 | 98.6545 | SDS-CHCl3 | mg/L | BMRL | 20.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.11 | 19.3 | --- | 61.7433 | --- | 94.2487 | 57.2872 | 98.0624 | SDS-CHCl3 | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.05 | 24.2 | --- | 80.8776 | --- | 95.6612 | 74.8343 | 98.5969
|  | (e.g., solute type and concentration) |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-05-09 | 12:05 | 2296.5 | 19.6 | 92 | 87 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 10.6469 | 10 | 79.5 | 0.13392 | 6.02 | 5.54 | 6.67 | 51.2 | NR | 896 | [21 empty] | SDS-BDCM | mg/L | 1.16 | 13.3 | --- | 44.5171 | --- | 91.2782 | 41.1128 | 97.1785 | SDS-BDCM | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.28 | 12.6 | --- | 39.0133 | --- | 89.8413 | 36.2402 | 96.468 | SDS-BDCM | mg/L | BMRL | 13.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.15 | 14.3 | --- | 46.4948 | --- | 91.958 | 43.062 | 97.3294
|  | Variability of rejection of reference solute (%) | 85-95% | Required influent pressure, PI (psi) | 142.3234 | [5 empty] | 1998-05-10 | 11:55 | 2320.2 | 19.9 | 90 | 84 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 10.5529 | 10 | 77 | 0.13705 | 6.38 | 5.98 | 7 | 51.2 | NR | 1011.2 | [21 empty] | SDS-DBCM | mg/L | 1.09 | 3.87 | --- | 11.0186 | --- | 71.8346 | 10.239 | 89.3544 | SDS-DBCM | mg/L | BMRL | 5.28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 1.01 | 5.63 | --- | 16.41 | --- | 82.0604 | 15.2782 | 93.3893 | SDS-DBCM | mg/L | BMRL | 5.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 1.01 | 5.48 | --- | 16.4238 | --- | 81.5693 | 15.2569 | 93.38
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-05-11 | 8:47 | 2341.2 | 20 | 94 | 89 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.70898 | 0.70297 | 3.7624 | 12.0282 | 10.3757 | 10 | 81.5 | 0.12731 | 6.99 | 6.2 | 7.16 | 57.6 | NR | 953.6 | [21 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 6.5-7.0 | [7 empty] | 1998-05-12 | 8:35 | 2365 | 20.6 | 94 | 89 | 0 | 3.8 | 0.71 | 0.3 | X | 1.01 | 4.81 | 0.70898 | 0.70297 | 3.7624 | 12.0282 | 10.1933 | 10 | 81.5 | 0.12507 | 6.64 | 6.16 | 7.19 | 57.6 | NR | 908.8 | [21 empty] | SDS-THM4 | mg/L | 3.47 | 45.57 | --- | 153.8271 | --- | 92.3853 | 142.0213 | 97.5567 | SDS-THM4 | mg/L | 0 | 37.48 | --- | 144.1538 | --- | 100 | 133.2187 | 100 | SDS-THM4 | mg/L | 3.4 | 37.53 | --- | 117.1667 | --- | 90.9406 | 108.8056 | 96.8752 | SDS-THM4 | mg/L | 0 | 41.6 | --- | 143.4483 | --- | 100 | 132.5887 | 100 | SDS-THM4 | mg/L | 3.21 | 43.98 | --- | 143.7962 | --- | 92.7012 | 133.1533 | 97.5892
|  | Acceptable range of operating pressures | less than or equal to 400 psi | [7 empty] | 1998-05-13 | 9:11 | 2389.5 | 20.7 | 98 | 93 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.70898 | 0.70297 | 3.7624 | 12.0282 | 10.1632 | 10 | 85.5 | 0.11887 | 7.53 | 6.82 | 7.7 | 51.2 | NR | 928 | [21 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 0.88 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3.0-10.0 | [7 empty] | 1998-05-14 | 8:55 | 2412.8 | 21.7 | 98 | 93 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.70819 | 0.7 | 3.8 | 11.8588 | 9.7282 | 10 | 85.5 | 0.11378 | 7.21 | 6.03 | 6.81 | 51.2 | NR | 972.8 | [21 empty] | SDS-DCAA* | mg/L | 1.41 | 14.2 | --- | 47.0886 | --- | 90.0704 | 43.502 | 96.7588 | SDS-DCAA* | mg/L | 1.48 | 9.84 | --- | 33.6338 | --- | 84.9593 | 31.1947 | 95.2556 | SDS-DCAA* | mg/L | 1.32 | 7.79 | --- | 22.8867 | --- | 83.0552 | 21.3017 | 93.8033 | SDS-DCAA* | mg/L | 1.43 | 9.49 | --- | 29.2231 | --- | 84.9315 | 27.1191 | 94.727 | SDS-DCAA* | mg/L | 1.34 | 9.38 | --- | 29.0641 | --- | 85.7143 | 26.9653 | 95.0307
|  | Typical pressure drop across a single element (psi) | 12 psi max | [7 empty] | 1998-05-15 | 8:40 | 2436.5 | 22.3 | 97 | 92 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.70978 | 0.70588 | 3.7255 | 12.1976 | 9.8302 | 10 | 84.5 | 0.11633 | 6.53 | 5.77 | 6.98 | 44.8 | NR | 947.2 | [21 empty] | SDS-TCAA* | mg/L | 1.12 | 14.8 | --- | 49.9771 | --- | 92.4324 | 46.141 | 97.5727 | SDS-TCAA* | mg/L | BMRL | 9.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 6.52 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 8.09 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 4 | [18 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [18 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 0.23 | 1.11 | --- | 3.2645 | --- | 79.2793 | 3.0348 | 92.4211
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0.0 mg/L | [18 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-BCAA* | mg/L | 0.8 | 6.45 | --- | 20.9786 | --- | 87.5969 | 19.3942 | 95.8751 | SDS-BCAA* | mg/L | BMRL | 4.94 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 4.25 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 4.66 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 0.66 | 4.63 | --- | 14.3497 | --- | 85.7451 | 13.3133 | 95.0425
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [19 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | 1.28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [19 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-CDBAA | mg/L | BMRL | 2.43 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.86 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.49 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.53 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-DCBAA | mg/L | BMRL | 11.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 7.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 5.81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | #DIV/0! | [27 empty] | SDS-HAA5 | mg/L | 2.53 | 29 | --- | 97.0657 | --- | 91.2759 | 89.6429 | 97.1777 | SDS-HAA5 | mg/L | 1.48 | 19.51 | --- | 70.8262 | --- | 92.4141 | 65.5657 | 97.7427 | SDS-HAA5 | mg/L | 1.32 | 16.4 | --- | 51.5867 | --- | 91.9512 | 47.8924 | 97.2438 | SDS-HAA5 | mg/L | 1.43 | 18.82 | --- | 61.3955 | --- | 92.4017 | 56.8559 | 97.4849 | SDS-HAA5 | mg/L | 1.57 | 18.49 | --- | 59.9148 | --- | 91.5089 | 55.4979 | 97.1711
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-HAA6 | mg/L | 3.33 | 35.45 | --- | 118.0443 | --- | 90.6065 | 109.0371 | 96.946 | SDS-HAA6 | mg/L | 1.48 | 24.45 | --- | 89.8262 | --- | 93.9468 | 83.1244 | 98.2195 | SDS-HAA6 | mg/L | 1.32 | 20.65 | --- | 65.7533 | --- | 93.6077 | 61.018 | 97.8367 | SDS-HAA6 | mg/L | 1.43 | 23.48 | --- | 77.4645 | --- | 93.9097 | 71.7084 | 98.0058 | SDS-HAA6 | mg/L | 2.23 | 23.12 | --- | 74.2645 | --- | 90.3547 | 68.8112 | 96.7592
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [28 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [28 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Qp/QT (THM4), % | -62.7791 | 22.7316 |  | Qp/QT (HAA5), % | -94.4465 | 7.5557 |  |  |  | Qp/QT (THM4), % | -92.1025 | 3.9488 |  | Qp/QT (HAA5), % | -191.2923 | -41.5419 |  |  |  | Qp/QT (THM4), % | -100.9962 | 4.4829 |  | Qp/QT (HAA5), % | -249.3369 | -70.2918 |  |  |  | Qp/QT (THM4), % | -73.0769 | 13.4615 |  | Qp/QT (HAA5), % | -202.3002 | -47.0385 |  |  |  | Qp/QT (THM4), % | -68.727 | 19.5732 |  | Qp/QT (HAA5), % | -209.87 | -50.2955
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 42.389 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-HAA5b, mg/L | NA | 22.9829 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 18.798 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 15.724 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 16.479 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 15.1782 |  | SDS-HAA5b, mg/L | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-CDb, mg/L | NA | 1.7363 |  | SDS-CDb, mg/L | NA | 1.9791 |  |  |  | SDS-CDb, mg/L | NA | 1.7467 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 2.126 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 2.0846 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.9868 |  | SDS-CDb, mg/L | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | TOCb, mg/L | NA | 2.0758 |  | TOCb, mg/L | NA | 2.3991 |  |  |  | TOCb, mg/L | NA | 3.0802 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 2.49 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 2.0777 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 1.8725 |  | TOCb, mg/L | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | UV254 b, cm-1 | NA | 0.046589 |  | UV254 b, cm-1 | NA | 0.052204 |  |  |  | UV254 b, cm-1 | NA | 0.066618 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.059162 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.050558 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.048366 |  | UV254 b, cm-1 | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Alkb, mg/L CaCO3 | NA | 21.3629 |  | Alkb, mg/L CaCO3 | NA | 23.7911 |  |  |  | Alkb, mg/L CaCO3 | NA | 24.2892 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 24.2379 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 51.6731 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 47.8006 |  | Alkb, mg/L CaCO3 | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | T-Hdb, mg/L CaCO3 | NA | 133.1678 |  | T-Hdb, mg/L CaCO3 | NA | 158.425 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 190.2671 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 168.2388 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Ca-Hdb, mg/L CaCO3 | NA | 108.301 |  | Ca-Hdb, mg/L CaCO3 | NA | 128.796 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 168.1753 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 151.0457 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on AA7: Carollo Engineers: Blown fuse shut down pilot plant.
Note on AA13: Carollo Engineers: Blown fuse shut down pilot plant.
Note on AA15: Carollo Engineers: Blown fuse shut down pilot plant.
Note on AI5: Carollo Engineers: Estimated osmotic pressure is representative of the 4th quarter data where TDS in the feed stream was measured appropriately.
Note on AM6: Carollo Engineers: pH was controlled by a metering pump manually. Daily variations in alkalinity caused fluctuations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of erratic permeate TDS concentrations.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CU16: Carollo Engineers: Data veririfed by Carollo 8/6/99.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.

## ESNA 4th Quarter
FIELD-SET 4: 4th QUARTER SEBST RESULTS (FILE: sebst-2.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: SEBST Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 4-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 4-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 4-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 4-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Osmonics | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.77 | [8 empty] | Recovery during sample collection (decimal) | 0.76 | [8 empty] | Recovery during sample collection (decimal) | 0.81 | [8 empty] | Recovery during sample collection (decimal) | 0.83 | [8 empty] | Recovery during sample collection (decimal) | 0.83 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | MS | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.74409 | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSP | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1.3 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.26 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.19 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.33 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.33 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | S4040 |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-05-15 | 10:25 | 2437 | 23.3 | 161 | 166 | 0 | 3.8 | 0.95 | 0.25 |  | 1.2 | 5 | 0.30551 | 0.79167 | 3.1667 | 16.0941 | 12.5927 | 10 | 153.5 | 0.082037 | 7.37 | 6.66 | 7.64 | 25.6 | NR | 1408 | [22 empty] | Influent flow rate during sample collection (gpm) | 5.1 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.06 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.99 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.13 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.13 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | < 300 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-05-16 | 13:05 | 2465 | 24.6 | 212 | 207 | 0 | 3.8 | 0.95 | 0.25 |  | 1.2 | 5 | 0.30551 | 0.79167 | 3.1667 | 16.0941 | 12.118 | 10 | 199.5 | 0.060742 | 6.36 | 5.91 | 7.25 | 38.4 | NR | 1273.6 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polysulfone with a Polyamide active layer | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-05-17 | 13:25 | 2488 | 24.7 | 220 | 215 | 0 | 3.8 | 0.94 | 0.25 |  | 1.19 | 4.99 | 0.30517 | 0.78992 | 3.1933 | 15.9247 | 11.955 | 10 | 207.5 | 0.057615 | 6.26 | 5.97 | 7.27 | 38.4 | NR | 1241.6 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin film composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-05-18 | 10:15 | 2508.8 | 25.2 | 221 | 215 | 0 | 3.8 | 0.68 | 0.25 |  | 0.93 | 4.73 | 0.29639 | 0.73118 | 4.086 | 11.52 | 8.5214 | 10 | 208 | 0.040968 | 5.77 | 5.6 | 6.85 | 51.2 | NR | 1075.2 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate, Qp (gpm) | 0.88542 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-05-19 | 9:55 | 2532.4 | 24.9 | 220 | 215 | 0 | 3.8 | 0.84 | 0.3 |  | 1.14 | 4.94 | 0.30517 | 0.73684 | 3.3333 | 14.2306 | 10.6202 | 10 | 207.5 | 0.051182 | 5.51 | 5.11 | 6.32 | 7.68 | NR | 1107.2 | [21 empty] | Sampling date | MM/DD/YY | 1998-05-21 | 1998-05-21 | 1998-05-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-19 | 1998-06-19 | 1998-06-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Neutral | Feed flow rate, QF (gpm) | 1.1806 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-05-20 | 15:20 | 2561.9 | 25.1 | 164 | 159 | 0 | 3.8 | 0.96 | 0.3 | X | 1.26 | 5.06 | 0.30922 | 0.7619 | 3.0159 | 16.2635 | 12.0659 | 10 | 151.5 | 0.079643 | 5.74 | 5.14 | 6.95 | 19.2 | NR | 1120 | [21 empty] | Sampling time | hh:mm | 8:55 | 8:55 | 8:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:05 | 8:05 | 8:05 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:22 | 9:22 | 9:22 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:20 | 9:20 | 9:20 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:20 | 9:20 | 9:20 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.29514 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-05-21 | 8:55 | 2579.5 | 24.8 | 163 | 158 | 0 | 3.8 | 1 | 0.3 |  | 1.3 | 5.1 | 0.31057 | 0.76923 | 2.9231 | 16.9412 | 12.6806 | 10 | 150.5 | 0.084256 | 6.5 | 6.49 | 6.89 | 12.8 | NR | 1100.8 | [21 empty] | Operation time | hh.hh | 2579.5 | 2579.5 | 2579.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2746.1 | 2746.1 | 2746.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2967.2 | 2967.2 | 2967.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3082.3 | 3082.3 | 3082.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3082.3 | 3082.3 | 3082.3 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | NA | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-05-22 | 8:50 | 2603.4 | 24.7 | 163 | 158 | 0 | 3.8 | 1 | 0.25 |  | 1.25 | 5.05 | 0.3072 | 0.8 | 3.04 | 16.9412 | 12.7181 | 10 | 150.5 | 0.084506 | 6.28 | 6.15 | 7.51 | 12.8 | NR | 1161.71 | [21 empty] | pH | --- | 6.5 | 6.49 | 6.89 | --- | --- | --- | --- | --- | pH | --- | 5.62 | 5.38 | 6.86 | --- | --- | --- | --- | --- | pH | --- | 6.35 | 7.23 | 7.55 | --- | --- | --- | --- | --- | pH | --- | 6.25 | 7.44 | 6.75 | --- | --- | --- | --- | --- | pH | --- | 6.25 | 7.44 | 6.75 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 3.9" x 40" | Maximum influent flow rate, QI, max (gpm) | 15 | Calcium (mg/L) | 51.5 |  |  |  | 1998-05-23 | 11:10 | 2629.6 | 25.4 | 160 | 155 | 0 | 3.8 | 1 | 0.3 |  | 1.3 | 5.1 | 0.31057 | 0.76923 | 2.9231 | 16.9412 | 12.4577 | 10 | 147.5 | 0.084459 | 7.48 | 6.41 | 7.7 | 12.8 | NR | 1280 | [21 empty] | Temperature | oC | 24.8 | 24.8 | 24.8 | --- | --- | --- | --- | --- | Temperature | oC | 22.3 | 22.3 | 22.3 | --- | --- | --- | --- | --- | Temperature | oC | 23.4 | 23.4 | 23.4 | --- | --- | --- | --- | --- | Temperature | oC | 26.7 | 26.7 | 26.7 | --- | --- | --- | --- | --- | Temperature | oC | 26.7 | 26.7 | 26.7 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Design influent flow rate2, QI (gpm) | 4.8 | Barium (mg/L) | 0.016 |  |  |  | 1998-05-24 | 11:50 | 2654.2 | 24.7 | 158 | 153 | 0 | 3.8 | 1 | 0.25 |  | 1.25 | 5.05 | 0.3072 | 0.8 | 3.04 | 16.9412 | 12.7181 | 10 | 145.5 | 0.08741 | 6.5 | 6.08 | 7.45 | 12.8 | NR | 1164.8 | [21 empty] | Alkalinity | mg/L as CaCO3 | BMRL | 11.7 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | 16 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 5 | 22 | 119 | 94.4737 | 20.6103 | 77.2727 | 85.832 | 94.1747 | Alkalinity | mg/L as CaCO3 | BMRL | 17 | 130 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | 20 | 45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | 22 | Design recycle flow rate, QR (gpm) | 3.6194 | Strontium (mg/L) | 0.247 |  |  |  | 1998-05-25 | 10:05 | 2676.4 | 23.3 | 155 | 150 | 0 | 3.8 | 0.95 | 0.25 |  | 1.2 | 5 | 0.30551 | 0.79167 | 3.1667 | 16.0941 | 12.5927 | 10 | 142.5 | 0.08837 | 6.15 | 6.1 | 7.38 | 12.8 | NR | 1030.4 | [21 empty] | Total dissolved solids | mg/L | 12.8 | NR | 1100.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 12.8 | NR | 1062.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 9.4 | 206 | 708 | 1044.1368 | -47.477 | 95.4369 | 944.1987 | 99.0044 | Total dissolved solids | mg/L | 12.3 | 239 | 707 | 1345.8294 | -90.3578 | 94.8536 | 1202.3515 | 98.977 | Total dissolved solids | mg/L | 12.3 | 239 | 707 | 1345.8294 | -90.3578 | 94.8536 | 1202.3515 | 98.977 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 220 | Recycle ratio, r | 3.0659 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-05-26 | 9:10 | 2699.6 | 22.7 | 160 | 155 | 0 | 3.8 | 0.94 | 0.23 |  | 1.17 | 4.97 | 0.30382 | 0.80342 | 3.2479 | 15.9247 | 12.6831 | 10 | 147.5 | 0.085987 | 7.82 | 6.98 | 7.81 | 12.8 | NR | 1049.6 | [21 empty] | Total hardness | mg/L as CaCO3 | BMRL | 180 | 569 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 3.32 | 139 | 426 | 568.6533 | -33.4867 | 97.6115 | 515.1589 | 99.3555 | Total hardness | mg/L as CaCO3 | 0.405 | 136 | 505 | 714.0629 | -41.3986 | 99.7022 | 645.1356 | 99.9372 | Total hardness | mg/L as CaCO3 | BMRL | 150 | 503 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | BMRL | 149 | 503 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 1 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-05-27 | 8:40 | 2722.6 | 21.9 | 162 | 157 | 0 | 3.8 | 0.95 | 0.23 |  | 1.18 | 4.98 | 0.30416 | 0.80508 | 3.2203 | 16.0941 | 13.1247 | 10 | 149.5 | 0.087791 | 5.58 | 5.52 | 7 | 12.8 | NR | 1004.8 | [21 empty] | Calcium hardness | mg/L as CaCO3 | BMRL | 171 | 534 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 3.32 | 126 | 382 | 514.4867 | -34.6824 | 97.3651 | 466.1178 | 99.2877 | Calcium hardness | mg/L as CaCO3 | 0.405 | 119 | 439 | 624.5892 | -42.2754 | 99.6597 | 564.3035 | 99.9282 | Calcium hardness | mg/L as CaCO3 | BMRL | 139 | 464 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 138 | 464 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-05-28 | 8:05 | 2746.1 | 22.3 | 162 | 157 | 0 | 3.8 | 0.96 | 0.3 |  | 1.26 | 5.06 | 0.30922 | 0.7619 | 3.0159 | 16.2635 | 13.107 | 10 | 149.5 | 0.087672 | 5.62 | 5.38 | 6.86 | 12.8 | NR | 953.6 | [21 empty] | Turbidity | ntu | 0.05 | 2.6 | 2.7 | 11.137 | -312.4799 | 98.0769 | 10.0489 | 99.5024 | Turbidity | ntu | 0 | 0.5 | 2.3 | 2.0833 | 9.4203 | 100 | 1.8862 | 100 | Turbidity | ntu | 0.05 | 0.95 | 0.45 | 4.7868 | -963.7427 | 94.7368 | 4.3293 | 98.8451 | Turbidity | ntu | 0 | 0.6 | 0.35 | 3.5294 | -908.4034 | 100 | 3.1497 | 100 | Turbidity | ntu | 0 | 0.6 | 0.35 | 3.5294 | -908.4034 | 100 | 3.1497 | 100 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 15 | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-05-29 | 9:00 | 2770.5 | 23.2 | 160 | 155 | 0 | 3.9 | 0.96 | 0.3 |  | 1.26 | 5.16 | 0.31597 | 0.7619 | 3.0952 | 16.2635 | 12.7629 | 10.727 | 146.773 | 0.086957 | 5.6 | 6.16 | 6.57 | 44.8 | 326.4 | 953.6 | 1227.52 | -28.7248 | 86.2745 | 1117.4995 | 95.991 | [16 empty] | Ammonia | mg NH3-N / L | 0.025 | 0.049 | 0.077 | 0.12935 | -67.9842 | 48.9796 | 0.11911 | 79.0105 | Ammonia | mg NH3-N / L | BMRL | 0.039 | 0.065 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | 0.0628 | 0.152 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.035 | 0.044 | 0.033 | 0.087941 | -166.4884 | 20.4545 | 0.082245 | 57.4443 | Ammonia | mg NH3-N / L | BMRL | 0.047 | 0.035 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | NA | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-05-30 | 7:00 | 2792.5 | 25.3 | 160 | 155 | 0 | 3.9 | 0.97 | 0.3 |  | 1.27 | 5.17 | 0.31631 | 0.76378 | 3.0709 | 16.4329 | 12.1197 | 11.7848 | 145.7152 | 0.083174 | 5.85 | 6.76 | 6.69 | 57.6 | 364.8 | 972.8 | 1358.08 | -39.6053 | 84.2105 | 1236.0814 | 95.3401 | [16 empty] | Total organic carbon | mg/L | 0.28 | 1.86 | 6.18 | 7.1496 | -15.6888 | 84.9462 | 6.4754 | 95.6759 | Total organic carbon | mg/L | 0.47 | 2.27 | 8.04 | 7.97 | 0.87065 | 79.2952 | 7.2603 | 93.5265 | Total organic carbon | mg/L | 0.31 | 1.7 | 6.1 | 7.6258 | -25.0129 | 81.7647 | 6.9192 | 95.5197 | Total organic carbon | mg/L | 0.38 | 2.91 | 8.06 | 15.2624 | -89.3592 | 86.9416 | 13.6611 | 97.2184 | Total organic carbon | mg/L | 0.26 | 2.81 | 8.48 | 15.26 | -79.9528 | 90.7473 | 13.6461 | 98.0947
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 16.5 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-05-31 | 10:30 | 2820 | 26.2 | 167 | 162 | 0 | 3.9 | 0.98 | 0.3 |  | 1.28 | 5.18 | 0.31665 | 0.76562 | 3.0469 | 16.6024 | 11.9232 | 8.9005 | 155.5995 | 0.076627 | 6.02 | 6.45 | 6.67 | 38.4 | 268.8 | 902.4 | 1021.44 | -13.1915 | 85.7143 | 928.4497 | 95.8641 | [16 empty] | UV254 | cm-1 | 0.018 | 0.048 | 0.128 | 0.14843 | -15.9647 | 62.5 | 0.13563 | 86.729 | UV254 | cm-1 | 0.019 | 0.052 | 0.113 | 0.1565 | -38.4956 | 63.4615 | 0.14349 | 86.7586 | UV254 | cm-1 | 0.016 | 0.054 | 0.155 | 0.216 | -39.3548 | 70.3704 | 0.19668 | 91.8651 | UV254 | cm-1 | 0.02 | 0.06 | 0.156 | 0.25529 | -63.6501 | 66.6667 | 0.22998 | 91.3035 | UV254 | cm-1 | 0.017 | 0.058 | 0.158 | 0.25818 | -63.4028 | 70.6897 | 0.23223 | 92.6796
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.002 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-06-01 | 10:00 | 2843.6 | 25.4 | 155 | 150 | 0 | 4 | 0.96 | 0.3 |  | 1.26 | 5.26 | 0.32272 | 0.7619 | 3.1746 | 16.2635 | 11.9594 | 10.9922 | 141.5078 | 0.084514 | 6.34 | 7.48 | 7.16 | 44.8 | 332.8 | 870.4 | 1254.4 | -44.1176 | 86.5385 | 1144.0183 | 96.084 | [16 empty] | SUVA | L/(mg*m) | 6.4286 | 2.5806 | 2.0712 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.0426 | 2.2907 | 1.4055 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.1613 | 3.1765 | 2.541 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.2632 | 2.0619 | 1.9355 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 6.5385 | 2.0641 | 1.8632 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | NA | Manufacturer reported TDS rejection, RejTDS (decimal) | NA | [5 empty] | 1998-06-02 | 10:00 | 2866.7 | 25.7 | 155 | 150 | 0 | 4 | 0.98 | 0.3 |  | 1.28 | 5.28 | 0.3234 | 0.76562 | 3.125 | 16.6024 | 12.1007 | 8.9181 | 143.5819 | 0.084278 | 5.82 | 6.64 | 6.65 | 57.6 | 288 | 1024 | 1040.64 | -1.625 | 80 | 949.4109 | 93.9331 | [16 empty] | Bromide | mg/L | BMRL | 80 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 70 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 50 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 70 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 70 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | NA | Feed TDS, TDSF (mg/L) | NA | [5 empty] | 1998-06-03 | 8:13 | 2889.8 | 24.8 | 162 | 157 | 0 | 3.8 | 1 | 0.25 |  | 1.25 | 5.05 | 0.3072 | 0.8 | 3.04 | 16.9412 | 12.6806 |  | 159.5 | 0.079502 | 5.95 | 5.73 | 7.02 | 12.8 | NR | 1062.4 |  |  | #VALUE! |  | #DIV/0! | [16 empty] | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | #VALUE! | [5 empty] | 1998-06-17 | 9:30 | 2919.4 | 22.2 | 185 | 180 | 0 | 3.8 | 0.94 | 0.23 |  | 1.17 | 4.97 | 0.30382 | 0.80342 | 3.2479 | 15.9247 | 12.8719 | 9.8106 | 172.6894 | 0.074538 | 6.33 | 7.3 | 7.82 | 23 | 236 | 866 | 1106.5217 | -27.7739 | 90.2542 | 1004.0559 | 97.7093 | [16 empty] | SDS-Free Cl2 residual | mg/L | 0.75 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.6 | 0.9 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | 0.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | 0.5 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | #VALUE! | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-06-18 | 9:23 | 2943.2 | 23.1 | 171 | 166 | 0 | 3.8 | 0.95 | 0.23 |  | 1.18 | 4.98 | 0.30416 | 0.80508 | 3.2203 | 16.0941 | 12.6673 | 9.3286 | 159.1714 | 0.079583 | 6.2 | 7.32 | 7.75 | 12 | 213 | 806 | 1043.2174 | -29.4314 | 94.3662 | 944.8583 | 98.73 | [16 empty] | SDS-Cl2 demand | mg/L | 0.45 | 2.35 | --- | 8.7109 | --- | 80.8511 | 7.9002 | 94.3039 | SDS-Cl2 demand | mg/L | 0.4 | 2.1 | --- | 7.4833 | --- | 80.9524 | 6.8131 | 94.1289 | SDS-Cl2 demand | mg/L | 0.3 | 2.2 | --- | 10.3 | --- | 86.3636 | 9.3342 | 96.786 | SDS-Cl2 demand | mg/L | 0.3 | 2.5 | --- | 13.2412 | --- | 88 | 11.8488 | 97.4681 | SDS-Cl2 demand | mg/L | 0.3 | 2.5 | --- | 13.2412 | --- | 88 | 11.8488 | 97.4681
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | NA | Influent TDS, TDSI (mg/L) | #VALUE! | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-06-19 | 9:22 | 2967.2 | 23.4 | 168 | 163 | 0 | 3.8 | 0.96 | 0.23 |  | 1.19 | 4.99 | 0.30449 | 0.80672 | 3.1933 | 16.2635 | 12.6877 | 9.1935 | 156.3065 | 0.081172 | 6.35 | 7.23 | 7.55 | 9.4 | 206 | 708 | 1026.5913 | -44.9988 | 95.4369 | 928.7452 | 98.9879 | [16 empty] | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | 6 | Osmotic pressure gradient, Dp (psi) | #VALUE! | [5 empty] | 1998-06-20 | 12:05 | 2993.8 | 24.7 | 189 | 184 | 0 | 3.8 | 1 | 0.23 |  | 1.23 | 5.03 | 0.30584 | 0.81301 | 3.0894 | 16.9412 | 12.7181 | 9.7432 | 176.7568 | 0.071953 | 6.16 | 6.95 | 7.54 | 10.7 | 213 | 910 | 1092.5652 | -20.0621 | 94.9765 | 985.0239 | 98.9137 | [16 empty] | SDS-Chlorination pH | --- | 7.73 | 7.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.61 | 7.57 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.34 | 7.44 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.33 | 7.36 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.33 | 7.36 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NA | [7 empty] | 1998-06-21 | 11:55 | 3017.6 | 25 | 194 | 188 | 0 | 3.8 | 1 | 0.23 |  | 1.23 | 5.03 | 0.30584 | 0.81301 | 3.0894 | 16.9412 | 12.6058 | 10.3742 | 180.6258 | 0.06979 | 7.35 | 7.61 | 8.61 | 8.6 | 224 | 650 | 1160.5217 | -78.5418 | 96.1607 | 1046.0166 | 99.1778 | [16 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | NA | Estimate the Required Influent Pressure | [6 empty] | 1998-06-22 | 9:10 | 3038.9 | 25.8 | 211 | 206 | 0 | 3.8 | 1.1 | 0.23 |  | 1.33 | 5.13 | 0.30922 | 0.82707 | 2.8571 | 18.6353 | 13.5424 | 11.5282 | 196.9718 | 0.068753 | 6.73 | 6.95 | 7.99 | 9.7 | 233 | 690 | 1300.9565 | -88.5444 | 95.8369 | 1162.5177 | 99.1656 | [16 empty] | SDS-TOX | mg Cl- /L | BMRL | 103 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 138 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 104 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 132 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 115 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | 1500 mg/L NaCl | Estimated system pressure losses, DPloss (psi) | NA | [5 empty] | 1998-06-23 | 9:20 | 3058.3 | 25.1 | 195 | 190 | 0 | 3.8 | 1 | 0.23 |  | 1.23 | 5.03 | 0.30584 | 0.81301 | 3.0894 | 16.9412 | 12.5686 | 10.8558 | 181.6442 | 0.069194 | 6.38 | 7.18 | 7.75 | 10.6 | 236 | 728 | 1216 | -67.033 | 95.5085 | 1096.1789 | 99.033 | [16 empty] | SDS-CHCl3 | mg/L | 2.94 | 25.7 | --- | 101.8965 | --- | 88.5603 | 92.1852 | 96.8108 | SDS-CHCl3 | mg/L | 2.75 | 29.5 | --- | 114.2083 | --- | 90.678 | 103.6616 | 97.3471 | SDS-CHCl3 | mg/L | 3.44 | 27.2 | --- | 128.4926 | --- | 87.3529 | 116.4147 | 97.045 | SDS-CHCl3 | mg/L | 2.28 | 29.6 | --- | 162.9859 | --- | 92.2973 | 145.6951 | 98.4351 | SDS-CHCl3 | mg/L | 2.29 | 28.6 | --- | 157.0547 | --- | 91.993 | 140.4032 | 98.369
|  | (e.g., solute type and concentration) |  | Design permeate pressure, Pp (psi) | NA | [5 empty] | 1998-06-24 | 9:20 | 3082.3 | 26.7 | 193 | 187 | 0 | 3.8 | 1.1 | 0.23 |  | 1.33 | 5.13 | 0.30922 | 0.82707 | 2.8571 | 18.6353 | 13.1868 | 11.7037 | 178.2963 | 0.07396 | 6.25 | 7.44 | 6.75 | 12.3 | 239 | 707 | 1323.2174 | -87.1595 | 94.8536 | 1182.6707 | 98.96 | [16 empty] | SDS-BDCM | mg/L | BMRL | 13.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 8.69 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 13.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 14.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 14.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | 32 | Required influent pressure, PI (psi) | #VALUE! | [5 empty] | 1998-06-25 | 9:15 | 3106.2 | 26.7 | 184 | 179 | 0 | 3.8 | 1.03 | 0.23 |  | 1.26 | 5.06 | 0.30686 | 0.81746 | 3.0159 | 17.4494 | 12.3477 | 10.3482 | 171.1518 | 0.072145 | 5.92 | 6.41 | 6.85 | 15.7 | 226 | 630 | 1167.7783 | -85.3616 | 93.0531 | 1050.5213 | 98.5055 | [16 empty] | SDS-DBCM | mg/L | BMRL | 5.42 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1.66 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 3.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 5.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 4.69 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-06-26 | 9:03 | 3130 | 27.3 | 183 | 178 | 0 | 3.8 | 1.05 | 0.4 |  | 1.45 | 5.25 | 0.31901 | 0.72414 | 2.6207 | 17.7882 | 12.3662 | 7.4711 | 173.0289 | 0.071469 | 5.95 | 6.64 | 7.08 | 12 | 241 | 644 | 842.125 | -30.7648 | 95.0207 | 759.1125 | 98.4192 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7 | [7 empty] | 1998-06-27 | 12:10 | 3157.2 | 28.9 | 200 | 195 | 0 | 3.8 | 1.09 | 0.4 |  | 1.49 | 5.29 | 0.32036 | 0.73154 | 2.5503 | 18.4659 | 12.2443 | 8.6638 | 188.8362 | 0.064841 | 6.45 | 6.35 | 7.78 | 12.7 | 272 | 788 | 978.5925 | -24.1869 | 95.3309 | 879.0818 | 98.5553 | [16 empty] | SDS-THM4 | mg/L | 2.94 | 44.22 | --- | 182.4183 | --- | 93.3514 | 164.8048 | 98.2161 | SDS-THM4 | mg/L | 2.75 | 39.85 | --- | 157.3333 | --- | 93.0991 | 142.706 | 98.073 | SDS-THM4 | mg/L | 3.44 | 44.2 | --- | 217.9663 | --- | 92.2172 | 197.2467 | 98.256 | SDS-THM4 | mg/L | 2.28 | 49.48 | --- | 279.9271 | --- | 95.3921 | 250.0543 | 99.0882 | SDS-THM4 | mg/L | 2.29 | 47.59 | --- | 268.7606 | --- | 95.1881 | 240.0903 | 99.0462
|  | Acceptable range of operating pressures | 250 max | [7 empty] | 1998-06-28 | 12:12 | 3181.2 | 29 | 197 | 192 | 0 | 3.8 | 1.14 | 0.4 |  | 1.54 | 5.34 | 0.32205 | 0.74026 | 2.4675 | 19.3129 | 12.7681 | 7.3596 | 187.1404 | 0.068228 | 5.85 | 6.54 | 6.76 | 25 | 239 | 706 | 848.9 | -20.2408 | 89.5397 | 760.9556 | 96.7147 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 2.46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 2.93 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 3.69 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 35896 | [7 empty] | 1998-06-29 | 10:00 | 3197 | 29 | 197 | 192 | 0 | 3.8 | 1.14 | 0.35 |  | 1.49 | 5.29 | 0.31867 | 0.7651 | 2.5503 | 19.3129 | 12.7681 | 8.9111 | 185.5889 | 0.068798 | 6.39 | 6.79 | 7.8 | 12.4 | 247 | 729 | 1011.1257 | -38.7004 | 94.9798 | 903.5125 | 98.6276 | [16 empty] | SDS-DCAA* | mg/L | 2.28 | 11.1 | --- | 40.6278 | --- | 79.4595 | 36.8645 | 93.8152 | SDS-DCAA* | mg/L | 2.47 | 14.6 | --- | 53.0117 | --- | 83.0822 | 48.2292 | 94.8786 | SDS-DCAA* | mg/L | 3.72 | 14.7 | --- | 61.5095 | --- | 74.6939 | 55.928 | 93.3486 | SDS-DCAA* | mg/L | 2.34 | 20 | --- | 106.2224 | --- | 88.3 | 95.0454 | 97.538 | SDS-DCAA* | mg/L | 3.34 | 22.6 | --- | 116.6341 | --- | 85.2212 | 104.4445 | 96.8021
|  | Typical pressure drop across a single element (psi) | [8 empty] | 1998-06-30 | 9:47 | 3206.9 | 30.3 | 203 | 197 | 0 | 3.8 | 1.15 | 0.35 |  | 1.5 | 5.3 | 0.31901 | 0.76667 | 2.5333 | 19.4824 | 12.3946 | 10.8777 | 189.1223 | 0.065537 | 9.22 | 8 | 8.03 | 12.3 | 297 | 703 | 1232.4429 | -75.3119 | 95.8586 | 1100.0689 | 98.8819 | [16 empty] | SDS-TCAA* | mg/L | 1.08 | 7.9 | --- | 30.7322 | --- | 86.3291 | 27.8222 | 96.1182 | SDS-TCAA* | mg/L | 1.52 | 13.3 | --- | 50.6033 | --- | 88.5714 | 45.9588 | 96.6927 | SDS-TCAA* | mg/L | 3.59 | 14.2 | --- | 59.4321 | --- | 74.7183 | 54.0387 | 93.3566 | SDS-TCAA* | mg/L | 2.18 | 18.9 | --- | 100.5329 | --- | 88.4656 | 89.9509 | 97.5765 | SDS-TCAA* | mg/L | 2.55 | 22 | --- | 116.9618 | --- | 88.4091 | 104.6519 | 97.5634
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-07-01 | 8:15 | 3230.4 | 29 | 190 | 195 | 0 | 3.8 | 1.15 | 0.35 |  | 1.5 | 5.3 | 0.31901 | 0.76667 | 2.5333 | 19.4824 | 12.8801 | 8.8336 | 183.6664 | 0.070128 | 5.91 | 6.72 | 7.22 | 16.8 | 248 | 660 | 1007.6571 | -52.6753 | 93.2258 | 900.1585 | 98.1337 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | 1.07 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [55 empty] | SDS-DBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.29 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1.3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1.05 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0.1 | [55 empty] | SDS-BCAA* | mg/L | BMRL | 5.89 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 7.34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 5.03 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 7.63 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 7.35 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [56 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [56 empty] | SDS-CDBAA | mg/L | BMRL | 2.14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 2.82 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.41 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-DCBAA | mg/L | BMRL | 7.61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 10.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 7.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 12.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 13.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5 | mg/L | 3.36 | 20.3 | --- | 77.0122 | --- | 83.4483 | 69.7842 | 95.1852 | SDS-HAA5 | mg/L | 3.99 | 31.65 | --- | 119.24 | --- | 87.3934 | 108.3345 | 96.317 | SDS-HAA5 | mg/L | 7.31 | 28.9 | --- | 120.9416 | --- | 74.7059 | 109.9667 | 93.3525 | SDS-HAA5 | mg/L | 5.82 | 42.9 | --- | 223.9376 | --- | 86.4336 | 200.4698 | 97.0968 | SDS-HAA5 | mg/L | 6.94 | 48.29 | --- | 250.1753 | --- | 85.6285 | 224.005 | 96.9019
[59 empty] | SDS-HAA6 | mg/L | 3.36 | 26.19 | --- | 102.6209 | --- | 87.1707 | 92.8797 | 96.3824 | SDS-HAA6 | mg/L | 3.99 | 38.99 | --- | 149.8233 | --- | 89.7666 | 136.0239 | 97.0667 | SDS-HAA6 | mg/L | 7.31 | 33.93 | --- | 147.4153 | --- | 78.4556 | 133.8835 | 94.54 | SDS-HAA6 | mg/L | 5.82 | 50.53 | --- | 268.82 | --- | 88.4821 | 240.5231 | 97.5803 | SDS-HAA6 | mg/L | 6.94 | 55.64 | --- | 293.4106 | --- | 87.527 | 262.5885 | 97.3571
[59 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[59 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[59 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[60 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[60 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[59 empty] | Qp/QT (THM4), % | -67.2965 | 19.9128 |  | Qp/QT (HAA5), % | -198.9374 | -39.5514 |  |  |  | Qp/QT (THM4), % | -86.6577 | 10.3774 |  | Qp/QT (HAA5), % | -80.8026 | 16.8113 |  |  |  | Qp/QT (THM4), % | -68.2041 | 20.1178 |  | Qp/QT (HAA5), % | -116.2575 | 8.8004 |  |  |  | Qp/QT (THM4), % | -47.7119 | 28.5593 |  | Qp/QT (HAA5), % | -29.9353 | 42.8803 |  |  |  | Qp/QT (THM4), % | -53.8852 | 25.585 |  | Qp/QT (HAA5), % | -13.8089 | 51.4873
[59 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 33.613 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 40.613 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 29.2405 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 24.2663
[59 empty] | SDS-HAA5b, mg/L | NA | 16.9268 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 28.7796 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 24.5566 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 32.3102 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 37.7106 |  | SDS-HAA5b, mg/L | NA | 27
[59 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE!
[59 empty] | SDS-CDb, mg/L | NA | 1.9717 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.9236 |  | SDS-CDb, mg/L | NA | 1.8142 |  |  |  | SDS-CDb, mg/L | NA | 1.8178 |  | SDS-CDb, mg/L | NA | 2.0328 |  |  |  | SDS-CDb, mg/L | NA | 1.8717 |  | SDS-CDb, mg/L | NA | 1.5566 |  |  |  | SDS-CDb, mg/L | NA | 1.9371 |  | SDS-CDb, mg/L | NA | 1.3673
[59 empty] | TOCb, mg/L | NA | 1.5454 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 2.0832 |  | TOCb, mg/L | NA | 1.9674 |  |  |  | TOCb, mg/L | NA | 1.4204 |  | TOCb, mg/L | NA | 1.5777 |  |  |  | TOCb, mg/L | NA | 2.1874 |  | TOCb, mg/L | NA | 1.8251 |  |  |  | TOCb, mg/L | NA | 2.1576 |  | TOCb, mg/L | NA | 1.4971
[59 empty] | UV254 b, cm-1 | NA | 0.042026 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.048575 |  | UV254 b, cm-1 | NA | 0.046452 |  |  |  | UV254 b, cm-1 | NA | 0.046355 |  | UV254 b, cm-1 | NA | 0.050656 |  |  |  | UV254 b, cm-1 | NA | 0.048576 |  | UV254 b, cm-1 | NA | 0.042848 |  |  |  | UV254 b, cm-1 | NA | 0.04751 |  | UV254 b, cm-1 | NA | 0.03689
[59 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE!
[59 empty] | Alkb, mg/L CaCO3 | NA | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | #VALUE! |  | Alkb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | 18.58 |  | Alkb, mg/L CaCO3 | NA | 20.5039 |  |  |  | Alkb, mg/L CaCO3 | NA | #VALUE! |  | Alkb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | #VALUE! |  | Alkb, mg/L CaCO3 | NA | #VALUE!
[59 empty] | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 124.92 |  | T-Hdb, mg/L CaCO3 | NA | 116.1905 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 108.7213 |  | T-Hdb, mg/L CaCO3 | NA | 124.0671 |  |  |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | #VALUE!
[59 empty] | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 113.2691 |  | Ca-Hdb, mg/L CaCO3 | NA | 105.3759 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 95.1413 |  | Ca-Hdb, mg/L CaCO3 | NA | 108.5632 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE!
[59 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[59 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[59 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[59 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[59 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[59 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[59 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[59 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[59 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[59 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on AA13: Carollo Engineers: Switched Scale inhibitor to Hypersperse SI 300 which is a proprietary organo-phosphonic acid.
Note on AA26: Carollo Engineers: WTP maintenance to settling basins prior to NF. Required pilot plant shut down.
Note on AA33: Carollo Engineers: Power outage due to electrical storm shut down pilot plant.
Note on AA39: Carollo Engineers: Power outage due to electrical storm shut down pilot plant.
Note on AA40: Carollo Engineers: Power outage due to electrical storm shut down pilot plant.
Note on AI5: Carollo Engineers: Estimated osmotic pressure is representative of the 4th quarter data where TDS in the feed stream was measured appropriately.
Note on AM6: Carollo Engineers: pH was controlled by a metering pump manually. Daily variations in alkalinity caused fluctuations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of erratic permeate TDS concentrations.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AP21: Carollo Engineers: Here recognition was made as to why the ERRORmb was previously so high. Previous feed TDS samples are representative of the "bulk" concentration rather than the feed.
Note on AR7: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS7: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT7: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU7: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV7: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CJ17: Carollo Engineers: At this point in the study, recongnition was made as to why ERRORmb was perviously so high. These concentrations are not "bulk" TDS Concentrations but rather feed concentration is as it should be.
Note on CJ22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CU17: Carollo Engineers: At this point in the study, recongnition was made as to why ERRORmb was perviously so high. These concentrations are not "bulk" TDS Concentrations but rather feed concentration is as it should be.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DA10: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.

## NF200 1st Quarter
FIELD-SET 1: 1st QUARTER SEBST RESULTS (FILE: sebst-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: SEBST Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 1-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 1-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 1-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 1-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Dow FilmTec | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | NF200B | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.17486 | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.95 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.88 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.9 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | NF200B-4040 |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-01-10 | 11:05 | 57.6 | 6.3 | 87 | 84 | 0.5 | 3.7 | 0.74 | 0.26 |  | 1 | 4.7 | 0.26215 | 0.74 | 3.7 | 13.4886 | 17.4442 | 5 | 80 | 0.21805 | 7.63 | 7.72 | 6.04 | 17 | NR | 1414 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.68 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.58 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.6 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.61 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.61 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 400 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-01-11 | 11:44 | 82.2 | 7.3 | 86 | 83 | 2.1 | 3.7 | 0.67 | 0.26 |  | 0.93 | 4.63 | 0.26004 | 0.72043 | 3.9785 | 12.2127 | 15.334 | 5 | 77.4 | 0.19811 | 7.27 | 6.47 | 6.54 | 22 | NR | 1088 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polypiperazine | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-01-12 | 11:30 | 105.8 | 7.5 | 84 | 80 | 1.5 | 3.6 | 0.6 | 0.2 |  | 0.8 | 4.4 | 0.24823 | 0.75 | 4.5 | 10.9367 | 13.651 | 5 | 75.5 | 0.18081 | 6.24 | 5.14 | 5.86 | 20 | NR | 1229 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | Design flux, FW (gfd) | 12 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-01-13 | 9:45 | 128.2 | 7.2 | 83 | 80 | 2 | 3.81 | 0.7 | 0.21 |  | 0.91 | 4.72 | 0.26458 | 0.76923 | 4.1868 | 12.7595 | 16.0681 | 5 | 74.5 | 0.21568 | 3.68 | 2.85 | 3.07 | 41 | NR | 1318 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Permeate flow rate, Qp (gpm) | 0.65833 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-01-14 | 11:00 | 153.5 | 7.5 | 83 | 80 | 1.5 | 3.8 | 0.68 | 0.23 |  | 0.91 | 4.71 | 0.26458 | 0.74725 | 4.1758 | 12.3949 | 15.4712 | 5 | 75 | 0.20628 | 4.02 | 2.93 | 3.09 | 45 | NR | 1075 | [21 empty] | Sampling date | MM/DD/YY | 1998-01-18 | 1998-01-18 | 1998-01-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-01-25 | 1998-01-25 | 1998-01-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-01 | 1998-02-01 | 1998-02-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-09 | 1998-02-09 | 1998-02-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-09 | 1998-02-09 | 1998-02-09 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Feed flow rate, QF (gpm) | 0.87778 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-01-15 | 10:30 | 176.1 | 8.2 | 83 | 80 | 1.5 | 3.78 | 0.68 | 0.3 |  | 0.98 | 4.76 | 0.2676 | 0.69388 | 3.8571 | 12.3949 | 15.1544 | 5 | 75 | 0.20206 | 3.24 | 2.65 | 2.78 | 52 | NR | 1114 | [21 empty] | Sampling time | hh:mm | 12:30 | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:40 | 10:40 | 10:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:25 | 12:25 | 12:25 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:31 | 10:31 | 10:31 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:31 | 10:31 | 10:31 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.21944 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-01-16 | 9:00 | 186.8 | 9 | 76 | 71 | 1 | 3.75 | 0.7 | 0.3 |  | 1 | 4.75 | 0.26639 | 0.7 | 3.75 | 12.7595 | 15.2355 | 5 | 67.5 | 0.22571 | 4.69 | 4.95 | 3.62 | 45 | NR | 1062 | [21 empty] | Operation time | hh.hh | 238 | 238 | 238 | --- | --- | --- | --- | --- | Operation time | hh.hh | 404.5 | 404.5 | 404.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 537 | 537 | 537 | --- | --- | --- | --- | --- | Operation time | hh.hh | 734.5 | 734.5 | 734.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 734.5 | 734.5 | 734.5 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-01-17 | 12:20 | 214.1 | 8.4 | 110 | 105 | 0 | 3.7 | 0.73 | 0.23 |  | 0.96 | 4.66 | 0.26004 | 0.76042 | 3.8542 | 13.3063 | 16.1728 | 5 | 102.5 | 0.15778 | 5.43 | 6.09 | 6.61 | 23 | NR | 1018 | [21 empty] | pH | --- | 7.04 | 6.88 | 6.23 | --- | --- | --- | --- | --- | pH | --- | 6.55 | 6.17 | 6.38 | --- | --- | --- | --- | --- | pH | --- | 6.69 | 6.32 | 6.53 | --- | --- | --- | --- | --- | pH | --- | 8.98 | 8.91 | 9.28 | --- | --- | --- | --- | --- | pH | --- | 8.98 | 8.91 | 9.28 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 51.5 |  |  |  | 1998-01-18 | 12:10 | 238 | 8 | 97 | 88 | 1 | 3.73 | 0.7 | 0.25 |  | 0.95 | 4.68 | 0.26215 | 0.73684 | 3.9263 | 12.7595 | 15.6926 | 5 | 86.5 | 0.18142 | 7.04 | 6.88 | 6.23 | 25 | NR | 890 | [21 empty] | Temperature | oC | 8 | 8 | 8 | --- | --- | --- | --- | --- | Temperature | oC | 7.9 | 7.9 | 7.9 | --- | --- | --- | --- | --- | Temperature | oC | 8.5 | 8.5 | 8.5 | --- | --- | --- | --- | --- | Temperature | oC | 8.2 | 8.2 | 8.2 | --- | --- | --- | --- | --- | Temperature | oC | 8.2 | 8.2 | 8.2 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 79 | Design influent flow rate2, QI (gpm) | 4.5 | Barium (mg/L) | 0.016 |  |  |  | 1998-01-19 | 9:15 | 259.1 | 7.4 | 101 | 97 | 1.5 | 3.74 | 0.67 | 0.25 |  | 0.92 | 4.66 | 0.26185 | 0.72826 | 4.0652 | 12.2127 | 15.2888 | 5 | 92.5 | 0.16528 | 6.58 | 5.91 | 5.9 | 18 | NR | 1184 | [21 empty] | Alkalinity | mg/L as CaCO3 | 13 | 18 | NA | 32.2308 | #VALUE! | 27.7778 | 30.7864 | 57.7736 | Alkalinity | mg/L as CaCO3 | 12 | 29 | NA | 77.3846 | #VALUE! | 58.6207 | 72.7363 | 83.5021 | Alkalinity | mg/L as CaCO3 | 21 | 28 | NA | 47.9231 | #VALUE! | 25 | 45.9741 | 54.3221 | Alkalinity | mg/L as CaCO3 | 6.1 | 10.1 | NA | 22.1 | #VALUE! | 39.604 | 20.9156 | 70.8352 | Alkalinity | mg/L as CaCO3 | 7.1 | 10.4 | NA | 20.3 | #VALUE! | 31.7308 | 19.3229 | 63.256 | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | 16.5 | Design recycle flow rate, QR (gpm) | 3.6222 | Strontium (mg/L) | 0.247 |  |  |  | 1998-01-20 | 8:47 | 282.6 | 7.3 | 103 | 100 | 1 | 3.69 | 0.67 | 0.23 |  | 0.9 | 4.59 | 0.25761 | 0.74444 | 4.1 | 12.2127 | 15.334 | 5 | 95.5 | 0.16057 | 7.06 | 6.43 | 6.18 | 61 | NR | 1165 | [21 empty] | Total dissolved solids | mg/L | 25 | NR | 890 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 34 | NR | 1056 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 160 | NR | 1075 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 78.08 | NR | 909 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 78.08 | NR | 909 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Recycle ratio, r | 4.1266 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-01-21 | 9:20 | 307.1 | 7.9 | 106 | 103 | 1 | 3.7 | 0.68 | 0.2 |  | 0.88 | 4.58 | 0.25671 | 0.77273 | 4.2045 | 12.3949 | 15.2893 | 5 | 98.5 | 0.15522 | 7.7 | 8.39 | 7.7 | 46 | NR | 1440 | [21 empty] | Total hardness | mg/L as CaCO3 | 1.88 | 132 | NA | 502.3415 | #VALUE! | 98.5758 | 464.7535 | 99.5955 | Total hardness | mg/L as CaCO3 | BMRL | 217 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 38.2 | 169 | NA | 541.2769 | #VALUE! | 77.3964 | 504.8585 | 92.4335 | Total hardness | mg/L as CaCO3 | 37.1 | 186 | NA | 632.7 | #VALUE! | 80.0538 | 588.6114 | 93.697 | Total hardness | mg/L as CaCO3 | 36.9 | 184 | NA | 625.3 | #VALUE! | 79.9457 | 581.7444 | 93.657 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-01-22 | 9:06 | 331 | 7.4 | 100 | 96 | 1.5 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.517 | 5 | 91.5 | 0.16958 | 6.35 | 5.42 | 5.78 | 24 | NR | 1229 | [21 empty] | Calcium hardness | mg/L as CaCO3 | 1.87 | 96.6 | NA | 366.2162 | #VALUE! | 98.0642 | 338.8513 | 99.4481 | Calcium hardness | mg/L as CaCO3 | BMRL | 164 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 21.9 | 101.5 | NA | 328.0538 | #VALUE! | 78.4236 | 305.891 | 92.8406 | Calcium hardness | mg/L as CaCO3 | 28 | 143 | NA | 488 | #VALUE! | 80.4196 | 453.949 | 93.8319 | Calcium hardness | mg/L as CaCO3 | 27.7 | 141 | NA | 480.9 | #VALUE! | 80.3546 | 447.3524 | 93.808 | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-01-23 | 8:55 | 354.8 | 7.9 | 101 | 97 | 1.9 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.2893 | 5 | 92.1 | 0.16601 | 6.64 | 6.23 | 6.54 | 58 | NR | 1075 | [21 empty] | Turbidity | ntu | 0.05 | 0.5 | NA | 1.7808 | #VALUE! | 90 | 1.6508 | 96.9711 | Turbidity | ntu | 0 | 0.25 | NA | 0.96154 | #VALUE! | 100 | 0.89318 | 100 | Turbidity | ntu | 0.05 | 0.8 | NA | 2.9346 | #VALUE! | 93.75 | 2.7258 | 98.1657 | Turbidity | ntu | 0.05 | 2.3 | NA | 9.05 | #VALUE! | 97.8261 | 8.3838 | 99.4036 | Turbidity | ntu | 0.05 | 2.3 | NA | 9.05 | #VALUE! | 97.8261 | 8.3838 | 99.4036 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-01-24 | 12:05 | 381.9 | 7.2 | 103 | 100 | 1.5 | 3.7 | 0.65 | 0.23 |  | 0.88 | 4.58 | 0.25761 | 0.73864 | 4.2045 | 11.8481 | 14.9204 | 5 | 95 | 0.15706 | 6.69 | 5.96 | 6.57 | 68 | NR | 1082 | [21 empty] | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-01-25 | 10:40 | 404.5 | 7.9 | 102 | 98 | 1.4 | 3.7 | 0.65 | 0.23 |  | 0.88 | 4.58 | 0.25761 | 0.73864 | 4.2045 | 11.8481 | 14.6148 | 5 | 93.6 | 0.15614 | 6.55 | 6.17 | 6.38 | 34 | NR | 1056 | [21 empty] | Total organic carbon | mg/L | 0.56 | 2 | NA | 6.0985 | #VALUE! | 72 | 5.6825 | 90.1452 | Total organic carbon | mg/L | 0.32 | 2.06 | NA | 7.0123 | #VALUE! | 84.466 | 6.5365 | 95.1044 | Total organic carbon | mg/L | 0.68 | 2.02 | NA | 5.8338 | #VALUE! | 66.3366 | 5.4608 | 87.5475 | Total organic carbon | mg/L | 0.59 | 1.84 | NA | 5.59 | #VALUE! | 67.9348 | 5.2199 | 88.6971 | Total organic carbon | mg/L | 0.46 | 1.81 | NA | 5.86 | #VALUE! | 74.5856 | 5.4603 | 91.5755
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 16 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-01-26 | 8:55 | 426.8 | 8.1 | 101 | 99 | 2.4 | 3.7 | 0.65 | 0.23 |  | 0.88 | 4.58 | 0.25761 | 0.73864 | 4.2045 | 11.8481 | 14.5287 | 5 | 92.6 | 0.1569 | 7 | 6.48 | 6.51 | 56 | NR | 1062 | [21 empty] | UV254 | cm-1 | 0.021 | 0.044 | NA | 0.10946 | #VALUE! | 52.2727 | 0.10282 | 79.5755 | UV254 | cm-1 | BMRL | 0.032 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.025 | 0.047 | NA | 0.10962 | #VALUE! | 46.8085 | 0.10349 | 75.8431 | UV254 | cm-1 | 0.022 | 0.049 | NA | 0.13 | #VALUE! | 55.102 | 0.12201 | 81.968 | UV254 | cm-1 | 0.025 | 0.05 | NA | 0.125 | #VALUE! | 50 | 0.1176 | 78.7411
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.0023 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-01-27 | 11:57 | 453.8 | 8.1 | 101 | 99 | 1.4 | 3.7 | 0.67 | 0.23 |  | 0.9 | 4.6 | 0.25822 | 0.74444 | 4.1111 | 12.2127 | 14.9757 | 5 | 93.6 | 0.16 | 7.35 | 6.38 | 6.64 | 74 | NR | 1082 | [21 empty] | SUVA | L/(mg*m) | 3.75 | 2.2 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.5534 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.6765 | 2.3267 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.7288 | 2.663 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.4348 | 2.7624 | NA | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.45 | [5 empty] | 1998-01-28 | 12:15 | 478.6 | 10.2 | 105 | 100 | 1 | 3.8 | 0.62 | 0.2 |  | 0.82 | 4.62 | 0.26094 | 0.7561 | 4.6341 | 11.3013 | 13.024 | 5 | 96.5 | 0.13496 | 6.55 | 6.03 | 6.4 | 0.01 | NR | 2810 | [21 empty] | Bromide | mg/L | 55 | 33 | --- | -29.6154 | --- | -66.6667 | -23.2602 | 336.4555 | Bromide | mg/L | BMRL | 80 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 90 | 120 | --- | 205.3846 | --- | 25 | 197.0318 | 54.3221 | Bromide | mg/L | 80 | 100 | --- | 160 | --- | 20 | 154.0781 | 48.0783 | Bromide | mg/L | 90 | 90 | --- | 90 | --- | 0 | 90 | 0
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Feed TDS, TDSF (mg/L) | 900 | [5 empty] | 1998-01-29 | 8:45 | 498.5 | 10 | 110 | 105 | 0.5 | 3.75 | 0.56 | 0.2 |  | 0.76 | 4.51 | 0.2561 | 0.73684 | 4.9342 | 10.2076 | 11.8334 | 5 | 102 | 0.11601 | 6.77 | 5.97 | 6.35 | 0.01 | NR | 2355 | [21 empty] | SDS-Cl2 dose | mg/L | 1 | 2.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 0.6 | 2.7 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.3 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.7 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.7 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | 1421.874 | [5 empty] | 1998-01-30 | 13:40 | 527.5 | 10.2 | 106 | 102 | 0 | 3.7 | 0.65 | 0.23 |  | 0.88 | 4.58 | 0.25761 | 0.73864 | 4.2045 | 11.8481 | 13.6542 | 5 | 99 | 0.13792 | 7.66 | 6.98 | 7.45 | 23 | NR | 1901 | [21 empty] | SDS-Free Cl2 residual | mg/L | 0.8 | 0.55 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.5 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | 726.042 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-01-31 | 12:25 | 550.1 | 8.7 | 110 | 106 | 0 | 3.7 | 0.65 | 0.23 |  | 0.88 | 4.58 | 0.25761 | 0.73864 | 4.2045 | 11.8481 | 14.2733 | 5 | 103 | 0.13858 | 7.34 | 7.07 | 6.92 | 97 | NR | 1037 | [21 empty] | SDS-Cl2 demand | mg/L | 0.2 | 2.25 | --- | 8.0846 | --- | 91.1111 | 7.4924 | 97.3306 | SDS-Cl2 demand | mg/L | 0.1 | 2.2 | --- | 8.1769 | --- | 95.4545 | 7.6027 | 98.6847 | SDS-Cl2 demand | mg/L | 0.8 | 1.7 | --- | 4.2615 | --- | 52.9412 | 4.011 | 80.0546 | SDS-Cl2 demand | mg/L | 0.7 | 2.2 | --- | 6.7 | --- | 68.1818 | 6.2559 | 88.8105 | SDS-Cl2 demand | mg/L | 0.7 | 2.2 | --- | 6.7 | --- | 68.1818 | 6.2559 | 88.8105
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | Not Measured | Influent TDS, TDSI (mg/L) | 1320.0764 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-02-01 | 11:12 | 573 | 8.5 | 104 | 101 | 0 | 3.7 | 0.67 | 0.23 |  | 0.9 | 4.6 | 0.25822 | 0.74444 | 4.1111 | 12.2127 | 14.7997 | 5 | 97.5 | 0.15179 | 6.69 | 6.32 | 6.53 | 164 | NR | 1075 | [21 empty] | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | Not Specified | Osmotic pressure gradient, Dp (psi) | 6.4493 | [5 empty] | 1998-02-02 | 10:25 | 595.9 | 8.2 | 105 | 100 | 0 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.1544 | 5 | 97.5 | 0.15543 | 7.8 | 8.27 | 7.9 | 184 | NR | 858 | [21 empty] | SDS-Chlorination pH | --- | 7.45 | 7.35 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.42 | 7.32 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.47 | 7.37 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.83 | 7.72 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.83 | 7.72 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15, but depends on application | [7 empty] | 1998-02-03 | 12:20 | 621.8 | 7.6 | 103 | 99 | 1.5 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.4255 | 5 | 94.5 | 0.16323 | 7.44 | 7.53 | 6.91 | 86 | NR | 832 | [21 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | -15%+20% | Estimate the Required Influent Pressure | [6 empty] | 1998-02-04 | 11:40 | 645.1 | 7.4 | 103 | 97 | 0.8 | 3.78 | 0.67 | 0.25 |  | 0.92 | 4.7 | 0.26427 | 0.72826 | 4.1087 | 12.2127 | 15.2888 | 5 | 94.2 | 0.1623 | 6.85 | 6.76 | 6.69 | 21 | NR | 954 | [21 empty] | SDS-TOX | mg Cl- /L | BMRL | 42.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 89.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 49 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 51 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | < 45% rejection of CaCl2; 70 psi, | Estimated system pressure losses, DPloss (psi) | 4 | [5 empty] | 1998-02-05 | NA | NA | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA | NA | NA | NA | [21 empty] | SDS-CHCl3 | mg/L | 1.17 | 5.31 | --- | 17.0931 | --- | 77.9661 | 15.8971 | 92.6402 | SDS-CHCl3 | mg/L | BMRL | 12.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 9.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 9.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 10.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) | 500 mg/l CaCl2 | Design permeate pressure, Pp (psi) | 1 | [5 empty] | 1998-02-06 | NA | NA | NA | NA | NA | NA | NA | NA | NA | [11 empty] | NA | NA | NA | NA | NA | NA | [21 empty] | SDS-BDCM | mg/L | BMRL | 2.32 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 6.26 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.3 | 9.44 | --- | 32.6077 | --- | 86.2288 | 30.3413 | 95.7154 | SDS-BDCM | mg/L | BMRL | 7.36 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 8.09 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | < 45% rejection of CaCl2 | Required influent pressure, PI (psi) | 80.0748 | [5 empty] | 1998-02-07 | 13:08 | 689.7 | 7.7 | 99 | 95 | 1.2 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.38 | 5 | 90.8 | 0.16938 | 6.78 | 6.22 | 6.47 | 143 | NR | 979 | [21 empty] | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 4.93 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 1.83 | 6.07 | --- | 18.1377 | --- | 69.8517 | 16.9572 | 89.2081 | SDS-DBCM | mg/L | BMRL | 6.46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 6.78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-02-08 | 11:54 | 712.5 | 7.8 | 113 | 110 | 1.2 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.3346 | 5 | 105.3 | 0.14563 | 7.29 | 6.24 | 7 | 129 | NR | 966 | [21 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | 1.01 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 8 | [7 empty] | 1998-02-09 | 10:31 | 734.5 | 8.2 | 121 | 118 | 1 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.1544 | 5 | 113.5 | 0.13352 | 8.98 | 8.91 | 9.28 | 78 | NR | 909 | [21 empty] | SDS-THM4 | mg/L | 1.17 | 7.63 | --- | 26.0162 | --- | 84.6658 | 24.15 | 95.1553 | SDS-THM4 | mg/L | 0 | 23.39 | --- | 89.9615 | --- | 100 | 83.566 | 100 | SDS-THM4 | mg/L | 3.13 | 25.18 | --- | 87.9377 | --- | 87.5695 | 81.7984 | 96.1735 | SDS-THM4 | mg/L | 0 | 23.52 | --- | 94.08 | --- | 100 | 87.1158 | 100 | SDS-THM4 | mg/L | 0 | 25.98 | --- | 103.92 | --- | 100 | 96.2274 | 100
|  | Acceptable range of operating pressures | 0 to 600 psi | [7 empty] | 1998-02-10 | 9:33 | 756.5 | 8.7 | 112 | 108 | 1 | 3.7 | 0.7 | 0.23 |  | 0.93 | 4.63 | 0.25913 | 0.75269 | 3.9785 | 12.7595 | 15.3712 | 5 | 104 | 0.1478 | 7.42 | 7.04 | 6.84 | 118 | NR | 896 | [21 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | 0 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3 to 10 | [7 empty] | 1998-02-11 | 9:58 | 781.9 | 7.8 | 112 | 108 | 1.2 | 3.7 | 0.67 | 0.23 |  | 0.9 | 4.6 | 0.25822 | 0.74444 | 4.1111 | 12.2127 | 15.1091 | 5 | 103.8 | 0.14556 | 7.13 | 6.68 | 6.82 | 116 | NR | 800 | [21 empty] | SDS-DCAA* | mg/L | BMRL | 5.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 5.54 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 4.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 3 to 5 psid | [7 empty] | 1998-02-12 | 13:12 | 809.2 | 8 | 115 | 111 | 0 | 3.7 | 0.68 | 0.23 |  | 0.91 | 4.61 | 0.25852 | 0.74725 | 4.0659 | 12.3949 | 15.2442 | 5 | 108 | 0.14115 | 7.16 | 6.35 | 7.2 | 138 | NR | 928 | [21 empty] | SDS-TCAA* | mg/L | BMRL | 1.41 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 4.12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 5.01 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 1.48 | 6.55 | --- | 21.76 | --- | 77.4046 | 20.2588 | 92.6945 | SDS-TCAA* | mg/L | 1.72 | 7.52 | --- | 24.92 | --- | 77.1277 | 23.2026 | 92.5871
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-02-13 | 9:45 | 829.7 | 8.3 | 121 | 118 | 1.5 | 3.7 | 0.7 | 0.23 |  | 0.93 | 4.63 | 0.25913 | 0.75269 | 3.9785 | 12.7595 | 15.554 | 5 | 113 | 0.13765 | 6.54 | 5.98 | 6.61 | 124 | NR | 1050 | [21 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | 5.35 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | 5.57 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [55 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 0.88 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 3.37 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 4.18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 mg/L for 1 hour | [55 empty] | SDS-BCAA* | mg/L | BMRL | 2.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.76 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.58 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 6.54 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 7.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [56 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | 1.34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | 2.17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [56 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.26 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.94 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 2.58 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 2.27 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 4.51 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5 | mg/L | 0 | 6.64 | --- | 25.5385 | --- | 100 | 23.6203 | 100 | SDS-HAA5 | mg/L | 0 | 10.54 | --- | 40.5385 | --- | 100 | 37.6565 | 100 | SDS-HAA5 | mg/L | 0 | 9.24 | --- | 35.5385 | --- | 100 | 32.9658 | 100 | SDS-HAA5 | mg/L | 1.48 | 15.27 | --- | 56.64 | --- | 90.3078 | 52.5568 | 97.184 | SDS-HAA5 | mg/L | 1.72 | 17.27 | --- | 63.92 | --- | 90.0405 | 59.3157 | 97.1003
[59 empty] | SDS-HAA6 | mg/L | 0 | 8.72 | --- | 33.5385 | --- | 100 | 31.0195 | 100 | SDS-HAA6 | mg/L | 0 | 13.3 | --- | 51.1538 | --- | 100 | 47.5172 | 100 | SDS-HAA6 | mg/L | 0 | 11.82 | --- | 45.4615 | --- | 100 | 42.1705 | 100 | SDS-HAA6 | mg/L | 1.48 | 21.81 | --- | 82.8 | --- | 93.2141 | 76.7804 | 98.0724 | SDS-HAA6 | mg/L | 1.72 | 24.35 | --- | 92.24 | --- | 92.9363 | 85.5394 | 97.9892
[59 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[59 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[59 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[60 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[60 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[59 empty] | Qp/QT (THM4), % | -996.4396 | -439.1641 |  | Qp/QT (HAA5), % | -713.253 | -306.6265 |  |  |  | Qp/QT (THM4), % | -207.8239 | -53.9119 |  | Qp/QT (HAA5), % | -412.334 | -156.167 |  |  |  | Qp/QT (THM4), % | -212.3356 | -49.0703 |  | Qp/QT (HAA5), % | -484.4156 | -192.2078 |  |  |  | Qp/QT (THM4), % | -206.1224 | -53.0612 |  | Qp/QT (HAA5), % | -280.8557 | -85.0616 |  |  |  | Qp/QT (THM4), % | -177.1363 | -38.5681 |  | Qp/QT (HAA5), % | -236.2058 | -62.5723
[59 empty] | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA
[59 empty] | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA
[59 empty] | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA
[59 empty] | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA
[59 empty] | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA
[59 empty] | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA
[59 empty] | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA
[59 empty] | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA
[59 empty] | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA
[59 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA
[59 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[59 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[59 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[59 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[59 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[59 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[59 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[59 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[59 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[59 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on AA27: Carollo Engineers: Concentrate Valve Plugged
Note on AA29: Carollo Engineers: Changed the prefilter
Note on AA32: Carollo Engineers: System low pressure alarm shut the pilot plant off.
Note on AI5: Carollo Engineers: Estimated Osmotic Pressure. Based on average permeate TDS concentration of 65 mg/L and estimated bulk concentration of 600 mg/L (which was measured but not reported.
Note on AM6: Carollo Engineers: pH was controlled by injecting sulfuric acid with a metering pump which was controlled manually. Daily shifts in alkalinity caused wide variations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of the variability in permeate TDS.
Note on AO27: Carollo Engineers: Spikes in TDS seem to be the result of mechanical difficulties with the concentrate valve being plugged by PAC which was breaking through both the sand and cartidge filters.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN25: Carollo Engineers: Data verified
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BQ37: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BQ47: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CA25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CX23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DI23: Carollo Engineers: Data verified by Carollo 8/6/99.

## NF200 2nd Quarter
FIELD-SET 2: 2nd QUARTER SEBST RESULTS (FILE: sebst-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: SEBST Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 2-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 2-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 2-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 2-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Osmonics-Desal-PPC | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.68 | [8 empty] | Recovery during sample collection (decimal) | 0.36 | [8 empty] | Recovery during sample collection (decimal) | 0.59 | [8 empty] | Recovery during sample collection (decimal) | 0.52 | [8 empty] | Recovery during sample collection (decimal) | 0.52 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | PPC B22-1 | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | #VALUE! | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.74 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.78 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.13 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.84 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.84 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | NR |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-02-27 | 9:14 | 927.3 | 11.9 | 180 | 178 | 0.5 | 3.8 | 0.76 | 0.24 |  | 1 | 4.8 | 0.32313 | 0.76 | 3.8 | 17.1 | 18.7409 | 4 | 174.5 | 0.1074 | 6.03 | 5.9 | 6.66 | 91.5 | NR | 429 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.58 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.54 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.93 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.64 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.64 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-02-28 | 12:30 | 954.8 | 11.7 | 164 | 160 | 0 | 3.8 | 0.53 | 0.24 |  | 0.77 | 4.57 | 0.31472 | 0.68831 | 4.9351 | 11.925 | 13.1468 | 4 | 158 | 0.083208 | 8.17 | 8.62 | 8.73 | 107 | NR | 422 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-03-01 | 12:10 | 978.2 | 13.3 | 250 | 247 | 0.5 | 3.8 | 0.57 | 0.24 |  | 0.81 | 4.61 | 0.31619 | 0.7037 | 4.6914 | 12.825 | 13.4859 | 4 | 244 | 0.05527 | 6.44 | 5.84 | 6.28 | 71 | NR | 545 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin film composite | Design flux, FW (gfd) | 10 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-03-06 | 9:38 | 1002.4 | 12.1 | 263 | 261 | 2 | 3.8 | 0.5 | 0.24 |  | 0.74 | 4.54 | 0.31363 | 0.67568 | 5.1351 | 11.25 | 12.2569 | 4 | 256 | 0.047878 | 6.25 | 5.96 | 6.41 | 55 | NR | 608 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | NR | Permeate flow rate, Qp (gpm) | 0.44444 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-03-07 | 12:19 | 1029.1 | 12.9 | 265 | 263 | 2.5 | 3.8 | 0.31 | 0.24 |  | 0.55 | 4.35 | 0.30668 | 0.56364 | 6.9091 | 6.975 | 7.4217 | 4 | 257.5 | 0.028822 | 6.38 | 7.69 | 6.92 | 147 | NR | 506 | [21 empty] | Sampling date | MM/DD/YY | 1998-03-06 | 1998-03-06 | 1998-03-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-11 | 1998-03-11 | 1998-03-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-29 | 1998-03-29 | 1998-03-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-02 | 1998-04-02 | 1998-04-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-02 | 1998-04-02 | 1998-04-02 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NR | Feed flow rate, QF (gpm) | 0.59259 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-03-08 | 12:10 | 1052.3 | 12.2 | 265 | 263 | 2.5 | 3.8 | 0.4 | 0.32 |  | 0.72 | 4.52 | 0.31582 | 0.55556 | 5.2778 | 9 | 9.7766 | 4 | 257.5 | 0.037967 | 6.08 | 6.1 | 6.14 | 154 | NR | 608 | [21 empty] | Sampling time | hh:mm | 9:38 | 9:38 | 9:38 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:37 | 9:37 | 9:37 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:11 | 11:11 | 11:11 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:03 | 9:03 | 9:03 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:03 | 9:03 | 9:03 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.14815 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-03-09 | 10:35 | 1075.4 | 11.4 | 266 | 264 | 4 | 3.8 | 0.29 | 0.32 |  | 0.61 | 4.41 | 0.3118 | 0.47541 | 6.2295 | 6.525 | 7.2576 | 4 | 257 | 0.02824 | 5.89 | 5.89 | 5.98 | 96 | NR | 538 | [21 empty] | Operation time | hh.hh | 1002.4 | 1002.4 | 1002.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1120.8 | 1120.8 | 1120.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1456 | 1456 | 1456 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1517.7 | 1517.7 | 1517.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1517.7 | 1517.7 | 1517.7 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | NR | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-03-10 | 9:41 | 1096.9 | 9.1 | 266 | 264 | 4 | 3.8 | 0.28 | 0.32 |  | 0.6 | 4.4 | 0.31143 | 0.46667 | 6.3333 | 6.3 | 7.5003 | 4 | 257 | 0.029184 | 6.93 | 7.82 | 6.59 | 102 | NR | 525 | [21 empty] | pH | --- | 6.83 | 7.26 | 6.59 | --- | --- | --- | --- | --- | pH | --- | 6.83 | 7.26 | 6.59 | --- | --- | --- | --- | --- | pH | --- | 5.98 | 7.3 | 6.23 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 5.93 | 6.73 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 5.93 | 6.73 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | NR | Calcium (mg/L) | 51.5 |  |  |  | 1998-03-11 | 9:37 | 1128.8 | 10.3 | 266 | 264 | 4.5 | 3.8 | 0.28 | 0.5 |  | 0.78 | 4.58 | 0.32459 | 0.35897 | 4.8718 | 6.3 | 7.2389 | 4 | 256.5 | 0.028222 | 6.83 | 7.26 | 6.59 | 96 | NR | 518 | [21 empty] | Temperature | oC | 12.1 | 12.1 | 12.1 | --- | --- | --- | --- | --- | Temperature | oC | 10.3 | 10.3 | 10.3 | --- | --- | --- | --- | --- | Temperature | oC | 14.4 | 14.4 | 14.4 | --- | --- | --- | --- | --- | Temperature | oC | 15.7 | 15.7 | 15.7 | --- | --- | --- | --- | --- | Temperature | oC | 15.7 | 15.7 | 15.7 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 64 | Design influent flow rate2, QI (gpm) | 4.5 | Barium (mg/L) | 0.016 |  |  |  | 1998-03-12 | 9:40 | 1144.9 | 9.8 | 267 | 265 | 5 | 3.8 | 0.29 | 0.5 |  | 0.79 | 4.59 | 0.32496 | 0.36709 | 4.8101 | 6.525 | 7.6091 | 4 | 257 | 0.029607 | 6.44 | 6.97 | 6.6 | 115 | NR | 499 | [21 empty] | Alkalinity | mg/L as CaCO3 | 11 | 18 | 34 | 32.875 | 3.3088 | 38.8889 | 31.6733 | 65.2704 | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 10 | 35 | 115 | 62.0833 | 46.0145 | 71.4286 | 59.6318 | 83.2304 | Alkalinity | mg/L as CaCO3 | 9 | 34 | 102 | 61.0833 | 40.1144 | 73.5294 | 58.6318 | 84.65 | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | NR | Design recycle flow rate, QR (gpm) | 3.9074 | Strontium (mg/L) | 0.247 |  |  |  | 1998-03-13 | 9:05 | 1168.1 | 13.5 | 266 | 264 | 4 | 3.8 | 0.22 | 0.32 |  | 0.54 | 4.34 | 0.30924 | 0.40741 | 7.037 | 4.95 | 5.1744 | 4 | 257 | 0.020134 | 6.22 | 5.84 | 6.27 | 90 | NR | 576 | [21 empty] | Total dissolved solids | mg/L | 96 | NR | 518 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 96 | NR | 518 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 147 | NR | 435 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 70 | NR | 314 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 70 | NR | 314 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | NR | Recycle ratio, r | 6.5938 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-03-14 | 11:36 | 1194.7 | 15 | 268 | 265 | 3.5 | 3.8 | 0.23 | 0.29 |  | 0.52 | 4.32 | 0.30741 | 0.44231 | 7.3077 | 5.175 | 5.175 | 4 | 259 | 0.019981 | 5.99 | 5.52 | 6.31 | 83 | NR | 602 | [21 empty] | Total hardness | mg/L as CaCO3 | 19.5 | 150 | 374 | 427.3125 | -14.2547 | 87 | 404.9095 | 95.1841 | Total hardness | mg/L as CaCO3 | BMRL | 293 | 507 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 32.8 | 186 | 191 | 406.4585 | -112.8055 | 82.3656 | 381.193 | 91.3954 | Total hardness | mg/L as CaCO3 | 4.44 | 200 | 331 | 411.8567 | -24.428 | 97.78 | 392.68 | 98.8693 | Total hardness | mg/L as CaCO3 | 4.1 | 204 | 336 | 420.5583 | -25.1662 | 97.9902 | 400.9561 | 98.9774 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | NR | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-03-15 | 11:55 | 1218.9 | 14.2 | 269 | 266 | 4 | 3.8 | 0.25 | 0.25 |  | 0.5 | 4.3 | 0.30522 | 0.5 | 7.6 | 5.625 | 5.7596 | 4 | 259.5 | 0.022195 | 5.84 | 5.53 | 5.94 | 90 | NR | 659 | [21 empty] | Calcium hardness | mg/L as CaCO3 | 12.9 | 104 | 255 | 297.5875 | -16.701 | 87.5962 | 281.9483 | 95.4247 | Calcium hardness | mg/L as CaCO3 | BMRL | 230 | 325 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 28.2 | 137 | 142 | 293.5659 | -106.7365 | 79.4161 | 275.6227 | 89.7686 | Calcium hardness | mg/L as CaCO3 | 3.87 | 176 | 292 | 362.4742 | -24.135 | 97.8011 | 345.595 | 98.8802 | Calcium hardness | mg/L as CaCO3 | 3.65 | 176 | 297 | 362.7125 | -22.1254 | 97.9261 | 345.8118 | 98.9445 | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | NR | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-03-16 | 9:01 | 1240 | 13.4 | 267 | 264 | 2.5 | 3.8 | 0.32 | 0.35 |  | 0.67 | 4.47 | 0.31509 | 0.47761 | 5.6716 | 7.2 | 7.5487 | 4 | 259 | 0.029146 | 6.42 | 6.89 | 6.48 | 122 | NR | 653 | [21 empty] | Turbidity | ntu | 0.1 | 0.9 | NA | 2.6 | #VALUE! | 88.8889 | 2.4627 | 95.9394 | Turbidity | ntu | 0.05 | 1.8 | NA | 2.7844 | #VALUE! | 97.2222 | 2.6998 | 98.148 | Turbidity | ntu | 0.05 | 1.4 | NA | 3.3427 | #VALUE! | 96.4286 | 3.12 | 98.3975 | Turbidity | ntu | 0.05 | 1.9 | NA | 3.9042 | #VALUE! | 97.3684 | 3.7228 | 98.6569 | Turbidity | ntu | 0.05 | 1.9 | NA | 3.9042 | #VALUE! | 97.3684 | 3.7228 | 98.6569 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | NR | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-03-17 | 10:37 | 1265.6 | 14.8 | 268 | 265 | 3 | 3.8 | 0.23 | 0.29 |  | 0.52 | 4.32 | 0.30741 | 0.44231 | 7.3077 | 5.175 | 5.2057 | 4 | 259.5 | 0.02006 | 6.75 | 6.6 | 6.43 | 115 | NR | 570 | [21 empty] | Ammonia | mg NH3-N / L | 0.0634 | 0.097 | 0.104 | 0.1684 | -61.9231 | 34.6392 | 0.16263 | 61.0163 | Ammonia | mg NH3-N / L | 0.041 | 0.1 | 0.204 | 0.13319 | 34.712 | 59 | 0.13034 | 68.543 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.054 | 0.125 | 0.148 | 0.20192 | -36.4302 | 56.8 | 0.19495 | 72.3012 | Ammonia | mg NH3-N / L | 0.05 | 0.145 | 0.137 | 0.24792 | -80.9611 | 65.5172 | 0.2386 | 79.0445
|  | Minimum flow rate to the element, QI, min (gpm) | NR | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-03-18 | 8:31 | 1287.4 | 15.2 | 269 | 266 | 3 | 3.8 | 0.25 | 0.23 |  | 0.48 | 4.28 | 0.30376 | 0.52083 | 7.9167 | 5.625 | 5.5918 | 4 | 260.5 | 0.021466 | 6.74 | 6.22 | 6.39 | 109 | NR | 634 | [21 empty] | Total organic carbon | mg/L | 0.57 | 2.29 | 4.72 | 5.945 | -25.9534 | 75.1092 | 5.6497 | 89.911 | Total organic carbon | mg/L | 0.26 | 2.05 | 5.25 | 3.0569 | 41.7738 | 87.3171 | 2.9704 | 91.2469 | Total organic carbon | mg/L | NA | 2.48 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.48 | 2.83 | 3.56 | 5.3758 | -51.0066 | 83.0389 | 5.1454 | 90.6713 | Total organic carbon | mg/L | 0.39 | 3.02 | 3.62 | 5.8692 | -62.1317 | 87.0861 | 5.6113 | 93.0497
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 11.2875 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-03-19 | 11:45 | 1314.8 | 13.6 | 268 | 265 | 3.1 | 3.75 | 0.28 | 0.23 |  | 0.51 | 4.26 | 0.3012 | 0.54902 | 7.3529 | 6.3 | 6.5662 | 4 | 259.4 | 0.025313 | 6.8 | 8.1 | 7.01 | 205 | NR | 582 | [21 empty] | UV254 | cm-1 | 0.024 | 0.055 | 0.097 | 0.12087 | -24.6134 | 56.3636 | 0.11555 | 79.2303 | UV254 | cm-1 | 0.017 | 0.05 | 0.109 | 0.068562 | 37.0986 | 66 | 0.066968 | 74.6147 | UV254 | cm-1 | 0.027 | 0.053 | 0.067 | 0.090415 | -34.9472 | 49.0566 | 0.086127 | 68.6509 | UV254 | cm-1 | 0.02 | 0.071 | 0.084 | 0.12625 | -50.2976 | 71.831 | 0.12125 | 83.505 | UV254 | cm-1 | 0.023 | 0.069 | 0.083 | 0.11883 | -43.1727 | 66.6667 | 0.11432 | 79.8815
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.0027 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-03-20 | 12:15 | 1339.3 | 14.8 | 268 | 265 | 3.1 | 3.75 | 0.3 | 0.2 |  | 0.5 | 4.25 | 0.29974 | 0.6 | 7.5 | 6.75 | 6.79 | 4 | 259.4 | 0.026176 | 7.04 | 8.3 | 8.14 | 200 | NR | 640 | [21 empty] | SUVA | L/(mg*m) | 4.2105 | 2.4017 | 2.0551 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 6.5385 | 2.439 | 2.0762 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.1371 | NR | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.1667 | 2.5088 | 2.3596 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 5.8974 | 2.2848 | 2.2928 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | This membrane has been discontinued | Manufacturer reported TDS rejection, RejTDS (decimal) | NA | [5 empty] | 1998-03-25 | 8:45 | 1358.9 | 12 | 269 | 266 | 2.9 | 3.8 | 0.38 | 0.4 |  | 0.78 | 4.58 | 0.32094 | 0.48718 | 4.8718 | 8.55 | 9.3428 | 4 | 260.6 | 0.035851 | 5.85 | 5.49 | 5.83 | 122 | NR | 499 | [21 empty] | Bromide | mg/L | 100 | 100 | --- | 100 | --- | 0 | 100 | 0 | Bromide | mg/L | BMRL | 80 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 70 | 50 | --- | 21.2195 | --- | -40 | 24.5179 | -185.5059 | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | This membrane has been discontinued | Feed TDS, TDSF (mg/L) | NA | [5 empty] | 1998-03-26 | 8:31 | 1382.1 | 15.1 | 254 | 251 | 2.1 | 3.8 | 0.32 | 0.38 |  | 0.7 | 4.5 | 0.31728 | 0.45714 | 5.4286 | 7.2 | 7.1787 | 4 | 246.4 | 0.029135 | 6.29 | 6.62 | 6.46 | 109 | NR | 480 | [21 empty] | SDS-Cl2 dose | mg/L | 1.4 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.3 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | #VALUE! | [5 empty] | 1998-03-27 | 9:20 | 1406.8 | 17.1 | 254 | 251 | 3 | 3.8 | 0.27 | 0.32 |  | 0.59 | 4.39 | 0.31107 | 0.45763 | 6.4407 | 6.075 | 5.7094 | 4 | 245.5 | 0.023256 | 6.18 | 5.83 | 6.27 | 77 | NR | 499 | [21 empty] | SDS-Free Cl2 residual | mg/L | 0.5 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.8 | 0.6 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.5 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | #VALUE! | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-03-28 | 11:10 | 1432.2 | 18.2 | 253 | 250 | 3 | 3.8 | 0.25 | 0.28 |  | 0.53 | 4.33 | 0.30741 | 0.4717 | 7.1698 | 5.625 | 5.1173 | 4 | 244.5 | 0.02093 | 5.97 | 5.51 | 5.82 | 83 | NR | 512 | [21 empty] | SDS-Cl2 demand | mg/L | 0.9 | 1.85 | --- | 3.8687 | --- | 51.3514 | 3.7057 | 75.7128 | SDS-Cl2 demand | mg/L | 0.4 | 1.9 | --- | 2.7437 | --- | 78.9474 | 2.6713 | 85.0258 | SDS-Cl2 demand | mg/L | 0.8 | 1.5 | --- | 2.5073 | --- | 46.6667 | 2.3919 | 66.5534 | SDS-Cl2 demand | mg/L | 0.7 | 2.5 | --- | 4.45 | --- | 72 | 4.2735 | 83.62 | SDS-Cl2 demand | mg/L | 0.7 | 2.5 | --- | 4.45 | --- | 72 | 4.2735 | 83.62
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | NR | Influent TDS, TDSI (mg/L) | #VALUE! | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-03-29 | 11:11 | 1456 | 14.4 | 203 | 200 | 0 | 3.8 | 0.67 | 0.46 | X | 1.13 | 4.93 | 0.33592 | 0.59292 | 3.3628 | 15.075 | 15.3447 | 4 | 197.5 | 0.077695 | 5.98 | 7.3 | 6.23 | 147 | NR | 435 | [21 empty] | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 7 | 7 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | NR | Osmotic pressure gradient, Dp (psi) | #VALUE! | [5 empty] | 1998-03-30 | 11:45 | 1480.6 | 15.5 | 214 | 210 | 3.5 | 3.8 | 0.24 | 0.23 |  | 0.47 | 4.27 | 0.30339 | 0.51064 | 8.0851 | 5.4 | 5.3208 | 4 | 204.5 | 0.026018 | 7.45 | 8.37 | 7.93 | 121 | NR | 576 | [21 empty] | SDS-Chlorination pH | --- | 7.01 | 7.01 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.09 | 7.06 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.2 | 7.38 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.3 | 7.13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.3 | 7.13 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NR | [7 empty] | 1998-03-31 | 10:40 | 1503.4 | 15.1 | 214 | 210 | 3.5 | 3.8 | 0.26 | 0.23 |  | 0.49 | 4.29 | 0.30412 | 0.53061 | 7.7551 | 5.85 | 5.8327 | 4 | 204.5 | 0.028522 | 6.03 | 5.9 | 6.22 | 115 | NR | 538 | [21 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | NR | Estimate the Required Influent Pressure | [6 empty] | 1998-04-02 | 9:03 | 1517.7 | 15.7 | 241 | 239 | 3.5 | 3.8 | 0.44 | 0.4 |  | 0.84 | 4.64 | 0.32313 | 0.52381 | 4.5238 | 9.9 | 9.6973 | 4 | 232.5 | 0.041709 | 6.65 | 6.94 | 6.82 | 70 | NR | 313 | [21 empty] | SDS-TOX | mg Cl- /L | BMRL | 81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 50 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 32 | 99 | --- | 195.4146 | --- | 67.6768 | 184.3651 | 82.6431 | SDS-TOX | mg Cl- /L | BMRL | 122 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | NR | Estimated system pressure losses, DPloss (psi) | NA | [5 empty] | 1998-04-03 | 8:19 | 1540.9 | 21.1 | 255 | 253 | 4 | 3.8 | 0.24 | 0.24 |  | 0.48 | 4.28 | 0.30412 | 0.5 | 7.9167 | 5.4 | 4.5091 | 4 | 246 | 0.01833 | 6.06 | 5.25 | 5.98 | 115 | NR | 570 | [21 empty] | SDS-CHCl3 | mg/L | 1.21 | 10.6 | --- | 30.5538 | --- | 88.5849 | 28.9418 | 95.8192 | SDS-CHCl3 | mg/L | BMRL | 8.59 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) |  | Design permeate pressure, Pp (psi) | NA | [5 empty] | 1998-04-04 | 9:29 | 1556.1 | 19 | 256 | 254 | 4 | 3.8 | 0.28 | 0.29 |  | 0.57 | 4.37 | 0.30924 | 0.49123 | 6.6667 | 6.3 | 5.5975 | 4 | 247 | 0.022662 | 7.1 | 6.57 | 7.21 | 58 | NR | 441 | [21 empty] | SDS-BDCM | mg/L | 1.56 | 7.24 | --- | 19.31 | --- | 78.453 | 18.3349 | 91.4916 | SDS-BDCM | mg/L | BMRL | 7.16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | NR | Required influent pressure, PI (psi) | #VALUE! | [5 empty] | 1998-04-05 | 10:40 | 1590.3 | 20 | 258 | 255 | 3.5 | 3.8 | 0.4 | 0.16 |  | 0.56 | 4.36 | 0.30412 | 0.71429 | 6.7857 | 9 | 7.7635 | 4 | 249 | 0.031179 | 6.39 | 5.5 | 6.29 | 90 | NR | 524 | [21 empty] | SDS-DBCM | mg/L | 2.57 | 4.45 | --- | 8.445 | --- | 42.2472 | 8.1223 | 68.3586 | SDS-DBCM | mg/L | BMRL | 5.18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | NR | [7 empty] | 1998-04-06 | 8:36 | 1612 | 15.6 | 258 | 255 | 3 | 3.8 | 0.48 | 0.29 | X | 0.77 | 4.57 | 0.31655 | 0.62338 | 4.9351 | 10.8 | 10.6101 | 4 | 249.5 | 0.042526 | 6.82 | 7.85 | 6.77 | 58 | NR | 371 | [21 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | NR | [7 empty] | 1998-04-07 | 8:47 | 1636.1 | 18.4 | 256 | 254 | 2.5 | 3.8 | 0.35 | 0.36 |  | 0.71 | 4.51 | 0.31692 | 0.49296 | 5.3521 | 7.875 | 7.122 | 4 | 248.5 | 0.02866 | 6.16 | 5.6 | 6.29 | 70 | NR | 435 | [21 empty] | SDS-THM4 | mg/L | 5.34 | 22.29 | --- | 58.3088 | --- | 76.0431 | 55.3989 | 90.3608 | SDS-THM4 | mg/L | 0 | 20.93 | --- | 32.7031 | --- | 100 | 31.6918 | 100 | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 225 max | [7 empty] | 1998-04-08 | 10:02 | 1661.3 | 18.5 | 258 | 255 | 3 | 3.8 | 0.25 | 0.4 |  | 0.65 | 4.45 | 0.31619 | 0.38462 | 5.8462 | 5.625 | 5.0722 | 4 | 249.5 | 0.020329 | 6.47 | 6.09 | 6.47 | 90 | NR | 467 | [21 empty] | SDS-MCAA* | mg/L | 5.47 | 3.02 | --- | -2.1862 | --- | -81.1258 | -1.7657 | 409.7996 | SDS-MCAA* | mg/L | 2.98 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 4-11 | [7 empty] | 1998-04-09 | 8:43 | 1684 | 17.7 | 258 | 255 | 3 | 3.8 | 0.4 | 0.4 |  | 0.8 | 4.6 | 0.32167 | 0.5 | 4.75 | 9 | 8.3096 | 4 | 249.5 | 0.033305 | 6.75 | 6.75 | 6.59 | 90 | NR | 531 | [21 empty] | SDS-DCAA* | mg/L | 3.02 | 9.71 | --- | 23.9262 | --- | 68.898 | 22.7778 | 86.7415 | SDS-DCAA* | mg/L | 1.68 | 7.31 | --- | 10.4769 | --- | 77.0178 | 10.2048 | 83.5372 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | NR | [55 empty] | SDS-TCAA* | mg/L | BMRL | 6.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 5.24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | NR | [55 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | NR | [55 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | NR | [55 empty] | SDS-BCAA* | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [56 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [56 empty] | SDS-CDBAA | mg/L | BMRL | 1.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.04 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-DCBAA | mg/L | BMRL | 4.89 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 4.25 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5 | mg/L | 8.49 | 18.96 | --- | 41.2088 | --- | 55.2215 | 39.4114 | 78.458 | SDS-HAA5 | mg/L | 4.66 | 12.55 | --- | 16.9881 | --- | 62.8685 | 16.6069 | 71.9393 | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA6 | mg/L | 8.49 | 22.16 | --- | 51.2088 | --- | 61.6877 | 48.862 | 82.6245 | SDS-HAA6 | mg/L | 4.66 | 15.33 | --- | 21.3319 | --- | 69.6021 | 20.8163 | 77.6137 | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[59 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[59 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[60 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[60 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[59 empty] | Qp/QT (THM4), % | -293.2743 | -80.885 |  | Qp/QT (HAA5), % | -334.6705 | -76.7908 |  |  |  | Qp/QT (THM4), % | -244.0038 | -72.0019 |  | Qp/QT (HAA5), % | -525.3485 | -183.1432 |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
[59 empty] | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
[59 empty] | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
[59 empty] | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
[59 empty] | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[59 empty] | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[59 empty] | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[59 empty] | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[59 empty] | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[59 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[59 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[59 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[59 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[59 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[59 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[59 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[59 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[59 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[59 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[59 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on AA9: Carollo Engineers: Fuse was blown and required temporary pilot plant shut down.
Note on AA24: Carollo Engineers: Electrical maintenance was performed to the building were pilot plants were located. Required pilot plants to be shut down.
Note on AA31: Carollo Engineers: Fuse was blown and required temporary pilot plant shut down.
Note on AI5: Carollo Engineers: Estimated Osmotic Pressure. Based on average permeate TDS concentration of 105 mg/L and estimated bulk concentration of 500 mg/L (which was measured but not reported.
Note on AM6: Carollo Engineers: pH was controlled by injecting sulfuric acid with a metering pump which was controlled manually. Daily shifts in alkalinity caused wide variations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of the variability in permeate TDS.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BN23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BN25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BY18: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BY22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BY23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BY25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CB32: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ18: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ19: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CJ37: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CJ47: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CU22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CU37: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on CU47: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on DF22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DF37: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.
Note on DF47: Carollo Engineers: These data are suspect. It is believed that the laboratory reported these data incorrectly and the feed and permeate samples were accidentally switched.

## NF200 3rd Quarter
FIELD-SET 3: 3rd QUARTER SEBST RESULTS (FILE: sebst-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: SEBST Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 3-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 3-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 3-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 3-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Dow FilmTec | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | NF200B | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.17486 | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1.04 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.04 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.03 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.02 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.02 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | NF200B-4040 |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-04-11 | 10:45 | 1710 | 12.4 | 61 | 57 | 2 | 3.8 | 0.82 | 0.27 |  | 1.09 | 4.89 | 0.27124 | 0.75229 | 3.4862 | 14.9468 | 16.1408 | 7 | 50 | 0.32282 | 6.84 | 6.79 | 6.73 | 230 | NR | 582 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.84 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.84 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 400 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-04-12 | 13:35 | 1737.8 | 12.9 | 66 | 64 | 1 | 3.8 | 0.76 | 0.32 |  | 1.08 | 4.88 | 0.27245 | 0.7037 | 3.5185 | 13.8532 | 14.7403 | 7 | 57 | 0.2586 | 6.55 | 5.89 | 6.67 | 154 | NR | 544 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polypiperazine | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-04-13 | 1:40 | 1761.8 | 14 | 66 | 62 | 0.5 | 3.8 | 0.71 | 0.31 |  | 1.02 | 4.82 | 0.27033 | 0.69608 | 3.7255 | 12.9418 | 13.33 | 7 | 56.5 | 0.23593 | 7.2 | 7.79 | 7.31 | 211 | NR | 595 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | Design flux, FW (gfd) | 12 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-04-14 | 8:31 | 1780.6 | 14 | 69 | 64 | 0.5 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 13.1423 | 7 | 59 | 0.22275 | 6.36 | 5.78 | 6.22 | 194 | NR | 678 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Permeate flow rate, Qp (gpm) | 0.65833 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-04-15 | 8:37 | 1804.7 | 15.3 | 79 | 74 | 0 | 3.8 | 0.73 | 0.32 |  | 1.05 | 4.85 | 0.27154 | 0.69524 | 3.619 | 13.3063 | 13.1889 | 7 | 69.5 | 0.18977 | 6.8 | 6.31 | 6.69 | 179 | NR | 730 | [21 empty] | Sampling date | MM/DD/YY | 1998-04-17 | 1998-04-17 | 1998-04-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-30 | 1998-04-30 | 1998-04-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-05 | 1998-05-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-05 | 1998-05-05 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Feed flow rate, QF (gpm) | 0.87778 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-04-16 | 9:40 | 1829.8 | 15.5 | 85 | 80 | 0.5 | 3.8 | 0.76 | 0.33 |  | 1.09 | 4.89 | 0.27305 | 0.69725 | 3.4862 | 13.8532 | 13.6499 | 7 | 75 | 0.182 | 5.98 | 5.27 | 5.59 | 218 | NR | 691 | [21 empty] | Sampling time | hh:mm | 8:45 | 8:45 | 8:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:40 | 8:40 | 8:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:26 | 9:26 | 9:26 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:07 | 9:07 | 9:07 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:07 | 9:07 | 9:07 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.21944 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-04-17 | 8:45 | 1850 | 14.8 | 76 | 71 | 0.5 | 3.8 | 0.74 | 0.3 |  | 1.04 | 4.84 | 0.27063 | 0.71154 | 3.6538 | 13.4886 | 13.5686 | 7 | 66 | 0.20558 | 6.06 | 6.12 | 5.51 | 218 | NR | 659 | [21 empty] | Operation time | hh.hh | 1850 | 1850 | 1850 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1963.2 | 1963.2 | 1963.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2155.9 | 2155.9 | 2155.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2257.8 | 2257.8 | 2257.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2257.8 | 2257.8 | 2257.8 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-04-18 | 11:35 | 1870.2 | 15.7 | 80 | 75 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 12.8553 | 7 | 70.5 | 0.18234 | 6.89 | 6.9 | 6.71 | 205 | NR | 717 | [21 empty] | pH | --- | 6.06 | 6.12 | 5.51 | --- | --- | --- | --- | --- | pH | --- | 6.19 | 5.72 | 6.23 | --- | --- | --- | --- | --- | pH | --- | 6.84 | 5.84 | 6.32 | --- | --- | --- | --- | --- | pH | --- | 5.25 | 8.85 | 5.87 | --- | --- | --- | --- | --- | pH | --- | 5.25 | 8.85 | 5.87 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 51.5 |  |  |  | 1998-04-19 | 12:32 | 1895 | 15.1 | 87 | 82 | 0 | 3.8 | 0.74 | 0.3 |  | 1.04 | 4.84 | 0.27063 | 0.71154 | 3.6538 | 13.4886 | 13.4488 | 7 | 77.5 | 0.17353 | 6.14 | 5.65 | 6.33 | 173 | NR | 800 | [21 empty] | Temperature | oC | 14.8 | 14.8 | 14.8 | --- | --- | --- | --- | --- | Temperature | oC | 14.8 | 14.8 | 14.8 | --- | --- | --- | --- | --- | Temperature | oC | 16.1 | 16.1 | 16.1 | --- | --- | --- | --- | --- | Temperature | oC | 18.1 | 18.1 | 18.1 | --- | --- | --- | --- | --- | Temperature | oC | 18.1 | 18.1 | 18.1 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 79 | Design influent flow rate2, QI (gpm) | 4.5 | Barium (mg/L) | 0.016 |  |  |  | 1998-04-20 | 9:00 | 1915.5 | 14.6 | 87 | 83 | 0 | 3.8 | 0.72 | 0.25 |  | 0.97 | 4.77 | 0.267 | 0.74227 | 3.9175 | 13.1241 | 13.2801 | 7 | 78 | 0.17026 | 6.35 | 6 | 6.2 | 173 | NR | 768 | [21 empty] | Alkalinity | mg/L as CaCO3 | 21 | 32 | 39 | 58.931 | -51.1052 | 34.375 | 56.0376 | 62.5252 | Alkalinity | mg/L as CaCO3 | 27 | 25 | 49 | 20.1034 | 58.9726 | -8 | 20.6295 | -30.8804 | Alkalinity | mg/L as CaCO3 | 20 | 25 | 30 | 37.2414 | -24.1379 | 20 | 35.9361 | 44.3457 | Alkalinity | mg/L as CaCO3 | 52 | 58 | 80 | 72.6897 | 9.1379 | 10.3448 | 71.1386 | 26.9032 | Alkalinity | mg/L as CaCO3 | 50 | 57 | 81 | 74.1379 | 8.4717 | 12.2807 | 72.3283 | 30.8708 | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | 16.5 | Design recycle flow rate, QR (gpm) | 3.6222 | Strontium (mg/L) | 0.247 |  |  |  | 1998-04-21 | 9:19 | 1939.9 | 14.6 | 89 | 84 | 0 | 3.8 | 0.72 | 0.25 |  | 0.97 | 4.77 | 0.267 | 0.74227 | 3.9175 | 13.1241 | 13.2801 | 7 | 79.5 | 0.16705 | 6.9 | 6.38 | 6.79 | 179.2 | NR | 704 | [21 empty] | Total dissolved solids | mg/L | 218 | NR | 659 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 160 | NR | 691.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 166.4 | NR | 838.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 217.6 | NR | 787.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 217.6 | NR | 787.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Recycle ratio, r | 4.1266 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-04-22 | 8:40 | 1963.2 | 14.8 | 120 | 115 | 0 | 3.8 | 0.74 | 0.3 |  | 1.04 | 4.84 | 0.27063 | 0.71154 | 3.6538 | 13.4886 | 13.5686 | 7 | 110.5 | 0.12279 | 6.19 | 5.72 | 6.23 | 160 | NR | 691.2 | [21 empty] | Total hardness | mg/L as CaCO3 | 44.6 | 205 | 381 | 597.7034 | -56.8775 | 78.2439 | 555.5122 | 91.9714 | Total hardness | mg/L as CaCO3 | 32.7 | 198 | 429 | 602.7 | -40.4895 | 83.4848 | 559.2198 | 94.1526 | Total hardness | mg/L as CaCO3 | 48.8 | 176 | 435 | 487.4207 | -12.0507 | 72.2727 | 454.2154 | 89.2562 | Total hardness | mg/L as CaCO3 | 82.6 | 205 | 440 | 504.669 | -14.6975 | 59.7073 | 473.0269 | 82.538 | Total hardness | mg/L as CaCO3 | 84.4 | 203 | 435 | 493.3655 | -13.4174 | 58.4236 | 462.7058 | 81.7595 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-04-23 | 8:45 | 1987.3 | 15.4 | 94 | 89 | 0.5 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 12.9698 | 7 | 84 | 0.1544 | 8.4 | 8.28 | 8.31 | 172.8 | NR | 736 | [21 empty] | Calcium hardness | mg/L as CaCO3 | 36.2 | 170 | 315 | 497.5793 | -57.9617 | 78.7059 | 462.3848 | 92.171 | Calcium hardness | mg/L as CaCO3 | 28.5 | 175 | 375 | 533.6724 | -42.3126 | 83.7143 | 495.1374 | 94.244 | Calcium hardness | mg/L as CaCO3 | 43.7 | 158 | 390 | 437.8379 | -12.2661 | 72.3418 | 408.0001 | 89.2892 | Calcium hardness | mg/L as CaCO3 | 79.7 | 197 | 422 | 484.1828 | -14.7353 | 59.5431 | 453.8591 | 82.4395 | Calcium hardness | mg/L as CaCO3 | 81.4 | 195 | 417 | 473.1241 | -13.459 | 58.2564 | 443.757 | 81.6566 | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-04-24 | 8:55 | 2011.4 | 16.1 | 94 | 89 | 1 | 3.8 | 0.73 | 0.3 |  | 1.03 | 4.83 | 0.27033 | 0.70874 | 3.6893 | 13.3063 | 12.8806 | 7 | 83.5 | 0.15426 | 7.57 | 7.37 | 7.35 | 192 | NR | 768 | [21 empty] | Turbidity | ntu | 0.05 | 0.4 | NA | 1.2569 | #VALUE! | 87.5 | 1.1648 | 95.7075 | Turbidity | ntu | 0.05 | 0.75 | 0.37 | 2.4638 | -565.89 | 93.3333 | 2.2797 | 97.8067 | Turbidity | ntu | 0.1 | 0.75 | 0.32 | 2.3414 | -631.681 | 86.6667 | 2.1717 | 95.3953 | Turbidity | ntu | 0.05 | 0.35 | 0.35 | 1.0845 | -209.8522 | 85.7143 | 1.0069 | 95.0344 | Turbidity | ntu | 0.05 | 0.35 | 0.35 | 1.0845 | -209.8522 | 85.7143 | 1.0069 | 95.0344 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-04-25 | 11:30 | 2037.9 | 16.7 | 82 | 78 | 0 | 3.8 | 0.74 | 0.25 |  | 0.99 | 4.79 | 0.2676 | 0.74747 | 3.8384 | 13.4886 | 12.8276 | 7 | 73 | 0.17572 | 6.7 | 6.01 | 6.67 | 198.4 | NR | 876.8 | [21 empty] | Ammonia | mg NH3-N / L | 0.063 | 0.077 | 0.086 | 0.11128 | -29.3905 | 18.1818 | 0.10759 | 41.4462 | Ammonia | mg NH3-N / L | 0.043 | 0.068 | 0.0665 | 0.12921 | -94.2961 | 36.7647 | 0.12263 | 64.9354 | Ammonia | mg NH3-N / L | 0.048 | 0.05 | 0.0942 | 0.054897 | 41.7234 | 4 | 0.054374 | 11.7233 | Ammonia | mg NH3-N / L | 0.052 | 0.049 | 0.111 | 0.041655 | 62.4728 | -6.1224 | 0.042431 | -22.5527 | Ammonia | mg NH3-N / L | 0.052 | 0.05 | 0.1 | 0.045103 | 54.8966 | -4 | 0.04562 | -13.9839
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-04-26 | 10:38 | 2061.1 | 17.3 | 97 | 92 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 12.2615 | 7 | 87.5 | 0.14013 | 6.67 | 6.11 | 6.58 | 179.2 | NR | 806.4 | [21 empty] | Total organic carbon | mg/L | 0.79 | 2.51 | 5.37 | 6.721 | -25.1589 | 68.5259 | 6.2686 | 87.3975 | Total organic carbon | mg/L | 0.64 | 3.19 | 6.17 | 9.4331 | -52.8866 | 79.9373 | 8.7624 | 92.696 | Total organic carbon | mg/L | 0.72 | 2.59 | 5.51 | 7.1683 | -30.0958 | 72.2008 | 6.6801 | 89.2217 | Total organic carbon | mg/L | 0.72 | 2.32 | 5.76 | 6.2372 | -8.2854 | 68.9655 | 5.8236 | 87.6366 | Total organic carbon | mg/L | 1.04 | 2.26 | 5.47 | 5.2469 | 4.0787 | 53.9823 | 4.9315 | 78.9111
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 16 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-04-27 | 15:25 | 2089.8 | 17.4 | 97 | 92 | 0 | 3.8 | 0.81 | 0.3 |  | 1.11 | 4.91 | 0.27275 | 0.72973 | 3.4234 | 14.7646 | 13.7534 | 7 | 87.5 | 0.15718 | 6.41 | 5.98 | 6.34 | 117.12 | NR | 838.4 | [21 empty] | UV254 | cm-1 | 0.024 | 0.06 | 0.116 | 0.14814 | -27.7051 | 60 | 0.13867 | 82.6925 | UV254 | cm-1 | 0.022 | 0.058 | 0.135 | 0.14614 | -8.2503 | 62.069 | 0.13667 | 83.9027 | UV254 | cm-1 | 0.027 | 0.061 | 0.107 | 0.14424 | -34.805 | 55.7377 | 0.13537 | 80.054 | UV254 | cm-1 | 0.026 | 0.055 | 0.115 | 0.126 | -9.5652 | 52.7273 | 0.1185 | 78.0596 | UV254 | cm-1 | 0.028 | 0.056 | 0.112 | 0.12455 | -11.2069 | 50 | 0.11731 | 76.1323
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.0023 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-04-28 | 10:40 | 2109.1 | 16.7 | 98 | 93 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 12.4809 | 7 | 88.5 | 0.14103 | 6.83 | 6.31 | 6.74 | 87.68 | NR | 832 | [21 empty] | SUVA | L/(mg*m) | 3.038 | 2.3904 | 2.1601 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.4375 | 1.8182 | 2.188 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.75 | 2.3552 | 1.9419 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.6111 | 2.3707 | 1.9965 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.6923 | 2.4779 | 2.0475 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.85 | [5 empty] | 1998-04-29 | 18:30 | 2140.9 | 16.4 | 99 | 94 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 12.592 | 7 | 89.5 | 0.14069 | 6.32 | 5.91 | 6.22 | 166.4 | NR | 819.2 | [21 empty] | Bromide | mg/L | 80 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 70 | 80 | --- | 104.4828 | --- | 12.5 | 101.8524 | 31.2731 | Bromide | mg/L | 90 | 90 | --- | 90 | --- | 0 | 90 | 0 | Bromide | mg/L | 100 | 90 | --- | 65.5172 | --- | -11.1111 | 68.1024 | -46.8378 | Bromide | mg/L | 100 | 100 | --- | 100 | --- | 0 | 100 | 0
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Feed TDS, TDSF (mg/L) | 1000 | [5 empty] | 1998-04-30 | 9:26 | 2155.9 | 16.1 | 98 | 93 | 0 | 3.8 | 0.73 | 0.3 |  | 1.03 | 4.83 | 0.27033 | 0.70874 | 3.6893 | 13.3063 | 12.8806 | 7 | 88.5 | 0.14554 | 6.84 | 5.84 | 6.32 | 166.4 | NR | 838.4 | [21 empty] | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | 2871.9413 | [5 empty] | 1998-05-01 | 9:25 | 2197.7 | 16 | 121 | 116 | 0 | 3.8 | 0.71 | 0.3 | X | 1.01 | 4.81 | 0.26972 | 0.70297 | 3.7624 | 12.9418 | 12.5648 | 7 | 111.5 | 0.11269 | 9.65 | 8.91 | 9.23 | 166.4 | NR | 742.4 | [21 empty] | SDS-Free Cl2 residual | mg/L | 0.5 | 0.9 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | 376.0196 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-05-02 | 12:07 | 2206.4 | 16 | 83 | 78 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 12.3879 | 7 | 73.5 | 0.16854 | 6.71 | 5.23 | 6.3 | 70.4 | NR | 1017.6 | [21 empty] | SDS-Cl2 demand | mg/L | 0.7 | 2.1 | --- | 5.5276 | --- | 66.6667 | 5.1593 | 86.4324 | SDS-Cl2 demand | mg/L | 0.7 | 1.8 | --- | 4.4931 | --- | 61.1111 | 4.2038 | 83.3482 | SDS-Cl2 demand | mg/L | 0.9 | 2.2 | --- | 5.3828 | --- | 59.0909 | 5.0434 | 82.1549 | SDS-Cl2 demand | mg/L | 0.9 | 2.3 | --- | 5.7276 | --- | 60.8696 | 5.3657 | 83.2267 | SDS-Cl2 demand | mg/L | 0.9 | 2.3 | --- | 5.7276 | --- | 60.8696 | 5.3657 | 83.2267
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | Not Measured | Influent TDS, TDSI (mg/L) | 2506.7972 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-05-03 | 11:57 | 2230.2 | 16.8 | 105 | 100 | 0.5 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 12.444 | 7 | 95 | 0.13099 | 6.59 | 5.98 | 6.26 | 153.6 | NR | 768 | [21 empty] | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 13 | 13 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | Not Specified | Osmotic pressure gradient, Dp (psi) | 23.1335 | [5 empty] | 1998-05-04 | 8:50 | 2251.1 | 17.4 | 135 | 130 | 0.5 | 3.8 | 0.7 | 0.3 | X | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 11.8857 | 7 | 125 | 0.095085 | 8.76 | 8.85 | 8.98 | 140.8 | NR | 774.4 | [21 empty] | SDS-Chlorination pH | --- | 7.29 | 7.26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.3 | 7.27 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.22 | 7.23 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.36 | 7.21 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.36 | 7.21 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15, but depends on application | [7 empty] | 1998-05-05 | 9:07 | 2257.8 | 18.1 | 61 | 56 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.26972 | 0.70297 | 3.7624 | 12.9418 | 11.8086 | 7 | 51.5 | 0.22929 | 5.25 | 8.85 | 5.87 | 224 | NR | 704 | [21 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | -15%+20% | Estimate the Required Influent Pressure | [6 empty] | 1998-05-06 | 8:33 | 2281.3 | 18.6 | 70 | 65 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 11.7992 | 7 | 60.5 | 0.19503 | 6.54 | 5.92 | 6.64 | 217.6 | NR | 787.2 | [21 empty] | SDS-TOX | mg Cl- /L | BMRL | 128 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 141 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 107 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 133 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | < 45% rejection of CaCl2; 70 psi, | Estimated system pressure losses, DPloss (psi) | 4 | [5 empty] | 1998-05-07 | 8:34 | 2304.7 | 19 | 80 | 75 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 11.3366 | 7 | 70.5 | 0.1608 | 6.57 | 6.14 | 6.6 | 179.2 | NR | 780.8 | [21 empty] | SDS-CHCl3 | mg/L | 1.13 | 28.4 | --- | 95.1645 | --- | 96.0211 | 87.9914 | 98.7158 | SDS-CHCl3 | mg/L | BMRL | 20.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 2.17 | 19.3 | --- | 61.239 | --- | 88.7565 | 56.7672 | 96.1774 | SDS-CHCl3 | mg/L | 2.42 | 23 | --- | 73.3855 | --- | 89.4783 | 68.0653 | 96.4446 | SDS-CHCl3 | mg/L | 2.68 | 24.2 | --- | 76.8869 | --- | 88.9256 | 71.3237 | 96.2425
|  | (e.g., solute type and concentration) | 500 mg/l CaCl2 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-05-08 | 8:45 | 2329 | 20.1 | 110 | 105 | 0 | 3.8 | 0.72 | 0.3 |  | 1.02 | 4.82 | 0.27003 | 0.70588 | 3.7255 | 13.1241 | 11.2875 | 7 | 100.5 | 0.11231 | 7.17 | 6.37 | 6.92 | 153.6 | NR | 755.2 | [21 empty] | SDS-BDCM | mg/L | 2.24 | 13.3 | --- | 40.3779 | --- | 83.1579 | 37.4687 | 94.0217 | SDS-BDCM | mg/L | 1.47 | 12 | --- | 37.7803 | --- | 87.75 | 35.0106 | 95.8013 | SDS-BDCM | mg/L | 3.8 | 12.6 | --- | 34.1448 | --- | 69.8413 | 31.8476 | 88.0682 | SDS-BDCM | mg/L | 5.2 | 13.4 | --- | 33.4759 | --- | 61.194 | 31.3561 | 83.4163 | SDS-BDCM | mg/L | 5.59 | 14.3 | --- | 35.6245 | --- | 60.9091 | 33.3728 | 83.2498
|  | Variability of rejection of reference solute (%) | < 45% rejection of CaCl2 | Required influent pressure, PI (psi) | 95.759 | [5 empty] | 1998-05-09 | 12:00 | 2356.3 | 21.1 | 133 | 128 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.26972 | 0.70297 | 3.7624 | 12.9418 | 10.8065 | 7 | 123.5 | 0.087502 | 6.04 | 5.27 | 6.23 | 134.4 | NR | 857.6 | [21 empty] | SDS-DBCM | mg/L | 3.32 | 3.87 | --- | 5.2166 | --- | 14.2119 | 5.0719 | 34.541 | SDS-DBCM | mg/L | 2.39 | 5.28 | --- | 12.3555 | --- | 54.7348 | 11.5953 | 79.3883 | SDS-DBCM | mg/L | 5.96 | 5.63 | --- | 4.8221 | --- | -5.8615 | 4.9082 | -21.4291 | SDS-DBCM | mg/L | 8.21 | 5.2 | --- | -2.1693 | --- | -57.8846 | -1.3912 | 690.1446 | SDS-DBCM | mg/L | 8.65 | 5.48 | --- | -2.281 | --- | -57.8467 | -1.4615 | 691.8389
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-05-10 | 12:00 | 2380.1 | 22.1 | 155 | 150 | 0 | 3.8 | 0.71 | 0.3 | X | 1.01 | 4.81 | 0.26972 | 0.70297 | 3.7624 | 12.9418 | 10.4918 | 7 | 145.5 | 0.072108 | 5.68 | 5.65 | 6.02 | 121.6 | NR | 780.8 | [21 empty] | SDS-CHBr3 | mg/L | 2.46 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 2.07 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 5.52 | 0.5 | --- | -11.7903 | --- | -1004 | -10.4799 | 152.6723 | SDS-CHBr3 | mg/L | 6.41 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 7.01 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 8 | [7 empty] | 1998-05-11 | 9:00 | 2401.2 | 21 | 68 | 63 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 10.6859 | 7 | 58.5 | 0.18266 | 6.11 | 5.48 | 6.22 | 166.4 | NR | 640 | [21 empty] | SDS-THM4 | mg/L | 9.15 | 45.57 | --- | 134.7362 | --- | 79.921 | 125.1564 | 92.6891 | SDS-THM4 | mg/L | 5.93 | 37.48 | --- | 114.7231 | --- | 84.1782 | 106.4243 | 94.428 | SDS-THM4 | mg/L | 17.45 | 38.03 | --- | 88.4155 | --- | 54.1152 | 83.0431 | 78.9868 | SDS-THM4 | mg/L | 22.24 | 41.6 | --- | 88.9986 | --- | 46.5385 | 83.9938 | 73.5219 | SDS-THM4 | mg/L | 23.93 | 43.98 | --- | 93.0679 | --- | 45.5889 | 87.8847 | 72.7712
|  | Acceptable range of operating pressures | 0 to 600 psi | [7 empty] | 1998-05-12 | 8:30 | 2424.7 | 21.4 | 89 | 84 | 0 | 3.8 | 0.69 | 0.3 |  | 0.99 | 4.79 | 0.26912 | 0.69697 | 3.8384 | 12.5772 | 10.4094 | 7 | 79.5 | 0.13094 | 6.29 | 5.71 | 6.39 | 166.4 | NR | 697.6 | [21 empty] | SDS-MCAA* | mg/L | BMRL | 1.26 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3 to 10 | [7 empty] | 1998-05-13 | 9:07 | 2449.3 | 22.1 | 115 | 110 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 10.344 | 7 | 105.5 | 0.098048 | 8.14 | 8.04 | 7.52 | 185.6 | NR | 716.8 | [21 empty] | SDS-DCAA* | mg/L | 2.62 | 14.2 | --- | 42.551 | --- | 81.5493 | 39.5051 | 93.3679 | SDS-DCAA* | mg/L | 1.86 | 9.84 | --- | 29.3772 | --- | 81.0976 | 27.2782 | 93.1814 | SDS-DCAA* | mg/L | 1.58 | 7.79 | --- | 22.9938 | --- | 79.7176 | 21.3727 | 92.6074 | SDS-DCAA* | mg/L | 3.03 | 9.49 | --- | 25.3059 | --- | 68.0717 | 23.6359 | 87.1805 | SDS-DCAA* | mg/L | 2.62 | 9.38 | --- | 25.9303 | --- | 72.0682 | 24.1828 | 89.1659
|  | Typical pressure drop across a single element (psi) | 3 to 5 psid | [7 empty] | 1998-05-14 | 8:50 | 2472.5 | 22.6 | 96 | 91 | 0 | 3.8 | 0.71 | 0.3 |  | 1.01 | 4.81 | 0.26972 | 0.70297 | 3.7624 | 12.9418 | 10.3379 | 7 | 86.5 | 0.11951 | 6.85 | 6.32 | 6.92 | 192 | NR | 761.6 | [21 empty] | SDS-TCAA* | mg/L | BMRL | 14.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 9.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 6.52 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 1.34 | 8.09 | --- | 24.6159 | --- | 83.4363 | 22.8709 | 94.141 | SDS-TCAA* | mg/L | BMRL | 8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-05-15 | 8:37 | 2496.3 | 23.2 | 97 | 92 | 0 | 3.8 | 0.7 | 0.3 |  | 1 | 4.8 | 0.26942 | 0.7 | 3.8 | 12.7595 | 10.0131 | 7 | 87.5 | 0.11444 | 6.24 | 5.6 | 6.44 | 179.2 | NR | 761.6 | [21 empty] | SDS-MBAA* | mg/L | BMRL | 0.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | 0.24 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [55 empty] | SDS-DBAA* | mg/L | 1.65 | 0.96 | --- | -0.72931 | --- | -71.875 | -0.54781 | 401.197 | SDS-DBAA* | mg/L | 1.13 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1.48 | 1.21 | --- | 0.54897 | --- | -22.314 | 0.61945 | -138.9222 | SDS-DBAA* | mg/L | 3.25 | 1.24 | --- | -3.681 | --- | -162.0968 | -3.1614 | 202.8018 | SDS-DBAA* | mg/L | 3.04 | 1.11 | --- | -3.6152 | --- | -173.8739 | -3.1162 | 197.5534
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 mg/L for 1 hour | [55 empty] | SDS-BCAA* | mg/L | 2.23 | 6.45 | --- | 16.7817 | --- | 65.4264 | 15.6717 | 85.7705 | SDS-BCAA* | mg/L | 1.62 | 4.94 | --- | 13.0683 | --- | 67.2065 | 12.195 | 86.7159 | SDS-BCAA* | mg/L | 1.42 | 4.25 | --- | 11.1786 | --- | 66.5882 | 10.4399 | 86.3983 | SDS-BCAA* | mg/L | 2.92 | 4.66 | --- | 8.92 | --- | 37.3391 | 8.4702 | 65.5261 | SDS-BCAA* | mg/L | 2.75 | 4.63 | --- | 9.2328 | --- | 40.6048 | 8.7468 | 68.5598
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [56 empty] | SDS-TBAA | mg/L | 1.49 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | 1.09 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | 1.28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [56 empty] | SDS-CDBAA | mg/L | 1.05 | 2.43 | --- | 5.8086 | --- | 56.7901 | 5.4456 | 80.7185 | SDS-CDBAA | mg/L | BMRL | 1.86 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.49 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.53 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-DCBAA | mg/L | 1.09 | 11.1 | --- | 35.6072 | --- | 90.1802 | 32.9742 | 96.6944 | SDS-DCBAA | mg/L | BMRL | 7.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 5.81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[59 empty] | SDS-HAA5 | mg/L | 4.27 | 31.82 | --- | 99.27 | --- | 86.5808 | 92.0233 | 95.3599 | SDS-HAA5 | mg/L | 3.23 | 19.51 | --- | 59.3679 | --- | 83.4444 | 55.0857 | 94.1364 | SDS-HAA5 | mg/L | 3.06 | 15.52 | --- | 46.0255 | --- | 80.2835 | 42.7729 | 92.8459 | SDS-HAA5 | mg/L | 7.62 | 18.82 | --- | 46.2407 | --- | 59.5112 | 43.3453 | 82.4203 | SDS-HAA5 | mg/L | 5.66 | 18.49 | --- | 49.9014 | --- | 69.3889 | 46.5846 | 87.8501
[59 empty] | SDS-HAA6 | mg/L | 6.5 | 38.27 | --- | 116.0517 | --- | 83.0154 | 107.695 | 93.9644 | SDS-HAA6 | mg/L | 4.85 | 24.45 | --- | 72.4362 | --- | 80.1636 | 67.2807 | 92.7914 | SDS-HAA6 | mg/L | 4.48 | 19.77 | --- | 57.2041 | --- | 77.3394 | 53.2127 | 91.581 | SDS-HAA6 | mg/L | 10.54 | 23.48 | --- | 55.1607 | --- | 55.1107 | 51.8155 | 79.6586 | SDS-HAA6 | mg/L | 8.41 | 23.12 | --- | 59.1341 | --- | 63.6246 | 55.3314 | 84.8007
[59 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[59 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[59 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[60 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[60 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[59 empty] | Qp/QT (THM4), % | -72.57 | 26.2768 |  | Qp/QT (HAA5), % | -80.5082 | 17.4955 |  |  |  | Qp/QT (THM4), % | -109.4136 | 4.691 |  | Qp/QT (HAA5), % | -211.855 | -46.0074 |  |  |  | Qp/QT (THM4), % | -165.0632 | 9.8639 |  | Qp/QT (HAA5), % | -308.8283 | -92.1348 |  |  |  | Qp/QT (THM4), % | -157.0248 | 28.9256 |  | Qp/QT (HAA5), % | -314.1071 | -73.0357 |  |  |  | Qp/QT (THM4), % | -139.7506 | 39.8005 |  | Qp/QT (HAA5), % | -276.7732 | -66.3289
[59 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 39.1982 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA
[59 empty] | SDS-HAA5b, mg/L | NA | 24.5807 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 18.7463 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 14.291 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 15.5803 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 13.3836 |  | SDS-HAA5b, mg/L | NA | NA
[59 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA
[59 empty] | SDS-CDb, mg/L | NA | 1.7321 |  | SDS-CDb, mg/L | NA | 1.8551 |  |  |  | SDS-CDb, mg/L | NA | 1.7484 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 2.0718 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.895 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.7428 |  | SDS-CDb, mg/L | NA | NA
[59 empty] | TOCb, mg/L | NA | 2.058 |  | TOCb, mg/L | NA | 2.2091 |  |  |  | TOCb, mg/L | NA | 3.0704 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 2.4055 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 1.8572 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 1.7744 |  | TOCb, mg/L | NA | NA
[59 empty] | UV254 b, cm-1 | NA | 0.05054 |  | UV254 b, cm-1 | NA | 0.053702 |  |  |  | UV254 b, cm-1 | NA | 0.056311 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.057646 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.046612 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.044856 |  | UV254 b, cm-1 | NA | NA
[59 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | 79.5309 |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | 90 |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | 92.8926 |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | 100 |  | Bromideb, mg/L | NA | NA
[59 empty] | Alkb, mg/L CaCO3 | NA | 29.1096 |  | Alkb, mg/L CaCO3 | NA | 30.0755 |  |  |  | Alkb, mg/L CaCO3 | NA | 25.0938 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 24.5068 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 56.2645 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 54.214 |  | Alkb, mg/L CaCO3 | NA | NA
[59 empty] | T-Hdb, mg/L CaCO3 | NA | 162.8521 |  | T-Hdb, mg/L CaCO3 | NA | 176.9373 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 190.2458 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 163.4531 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 169.595 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 155.7966 |  | T-Hdb, mg/L CaCO3 | NA | NA
[59 empty] | Ca-Hdb, mg/L CaCO3 | NA | 134.8417 |  | Ca-Hdb, mg/L CaCO3 | NA | 146.5911 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 168.1277 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 146.7255 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 163.0702 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 149.7866 |  | Ca-Hdb, mg/L CaCO3 | NA | NA
[59 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[59 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[59 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[59 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[59 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[59 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[59 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[59 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[59 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[59 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on AA31: Carollo Engineers: Fuse was blown and required temporary pilot plant shut down.
Note on AI5: Carollo Engineers: Estimated osmotic pressure is representative of the 4th quarter data where TDS in the feed stream was measured appropriately.
Note on AM6: Carollo Engineers: pH was controlled by injecting sulfuric acid with a metering pump which was controlled manually. Daily shifts in alkalinity caused wide variations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of the variability in permeate TDS.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CL37: Carollo Engineers: Data verified by Carollo 8/6/99. Note that brominated THM concentrations are high. This is expected since this membrane allows more TDS and bromide to pass to the permeate.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CW37: Carollo Engineers: Data verified by Carollo 8/6/99. Note that brominated THM concentrations are high. This is expected since this membrane allows more TDS and bromide to pass to the permeate.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DH37: Carollo Engineers: Data verified by Carollo 8/6/99. Note that brominated THM concentrations are high. This is expected since this membrane allows more TDS and bromide to pass to the permeate.

## NF200 4th Quarter
FIELD-SET 4: 4th QUARTER SEBST RESULTS (FILE: sebst-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: SEBST Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 4-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 4-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 4-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 4-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [52 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Water District No. 1 of Johnson County, KS | Membrane manufacturer | Osmonics-Desal-PPC | Average yearly temperature of feed water, TavgoC (oC) | 15 | Alkalinity (mg/L as CaCO3) | 50 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.68 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | 0.72 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | KS 2009110 | Membrane trade name | PPC B22-1 | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | #VALUE! | Calcium Hardness (mg/L as CaCO3) | 128.75 | Lime Softening (Ca(OH)2) | 1802 pounds per M.G. net filtered as Ca(OH)2 | Full-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.95 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.87 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.82 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.89 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.89 | [7 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Membrane element model number | NR |  |  | LSI | 1.1 | Ferric Sulfate (Fe2(SO4)3) | 107.8 pounds per M.G. net filtered as Fe | Full-Scale | 1998-05-15 | 10:30 | 2497 | 23 | 58 | 54 | 0 | 3.8 | 0.56 | 0.3 |  | 0.86 | 4.66 | 0.32021 | 0.65116 | 4.4186 | 12.6 | 9.9466 | 7 | 49 | 0.20299 | 5.83 | 5.08 | 5.45 | 76.8 | NR | 953.6 | [22 empty] | Influent flow rate during sample collection (gpm) | 4.74 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.67 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.62 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.69 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.69 | [7 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) |  | Potassium Perm. (KMnO4) | 1.9 pounds per M.G. net filtered | Full-Scale | 1998-05-16 | 13:00 | 2523.7 | 23.8 | 70 | 66 | 0 | 3.8 | 0.56 | 0.3 |  | 0.86 | 4.66 | 0.32021 | 0.65116 | 4.4186 | 12.6 | 9.7141 | 7 | 61 | 0.15925 | 6.35 | 6.45 | 6.78 | 44.8 | NR | 819.2 | [71 empty] | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | < 0.006 | Polymer | 5.5 pounds per M.G. net filtered | Full-Scale | 1998-05-17 | 13:40 | 2526.7 | 24 | 60 | 56 | 0 | 3.8 | 0.58 | 0.3 |  | 0.88 | 4.68 | 0.32094 | 0.65909 | 4.3182 | 13.05 | 10.0017 | 7 | 51 | 0.19611 | 8.75 | 8.64 | 8.81 | 76.8 | NR | 723.2 | [21 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin film composite | Design flux, FW (gfd) | 10 | Dissolved aluminum (mg/L) | 5 | Carbon | 14.6 pounds per M.G. net filtered | Full-Scale | 1998-05-18 | 10:00 | 2547.3 | 23.4 | 65 | 59 | 0 | 3.8 | 0.64 | 0.25 |  | 0.89 | 4.69 | 0.31948 | 0.7191 | 4.2697 | 14.4 | 11.2339 | 7 | 55 | 0.20425 | 6.14 | 6.29 | 6.9 | 17.28 | NR | 908.8 | [21 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | NR | Permeate flow rate, Qp (gpm) | 0.44444 | Total aluminum (mg/L) | NA | Sand filtration |  | Pilot-Scale | 1998-05-19 | 9:40 | 2571 | 24 | 85 | 80 | 0 | 3.8 | 0.74 | 0.3 |  | 1.04 | 4.84 | 0.32679 | 0.71154 | 3.6538 | 16.65 | 12.7608 | 7 | 75.5 | 0.16902 | 5.15 | 3.65 | 4.2 | 31.36 | NR | 1068.8 | [21 empty] | Sampling date | MM/DD/YY | 1998-05-21 | 1998-05-21 | 1998-05-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-19 | 1998-06-19 | 1998-06-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NR | Feed flow rate, QF (gpm) | 0.59259 | Fluoride (mg/L) | 0.44 | Pre-filter | 5 mm inline cartridge filter | Pilot-Scale | 1998-05-20 | 15:15 | 2600.5 | 25.3 | 60 | 56 | 0 | 3.8 | 0.56 | 0.3 |  | 0.86 | 4.66 | 0.32021 | 0.65116 | 4.4186 | 12.6 | 9.2928 | 7 | 51 | 0.18221 | 5.03 | 3.46 | 3.95 | 70.4 | NR | 1335.68 | [21 empty] | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:33 | 9:33 | 9:33 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:15 | 9:15 | 9:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:15 | 9:15 | 9:15 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5973.17
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.14815 | Phosphate (mg/L) | 0.48 | Acid addition | 93% H2SO4; 0.33 ml/L | Pilot-Scale | 1998-05-21 | 9:00 | 2618.3 | 24.8 | 57 | 53 | 0 | 3.8 | 0.65 | 0.3 |  | 0.95 | 4.75 | 0.3235 | 0.68421 | 4 | 14.625 | 10.9469 | 7 | 48 | 0.22806 | 7.74 | 6.94 | 7.57 | 32 | NR | 742.4 | [21 empty] | Operation time | hh.hh | 2618.3 | 2618.3 | 2618.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2784.8 | 2784.8 | 2784.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2990.9 | 2990.9 | 2990.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3105.9 | 3105.9 | 3105.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3105.9 | 3105.9 | 3105.9 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 406
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | NR | Sulfate (mg/L) | 201 | Antiscalant addition | 3000 mg/L Sodium Hexametaphospate; 1.3 ml/L | Pilot-Scale | 1998-05-22 | 8:45 | 2642.1 | 24.6 | 57 | 53 | 0 | 3.8 | 0.65 | 0.23 |  | 0.88 | 4.68 | 0.31838 | 0.73864 | 4.3182 | 14.625 | 11.0118 | 7 | 48 | 0.22941 | 8.32 | 7.68 | 8 | 51.2 | NR | 908.8 | [21 empty] | pH | --- | 7.78 | 6.94 | 7.57 | --- | --- | --- | --- | --- | pH | --- | 6.24 | 6.19 | 6.95 | --- | --- | --- | --- | --- | pH | --- | 6.6 | 6.71 | 7.31 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 6.4 | 6.72 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 6.4 | 6.72 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 30
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | NR | Calcium (mg/L) | 51.5 |  |  |  | 1998-05-23 | 11:15 | 2668.4 | 25.1 | 57 | 53 | 0 | 3.8 | 0.68 | 0.3 |  | 0.98 | 4.78 | 0.32459 | 0.69388 | 3.8776 | 15.3 | 11.351 | 7 | 48 | 0.23648 | 6.53 | 6.38 | 7.25 | 64 | NR | 1017.6 | [21 empty] | Temperature | oC | 24.8 | 24.8 | 24.8 | --- | --- | --- | --- | --- | Temperature | oC | 22.3 | 22.3 | 22.3 | --- | --- | --- | --- | --- | Temperature | oC | 22.9 | 22.9 | 22.9 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 64 | Design influent flow rate2, QI (gpm) | 4.4 | Barium (mg/L) | 0.016 |  |  |  | 1998-05-24 | 11:45 | 2692.9 | 24.3 | 57 | 53 | 0 | 3.8 | 0.67 | 0.23 |  | 0.9 | 4.7 | 0.31911 | 0.74444 | 4.2222 | 15.075 | 11.4517 | 7 | 48 | 0.23858 | 6.45 | 6.38 | 7.2 | 76.8 | NR | 947.2 | [21 empty] | Alkalinity | mg/L as CaCO3 | BMRL | 11.7 | 27 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 6 | 16 | 34 | 44.4615 | -30.7692 | 62.5 | 41.8104 | 85.6495 | Alkalinity | mg/L as CaCO3 | 13 | 22 | 63 | 45.1429 | 28.3447 | 40.9091 | 43.0891 | 69.8299 | Alkalinity | mg/L as CaCO3 | 8 | 17 | 44 | 42.6154 | 3.1469 | 52.9412 | 40.1849 | 80.092 | Alkalinity | mg/L as CaCO3 | 8 | 20 | 45 | 54.1538 | -20.3419 | 60 | 50.9132 | 84.287 | Electric Rate ($/kW-h) | 0.044
Mailing Address |  | Design flux, FW (gfd) | NR | Design recycle flow rate, QR (gpm) | 3.8074 | Strontium (mg/L) | 0.247 |  |  |  | 1998-05-25 | 10:00 | 2715.1 | 23 | 55 | 51 | 0 | 3.8 | 0.65 | 0.23 |  | 0.88 | 4.68 | 0.31838 | 0.73864 | 4.3182 | 14.625 | 11.5451 | 7 | 46 | 0.25098 | 6.85 | 6.65 | 7.29 | 51.2 | NR | 774.4 | [21 empty] | Total dissolved solids | mg/L | 32 | NR | 742.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 70.4 | NR | 825.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 40.3 | 213 | 472 | 657.0857 | -39.2131 | 81.0798 | 617.6755 | 93.4755 | Total dissolved solids | mg/L | 59 | 258 | 718 | 824.3846 | -14.8168 | 77.1318 | 770.6445 | 92.3441 | Total dissolved solids | mg/L | 59 | 258 | 718 | 824.3846 | -14.8168 | 77.1318 | 770.6445 | 92.3441 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | NR | Recycle ratio, r | 6.425 | Reactive silica (mg/L as SiO2) | 8.11 |  |  |  | 1998-05-26 | 9:05 | 2738.2 | 22.1 | 56 | 52 | 0 | 3.8 | 0.64 | 0.23 |  | 0.87 | 4.67 | 0.31801 | 0.73563 | 4.3678 | 14.4 | 11.674 | 7 | 47 | 0.24838 | 7.99 | 7.6 | 7.87 | 51.2 | NR | 768 | [21 empty] | Total hardness | mg/L as CaCO3 | 1.24 | 180 | 304 | 559.865 | -84.1661 | 99.3111 | 521.7984 | 99.7624 | Total hardness | mg/L as CaCO3 | BMRL | 139 | 394 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 12.8 | 138 | 342 | 459.9429 | -34.4862 | 90.7246 | 431.3722 | 97.0327 | Total hardness | mg/L as CaCO3 | 10.2 | 150 | 381 | 547.8923 | -43.8038 | 93.2 | 510.1392 | 98.0005 | Total hardness | mg/L as CaCO3 | 10 | 149 | 381 | 544.6154 | -42.9437 | 93.2886 | 507.0783 | 98.0279 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | NR | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | < 1.0 |  |  |  | 1998-05-27 | 8:35 | 2761.3 | 21.7 | 55 | 51 | 0 | 3.8 | 0.64 | 0.23 |  | 0.87 | 4.67 | 0.31801 | 0.73563 | 4.3678 | 14.4 | 11.8128 | 7 | 46 | 0.2568 | 5.61 | 4.67 | 6.23 | 51.2 | NR | 844.8 | [21 empty] | Calcium hardness | mg/L as CaCO3 | 1.24 | 171 | 282 | 531.74 | -88.5603 | 99.2749 | 495.5899 | 99.7498 | Calcium hardness | mg/L as CaCO3 | BMRL | 126 | 350 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 11.4 | 119 | 300 | 395.6857 | -31.8952 | 90.4202 | 371.1314 | 96.9283 | Calcium hardness | mg/L as CaCO3 | 9.71 | 139 | 352 | 506.9792 | -44.0282 | 93.0144 | 472.0644 | 97.9431 | Calcium hardness | mg/L as CaCO3 | 9.46 | 138 | 352 | 503.8446 | -43.1377 | 93.1449 | 469.1323 | 97.9835 | Current Process Water Rate ($/1000 gal) | 3.04
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | NR | the desired operating conditions. |  | SDI | 4.6 |  |  |  | 1998-05-28 | 8:00 | 2784.8 | 22.3 | 55 | 51 | 0 | 3.8 | 0.64 | 0.23 |  | 0.87 | 4.67 | 0.31801 | 0.73563 | 4.3678 | 14.4 | 11.6051 | 7 | 46 | 0.25229 | 6.24 | 6.19 | 6.95 | 70.4 | NR | 832 | [21 empty] | Turbidity | ntu | 0.1 | 2.6 | 0.6 | 7.9125 | -1218.75 | 96.1538 | 7.3801 | 98.645 | Turbidity | ntu | 0.05 | 0.5 | 0.15 | 1.7808 | -1087.1795 | 90 | 1.6615 | 96.9906 | Turbidity | ntu | 0.05 | 0.95 | 0.75 | 3.2643 | -335.2381 | 94.7368 | 3.0589 | 98.3654 | Turbidity | ntu | 0.05 | 0.6 | 0.35 | 2.1654 | -518.6813 | 91.6667 | 2.0169 | 97.5209 | Turbidity | ntu | 0.05 | 0.6 | 0.35 | 2.1654 | -518.6813 | 91.6667 | 2.0169 | 97.5209 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | NR | 2: The design influent flow rate must be within the range established by the |  | MFI | 0.55 |  |  |  | 1998-05-29 | 9:00 | 2809.2 | 23 | 55 | 50 | 0 | 3.8 | 0.64 | 0.23 |  | 0.87 | 4.67 | 0.31801 | 0.73563 | 4.3678 | 14.4 | 11.3675 | 8.1179 | 44.3821 | 0.25613 | 6.2 | 6.83 | 6.83 | 57.6 | 288 | 608 | 929.113 | -52.8146 | 80 | 869.3948 | 93.3747 | [16 empty] | Ammonia | mg NH3-N / L | 0.026 | 0.049 | 0.046 | 0.097875 | -112.7717 | 46.9388 | 0.092977 | 72.0362 | Ammonia | mg NH3-N / L | BMRL | 0.039 | 0.068 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.0337 | 0.0628 | 0.139 | 0.13763 | 0.98664 | 46.3376 | 0.13099 | 74.2724 | Ammonia | mg NH3-N / L | 0.036 | 0.044 | 0.068 | 0.066769 | 1.81 | 18.1818 | 0.064609 | 44.2801 | Ammonia | mg NH3-N / L | 0.036 | 0.047 | 0.083 | 0.078308 | 5.6534 | 23.4043 | 0.075337 | 52.2148
|  | Minimum flow rate to the element, QI, min (gpm) | NR | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-05-30 | 7:00 | 2831.2 | 24.9 | 55 | 50 | 0 | 3.8 | 0.64 | 0.23 |  | 0.87 | 4.67 | 0.31801 | 0.73563 | 4.3678 | 14.4 | 10.7467 | 7.8924 | 44.6076 | 0.24092 | 6.62 | 6.95 | 7.07 | 102.4 | 326.4 | 684.8 | 949.7043 | -38.6835 | 68.6275 | 891.6449 | 88.5156 | [16 empty] | Total organic carbon | mg/L | 0.4 | 1.86 | 4.71 | 4.9625 | -5.3609 | 78.4946 | 4.6516 | 91.4008 | Total organic carbon | mg/L | 0.57 | 2.27 | 7 | 7.1085 | -1.5495 | 74.8899 | 6.6578 | 91.4386 | Total organic carbon | mg/L | 0.15 | 1.7 | 4.1 | 5.6857 | -38.676 | 91.1765 | 5.332 | 97.1868 | Total organic carbon | mg/L | 0.57 | 2.91 | 6.49 | 9.57 | -47.4576 | 80.4124 | 8.9381 | 93.6228 | Total organic carbon | mg/L | 0.44 | 2.81 | 6.63 | 9.5554 | -44.1234 | 84.3416 | 8.9154 | 95.0647
Plant Name | Facility 2 | Total width of all membrane envelopes in the element, w (ft) | 11.2875 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-05-31 | 10:30 | 2858.7 | 23.6 | 55 | 50 | 0 | 3.8 | 0.66 | 0.23 |  | 0.89 | 4.69 | 0.31874 | 0.74157 | 4.2697 | 14.85 | 11.5167 | 9.6695 | 42.8305 | 0.26889 | 6.67 | 6.93 | 6.95 | 204.8 | 473.6 | 691.2 | 1244.9391 | -80.1127 | 56.7568 | 1171.7524 | 82.5219 | [16 empty] | UV254 | cm-1 | 0.024 | 0.048 | 0.05 | 0.099 | -98 | 50 | 0.093889 | 74.438 | UV254 | cm-1 | 0.022 | 0.052 | 0.119 | 0.13738 | -15.4493 | 57.6923 | 0.12943 | 83.0026 | UV254 | cm-1 | 0.018 | 0.054 | 0.108 | 0.14657 | -35.7143 | 66.6667 | 0.13836 | 86.9901 | UV254 | cm-1 | 0.022 | 0.06 | 0.128 | 0.16815 | -31.3702 | 63.3333 | 0.15789 | 86.0664 | UV254 | cm-1 | 0.02 | 0.058 | 0.13 | 0.16615 | -27.8107 | 65.5172 | 0.15589 | 87.1706
Treatment Plant Category | CS/SOFT | Feed spacer thickness, T (ft) | 0.0027 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-06-01 | 10:00 | 2882.3 | 24.9 | 55 | 50 | 0 | 3.8 | 0.68 | 0.23 |  | 0.91 | 4.71 | 0.31948 | 0.74725 | 4.1758 | 15.3 | 11.4183 | 7.518 | 44.982 | 0.25384 | 8.32 | 7.92 | 7.75 | 96 | 300.8 | 652.8 | 906.2957 | -38.8321 | 68.0851 | 847.803 | 88.6766 | [16 empty] | SUVA | L/(mg*m) | 6 | 2.5806 | 1.0616 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.8596 | 2.2907 | 1.7 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 12 | 3.1765 | 2.6341 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.8596 | 2.0619 | 1.9723 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.5455 | 2.0641 | 1.9608 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | This membrane has been discontinued | Manufacturer reported TDS rejection, RejTDS (decimal) | NA | [5 empty] | 1998-06-02 | 10:00 | 2905.4 | 25 | 55 | 50 | 0 | 3.8 | 0.66 | 0.23 |  | 0.89 | 4.69 | 0.31874 | 0.74157 | 4.2697 | 14.85 | 11.0498 | 5.9859 | 46.5141 | 0.23756 | 6.46 | 7.41 | 7.14 | 121.6 | 288 | 755.2 | 765.4957 | -1.3633 | 57.7778 | 720.1896 | 83.1156 | [16 empty] | Bromide | mg/L | BMRL | 80 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 70 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 50 | 50 | --- | 50 | --- | 0 | 50 | 0 | Bromide | mg/L | BMRL | 70 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 70 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 380 | Purchase price for an equivalent 8" x 40 " element ($) | This membrane has been discontinued | Feed TDS, TDSF (mg/L) | NA | [5 empty] | 1998-06-03 | 8:23 | 2928.8 | 24.7 | 53 | 49 | 0 | 3.8 | 0.65 | 0.23 |  | 0.88 | 4.68 | 0.31838 | 0.73864 | 4.3182 | 14.625 | 10.9793 |  | 51 | 0.21528 | 7.12 | 6.79 | 7.56 | 57.6 | NR | 825.6 | [21 empty] | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.4 | 3 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | KS 2009110 |  |  | Waste TDS, TDSW (mg/L) | #VALUE! | [5 empty] | 1998-06-17 | 9:15 | 2958.2 | 21.7 | 54 | 50 | 0 | 3.8 | 0.6 | 0.23 |  | 0.83 | 4.63 | 0.31655 | 0.72289 | 4.5783 | 13.5 | 11.0745 | 5.231 | 46.769 | 0.23679 | 7.54 | 7.55 | 8.2 | 88 | 243 | 534 | 647.3478 | -21.2262 | 63.786 | 611.105 | 85.5999 | [16 empty] | SDS-Free Cl2 residual | mg/L | 0.7 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | 0.9 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.7 | 0.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.8 | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.8 | 0.5 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 1 | Additional Information |  | Permeate TDS, TDSp (mg/L) | #VALUE! | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-06-18 | 9:15 | 2982.2 | 22.6 | 47 | 43 | 0 | 3.8 | 0.57 | 0.23 |  | 0.8 | 4.6 | 0.31545 | 0.7125 | 4.75 | 12.825 | 10.2446 | 6.3298 | 38.6702 | 0.26492 | 6.18 | 6.5 | 6.8 | 47 | 241 | 532 | 721.7826 | -35.6734 | 80.4979 | 679.9754 | 93.088 | [16 empty] | SDS-Cl2 demand | mg/L | 0.7 | 2.35 | --- | 5.8563 | --- | 70.2128 | 5.5049 | 87.284 | SDS-Cl2 demand | mg/L | 0.7 | 2.1 | --- | 6.0846 | --- | 66.6667 | 5.7135 | 87.7482 | SDS-Cl2 demand | mg/L | 0.7 | 2.2 | --- | 6.0571 | --- | 68.1818 | 5.7148 | 87.7512 | SDS-Cl2 demand | mg/L | 0.6 | 2.5 | --- | 7.9077 | --- | 76 | 7.3946 | 91.886 | SDS-Cl2 demand | mg/L | 0.6 | 2.5 | --- | 7.9077 | --- | 76 | 7.3946 | 91.886
Historical Average Water Temperature (oC) | 13.1 | Design cross-flow velocity (fps) | NR | Influent TDS, TDSI (mg/L) | #VALUE! | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-06-19 | 9:33 | 2990.9 | 22.9 | 54 | 50 | 0 | 3.8 | 0.59 | 0.23 |  | 0.82 | 4.62 | 0.31619 | 0.71951 | 4.6341 | 13.275 | 10.5104 | 5.764 | 46.236 | 0.22732 | 6.6 | 6.71 | 7.31 | 40.3 | 213 | 472 | 656.013 | -38.9858 | 81.0798 | 616.698 | 93.4652 | [16 empty] | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15 | 15 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 94 | Required influent flow to permeate flow rate ratio, QI:Qp | NR | Osmotic pressure gradient, Dp (psi) | #VALUE! | [5 empty] | 1998-06-20 | 12:00 | 3017.4 | 24.1 | 54 | 50 | 0 | 3.8 | 0.68 | 0.23 |  | 0.91 | 4.71 | 0.31948 | 0.74725 | 4.1758 | 15.3 | 11.6916 | 6.5012 | 45.4988 | 0.25696 | 6.61 | 7.06 | 7.41 | 41.9 | 219 | 515 | 742.6 | -44.1942 | 80.8676 | 692.0187 | 93.9453 | [16 empty] | SDS-Chlorination pH | --- | 7.82 | 7.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.63 | 7.57 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.32 | 7.4 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.45 | 7.49 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.45 | 7.49 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NR | [7 empty] | 1998-06-21 | 11:55 | 3041.2 | 24.8 | 52 | 48 | 0 | 3.8 | 0.67 | 0.23 |  | 0.9 | 4.7 | 0.31911 | 0.74444 | 4.2222 | 15.075 | 11.2837 | 6.9521 | 43.0479 | 0.26212 | 7.1 | 7.56 | 7.7 | 44.7 | 236 | 550 | 793.2652 | -44.23 | 81.0593 | 739.91 | 93.9587 | [16 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | NR | Estimate the Required Influent Pressure | [6 empty] | 1998-06-22 | 9:05 | 3062.4 | 24.7 | 50 | 45 | 0 | 3.8 | 0.64 | 0.23 |  | 0.87 | 4.67 | 0.31801 | 0.73563 | 4.3678 | 14.4 | 10.8104 | 7.1138 | 40.3862 | 0.26768 | 6.14 | 5.66 | 6.79 | 48.1 | 250 | 586 | 811.8087 | -38.5339 | 80.76 | 759.4775 | 93.6667 | [16 empty] | SDS-TOX | mg Cl- /L | BMRL | 103 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 138 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 25 | 105 | --- | 310.7143 | --- | 76.1905 | 292.4583 | 91.4518 | SDS-TOX | mg Cl- /L | BMRL | 132 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 115 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | NR | Estimated system pressure losses, DPloss (psi) | NA | [5 empty] | 1998-06-23 | 9:15 | 3081.9 | 25.2 | 59 | 54 | 0 | 3.8 | 0.6 | 0.23 |  | 0.83 | 4.63 | 0.31655 | 0.72289 | 4.5783 | 13.5 | 9.9861 | 6.6654 | 49.8346 | 0.20038 | 6.62 | 6.4 | 7.5 | 51.5 | 249 | 604 | 764.2174 | -26.5261 | 79.3173 | 718.037 | 92.8277 | [16 empty] | SDS-CHCl3 | mg/L | 2.29 | 25.7 | --- | 75.4463 | --- | 91.0895 | 70.4611 | 96.75 | SDS-CHCl3 | mg/L | 2.01 | 29.5 | --- | 107.7408 | --- | 93.1864 | 100.4528 | 97.9991 | SDS-CHCl3 | mg/L | 2.4 | 27.2 | --- | 90.9714 | --- | 91.1765 | 85.3121 | 97.1868 | SDS-CHCl3 | mg/L | 2.49 | 29.7 | --- | 107.1438 | --- | 91.6162 | 99.7958 | 97.5049 | SDS-CHCl3 | mg/L | 2.61 | 28.6 | --- | 102.5715 | --- | 90.8741 | 95.5529 | 97.2685
|  | (e.g., solute type and concentration) |  | Design permeate pressure, Pp (psi) | NA | [5 empty] | 1998-06-24 | 9:15 | 3105.9 | 26 | 54 | 50 | 0 | 3.8 | 0.66 | 0.23 |  | 0.89 | 4.69 | 0.31874 | 0.74157 | 4.2697 | 14.85 | 10.728 | 7.1586 | 44.8414 | 0.23924 | 6.16 | 6.4 | 6.72 | 59 | 258 | 718 | 829.0435 | -15.4657 | 77.1318 | 774.8613 | 92.3857 | [16 empty] | SDS-BDCM | mg/L | BMRL | 13.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.58 | 8.69 | --- | 28.9262 | --- | 81.8182 | 27.0412 | 94.1571 | SDS-BDCM | mg/L | 2.14 | 12.7 | --- | 39.8543 | --- | 83.1496 | 37.4445 | 94.2849 | SDS-BDCM | mg/L | 2.74 | 14.8 | --- | 49.1246 | --- | 81.4865 | 45.8678 | 94.0263 | SDS-BDCM | mg/L | 2.86 | 14.3 | --- | 46.86 | --- | 80 | 43.7706 | 93.4659
|  | Variability of rejection of reference solute (%) | NR | Required influent pressure, PI (psi) | #VALUE! | [5 empty] | 1998-06-25 | 9:15 | 3129.8 | 26.4 | 53 | 49 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.32021 | 0.75269 | 4.086 | 15.75 | 11.2444 | 6.0283 | 44.9717 | 0.25003 | 5.37 | 5.8 | 4.4 | 43 | 204 | 535 | 694 | -29.7196 | 78.9216 | 645.8288 | 93.3419 | [16 empty] | SDS-DBCM | mg/L | BMRL | 5.42 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1.66 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 3.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 1.27 | 5.08 | --- | 15.9238 | --- | 75 | 14.895 | 91.4736 | SDS-DBCM | mg/L | 1.41 | 4.69 | --- | 14.0254 | --- | 69.936 | 13.1396 | 89.2691
|  | Standard testing recovery (%) | NR | [7 empty] | 1998-06-26 | 9:06 | 3153.7 | 27.1 | 53 | 49 | 0 | 3.8 | 0.72 | 0.23 |  | 0.95 | 4.75 | 0.32094 | 0.75789 | 4 | 16.2 | 11.3288 | 6.7682 | 44.2318 | 0.25612 | 6.78 | 6.68 | 7.45 | 44.7 | 222 | 626 | 777.0261 | -24.1256 | 79.8649 | 721.5235 | 93.8048 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | NR | [7 empty] | 1998-06-27 | 12:20 | 3180.9 | 28.3 | 53 | 49 | 0 | 3.8 | 0.67 | 0.23 |  | 0.9 | 4.7 | 0.31911 | 0.74444 | 4.2222 | 15.075 | 10.1747 | 8.373 | 42.627 | 0.23869 | 6.59 | 6.34 | 7.36 | 69.6 | 300 | 723 | 971.1652 | -34.3244 | 76.8 | 906.9047 | 92.3255 | [16 empty] | SDS-THM4 | mg/L | 2.29 | 44.22 | --- | 133.3212 | --- | 94.8213 | 124.3923 | 98.1591 | SDS-THM4 | mg/L | 3.59 | 39.85 | --- | 143.0515 | --- | 90.9912 | 133.4385 | 97.3096 | SDS-THM4 | mg/L | 4.54 | 43.2 | --- | 142.6114 | --- | 89.4907 | 133.7892 | 96.6066 | SDS-THM4 | mg/L | 6.5 | 49.58 | --- | 172.1923 | --- | 86.8899 | 160.5585 | 95.9516 | SDS-THM4 | mg/L | 6.88 | 47.59 | --- | 163.4569 | --- | 85.5432 | 152.4632 | 95.4874
|  | Acceptable range of operating pressures | 225 max | [7 empty] | 1998-06-28 | 12:15 | 3204.8 | 28.7 | 53 | 49 | 0 | 3.8 | 0.75 | 0.23 |  | 0.98 | 4.78 | 0.32203 | 0.76531 | 3.8776 | 16.875 | 11.2557 | 7.594 | 43.406 | 0.25931 | 6.05 | 6.8 | 6.68 | 46.6 | 240 | 626 | 870.6522 | -39.0818 | 80.5833 | 806.0037 | 94.2184 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 2.46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 2.93 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 3.69 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 4-11 | [7 empty] | 1998-06-29 | 10:10 | 3220.4 | 28.5 | 51 | 47 | 0 | 3.8 | 0.75 | 0.23 |  | 0.98 | 4.78 | 0.32203 | 0.76531 | 3.8776 | 16.875 | 11.3225 | 7.5862 | 41.4138 | 0.2734 | 6.39 | 6.58 | 7.18 | 58.8 | 252 | 625 | 882 | -41.12 | 76.6667 | 817.4184 | 92.8066 | [16 empty] | SDS-DCAA* | mg/L | 2.18 | 11.1 | --- | 30.055 | --- | 80.3604 | 28.1555 | 92.2573 | SDS-DCAA* | mg/L | 2.35 | 14.6 | --- | 49.4654 | --- | 83.9041 | 46.2178 | 94.9154 | SDS-DCAA* | mg/L | 1.74 | 14.7 | --- | 48.0257 | --- | 88.1633 | 45.0682 | 96.1392 | SDS-DCAA* | mg/L | 3.05 | 20 | --- | 68.2423 | --- | 84.75 | 63.6649 | 95.2093 | SDS-DCAA* | mg/L | 2.24 | 22.6 | --- | 80.5477 | --- | 90.0885 | 75.0495 | 97.0153
|  | Typical pressure drop across a single element (psi) | NR | [7 empty] | 1998-06-30 | 8:55 | 3230.6 | 28.7 | 53 | 49 | 0 | 3.8 | 0.7 | 0.23 |  | 0.93 | 4.73 | 0.32021 | 0.75269 | 4.086 | 15.75 | 10.5054 | 7.1928 | 43.8072 | 0.23981 | 8.28 | 7.4 | 8.19 | 65.9 | 258 | 653 | 842.6522 | -29.0432 | 74.4574 | 785.1758 | 91.607 | [16 empty] | SDS-TCAA* | mg/L | 1.12 | 7.9 | --- | 22.3075 | --- | 85.8228 | 20.8637 | 94.6318 | SDS-TCAA* | mg/L | 2.01 | 13.3 | --- | 45.4331 | --- | 84.8872 | 42.44 | 95.2639 | SDS-TCAA* | mg/L | BMRL | 14.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 1.55 | 18.9 | --- | 68.2808 | --- | 91.7989 | 63.5954 | 97.5627 | SDS-TCAA* | mg/L | 1.02 | 22 | --- | 81.7123 | --- | 95.3636 | 76.0466 | 98.6587
|  | Maximum permissible SDI | NR | [7 empty] | 1998-07-01 | 8:25 | 3254.1 | 28.4 | 53 | 49 | 0 | 3.8 | 0.71 | 0.23 |  | 0.94 | 4.74 | 0.32057 | 0.75532 | 4.0426 | 15.975 | 10.7503 | 6.5409 | 44.4591 | 0.2418 | 6.53 | 7 | 7.59 | 57 | 230 | 657 | 764.0435 | -16.2928 | 75.2174 | 711.0898 | 91.9841 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | 1.07 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | NR | [18 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-DBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.29 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1.19 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1.11 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | NR | [18 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-BCAA* | mg/L | BMRL | 5.89 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.53 | 7.34 | --- | 23.8762 | --- | 79.1553 | 22.3358 | 93.15 | SDS-BCAA* | mg/L | BMRL | 5.03 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.9 | 7.63 | --- | 23.9385 | --- | 75.0983 | 22.3911 | 91.5145 | SDS-BCAA* | mg/L | 1.37 | 7.35 | --- | 24.37 | --- | 81.3605 | 22.7551 | 93.9794
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [19 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [19 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-CDBAA | mg/L | BMRL | 2.14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 2.82 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 1.41 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-DCBAA | mg/L | BMRL | 7.61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 10.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 7.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 12.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 13.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-HAA5 | mg/L | 3.3 | 20.3 | --- | 56.425 | --- | 83.7438 | 52.8049 | 93.7506 | SDS-HAA5 | mg/L | 4.36 | 31.65 | --- | 109.3215 | --- | 86.2243 | 102.0866 | 95.7291 | SDS-HAA5 | mg/L | 2.93 | 28.9 | --- | 95.68 | --- | 89.8616 | 89.7536 | 96.7355 | SDS-HAA5 | mg/L | 5.71 | 42.9 | --- | 148.7485 | --- | 86.69 | 138.7053 | 95.8834 | SDS-HAA5 | mg/L | 3.26 | 48.29 | --- | 176.4523 | --- | 93.2491 | 164.2919 | 98.0157
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-HAA6 | mg/L | 3.3 | 26.19 | --- | 74.8312 | --- | 87.3998 | 69.9569 | 95.2828 | SDS-HAA6 | mg/L | 5.89 | 38.99 | --- | 133.1977 | --- | 84.8936 | 124.4225 | 95.2661 | SDS-HAA6 | mg/L | 2.93 | 33.93 | --- | 113.6443 | --- | 91.3646 | 106.5701 | 97.2506 | SDS-HAA6 | mg/L | 7.61 | 50.53 | --- | 172.6869 | --- | 84.9396 | 161.0963 | 95.2761 | SDS-HAA6 | mg/L | 4.63 | 55.64 | --- | 200.8223 | --- | 91.6786 | 187.047 | 97.5247
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [28 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [28 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Qp/QT (THM4), % | -66.2533 | 19.6041 |  | Qp/QT (HAA5), % | -198.2353 | -39.4118 |  |  |  | Qp/QT (THM4), % | -88.6652 | 10.6178 |  | Qp/QT (HAA5), % | -81.8981 | 17.0392 |  |  |  | Qp/QT (THM4), % | -74.4956 | 18.6239 |  | Qp/QT (HAA5), % | -96.65 | 7.3161 |  |  |  | Qp/QT (THM4), % | -52.0427 | 31.5227 |  | Qp/QT (HAA5), % | -29.8467 | 42.7534 |  |  |  | Qp/QT (THM4), % | -59.9607 | 28.4697 |  | Qp/QT (HAA5), % | -12.6804 | 47.2796
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 33.6716 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 40.3716 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 31.1618 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 28.3425
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-HAA5b, mg/L | NA | 16.9673 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 28.7524 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 24.0634 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 31.1767 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 35.4701 |  | SDS-HAA5b, mg/L | NA | 27
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | 90.1009 |  | SDS-TOXb, mg Cl- /L | NA | 99.1471 |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | SDS-CDb, mg/L | NA | 2.0265 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.9514 |  | SDS-CDb, mg/L | NA | 1.8615 |  |  |  | SDS-CDb, mg/L | NA | 1.9206 |  | SDS-CDb, mg/L | NA | 2.0903 |  |  |  | SDS-CDb, mg/L | NA | 1.9011 |  | SDS-CDb, mg/L | NA | 1.6877 |  |  |  | SDS-CDb, mg/L | NA | 1.9591 |  | SDS-CDb, mg/L | NA | 1.6017
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | TOCb, mg/L | NA | 1.5738 |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | 2.0895 |  | TOCb, mg/L | NA | 1.9803 |  |  |  | TOCb, mg/L | NA | 1.4113 |  | TOCb, mg/L | NA | 1.5866 |  |  |  | TOCb, mg/L | NA | 2.1724 |  | TOCb, mg/L | NA | 1.9096 |  |  |  | TOCb, mg/L | NA | 2.1353 |  | TOCb, mg/L | NA | 1.6895
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | UV254 b, cm-1 | NA | 0.043295 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | 0.048815 |  | UV254 b, cm-1 | NA | 0.046888 |  |  |  | UV254 b, cm-1 | NA | 0.047295 |  | UV254 b, cm-1 | NA | 0.051366 |  |  |  | UV254 b, cm-1 | NA | 0.048021 |  | UV254 b, cm-1 | NA | 0.043754 |  |  |  | UV254 b, cm-1 | NA | 0.047182 |  | UV254 b, cm-1 | NA | 0.040034
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | 50 |  | Bromideb, mg/L | NA | 50 |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Alkb, mg/L CaCO3 | NA | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 14.9382 |  | Alkb, mg/L CaCO3 | NA | 14.2961 |  |  |  | Alkb, mg/L CaCO3 | NA | 20.3238 |  | Alkb, mg/L CaCO3 | NA | 21.3415 |  |  |  | Alkb, mg/L CaCO3 | NA | 14.163 |  | Alkb, mg/L CaCO3 | NA | 13.1522 |  |  |  | Alkb, mg/L CaCO3 | NA | 16.5836 |  | Alkb, mg/L CaCO3 | NA | 14.3264
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | T-Hdb, mg/L CaCO3 | NA | 144.9557 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | NA | 114.6829 |  | T-Hdb, mg/L CaCO3 | NA | 128.8402 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 105.9312 |  | T-Hdb, mg/L CaCO3 | NA | 90.2307 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 109.4272 |  | T-Hdb, mg/L CaCO3 | NA | 83.2814
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Ca-Hdb, mg/L CaCO3 | NA | 137.7201 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 98.9607 |  | Ca-Hdb, mg/L CaCO3 | NA | 111.1278 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 98.2442 |  | Ca-Hdb, mg/L CaCO3 | NA | 83.7241 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 101.4051 |  | Ca-Hdb, mg/L CaCO3 | NA | 77.2268
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [27 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on AA8: Carollo Engineers: Fuse was blown and required temporary pilot plant shut down.
Note on AA13: Carollo Engineers: Switched Scale inhibitor to Hypersperse SI 300 which is a proprietary organo-phosphonic acid.
Note on AA26: Carollo Engineers: WTP maintenance to settling basins prior to NF. Required pilot plant shut down.
Note on AA29: Carollo Engineers: Low Feed pressure alarm shut down pilot plant.
Note on AA33: Carollo Engineers: Power outage due to electrical storm shut down pilot plant.
Note on AA39: Carollo Engineers: Power outage due to electrical storm shut down pilot plant.
Note on AA40: Carollo Engineers: Power outage due to electrical storm shut down pilot plant.
Note on AI5: Carollo Engineers: Estimated osmotic pressure is representative of the 4th quarter data where TDS in the feed stream was measured appropriately.
Note on AK5: Carollo Engineers: MTCw trend is erratic due to inaccurate feed TDS measurements made during the first part of this study and testing quarter. Feed TDS concentrations effect the osmotic pressure which in turn effect NDP and MTCw.
Note on AM6: Carollo Engineers: pH was controlled by injecting sulfuric acid with a metering pump which was controlled manually. Daily shifts in alkalinity caused wide variations in pH.
Note on AO6: TSC_ADM: Difficulties with pH control and resulting variability in pH may be the cause of the variability in permeate TDS.
Note on AP6: Carollo Engineers: TDS concentrations were measured in the wrong location. Including them here would result in an improper representation of TDS(bulk) and osmotic pressure.
Note on AP20: Carollo Engineers: After this point data was taken from a new sample location. Previous samples were representive of "bulk" TDS concentrations, not feed concentrations.
Note on AP26: Carollo Engineers: After this point it was identified that the Feed TDS was being sampled from the wrong location.
Note on AR6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AS6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AT6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AU6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on AV6: Carollo Engineers: Calculation based on TDS feed concentration which is not reported.
Note on BN18: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BN19: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BN25: Carollo Engineers: Remember also that this membrane was fouled during the first quarter which produced different trends.
Note on BN29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BN30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BN31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on BP25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BT17: Carollo Engineers: ERRORmb is high due to inaccurate measurement of the feed TDS. Feed TDS concentrations are representative of the bulk concentration, not the feed.
Note on BT23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on BY29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on BY30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on BY31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CA25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CE17: Carollo Engineers: ERRORmb is high due to inaccurate measurement of the feed TDS. Feed TDS concentrations are representative of the bulk concentra
Note on CJ18: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ19: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CJ29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CJ30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CJ31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CL34: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CM17: Carollo Engineers: Feed TDS here is representative of actual feed concentrations. Prior to week three, feed TDS was representative of "bulk" TDS concentrations.
Note on CP17: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CP23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU18: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU19: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CU29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on CU30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on CU31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on CW25: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CW34: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on CX17: Carollo Engineers: Feed TDS here is representative of actual feed concentrations. Prior to week three, feed TDS was representative of "bulk" TDS concentrations.
Note on DA22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DA23: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF18: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF19: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DF29: Carollo Engineers: SDS Incubation was performed in a water bath incubator at constant temperature.
Note on DF30: Carollo Engineers: SDS pH was fixed by using a buffer solution. Discreet additions of either acid or base allowed for percision adjusting the pH to our goal. All pHs were verified at the time of testing.
Note on DF31: Carollo Engineers: SDS Incubation time is accurate as reported within 30 minutes.
Note on DH34: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DI17: Carollo Engineers: Feed TDS here is representative of actual feed concentrations. Prior to week three, feed TDS was representative of "bulk" TDS concentrations.
Note on DL22: Carollo Engineers: Data verified by Carollo 8/6/99.
Note on DL23: Carollo Engineers: Data verified by Carollo 8/6/99.