## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Saint Paul Water Utility | Carbon manufacturer | PICA USA | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | MN1620026 | Carbon trade name | PICACARB 8X30 | mesh size | (mm) | Softening/Coagulation | 150mg/L Lime, 16mg/L Alum | Full-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Coal Base Carbon (bituminous) | 4 | 4.75 | Flocculation | 3-stage | Full-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 4.3 | 6 | 3.35 | Sedimentation | 3 rectangular and 2 circular clarifiers (5.8 hours) | Full-scale | START | --- | 1998-10-21 | 8:30 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-10-21 | 8:30 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-10-21 | 8:30 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 12
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | Recarbonation | pH = 6.50 | Pilot-scale | A-1 | N | 1998-10-22 | 8:30 | 24 | 72 | 144 | 7.01 | 0.16 | 58 | 21.5 | 81 | 54 | 0.09 | BMRL | 4.3 | 0.079 | 1.8372 | 7.12 | 0.1 | 7.02 | 23 | 8.94 | 168 | 385 | 200 | 19 | 1.6 | BMRL | 220.6 | 4.9 | 40 | 18 | BMRL | BMRL | 6 | BMRL | BMRL | 2.7 | 62.9 | 68.9 | B-1 | N | 1998-10-22 | 8:30 | 24 | 144 | 7.33 | 0.13 | 22 | 0.09 | 0.9 | 0.01 | 1.1111 | 3.05 | 0.3 | 2.75 | 23 | 8.93 | 168 | 63 | 30 | 7.4 | 2.1 | BMRL | 39.5 | BMRL | 6.3 | 1.9 | BMRL | BMRL | 2.1 | BMRL | BMRL | BMRL | 8.2 | 10.3 | C-1 | N | 1998-10-22 | 8:30 | 24 | 72 | 8.85 | 0.11 | 22 | BMRL | BMRL | BMRL | #VALUE! | 2.54 | 0.8 | 1.74 | 23 | 9.07 | 168 | BMRL | 4.6 | 1.7 | BMRL | BMRL | 6.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 15
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 450 | 10 | 2 | Dual media filtration | 36 inches of anthracite over 4 inches of sand | Pilot-scale | A-2 | N | 1998-10-26 | 14:40 | 126.1667 | 378.5 | 757 | 6.76 | 0.09 | 63 | 22.5 | 87 | 67 | 0.14 | BMRL | 4 | 0.068 | 1.7 | 7.12 | 0.1 | 7.02 | 23 | 8.88 | 168 | 370 | 200 | 17 | 1.6 | BMRL | 218.6 | 5.9 | 41 | 17 | BMRL | BMRL | 4.7 | BMRL | BMRL | 3.4 | 63.9 | 68.6 | B-2 | N | 1998-10-23 | 9:15 | 48.75 | 292.5 | 6.92 | 0.1 | 23.5 | 0.1 | 1.6 | 0.025 | 1.5625 | 3.05 | 0.1 | 2.95 | 23 | 8.88 | 168 | 100 | 47 | 9.6 | 2.4 | BMRL | 59 | BMRL | 9.9 | 2.8 | BMRL | BMRL | 2.8 | BMRL | BMRL | 1.6 | 12.7 | 15.5 | C-2 | N | 1998-10-26 | 14:40 | 126.1667 | 378.5 | 6.87 | 0.07 | 23 | 0.05 | BMRL | BMRL | #VALUE! | 2.54 | 1.1 | 1.44 | 23 | 8.87 | 168 | BMRL | 4.3 | 2.5 | 2.1 | BMRL | 8.9 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.1 | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | Dup-A-3 | Y | 1998-10-28 | 7:30 | 167 | 501 | 1002 | 6.72 | 0.08 | 61 | 21 | 84 | 64 | 0.06 | BMRL | 3.9 | 0.072 | 1.8462 | 7.12 | 0.1 | 7.02 | 23 | 9.05 | 168 | 430 | 240 | 20 | 1.8 | BMRL | 261.8 | 6 | 41 | 19 | BMRL | BMRL | 5.1 | BMRL | BMRL | 3 | 66 | 71.1 | Avg-B-3 | Y | 1998-10-26 | 14:15 | 125.75 | 754.5 | 6.89 | 0.07 | 24 | 0.07 | 1.2 | 0.016 | 1.3333 | 3.05 | 0.6 | 2.45 | 23 | 8.71 | 168 | 93.5 | 40.5 | 10.5 | 3.25 | BMRL | 54.25 | BMRL | 8.05 | 2.55 | BMRL | 1 | 2.85 | BMRL | BMRL | 1.65 | 11.6 | 14.45 | Avg-C-3 | Y | 1998-10-28 | 7:30 | 167 | 501 | 6.82 | 0.06 | 21 | 0.05 | 0.6 | BMRL | #VALUE! | 2.54 | 0.75 | 1.79 | 23 | 9.01 | 168 | 37.5 | 17 | 6.45 | 2.9 | BMRL | 26.35 | BMRL | 2.6 | 1 | BMRL | BMRL | 1.6 | BMRL | BMRL | 1.25 | 3.6 | 5.2 | Engineering Fee Factor (% of construction costs) | 12.5
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 |  |  |  | A-4 | N | 1998-10-29 | 8:45 | 192.25 | 576.75 | 1153.5 | 6.8 | 0.18 | 60 | 22 | 86 | 64 | 0.06 | BMRL | 4 | 0.071 | 1.775 | 7.12 | 1.4 | 5.72 | 23 | 8.83 | 168 | 525 | 290 | 20 | 1.8 | BMRL | 311.8 | 8.1 | 50 | 26 | BMRL | BMRL | 6.5 | BMRL | 2.4 | 3.9 | 84.1 | 90.6 | B-4 | N | 1998-10-27 | 11:30 | 147 | 882 | 6.99 | 0.07 | 22 | 0.17 | 1.5 | 0.02 | 1.3333 | 3.05 | 0.4 | 2.65 | 23 | 8.71 | 168 | 125 | 67 | 11 | 2.3 | BMRL | 80.3 | 2.7 | 11 | 3.8 | BMRL | BMRL | 3.1 | BMRL | BMRL | 1 | 17.5 | 20.6 | C-4 | N | 1998-10-29 | 8:45 | 192.25 | 576.75 | 6.94 | 0.08 | 21 | BMRL | 0.8 | BMRL | #VALUE! | 2.54 | 0.8 | 1.74 | 23 | 8.83 | 168 | 52 | 25 | 7 | 2.9 | BMRL | 34.9 | BMRL | 4.6 | 1.4 | BMRL | BMRL | 2.1 | BMRL | BMRL | 1.2 | 6 | 8.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | NA
FAX Number |  | Flow rate, Q (L/hr) | 48.6 | 20 | 0.85 |  |  |  | A-5 | N | 1998-10-31 | 8:00 | 239.5 | 718.5 | 1437 | 6.6 | 0.05 | 64 | 22 | 88 | 69 | 0.05 | BMRL | 3.7 | 0.01 | 0.27027 | 10.17 | 1.2 | 8.97 | 23 | 9.01 | 168 | 490 | 250 | 20 | 2 | BMRL | 272 | 8 | 43 | 25 | BMRL | BMRL | 5.8 | BMRL | BMRL | 4.3 | 76 | 81.8 | B-5 | N | 1998-10-28 | 9:00 | 168.5 | 1011 | 6.9 | 0.08 | 20.5 | 0.06 | 1.9 | 0.027 | 1.4211 | 3.05 | 0.1 | 2.95 | 23 | 8.76 | 168 | 160 | 79 | 11 | 2.1 | BMRL | 92.1 | BMRL | 13 | 4.1 | BMRL | BMRL | 3 | BMRL | BMRL | 1.5 | 17.1 | 20.1 | C-5 | N | 1998-10-31 | 8:00 | 239.5 | 718.5 | 6.61 | 0.07 | 22 | 0.07 | 0.9 | 0.068 | 7.5556 | 3.39 | 1 | 2.39 | 23 | 8.95 | 216 | 63 | 33 | 8.6 | 3.4 | BMRL | 45 | BMRL | 5.1 | 2.1 | BMRL | BMRL | 2.3 | BMRL | BMRL | 1.5 | 7.2 | 9.5 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A-6 | N | 1998-11-02 | 8:00 | 287.5 | 862.5 | 1725 | 6.7 | 0.15 | 59 | 22.5 | 82 | 59 | 0.05 | BMRL | 4 | 0.074 | 1.85 | 10.17 | 0.2 | 9.97 | 23 | 9.05 | 432 | 530 | 300 | 19 | 1.8 | BMRL | 320.8 | 7.6 | 72 | 28 | BMRL | BMRL | 5.4 | BMRL | BMRL | 2.2 | 107.6 | 113 | B-6 | N | 1998-10-29 | 8:45 | 192.25 | 1153.5 | 6.86 | 0.14 | 22 | 0.08 | 2.2 | 0.032 | 1.4545 | 3.05 | 0.8 | 2.25 | 23 | 8.8 | 168 | 230 | 130 | 13 | 2 | BMRL | 145 | 3 | 21 | 8.9 | BMRL | BMRL | 4.2 | BMRL | 2.1 | 2 | 32.9 | 37.1 | C-6 | N | 1998-11-02 | 9:15 | 288.75 | 866.25 | 6.68 | 0.11 | 22.5 | BMRL | 1.3 | 0.017 | 1.3077 | 3.39 | 0.3 | 3.09 | 23 | 9.07 | 168 | 110 | 48 | 9.8 | 3.1 | BMRL | 60.9 | 2.6 | 11 | 3.7 | BMRL | BMRL | 3.3 | BMRL | BMRL | 1.5 | 17.3 | 20.6 | Labor Rate + Fringe ($/work-hour) | 30
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A-7 | N | 1998-11-04 | 7:50 | 335.3333 | 1006 | 2012 | 6.72 | 0.1 | 62 | 19.5 | 87 | 60 | 0.09 | BMRL | 3.9 | 0.073 | 1.8718 | 10.17 | 0.3 | 9.87 | 23 | 9 | 384 | 545 | 280 | 20 | 1.7 | BMRL | 301.7 | 6.7 | 69 | 27 | BMRL | BMRL | 5.2 | BMRL | BMRL | 2.1 | 102.7 | 107.9 | B-7 | N | 1998-11-01 | 7:50 | 263.3333 | 1580 | 6.71 | 0.06 | 21 | 0.06 | 2.4 | 0.037 | 1.5417 | 6.78 | 0.2 | 6.58 | 23 | 9.08 | 456 | 315 | 180 | 15 | 2.1 | BMRL | 197.1 | 4.7 | 44 | 14 | BMRL | BMRL | 4.8 | BMRL | BMRL | 1.5 | 62.7 | 67.5 | C-7 | N | 1998-11-04 | 7:50 | 335.3333 | 1006 | 6.73 | 0.07 | 22.5 | 0.07 | 1.6 | 0.021 | 1.3125 | 3.39 | 0.2 | 3.19 | 23 | 9 | 384 | 145 | 81 | 11 | 2.8 | BMRL | 94.8 | 2.3 | 20 | 5 | BMRL | BMRL | 3.9 | BMRL | BMRL | BMRL | 27.3 | 31.2 | Labor Overhead Factor (% of labor) | 15
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 3257.9975 | 50 | 0.3 |  |  |  | Avg-A-8 | Y | 1998-11-05 | 12:00 | 363.5 | 1090.5 | 2181 | 6.72 | 0.19 | 60 | 22 | 85.5 | 62 | 0.1 | BMRL | 3.9 | 0.073 | 1.8718 | 10.17 | 0.1 | 10.07 | 23 | 9 | 360 | 532.5 | 285 | 19.5 | 1.85 | BMRL | 306.35 | 7.1 | 75.5 | 30 | BMRL | BMRL | 5.8 | BMRL | BMRL | 2.6 | 112.6 | 118.4 | Avg-B-8 | Y | 1998-11-02 | 9:15 | 288.75 | 1732.5 | 6.84 | 0.06 | 22.5 | 0.075 | 2.95 | 0.041 | 1.3898 | 6.78 | 0.4 | 6.38 | 23 | 9.05 | 432 | 220 | 185 | 15.5 | 2.25 | BMRL | 202.75 | 4.75 | 46.5 | 17 | BMRL | BMRL | 5.2 | BMRL | BMRL | 1.9 | 68.25 | 73.45 | Avg-C-8 | Y | 1998-11-05 | 12:00 | 363.5 | 1090.5 | 6.66 | 0.22 | 19.5 | 0.1 | 1.7 | 0.023 | 1.3529 | 3.39 | 0.15 | 3.24 | 23 | 8.94 | 360 | 220 | 59 | 11 | 3 | BMRL | 73 | BMRL | 15 | 3.15 | BMRL | BMRL | 3.65 | BMRL | BMRL | BMRL | 18.15 | 21.8 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 6515.9949 | 60 | 0.25 |  |  |  | A-9 | N | 1998-11-07 | 15:00 | 414.5 | 1243.5 | 2487 | 6.78 | 0.1 | 62 | 11 | 84 | 53 | 0.13 | BMRL | 4.3 | 0.085 | 1.9767 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B-9 | N | 1998-11-04 | 8:50 | 336.3333 | 2018 | 6.83 | 0.1 | 19.5 | 0.07 | 2.7 | 0.044 | 1.6296 | 6.78 | 0.2 | 6.58 | 23 | 9.03 | 384 | 345 | 180 | 16 | 2 | BMRL | 198 | 3.9 | 48 | 15 | BMRL | BMRL | 5.1 | BMRL | BMRL | 1.5 | 66.9 | 72 | C-9 | N | 1998-11-07 | 15:00 | 414.5 | 1243.5 | 6.8 | 0.1 | 22 | NA | 1.93 | 0.029 | 1.5026 | 3.39 | 0.6 | 2.79 | 23 | 9.14 | 312 | 215 | 120 | 12 | 1.8 | BMRL | 133.8 | 2.7 | 26 | 6.5 | BMRL | BMRL | 3.3 | BMRL | BMRL | BMRL | 35.2 | 38.5 | Fuel Oil Rate ($/gal) | NA
|  |  |  | 70 | 0.21 |  |  |  | A-10 | N | 1998-11-09 | 9:30 | 457 | 1371 | 2742 | 6.85 | 0.14 | 128 | 17 | 91 | 58 | NA | BMRL | 4.31 | 0.094 | 2.181 | 10.17 | 0.2 | 9.97 | 23 | 9.1 | 264 | 535 | 320 | 21 | 1.7 | BMRL | 342.7 | 7.9 | 74 | 28 | BMRL | BMRL | 5.7 | BMRL | BMRL | 2.3 | 109.9 | 115.6 | B-10 | N | 1998-11-07 | 15:00 | 414.5 | 2487 | 6.8 | 0.08 | 11 | 0.08 | 3.1 | 0.055 | 1.7742 | 6.78 | 0.2 | 6.58 | 23 | 9.03 | 312 | 355 | 170 | 16 | 1.9 | BMRL | 187.9 | 4.6 | 49 | 17 | BMRL | BMRL | 5.1 | BMRL | BMRL | 1.6 | 70.6 | 75.7 | C-10 | N | 1998-11-09 | 9:30 | 457 | 1371 | 6.88 | 0.09 | 11 | 0.08 | 2 | 0.029 | 1.45 | 3.39 | 1.1 | 2.29 | 23 | 9.13 | 264 | 250 | 130 | 14 | 2.5 | BMRL | 146.5 | 2.9 | 34 | 12 | BMRL | BMRL | 4.5 | BMRL | BMRL | 1.4 | 48.9 | 53.4 | Natural Gas Rate ($/ft3) | 0.6
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A-11 | N | 1998-11-10 | 7:30 | 479 | 1437 | 2874 | 6.85 | 0.12 | 64 | 17 | NA | NA | NA | NA | 3.81 | 0.084 | 2.2047 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B-11 | N | 1998-11-09 | 9:30 | 457 | 2742 | 6.86 | 0.14 | 17 | 0.06 | 3.3 | 0.055 | 1.6667 | 6.78 | 0.2 | 6.58 | 23 | 9.12 | 264 | 405 | 180 | 17 | 2.2 | BMRL | 199.2 | 4.9 | 50 | 14 | BMRL | BMRL | 5.3 | BMRL | BMRL | 1.5 | 68.9 | 74.2 | C-11 | N | 1998-11-10 | 7:30 | 479 | 1437 | 6.91 | 0.09 | 17 | NA | 2.32 | 0.0362 | 1.5603 | 4.24 | 0.3 | 3.94 | 23 | 9.1 | 240 | 210 | 110 | 13 | 2.4 | BMRL | 125.4 | 2.6 | 26 | 6.7 | BMRL | BMRL | 4.1 | BMRL | BMRL | 1.1 | 35.3 | 39.4 | Current Process Water Rate ($/1000 gal) | 0.53
FAX Number |  | Carbon particle diameter, d (mm) | 1.48 | [5 empty] | A-12 | N | 1998-11-12 | 10:20 | 529.8333 | 1589.5 | 3179 | 6.98 | 0.13 | 64 | 19 | NA | NA | NA | NA | 4.52 | 0.081 | 1.792 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B-12 | N | 1998-11-10 | 7:30 | 479 | 2874 | 6.91 | 0.09 | 17 | NA | 3.02 | 0.058 | 1.9205 | 6.78 | 0.4 | 6.38 | 23 | 9.13 | 240 | 365 | 190 | 17 | 2 | BMRL | 209 | 4.5 | 44 | 13 | BMRL | BMRL | 4.7 | BMRL | BMRL | 1.4 | 61.5 | 66.2 | C-12 | N | 1998-11-12 | 10:20 | 529.8333 | 1589.5 | 7.01 | 0.06 | 17 | NA | 2.6 | 0.035 | 1.3462 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 14.2
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | Avg-A-13 | Y | 1998-11-13 | 7:30 | 551 | 1653 | 3306 | 6.82 | 0.09 | 62 | 19 | NA | NA | NA | NA | 4.55 | 0.083 | 1.8242 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | Avg-B-13 | Y | 1998-11-12 | 10:20 | 529.8333 | 3179 | 7.03 | 0.09 | 19 | NA | 3.46 | 0.054 | 1.5607 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | Avg-C-13 | Y | 1998-11-13 | 7:30 | 551 | 1653 | 6.9 | 0.06 | 19 | NA | 2.72 | 0.037 | 1.3603 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
|  | Hydraulic loading rate1, v (m/hr) | 10.657 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A-14 | N | 1998-11-15 | 14:30 | 606 | 1818 | 3636 | 6.98 | 0.12 | 61 | 19 | NA | NA | NA | NA | 4.92 | 0.083 | 1.687 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B-14 | N | 1998-11-13 | 7:30 | 551 | 3306 | 6.88 | 0.06 | 19 | NA | 3.58 | 0.058 | 1.6201 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C-14 | N | 1998-11-15 | 14:30 | 606 | 1818 | 6.92 | 0.08 | 19 | NA | 2.84 | 0.04 | 1.4085 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
Plant Name | McCarron's Filtration Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A-15 | N | 1998-11-17 | 7:30 | 647 | 1941 | 3882 | 7 | 0.14 | 66 | 18 | NA | NA | NA | NA | 4.92 | 0.082 | 1.6667 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B-15 | N | 1998-11-15 | 14:30 | 606 | 3636 | 6.94 | 0.08 | 19 | NA | 3.87 | 0.059 | 1.5245 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C-15 | N | 1998-11-17 | 7:30 | 647 | 1941 | 6.9 | 0.09 | 19 | NA | 3.18 | 0.049 | 1.5409 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
Treatment Plant Category | CS/SOFT |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A-16 | N | 1998-11-18 | 9:30 | 673 | 2019 | 4038 | 6.95 | 0.17 | 66 | 18 | NA | NA | NA | NA | 4.1 | 0.096 | 2.3415 | 10 | 1 | 9 | 23 | 9.21 | 168 | 570 | 260 | 19 | 1.7 | BMRL | 280.7 | 11 | 58 | 29 | BMRL | BMRL | 6.8 | BMRL | BMRL | 4.8 | 98 | 104.8 | B-16 | N | 1998-11-17 | 7:30 | 647 | 3882 | 6.95 | 0.1 | 18 | NA | 4.02 | 0.068 | 1.6915 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C-16 | N | 1998-11-18 | 9:30 | 673 | 2019 | 6.98 | 0.08 | 18 | NA | 3.3 | 0.041 | 1.2424 | 3.6 | 0.2 | 3.4 | 23 | 9.2 | 168 | 110 | 96 | 12 | 2.1 | BMRL | 110.1 | 4.3 | 24 | 6.8 | BMRL | BMRL | 4.6 | BMRL | BMRL | 1.4 | 35.1 | 39.7
Process Train Name | Main | 10-Minute EBCT Run | [6 empty] | A-17 | N | 1998-11-20 | 8:00 | 719.5 | 2158.5 | 4317 | 7.27 | 0.08 | 68 | 16 | NA | NA | NA | NA | 4.79 | 0.096 | 2.0042 | 10 | 0.7 | 9.3 | 23 | 9.2 | 240 | 465 | 250 | 19 | 2.1 | BMRL | 271.1 | 8.6 | 45 | 21 | BMRL | BMRL | 6.8 | BMRL | BMRL | 3 | 74.6 | 81.4 | B-17 | N | 1998-11-18 | 9:30 | 673 | 4038 | 6.97 | 0.09 | 18 | NA | 4.08 | 0.067 | 1.6422 | 6.8 | 0.3 | 6.5 | 23 | 9.22 | 168 | 395 | 180 | 16 | 2 | BMRL | 198 | 7 | 42 | 16 | BMRL | BMRL | 6.2 | BMRL | BMRL | 2.2 | 65 | 71.2 | C-17 | N | 1998-11-20 | 8:00 | 719.5 | 2158.5 | 7.34 | 0.07 | 18 | NA | 2.83 | 0.039 | 1.3781 | 3.6 | 0 | 3.6 | 23 | 9.16 | 240 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0
ICR Treatment Plant Identification Number | 428 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | Avg-A-18 | Y | 1998-11-23 | 8:30 | 792 | 2376 | 4752 | 6.88 | 0.15 | 66 | 18 | NA | NA | NA | NA | 4.82 | 0.09 | 1.8672 | 10 | 0.65 | 9.35 | 23 | 9.17 | 168 | 502.5 | 265 | 19.5 | 1.5 | BMRL | 286 | 11 | 53 | 27 | BMRL | BMRL | 6.15 | BMRL | BMRL | 3 | 91 | 97.15 | B-18 | N | 1998-11-20 | 8:00 | 719.5 | 4317 | 7.36 | 0.06 | 18 | NA | 3.52 | 0.056 | 1.5909 | 6.8 | 0.1 | 6.7 | 23 | 9.2 | 240 | 325 | 190 | 17 | 2.3 | BMRL | 209.3 | 7.7 | 35 | 13 | BMRL | BMRL | 5.5 | BMRL | BMRL | 2.2 | 55.7 | 61.2 | Avg-C-18 | Y | 1998-11-23 | 8:30 | 792 | 2376 | 6.88 | 0.1 | 18 | NA | 3.28 | 0.052 | 1.5854 | 3.6 | 0 | 3.6 | 23 | 9.19 | 168 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0
PWSID Number of Plant (if assigned) | NA | Estimated run time, t (days) | 45.25 | [5 empty] | A-19 | N | 1998-11-30 | 12:00 | 963.5 | 2890.5 | 5781 | 6.51 | 0.15 | 59 | 18 | 87 | 56 | BMRL | BMRL | 4.2 | 0.076 | 1.8095 | 15 | 3.6 | 11.4 | 23 | 9.09 | 168 | 640 | 310 | 20 | 1.6 | BMRL | 331.6 | BMRL | 62 | 38 | BMRL | BMRL | 7.2 | BMRL | BMRL | 5.6 | 100 | 107.2 | Avg-B-19 | Y | 1998-11-23 | 8:30 | 792 | 4752 | 6.93 | 0.1 | 18 | BMRL | 4 | 0.07 | 1.75 | 6.8 | 0.2 | 6.6 | 23 | 9.2 | 168 | 385 | 190 | 17 | 1.8 | BMRL | 208.8 | 7 | 38 | 16.5 | BMRL | BMRL | 5.35 | BMRL | BMRL | 2.25 | 61.5 | 66.85 | C-19 | N | 1998-11-30 | 12:00 | 963.5 | 2890.5 | 6.86 | 0.06 | 18 | BMRL | 2.5 | 0.037 | 1.48 | 8.47 | 2.2 | 6.27 | 23 | 9.09 | 168 | 305 | 140 | 15 | 2.7 | BMRL | 157.7 | 5.5 | 26 | 13 | BMRL | BMRL | 5.1 | BMRL | BMRL | 2.3 | 44.5 | 49.6
Historical Minimum Water Temperature (oC) | 2 | Pilot column bed length, l (m) | 1.7762 | [9 empty] | -866144.5 | -2598433.5 | -5196867 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | B-20 | N | 1998-11-30 | 12:00 | 963.5 | 5781 | 6.83 | 0.1 | 18 | BMRL | 3.4 | 0.056 | 1.6471 | 11.86 | 2.9 | 8.96 | 23 | 9.09 | 168 | 410 | 220 | 18 | 2.1 | BMRL | 240.1 | BMRL | 41 | 23 | BMRL | BMRL | 6.3 | BMRL | BMRL | 4.3 | 64 | 70.3 |  |  |  |  | -866144.5 | -2598433.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Average Water Temperature (oC) | 16 | Mass GAC required, m (kg) | 3.645 | [9 empty] | -866144.5 | -2598433.5 | -5196867 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -5196867 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -2598433.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
State Approved Plant Capacity (MGD) | 144 | [11 empty] | -866144.5 | -2598433.5 | -5196867 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -5196867 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -2598433.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | 20-Minute EBCT Run | [10 empty] | -866144.5 | -2598433.5 | -5196867 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -5196867 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -2598433.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Empty bed contact time, EBCT (min) | 20 | [9 empty] | -866144.5 | -2598433.5 | -5196867 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -5196867 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -2598433.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Estimated run time, t (days) | 90.4999 | [9 empty] | -866144.5 | -2598433.5 | -5196867 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -5196867 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -866144.5 | -2598433.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Pilot column bed length, l (m) | 3.5523 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 7.29 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A-3 | Primary | 1998-10-28 | 7:30 | 167 | 501 | 1002 | 6.72 | 0.08 | 61 | 21 | 84 | 64 | 0.06 | BMRL | 3.9 | 0.072 | 1.8462 | 7.12 | 0 | 7.12 | 23 | 9.06 | 168 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0 | B-3 | Primary | 1998-10-26 | 14:15 | 125.75 | 754.5 | 6.89 | 0.07 | 24 | 0.07 | 1.2 | 0.016 | 1.3333 | 3.05 | 0.6 | 2.45 | 23 | 8.71 | 168 | 92 | 39 | 11 | 3.3 | BMRL | 53.3 | BMRL | 7.8 | 2.4 | BMRL | 1 | 2.8 | BMRL | BMRL | 1.6 | 11.2 | 14 | C-3 | Primary | 1998-10-28 | 7:30 | 167 | 501 | 6.82 | 0.06 | 21 | 0.05 | 0.6 | BMRL | #VALUE! | 2.54 | 0.8 | 1.74 | 23 | 9.01 | 168 | 38 | 17 | 6.4 | 2.8 | BMRL | 26.2 | BMRL | 2.6 | 1 | BMRL | BMRL | 1.6 | BMRL | BMRL | 1.3 | 3.6 | 5.2
[9 empty] | D-A-3 | Duplicate | 1998-10-28 | 7:30 | 167 | 501 | 1002 | 6.72 | 0.08 | 61 | 21 | 84 | 64 | 0.06 | BMRL | 3.9 | 0.072 | 1.8462 | 7.12 | 0.1 | 7.02 | 23 | 9.05 | 168 | 430 | 240 | 20 | 1.8 | BMRL | 261.8 | 6 | 41 | 19 | BMRL | BMRL | 5.1 | BMRL | BMRL | 3 | 66 | 71.1 | D-B-3 | Duplicate | 1998-10-26 | 14:15 | 125.75 | 754.5 | 6.89 | 0.07 | 24 | 0.1 | 1.3 | 0.015 | 1.1538 | 3.05 | 0.6 | 2.45 | 23 | 8.65 | 168 | 95 | 42 | 10 | 3.2 | BMRL | 55.2 | BMRL | 8.3 | 2.7 | BMRL | BMRL | 2.9 | BMRL | BMRL | 1.7 | 11 | 13.9 | D-C-3 | Duplicate | 1998-10-28 | 7:30 | 167 | 501 | 6.82 | 0.06 | 21 | 0.08 | 0.6 | BMRL | #VALUE! | 2.54 | 0.7 | 1.84 | 23 | 8.99 | 168 | 37 | 17 | 6.5 | 3 | BMRL | 26.5 | BMRL | 2.6 | BMRL | BMRL | BMRL | 1.6 | BMRL | BMRL | 1.2 | 2.6 | 4.2
[9 empty] | Avg-A-3 | Average | --- | --- | --- | --- | --- | 6.72 | 0.08 | 61 | 21 | 84 | 64 | 0.06 | #DIV/0! | 3.9 | 0.072 | 1.8462 | 7.12 | 0.05 | 7.07 | 23 | 9.055 | 168 | 430 | 240 | 20 | 1.8 | #DIV/0! | 130.9 | 6 | 41 | 19 | #DIV/0! | #DIV/0! | 5.1 | #DIV/0! | #DIV/0! | 3 | 33 | 35.55 | Avg-B-3 | Average | --- | --- | --- | --- | 6.89 | 0.07 | 24 | 0.085 | 1.25 | 0.0155 | 1.2436 | 3.05 | 0.6 | 2.45 | 23 | 8.68 | 168 | 93.5 | 40.5 | 10.5 | 3.25 | #DIV/0! | 54.25 | #DIV/0! | 8.05 | 2.55 | #DIV/0! | 1 | 2.85 | #DIV/0! | #DIV/0! | 1.65 | 11.1 | 13.95 | Avg-C-3 | Average | --- | --- | --- | --- | 6.82 | 0.06 | 21 | 0.065 | 0.6 | #DIV/0! | #VALUE! | 2.54 | 0.75 | 1.79 | 23 | 9 | 168 | 37.5 | 17 | 6.45 | 2.9 | #DIV/0! | 26.35 | #DIV/0! | 2.6 | 1 | #DIV/0! | #DIV/0! | 1.6 | #DIV/0! | #DIV/0! | 1.25 | 3.1 | 4.7
[9 empty] | RPD-A-3 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | 200 | 1.4144 | 0 | 0.11044 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | 200 | RPD-B-3 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 35.2941 | 8 | 6.4516 | 14.433 | 0 | 0 | 0 | 0 | 0.69124 | 0 | 3.2086 | 7.4074 | 9.5238 | 3.0769 | #VALUE! | 3.5023 | #VALUE! | 6.2112 | 11.7647 | #VALUE! | #VALUE! | 3.5088 | #VALUE! | #VALUE! | 6.0606 | 1.8018 | 0.71685 | RPD-C-3 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 46.1538 | 0 | #VALUE! | #VALUE! | 0 | 13.3333 | 5.5866 | 0 | 0.22222 | 0 | 2.6667 | 0 | 1.5504 | 6.8966 | #VALUE! | 1.1385 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 8 | 32.2581 | 21.2766
[9 empty] | A-8 | Primary | 1998-11-05 | 12:00 | 363.5 | 1090.5 | 2181 | 6.72 | 0.19 | 60 | 22 | 86 | 62 | 0.14 | BMRL | 3.9 | 0.073 | 1.8718 | 10.17 | 0.1 | 10.07 | 23 | 9 | 360 | 550 | 300 | 20 | 1.8 | BMRL | 321.8 | 6.8 | 75 | 30 | BMRL | BMRL | 5.6 | BMRL | BMRL | 2.6 | 111.8 | 117.4 | B-8 | Primary | 1998-11-02 | 9:15 | 288.75 | 1732.5 | 6.84 | 0.06 | 22.5 | 0.07 | 3.4 | 0.041 | 1.2059 | 6.78 | 0.4 | 6.38 | 23 | 9.05 | 432 | NR | 190 | 16 | 2.2 | BMRL | 208.2 | 4.9 | 45 | 13 | BMRL | BMRL | 4.8 | BMRL | BMRL | 1.5 | 62.9 | 67.7 | C-8 | Primary | 1998-11-05 | 12:00 | 363.5 | 1090.5 | 6.66 | 0.22 | 22 | 0.1 | 1.7 | 0.023 | 1.3529 | 3.39 | 0.2 | 3.19 | 23 | 8.94 | 360 | NR | 59 | 11 | 3 | BMRL | 73 | BMRL | 15 | 3 | BMRL | BMRL | 3.7 | BMRL | BMRL | BMRL | 18 | 21.7
[9 empty] | D-A-8 | Duplicate | 1998-11-05 | 12:00 | 363.5 | 1090.5 | 2181 | 6.72 | 0.19 | 60 | 22 | 85 | 62 | 0.11 | BMRL | 3.9 | 0.072 | 1.8462 | 10.17 | 0.1 | 10.07 | 23 | 9 | 360 | 515 | 270 | 19 | 1.9 | BMRL | 290.9 | 7.4 | 76 | 30 | BMRL | BMRL | 6 | BMRL | BMRL | 2.6 | 113.4 | 119.4 | D-B-8 | Duplicate | 1998-11-02 | 9:15 | 288.75 | 1732.5 | 6.84 | 0.06 | 22.5 | 0.08 | 2.5 | 0.041 | 1.64 | 6.78 | 0.4 | 6.38 | 23 | 9.03 | 432 | 315 | 180 | 15 | 2.3 | BMRL | 197.3 | 4.6 | 48 | 21 | BMRL | BMRL | 5.6 | BMRL | BMRL | 2.3 | 73.6 | 79.2 | D-C-8 | Duplicate | 1998-11-05 | 12:00 | 363.5 | 1090.5 | 6.66 | 0.23 | 22 | 0.11 | 1.7 | 0.023 | 1.3529 | 3.39 | 0.1 | 3.29 | 23 | 8.97 | 360 | 325 | 59 | 11 | 3 | BMRL | 73 | BMRL | 15 | 3.3 | BMRL | BMRL | 3.6 | BMRL | BMRL | BMRL | 18.3 | 21.9
[9 empty] | Avg-A-8 | Average | --- | --- | --- | --- | --- | 6.72 | 0.19 | 60 | 22 | 85.5 | 62 | 0.125 | #DIV/0! | 3.9 | 0.0725 | 1.859 | 10.17 | 0.1 | 10.07 | 23 | 9 | 360 | 532.5 | 285 | 19.5 | 1.85 | #DIV/0! | 306.35 | 7.1 | 75.5 | 30 | #DIV/0! | #DIV/0! | 5.8 | #DIV/0! | #DIV/0! | 2.6 | 112.6 | 118.4 | Avg-B-8 | Average | --- | --- | --- | --- | 6.84 | 0.06 | 22.5 | 0.075 | 2.95 | 0.041 | 1.4229 | 6.78 | 0.4 | 6.38 | 23 | 9.04 | 432 | 315 | 185 | 15.5 | 2.25 | #DIV/0! | 202.75 | 4.75 | 46.5 | 17 | #DIV/0! | #DIV/0! | 5.2 | #DIV/0! | #DIV/0! | 1.9 | 68.25 | 73.45 | Avg-C-8 | Average | --- | --- | --- | --- | 6.66 | 0.225 | 22 | 0.105 | 1.7 | 0.023 | 1.3529 | 3.39 | 0.15 | 3.24 | 23 | 8.955 | 360 | 325 | 59 | 11 | 3 | #DIV/0! | 73 | #DIV/0! | 15 | 3.15 | #DIV/0! | #DIV/0! | 3.65 | #DIV/0! | #DIV/0! | #DIV/0! | 18.15 | 21.8
[9 empty] | RPD-A-8 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 1.1696 | 0 | 24 | #VALUE! | 0 | 1.3793 | 1.3793 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5728 | 10.5263 | 5.1282 | 5.4054 | #VALUE! | 10.0865 | 8.4507 | 1.3245 | 0 | #VALUE! | #VALUE! | 6.8966 | #VALUE! | #VALUE! | 0 | 1.421 | 1.6892 | RPD-B-8 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 13.3333 | 30.5085 | 0 | 30.5085 | 0 | 0 | 0 | 0 | 0.22124 | 0 | #VALUE! | 5.4054 | 6.4516 | 4.4444 | #VALUE! | 5.3761 | 6.3158 | 6.4516 | 47.0588 | #VALUE! | #VALUE! | 15.3846 | #VALUE! | #VALUE! | 42.1053 | 15.6777 | 15.6569 | RPD-C-8 | RPD | --- | --- | --- | --- | 0 | 4.4444 | 0 | 9.5238 | 0 | 0 | 0 | 0 | 66.6667 | 3.0864 | 0 | 0.33501 | 0 | #VALUE! | 0 | 0 | 0 | #VALUE! | 0 | #VALUE! | 0 | 9.5238 | #VALUE! | #VALUE! | 2.7397 | #VALUE! | #VALUE! | #VALUE! | 1.6529 | 0.91743
[9 empty] | A-13 | Primary | 1998-11-13 | 7:30 | 551 | 1653 | 3306 | 6.82 | 0.09 | 62 | 19 | NA | NA | NA | NA | 4.48 | 0.084 | 1.875 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B-13 | Primary | 1998-11-12 | 10:20 | 529.8333 | 3179 | 7.03 | 0.09 | 19 | NA | 3.43 | 0.053 | 1.5452 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C-13 | Primary | 1998-11-13 | 7:30 | 551 | 1653 | 6.9 | 0.06 | 19 | NA | 2.69 | 0.036 | 1.3383 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[9 empty] | D-A-13 | Duplicate | 1998-11-13 | 7:30 | 551 | 1653 | 3306 | 6.82 | 0.09 | 60 | 19 | NA | NA | NA | NA | 4.62 | 0.082 | 1.7749 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | D-B-13 | Duplicate | 1998-11-12 | 10:20 | 529.8333 | 3179 | 7.03 | 0.09 | 19 | NA | 3.49 | 0.054 | 1.5473 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | D-C-13 | Duplicate | 1998-11-13 | 7:30 | 551 | 1653 | 6.9 | 0.06 | 19 | NA | 2.75 | 0.037 | 1.3455 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[9 empty] | Avg-A-13 | Average | --- | --- | --- | --- | --- | 6.82 | 0.09 | 61 | 19 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.55 | 0.083 | 1.8249 | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | Avg-B-13 | Average | --- | --- | --- | --- | 7.03 | 0.09 | 19 | #DIV/0! | 3.46 | 0.0535 | 1.5462 | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | Avg-C-13 | Average | --- | --- | --- | --- | 6.9 | 0.06 | 19 | #DIV/0! | 2.72 | 0.0365 | 1.3419 | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[9 empty] | RPD-A-13 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 3.2787 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.0769 | 2.4096 | 5.4855 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | RPD-B-13 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 1.7341 | 1.8692 | 0.13507 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | RPD-C-13 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 2.2059 | 2.7397 | 0.53392 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A-18 | Primary | 1998-11-23 | 8:30 | 599.75 | 1799.25 | 3598.5 | 6.88 | 0.15 | 64 | 18 | 89 | 51 | BMRL | BMRL | 4.79 | 0.093 | 1.9415 | 10 | 0.4 | 9.6 | 23 | 9.17 | 168 | 505 | 250 | 19 | 1.5 | BMRL | 270.5 | 11 | 52 | 27 | BMRL | BMRL | 6.2 | BMRL | BMRL | 3 | 90 | 96.2 | B-19 | Primary | 1998-11-23 | 8:30 | 645 | 3870 | 6.93 | 0.1 | 18 | BMRL | 3.97 | 0.07 | 1.7632 | 6.8 | 0.2 | 6.6 | 23 | 9.2 | 168 | 375 | 190 | 17 | 1.7 | BMRL | 208.7 | 6.9 | 37 | 16 | BMRL | BMRL | 5.4 | BMRL | BMRL | 2.2 | 59.9 | 65.3 | C-18 | Primary | 1998-11-23 | 8:30 | 599.75 | 1799.25 | 6.88 | 0.1 | 18 | BMRL | 3.1 | 0.051 | 1.6452 | 3.6 | 0 | 3.6 | 23 | 9.19 | 168 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0
[9 empty] | D-A-18 | Duplicate | 1998-11-23 | 8:30 | 599.75 | 1799.25 | 3598.5 | 6.88 | 0.15 | 66 | 18 | 89 | 51 | BMRL | BMRL | 4.85 | 0.087 | 1.7938 | 10 | 0.9 | 9.1 | 23 | 9.15 | 168 | 500 | 280 | 20 | 1.5 | BMRL | 301.5 | 11 | 54 | 27 | BMRL | BMRL | 6.1 | BMRL | BMRL | 3 | 92 | 98.1 | D-B-19 | Duplicate | 1998-11-23 | 8:30 | 645 | 3870 | 6.93 | 0.1 | 18 | BMRL | 4.03 | 0.07 | 1.737 | 6.8 | 0.2 | 6.6 | 23 | 9.19 | 168 | 395 | 190 | 17 | 1.9 | BMRL | 208.9 | 7.1 | 39 | 17 | BMRL | BMRL | 5.3 | BMRL | BMRL | 2.3 | 63.1 | 68.4 | D-C-18 | Duplicate | 1998-11-23 | 8:30 | 599.75 | 1799.25 | 6.88 | 0.1 | 18 | BMRL | 3.1 | 0.05 | 1.6129 | 3.6 | 0 | 3.6 | 23 | 9.19 | 168 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0
[9 empty] | Avg-A-18 | Average | --- | --- | --- | --- | --- | 6.88 | 0.15 | 65 | 18 | 89 | 51 | #DIV/0! | #DIV/0! | 4.82 | 0.09 | 1.8677 | 10 | 0.65 | 9.35 | 23 | 9.16 | 168 | 502.5 | 265 | 19.5 | 1.5 | #DIV/0! | 286 | 11 | 53 | 27 | #DIV/0! | #DIV/0! | 6.15 | #DIV/0! | #DIV/0! | 3 | 91 | 97.15 | Avg-B-19 | Average | --- | --- | --- | --- | 6.93 | 0.1 | 18 | #DIV/0! | 4 | 0.07 | 1.7501 | 6.8 | 0.2 | 6.6 | 23 | 9.195 | 168 | 385 | 190 | 17 | 1.8 | #DIV/0! | 208.8 | 7 | 38 | 16.5 | #DIV/0! | #DIV/0! | 5.35 | #DIV/0! | #DIV/0! | 2.25 | 61.5 | 66.85 | Avg-C-18 | Average | --- | --- | --- | --- | 6.88 | 0.1 | 18 | #DIV/0! | 3.1 | 0.0505 | 1.629 | 3.6 | 0 | 3.6 | 23 | 9.19 | 168 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[9 empty] | RPD-A-18 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 3.0769 | 0 | 0 | 0 | #VALUE! | #VALUE! | 1.2448 | 6.6667 | 7.9098 | 0 | 76.9231 | 5.3476 | 0 | 0.21834 | 0 | 0.99502 | 11.3208 | 5.1282 | 0 | #VALUE! | 10.8392 | 0 | 3.7736 | 0 | #VALUE! | #VALUE! | 1.626 | #VALUE! | #VALUE! | 0 | 2.1978 | 1.9557 | RPD-B-19 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 1.5 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0.10875 | 0 | 5.1948 | 0 | 0 | 11.1111 | #VALUE! | 0.095785 | 2.8571 | 5.2632 | 6.0606 | #VALUE! | #VALUE! | 1.8692 | #VALUE! | #VALUE! | 4.4444 | 5.2033 | 4.6372 | RPD-C-18 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 0 | 1.9802 | 1.9802 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
*: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on N11: Martha Burckhardt: The duplicate had a Cl2 residual of 0.1 mg/L, so I didn't use the average.
Note on N19: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on N20: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on N21: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on N22: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on N23: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on N50: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on N51: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on W54: Martha Burckhardt: Entered missing values
Note on AD13: Martha Burckhardt: Montgomery Lab reported UV254= 0.01, our lab measured 0.0667 when taking sample.
Note on AG27: Martha Burckhardt: Yes, the residual is correct
Note on AK5: Reviewer M.H. (12/17/99): Per Consultant: "The target incubation time was 7 days (168 hours) A tracer study done earlier showed us an average residence time of seven days in our distribution system. Due to the same logistic problems mentioned earlier (faster than expected breakthrough), we ran out of bottles to sample the incubated SDS samples on time. We reported the measured temperature taken at the end of the incubation period. Since the samples sat there for at least seven days, they all achieved the same temperature. The initial temperature is reported in the first set of parameters analyzed (water quality parameters) in the spreadsheet."
Note on AL27: Martha Burckhardt: DBP values entered
Note on AL42: Martha Burckhardt: Residual Cl2=0 mg/L, DBP formation wasn't achieved
Note on BD21: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on BD22: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on BD23: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on BD24: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on BD50: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on BD51: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on BM27: Martha Burckhardt: Entered missing value
Note on BM54: Martha Burckhardt: Entered missing value
Note on BM55: Martha Burckhardt: Entered missing value
Note on BN46: Martha Burckhardt: Checked
Note on BN47: Martha Burckhardt: checked
Note on BV5: Reviewer M.H. (12/17/99): Per Consultant: "The target incubation time was 7 days (168 hours) A tracer study done earlier showed us an average residence time of seven days in our distribution system. Due to the same logistic problems mentioned earlier (faster than expected breakthrough), we ran out of bottles to sample the incubated SDS samples on time. We reported the measured temperature taken at the end of the incubation period. Since the samples sat there for at least seven days, they all achieved the same temperature. The initial temperature is reported in the first set of parameters analyzed (water quality parameters) in the spreadsheet."
Note on BW28: Martha Burckhardt: Entered missing values
Note on BW46: Martha Burckhardt: Result of 125 mg/L seems to be an outlier
Note on BW47: Martha Burckhardt: checked
Note on CE46: Martha Burckhardt: checked
Note on CE47: Martha Burckhardt: checked
Note on CO20: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on CO21: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on CO22: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on CO23: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on CO50: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on CO51: Reviewer M.H. (12/17/99): Regarding the NAs, per Consultant: "We didn’t anticipate the breakthrough to happen so fast, so we didn’t prepare ourselves with enough sample bottles to ship out to California and to incubate for SDS conditions. The initial run time length estimate (considering our influent TOC) was of about 3 months, so we had some logistic difficulties to get the samples to the laboratory within the holding time."
Note on CX54: Martha Burckhardt: ADDED MISSING VALUE
Note on CX55: Martha Burckhardt: ADDED MISSING VALUE
Note on CY27: Reviewer M.H. (12/17/99): Per Consultant: "Our in-house TOC measurement indicated we had achieved the 70% breakthrough for two consecutive samples."
Note on CZ13: Martha Burckhardt: Result obtained from Montgomery Watson= 0.068, UV254 at sampling = 0.01
Note on DG5: Reviewer M.H. (12/17/99): Per Consultant: "The target incubation time was 7 days (168 hours) A tracer study done earlier showed us an average residence time of seven days in our distribution system. Due to the same logistic problems mentioned earlier (faster than expected breakthrough), we ran out of bottles to sample the incubated SDS samples on time. We reported the measured temperature taken at the end of the incubation period. Since the samples sat there for at least seven days, they all achieved the same temperature. The initial temperature is reported in the first set of parameters analyzed (water quality parameters) in the spreadsheet."
Note on DH25: Martha Burckhardt: Cl2 residual = 0 mg/L, DBP formation wasn't complete
Note on DH27: Martha Burckhardt: added missing values
Note on DH46: Martha Burckhardt: It seems to be an outlier, changed from 115 mg/L to "NR"
Note on DH47: Martha Burckhardt: checked
Note on DH54: Martha Burckhardt: Cl2 residual =0.0 mg/L, so DBP formation wasn't complete
Note on DH55: Martha Burckhardt: Cl2 residual =0.0 mg/L, so DBP formation wasn't complete
Note on DI46: Martha Burckhardt: THM results are correct as reported by Montgomery Lab
Note on EA19: Martha Burckhardt: $1.87/1000 gal retail $0.53/1000 gal production

## Sheet2. 2nd Pilot Study
FIELD-SET 2: RESULTS FROM 2nd PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 2-3: Pretreatment Used Prior To GAC1 |  |  | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 2-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 2-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 2-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 2-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 2-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Saint Paul Water Utility | Carbon manufacturer | CALGON CARBON | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | MN1620026 | Carbon trade name | Filtrasorb 400 | mesh size | (mm) | Softening/Coagulation | 150mg/L Lime, 16mg/L Alum | Full-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Coal Base Carbon | 4 | 4.75 | Flocculation | 3-stage | Full-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 4.3 | 6 | 3.35 | Sedimentation | 3 rectangular and 2 circular clarifiers (5.8 hours) | Full-scale | START | --- | 1999-02-18 | 13:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1999-02-18 | 13:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1999-02-18 | 13:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 12
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | Recarbonation | pH = 6.50 | Pilot-scale | A-1 | N | 1999-02-19 | 13:00 | 24 | 72 | 144 | 7.17 | 0.03 | 65 | 9 | 95 | 54 | 0.1 | BMRL | 3.2 | 0.059 | 1.8438 | 5 | 1.7 | 3.3 | 10 | 9.13 | 168 | NR | 110 | 17 | 2.4 | BMRL | 129.4 | BMRL | 26 | 16 | BMRL | BMRL | 5.6 | BMRL | BMRL | 3.4 | 42 | 47.6 | B-1 | N | 1999-02-19 | 13:00 | 24 | 144 | 8.31 | 0.01 | 10 | 0.09 | BMRL | BMRL | #VALUE! | 3 | 2.1 | 0.9 | 10 | 9.17 | 168 | 63 | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C-1 | N | 1999-02-19 | 13:00 | 24 | 72 | 9.67 | 0 | 11 | 0.13 | BMRL | BMRL | #VALUE! | 3 | 2.2 | 0.8 | 10 | 9.37 | 168 | BMRL | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Special Sitework Factor (% of construction costs) | 15
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 440 | 10 | 2 | Dual media filtration | 36 inches of anthracite over 4 inches of sand | Pilot-scale | A-2 | N | 1999-02-24 | 9:30 | 140.5 | 421.5 | 843 | 7.11 | 0.04 | 60 | 9 | 92 | 52 | 0.15 | BMRL | 3 | 0.057 | 1.9 | 5 | 1.7 | 3.3 | 10 | 9.13 | 168 | 470 | 100 | 16 | 2.3 | BMRL | 118.3 | BMRL | 24 | 15 | BMRL | BMRL | 5.5 | BMRL | BMRL | 4.2 | 39 | 44.5 | B-2 | N | 1999-02-24 | 9:30 | 140.5 | 843 | 7.27 | 0.05 | 10 | 0.13 | BMRL | BMRL | #VALUE! | 3 | 2.2 | 0.8 | 10 | 9.22 | 168 | BMRL | 0.8 | 0.6 | 0.5 | BMRL | 1.9 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C-2 | N | 1999-02-24 | 9:30 | 140.5 | 421.5 | 7.36 | 0.01 | 11 | 0.21 | 1 | BMRL | #VALUE! | 3 | 2.2 | 0.8 | 10 | 9.2 | 168 | BMRL | 0.6 | 0.5 | BMRL | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Pilot GAC mesh size, upper (US standard mesh) | 12 | 12 | 1.68 |  |  |  | Avg-A-3 | Y | 1999-03-04 | 13:00 | 336 | 1008 | 2016 | 7.195 | 0.025 | 60 | 10 | 88 | 44 | 0.2 | BMRL | 3.35 | 0.064 | 1.9104 | 5 | 1.35 | 3.65 | 10 | 9.27 | 168 | 375 | 130 | 17.5 | 2.35 | BMRL | 149.85 | 3.55 | 27 | 16.5 | BMRL | BMRL | 5.9 | BMRL | BMRL | 3.3 | 47.05 | 52.95 | Avg-B-3 | Y | 1999-03-01 | 10:45 | 261.75 | 1570.5 | 7.19 | 0.02 | 12 | 0.1 | BMRL | BMRL | #VALUE! | 3 | 2.15 | 0.85 | 10 | 9.26 | 240 | BMRL | 0.95 | 1.4 | 1 | BMRL | 3.35 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Avg-C-3 | Y | 1999-03-04 | 13:00 | 336 | 1008 | 7.29 | 0 | 12 | 0.1 | BMRL | BMRL | #VALUE! | 3 | 2.3 | 0.7 | 10 | 9.23 | 168 | BMRL | 0.85 | 0.8 | 0.7 | BMRL | 2.35 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Engineering Fee Factor (% of construction costs) | 12.5
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 40 | 16 | 1.18 |  |  |  | A-4 | N | 1999-03-05 | 14:00 | 361 | 1083 | 2166 | 7.13 | 0.03 | 56 | 10 | 86 | 47 | 0.12 | BMRL | 2.9 | 0.058 | 2 | 5 | 1.35 | 3.65 | 10 | 9.26 | 240 | 340 | 140 | 16 | 2.1 | BMRL | 158.1 | BMRL | 27 | 16 | BMRL | BMRL | 5.7 | BMRL | BMRL | 3.3 | 43 | 48.7 | B-4 | N | 1999-03-05 | 14:00 | 361 | 2166 | 7.29 | 0.01 | 12 | 0.11 | 0.6 | BMRL | #VALUE! | 3 | 2.1 | 0.9 | 10 | 9.24 | 240 | BMRL | 2.5 | 2.9 | 2.4 | 0.6 | 8.4 | BMRL | BMRL | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | 1 | 0 | 1 | C-4 | N | 1999-03-05 | 14:00 | 361 | 1083 | 7.28 | 0.03 | 12 | 0.07 | BMRL | BMRL | #VALUE! | 3 | 2.3 | 0.7 | 10 | 9.2 | 240 | BMRL | 0.7 | 0.8 | 0.6 | BMRL | 2.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | NA
FAX Number |  | Flow rate, Q (L/hr) | 48.6 | 20 | 0.85 |  |  |  | A-5 | N | 1999-03-09 | 11:30 | 454.5 | 1363.5 | 2727 | 7.07 | 0.02 | 56 | 10 | 90 | 47 | 0.09 | BMRL | 3.8 | 0.075 | 1.9737 | 5 | 1.1 | 3.9 | 10 | 9.2 | 192 | 590 | 150 | 16 | 1.5 | BMRL | 167.5 | BMRL | 35 | 20 | BMRL | BMRL | 5.9 | BMRL | BMRL | 3.2 | 55 | 60.9 | B-5 | N | 1999-03-09 | 11:30 | 454.5 | 2727 | 7.14 | 0.03 | 11 | 0.08 | 0.8 | BMRL | #VALUE! | 3 | 2.3 | 0.7 | 10 | 9.22 | 192 | 35 | 10 | 6.4 | 4.1 | BMRL | 20.5 | BMRL | 2.4 | BMRL | BMRL | 1.7 | 1.7 | BMRL | BMRL | 1.6 | 4.1 | 5.8 | C-5 | N | 1999-03-09 | 11:30 | 454.5 | 1363.5 | 7.07 | 0.02 | 12 | BMRL | BMRL | BMRL | #VALUE! | 3 | 2.9 | 0.1 | 10 | 9.22 | 192 | BMRL | 0.9 | 0.8 | 0.6 | BMRL | 2.3 | BMRL | BMRL | 2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 2 | 2 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A-6 | N | 1999-03-17 | 15:00 | 650 | 1950 | 3900 | 7.11 | 0.08 | 55 | 10 | 91 | 55 | 0.12 | BMRL | 3.9 | 0.068 | 1.7436 | 5 | 1.6 | 3.4 | 10 | 9.21 | 168 | 630 | 140 | 16 | 1.7 | BMRL | 157.7 | 3.7 | 31 | 18 | BMRL | BMRL | 5.6 | BMRL | 2 | 3.2 | 52.7 | 58.3 | B-6 | N | 1999-03-11 | 14:00 | 505 | 3030 | 7.04 | 0.04 | 11 | 0.05 | 1.2 | 0.009 | 0.75 | 3 | 2.3 | 0.7 | 10 | 9.14 | 264 | 75 | 13 | 7.7 | 5.2 | 0.5 | 26.4 | BMRL | 13 | 7.9 | BMRL | 1.3 | 4.8 | BMRL | 2.7 | 3.7 | 22.2 | 27 | C-6 | N | 1999-03-17 | 15:00 | 650 | 1950 | 7.33 | 0.04 | 12 | BMRL | BMRL | BMRL | #VALUE! | 3 | 2.6 | 0.4 | 10 | 9.14 | 168 | BMRL | 3.1 | 3.9 | 2.5 | BMRL | 9.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.2 | 0 | 0 | Labor Rate + Fringe ($/work-hour) | 30
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A-7 | N | 1999-03-22 | 9:00 | 764 | 2292 | 4584 | 6.48 | 0.07 | 54 | 10 | 85 | 53 | BMRL | 20 | 3.4 | 0.057 | 1.6765 | 5 | 1.6 | 3.4 | 10 | 8.92 | 168 | 290 | 130 | 19 | 2.8 | BMRL | 151.8 | 2.4 | 29 | 23 | BMRL | BMRL | 5.7 | NR | 2.4 | 4.4 | 54.4 | 60.1 | B-7 | N | 1999-03-15 | 13:00 | 600 | 3600 | 7.14 | 0.04 | 12 | BMRL | 0.9 | 0.01 | 1.1111 | 3 | 2.3 | 0.7 | 10 | 9.06 | 216 | 66 | 21 | 8.5 | 4.4 | BMRL | 33.9 | BMRL | 4.7 | 2.4 | BMRL | 1.4 | 2.7 | BMRL | BMRL | 1.7 | 8.5 | 11.2 | C-7 | N | 1999-03-22 | 9:00 | 764 | 2292 | 5.95 | 0.06 | 14 | 0.08 | 0.7 | BMRL | #VALUE! | 3 | 2.4 | 0.6 | 10 | 7.31 | 168 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0 | Labor Overhead Factor (% of labor) | 15
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 3257.9975 | 50 | 0.3 |  |  |  | Avg-A-8 | Y | 1999-03-24 | 14:00 | 817 | 2451 | 4902 | 7.05 | 0.04 | 59 | 10 | 89 | 54 | 0.1 | BMRL | 3.8 | 0.057 | 1.5 | 5 | 1.9 | 3.1 | 10 | 9.27 | 168 | 317.5 | 165 | 18 | 2.15 | BMRL | 185.15 | BMRL | 29.5 | 17.5 | BMRL | BMRL | 5.6 | BMRL | BMRL | 3.15 | 47 | 52.6 | Avg-B-8 | Y | 1999-03-17 | 15:00 | 650 | 3900 | 7.37 | 0.06 | 12 | BMRL | 1 | 0.01 | 1 | 3 | 2.3 | 0.7 | 10 | 9.2 | 168 | 68.5 | 22.5 | 7.1 | 3.05 | BMRL | 32.65 | BMRL | 4.7 | 2.4 | BMRL | 1.2 | 2.5 | BMRL | BMRL | 1.6 | 8.3 | 10.8 | Avg-C-8 | Y | 1999-03-24 | 14:00 | 817 | 2451 | 7.05 | 0.04 | 12 | BMRL | 0.7 | BMRL | #VALUE! | 3 | 2.85 | 0.15 | 10 | 9.28 | 168 | BMRL | 1.7 | 2.45 | 1.9 | BMRL | 6.05 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 6515.9949 | 60 | 0.25 |  |  |  | A-9 | N | 1999-03-30 | 8:30 | 955.5 | 2866.5 | 5733 | 7.04 | 0.08 | 52 | 13 | 83 | 52 | 0.47 | BMRL | 4 | 0.064 | 1.6 | 5 | 2.4 | 2.6 | 10 | 9.3 | 168 | 305 | 130 | 16 | 1.6 | BMRL | 147.6 | BMRL | 28 | 18 | BMRL | BMRL | 5.1 | BMRL | BMRL | 3 | 46 | 51.1 | B-9 | N | 1999-03-22 | 9:00 | 764 | 4584 | 5.98 | 0.04 | 12 | BMRL | 1.1 | BMRL | #VALUE! | 3 | 2.1 | 0.9 | 10 | 7.67 | 168 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | 0 | C-9 | N | 1999-03-30 | 8:30 | 955.5 | 2866.5 | 6.91 | 0.08 | 18 | 0.26 | BMRL | BMRL | #VALUE! | 3 | 2.8 | 0.2 | 10 | 9.23 | 168 | BMRL | 2.1 | 3 | 2.6 | 0.5 | 8.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Fuel Oil Rate ($/gal) | NA
|  |  |  | 70 | 0.21 |  |  |  | A-10 | N | 1999-04-02 | 9:00 | 1028 | 3084 | 6168 | 7.1 | 0.12 | 54 | 10 | 85 | 48 | 0.49 | BMRL | 4 | 0.069 | 1.725 | 5 | 2.1 | 2.9 | 10 | 9.18 | 240 | 340 | 160 | 17 | 1.5 | BMRL | 178.5 | 4.5 | 30 | 21 | BMRL | BMRL | 5.3 | NR | BMRL | 3.5 | 55.5 | 60.8 | B-10 | N | 1999-03-24 | 14:00 | 817 | 4902 | 7.14 | 0.04 | 12 | 0.06 | 1.8 | 0.018 | 1 | 3 | 1.7 | 1.3 | 10 | 9.28 | 168 | 115 | 43 | 11 | 4.5 | BMRL | 58.5 | BMRL | 8.7 | 4.2 | BMRL | BMRL | 3.7 | BMRL | BMRL | 1.9 | 12.9 | 16.6 | C-10 | N | 1999-04-02 | 9:00 | 1028 | 3084 | 7.22 | 0.06 | 13 | 0.08 | BMRL | BMRL | #VALUE! | 3 | 2.8 | 0.2 | 10 | 9.12 | 240 | 54 | 2.7 | 2.6 | 2 | BMRL | 7.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NR | BMRL | BMRL | 0 | 0 | Natural Gas Rate ($/ft3) | 0.6
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A-11 | N | 1999-04-08 | 10:00 | 1173 | 3519 | 7038 | 6.99 | 0.03 | 53 | 10 | 85 | 56 | BMRL | BMRL | 3.6 | 0.06 | 1.6667 | 5 | 2.4 | 2.6 | 10 | 9.03 | 144 | 295 | 120 | 14 | 1.6 | BMRL | 135.6 | 3 | 26 | 18 | BMRL | BMRL | 4.8 | BMRL | BMRL | 3.2 | 47 | 51.8 | B-11 | N | 1999-03-30 | 8:30 | 955.5 | 5733 | 6.92 | 0.08 | 16 | 0.33 | 1.8 | 0.015 | 0.83333 | 3 | 2.3 | 0.7 | 10 | 9.24 | 192 | 87 | 28 | 10 | 5 | BMRL | 43 | BMRL | 7.4 | 3.9 | BMRL | 1.5 | 3.6 | BMRL | BMRL | 1.9 | 12.8 | 16.4 | C-11 | N | 1999-04-08 | 10:00 | 1173 | 3519 | 7.11 | 0.02 | 12 | BMRL | BMRL | BMRL | #VALUE! | 3 | 2.8 | 0.2 | 10 | 9.03 | 144 | 65 | 6.2 | 1.6 | 1.2 | BMRL | 9 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Current Process Water Rate ($/1000 gal) | 0.53
FAX Number |  | Carbon particle diameter, d (mm) | 1.0525 | [5 empty] | A-12 | N | 1999-04-14 | 10:00 | 1317 | 3951 | 7902 | 7.16 | 0.05 | 48 | 10 | 76 | 44 | 0.1 | BMRL | 4.1 | 0.066 | 1.6098 | 5 | 2.3 | 2.7 | 10 | 9.18 | 144 | 670 | 130 | 16 | 1.6 | BMRL | 147.6 | 3.4 | 30 | 18 | BMRL | BMRL | 5.2 | BMRL | BMRL | 2.5 | 51.4 | 56.6 | B-12 | N | 1999-04-02 | 9:00 | 1028 | 6168 | 7.04 | 0.12 | 12 | 0.47 | 1.7 | 0.02 | 1.1765 | 3 | 2 | 1 | 10 | 9.13 | 240 | 220 | 43 | 11 | 3.3 | BMRL | 57.3 | BMRL | 9.8 | 5.2 | BMRL | BMRL | 3.2 | NR | BMRL | 1.9 | 15 | 18.2 | C-12 | N | 1999-04-14 | 10:00 | 1317 | 3951 | 7.07 | 0.04 | 12 | 0.14 | 0.5 | BMRL | #VALUE! | 3 | 2.9 | 0.1 | 10 | 9.18 | 144 | BMRL | 4.8 | 4.5 | 3.1 | 0.5 | 12.9 | BMRL | 1.6 | BMRL | BMRL | 1 | 1.5 | BMRL | BMRL | BMRL | 2.6 | 4.1 | Modifications to Existing Plant (% of construction costs) | 14.2
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | Avg-A-13 | Y | 1999-04-20 | 8:30 | 1459.5 | 4378.5 | 8757 | 10.83 | 0.04 | 45 | 10 | 72.5 | 56 | 0.5 | BMRL | 3.85 | 0.057 | 1.4805 | 5 | 2 | 3 | 10 | 9.38 | 192 | 345 | 160 | 15.5 | 1.65 | BMRL | 177.15 | 3.5 | 28 | 14 | BMRL | BMRL | 4.85 | BMRL | BMRL | 2.15 | 45.5 | 50.35 | Avg-B-13 | Y | 1999-04-06 | 13:00 | 1128 | 6768 | 7.38 | 0.05 | 12 | 0.1 | 2.3 | 0.022 | 0.95652 | 3 | 2.05 | 0.95 | 10 | 9.03 | 192 | 122.5 | 35.5 | 9.85 | 3.15 | BMRL | 48.5 | BMRL | 10.25 | 5.5 | BMRL | BMRL | 3.5 | BMRL | BMRL | 2.1 | 15.75 | 19.25 | Avg-C-13 | Y | 1999-04-20 | 8:30 | 1459.5 | 4378.5 | 6.9 | 0.04 | 12 | 0.3 | 1.3 | 0.013 | 1 | 3 | 2.4 | 0.6 | 10 | 9.21 | 192 | 70 | 22 | 9.3 | 4.65 | BMRL | 35.95 | BMRL | 5.4 | 3 | BMRL | 1.25 | 2.75 | BMRL | BMRL | 1.3 | 9.65 | 12.4
|  | Hydraulic loading rate1, v (m/hr) | 10.657 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A-14 | N | 1999-05-06 | 10:00 | 1845 | 5535 | 11070 | 7.19 | 0.05 | 53 | 10 | 175 | 148 | 0.19 | BMRL | 3.3 | 0.05 | 1.5152 | 5 | 1.6 | 3.4 | 10 | 9.2 | 168 | 360 | 150 | 15 | 1.8 | BMRL | 166.8 | 4.4 | 28 | 16 | BMRL | BMRL | 5 | BMRL | BMRL | 3 | 48.4 | 53.4 | B-14 | N | 1999-04-12 | 9:30 | 1268.5 | 7611 | 7.06 | 0.06 | 12 | 0.07 | 2.2 | 0.029 | 1.3182 | 3 | 1.7 | 1.3 | 10 | 9.16 | 192 | 165 | 63 | 12 | 2.7 | BMRL | 77.7 | BMRL | 14 | 7.4 | BMRL | BMRL | 3.9 | BMRL | BMRL | 2.4 | 21.4 | 25.3 | C-14 | N | 1999-05-06 | 10:00 | 1845 | 5535 | 7.48 | 0.05 | 12 | 0.23 | 1.3 | 0.013 | 1 | 3 | 2.5 | 0.5 | 10 | 9.2 | 168 | 73 | 24 | 9 | 5.2 | 0.5 | 38.7 | 2.1 | 5.2 | 2.5 | BMRL | 1.2 | 3 | BMRL | BMRL | 1.5 | 11 | 14
Plant Name | McCarron's Filtration Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A-15 | N | 1999-05-19 | 13:00 | 2160 | 6480 | 12960 | 7.48 | 0.02 | 47 | 15 | 78 | 58 | 0.055 | BMRL | 3.1 | 0.058 | 1.871 | 5 | 2 | 3 | 8 | 9.27 | 192 | 240 | 87 | 13 | 1.7 | BMRL | 101.7 | BMRL | 23 | 15 | BMRL | BMRL | 4.2 | BMRL | BMRL | 3 | 38 | 42.2 | B-15 | N | 1999-04-14 | 10:00 | 1317 | 7902 | 7.12 | 0.05 | 12 | 0.24 | 2.4 | 0.033 | 1.375 | 3 | 1.7 | 1.3 | 10 | 9.16 | 144 | 175 | 59 | 12 | 2.7 | BMRL | 73.7 | BMRL | 14 | 7.3 | BMRL | BMRL | 4.2 | BMRL | BMRL | 1.7 | 21.3 | 25.5 | C-15 | N | 1999-05-19 | 13:00 | 2160 | 6480 | 6.93 | 0.05 | 15 | BMRL | 1.4 | 0.014 | 1 | 3 | 2.6 | 0.4 | 8 | 9.31 | 192 | 59 | 11 | 7.4 | 4.7 | BMRL | 23.1 | BMRL | 4.4 | 2.4 | BMRL | 1.3 | 2.6 | BMRL | 2 | 1.8 | 8.1 | 10.7
Treatment Plant Category | CS/SOFT |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A-16 | N | 1999-05-24 | 9:00 | 2276 | 6828 | 13656 | 7.14 | 0.02 | 43 | 16 | 75 | 54 | BMRL | BMRL | 3.3 | 0.06 | 1.8182 | 5 | 2.4 | 2.6 | 8 | 9.31 | 168 | 270 | 84 | 12 | 1.5 | BMRL | 97.5 | 3.1 | 25 | 16 | BMRL | BMRL | 4 | BMRL | BMRL | 2.7 | 44.1 | 48.1 | B-16 | N | 1999-04-20 | 10:00 | 1461 | 8766 | 7.11 | 0.03 | 12 | 0.07 | 5.5 | 0.081 | 1.4727 | 3 | 1.5 | 1.5 | 10 | 9.21 | 192 | 330 | 150 | 21 | 3.3 | BMRL | 174.3 | 3.6 | 33 | 16 | BMRL | BMRL | 5.9 | BMRL | BMRL | 2.5 | 52.6 | 58.5 | C-16 | N | 1999-05-24 | 9:00 | 2276 | 6828 | 7.12 | 0.03 | 16 | BMRL | 1.5 | 0.035 | 2.3333 | 3 | 2.3 | 0.7 | 8 | 9.29 | 168 | 69 | 12 | 6.6 | 3.6 | BMRL | 22.2 | BMRL | 5.4 | 2.5 | BMRL | 1 | 2.6 | BMRL | BMRL | 1.6 | 8.9 | 11.5
Process Train Name | Main | 10-Minute EBCT Run | [6 empty] | A-17 | N | 1999-06-02 | 9:00 | 2492 | 7476 | 14952 | 7.05 | 0.05 | 50 | 18 | 78 | 60 | 0.11 | 20 | 3.6 | 0.063 | 1.75 | 5 | 2.5 | 2.5 | 8 | 9.25 | 144 | 215 | 89 | 12 | 1.5 | BMRL | 102.5 | BMRL | 22 | 14 | BMRL | BMRL | 4 | BMRL | BMRL | 2.8 | 36 | 40 | B-17 | N | 1999-05-06 | 10:00 | 1845 | 11070 | 7.55 | 0.03 | 12 | 0.81 | 2.6 | 0.037 | 1.4231 | 3 | 1.5 | 1.5 | 10 | 9.2 | 168 | 215 | 90 | 14 | 3 | BMRL | 107 | 3.8 | 18 | 7.9 | BMRL | BMRL | 4.8 | BMRL | BMRL | 2 | 29.7 | 34.5 | C-17 | N | 1999-06-02 | 9:00 | 2492 | 7476 | 7.71 | 0.04 | 18 | BMRL | 4 | 0.054 | 1.35 | 3 | 1.7 | 1.3 | 8 | 9.3 | 144 | 185 | 58 | 12 | 2.6 | BMRL | 72.6 | BMRL | 16 | 7.3 | BMRL | BMRL | 4.4 | BMRL | BMRL | 2.2 | 23.3 | 27.7
ICR Treatment Plant Identification Number | 428 | Empty bed contact time, EBCT (min) | 10 | [9 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | B-18 | N | 1999-05-19 | 13:00 | 2160 | 12960 | 7.2 | 0.05 | 15 | BMRL | 3 | 0.048 | 1.6 | 4 | 2.5 | 1.5 | 8 | 9.3 | 192 | 200 | 59 | 13 | 2.7 | BMRL | 74.7 | BMRL | 17 | 11 | BMRL | BMRL | 4.8 | BMRL | BMRL | 2.9 | 28 | 32.8 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
PWSID Number of Plant (if assigned) | NA | Estimated run time, t (days) | 45.25 | [9 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | B-19 | N | 1999-05-24 | 9:00 | 2276 | 13656 | 7.14 | 0.07 | 16 | BMRL | 2.5 | 0.036 | 1.44 | 4 | 2.5 | 1.5 | 8 | 9.31 | 168 | 175 | 44 | 10 | 2.3 | BMRL | 56.3 | BMRL | 13 | 7.6 | BMRL | BMRL | 3.6 | BMRL | BMRL | 2.2 | 20.6 | 24.2 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Minimum Water Temperature (oC) | 2 | Pilot column bed length, l (m) | 1.7762 | [9 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -5214174 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Average Water Temperature (oC) | 16 | Mass GAC required, m (kg) | 3.564 | [9 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -5214174 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
State Approved Plant Capacity (MGD) | 144 | [11 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -5214174 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | 20-Minute EBCT Run | [10 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -5214174 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Empty bed contact time, EBCT (min) | 20 | [9 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -5214174 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Estimated run time, t (days) | 90.4999 | [9 empty] | -869029 | -2607087 | -5214174 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -5214174 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869029 | -2607087 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Pilot column bed length, l (m) | 3.5523 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 7.128 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A-3 | Primary | 1999-03-04 | 13:00 | 336 | 1008 | 2016 | 7.19 | 0.03 | 60 | 10 | 88 | 44 | 0.2 | BMRL | 3.4 | 0.064 | 1.8824 | 5 | 1.3 | 3.7 | 10 | 9.25 | 168 | NR | 130 | 18 | 2.4 | BMRL | 150.4 | 4.3 | 27 | 16 | BMRL | BMRL | 5.9 | BMRL | BMRL | 3.3 | 47.3 | 53.2 | B-3 | Primary | 1999-03-01 | 10:45 | 261.75 | 1570.5 | 7.19 | 0.02 | 12 | 0.09 | BMRL | BMRL | #VALUE! | 3 | 2.2 | 0.8 | 10 | 9.24 | 240 | BMRL | 1 | 1.4 | 1 | BMRL | 3.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | C-3 | Primary | 1999-03-04 | 13:00 | 336 | 1008 | 7.28 | 0 | 12 | 0.09 | BMRL | BMRL | #VALUE! | 3 | 2.3 | 0.7 | 10 | 9.22 | 168 | BMRL | 0.7 | 1 | 0.7 | BMRL | 2.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[9 empty] | D-A-3 | Duplicate | 1999-03-04 | 13:00 | 336 | 1008 | 2016 | 7.2 | 0.02 | 60 | 10 | 88 | 44 | 0.12 | BMRL | 3.3 | 0.064 | 1.9394 | 5 | 1.4 | 3.6 | 10 | 9.28 | 168 | 510 | 130 | 17 | 2.3 | BMRL | 149.3 | 2.8 | 27 | 17 | BMRL | BMRL | 5.9 | BMRL | BMRL | 3.3 | 46.8 | 52.7 | D-B-3 | Duplicate | 1999-03-01 | 10:45 | 261.75 | 1570.5 | 7.19 | 0.02 | 12 | 0.12 | BMRL | BMRL | #VALUE! | 3 | 2.1 | 0.9 | 10 | 9.27 | 240 | BMRL | 0.9 | 1.4 | 1 | BMRL | 3.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | D-C-3 | Duplicate | 1999-03-04 | 13:00 | 336 | 1008 | 7.3 | 0 | 12 | 0.09 | BMRL | BMRL | #VALUE! | 3 | 2.3 | 0.7 | 10 | 9.24 | 168 | BMRL | 1 | 0.6 | BMRL | BMRL | 1.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[9 empty] | Avg-A-3 | Average | --- | --- | --- | --- | --- | 7.195 | 0.025 | 60 | 10 | 88 | 44 | 0.16 | #DIV/0! | 3.35 | 0.064 | 1.9109 | 5 | 1.35 | 3.65 | 10 | 9.265 | 168 | 510 | 130 | 17.5 | 2.35 | #DIV/0! | 149.85 | 3.55 | 27 | 16.5 | #DIV/0! | #DIV/0! | 5.9 | #DIV/0! | #DIV/0! | 3.3 | 47.05 | 52.95 | Avg-B-3 | Average | --- | --- | --- | --- | 7.19 | 0.02 | 12 | 0.105 | #DIV/0! | #DIV/0! | #VALUE! | 3 | 2.15 | 0.85 | 10 | 9.255 | 240 | #DIV/0! | 0.95 | 1.4 | 1 | #DIV/0! | 3.35 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | Avg-C-3 | Average | --- | --- | --- | --- | 7.29 | 0 | 12 | 0.09 | #DIV/0! | #DIV/0! | #VALUE! | 3 | 2.3 | 0.7 | 10 | 9.23 | 168 | #DIV/0! | 0.85 | 0.8 | 0.7 | #DIV/0! | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[9 empty] | RPD-A-3 | RPD | --- | --- | --- | --- | --- | 0.13899 | 40 | 0 | 0 | 0 | 0 | 50 | #VALUE! | 2.9851 | 0 | 2.9851 | 0 | 7.4074 | 2.7397 | 0 | 0.3238 | 0 | #VALUE! | 0 | 5.7143 | 4.2553 | #VALUE! | 0.73407 | 42.2535 | 0 | 6.0606 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 1.0627 | 0.94429 | RPD-B-3 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 28.5714 | #VALUE! | #VALUE! | #VALUE! | 0 | 4.6512 | 11.7647 | 0 | 0.32415 | 0 | #VALUE! | 10.5263 | 0 | 0 | #VALUE! | 2.9851 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | RPD-C-3 | RPD | --- | --- | --- | --- | 0.27435 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0.21668 | 0 | #VALUE! | 35.2941 | 50 | #VALUE! | #VALUE! | 40 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A-8 | Primary | 1999-03-24 | 14:00 | 817 | 2451 | 4902 | 7.05 | 0.04 | 60 | 10 | 89 | 54 | 0.07 | BMRL | 3.8 | 0.057 | 1.5 | 5 | 1.8 | 3.2 | 10 | 9.24 | 168 | 300 | 170 | 18 | 2.2 | BMRL | 190.2 | BMRL | 29 | 17 | BMRL | BMRL | 5.5 | BMRL | BMRL | 3.1 | 46 | 51.5 | B-8 | Primary | 1999-03-17 | 15:00 | 650 | 3900 | 7.37 | 0.06 | 12 | BMRL | 1 | 0.01 | 1 | 3 | 2.2 | 0.8 | 10 | 9.2 | 168 | 69 | 23 | 7.1 | 3 | BMRL | 33.1 | BMRL | 5 | 2.5 | BMRL | 1.1 | 2.5 | BMRL | BMRL | 1.6 | 8.6 | 11.1 | C-8 | Primary | 1999-03-24 | 14:00 | 817 | 2451 | 7.04 | 0.04 | 12 | BMRL | 0.6 | BMRL | #VALUE! | 3 | 2.9 | 0.1 | 10 | 9.28 | 168 | BMRL | 1.2 | 1.6 | 1.3 | BMRL | 4.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[9 empty] | D-A-8 | Duplicate | 1999-03-24 | 14:00 | 817 | 2451 | 4902 | 7.05 | 0.04 | 58 | 10 | 89 | 54 | 0.06 | BMRL | 3.8 | 0.057 | 1.5 | 5 | 2 | 3 | 10 | 9.3 | 168 | 335 | 160 | 18 | 2.1 | BMRL | 180.1 | BMRL | 30 | 18 | BMRL | BMRL | 5.7 | BMRL | BMRL | 3.2 | 48 | 53.7 | D-B-8 | Duplicate | 1999-03-17 | 15:00 | 650 | 3900 | 7.37 | 0.06 | 12 | BMRL | 1 | 0.01 | 1 | 3 | 2.4 | 0.6 | 10 | 9.2 | 168 | 68 | 22 | 7.1 | 3.1 | BMRL | 32.2 | BMRL | 4.7 | 2.4 | BMRL | 1.2 | 2.5 | BMRL | BMRL | 1.6 | 8.3 | 10.8 | D-C-8 | Duplicate | 1999-03-24 | 14:00 | 817 | 2451 | 7.05 | 0.03 | 12 | BMRL | 0.8 | BMRL | #VALUE! | 3 | 2.8 | 0.2 | 10 | 9.28 | 168 | BMRL | 2.2 | 3.3 | 2.5 | BMRL | 8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0
[9 empty] | Avg-A-8 | Average | --- | --- | --- | --- | --- | 7.05 | 0.04 | 59 | 10 | 89 | 54 | 0.065 | #DIV/0! | 3.8 | 0.057 | 1.5 | 5 | 1.9 | 3.1 | 10 | 9.27 | 168 | 317.5 | 165 | 18 | 2.15 | #DIV/0! | 185.15 | #DIV/0! | 29.5 | 17.5 | #DIV/0! | #DIV/0! | 5.6 | #DIV/0! | #DIV/0! | 3.15 | 47 | 52.6 | Avg-B-8 | Average | --- | --- | --- | --- | 7.37 | 0.06 | 12 | #DIV/0! | 1 | 0.01 | 1 | 3 | 2.3 | 0.7 | 10 | 9.2 | 168 | 68.5 | 22.5 | 7.1 | 3.05 | #DIV/0! | 32.65 | #DIV/0! | 4.85 | 2.45 | #DIV/0! | 1.15 | 2.5 | #DIV/0! | #DIV/0! | 1.6 | 8.45 | 10.95 | Avg-C-8 | Average | --- | --- | --- | --- | 7.045 | 0.035 | 12 | #DIV/0! | 0.7 | #DIV/0! | #VALUE! | 3 | 2.85 | 0.15 | 10 | 9.28 | 168 | #DIV/0! | 1.7 | 2.45 | 1.9 | #DIV/0! | 6.05 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[9 empty] | RPD-A-8 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 3.3898 | 0 | 0 | 0 | 15.3846 | #VALUE! | 0 | 0 | 0 | 0 | 10.5263 | 6.4516 | 0 | 0.64725 | 0 | 11.0236 | 6.0606 | 0 | 4.6512 | #VALUE! | 5.455 | #VALUE! | 3.3898 | 5.7143 | #VALUE! | #VALUE! | 3.5714 | #VALUE! | #VALUE! | 3.1746 | 4.2553 | 4.1825 | RPD-B-8 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | 8.6957 | 28.5714 | 0 | 0 | 0 | 1.4599 | 4.4444 | 0 | 3.2787 | #VALUE! | 2.7565 | #VALUE! | 6.1856 | 4.0816 | #VALUE! | 8.6957 | 0 | #VALUE! | #VALUE! | 0 | 3.5503 | 2.7397 | RPD-C-8 | RPD | --- | --- | --- | --- | 0.14194 | 28.5714 | 0 | #VALUE! | 28.5714 | #VALUE! | #VALUE! | 0 | 3.5088 | 66.6667 | 0 | 0 | 0 | #VALUE! | 58.8235 | 69.3878 | 63.1579 | #VALUE! | 64.4628 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A-13 | Primary | 1999-04-20 | 8:30 | 1459.5 | 4378.5 | 8757 | 10.83 | 0.04 | 45 | 10 | 73 | 56 | NR | BMRL | 3.4 | 0.056 | 1.6471 | 5 | 2 | 3 | 10 | 9.36 | 192 | 370 | 160 | 16 | 1.8 | BMRL | 177.8 | 3.7 | 28 | 14 | BMRL | BMRL | 4.9 | BMRL | BMRL | 2.2 | 45.7 | 50.6 | B-13 | Primary | 1999-04-06 | 13:00 | 1128 | 6768 | 7.38 | 0.05 | 12 | BMRL | 2 | 0.022 | 1.1 | 3 | 2.1 | 0.9 | 10 | 9.03 | 192 | 115 | 34 | 9.7 | 3.1 | BMRL | 46.8 | BMRL | 9.5 | 5.5 | BMRL | BMRL | 3.5 | BMRL | BMRL | 2.1 | 15 | 18.5 | C-13 | Primary | 1999-04-20 | 8:30 | 1459.5 | 4378.5 | 6.89 | 0.04 | 12 | BMRL | 1.3 | 0.013 | 1 | 3 | 2.4 | 0.6 | 10 | 9.19 | 192 | 66 | 22 | 9.5 | 4.7 | BMRL | 36.2 | BMRL | 5.4 | 3 | BMRL | 1.2 | 2.7 | BMRL | BMRL | 1.3 | 9.6 | 12.3
[9 empty] | D-A-13 | Duplicate | 1999-04-20 | 8:30 | 1459.5 | 4378.5 | 8757 | 10.83 | 0.04 | 45 | 10 | 72 | 56 | 0.06 | BMRL | 4.3 | 0.057 | 1.3256 | 5 | 2 | 3 | 10 | 9.39 | 192 | 320 | 160 | 15 | 1.5 | BMRL | 176.5 | 3.3 | 28 | 14 | BMRL | BMRL | 4.8 | BMRL | BMRL | 2.1 | 45.3 | 50.1 | D-B-13 | Duplicate | 1999-04-06 | 13:00 | 1128 | 6768 | 7.37 | 0.05 | 12 | 0.13 | 2.6 | 0.022 | 0.84615 | 3 | 2 | 1 | 10 | 9.03 | 192 | 130 | 37 | 10 | 3.2 | BMRL | 50.2 | BMRL | 11 | 5.5 | BMRL | BMRL | 3.5 | BMRL | BMRL | 2.1 | 16.5 | 20 | D-C-13 | Duplicate | 1999-04-20 | 8:30 | 1459.5 | 4378.5 | 6.9 | 0.04 | 12 | 0.32 | 1.3 | 0.013 | 1 | 3 | 2.4 | 0.6 | 10 | 9.22 | 192 | 74 | 22 | 9.1 | 4.6 | BMRL | 35.7 | BMRL | 5.4 | 3 | BMRL | 1.3 | 2.8 | BMRL | BMRL | 1.3 | 9.7 | 12.5
[9 empty] | Avg-A-13 | Average | --- | --- | --- | --- | --- | 10.83 | 0.04 | 45 | 10 | 72.5 | 56 | 0.06 | #DIV/0! | 3.85 | 0.0565 | 1.4863 | 5 | 2 | 3 | 10 | 9.375 | 192 | 345 | 160 | 15.5 | 1.65 | #DIV/0! | 177.15 | 3.5 | 28 | 14 | #DIV/0! | #DIV/0! | 4.85 | #DIV/0! | #DIV/0! | 2.15 | 45.5 | 50.35 | Avg-B-13 | Average | --- | --- | --- | --- | 7.375 | 0.05 | 12 | 0.13 | 2.3 | 0.022 | 0.97308 | 3 | 2.05 | 0.95 | 10 | 9.03 | 192 | 122.5 | 35.5 | 9.85 | 3.15 | #DIV/0! | 48.5 | #DIV/0! | 10.25 | 5.5 | #DIV/0! | #DIV/0! | 3.5 | #DIV/0! | #DIV/0! | 2.1 | 15.75 | 19.25 | Avg-C-13 | Average | --- | --- | --- | --- | 6.895 | 0.04 | 12 | 0.32 | 1.3 | 0.013 | 1 | 3 | 2.4 | 0.6 | 10 | 9.205 | 192 | 70 | 22 | 9.3 | 4.65 | #DIV/0! | 35.95 | #DIV/0! | 5.4 | 3 | #DIV/0! | 1.25 | 2.75 | #DIV/0! | #DIV/0! | 1.3 | 9.65 | 12.4
[9 empty] | RPD-A-13 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 1.3793 | 0 | #VALUE! | #VALUE! | 23.3766 | 1.7699 | 21.6291 | 0 | 0 | 0 | 0 | 0.32 | 0 | 14.4928 | 0 | 6.4516 | 18.1818 | #VALUE! | 0.73384 | 11.4286 | 0 | 0 | #VALUE! | #VALUE! | 2.0619 | #VALUE! | #VALUE! | 4.6512 | 0.87912 | 0.99305 | RPD-B-13 | RPD | --- | --- | --- | --- | 0.13559 | 0 | 0 | #VALUE! | 26.087 | 0 | 26.087 | 0 | 4.878 | 10.5263 | 0 | 0 | 0 | 12.2449 | 8.4507 | 3.0457 | 3.1746 | #VALUE! | 7.0103 | #VALUE! | 14.6341 | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 9.5238 | 7.7922 | RPD-C-13 | RPD | --- | --- | --- | --- | 0.14503 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32591 | 0 | 11.4286 | 0 | 4.3011 | 2.1505 | #VALUE! | 1.3908 | #VALUE! | 0 | 0 | #VALUE! | 8 | 3.6364 | #VALUE! | #VALUE! | 0 | 1.0363 | 1.6129
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AC53: Reviewer M.H. (12/17/99): Per Consultant: "TOC results in cells (AC50-1) are correct."
Note on AG6: Reviewer M.H. (12/17/99): Per Consultant: "SDS influent fluctuation attributed to seasonal variation. Study ran from February to June, temperature ranged from 10 to 18 degrees. Algae species in resevoir system changed from diatoms to blue-greens."
Note on AK6: Reviewer M.H. (12/17/99): Per Consultant: "The target SDS temperature was 168 hours. The fluctuations major were probably due to sampling error. The SDS incubation temperatures are measured results."
Note on AR45: Reviewer M.H. (12/17/99): Per Consultant: "TOX and MCAA results are correct."
Note on BN24: Reviewer M.H. (12/17/99): Per Consultant: "Day 61 appears to be an outlier. The results for TOC, UV254, THM4, HAA6, and TOX all much higher than expected. They have been changed to NR. The last sample however, we believe is accurate, our in-house TOC analysis was similar to MWL. We believe TOC was high due to breakthrough."
Note on CY25: Reviewer M.H. (12/17/99): Per Consultant: "The last TOC sample we believe is not an outlier. UV254 was also high. We believe breakthrough was achieved. We just failed to confirm it with another sample."
Note on CY49: Reviewer M.H. (12/17/99): Per Consultant: "TOC results are correct."
Note on DI49: Reviewer M.H. (12/17/99): Per Consultant: "THM results (cells DI46-DK47) are correct."
Note on DJ49: Reviewer M.H. (12/17/99): Per Consultant: "THM results (cells DI46-DK47) are correct."
Note on DK49: Reviewer M.H. (12/17/99): Per Consultant: "THM results (cells DI46-DK47) are correct."
Note on DM49: Reviewer M.H. (12/17/99): Per Consultant: "THM results (cells DI46-DK47) are correct."
Note on EA19: Martha Burckhardt: $1.87/1000 gal retail $0.53/1000 gal production