## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
[31 empty] | Platte River WTP - Spring Test | [35 empty] | Platte River WTP - Spring Test
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run |  |  |  | Platte River WTP - Spring Test |  |  | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 |  |  |  | Platte River WTP - Spring Test |  |  | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [5 empty] | (Note: Test actually started on April 16, but had to be aborted after 4 hours until problems with air in columns due to CO2 generation could be resolved; | [10 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [8 empty] | Platte River WTP - Spring Test | [7 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [7 empty] | (Note: Test actually started on April 16, but had to be aborted after 4 hours until problems with air in columns due to CO2 generation could be resolved; | [7 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Platte River WTP - Spring Test | [10 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [6 empty] | those 4 hours were moved to April 22 and accounted for by changing start time from 7:00 AM to 3:00 AM ) | [26 empty] | Group C, 12 effluent samples per run | [8 empty] | those 4 hours were moved to April 22 and accounted for by changing start time from 7:00 AM to 3:00 AM )
PWS Name | Metropolitan Utilities District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 3.25 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-04-22 | [5 empty] | 20-min. EBCT Start Date | 1998-04-22 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NE 3105507 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Lime softening | 77.9 mg/l as CaO | Full-Scale | 10-min. EBCT Start Time | 3:00 | [5 empty] | 20-min. EBCT Start Time | 3:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Coagulation | 1.9 mg/l alum | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 15 | 6 | 3.35 | Flocculation | 1-stage | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-04-22 | 4:00 | 1 | 44.4 | 7.3 | 21 | 1.05 | 0.01 | 0.95238 | 0.5 | 0.5 | 0 | 4.1 | 9.3 | 12 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C1-20 | N | 1998-04-22 | 4:00 | 1 | 22.2 | 7.3 | 21 | 0.85 | 0.001 | 0.11765 | 0.5 | 0.5 | 0 | 4.1 | 9.3 | 12 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | NR | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | NR | NR | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Clarification | solids contact (255 minutes detention) | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-04-23 | 9:30 | 30.5 | 1354.2 | 8.2 | 21 | NR | 0.025 | #VALUE! | 0.8 | 0.34 | 0.46 | 4 | 9.6 | 15 | BMRL | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | C2-20 | N | 1998-04-25 | 7:30 | 76.5 | 1698.3 | 7.7 | 21 | 1.1 | 0.006 | 0.54545 | 0.7 | 0.61 | 0.09 | 7 | 10.4 | 13 | BMRL | BMRL | 1 | 1.8 | 2.1 | 4.9 | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1 | 1 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Dual media filtration | anthracite(dep=18"; 0.95 to 1.05 mm)/sand(dep=12"; 0.45 to 0.55 mm) | Full-Scale | Sampling date | MM/DD/YY | 1998-04-22 | 1998-05-02 | --- | --- |  | Sampling date | MM/DD/YY | 1998-04-22 | 1998-05-02 | --- | --- |  | C3-10 | N | 1998-04-25 | 7:30 | 76.5 | 3396.6 | 7.7 | 21 | 1.7 | 0.03 | 1.7647 | 1.2 | 0.55 | 0.65 | 10.4 | 10.4 | 13 | 48 | 3.6 | 3.9 | 2.9 | 1.3 | 11.7 | BMRL | 1.3 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.3 | 1.3 | C3-20 | N | 1998-04-26 | 12:00 | 105 | 2331 | 8.4 | 21 | 1.05 | 0.009 | 0.85714 | 0.7 | 0.6 | 0.1 | 7 | 10.4 | 13 | BMRL | BMRL | 1.4 | 4.1 | 4.7 | 10.2 | BMRL | 1 | BMRL | BMRL | 4.7 | BMRL | NA | NA | NA | 5.7 | 5.7 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 60 | 12 | 1.68 | Sulfuric acid addition | pH = 7.5 | Bench-Scale | Sampling time | hh:mm | 3:00 | 12:00 | --- | --- |  | Sampling time | hh:mm | 3:00 | 12:00 | --- | --- |  | C4-10 | N | 1998-04-26 | 8:00 | 101 | 4484.4 | 8.3 | 21 | NR | 0.039 | #VALUE! | 1.2 | 0.29 | 0.91 | 7 | 9.4 | 11 | NR | 7.6 | 15 | 7.8 | 2.3 | NR | BMRL | 1.5 | BMRL | BMRL | 4.1 | 2 | NA | NA | NA | 5.6 | 7.6 | C4-20 | N | 1998-04-28 | 9:00 | 150 | 3330 | 8 | 21.5 | 1.5 | 0.017 | 1.1333 | 0.8 | 0.6 | 0.2 | 10 | 9.7 | 10 | 34 | 3.7 | 3.9 | 4.7 | 2.6 | 14.9 | BMRL | 1 | BMRL | BMRL | 5 | BMRL | NA | NA | NA | 6 | 6 | Engineering Fee Factor (% of construction costs) | 8
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 | In-line filtration | 1 um to 2 um exclusion size | Bench-Scale | Operation time | hh.hh | 0 | 249 | --- | --- |  | Operation time | hh.hh | 0 | 249 | --- | --- |  | C5-10 | N | 1998-04-27 | 8:00 | 125 | 5550 | 8.4 | 21.3 | 2.3 | 0.04 | 1.7391 | 1.2 | 0.13 | 1.07 | 8 | 8.8 | 9 | 70 | 4.7 | 9.4 | 8.6 | 3.7 | 26.4 | 2.2 | 1.6 | BMRL | BMRL | 5.4 | 2.4 | NA | NA | NA | NR | NR | Avg-C5- 20 | Y | 1998-04-30 | 10:00 | 199 | 4417.8 | 8.1 | 21.5 | 1.83 | 0.028 | 1.5301 | 0.9 | 0.505 | 0.395 | 9 | 9.3 | 9 | 55 | 2.1 | 6.8 | 9.95 | 6.4 | 25.25 | BMRL | 1.1 | BMRL | BMRL | 6.45 | 1.7 | NA | NA | NA | 7.55 | 9.25 | 1999 ENR Construction Cost Index (CCI base year 1913) | 6039
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 11055.6 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 5527.8 | --- | --- |  | C6-10 | N | 1998-04-28 | 8:00 | 149 | 6615.6 | 8.2 | 21.5 | 2.65 | 0.039 | 1.4717 | 1.2 | 0.4 | 0.8 | 8 | 10 | 10 | 80 | 1.1 | 2.5 | 4.6 | 4.9 | NR | BMRL | 2.9 | BMRL | BMRL | 4.2 | 2.6 | NA | NA | NA | 7.1 | 9.7 | Avg-C6-20 | Y | 1998-05-02 | 12:00 | 249 | 5527.8 | 8.2 | 21 | 1.9 | 0.029 | 1.5263 | 0.9 | 0.4 | 0.5 | 9 | 9.1 | 12 | 60.5 | 2.35 | 7.95 | 12 | 4.5 | 26.8 | BMRL | 1.15 | BMRL | BMRL | 7.1 | 2.3 | NA | NA | NA | 8.25 | 10.55 | 1999 Producers Price Index (PPI base year 1967 = 100) | 1947
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 141 | 107 | 124 | 27.4194 |  | Alkalinity | mg/L as CaCO3 | 141 | 107 | 124 | 27.4194 |  | C7-10 | N | 1998-04-29 | 8:00 | 173 | 7681.2 | 8 | 21 | 2.8 | 0.044 | 1.5714 | 0.9 | 0.17 | 0.73 | 9.5 | 9.3 | 13 | 87 | 6.3 | 8.9 | 7.1 | 6.3 | 28.6 | BMRL | 2.1 | BMRL | BMRL | 4.6 | 2.5 | NA | NA | NA | 6.7 | 9.2 | C7-20 | N | 1998-05-04 | 8:30 | 293.5 | 6515.7 | 8.5 | 21.5 | 2.35 | 0.036 | 1.5319 | 1 | 0.36 | 0.64 | 8 | 9.1 | 11 | 56.5 | 3.2 | 7.1 | 5.9 | 2.6 | 18.8 | BMRL | 1.4 | BMRL | BMRL | 4 | 1.9 | NA | NA | NA | 5.4 | 7.3 | Labor Rate + Fringe ($/work-hour) | 26
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 4688.2565 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 182 | 182 | 182 | 0 |  | Total hardness | mg/L as CaCO3 | 182 | 182 | 182 | 0 |  | Avg-C8-10 | Y | 1998-04-30 | 8:00 | 197 | 8746.8 | 8.2 | 21 | 2.55 | 0.043 | 1.6863 | 1.2 | 0.53 | 0.67 | 9.5 | 9.27 | 9 | 93.25 | 7.75 | 11 | 10.5 | 3.5 | 32.75 | BMRL | 2.55 | 1 | BMRL | 5.8544 | 3.2 | NA | NA | NA | 9.4044 | 12.6044 | Avg-C8-20 | Y | 1998-05-06 | 8:30 | 341.5 | 7581.3 | 8.4 | 22 | 2.55 | 0.038 | 1.4902 | 1 | 0.09 | 0.91 | 10 | 9.3 | 11 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 9376.513 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 118 | 113 | 115.5 | 4.329 |  | Calcium hardness | mg/L as CaCO3 | 118 | 113 | 115.5 | 4.329 |  | C9-10 | N | 1998-05-01 | 8:00 | 221 | 9812.4 | 8.4 | 21 | 2.8 | 0.043 | 1.5357 | 1.2 | 0.03 | 1.17 | 10 | 8.9 | 10 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | C9-20 | N | 1998-05-08 | 10:00 | 391 | 8680.2 | 8.45 | 21.5 | 2.05 | 0.038 | 1.8537 | 1.2 | 0.05 | 1.15 | 10 | 9.3 | 10.5 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Electric Rate ($/kW-h) | 0.05
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 12189.4669 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Avg-C10-10 | Y | 1998-05-02 | 12:00 | 249 | 11055.6 | 8.3 | 21.5 | 2.65 | 0.046 | 1.7358 | 1.6 | 0.91 | 0.69 | 9 | 8.9 | 12 | 98.25 | 9.65 | 12.5 | 12 | 2.65 | 36.8 | BMRL | 9.3 | 1.25 | BMRL | 6.5 | 3.85 | NA | NA | NA | NR | NR | C10-20 | N | 1998-05-10 | 9:30 | 438.5 | 9734.7 | 8.4 | 21 | 2.6 | NR | #VALUE! | 1.4 | 0.9 | 0.5 | 7 | 9.3 | 9 | 71 | 4.6 | 8 | 6.5 | 4.6 | 23.7 | BMRL | 5 | BMRL | BMRL | 1.8 | 2.8 | NA | NA | NA | 6.8 | 9.6 | Fuel Oil Rate ($/gal) | 0.5
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 85 | 92 | 88.5 | 7.9096 |  | Bromide | mg/L | 85 | 92 | 88.5 | 7.9096 |  | C11-10 | N | 1998-05-03 | 8:30 | 269.5 | 11965.8 | 8.2 | 21 | 2.7 | 0.041 | 1.5185 | 1.4 | 0.22 | 1.18 | 9 | 9.5 | 10.5 | 97 | 12 | 11 | 8.1 | 2.3 | 33.4 | BMRL | 4.3 | 1.4 | BMRL | 4.3 | 3.2 | NA | NA | NA | 10 | 13.2 | C11-20 | N | 1998-05-13 | 10:00 | 511 | 11344.2 | 8.6 | 21.5 | 3.35 | 0.028 | 0.83582 | 1.4 | 0.72 | 0.68 | 8 | 9.1 | 10 | 91.5 | 10 | 13 | 14 | 4.2 | 41.2 | BMRL | 4.2 | BMRL | BMRL | 2.6 | 3.7 | NA | NA | NA | 6.8 | 10.5 | Natural Gas Rate ($/ft3) | 3.5
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-05-04 | 8:30 | 293.5 | 13031.4 | 8.5 | 21.5 | 2.55 | 0.04 | 1.5686 | 1.2 | 0.48 | 0.72 | 8 | 9 | 11 | NR | 4.3 | 8 | 6.6 | 2.4 | NR | BMRL | 2.1 | BMRL | BMRL | 5.4 | 3.1 | NA | NA | NA | 7.5 | 10.6 |  |  |  |  | -861771 | -19131316.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Current Process Water Rate ($/1000 gal) | 0.3
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1625e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [6 empty] | C13-10 | N | 1998-05-05 | 10:00 | 319 | 14163.6 | 8.2 | 21.9 | 2.5 | 0.052 | 2.08 | 1.2 | 0.44 | 0.76 | 8 | 9.5 | 11 | 102.5 | 11 | 12 | 9.4 | 2.5 | 34.9 | BMRL | 4.9 | BMRL | BMRL | 1.8 | 3.4 | NA | NA | NA | 6.7 | 10.1 |  |  |  |  | -861771 | -19131316.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.2 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD |  |  |  |  | -861771 | -38262632.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861771 | -19131316.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 7.4 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-29 | 1998-05-12 | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-29 | 1998-05-12 | --- | --- |  |  |  |  | -861771 | -38262632.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861771 | -19131316.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Platte River Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 4.7081 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 3:00 | 8:00 | 8:30 | --- | --- | Sampling time | hh:mm | 3:00 | 8:00 | 8:30 | --- | --- |  |  |  |  | -861771 | -38262632.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861771 | -19131316.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | STS |  |  | RSSCT flow rate, QSC (mL/min) | 7.4572 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 173 | 485.5 | --- | --- | Operation time | hh.hh | 0 | 173 | 485.5 | --- | --- |  |  |  |  | -861771 | -38262632.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861771 | -19131316.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | SplitTrt/Softening |  |  | Estimated total influent volume required, VSCT (L) | 368.5088 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 7681.2 | 21556.2 | --- | --- | Bed volumes | (20 minute) | 0 | 3840.6 | 10778.1 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 454 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.1 | 8 | 8.6 | 8.2333 | 3.9043 | pH | --- | 8.1 | 8 | 8.6 | 8.2333 | 3.9043 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | 28507002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.3 | 0.2 | 0.1 | 0.2 | 50 | Turbidity | ntu | 0.3 | 0.2 | 0.1 | 0.2 | 50 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 18.8 | 21 | 21.9 | 20.5667 | 7.7542 | Temperature | oC | 4.1 | 9.5 | 10 | 7.8667 | 41.5881
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 84.6491 | [5 empty] | Total organic carbon | mg/L | 3.25 | 3 | 3.5 | 3.25 | 7.6923 | Total organic carbon | mg/L | 3.25 | 3 | 3.5 | 3.25 | 7.6923 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3514 | [5 empty] | UV254 | cm-1 | 0.071 | 0.081 | 0.065 | 0.072333 | 11.1745 | UV254 | cm-1 | 0.071 | 0.081 | 0.065 | 0.072333 | 11.1745 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 11.4391 | [5 empty] | SUVA | L/(mg*m) | 2.1846 | 2.7 | 1.8571 | 2.2473 | 18.9078 | SUVA | L/(mg*m) | 2.1846 | 2.7 | 1.8571 | 2.2473 | 18.9078 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.6039 | [5 empty] | SDS-Cl2 dose | mg/L | 1.5 | 1.5 | 1.5 | 1.5 | 0 | SDS-Cl2 dose | mg/L | 1.5 | 1.5 | 1.5 | 1.5 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 122.8363 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.5 | 0.2 | 0.62 | 0.44 | 49.1666 | SDS-Free Cl2 residual | mg/L | 0.5 | 0.2 | 0.62 | 0.44 | 49.1666 | C8-10 | Primary | 1998-04-30 | 8:00 | 197 | 8746.8 | 8.2 | 21 | 2.65 | 0.043 | 1.6226 | 1.2 | 0.52 | 0.68 | 9.5 | 9.24 | 9 | 94 | 7.6 | 11 | 10 | 3.6 | 32.2 | BMRL | 2.6 | 1 | BMRL | 5.7 | 3 | NA | NA | NA | 9.3 | 12.3 | C5-20 | Primary | 1998-04-30 | 10:00 | 199 | 4417.8 | 8.1 | 21.5 | 1.85 | 0.028 | 1.5135 | 0.9 | 0.5 | 0.4 | 9 | 9.3 | 12 | 57 | 2.2 | 7 | 10 | 6.3 | 25.5 | BMRL | 1.1 | BMRL | BMRL | 6.5 | 1.8 | NA | NA | NA | 7.6 | 9.4
|  |  |  | Mass GAC required, mSC (g) | 5.0386 | [5 empty] | SDS-Cl2 demand | mg/L | 1 | 1.3 | 0.88 | 1.06 | 20.4088 | SDS-Cl2 demand | mg/L | 1 | 1.3 | 0.88 | 1.06 | 20.4088 | D-C8-10 | Duplicate | 1998-04-30 | 8:00 | 197 | 8746.8 | 8.2 | 21 | 2.5 | 0.043 | 1.72 | 1.2 | 0.54 | 0.66 | 9.5 | 9.3 | 9 | 92.5 | 7.9 | 11 | 11 | 3.4 | 33.3 | BMRL | 2.5 | BMRL | BMRL | 6 | 3.4 | NA | NA | NA | 8.5 | 11.9 | D-C5-20 | Duplicate | 1998-04-30 | 10:00 | 199 | 4417.8 | 8.1 | 21.5 | 1.8 | 0.028 | 1.5556 | 0.9 | 0.51 | 0.39 | 9 | 9.3 | 9.3 | 53 | 2 | 6.6 | 9.9 | 6.5 | 25 | BMRL | 1.1 | BMRL | BMRL | 6.4 | 1.6 | NA | NA | NA | 7.5 | 9.1
[11 empty] | SDS-Chlorination temp. | oC | 4.1 | 9.5 | 10 | 7.8667 | 41.5881 | SDS-Chlorination temp. | oC | 4.1 | 9.5 | 10 | 7.8667 | 41.5881 | Avg-C8-10 | Average | --- | --- | --- | --- | 8.2 | 21 | 2.575 | 0.043 | 1.6713 | 1.2 | 0.53 | 0.67 | 9.5 | 9.27 | 9 | 93.25 | 7.75 | 11 | 10.5 | 3.5 | 32.75 | #DIV/0! | 2.55 | 1 | #DIV/0! | 5.85 | 3.2 | #DIV/0! | #DIV/0! | #DIV/0! | 8.9 | 12.1 | Avg-C5-20 | Average | --- | --- | --- | --- | 8.1 | 21.5 | 1.825 | 0.028 | 1.5345 | 0.9 | 0.505 | 0.395 | 9 | 9.3 | 10.65 | 55 | 2.1 | 6.8 | 9.95 | 6.4 | 25.25 | #DIV/0! | 1.1 | #DIV/0! | #DIV/0! | 6.45 | 1.7 | #DIV/0! | #DIV/0! | #DIV/0! | 7.55 | 9.25
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9.3 | 9.3 | 9.4 | 9.3333 | 0.61859 | SDS-Chlorination pH | --- | 9.3 | 9.3 | 9.4 | 9.3333 | 0.61859 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0 | 0 | 5.8252 | 0 | 5.8252 | 0 | 3.7736 | 2.9851 | 0 | 0.64725 | 0 | 1.6086 | 3.871 | 0 | 9.5238 | 5.7143 | 3.3588 | #VALUE! | 3.9216 | #VALUE! | #VALUE! | 5.1282 | 12.5 | #VALUE! | #VALUE! | #VALUE! | 8.9888 | 3.3058 | RPD-C5-20 | RPD | --- | --- | --- | --- | 0 | 0 | 1.8 | 0 | 2.7397 | 0 | 1.9802 | 2.5316 | 0 | 0 | 25.3521 | 7.2727 | 9.5238 | 5.8824 | 1.005 | 3.125 | 1.9802 | #VALUE! | 0 | #VALUE! | #VALUE! | 1.5504 | 11.7647 | #VALUE! | #VALUE! | #VALUE! | 1.3245 | 3.2432
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 12 | 13 | 10 | 11.6667 | 13.0931 | SDS-Incubation time | hours | 12 | 13 | 10 | 11.6667 | 13.0931 | C10-10 | Primary | 1998-05-02 | 12:00 | 249 | 11055.6 | 8.3 | 21.5 | 2.75 | 0.047 | 1.7091 | 1.6 | 0.89 | 0.71 | 9 | 8.9 | 12 | 97.5 | 9.8 | 13 | 12 | 2.7 | 37.5 | BMRL | 9.2 | 1.2 | BMRL | 6.5 | 3.8 | NA | NA | NA | 16.9 | 20.7 | C6-20 | Primary | 1998-05-02 | 12:00 | 249 | 5527.8 | 8.2 | 21 | 1.85 | 0.028 | 1.5135 | 0.9 | 0.42 | 0.48 | 9 | 9.1 | 12 | 58 | 2.5 | 7.8 | 12 | 6 | 28.3 | BMRL | 1.2 | BMRL | BMRL | 7.1 | 2.3 | NA | NA | NA | 8.3 | 10.6
|  |  |  | Estimated full-scale run time, tLCT (days) | 169.2982 | [5 empty] | SDS-TOX | mg Cl- /L | 110.5 | 143 | 132 | 128.5 | 12.864 | SDS-TOX | mg Cl- /L | 110.5 | 143 | 132 | 128.5 | 12.864 | D-C10-10 | Duplicate | 1998-05-02 | 12:00 | 249 | 11055.6 | 8.3 | 21.5 | 2.55 | 0.045 | 1.7647 | 1.6 | 0.93 | 0.67 | 9 | 8.9 | 12 | 99 | 9.5 | 12 | 12 | 2.6 | 36.1 | BMRL | 9.4 | 1.3 | BMRL | 6.5 | 3.9 | NA | NA | NA | 17.2 | 21.1 | D-C6-20 | Duplicate | 1998-05-02 | 12:00 | 249 | 5527.8 | 8.2 | 21 | 1.95 | 0.03 | 1.5385 | 0.9 | 0.38 | 0.52 | 9 | 9.1 | 12 | 63 | 2.2 | 8.1 | 12 | 3 | 25.3 | BMRL | 1.1 | BMRL | BMRL | 7.1 | 2.3 | NA | NA | NA | 8.2 | 10.5
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.7027 | [5 empty] | SDS-CHCl3 | mg/L | 20 | 17 | 20 | 19 | 9.1161 | SDS-CHCl3 | mg/L | 20 | 17 | 20 | 19 | 9.1161 | Avg-C10-10 | Average | --- | --- | --- | --- | 8.3 | 21.5 | 2.65 | 0.046 | 1.7369 | 1.6 | 0.91 | 0.69 | 9 | 8.9 | 12 | 98.25 | 9.65 | 12.5 | 12 | 2.65 | 36.8 | #DIV/0! | 9.3 | 1.25 | #DIV/0! | 6.5 | 3.85 | #DIV/0! | #DIV/0! | #DIV/0! | 17.05 | 20.9 | Avg-C6-20 | Average | --- | --- | --- | --- | 8.2 | 21 | 1.9 | 0.029 | 1.526 | 0.9 | 0.4 | 0.5 | 9 | 9.1 | 12 | 60.5 | 2.35 | 7.95 | 12 | 4.5 | 26.8 | #DIV/0! | 1.15 | #DIV/0! | #DIV/0! | 7.1 | 2.3 | #DIV/0! | #DIV/0! | #DIV/0! | 8.25 | 10.55
|  |  |  | Estimated RSSCT run time, tSCT (days) | 22.8781 | [5 empty] | SDS-BDCM | mg/L | 12 | 14 | 14 | 13.3333 | 8.6603 | SDS-BDCM | mg/L | 12 | 14 | 14 | 13.3333 | 8.6603 | RPD-C10-10 | RPD | --- | --- | --- | --- | 0 | 0 | 7.5472 | 4.3478 | 3.202 | 0 | 4.3956 | 5.7971 | 0 | 0 | 0 | 1.5267 | 3.1088 | 8 | 0 | 3.7736 | 3.8043 | #VALUE! | 2.1505 | 8 | #VALUE! | 0 | 2.5974 | #VALUE! | #VALUE! | #VALUE! | 1.7595 | 1.9139 | RPD-C6-20 | RPD | --- | --- | --- | --- | 0 | 0 | 5.2632 | 6.8966 | 1.6349 | 0 | 10 | 8 | 0 | 0 | 0 | 8.2645 | 12.766 | 3.7736 | 0 | 66.6667 | 11.194 | #VALUE! | 8.6957 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 1.2121 | 0.94787
|  |  |  | RSSCT bed length, lSC (cm) | 21.2079 | [5 empty] | SDS-DBCM | mg/L | 8.7 | 9 | 9.9 | 9.2 | 6.788 | SDS-DBCM | mg/L | 8.7 | 9 | 9.9 | 9.2 | 6.788 | NA | Primary | NA | NA | #VALUE! | #VALUE! | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C8-20 | Primary | 1998-05-06 | 8:30 | 341.5 | 7581.3 | 8.4 | 22 | 2.75 | 0.04 | 1.4545 | 1 | 0.1 | 0.9 | 10 | 9.3 | 11 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 245.6725 | [5 empty] | SDS-CHBr3 | mg/L | 1.9 | 1.9 | 1.7 | 1.8333 | 6.2984 | SDS-CHBr3 | mg/L | 1.9 | 1.9 | 1.7 | 1.8333 | 6.2984 | NA | Duplicate | NA | NA | #VALUE! | #VALUE! | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | D-C8-20 | Duplicate | 1998-05-06 | 8:30 | 341.5 | 7581.3 | 8.4 | 22 | 2.35 | 0.036 | 1.5319 | 1 | 0.08 | 0.92 | 10 | 9.3 | 11 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0
|  |  |  | Mass GAC required, mSC (g) | 10.0772 | [5 empty] | SDS-THM4 | mg/L | 42.6 | 41.9 | 45.6 | 43.3667 | 4.5324 | SDS-THM4 | mg/L | 42.6 | 41.9 | 45.6 | 43.3667 | 4.5324 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | Avg-C8-20 | Average | --- | --- | --- | --- | 8.4 | 22 | 2.55 | 0.038 | 1.4932 | 1 | 0.09 | 0.91 | 10 | 9.3 | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | RPD-C8-20 | RPD | --- | --- | --- | --- | 0 | 0 | 15.6863 | 10.5263 | 5.1813 | 0 | 22.2222 | 2.1978 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | 4.7 | 6.6 | 7.6 | 6.3 | 23.3824 | SDS-DCAA* | mg/L | 4.7 | 6.6 | 7.6 | 6.3 | 23.3824 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | BMRL | 1.8 | 2.2 | 2 | 14.1421 | SDS-TCAA* | mg/L | BMRL | 1.8 | 2.2 | 2 | 14.1421 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | BMRL | 5.1 | 2.41 | 3.755 | 50.6556 | SDS-DBAA* | mg/L | BMRL | 5.1 | 2.41 | 3.755 | 50.6556
[11 empty] | SDS-BCAA* | mg/L | 1.1 | 4.5 | 5.3 | 3.6333 | 61.3788 | SDS-BCAA* | mg/L | 1.1 | 4.5 | 5.3 | 3.6333 | 61.3788
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 4.7 | 13.5 | 12.21 | 10.1367 | 46.8819 | SDS-HAA5 | mg/L | 4.7 | 13.5 | 12.21 | 10.1367 | 46.8819
[11 empty] | SDS-HAA6 | mg/L | 5.8 | 18 | 17.51 | 13.77 | 50.1566 | SDS-HAA6 | mg/L | 5.8 | 18 | 17.51 | 13.77 | 50.1566
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on Q33: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on Q35: Reviewer D.S. (10/12/99): Per Consultant: "Samples were incubated in refrigerators in range of 4C to 7C (thermostat was never adjusted). Higher reported temperatures were due to slight warming following removal from refrigerator before temperature was measured."
Note on S53: Reviewer D.S. (10/12/99): Per Consultant: "Low influent Sample B1 HAA probably not due to low reported temperature (sample incubation temperature of influent samples were probably similar to sample B1, but were not checked soon enough after removal from refrigerator). Sample results correct as reported on laboratory analysis report. Not able to determine why HAA result is so low."
Note on S54: Reviewer D.S. (10/12/99): Per Consultant: "Low influent Sample B1 HAA probably not due to low reported temperature (sample incubation temperature of influent samples were probably similar to sample B1, but were not checked soon enough after removal from refrigerator). Sample results correct as reported on laboratory analysis report. Not able to determine why HAA result is so low."
Note on Y33: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on Y35: Reviewer D.S. (10/12/99): Per Consultant: "Samples were incubated in refrigerators in range of 4C to 7C (thermostat was never adjusted). Higher reported temperatures were due to slight warming following removal from refrigerator before temperature was measured."
Note on AA53: Reviewer D.S. (10/12/99): Per Consultant: "Low influent Sample B1 HAA probably not due to low reported temperature (sample incubation temperature of influent samples were probably similar to sample B1, but were not checked soon enough after removal from refrigerator). Sample results correct as reported on laboratory analysis report. Not able to determine why HAA result is so low."
Note on AA54: Reviewer D.S. (10/12/99): Per Consultant: "Low influent Sample B1 HAA probably not due to low reported temperature (sample incubation temperature of influent samples were probably similar to sample B1, but were not checked soon enough after removal from refrigerator). Sample results correct as reported on laboratory analysis report. Not able to determine why HAA result is so low."
Note on AG41: Reviewer D.S. (10/12/99): Per Consultant: "The missing third duplicate set of results was due to a miscommunication between sample collectors."
Note on AS5: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on AS30: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on AU5: Reviewer D.S. (10/12/99): Per Consultant: "Samples were incubated in refrigerators in range of 4C to 7C (thermostat was never adjusted). Higher reported temperatures were due to slight warming following removal from refrigerator before temperature was measured."
Note on AU30: Reviewer D.S. (10/12/99): Per Consultant: "Samples were incubated in refrigerators in range of 4C to 7C (thermostat was never adjusted). Higher reported temperatures were due to slight warming following removal from refrigerator before temperature was measured."
Note on BY33: Reviewer D.S. (2/1/00): Verified by Doug Abbey of Gannett Fleming 2/1/00.
Note on BY34: Reviewer D.S. (2/1/00): Verified by Doug Abbey of Gannett Fleming 2/1/00.
Note on CB5: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on CB30: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on CD5: Reviewer D.S. (10/12/99): Per Consultant: "Samples were incubated in refrigerators in range of 4C to 7C (thermostat was never adjusted). Higher reported temperatures were due to slight warming following removal from refrigerator before temperature was measured."
Note on CD30: Reviewer D.S. (10/12/99): Per Consultant: "Samples were incubated in refrigerators in range of 4C to 7C (thermostat was never adjusted). Higher reported temperatures were due to slight warming following removal from refrigerator before temperature was measured."
Note on CK39: Reviewer D.S. (10/12/99): Per Consultant: "CHBr3 results in cells CK37-8 as reported on laboratory analysis report."
Measured Depth = 8.7 cm
Measured Depth = 18.2 cm

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run |  |  |  | Platte River WTP - Summer Test |  |  | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 |  |  |  | Platte River WTP - Summer Test |  |  | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [6 empty] | Platte River WTP - Summer Test | [8 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [7 empty] | Platte River WTP - Summer Test | [9 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [5 empty] | Platte River WTP - Summer Test | [8 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [6 empty] | Platte River WTP - Summer Test | [11 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Metropolitan Utilities District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.4 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-07-30 | [5 empty] | 20-min. EBCT Start Date | 1998-07-30 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NE 3105507 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Lime Softening | 71.6 mg/l as CaO | Full-Scale | 10-min. EBCT Start Time | 8:00 | [5 empty] | 20-min. EBCT Start Time | 8:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Coagulation | 1.2 mg/l alum | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 15 | 6 | 3.35 | Flocculation | 1-stage | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-07-30 | 8:00 | 0 | 0 | 8.4 | 21 | 1.45 | 0.003 | 0.2069 | 1 | 0.63 | 0.37 | 24.5 | 8.5 | 5 | BMRL | 1.8 | 4.3 | 4.9 | 3.5 | 14.5 | NR | 5.8 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 5.8 | 5.8 | C1-20 | N | 1998-07-30 | 8:00 | 0 | 0 | 8.5 | 21 | 1.25 | 0.002 | 0.16 | 1 | 0.84 | 0.16 | 24 | 8.5 | 5 | BMRL | 3.5 | 7.5 | 6 | 3.3 | 20.3 | 2.2 | 6.6 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 8.8 | 8.8 | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Clarification | solids contact (225 minutes detention) | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-07-31 | 9:00 | 25 | 1110 | 8.4 | 21.9 | 1.15 | 0.006 | 0.52174 | 0.9 | 0.13 | 0.77 | 25.5 | 8.5 | 5 | BMRL | 2.3 | 2.6 | 5.1 | 5 | 15 | 2.6 | 2.1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 4.7 | 4.7 | Avg-C2-20 | Y | 1998-08-01 | 9:00 | 49 | 1087.8 | 8.3 | 25 | 1.05 | 0.005 | 0.47619 | 1 | 0.625 | 0.375 | 25 | 7.95 | 5 | BMRL | BMRL | 1.25 | 3.25 | 3.65 | 8.15 | BMRL | 1.75 | BMRL | BMRL | 1 | BMRL | NA | NA | NA | 2.75 | 2.75 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Dual media filtration | anthracite(dep=18"; 0.95 to 1.05 mm)/sand(dep=12"; 0.45 to 0.55 mm) | Full-Scale | Sampling date | MM/DD/YY | 1998-07-30 | 1998-08-10 | --- | --- |  | Sampling date | MM/DD/YY | 1998-07-30 | 1998-08-10 | --- | --- |  | Avg-C3-10 | Y | 1998-08-01 | 9:00 | 49 | 2175.6 | 8.2 | 25 | 1.6 | 0.0205 | 1.2812 | 1.25 | 0.78 | 0.47 | 25 | 8.3 | 5 | BMRL | 3.4 | 5.45 | 7.75 | 3.9 | 17.1 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C3-20 | N | 1998-08-03 | 9:00 | 97 | 2153.4 | 8.2 | 21.7 | 1.25 | 0.009 | 0.72 | 0.9 | 0.02 | 0.88 | 22.5 | 7.1 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 60 | 12 | 1.68 | Cartridge filtration | 5 um nominal size | Bench-Scale | Sampling time | hh:mm | 8:00 | 7:30 | --- | --- |  | Sampling time | hh:mm | 8:00 | 7:30 | --- | --- |  | C4-10 | N | 1998-08-02 | 9:00 | 73 | 3241.2 | 8.4 | 25 | 2.05 | 0.025 | 1.2195 | 1.2 | 0.12 | 1.08 | 25 | 7.3 | 5 | 50 | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Avg-C4-20 | Y | 1998-08-06 | 8:00 | 168 | 3729.6 | 8.2 | 21.7 | 1.6 | 0.019 | 1.1875 | 1.5 | 0.725 | 0.775 | 24.2 | 7.05 | 5 | 41.5 | 5.3 | 7.2 | 8.1 | 3.5 | 24.1 | BMRL | 2.4 | BMRL | BMRL | 1.2 | 1.1 | NA | NA | NA | 3.6 | 4.7 | Engineering Fee Factor (% of construction costs) | 8
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 | In-line filtration | 1 um to 2 um exclusion size | Bench-Scale | Operation time | hh.hh | 0 | 263.5 | --- | --- |  | Operation time | hh.hh | 0 | 263.5 | --- | --- |  | C5-10 | N | 1998-08-03 | 9:00 | 97 | 4306.8 | 8.2 | 21.8 | 2.15 | 0.03 | 1.3953 | 1.1 | 0.03 | 1.07 | 22.5 | 8.3 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C5-20 | N | 1998-08-07 | 10:00 | 194 | 4306.8 | 8.3 | 21.5 | 1.5 | 0.022 | 1.4667 | 1.52 | 0.02 | 1.5 | 22.2 | 7 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1999 ENR Construction Cost Index (CCI base year 1913) | 6039
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 11699.4 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 5849.7 | --- | --- |  | C6-10 | N | 1998-08-04 | 7:00 | 119 | 5283.6 | 8.1 | 21.7 | 2.2 | 0.031 | 1.4091 | 1.6 | 0.69 | 0.91 | 22.4 | 8.8 | 5 | 70.5 | 9.9 | 9.8 | 6.5 | 1.7 | 27.9 | BMRL | 4.6 | BMRL | BMRL | 1.1 | 1.2 | NA | NA | NA | 5.7 | 6.9 | C6-20 | N | 1998-08-09 | 10:00 | 242 | 5372.4 | 8.5 | 22 | 1.95 | 0.03 | 1.5385 | 1.8 | 0.05 | 1.75 | 22 | 8 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1999 Producers Price Index (PPI base year 1967 = 100) | 1947
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 120 | 124 | 122 | 3.2787 |  | Alkalinity | mg/L as CaCO3 | 120 | 124 | 122 | 3.2787 |  | Avg-C7-10 | Y | 1998-08-05 | 10:00 | 146 | 6482.4 | 8 | 21.7 | 2.45 | 0.037 | 1.5102 | 1.2 | 0.025 | 1.175 | 22.1 | 6.55 | 4.5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Avg-C7-20 | Y | 1998-08-11 | 8:00 | 288 | 6393.6 | 8.3 | 21.5 | 2.5 | 0.03 | 1.2 | 2 | 0.765 | 1.235 | 22.8 | 8.8 | 5 | 63 | 9.5 | 9.5 | 8.85 | 2.2 | 30.05 | 5.35 | 4.8 | BMRL | BMRL | 2.35 | 2.65 | NA | NA | NA | 12.5 | 15.15 | Labor Rate + Fringe ($/work-hour) | 26
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3162.0684 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 140 | 136 | 138 | 2.8986 |  | Total hardness | mg/L as CaCO3 | 140 | 136 | 138 | 2.8986 |  | C8-10 | N | 1998-08-06 | 8:00 | 168 | 7459.2 | 8.1 | 21.8 | 2.65 | 0.045 | 1.6981 | 1.8 | 0.46 | 1.34 | 23.2 | 7.2 | 5 | NA | 17 | 13 | 8.1 | 1.1 | 39.2 | BMRL | 5 | BMRL | BMRL | 1.1 | 2 | NA | NA | NA | 6.1 | 8.1 | C8-20 | N | 1998-08-12 | 9:30 | 313.5 | 6959.7 | 7.5 | 25 | 2.45 | 0.034 | 1.3878 | 1.8 | 0.07 | 1.73 | 25 | 8.6 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 6324.1367 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 92 | 94 | 93 | 2.1505 |  | Calcium hardness | mg/L as CaCO3 | 92 | 94 | 93 | 2.1505 |  | C9-10 | N | 1998-08-07 | 10:00 | 194 | 8613.6 | 8.1 | 21.8 | 2.4 | 0.047 | 1.9583 | 1.9 | 0.05 | 1.85 | 22.5 | 8.7 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C9-20 | N | 1998-08-14 | 8:00 | 360 | 7992 | 7.4 | 21.7 | 3.2 | 0.036 | 1.125 | 1.8 | 0.94 | 0.86 | 25 | 8.6 | 5 | 62.5 | 9.6 | 11 | 10 | 2.7 | 33.3 | 4.1 | 4.4 | BMRL | BMRL | 2.5 | 3.1 | NA | NA | NA | 11 | 14.1 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 8221.3777 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.1 | BMRL | 0.1 | #VALUE! |  | Ammonia | mg NH3-N / L | 0.1 | BMRL | 0.1 | #VALUE! |  | C10-10 | N | 1998-08-08 | 9:00 | 217 | 9634.8 | 8.2 | 22.3 | 2.5 | 0.05 | 2 | 2.3 | 0.05 | 2.25 | 25.5 | 8.1 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C10-20 | N | 1998-08-15 | 9:00 | 385 | 8547 | 7.3 | 25 | 3.25 | 0.039 | 1.2 | 1.8 | 0.65 | 1.15 | 25 | 8.4 | 5 | 58 | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Fuel Oil Rate ($/gal) | 0.5
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 56 | 49 | 52.5 | 13.3333 |  | Bromide | mg/L | 56 | 49 | 52.5 | 13.3333 |  | C11-10 | N | 1998-08-09 | 10:00 | 242 | 10744.8 | 8.2 | 22 | 2.5 | 0.052 | 2.08 | 2.3 | 1.46 | 0.84 | 22 | 8 | 5 | 94 | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C11-20 | N | 1998-08-16 | 9:30 | 409.5 | 9090.9 | 7.4 | 25 | 4.5 | 0.036 | 0.8 | 2 | 0.09 | 1.91 | 25 | 7.9 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Natural Gas Rate ($/ft3) | 3.5
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | Avg-C12-10 | Y | 1998-08-11 | 8:00 | 288 | 12787.2 | 8.2 | 21.75 | 2.6 | 0.0545 | 2.0962 | 2 | 1.02 | 0.98 | 22.75 | 8.95 | 5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C12-20 | N | 1998-08-17 | 9:30 | 433.5 | 9623.7 | 7.7 | 21.5 | NR | 0.037 | #VALUE! | 2.3 | 0.75 | 1.55 | 21.7 | 8.4 | 5 | 62 | 8.9 | 9.9 | 8.7 | 1.9 | 29.4 | 2.3 | 3.4 | 1.1 | BMRL | 1.2 | 1.3 | NA | NA | NA | 8 | 9.3 | Current Process Water Rate ($/1000 gal) | 0.3
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1625e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -864152 | -38368348.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864152 | -19184174.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.2 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  |  |  |  | -864152 | -38368348.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864152 | -19184174.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 7.4 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-07-30 | 1998-08-07 | 1998-08-10 | --- | --- | Sampling date | MM/DD/YY | 1998-07-30 | 1998-08-07 | 1998-08-10 | --- | --- |  |  |  |  | -864152 | -38368348.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864152 | -19184174.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Platte River Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 4.7081 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 8:00 | 10:30 | 7:30 | --- | --- | Sampling time | hh:mm | 8:00 | 10:30 | 7:30 | --- | --- |  |  |  |  | -864152 | -38368348.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864152 | -19184174.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | STS |  |  | RSSCT flow rate, QSC (mL/min) | 7.4572 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 194.5 | 263.5 | --- | --- | Operation time | hh.hh | 0 | 194.5 | 263.5 | --- | --- |  |  |  |  | -864152 | -38368348.8 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -864152 | -19184174.4 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | SplitTrt/Softening |  |  | Estimated total influent volume required, VSCT (L) | 248.5466 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 8635.8 | 11699.4 | --- | --- | Bed volumes | (20 minute) | 0 | 4317.9 | 5849.7 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 454 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 9 | 8.3 | 8.5 | 8.6 | 4.1925 | pH | --- | 9 | 8.3 | 8.5 | 8.6 | 4.1925 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | 28507002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.4 | 0.2 | 0.2 | 0.26667 | 43.3013 | Turbidity | ntu | 0.4 | 0.2 | 0.2 | 0.26667 | 43.3013 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 22 | 22.6 | 22.7 | 22.4333 | 1.6876 | Temperature | oC | 22 | 22.6 | 22.7 | 22.4333 | 1.6876
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 57.0929 | [5 empty] | Total organic carbon | mg/L | 4.45 | 3.7 | 3.2 | 3.7833 | 16.6296 | Total organic carbon | mg/L | 4.45 | 3.7 | 3.2 | 3.7833 | 16.6296 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3514 | [5 empty] | UV254 | cm-1 | 0.079 | 0.074 | 0.074 | 0.075667 | 3.8151 | UV254 | cm-1 | 0.079 | 0.074 | 0.074 | 0.075667 | 3.8151 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 7.7153 | [5 empty] | SUVA | L/(mg*m) | 1.7753 | 2 | 2.3125 | 2.0293 | 13.2956 | SUVA | L/(mg*m) | 1.7753 | 2 | 2.3125 | 2.0293 | 13.2956 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.6039 | [5 empty] | SDS-Cl2 dose | mg/L | 1.8 | 1.8 | 2 | 1.8667 | 6.1859 | SDS-Cl2 dose | mg/L | 1.8 | 1.8 | 2 | 1.8667 | 6.1859 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 82.8489 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.46 | 0.04 | 0.7 | 0.4 | 83.5165 | SDS-Free Cl2 residual | mg/L | 0.46 | 0.04 | 0.7 | 0.4 | 83.5165 | C3-10A | Primary | 1998-08-01 | 9:00 | 49 | 2175.6 | 8.2 | 25 | 1.6 | 0.021 | 1.3125 | 1 | 0.54 | 0.46 | 25 | 8.3 | 5 | BMRL | 2.9 | 4.7 | 7.5 | 4.1 | 19.2 | 2.9 | 1.3 | BMRL | BMRL | 2.7 | 1.8 | NA | NA | NA | 6.9 | 8.7 | C2-20A | Primary | 1998-08-01 | 9:00 | 49 | 1087.8 | 8.3 | 25 | 1.1 | 0.005 | 0.45455 | 0.8 | 0.37 | 0.43 | 25 | 8.2 | 5 | BMRL | BMRL | 1.1 | 3.2 | 4.1 | 8.4 | BMRL | 1.3 | BMRL | BMRL | 1 | BMRL | NA | NA | NA | 2.3 | 2.3
|  |  |  | Mass GAC required, mSC (g) | 5.0386 | [5 empty] | SDS-Cl2 demand | mg/L | 1.34 | 1.76 | 1.3 | 1.4667 | 17.3741 | SDS-Cl2 demand | mg/L | 1.34 | 1.76 | 1.3 | 1.4667 | 17.3741 | C3-10B | Duplicate | 1998-08-01 | 9:00 | 49 | 2175.6 | 8.2 | 25 | 1.6 | 0.02 | 1.25 | 1.5 | 1.02 | 0.48 | 25 | 8.3 | 5 | BMRL | 3.9 | 6.2 | 8 | 3.7 | 21.8 | BMRL | 2.3 | 4.3 | BMRL | 1.9 | 1.8 | NA | NA | NA | 8.5 | 10.3 | C2-20B | Duplicate | 1998-08-01 | 9:00 | 49 | 1087.8 | 8.3 | 25 | 1 | 0.005 | 0.5 | 1.2 | 0.88 | 0.32 | 25 | 7.7 | 5 | BMRL | BMRL | 1.4 | 3.3 | 3.2 | 7.9 | NR | 2.2 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 2.2 | 2.2
[11 empty] | SDS-Chlorination temp. | oC | 22.2 | 22 | 22 | 22.0667 | 0.52328 | SDS-Chlorination temp. | oC | 22.2 | 22 | 22 | 22.0667 | 0.52328 | Avg-C3-10 | Average | --- | --- | --- | --- | 8.2 | 25 | 1.6 | 0.0205 | 1.2812 | 1.25 | 0.78 | 0.47 | 25 | 8.3 | 5 | #DIV/0! | 3.4 | 5.45 | 7.75 | 3.9 | 20.5 | 2.9 | 1.8 | 4.3 | #DIV/0! | 2.3 | 1.8 | #DIV/0! | #DIV/0! | #DIV/0! | 7.7 | 9.5 | Avg-C2-20 | Average | --- | --- | --- | --- | 8.3 | 25 | 1.05 | 0.005 | 0.47727 | 1 | 0.625 | 0.375 | 25 | 7.95 | 5 | #DIV/0! | #DIV/0! | 1.25 | 3.25 | 3.65 | 8.15 | #DIV/0! | 1.75 | #DIV/0! | #DIV/0! | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2.25 | 2.25
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.3 | 7.1 | 8.8 | 8.0667 | 10.8309 | SDS-Chlorination pH | --- | 8.3 | 7.1 | 8.8 | 8.0667 | 10.8309 | RPD-C3-10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 4.878 | 4.878 | 40 | 61.5385 | 4.2553 | 0 | 0 | 0 | #VALUE! | 29.4118 | 27.5229 | 6.4516 | 10.2564 | 12.6829 | #VALUE! | 55.5556 | #VALUE! | #VALUE! | 34.7826 | 0 | #VALUE! | #VALUE! | #VALUE! | 20.7792 | 16.8421 | RPD-C2-20 | RPD | --- | --- | --- | --- | 0 | 0 | 9.5238 | 0 | 9.5238 | 40 | 81.6 | 29.3333 | 0 | 6.2893 | 0 | #VALUE! | #VALUE! | 24 | 3.0769 | 24.6575 | 6.135 | #VALUE! | 51.4286 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 4.4444 | 4.4444
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 5 | 5 | 5 | 5 | 0 | SDS-Incubation time | hours | 5 | 5 | 5 | 5 | 0 | C7-10A | Primary | 1998-08-05 | 10:00 | 146 | 6482.4 | 8 | 21.7 | 2.4 | 0.036 | 1.5 | 1.2 | 0.02 | 1.18 | 22.1 | 6.5 | 4.5 | 46.5 | 5.8 | 3.4 | 3.1 | BMRL | 12.3 | BMRL | 1.6 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.6 | 1.6 | C4-20A | Primary | 1998-08-06 | 8:00 | 168 | 3729.6 | 8.2 | 21.7 | 1.6 | 0.019 | 1.1875 | 1.5 | 0.68 | 0.82 | 24.3 | 7.1 | 5 | 41 | 5 | 6.7 | 7.7 | 3.4 | 22.8 | BMRL | 2.4 | BMRL | BMRL | 1.2 | 1.1 | NA | NA | NA | 3.6 | 4.7
|  |  |  | Estimated full-scale run time, tLCT (days) | 114.1858 | [5 empty] | SDS-TOX | mg Cl- /L | 138 | NA | 132 | 135 | 3.1427 | SDS-TOX | mg Cl- /L | 138 | NR | 132 | 135 | 3.1427 | C7-10B | Duplicate | 1998-08-05 | 10:00 | 146 | 6482.4 | 8 | 21.7 | 2.5 | 0.038 | 1.52 | 1.2 | 0.03 | 1.17 | 22.1 | 6.6 | 4.5 | 51 | 8.2 | 8.6 | 6.4 | 2 | 25.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C4-20B | Duplicate | 1998-08-06 | 8:00 | 168 | 3729.6 | 8.2 | 21.7 | 1.6 | 0.019 | 1.1875 | 1.5 | 0.77 | 0.73 | 24.2 | 7 | 5 | 42 | 5.6 | 7.7 | 8.5 | 3.6 | 25.4 | BMRL | 2.4 | BMRL | BMRL | 1.2 | 1.1 | NA | NA | NA | 3.6 | 4.7
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.7027 | [5 empty] | SDS-CHCl3 | mg/L | 28 | NR | 24 | 26 | 10.8786 | SDS-CHCl3 | mg/L | 28 | NR | 24 | 26 | 10.8786 | Avg-C7-10 | Average | --- | --- | --- | --- | 8 | 21.7 | 2.45 | 0.037 | 1.51 | 1.2 | 0.025 | 1.175 | 22.1 | 6.55 | 4.5 | 48.75 | 7 | 6 | 4.75 | 2 | 18.75 | #DIV/0! | 1.6 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.8 | 0.8 | Avg-C4-20 | Average | --- | --- | --- | --- | 8.2 | 21.7 | 1.6 | 0.019 | 1.1875 | 1.5 | 0.725 | 0.775 | 24.25 | 7.05 | 5 | 41.5 | 5.3 | 7.2 | 8.1 | 3.5 | 24.1 | #DIV/0! | 2.4 | #DIV/0! | #DIV/0! | 1.2 | 1.1 | #DIV/0! | #DIV/0! | #DIV/0! | 3.6 | 4.7
|  |  |  | Estimated RSSCT run time, tSCT (days) | 15.4305 | [5 empty] | SDS-BDCM | mg/L | 16 | NR | 14 | 15 | 9.4281 | SDS-BDCM | mg/L | 16 | NR | 14 | 15 | 9.4281 | RPD-C7-10 | RPD | --- | --- | --- | --- | 0 | 0 | 4.0816 | 5.4054 | 1.3245 | 0 | 40 | 0.85106 | 0 | 1.5267 | 0 | 9.2308 | 34.2857 | 86.6667 | 69.4737 | #VALUE! | 68.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | 200 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 12.4138 | 11.6129 | 0.41237 | 1.4184 | 0 | 2.4096 | 11.3208 | 13.8889 | 9.8765 | 5.7143 | 10.7884 | #VALUE! | 0 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 0
|  |  |  | RSSCT bed length, lSC (cm) | 21.2079 | [5 empty] | SDS-DBCM | mg/L | 7.1 | NR | 5.5 | 6.3 | 17.9583 | SDS-DBCM | mg/L | 7.1 | NR | 5.5 | 6.3 | 17.9583 | C12-10A | Primary | 1998-08-11 | 8:00 | 288 | 12787.2 | 8.1 | 21.8 | 2.6 | 0.054 | 2.0769 | 2 | 0.94 | 1.06 | 23.2 | 8.9 | 5 | 96 | 17 | 12 | 8 | 1.4 | 38.4 | 3.4 | 7.4 | 2.9 | BMRL | 1.8 | 3.5 | NA | NA | NA | 15.5 | 19 | C7-20A | Primary | 1998-08-11 | 8:00 | 288 | 6393.6 | 8.3 | 21.5 | 2.5 | 0.03 | 1.2 | 2 | 0.86 | 1.14 | 23 | 8.8 | 5 | 65 | 9.9 | 9.7 | 8.7 | 2 | 30.3 | 5.5 | 5.1 | BMRL | BMRL | 2.3 | 2.7 | NA | NA | NA | 12.9 | 15.6
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 165.6977 | [5 empty] | SDS-CHBr3 | mg/L | 1.3 | NR | BMRL | 1.3 | #DIV/0! | SDS-CHBr3 | mg/L | 1.3 | NR | BMRL | 1.3 | #DIV/0! | C12-10B | Duplicate | 1998-08-11 | 8:00 | 288 | 12787.2 | 8.3 | 21.7 | 2.6 | 0.055 | 2.1154 | 2 | 1.1 | 0.9 | 22.3 | 9 | 5 | 95 | 16 | 12 | 8 | 1.4 | 37.4 | 4 | 6.7 | 2.4 | BMRL | 1.6 | 3.1 | NA | NA | NA | 14.7 | 17.8 | C7-20B | Duplicate | 1998-08-11 | 8:00 | 288 | 6393.6 | 8.4 | 21.4 | 2.5 | 0.03 | 1.2 | 2 | 0.67 | 1.33 | 22.6 | 8.8 | 5 | 61 | 9.1 | 9.3 | 9 | 2.4 | 29.8 | 5.2 | 4.5 | BMRL | BMRL | 2.4 | 2.6 | NA | NA | NA | 12.1 | 14.7
|  |  |  | Mass GAC required, mSC (g) | 10.0772 | [5 empty] | SDS-THM4 | mg/L | 52.4 | NR | 43.5 | 47.95 | 13.1246 | SDS-THM4 | mg/L | 52.4 | NR | 43.5 | 47.95 | 13.1246 | Avg-C12-10 | Average | --- | --- | --- | --- | 8.2 | 21.75 | 2.6 | 0.0545 | 2.0962 | 2 | 1.02 | 0.98 | 22.75 | 8.95 | 5 | 95.5 | 16.5 | 12 | 8 | 1.4 | 37.9 | 3.7 | 7.05 | 2.65 | #DIV/0! | 1.7 | 3.3 | #DIV/0! | #DIV/0! | #DIV/0! | 15.1 | 18.4 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.35 | 21.45 | 2.5 | 0.03 | 1.2 | 2 | 0.765 | 1.235 | 22.8 | 8.8 | 5 | 63 | 9.5 | 9.5 | 8.85 | 2.2 | 30.05 | 5.35 | 4.8 | #DIV/0! | #DIV/0! | 2.35 | 2.65 | #DIV/0! | #DIV/0! | #DIV/0! | 12.5 | 15.15
[11 empty] | SDS-MCAA* | mg/L | 3.9 | NR | 4.1 | 4 | 3.5355 | SDS-MCAA* | mg/L | 3.9 | NR | 4.1 | 4 | 3.5355 | RPD-C12-10 | RPD | --- | --- | --- | --- | 2.439 | 0.45977 | 0 | 1.8349 | 1.8349 | 0 | 15.6863 | 16.3265 | 3.956 | 1.1173 | 0 | 1.0471 | 6.0606 | 0 | 0 | 0 | 2.6385 | 16.2162 | 9.9291 | 18.8679 | #VALUE! | 11.7647 | 12.1212 | #VALUE! | #VALUE! | #VALUE! | 5.298 | 6.5217 | RPD-C7-20 | RPD | --- | --- | --- | --- | 1.1976 | 0.4662 | 0 | 0 | 0 | 0 | 24.8366 | 15.3846 | 1.7544 | 0 | 0 | 6.3492 | 8.4211 | 4.2105 | 3.3898 | 18.1818 | 1.6639 | 5.6075 | 12.5 | #VALUE! | #VALUE! | 4.2553 | 3.7736 | #VALUE! | #VALUE! | #VALUE! | 6.4 | 5.9406
[11 empty] | SDS-DCAA* | mg/L | 7.8 | NR | 8.2 | 8 | 3.5355 | SDS-DCAA* | mg/L | 7.8 | NR | 8.2 | 8 | 3.5355 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 1.5 | NR | 3.6 | 2.55 | 58.2323 | SDS-TCAA* | mg/L | 1.5 | NR | 3.6 | 2.55 | 58.2323 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | NR | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | NR | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | BMRL | NR | 1.4 | 1.4 | #DIV/0! | SDS-DBAA* | mg/L | BMRL | NR | 1.4 | 1.4 | #DIV/0!
[11 empty] | SDS-BCAA* | mg/L | 1.4 | NR | 3.6 | 2.5 | 62.2254 | SDS-BCAA* | mg/L | 1.4 | NR | 3.6 | 2.5 | 62.2254
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 13.2 | NR | 17.3 | 15.25 | 19.0107 | SDS-HAA5 | mg/L | 13.2 | NR | 17.3 | 15.25 | 19.0107
[11 empty] | SDS-HAA6 | mg/L | 14.6 | NR | 20.9 | 17.75 | 25.0973 | SDS-HAA6 | mg/L | 14.6 | NR | 20.9 | 17.75 | 25.0973
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on Q33: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on Q35: Reviewer D.S. (10/12/99): Per Consultant: "Variation from SDS target temperature due to not having access to warm water incubation (warm water SDS samples stored at room temperature)."
Note on Y33: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on Y35: Reviewer D.S. (10/12/99): Per Consultant: "Variation from SDS target temperature due to not having access to warm water incubation (warm water SDS samples stored at room temperature)."
Note on AR33: Reviewer M.H. (12/13/99): Using two different chlorine dosages for the duplicate samples was due to a misunderstanding of the ICR Treatmnet Study procedures.
Note on AR34: Reviewer M.H. (12/13/99): Using two different chlorine dosages for the duplicate samples was due to a misunderstanding of the ICR Treatmnet Study procedures.
Note on AS5: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on AS30: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on AU5: Reviewer D.S. (10/12/99): Per Consultant: "Variation from SDS target temperature due to not having access to warm water incubation (warm water SDS samples stored at room temperature)."
Note on AU30: Reviewer D.S. (10/12/99): Per Consultant: "Variation from SDS target temperature due to not having access to warm water incubation (warm water SDS samples stored at room temperature)."
Note on CA33: Reviewer M.H. (12/13/99): Using two different chlorine dosages for the duplicate samples was due to a misunderstanding of the ICR Treatmnet Study procedures.
Note on CA34: Reviewer M.H. (12/13/99): Using two different chlorine dosages for the duplicate samples was due to a misunderstanding of the ICR Treatmnet Study procedures.
Note on CB5: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on CB30: Reviewer D.S. (10/12/99): Per Consultant: "Chlorine demand tests were conducted prior to actual SDS test to determine chlorine dose required for target residual. Results from demand tests were often not accurate predictors for determining SDS chlorine doses that would result in target chlorine residual."
Note on CD5: Reviewer D.S. (10/12/99): Per Consultant: "Variation from SDS target temperature due to not having access to warm water incubation (warm water SDS samples stored at room temperature)."
Note on CD30: Reviewer D.S. (10/12/99): Per Consultant: "Variation from SDS target temperature due to not having access to warm water incubation (warm water SDS samples stored at room temperature)."
Note on CN39: Reviewer D.S. (10/12/99): Per Consultant: "HAA results are as reported on laboratory analysis report."
Note on CQ39: Reviewer D.S. (10/12/99): Per Consultant: "HAA results are as reported on laboratory analysis report."
Note on CR39: Reviewer D.S. (10/12/99): Per Consultant: "HAA results are as reported on laboratory analysis report."
Measured Depth + 10 cm
Measured Depth = 20 cm

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [7 empty] | Platte River WTP - Fall Test | [7 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [7 empty] | Platte River WTP - Fall Test | [6 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Metropolitan Utilities District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 3 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-11-27 |  | Platte River WTP - Autumn Test |  |  |  | 20-min. EBCT Start Date | 1998-11-27 |  | Platte River WTP - Autumn Test |  |  |  | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NE 3105507 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Lime softening | 60.2 mg/l as CaO | Full-Scale | 10-min. EBCT Start Time | 16:30 | [5 empty] | 20-min. EBCT Start Time | 16:30 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Coagulation | 1.2 mg/l alum | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 15 | 6 | 3.35 | Flocculation | 1-stage | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-11-27 | 18:00 | 1.5 | 66.6 | 8.7 | 19.4 | 1.3 | 0.003 | 0.23077 | 1 | 0.49 | 0.51 | 14.8 | 8.8 | 11.5 | BMRL | BMRL | 1.6 | 2.8 | 3.9 | 8.3 | BMRL | 3.5 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3.5 | 3.5 | C1-20 | N | 1998-11-27 | 18:00 | 1.5 | 33.3 | 8.7 | 19.8 | 1.6 | 0.003 | 0.1875 | 0.8 | 0.33 | 0.47 | 14.5 | 8.9 | 11.5 | BMRL | 1.2 | 2.1 | 2.3 | 2.8 | 8.4 | BMRL | 3.9 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3.9 | 3.9 | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Clarification | solids contact (340 minutes detention time) | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-11-28 | 8:00 | 15.5 | 688.2 | 8.6 | 20.2 | 1.05 | 0.005 | 0.47619 | 1 | 0.71 | 0.29 | 15.9 | 8.8 | 11.75 | BMRL | BMRL | BMRL | 1.8 | 3.3 | 5.1 | BMRL | 1.5 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.5 | 1.5 | C2-20 | N | 1998-11-28 | 8:00 | 15.5 | 344.1 | 8.6 | 20.4 | 0.5 | 0.004 | 0.8 | 0.8 | 0.67 | 0.13 | 17.1 | 8.7 | 11.75 | BMRL | BMRL | BMRL | 1.4 | 2.4 | 3.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Dual media filtration | anthracite(dep=18"; 0.95 to 1.05 mm)/sand(dep=12"; 0.45 to 0.55 mm) | Full-Scale | Sampling date | MM/DD/YY | 1998-11-27 | 1998-12-11 | --- | --- |  | Sampling date | MM/DD/YY | 1998-11-27 | 1998-12-11 | --- | --- |  | C3-10 | N | 1998-11-28 | 20:00 | 27.5 | 1221 | 8.3 | 20.6 | 1.1 | BMRL | #VALUE! | 0.9 | 0.42 | 0.48 | 18.7 | 8.9 | 11.75 | BMRL | BMRL | 1.1 | 2.8 | 6 | 9.9 | BMRL | 2 | BMRL | BMRL | 1 | BMRL | NA | NA | NA | 3 | 3 | Avg-C3-20 | Y | 1998-11-30 | 8:00 | 63.5 | 1409.7 | 8.3 | 20.8 | 0.6 | 0.01 | 1.6667 | 0.9 | 0.59 | 0.31 | 15.7 | 8.9 | 11.5 | BMRL | BMRL | BMRL | 2.3 | 4.9 | 7.2 | BMRL | 3.1 | BMRL | BMRL | 1.15 | BMRL | NA | NA | NA | 4.25 | 4.25 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 60 | 12 | 1.68 | Cartridge filtration | 5 um nominal size | Bench-Scale | Sampling time | hh:mm | 16:30 | 8:00 | --- | --- |  | Sampling time | hh:mm | 16:30 | 8:00 | --- | --- |  | C4-10 | N | 1998-11-29 | 8:00 | 39.5 | 1753.8 | 8.5 | 20.4 | 0.9 | 0.012 | 1.3333 | 1 | 0.75 | 0.25 | 18.6 | 8.9 | 11.75 | BMRL | BMRL | 1.1 | 3.2 | 6.4 | 10.7 | BMRL | 2.1 | BMRL | BMRL | 1.1 | BMRL | NA | NA | NA | 3.2 | 3.2 | C4-20 | N | 1998-12-02 | 8:00 | 111.5 | 2475.3 | 8.6 | 20.1 | 1 | 0.016 | 1.6 | 1 | 0.52 | 0.48 | 16.9 | 8.9 | 11.5 | BMRL | BMRL | 1.7 | 4.6 | 7.2 | 13.5 | BMRL | 3.6 | BMRL | BMRL | 1.3 | BMRL | NA | NA | NA | 4.9 | 4.9 | Engineering Fee Factor (% of construction costs) | 8
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 | In-line filtration | 1 um to 2 um exclusion size | Bench-Scale | Operation time | hh.hh | 0 | 327.5 | --- | --- |  | Operation time | hh.hh | 0 | 327.5 | --- | --- |  | Avg-C5-10 | Y | 1998-11-30 | 8:00 | 63.5 | 2819.4 | 8.3 | 20.8 | 1.2 | 0.018 | 1.5 | 1 | 0.445 | 0.555 | 15.4 | 8.8 | 11.5 | 26 | BMRL | 2.65 | 6.05 | 7.55 | 16.25 | BMRL | 2.7 | BMRL | BMRL | 1.3 | BMRL | NA | NA | NA | 4 | 4 | C5-20 | N | 1998-12-04 | 8:00 | 159.5 | 3540.9 | 8.7 | 20.5 | 1.2 | 0.013 | 1.0833 | 1.1 | 0.68 | 0.42 | 14.5 | 9 | 11.75 | BMRL | BMRL | 2.3 | 6.1 | 7.6 | 16 | BMRL | 3 | BMRL | BMRL | 1.6 | BMRL | NA | NA | NA | 4.6 | 4.6 | 1999 ENR Construction Cost Index (CCI base year 1913) | 6039
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 14541 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 14541 | --- | --- |  | C6-10 | N | 1998-12-01 | 7:00 | 86.5 | 3840.6 | 8.9 | 20.3 | 1.55 | 0.024 | 1.5484 | 1.1 | 0.61 | 0.49 | 17.1 | 8.9 | 11.75 | 38 | 1.6 | 3.8 | 8.7 | 8.5 | 22.6 | BMRL | 2.6 | BMRL | BMRL | 1.8 | 1.2 | NA | NA | NA | 4.4 | 5.6 | C6-20 | N | 1998-12-07 | 8:30 | 232 | 5150.4 | 8.8 | 20.4 | 1.45 | 0.016 | 1.1034 | 1.1 | 0.62 | 0.48 | 17 | 8.7 | 11.5 | 34 | 1.8 | 3.6 | 8.3 | 8.1 | 21.8 | BMRL | 3.9 | BMRL | BMRL | 1.5 | 1.1 | NA | NA | NA | 5.4 | 6.5 | 1999 Producers Price Index (PPI base year 1967 = 100) | 1947
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 130 | 149 | 139.5 | 13.6201 |  | Alkalinity | mg/L as CaCO3 | 130 | 149 | 139.5 | 13.6201 |  | C7-10 | N | 1998-12-02 | 8:00 | 111.5 | 4950.6 | 8.7 | 20.5 | 1.65 | 0.027 | 1.6364 | 1.2 | 0.51 | 0.69 | 17.2 | 8.9 | 11.5 | 32.5 | 3.4 | 6 | 8.8 | 7 | 25.2 | BMRL | 3.7 | BMRL | BMRL | 1.8 | 1.3 | NA | NA | NA | 5.5 | 6.8 | Avg-C7-20 | Y | 1998-12-09 | 9:00 | 280.5 | 6227.1 | 8.8 | 20.8 | 1.6 | 0.02 | 1.25 | 1.1 | 0.49 | 0.61 | 13.3 | 8.8 | 11.4 | 38.5 | 2.55 | 4.6 | 8.55 | 7.8 | 23.5 | BMRL | 3.3 | BMRL | BMRL | 2.1 | 1.25 | NA | NA | NA | 5.4 | 6.65 | Labor Rate + Fringe ($/work-hour) | 26
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5202.3804 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 150 | 164 | 157 | 8.9172 |  | Total hardness | mg/L as CaCO3 | 150 | 164 | 157 | 8.9172 |  | C8-10 | N | 1998-12-03 | 8:00 | 135.5 | 6016.2 | 8.8 | 20.5 | 1.7 | 0.029 | 1.7059 | 1.2 | 0.5 | 0.7 | 14.6 | 9 | 10.5 | 49 | 3.5 | 5.8 | 9.1 | 6.1 | 24.5 | BMRL | 4.2 | BMRL | BMRL | 2.3 | 1.5 | NA | NA | NA | 6.5 | 8 | C8-20 | N | 1998-12-11 | 8:00 | 327.5 | 7270.5 | 8.9 | 20.1 | 1.35 | 0.02 | 1.4815 | 1.2 | 0.45 | 0.75 | 17.2 | 9 | 11.75 | 44.5 | 3.6 | 6.8 | 11 | 7.4 | 28.8 | BMRL | 3.4 | 1.2 | BMRL | 2.2 | 2.7 | NA | NA | NA | 6.8 | 9.5 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 10404.7608 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 98 | 106 | 102 | 7.8431 |  | Calcium hardness | mg/L as CaCO3 | 98 | 106 | 102 | 7.8431 |  | Avg-C9-10 | Y | 1998-12-04 | 8:00 | 159.5 | 7081.8 | 8.7 | 20.7 | 2.1 | 0.031 | 1.4762 | 1.3 | 0.49 | 0.81 | 16.7 | 8.95 | 11.75 | 55.05 | 5.35 | 8.45 | 9.2 | 5.75 | 28.75 | BMRL | 4.35 | BMRL | BMRL | 1.9 | 1.6 | NA | NA | NA | 6.25 | 7.85 | C9-20 | N | 1998-12-14 | 7:00 | 398.5 | 8846.7 | 8.8 | 19.9 | 1.45 | 0.027 | 1.8621 | 1.4 | 0.73 | 0.67 | 14.7 | 9.1 | 12 | 46 | 2.6 | 5.9 | 8.6 | 6.6 | 23.7 | BMRL | 4.3 | 2 | BMRL | 2.6 | 3.2 | NA | NA | NA | 8.9 | 12.1 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 13526.189 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-12-06 | 10:00 | 209.5 | 9301.8 | 8.8 | 20 | 2.2 | 0.029 | 1.3182 | 1.4 | 0.66 | 0.74 | 15.5 | 8.8 | 11.75 | 52 | 4.9 | 6.6 | 7.6 | 5.1 | 24.2 | 2.3 | 4.4 | 1.1 | BMRL | 1.8 | 1.6 | NA | NA | NA | 9.6 | 11.2 | C10-20 | N | 1998-12-17 | 8:00 | 471.5 | 10467.3 | 8.6 | 20.2 | 1.45 | 0.025 | 1.7241 | 1.3 | 0.1 | 1.2 | 13.5 | 8.6 | 12.5 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Fuel Oil Rate ($/gal) | 0.5
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 46 | 59 | 52.5 | 24.7619 |  | Bromide | mg/L | 46 | 59 | 52.5 | 24.7619 |  | Avg-C11-10 | Y | 1998-12-09 | 9:00 | 280.5 | 12454.2 | 8.9 | 20.8 | 2.25 | 0.0275 | 1.2222 | 1.4 | 0.4 | 1 | 13.2 | 8.7 | 11.1 | 66.25 | 8.1 | 10.5 | 11 | 5.1 | 34.7 | BMRL | 5.4 | 1.2 | BMRL | 1.75 | 1.8 | NA | NA | NA | 8.35 | 10.15 | C11-20 | N | 1998-12-28 | 8:30 | 736 | 16339.2 | 8.7 | 19.7 | 1.85 | 0.031 | 1.6757 | 1.6 | 0.55 | 1.05 | 16.9 | 8.9 | 11.5 | 65.5 | 8.4 | 10 | 11 | 6.4 | 35.8 | BMRL | 5.6 | 1.4 | BMRL | 2 | 1.2 | NA | NA | NA | 9 | 10.2 | Natural Gas Rate ($/ft3) | 3.5
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-12-11 | 8:00 | 327.5 | 14541 | 8.9 | 20.2 | 1.75 | 0.034 | 1.9429 | 1.6 | 0.77 | 0.83 | 16.9 | 9.1 | 11.75 | 68 | 9.4 | 11 | 12 | 4.9 | 37.3 | BMRL | 5.6 | 2.7 | BMRL | 2.1 | 4.4 | NA | NA | NA | 10.4 | 14.8 | C12-20 | N | 1999-01-02 | 9:00 | 856.5 | 19014.3 | 8.7 | 16.8 | 2.4 | 0.033 | 1.375 | 1.6 | 0.62 | 0.98 | 13.4 | 8.8 | 11.5 | 71.5 | 6.9 | 10 | 10 | 5.7 | 32.6 | BMRL | 5.3 | 2.1 | BMRL | 1.7 | 1.1 | NA | NA | NA | 9.1 | 10.2 | Current Process Water Rate ($/1000 gal) | 0.3
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1625e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -867040.5 | -38496598.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867040.5 | -19248299.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.2 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  |  |  |  | -867040.5 | -38496598.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867040.5 | -19248299.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 7.4 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-11-27 | 1998-12-04 | 1998-12-11 | --- | --- | Sampling date | MM/DD/YY | 1998-11-27 | 1998-12-04 | 1998-12-11 | --- | --- |  |  |  |  | -867040.5 | -38496598.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867040.5 | -19248299.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Platte River Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 4.7081 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:30 | 8:00 | 8:00 | --- | --- | Sampling time | hh:mm | 16:30 | 8:00 | 8:00 | --- | --- |  |  |  |  | -867040.5 | -38496598.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867040.5 | -19248299.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | STS |  |  | RSSCT flow rate, QSC (mL/min) | 7.4572 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 159.5 | 327.5 | --- | --- | Operation time | hh.hh | 0 | 159.5 | 327.5 | --- | --- |  |  |  |  | -867040.5 | -38496598.2 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867040.5 | -19248299.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | SplitTrt/Softening |  |  | Estimated total influent volume required, VSCT (L) | 408.9203 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 7081.8 | 14541 | --- | --- | Bed volumes | (20 minute) | 0 | 3540.9 | 7270.5 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 454 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.6 | 8.7 | 8.9 | 8.7333 | 1.7491 | pH | --- | 8.6 | 8.7 | 8.9 | 8.7333 | 1.7491 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | 28507002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.2 | 0.2 | 0.1 | 0.16667 | 34.641 | Turbidity | ntu | 0.2 | 0.2 | 0.1 | 0.16667 | 34.641 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 20.4 | 20.7 | 20.3 | 20.4667 | 1.0171 | Temperature | oC | 20.4 | 20.7 | 20.3 | 20.4667 | 1.0171
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 93.9319 | [5 empty] | Total organic carbon | mg/L | 3.1 | 3.45 | 2.4 | 2.9833 | 17.9207 | Total organic carbon | mg/L | 3.1 | 3.45 | 2.4 | 2.9833 | 17.9207 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3514 | [5 empty] | UV254 | cm-1 | 0.048 | 0.049 | 0.05 | 0.049 | 2.0408 | UV254 | cm-1 | 0.048 | 0.049 | 0.05 | 0.049 | 2.0408 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 12.6935 | [5 empty] | SUVA | L/(mg*m) | 1.5484 | 1.4203 | 2.0833 | 1.684 | 20.8854 | SUVA | L/(mg*m) | 1.5484 | 1.4203 | 2.0833 | 1.684 | 20.8854 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.6039 | [5 empty] | SDS-Cl2 dose | mg/L | 1.5 | 1.8 | 1.8 | 1.7 | 10.1885 | SDS-Cl2 dose | mg/L | 1.5 | 1.8 | 1.8 | 1.7 | 10.1885 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 136.3068 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.28 | 0.63 | 0.61 | 0.50667 | 38.7935 | SDS-Free Cl2 residual | mg/L | 0.28 | 0.63 | 0.61 | 0.50667 | 38.7935 | C5A-10 | Primary | 1998-11-30 | 8:00 | 63.5 | 2819.4 | 8.3 | 20.8 | 1.2 | 0.018 | 1.5 | 1 | 0.44 | 0.56 | 15.2 | 8.8 | 11.5 | 26 | BMRL | 2.7 | 6.2 | 7.6 | 16.5 | BMRL | 2.9 | BMRL | BMRL | 1.3 | BMRL | NA | NA | NA | 4.2 | 4.2 | C3A-20 | Primary | 1998-11-30 | 8:00 | 63.5 | 1409.7 | 8.3 | 20.8 | 0.6 | 0.01 | 1.6667 | 0.9 | 0.62 | 0.28 | 16.1 | 8.9 | 11.5 | BMRL | BMRL | BMRL | 2.4 | 5.1 | 7.5 | BML | 3.3 | BMRL | BMRL | 1.2 | BMRL | NA | NA | NA | 4.5 | 4.5
|  |  |  | Mass GAC required, mSC (g) | 5.0386 | [5 empty] | SDS-Cl2 demand | mg/L | 1.22 | 1.17 | 1.19 | 1.1933 | 2.1089 | SDS-Cl2 demand | mg/L | 1.22 | 1.17 | 1.19 | 1.1933 | 2.1089 | C5B-10 | Duplicate | 1998-11-30 | 8:00 | 63.5 | 2819.4 | 8.3 | 20.8 | 1.2 | 0.018 | 1.5 | 1 | 0.45 | 0.55 | 15.6 | 8.8 | 11.5 | BMRL | BMRL | 2.6 | 5.9 | 7.5 | 16 | BMRL | 2.5 | BMRL | BMRL | 1.3 | BMRL | NA | NA | NA | 3.8 | 3.8 | C3B-20 | Duplicate | 1998-11-30 | 8:00 | 63.5 | 1409.7 | 8.3 | 20.8 | 0.6 | 0.01 | 1.6667 | 0.9 | 0.55 | 0.35 | 15.2 | 8.9 | 11.5 | BMRL | BMRL | BMRL | 2.2 | 4.7 | 6.9 | BMRL | 2.9 | BMRL | BMRL | 1.1 | BMRL | NA | NA | NA | 4 | 4
[11 empty] | SDS-Chlorination temp. | oC | 14.9 | 14.5 | 17.6 | 15.6667 | 10.7631 | SDS-Chlorination temp. | oC | 14.9 | 14.5 | 17.6 | 15.6667 | 10.7631 | Avg-C5-10 | Average | --- | --- | --- | --- | 8.3 | 20.8 | 1.2 | 0.018 | 1.5 | 1 | 0.445 | 0.555 | 15.4 | 8.8 | 11.5 | 26 | #DIV/0! | 2.65 | 6.05 | 7.55 | 16.25 | #DIV/0! | 2.7 | #DIV/0! | #DIV/0! | 1.3 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 4 | Avg-C3-20 | Average | --- | --- | --- | --- | 8.3 | 20.8 | 0.6 | 0.01 | 1.6667 | 0.9 | 0.585 | 0.315 | 15.65 | 8.9 | 11.5 | #DIV/0! | #DIV/0! | #DIV/0! | 2.3 | 4.9 | 7.2 | #DIV/0! | 3.1 | #DIV/0! | #DIV/0! | 1.15 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.25 | 4.25
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.9 | 9 | 9 | 8.9667 | 0.64389 | SDS-Chlorination pH | --- | 8.9 | 9 | 9 | 8.9667 | 0.64389 | RPD-C5-10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 2.2472 | 1.8018 | 2.5974 | 0 | 0 | #VALUE! | #VALUE! | 3.7736 | 4.9587 | 1.3245 | 3.0769 | #VALUE! | 14.8148 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 10 | 10 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 11.9658 | 22.2222 | 5.7508 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 8.6957 | 8.1633 | 8.3333 | #VALUE! | 12.9032 | #VALUE! | #VALUE! | 8.6957 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 11.7647 | 11.7647
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 11.5 | 11.75 | 11.75 | 11.6667 | 1.2372 | SDS-Incubation time | hours | 11.5 | 11.75 | 11.75 | 11.6667 | 1.2372 | C9A-10 | Primary | 1998-12-04 | 8:00 | 159.5 | 7081.8 | 8.7 | 20.7 | 2.1 | 0.031 | 1.4762 | 1.3 | 0.52 | 0.78 | 16.8 | 9 | 11.75 | 54.5 | 5.5 | 8.9 | 9.5 | 5.9 | 29.8 | BMRL | 4.5 | BMRL | BMRL | 2.1 | 1.7 | NA | NA | NA | 6.6 | 8.3 | C7A-20 | Primary | 1998-12-09 | 9:00 | 280.5 | 6227.1 | 8.9 | 20.8 | 1.6 | 0.02 | 1.25 | 1.1 | 0.36 | 0.74 | 13.3 | 8.8 | 11.25 | 37.5 | 2.6 | 4.8 | 8.7 | 7.8 | 23.9 | BMRL | 3.3 | BMRL | BMRL | 2.3 | 1.3 | NA | NA | NA | 5.6 | 6.9
|  |  |  | Estimated full-scale run time, tLCT (days) | 187.8637 | [5 empty] | SDS-TOX | mg Cl- /L | 95 | 108 | 104 | 102.3333 | 6.5065 | SDS-TOX | mg Cl- /L | 95 | 108 | 104 | 102.3333 | 6.5065 | C9B-10 | Duplicate | 1998-12-04 | 8:00 | 159.5 | 7081.8 | 8.7 | 20.7 | 2.1 | 0.031 | 1.4762 | 1.3 | 0.46 | 0.84 | 16.6 | 8.9 | 11.75 | 55.6 | 5.2 | 8 | 8.9 | 5.6 | 27.7 | BMRL | 4.2 | BMRL | BMRL | 1.7 | 1.5 | NA | NA | NA | 5.9 | 7.4 | C7B-20 | Duplicate | 1998-12-09 | 9:00 | 280.5 | 6227.1 | 8.9 | 20.8 | 1.6 | 0.02 | 1.25 | 1.1 | 0.62 | 0.48 | 13.2 | 8.8 | 11.5 | 39.5 | 2.5 | 4.4 | 8.4 | 7.8 | 23.1 | BMRL | 3.3 | BMRL | BMRL | 1.9 | 1.2 | NA | NA | NA | 5.2 | 6.4
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.7027 | [5 empty] | SDS-CHCl3 | mg/L | 9.8 | 19 | 19 | 15.9333 | 33.3365 | SDS-CHCl3 | mg/L | 9.8 | 19 | 19 | 15.9333 | 33.3365 | Avg-C9-10 | Average | --- | --- | --- | --- | 8.7 | 20.7 | 2.1 | 0.031 | 1.4762 | 1.3 | 0.49 | 0.81 | 16.7 | 8.95 | 11.75 | 55.05 | 5.35 | 8.45 | 9.2 | 5.75 | 28.75 | #DIV/0! | 4.35 | #DIV/0! | #DIV/0! | 1.9 | 1.6 | #DIV/0! | #DIV/0! | #DIV/0! | 6.25 | 7.85 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.9 | 20.8 | 1.6 | 0.02 | 1.25 | 1.1 | 0.49 | 0.61 | 13.25 | 8.8 | 11.375 | 38.5 | 2.55 | 4.6 | 8.55 | 7.8 | 23.5 | #DIV/0! | 3.3 | #DIV/0! | #DIV/0! | 2.1 | 1.25 | #DIV/0! | #DIV/0! | #DIV/0! | 5.4 | 6.65
|  |  |  | Estimated RSSCT run time, tSCT (days) | 25.387 | [5 empty] | SDS-BDCM | mg/L | 6.4 | 15 | 12 | 11.1333 | 39.2067 | SDS-BDCM | mg/L | 6.4 | 15 | 12 | 11.1333 | 39.2067 | RPD-C9-10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 12.2449 | 7.4074 | 1.1976 | 1.1173 | 0 | 1.9982 | 5.6075 | 10.6509 | 6.5217 | 5.2174 | 7.3043 | #VALUE! | 6.8966 | #VALUE! | #VALUE! | 21.0526 | 12.5 | #VALUE! | #VALUE! | #VALUE! | 11.2 | 11.465 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 53.0612 | 42.623 | 0.75472 | 0 | 2.1978 | 5.1948 | 3.9216 | 8.6957 | 3.5088 | 0 | 3.4043 | #VALUE! | 0 | #VALUE! | #VALUE! | 19.0476 | 8 | #VALUE! | #VALUE! | #VALUE! | 7.4074 | 7.5188
|  |  |  | RSSCT bed length, lSC (cm) | 21.2079 | [5 empty] | SDS-DBCM | mg/L | 2.3 | 7.4 | 6.5 | 5.4 | 50.4098 | SDS-DBCM | mg/L | 2.3 | 7.4 | 6.5 | 5.4 | 50.4098 | C11A-10 | Primary | 1998-12-09 | 9:00 | 280.5 | 12454.2 | 8.9 | 20.8 | 2.2 | 0.028 | 1.2727 | 1.4 | 0.53 | 0.87 | 13 | 8.7 | 11 | 66.5 | 8.8 | 10 | 12 | 5.1 | 35.9 | BMRL | 5.4 | 1.2 | BMRL | 1.6 | 1.7 | NA | NA | NA | 8.2 | 9.9 | NA | Primary | NA | NA | #VALUE! | #VALUE! | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 272.6135 | [5 empty] | SDS-CHBr3 | mg/L | BMRL | 2.6 | 1.8 | 2.2 | 25.713 | SDS-CHBr3 | mg/L | BMRL | 2.6 | 1.8 | 2.2 | 25.713 | C11B-10 | Duplicate | 1998-12-09 | 9:00 | 280.5 | 12454.2 | 8.9 | 20.8 | 2.3 | 0.027 | 1.1739 | 1.4 | 0.27 | 1.13 | 13.4 | 8.7 | 11.25 | 66 | 7.4 | 11 | 10 | 5.1 | 33.5 | BMRL | 5.4 | 1.2 | BMRL | 1.9 | 1.9 | NA | NA | NA | 8.5 | 10.4 | NA | Duplicate | NA | NA | #VALUE! | #VALUE! | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
|  |  |  | Mass GAC required, mSC (g) | 10.0772 | [5 empty] | SDS-THM4 | mg/L | 18.5 | 44 | 39.3 | 33.9333 | 39.9922 | SDS-THM4 | mg/L | 18.5 | 44 | 39.3 | 33.9333 | 39.9922 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.9 | 20.8 | 2.25 | 0.0275 | 1.2233 | 1.4 | 0.4 | 1 | 13.2 | 8.7 | 11.125 | 66.25 | 8.1 | 10.5 | 11 | 5.1 | 34.7 | #DIV/0! | 5.4 | 1.2 | #DIV/0! | 1.75 | 1.8 | #DIV/0! | #DIV/0! | #DIV/0! | 8.35 | 10.15 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | RPD-C11-10 | RPD | --- | --- | --- | --- | 0 | 0 | 4.4444 | 3.6364 | 8.0775 | 0 | 65 | 26 | 3.0303 | 0 | 2.2472 | 0.75472 | 17.284 | 9.5238 | 18.1818 | 0 | 6.9164 | #VALUE! | 0 | 0 | #VALUE! | 17.1429 | 11.1111 | #VALUE! | #VALUE! | #VALUE! | 3.5928 | 4.9261 |  | RPD | --- | --- | --- | --- | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | 6 | 7.5 | 10 | 7.8333 | 25.7965 | SDS-DCAA* | mg/L | 6 | 7.5 | 10 | 7.8333 | 25.7965 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 1.5 | 1.8 | 4.2 | 2.5 | 59.1946 | SDS-TCAA* | mg/L | 1.5 | 1.8 | 4.2 | 2.5 | 59.1946 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | BMRL | 1.4 | 1.6 | 1.5 | 9.4281 | SDS-DBAA* | mg/L | BMRL | 1.4 | 1.6 | 1.5 | 9.4281
[11 empty] | SDS-BCAA* | mg/L | 1.4 | 2.7 | 4.9 | 3 | 58.9727 | SDS-BCAA* | mg/L | 1.4 | 2.7 | 4.9 | 3 | 58.9727
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 7.5 | 10.7 | 15.8 | 11.3333 | 36.9361 | SDS-HAA5 | mg/L | 7.5 | 10.7 | 15.8 | 11.3333 | 36.9361
[11 empty] | SDS-HAA6 | mg/L | 8.9 | 13.4 | 20.7 | 14.3333 | 41.5473 | SDS-HAA6 | mg/L | 8.9 | 13.4 | 20.7 | 14.3333 | 41.5473
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on W21: Reviewer D.S. (10/12/99): Per Consultant: "Greater than 20% SD for THM and HAA may be due to lower chlorine residual in samples B2 and B3. The influent SUVA SD is greater than 20% due to sample B3 having a lower TOC result of 2.40mg/L. Perhaps the lower TOC was due to ongoing softening/settling in the drums that also may have settled a percentage of TOC (significant calcium carbonate percipitation was noticed in the bottom of the drums). Influent bromide samples as reported on laboratory analysis report; unknown why there is a wide range."
Note on W43: Reviewer D.S. (10/12/99): Per Consultant: "Higher THM and HAA results in influent samples B2 and B3 possibly due to higher chlorine doses and residuals than in first sample B1. The influent batch samples were stored in 55 gallon polyethylene drums. See %SD comment on possible explaination of TOC result sample B3."
Note on W53: Reviewer D.S. (10/12/99): Per Consultant: "Higher THM and HAA results in influent samples B2 and B3 possibly due to higher chlorine doses and residuals than in first sample B1. The influent batch samples were stored in 55 gallon polyethylene drums. See %SD comment on possible explaination of TOC result sample B3."
Note on W54: Reviewer D.S. (10/12/99): Per Consultant: "Higher THM and HAA results in influent samples B2 and B3 possibly due to higher chlorine doses and residuals than in first sample B1. The influent batch samples were stored in 55 gallon polyethylene drums. See %SD comment on possible explaination of TOC result sample B3."
Note on AE21: Reviewer D.S. (10/12/99): Per Consultant: "Greater than 20% SD for THM and HAA may be due to lower chlorine residual in samples B2 and B3. The influent SUVA SD is greater than 20% due to sample B3 having a lower TOC result of 2.40mg/L. Perhaps the lower TOC was due to ongoing softening/settling in the drums that also may have settled a percentage of TOC (significant calcium carbonate percipitation was noticed in the bottom of the drums). Influent bromide samples as reported on laboratory analysis report; unknown why there is a wide range."
Note on AE43: Reviewer D.S. (10/12/99): Per Consultant: "Higher THM and HAA results in influent samples B2 and B3 possibly due to higher chlorine doses and residuals than in first sample B1. The influent batch samples were stored in 55 gallon polyethylene drums. See %SD comment on possible explaination of TOC result sample B3."
Note on AE53: Reviewer D.S. (10/12/99): Per Consultant: "Higher THM and HAA results in influent samples B2 and B3 possibly due to higher chlorine doses and residuals than in first sample B1. The influent batch samples were stored in 55 gallon polyethylene drums. See %SD comment on possible explaination of TOC result sample B3."
Note on AE54: Reviewer D.S. (10/12/99): Per Consultant: "Higher THM and HAA results in influent samples B2 and B3 possibly due to higher chlorine doses and residuals than in first sample B1. The influent batch samples were stored in 55 gallon polyethylene drums. See %SD comment on possible explaination of TOC result sample B3."
Note on BP41: Reviewer D.S. (10/12/99): Per Consultant: "The missing third duplicate set of results was due to a miscommunication between sample collectors."
Note on BX5: Reviewer D.S. (10/12/99): Per Consultant: "Very slow laboratory turnaround on TOC results for samples number 11 and 12; consequently made assumption based on run time that TOC levels for these samples exceeded 70% of influent TOC."
Measured Depth = 19.2 cm
Measured Depth = 10 cm

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [8 empty] | Platte River WTP - Winter Test | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [8 empty] | Platte River WTP - Winter Test | [5 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Metropolitan Utilities District | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 3 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1999-03-24 |  | Platte River WTP - Winter Test |  |  |  | 20-min. EBCT Start Date | 1999-03-24 |  | Platte River WTP - Winter Test |  |  |  | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NE 3105507 | Carbon trade name | Filtrasorb 300 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Lime softening | 71.9 mg/l as CaO | Full-Scale | 10-min. EBCT Start Time | 8:15 | [5 empty] | 20-min. EBCT Start Time | 8:15 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Coagulation | 1.9 mg/l alum | Full-Scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 15 | 6 | 3.35 | Flocculation | 1-stage | Full-Scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1999-03-24 | 10:00 | 1.75 | 77.7 | 9 | 19.4 | 0.85 | 0.003 | 0.35294 | 1.2 | 0.61 | 0.59 | 11 | 9.7 | 10 | BMRL | 4.9 | 1.7 | 3 | 1.7 | 11.3 | BMRL | 3.3 | 1.1 | BMRL | BMRL | BMRL | NA | NA | NA | 4.4 | 4.4 | C1-20 | N | 1999-03-24 | 10:00 | 1.75 | 38.85 | 9 | 19.3 | 0.85 | 0.004 | 0.47059 | 1.2 | 0.32 | 0.88 | 11 | 9 | 10 | BMRL | 2.7 | 1.2 | 2.1 | 2 | 8 | BMRL | 2.3 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 2.3 | 2.3 | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Clarification | solids contact (255 minutes detention time) | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1999-03-24 | 20:00 | 11.75 | 521.7 | 9.4 | 20.6 | BMRL | 0.004 | #VALUE! | 1.2 | 0.95 | 0.25 | 9.7 | 10 | 10.25 | BMRL | BMRL | BMRL | 4.2 | 4.1 | 8.3 | BMRL | 3.2 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3.2 | 3.2 | C2-20 | N | 1999-03-24 | 20:00 | 11.75 | 260.85 | 9.4 | 20.6 | BMRL | 0.002 | #VALUE! | 1.2 | 0.95 | 0.25 | 10 | 9.6 | 10.5 | BMRL | BMRL | BMRL | 1.5 | 2.4 | 3.9 | BMRL | 3 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3 | 3 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Dual media filtration | anthracite(dep=18"; 0.95 to 1.05 mm)/sand(dep=12"; 0.45 to 0.55 mm) | Full-Scale | Sampling date | MM/DD/YY | 1999-03-24 | 1999-04-01 | --- | --- |  | Sampling date | MM/DD/YY | 1999-03-24 | 1999-04-01 | --- | --- |  | C3-10 | N | 1999-03-25 | 8:00 | 23.75 | 1054.5 | 9.4 | 20.3 | 0.8 | 0.008 | 1 | 1.2 | 0.65 | 0.55 | 9.4 | 8.6 | 9.5 | BMRL | BMRL | BMRL | 4.2 | 3.5 | 7.7 | BMRL | 3.4 | 1.1 | BMRL | 1.1 | BMRL | NA | NA | NA | 5.6 | 5.6 | Avg-C3-20 | Y | 1999-03-26 | 8:00 | 47.75 | 1060.05 | 9.1 | 20.3 | BMRL | 0.006 | #VALUE! | 1.4 | 1.055 | 0.345 | 6.6 | 9.05 | 9.75 | BMRL | BMRL | BMRL | 4 | 4.3 | 8.3 | BMRL | 3.4 | 1.1 | BMRL | 1 | BMRL | NA | NA | NA | 5.5 | 5.5 | Construction Contingencies (% of construction costs) | 15
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 60 | 12 | 1.68 | Cartridge filtration | 5 um nominal size | Bench-Scale | Sampling time | hh:mm | 8:15 | 9:00 | --- | --- |  | Sampling time | hh:mm | 8:15 | 9:00 | --- | --- |  | C4-10 | N | 1999-03-25 | 18:00 | 33.75 | 1498.5 | 9 | 20.7 | 0.9 | 0.01 | 1.1111 | 1.2 | 0.5 | 0.7 | 10 | 9.2 | 10.3 | BMRL | BMRL | 1.3 | 6.1 | 4.8 | 12.2 | BMRL | 5.7 | 1.1 | BMRL | 1.1 | BMRL | NA | NA | NA | 7.9 | 7.9 | Avg-C4-20 | Y | 1999-03-28 | 10:00 | 97.75 | 2170.05 | 9 | 20 | 1.275 | 0.009 | 0.70588 | 1.6 | 1.17 | 0.43 | 8.55 | 8.95 | 9.5 | BMRL | BMRL | 2.1 | 8.55 | 6.5 | 17.15 | BMRL | 3.5 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3.5 | 3.5 | Engineering Fee Factor (% of construction costs) | 8
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 | In-line filtration | 1 um to 2 um exclusion size | Bench-Scale | Operation time | hh.hh | 0 | 192.75 | --- | --- |  | Operation time | hh.hh | 0 | 192.75 | --- | --- |  | Avg-C5-10 | Y | 1999-03-26 | 8:00 | 47.75 | 2120.1 | 9.2 | 20.3 | 1.05 | 0.015 | 1.4286 | 1.6 | 1.175 | 0.425 | 8.2 | 9.25 | 9.5 | 25 | BMRL | 2.3 | 8.5 | 6.9 | 17.7 | BMRL | 4.7 | 1.2 | 1.15 | 1.6 | 1.1 | NA | NA | NA | 8.65 | 9.75 | C5-20 | N | 1999-03-30 | 8:00 | 143.75 | 3191.25 | 9 | 20.8 | 1.15 | 0.015 | 1.3043 | 1.8 | 1.24 | 0.56 | 10.2 | 9.2 | 9.5 | 28 | 1.3 | 7 | 6.6 | 6.8 | 21.7 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1 | NA | NA | NA | 1.7 | 2.7 | 1999 ENR Construction Cost Index (CCI base year 1913) | 6039
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 8558.1 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 4279.05 | --- | --- |  | C6-10 | N | 1999-03-26 | 20:00 | 59.75 | 2652.9 | 9.1 | 20.3 | 1.2 | 0.015 | 1.25 | 1.7 | 1.11 | 0.59 | 8.5 | 9.2 | 10 | 33.5 | 2.5 | 2.7 | 6.9 | 2.2 | 14.3 | BMRL | 2.7 | 1.2 | BMRL | 1.1 | 1.1 | NA | NA | NA | 5 | 6.1 | C6-20 | N | 1999-03-31 | 8:30 | 168.25 | 3735.15 | 8.8 | 21.1 | 1.15 | 0.015 | 1.3043 | 1.6 | 0.84 | 0.76 | 10 | 9.3 | 10 | 31 | 1.6 | 8.3 | 8.1 | 7.8 | 25.8 | BMRL | 2.8 | BMRL | BMRL | BMRL | 1 | NA | NA | NA | 2.8 | 3.8 | 1999 Producers Price Index (PPI base year 1967 = 100) | 1947
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 135 | 131 | 133 | 3.0075 |  | Alkalinity | mg/L as CaCO3 | 135 | 131 | 133 | 3.0075 |  | C7-10 | N | 1999-03-27 | 8:00 | 71.75 | 3185.7 | 9.1 | 20.6 | 1.35 | 0.019 | 1.4074 | 1.7 | 1.17 | 0.53 | 8 | 9.3 | 9.5 | 45.5 | 2.8 | 4.3 | 9 | 6.4 | 22.5 | BMRL | 4.8 | BMRL | BMRL | 1.8 | 1.2 | NA | NA | NA | 6.6 | 7.8 | Avg-C7-20 | Y | 1999-04-01 | 9:00 | 192.75 | 4279.05 | 8.8 | 21.1 | 1.5 | 0.02 | 1.3333 | 1.8 | 0.94 | 0.86 | 10 | 8.75 | 10.875 | 32.25 | 1.25 | 6.45 | 5.5 | 6 | 19.2 | BMRL | 4.7 | BMRL | BMRL | 4.65 | 1.25 | NA | NA | NA | 9.35 | 10.6 | Labor Rate + Fringe ($/work-hour) | 26
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5202.3804 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 168 | 158 | 163 | 6.135 |  | Total hardness | mg/L as CaCO3 | 168 | 158 | 163 | 6.135 |  | C8-10 | N | 1999-03-27 | 18:00 | 81.75 | 3629.7 | 9 | 20.7 | 1.65 | 0.02 | 1.2121 | 1.7 | 1.09 | 0.61 | 8 | 9.3 | 9.75 | 47.5 | 3.5 | 5.4 | 9.7 | 6.1 | 24.7 | BMRL | 3.4 | 1.1 | BMRL | 2 | 1.3 | NA | NA | NA | 6.5 | 7.8 | C8-20 | N | 1999-04-03 | 10:00 | 241.75 | 5366.85 | 9.1 | 20.3 | 2.35 | 0.022 | 0.93617 | 1.8 | 0.97 | 0.83 | 5.3 | 9.2 | 9.75 | 45 | 3.8 | 9.3 | 8.1 | 6.5 | 27.7 | BMRL | 2.8 | BMRL | BMRL | 2.8 | 1.3 | NA | NA | NA | 5.6 | 6.9 | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 10404.7608 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 130 | 104 | 117 | 22.2222 |  | Calcium hardness | mg/L as CaCO3 | 130 | 104 | 117 | 22.2222 |  | Avg-C9-10 | Y | 1999-03-28 | 10:00 | 97.75 | 4340.1 | 9.1 | 20.3 | 1.9 | 0.024 | 1.2632 | 2 | 1.2 | 0.8 | 8.5 | 9.1 | 9.5 | 49.5 | 6.35 | 7.5 | 11 | 6.15 | 31 | BMRL | 1.75 | BMRL | BMRL | 1.45 | 1.25 | NA | NA | NA | 3.2 | 4.45 | C9-20 | N | 1999-04-08 | 8:00 | 359.75 | 7986.45 | 8.6 | 20.8 | 2.8 | 0.026 | 0.92857 | 1.8 | 0.57 | 1.23 | 9.2 | 9.6 | 9.75 | 49 | 5.5 | 9.7 | 8.9 | 5.6 | 29.7 | BMRL | 4.2 | 1.1 | BMRL | 3.6 | 2 | NA | NA | NA | 8.9 | 10.9 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 13526.189 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1999-03-30 | 8:00 | 143.75 | 6382.5 | 9 | 20.2 | 1.8 | 0.031 | 1.7222 | 2.2 | 1.23 | 0.97 | 8.8 | 9.3 | 9.5 | 49.5 | 6.7 | 7.5 | 10 | 4.9 | 29.1 | BMRL | 2.1 | BMRL | BMRL | 1.1 | 1.3 | NA | NA | NA | 3.2 | 4.5 | C10-20 | N | 1999-04-12 | 8:00 | 455.75 | 10117.65 | 9.2 | 20.2 | 3.25 | 0.029 | 0.89231 | 1.9 | 0.89 | 1.01 | 10 | 8.6 | 9.75 | 56 | 3.9 | 9.6 | 7.7 | 5 | 26.2 | BMRL | 4 | 1.1 | 1 | 3.9 | 2.1 | NA | NA | NA | 10 | 12.1 | Fuel Oil Rate ($/gal) | 0.5
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 85 | 81 | 83 | 4.8193 |  | Bromide | mg/L | 85 | 81 | 83 | 4.8193 |  | Avg-C11-10 | Y | 1999-04-01 | 9:00 | 192.75 | 8558.1 | 8.8 | 21 | 2.1 | 0.033 | 1.5714 | 2.2 | 1.43 | 0.77 | 9.8 | 8.85 | 10.25 | 55.25 | 4.2 | 9.7 | 7.55 | 4.6 | 26.05 | BMRL | 3.7 | BMRL | BMRL | 5.3 | 3.9 | NA | NA | NA | 9 | 12.9 | C11-20 | N | 1999-04-14 | 8:00 | 503.75 | 11183.25 | 9 | 20.7 | 3 | 0.033 | 1.1 | 2 | 0.96 | 1.04 | 6 | 9.4 | 10.2 | 46.5 | 5.2 | 8.1 | 8.8 | 3.7 | 25.8 | BMRL | 4.4 | 1 | 1.1 | 1.7 | 1.6 | NA | NA | NA | 8.2 | 9.8 | Natural Gas Rate ($/ft3) | 3.5
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1999-04-03 | 10:00 | 241.75 | 10733.7 | 9.2 | 20.2 | 2.95 | 0.037 | 1.2542 | 2.2 | 1.03 | 1.17 | 5.6 | 9.4 | 9.75 | 71.5 | 8.2 | 9.9 | 9.1 | 4.2 | 31.4 | BMRL | 5.4 | 1.1 | BMRL | 2.4 | 2.4 | NA | NA | NA | 8.9 | 11.3 | C12-20 | N | 1999-04-16 | 8:00 | 551.75 | 12248.85 | 8.7 | 20.4 | 3.45 | 0.03 | 0.86957 | 2 | 1.01 | 0.99 | 10 | 9.7 | 9.75 | 57.5 | 4.3 | 8.1 | 8.9 | 3.7 | 25 | BMRL | 3.9 | 1 | BMRL | 2.3 | 1.8 | NA | NA | NA | 7.2 | 9 | Current Process Water Rate ($/1000 gal) | 0.3
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1625e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [10 empty] | -869840.25 | -38620907.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869840.25 | -19310453.55 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.2 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD |  |  |  |  | -869840.25 | -38620907.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869840.25 | -19310453.55 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 7.4 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-30 | 1999-04-01 | --- | --- | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-30 | 1999-04-01 | --- | --- |  |  |  |  | -869840.25 | -38620907.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869840.25 | -19310453.55 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Platte River Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 4.7081 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 8:15 | 8:00 | 9:00 | --- | --- | Sampling time | hh:mm | 8:15 | 8:00 | 9:00 | --- | --- |  |  |  |  | -869840.25 | -38620907.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869840.25 | -19310453.55 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | STS |  |  | RSSCT flow rate, QSC (mL/min) | 7.4572 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 143.75 | 192.75 | --- | --- | Operation time | hh.hh | 0 | 143.75 | 192.75 | --- | --- |  |  |  |  | -869840.25 | -38620907.1 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -869840.25 | -19310453.55 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | SplitTrt/Softening |  |  | Estimated total influent volume required, VSCT (L) | 408.9203 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 6382.5 | 8558.1 | --- | --- | Bed volumes | (20 minute) | 0 | 3191.25 | 4279.05 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 454 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.5 | 9.1 | 9 | 8.8667 | 3.6254 | pH | --- | 8.5 | 9.1 | 9 | 8.8667 | 3.6254 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | 28507002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.1 | 0.2 | 0.2 | 0.16667 | 34.641 | Turbidity | ntu | 0.1 | 0.2 | 0.2 | 0.16667 | 34.641 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 4 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 18.3 | 20.9 | 22.1 | 20.4333 | 9.5066 | Temperature | oC | 18.3 | 20.9 | 22.1 | 20.4333 | 9.5066
Historical Average Water Temperature (oC) | 14 |  |  | Estimated full-scale run time, tLCT (days) | 93.9319 | [5 empty] | Total organic carbon | mg/L | 3 | 2.65 | 2.8 | 2.8167 | 6.2341 | Total organic carbon | mg/L | 3 | 2.65 | 2.8 | 2.8167 | 6.2341 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.3514 | [5 empty] | UV254 | cm-1 | 0.052 | 0.057 | 0.053 | 0.054 | 4.8995 | UV254 | cm-1 | 0.052 | 0.057 | 0.053 | 0.054 | 4.8995 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 12.6935 | [5 empty] | SUVA | L/(mg*m) | 1.7333 | 2.1509 | 1.8929 | 1.9257 | 10.9432 | SUVA | L/(mg*m) | 1.7333 | 2.1509 | 1.8929 | 1.9257 | 10.9432 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.6039 | [5 empty] | SDS-Cl2 dose | mg/L | 2 | 3 | 2.5 | 2.5 | 20 | SDS-Cl2 dose | mg/L | 2 | 3 | 2.5 | 2.5 | 20 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 136.3068 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.07 | 2.1 | 0.91 | 1.0267 | 99.3522 | SDS-Free Cl2 residual | mg/L | 0.07 | 2.1 | 0.91 | 1.0267 | 99.3522 | C5A-10 | Primary | 1999-03-26 | 8:00 | 47.75 | 2120.1 | 9.2 | 20.3 | 1.1 | 0.015 | 1.3636 | 1.6 | 1.2 | 0.4 | 8.1 | 9.2 | 9.5 | 25 | BMRL | 2.3 | 8.5 | 6.9 | 17.7 | BMRL | 4.4 | 1.2 | 1.1 | 1.6 | 1.1 | NA | NA | NA | 8.3 | 9.4 | C3A-20 | Primary | 1999-03-26 | 8:00 | 47.75 | 1060.05 | 9.1 | 20.3 | BMRL | 0.006 | #VALUE! | 1.4 | 1.04 | 0.36 | 6.4 | 9 | 9.75 | BMRL | BMRL | BMRL | 4.1 | 4.5 | 8.6 | BMRL | 3.5 | 1.1 | BMRL | 1 | BMRL | NA | NA | NA | 5.6 | 5.6
|  |  |  | Mass GAC required, mSC (g) | 5.0386 | [5 empty] | SDS-Cl2 demand | mg/L | 1.93 | 0.9 | 1.59 | 1.4733 | 35.6211 | SDS-Cl2 demand | mg/L | 1.93 | 0.9 | 1.59 | 1.4733 | 35.6211 | C5B-10 | Duplicate | 1999-03-26 | 8:00 | 47.75 | 2120.1 | 9.2 | 20.3 | 1 | 0.015 | 1.5 | 1.6 | 1.15 | 0.45 | 8.3 | 9.3 | 9.5 | BMRL | BMRL | 2.3 | 8.5 | 6.9 | 17.7 | BMRL | 5 | 1.2 | 1.2 | 1.6 | 1.1 | NA | NA | NA | 9 | 10.1 | C3B-20 | Duplicate | 1999-03-26 | 8:00 | 47.75 | 1060.05 | 9.1 | 20.3 | BMRL | 0.006 | #VALUE! | 1.4 | 1.07 | 0.33 | 6.8 | 9.1 | 9.75 | BMRL | BMRL | BMRL | 3.9 | 4.1 | 8 | BMRL | 3.3 | 1.1 | BMRL | BMRL | BMRL | NA | NA | NA | 4.4 | 4.4
[11 empty] | SDS-Chlorination temp. | oC | 8.5 | 8.5 | 9.8 | 8.9333 | 8.4017 | SDS-Chlorination temp. | oC | 8.5 | 8.5 | 9.8 | 8.9333 | 8.4017 | Avg-C5-10 | Average | --- | --- | --- | --- | 9.2 | 20.3 | 1.05 | 0.015 | 1.4318 | 1.6 | 1.175 | 0.425 | 8.2 | 9.25 | 9.5 | 25 | #DIV/0! | 2.3 | 8.5 | 6.9 | 17.7 | #DIV/0! | 4.7 | 1.2 | 1.15 | 1.6 | 1.1 | #DIV/0! | #DIV/0! | #DIV/0! | 8.65 | 9.75 | Avg-C3-20 | Average | --- | --- | --- | --- | 9.1 | 20.3 | #DIV/0! | 0.006 | #VALUE! | 1.4 | 1.055 | 0.345 | 6.6 | 9.05 | 9.75 | #DIV/0! | #DIV/0! | #DIV/0! | 4 | 4.3 | 8.3 | #DIV/0! | 3.4 | 1.1 | #DIV/0! | 1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 5 | 5
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9 | 9 | 8 | 8.6667 | 6.6617 | SDS-Chlorination pH | --- | 9 | 9 | 8 | 8.6667 | 6.6617 | RPD-C5-10 | RPD | --- | --- | --- | --- | 0 | 0 | 9.5238 | 0 | 9.5238 | 0 | 4.2553 | 11.7647 | 2.439 | 1.0811 | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | #VALUE! | 12.766 | 0 | 8.6957 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 8.0925 | 7.1795 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0 | 0 | #VALUE! | 0 | #VALUE! | 0 | 2.8436 | 8.6957 | 6.0606 | 1.105 | 0 | #VALUE! | #VALUE! | #VALUE! | 5 | 9.3023 | 7.2289 | #VALUE! | 5.8824 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 24 | 24
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 10 | 10 | 10.25 | 10.0833 | 1.4314 | SDS-Incubation time | hours | 10 | 10 | 10.25 | 10.0833 | 1.4314 | C9A-10 | Primary | 1999-03-28 | 10:00 | 97.75 | 4340.1 | 9.1 | 20.3 | 1.9 | 0.024 | 1.2632 | 2 | 1.19 | 0.81 | 8.4 | 9.1 | 9.5 | 50.5 | 6.2 | 7.3 | 11 | 6.1 | 30.6 | BMRL | 1.7 | BMRL | BMRL | 1.3 | 1.2 | NA | NA | NA | 3 | 4.2 | C4A-20 | Primary | 1999-03-28 | 10:00 | 97.75 | 2170.05 | 9 | 20 | 1.3 | 0.009 | 0.69231 | 1.6 | 1.16 | 0.44 | 8.3 | 9 | 9.5 | BMRL | BMRL | 1.6 | 8.1 | 6.2 | 15.9 | BMRL | 3.5 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3.5 | 3.5
|  |  |  | Estimated full-scale run time, tLCT (days) | 187.8637 | [5 empty] | SDS-TOX | mg Cl- /L | NR | 104 | 102.5 | 103.25 | 1.0273 | SDS-TOX | mg Cl- /L | NR | 104 | 102.5 | 103.25 | 1.0273 | C9B-10 | Duplicate | 1999-03-28 | 10:00 | 97.75 | 4340.1 | 9.1 | 20.3 | 1.9 | 0.024 | 1.2632 | 2 | 1.21 | 0.79 | 8.6 | 9.1 | 9.5 | 48.5 | 6.5 | 7.7 | 11 | 6.2 | 31.4 | BMRL | 1.8 | BMRL | BMRL | 1.6 | 1.3 | NA | NA | NA | 3.4 | 4.7 | C4B-20 | Duplicate | 1999-03-28 | 10:00 | 97.75 | 2170.05 | 9 | 20 | 1.25 | 0.009 | 0.72 | 1.6 | 1.18 | 0.42 | 8.8 | 8.9 | 9.5 | BMRL | BMRL | 2.6 | 9 | 6.8 | 18.4 | BMRL | NR | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | NR | NR
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.7027 | [5 empty] | SDS-CHCl3 | mg/L | NR | 13 | 12 | 12.5 | 5.6569 | SDS-CHCl3 | mg/L | NR | 13 | 12 | 12.5 | 5.6569 | Avg-C9-10 | Average | --- | --- | --- | --- | 9.1 | 20.3 | 1.9 | 0.024 | 1.2632 | 2 | 1.2 | 0.8 | 8.5 | 9.1 | 9.5 | 49.5 | 6.35 | 7.5 | 11 | 6.15 | 31 | #DIV/0! | 1.75 | #DIV/0! | #DIV/0! | 1.45 | 1.25 | #DIV/0! | #DIV/0! | #DIV/0! | 3.2 | 4.45 | Avg-C4-20 | Average | --- | --- | --- | --- | 9 | 20 | 1.275 | 0.009 | 0.70615 | 1.6 | 1.17 | 0.43 | 8.55 | 8.95 | 9.5 | #DIV/0! | #DIV/0! | 2.1 | 8.55 | 6.5 | 17.15 | #DIV/0! | 3.5 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.5 | 3.5
|  |  |  | Estimated RSSCT run time, tSCT (days) | 25.387 | [5 empty] | SDS-BDCM | mg/L | NR | 8.9 | 10 | 9.45 | 8.2309 | SDS-BDCM | mg/L | NR | 8.9 | 10 | 9.45 | 8.2309 | RPD-C9-10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1.6667 | 2.5 | 2.3529 | 0 | 0 | 4.0404 | 4.7244 | 5.3333 | 0 | 1.626 | 2.5806 | #VALUE! | 5.7143 | #VALUE! | #VALUE! | 20.6897 | 8 | #VALUE! | #VALUE! | #VALUE! | 12.5 | 11.236 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0 | 0 | 3.9216 | 0 | 3.9216 | 0 | 1.7094 | 4.6512 | 5.848 | 1.1173 | 0 | #VALUE! | #VALUE! | 47.619 | 10.5263 | 9.2308 | 14.5773 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | RSSCT bed length, lSC (cm) | 21.2079 | [5 empty] | SDS-DBCM | mg/L | NR | 9.4 | 6.6 | 8 | 24.7487 | SDS-DBCM | mg/L | NR | 9.4 | 6.6 | 8 | 24.7487 | C11A-10 | Primary | 1999-04-01 | 9:00 | 192.75 | 8558.1 | 8.8 | 21 | 2.1 | 0.033 | 1.5714 | 2.2 | 1.41 | 0.79 | 9.8 | 8.9 | 10.25 | 52.5 | 4 | 9.7 | 7.3 | 4.6 | 25.6 | BMRL | 3.9 | BMRL | BMRL | 5 | 3.6 | NA | NA | NA | 8.9 | 12.5 | C7A-20 | Primary | 1999-04-01 | 9:00 | 192.75 | 4279.05 | 8.8 | 21.1 | 1.5 | 0.02 | 1.3333 | 1.8 | 0.94 | 0.86 | 10 | 8.8 | 10.75 | 31 | 1.4 | 7 | 5.6 | 5.8 | 19.8 | BMRL | 4.7 | BMRL | BMRL | 4.6 | 1.2 | NA | NA | NA | 9.3 | 10.5
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 272.6135 | [5 empty] | SDS-CHBr3 | mg/L | NR | 2 | 2.1 | 2.05 | 3.4493 | SDS-CHBr3 | mg/L | NR | 2 | 2.1 | 2.05 | 3.4493 | C11B-10 | Duplicate | 1999-04-01 | 9:00 | 192.75 | 8558.1 | 8.8 | 21 | 2.1 | 0.033 | 1.5714 | 2.2 | 1.45 | 0.75 | 9.8 | 8.8 | 10.5 | 58 | 4.4 | 9.7 | 7.8 | 4.6 | 26.5 | BMRL | 3.5 | BMRL | BMRL | 5.6 | 4.2 | NA | NA | NA | 9.1 | 13.3 | C7B-20 | Duplicate | 1999-04-01 | 9:00 | 192.75 | 4279.05 | 8.8 | 21.1 | 1.5 | 0.02 | 1.3333 | 1.8 | 1.2 | 0.6 | 10 | 8.7 | 11 | 33.5 | 1.1 | 5.9 | 5.4 | 6.2 | 18.6 | BMRL | NR | BMRL | BMRL | 4.7 | 1.3 | NA | NA | NA | NR | NR
|  |  |  | Mass GAC required, mSC (g) | 10.0772 | [5 empty] | SDS-THM4 | mg/L | 0 | 33.3 | 30.7 | 21.3333 | 86.8167 | SDS-THM4 | mg/L | 0 | 33.3 | 30.7 | 21.3333 | 86.8167 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.8 | 21 | 2.1 | 0.033 | 1.5714 | 2.2 | 1.43 | 0.77 | 9.8 | 8.85 | 10.375 | 55.25 | 4.2 | 9.7 | 7.55 | 4.6 | 26.05 | #DIV/0! | 3.7 | #DIV/0! | #DIV/0! | 5.3 | 3.9 | #DIV/0! | #DIV/0! | #DIV/0! | 9 | 12.9 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.8 | 21.1 | 1.5 | 0.02 | 1.3333 | 1.8 | 1.07 | 0.73 | 10 | 8.75 | 10.875 | 32.25 | 1.25 | 6.45 | 5.5 | 6 | 19.2 | #DIV/0! | 4.7 | #DIV/0! | #DIV/0! | 4.65 | 1.25 | #DIV/0! | #DIV/0! | #DIV/0! | 9.3 | 10.5
[11 empty] | SDS-MCAA* | mg/L | NR | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | NR | BMRL | BMRL | #DIV/0! | #DIV/0! | RPD-C11-10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 2.7972 | 5.1948 | 0 | 1.1299 | 2.4096 | 9.9548 | 9.5238 | 0 | 6.6225 | 0 | 3.4549 | #VALUE! | 10.8108 | #VALUE! | #VALUE! | 11.3208 | 15.3846 | #VALUE! | #VALUE! | #VALUE! | 2.2222 | 6.2016 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | 24.2991 | 35.6164 | 0 | 1.1429 | 2.2989 | 7.7519 | 24 | 17.0543 | 3.6364 | 6.6667 | 6.25 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1505 | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | SDS-DCAA* | mg/L | NR | 4.7 | 5.5 | 5.1 | 11.0919 | SDS-DCAA* | mg/L | NR | 4.7 | 5.5 | 5.1 | 11.0919 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | NR | BMRL | 3 | 3 | #DIV/0! | SDS-TCAA* | mg/L | NR | BMRL | 3 | 3 | #DIV/0! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | NR | BMRL | BMRL | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | NR | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | NR | BMRL | 4 | 4 | #DIV/0! | SDS-DBAA* | mg/L | NR | BMRL | 4 | 4 | #DIV/0!
[11 empty] | SDS-BCAA* | mg/L | NR | 2.2 | 6.1 | 4.15 | 66.451 | SDS-BCAA* | mg/L | NR | 2.2 | 6.1 | 4.15 | 66.451
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 0 | 4.7 | 12.5 | 5.7333 | 110.1234 | SDS-HAA5 | mg/L | 0 | 4.7 | 12.5 | 5.7333 | 110.1234
[11 empty] | SDS-HAA6 | mg/L | 0 | 6.9 | 18.6 | 8.5 | 110.6195 | SDS-HAA6 | mg/L | 0 | 6.9 | 18.6 | 8.5 | 110.6195
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on Q35: Reviewer D.S. (10/12/99): Per Consultant: "SDS reported temperature is measured reported temperature. All samples refrigerated to 4C to 7C, higher reported temperature due to slight warming after removal from refrigerator."
Note on Y35: Reviewer D.S. (10/12/99): Per Consultant: "SDS reported temperature is measured reported temperature. All samples refrigerated to 4C to 7C, higher reported temperature due to slight warming after removal from refrigerator."
Note on AU5: Reviewer D.S. (10/12/99): Per Consultant: "SDS reported temperature is measured reported temperature. All samples refrigerated to 4C to 7C, higher reported temperature due to slight warming after removal from refrigerator."
Note on AU30: Reviewer D.S. (10/12/99): Per Consultant: "SDS reported temperature is measured reported temperature. All samples refrigerated to 4C to 7C, higher reported temperature due to slight warming after removal from refrigerator."
Note on BX5: Reviewer M.H. (12/13/99): Per Consultant, regarding the relatively high TOC breakthrough curve: "TOC breakthrough sooner than predicted, didn't allow for 12 samples collected prior to 70% breakthrough. Effluent TOC, THM, HAA samples that exceeded influent levels of these parameters were possibly due to desorption of TOC from the exhausted GAC."
Note on CD5: Reviewer D.S. (10/12/99): Per Consultant: "SDS reported temperature is measured reported temperature. All samples refrigerated to 4C to 7C, higher reported temperature due to slight warming after removal from refrigerator."
Note on CD30: Reviewer D.S. (10/12/99): Per Consultant: "SDS reported temperature is measured reported temperature. All samples refrigerated to 4C to 7C, higher reported temperature due to slight warming after removal from refrigerator."
Measured Depth = 9.7 cm
Measured Depth = 18.6 cm