## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | North Texas Municipal Water Dist | Carbon manufacturer | Calgon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0430044 | Carbon trade name | Filtrasorb 400 | mesh size | (mm) | Coagulation | 5.4 ±1 mg/L of Ferric Iron plus 50±10 mg/L of CaO | Full-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous Coal base | 4 | 4.75 | Flocculation | 3 Stage, Detention time of 0.36 hours at design flow of 35 MGD | Full-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Pilot GAC influent TOC (mg/L) | 3.74 | 6 | 3.35 | Sedimentation | Straight Flow, detention time of 2.7 hours at design flow of 35 MGD | Full-scale | START | --- | 1998-04-14 | 8:15 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 8:15 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 8:15 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 155.6 | 8 | 2.36 | Dual Media Filtration | sand/anthracite | Pilot-scale | A1 | N | 1998-04-15 | 8:30 | 24.25 | 72.75 | 145.5 | 8.45 | 0.39 | 122 | 20.3 | 149 | 140 | BMRL | 39 | 2.95 | 0.071 | 2.4068 | 1.5 | BMRL | #VALUE! | 20 | 8.4 | 23 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | B1 | N | 1998-04-15 | 8:30 | 24.25 | 145.5 | 8.9 | 0.77 | 20.3 | BMRL | BMRL | 0 | #VALUE! | 0.45 | BMRL | #VALUE! | 20 | 8.42 | 24 | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | C1 | N | 1998-04-15 | 8:30 | 24.25 | 72.75 | 8.6 | 0.26 | 20.7 | BMRL | BMRL | 0.001 | #VALUE! | 1 | 0.3 | 0.7 | 20 | 8.45 | 23.1 | BMRL | BMRL | BMRL | 1.7 | 2.5 | 4.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 434.4 | 10 | 2 |  |  |  | A2 | N | 1998-04-20 | 9:00 | 144.75 | 434.25 | 868.5 | 8.3 | 0.4 | 123 | 21.7 | 149 | 140 | BMRL | 43 | 2.8 | 0.0675 | 2.4107 | 4.8 | 1.85 | 2.95 | 20 | 8.29 | 24 | 266 | 17 | 6.3 | 1.3 | BMRL | 24.6 | 2.4 | 26 | 18 | BMRL | BMRL | 26 | NA | NA | NA | 46.4 | 72.4 | B2 | N | 1998-04-20 | 9:00 | 144.75 | 868.5 | 8.1 | 0.28 | 21.3 | BMRL | BMRL | 0 | #VALUE! | 2.19 | 1.5 | 0.69 | 20 | 8.28 | 24 | BMRL | BMRL | 1.3 | 1.4 | BMRL | 2.7 | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1 | 1 | C2 | N | 1998-04-20 | 9:00 | 144.75 | 434.25 | 8 | 0.29 | 21.8 | BMRL | BMRL | 0 | #VALUE! | 2.19 | 1.8 | 0.39 | 20 | 8.23 | 23.9 | BMRL | 1.1 | 1.1 | BMRL | BMRL | 2.2 | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1 | 1 | Construction Contingencies (% of construction costs) | 20
|  | Pilot GAC mesh size, upper (US standard mesh) | 12 | 12 | 1.68 |  |  |  | A3 | N | 1998-04-27 | 9:00 | 312.75 | 938.25 | 1876.5 | 8.3 | 0.33 | 120 | 19.9 | 147 | 143 | BMRL | 41 | 2.8 | 0.0675 | 2.4107 | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B3 Avg. | Y | 1998-04-24 | 9:00 | 240.75 | 1444.5 | 8.185 | 0.235 | 20 | BMRL | BMRL | 0 | #VALUE! | 2.025 | 1.1 | 0.925 | 20 | 8.25 | 24 | 28.5 | 3 | 4.2 | 5.4 | 2.9 | 15.5 | BMRL | 1 | BMRL | BMRL | 2.05 | BMRL | NA | NA | NA | 3.05 | 3.05 | C3 | N | 1998-04-27 | 9:00 | 312.75 | 938.25 | 8 | 0.25 | 20.4 | BMRL | BMRL | 0 | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | Engineering Fee Factor (% of construction costs) | 6
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 40 | 16 | 1.18 |  |  |  | A4 | N | 1998-04-30 | 9:00 | 384.75 | 1154.25 | 2308.5 | 8.3 | 0.34 | 120 | 18.8 | 147 | 140 | BMRL | 42 | 3.15 | 0.068 | 2.1587 | 4.5 | 1.35 | 3.15 | 20 | 8.27 | 24 | 268 | 40 | 24 | 5.2 | BMRL | 69.2 | BMRL | 23 | 19 | BMRL | BMRL | 5.9 | NA | NA | NA | 42 | 47.9 | B4 | N | 1998-04-27 | 9:00 | 312.75 | 1876.5 | 8.1 | 0.19 | 20 | BMRL | BMRL | 0.004 | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C4 Avg. | Y | 1998-04-30 | 9:00 | 384.75 | 1154.25 | 8 | 0.245 | 18.8 | BMRL | 0.625 | 0.001 | 0.16 | 2.01 | 1.575 | 0.435 | 20 | 8.2 | 24 | BMRL | 5.6 | 1.85 | 1.15 | BMRL | 8.6 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.1 | 1.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Flow rate, Q (L/hr) | 138.5 | 20 | 0.85 |  |  |  | A5 Avg. | Y | 1998-05-04 | 9:00 | 480.75 | 1442.25 | 2884.5 | 8.1 | 0.335 | 126.5 | 21.95 | 157.5 | 153 | BMRL | 41 | 2.975 | 0.063 | 2.1176 | 4.35 | 1.4 | 2.95 | 20 | 8.3 | 24 | 253.25 | 44.5 | 19.5 | 5.5 | BMRL | 69.5 | BMRL | 20.5 | 18 | BMRL | BMRL | 5.7 | NA | NA | NA | 38.5 | 44.2 | B5 | N | 1998-04-30 | 9:00 | 384.75 | 2308.5 | 8.1 | 0.29 | 18.8 | BMRL | 1.15 | 0.009 | 0.78261 | 2.1 | 1.2 | 0.9 | 20 | 8.26 | 24 | 41 | 8 | 7.2 | 8.3 | 3.3 | 26.8 | BMRL | 1.4 | BMRL | BMRL | 1.6 | 1.4 | NA | NA | NA | 3 | 4.4 | C5 | N | 1998-05-04 | 9:00 | 480.75 | 1442.25 | 7.9 | 0.24 | 22 | BMRL | 0.55 | 0 | 0 | 1.8 | 1.31 | 0.49 | 20 | 8 | 24 | BMRL | 4.6 | 1.9 | 1.3 | BMRL | 7.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1998-05-11 | 9:00 | 648.75 | 1946.25 | 3892.5 | 8.2 | 0.38 | 125 | 22 | 154 | 150 | BMRL | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B6 | N | 1998-05-04 | 9:00 | 480.75 | 2884.5 | 8 | 0.21 | 22 | BMRL | 0.85 | 0.008 | 0.94118 | 1.95 | 1.3 | 0.65 | 20 | 8.22 | 24 | 34 | 5.7 | 6.2 | 7.4 | 3.7 | 23 | BMRL | 1.5 | BMRL | BMRL | 1.6 | 1.5 | NA | NA | NA | 3.1 | 4.6 | C6 | N | 1998-05-11 | 9:00 | 648.75 | 1946.25 | 7.8 | 0.26 | 22.2 | BMRL | NA | 0 | #VALUE! | NA | NA | #VALUE! | NR | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | Labor Rate + Fringe ($/work-hour) | 35
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | N | 1998-05-26 | 9:45 | 1009.5 | 3028.5 | 6057 | 8.2 | 0.36 | 90 | 23.6 | 114 | 113 | BMRL | 42 | 3.4 | 0.062 | 1.8235 | 4.125 | 1.65 | 2.475 | 20 | 8.35 | 24 | 234 | 66 | 22 | 9.5 | BMRL | 97.5 | BMRL | 19 | 13 | BMRL | 1.3 | 7.8 | NA | NA | NA | 33.3 | 41.1 | B7 | N | 1998-05-11 | 9:00 | 648.75 | 3892.5 | 8 | 0.27 | 21.7 | BMRL | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C7 | N | 1998-05-26 | 9:20 | 1009.0833 | 3027.25 | 7.8 | 0.21 | 23.6 | BMRL | 1.35 | 0 | 0 | 1.575 | 1.3 | 0.275 | 20 | 8.26 | 24 | BMRL | 2.2 | 1.6 | 2.5 | 1.1 | 7.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 3905.9497 | 50 | 0.3 |  |  |  | A8 | N | 1998-06-15 | 9:20 | 1489.0833 | 4467.25 | 8934.5 | 7.86 | 0.37 | 90 | 24.3 | 110 | 108 | BMRL | 52 | 3.15 | 0.066 | 2.0952 | 4.05 | 1.5 | 2.55 | 20 | 8.26 | 23.9 | NA | 62 | 27 | 9.9 | BMRL | 98.9 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | B8 | N | 1998-05-18 | 8:30 | 816.25 | 4897.5 | 7.9 | 0.23 | 23.5 | BMRL | 2 | 0.0165 | 0.825 | 1.95 | 1.3 | 0.65 | 20 | 8.22 | 23.2 | 52 | 9.9 | 10 | 12 | 5.4 | 37.3 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C8 | N | 1998-06-15 | 8:45 | 1488.5 | 4465.5 | 7.6 | 0.18 | 24.7 | BMRL | 0.95 | 0.009 | 0.94737 | 1.575 | 1.22 | 0.355 | 20 | 8.18 | 23.25 | BMRL | 3.9 | 2.9 | 7.7 | 3.9 | 18.4 | BMRL | BMRL | BMRL | BMRL | 1.8 | BMRL | NA | NA | NA | 1.8 | 1.8 | Electric Rate ($/kW-h) | 0.07
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 7811.8995 | 60 | 0.25 |  |  |  | A9 | N | 1998-07-01 | 9:30 | 1873.25 | 5619.75 | 11239.5 | 8.2 | 0.32 | 63 | 27.2 | 89 | 87 | BMRL | 58 | 3.75 | 0.066 | 1.76 | 3.9 | 1.3 | 2.6 | 20 | 8.33 | 23.4 | 204.5 | 57 | 31 | 11 | BMRL | 99 | BMRL | 16 | 12 | BMRL | 2.8 | 6 | NA | NA | NA | 30.8 | 36.8 | B9 | N | 1998-05-26 | 9:30 | 1009.25 | 6055.5 | 7.8 | 0.27 | 23.8 | BMRL | 1.6 | 0.018 | 1.125 | 1.725 | 1 | 0.725 | 20 | 8.17 | 24 | 54.5 | 8.5 | 11 | 11 | 4.2 | 34.7 | BMRL | 1.6 | 2.3 | BMRL | 5.7 | 6.1 | NA | NA | NA | 9.6 | 15.7 | C9 | N | 1998-07-01 | 9:30 | 1873.25 | 5619.75 | 7.7 | 0.15 | 27.7 | BMRL | 2.05 | 0.008 | 0.39024 | 1.575 | 1 | 0.575 | 20 | 8.27 | 23.42 | BMRL | 3.9 | 3.6 | 8.6 | 5.5 | 21.6 | BMRL | BMRL | BMRL | BMRL | 3.1 | BMRL | NA | NA | NA | 3.1 | 3.1 | Fuel Oil Rate ($/gal) | 2
|  |  |  | 70 | 0.21 |  |  |  | A10 Avg. | Y | 1998-07-15 | 9:30 | 2209.25 | 6627.75 | 13255.5 | 7.95 | 0.49 | 62.5 | 28.7 | 92 | 90 | BMRL | 70.5 | 4.23 | 0.055 | 1.3002 | 3.75 | 0.99 | 2.76 | 20 | 8.29 | 23.75 | 194.5 | 47.5 | 26.5 | 12.5 | 1 | 87.5 | BMRL | 20 | 15 | BMRL | 3.7 | 7.7 | NA | NA | NA | 38.7 | 46.4 | B10 | N | 1998-06-01 | 9:00 | 1152.75 | 6916.5 | 7.7 | 0.32 | 25.3 | BMRL | 2.9 | 0.022 | 0.75862 | 1.725 | 0.9 | 0.825 | 20 | 8.29 | 24 | 69 | 9.8 | 11 | 11 | 3.8 | 35.6 | BMRL | 2.1 | 5.1 | BMRL | 6.2 | 7 | NA | NA | NA | 13.4 | 20.4 | C10 | N | 1998-07-15 | 9:00 | 2208.75 | 6626.25 | 7.49 | 0.21 | 28.6 | BMRL | 1.2 | 0.006 | 0.5 | 1.575 | 0.83 | 0.745 | 20 | 8.18 | 23.75 | 28.5 | 6.7 | 6 | 8.1 | 5.9 | 26.7 | BMRL | 1.5 | BMRL | BMRL | 4.2 | 1.5 | NA | NA | NA | 5.7 | 7.2 | Natural Gas Rate ($/ft3) | 0.002
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-07-27 | 9:00 | 2496.75 | 7490.25 | 14980.5 | 8.25 | 0.53 | 56 | 29 | 81 | 78 | BMRL | 67 | 3.5 | 0.057 | 1.6286 | 3.75 | 1.4 | 2.35 | 23 | 8.33 | 25 | 211.5 | 36 | 21 | 12 | BMRL | 69 | BMRL | 15 | 9.2 | BMRL | 1 | 3.6 | NA | NA | NA | 25.2 | 28.8 | B11 | N | 1998-06-08 | 9:00 | 1320.75 | 7924.5 | 7.7 | 0.45 | 23.6 | BMRL | 1.65 | 0.023 | 1.3939 | 1.725 | 1.1 | 0.625 | 20 | 8.19 | 23.6 | 53.5 | 6.4 | 10 | 11 | 7.1 | 34.5 | BMRL | 1.3 | BMRL | BMRL | 3.2 | 2 | NA | NA | NA | 4.5 | 6.5 | C11 Avg. | Y | 1998-07-27 | 9:00 | 2496.75 | 7490.25 | 7.66 | 0.14 | 28.9 | 0.228 | 1.28 | 0.008 | 0.625 | 1.65 | 1.25 | 0.4 | 22.25 | 8.265 | 25 | 27.75 | 3.25 | 5.55 | 10 | 6.55 | 25.35 | BMRL | 1.65 | BMRL | BMRL | 1 | 1.1 | NA | NA | NA | 2.65 | 3.75 | Current Process Water Rate ($/1000 gal) | 0.719
FAX Number |  | Carbon particle diameter, d (mm) | 1.0525 | [5 empty] | A12 | N | 1998-08-11 | 9:00 | 2856.75 | 8570.25 | 17140.5 | 7.92 | 0.46 | 71 | 24.4 | 99 | 95 | BMRL | NA | 3.9 | 0.057 | 1.4615 | 3.75 | 1.3 | 2.45 | 21.6 | 8.25 | 24.75 | 216 | 36 | 22 | 12 | 1 | 71 | 5.5 | 15 | 9.1 | 2.2 | 2.5 | 6.2 | NA | NA | NA | 34.3 | 40.5 | B12 Avg. | Y | 1998-06-15 | 9:15 | 1489 | 8934 | 7.75 | 0.225 | 24.5 | BMRL | 2.125 | 0.027 | 1.2706 | 1.725 | 0.8 | 0.925 | 20 | 8.23 | 23.25 | 65.5 | 14 | 13.5 | 13.5 | 3.55 | 44.55 | BMRL | 2.55 | 3.4 | BMRL | 3.35 | 3.25 | NA | NA | NA | 9.3 | 12.55 | C12 | N | 1998-08-11 | 9:00 | 2856.75 | 8570.25 | 7.59 | 0.19 | 24.2 | BMRL | 1.6 | 0.014 | 0.875 | 1.65 | 0.73 | 0.92 | 21.2 | 8.13 | 24.75 | 34.5 | 4.9 | 6.8 | 11 | 6.3 | 29 | BMRL | 1.4 | BMRL | BMRL | 2 | 1.1 | NA | NA | NA | 3.4 | 4.5 | Modifications to Existing Plant (% of construction costs) | 30
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.019016 | [5 empty] | A13 | N | 1998-08-17 | 9:35 | 3001.3333 | 9004 | 18008 | 8.27 | 0.59 | 62 | 28.8 | 88 | 85 | BMRL | 64 | 3.4 | 0.054 | 1.5882 | 3.675 | 1.55 | 2.125 | 20.8 | 8.25 | 25 | 204.5 | 38 | 24 | 13 | 1.1 | 76.1 | 6.2 | 14 | 8.2 | 1.8 | 1.6 | 4.7 | NA | NA | NA | 31.8 | 36.5 | B13 | N | 1998-06-22 | 9:30 | 1657.25 | 9943.5 | 7.9 | 0.3 | 26.7 | BMRL | 2.5 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C13 | N | 1998-08-17 | 9:20 | 3001.0833 | 9003.25 | 7.6 | 0.13 | 28.8 | BMRL | 1.55 | 0.015 | 0.96774 | 1.8 | 0.75 | 1.05 | 21.6 | 8 | 25 | 34 | 4.8 | 7.3 | 12 | 6.9 | 31 | BMRL | 1.3 | BMRL | 1.5 | 2.6 | 1.1 | NA | NA | NA | 5.4 | 6.5
|  | Hydraulic loading rate1, v (m/hr) | 7.2835 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1998-08-24 | 9:15 | 3169 | 9507 | 19014 | 7.91 | 0.53 | 64 | 28.5 | 93 | 90 | BMRL | 68 | 3.3 | 0.053 | 1.6061 | 3.6 | 1.13 | 2.47 | 20.8 | 8.23 | 25 | 200 | 42 | 27 | 12 | 1.3 | 82.3 | 4.1 | 15 | 9.1 | 1.7 | 1.5 | 5 | NA | NA | NA | 31.4 | 36.4 | B14 | N | 1998-07-01 | 9:30 | 1873.25 | 11239.5 | 7.8 | 0.19 | 27.6 | BMRL | 2.75 | 0.028 | 1.0182 | 1.8 | 0.67 | 1.13 | 20 | 8.3 | 23.4 | 83 | 17 | 18 | 15 | 4 | 54 | BMRL | 2.6 | 3.1 | BMRL | 4.2 | 4.1 | NA | NA | NA | 9.9 | 14 | C14 | N | 1998-08-24 | 9:00 | 3168.75 | 9506.25 | 7.41 | 0.2 | 23 | BMRL | 1.75 | 0.012 | 0.68571 | 1.95 | 0.92 | 1.03 | 21 | 8.08 | 25 | 40.5 | 6.5 | 8.9 | 13 | 6.5 | 34.9 | 3.2 | 1.8 | BMRL | 1.4 | 2.2 | 1.1 | NA | NA | NA | 8.6 | 9.7
Plant Name | NTMWD Wylie Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A15 | N | 1998-09-08 | 9:30 | 3529.25 | 10587.75 | 21175.5 | 7.79 | 0.52 | 86 | 28.2 | 110 | 108 | BMRL | 78 | 4.1 | 0.0545 | 1.3293 | 3.6 | 1.1 | 2.5 | 20.8 | 8.18 | 23.9 | 208.5 | 41 | 27 | 14 | 1.4 | 83.4 | BMRL | 13 | 11 | BMRL | 1.1 | 6.2 | NA | NA | NA | 25.1 | 31.3 | B15 | N | 1998-07-15 | 8:40 | 2208.4167 | 13250.5 | 7.54 | 0.31 | 28.4 | BMRL | 2.55 | 0.023 | 0.90196 | 1.8 | 0.6 | 1.2 | 20 | 8.19 | 23.75 | 73.5 | 15 | 15 | 17 | 4.8 | 51.8 | BMRL | 6.6 | 3.6 | BMRL | 5.1 | 5 | NA | NA | NA | 15.3 | 20.3 | C15 | N | 1998-09-08 | 8:50 | 3528.5833 | 10585.75 | 7.36 | 0.25 | 27.6 | BMRL | 2 | 0.0115 | 0.575 | 1.95 | 0.62 | 1.33 | 20.8 | 7.9 | 23.9 | 37 | 5.5 | 6.7 | 11 | 6.2 | 29.4 | BMRL | 1.1 | BMRL | BMRL | 1.4 | BMRL | NA | NA | NA | 2.5 | 2.5
Treatment Plant Category | Conv |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A16 | N | 1998-09-14 | 9:40 | 3673.4167 | 11020.25 | 22040.5 | 7.85 | 0.51 | 82 | 24.8 | 115 | 113 | BMRL | 73 | 3.65 | 0.052 | 1.4247 | 3.6 | 0.82 | 2.78 | 20.4 | 8.16 | 25 | 199.5 | 39 | 24 | 15 | 2.5 | 80.5 | BMRL | 14 | 8.3 | BMRL | 1.8 | 5.9 | NA | NA | NA | 24.1 | 30 | B16 Avg. | Y | 1998-08-03 | 8:50 | 2664.5833 | 15987.5 | 7.51 | 0.32 | 28.5 | BMRL | 2.2 | 0.026 | 1.1818 | 1.95 | 0.91 | 1.04 | 20 | 8.235 | 25.5 | 80.75 | 14 | 16 | 16.5 | 4.2 | 50.7 | BMRL | 3.5 | 1.05 | BMRL | 2.15 | 3.2 | NA | NA | NA | 6.7 | 9.9 | C16 Avg. | Y | 1998-09-14 | 9:10 | 3672.9167 | 11018.75 | 7.3 | 0.2 | 24.8 | BMRL | 1.625 | 0.011 | 0.67692 | 2.1 | 1.3 | 0.8 | 20.55 | 7.935 | 25 | 41.3 | 6.8 | 8.6 | 12.5 | 7 | 34.9 | BMRL | 2.9 | BMRL | BMRL | 2.2 | 1.7 | NA | NA | NA | 5.1 | 6.8
Process Train Name | Train 2 | 10-Minute EBCT Run | [6 empty] | A17 Avg. | Y | 1998-09-21 | 9:00 | 3840.75 | 11522.25 | 23044.5 | 7.7 | 0.33 | 83.5 | 26.2 | 122.5 | 119 | BMRL | 70 | 3.48 | 0.046 | 1.3218 | 3.6 | 1.33 | 2.27 | 20.8 | 8.1 | 23.75 | 177.8 | 36.5 | 25.5 | 13.5 | 2.4 | 77.9 | BMRL | 12.5 | 7.9 | BMRL | 1.6 | 5.2 | NA | NA | NA | 22 | 27.2 | B17 | N | 1998-08-11 | 9:15 | 2857 | 17142 | 7.5 | 0.29 | 24.2 | BMRL | 2.35 | 0.0225 | 0.95745 | 1.95 | 1 | 0.95 | 21.3 | 8.07 | 24.75 | 62.5 | 10 | 12 | 14 | 5.4 | 41.4 | BMRL | 2.9 | 1 | 1.3 | 2.3 | 1.7 | NA | NA | NA | 7.5 | 9.2 | C17 | N | 1998-09-21 | 9:00 | 3840.75 | 11522.25 | 7.29 | 0.2 | 26.2 | BMRL | 0.9 | 0.008 | 0.88889 | 2.1 | 0.3 | 1.8 | 21 | 7.73 | 23.75 | 30.5 | 3.3 | 3.4 | 6.3 | 7.3 | 20.3 | BMRL | BMRL | BMRL | BMRL | 1.6 | 1.3 | NA | NA | NA | 1.6 | 2.9
ICR Treatment Plant Identification Number | 617 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A18 | N | 1998-10-05 | 8:50 | 4176.5833 | 12529.75 | 25059.5 | 7.78 | 0.39 | 76 | 25.8 | 114 | 110 | BMRL | 65 | 3.05 | 0.0485 | 1.5902 | 3.6 | 1.2 | 2.4 | 20.2 | 8.18 | 23.5 | 170.5 | 27 | 17 | 14 | 1.8 | 59.8 | BMRL | 13 | 9.7 | BMRL | 1.6 | 6 | NA | NA | NA | 24.3 | 30.3 | B18 | N | 1998-08-17 | 9:30 | 3001.25 | 18007.5 | 7.68 | 0.18 | 28.4 | BMRL | 2.6 | 0.0265 | 1.0192 | 1.95 | 0.9 | 1.05 | 20.8 | 8.06 | 25 | 81.5 | 12 | 16 | 15 | 4.1 | 47.1 | 2.9 | 3.8 | 1.2 | 1.6 | 3.1 | 2.5 | NA | NA | NA | 12.6 | 15.1 | C18 | N | 1998-10-05 | 9:30 | 4177.25 | 12531.75 | 7.44 | 0.15 | 25.8 | BMRL | 1.1 | 0.011 | 1 | 2.4 | 1.5 | 0.9 | 20.2 | 8.02 | 23.5 | 38 | 4.8 | 6.9 | 11 | 5.8 | 28.5 | BMRL | 3.7 | BMRL | BMRL | 1.8 | 1.4 | NA | NA | NA | 5.5 | 6.9
PWSID Number of Plant (if assigned) | TX0430044 | Estimated run time, t (days) | 54.2493 | [5 empty] | A19 | N | 1998-10-19 | 9:00 | 4512.75 | 13538.25 | 27076.5 | 8.22 | 0.32 | 73 | 21.8 | 117 | 113 | BMRL | 73 | 3.45 | 0.053 | 1.5362 | 3.6 | 2 | 1.6 | 20 | 8.27 | 24 | 212 | 48 | 32 | 16 | 3.4 | 99.4 | BMRL | 17 | 15 | BMRL | 1.5 | 5.1 | NA | NA | NA | 33.5 | 38.6 | B19 | N | 1998-09-08 | 8:50 | 3528.5833 | 21171.5 | 7.18 | 0.3 | 27.4 | BMRL | 2.5 | 0.0245 | 0.98 | 1.95 | 0.65 | 1.3 | 20.9 | 7.8 | 23.9 | 83.5 | 12 | 16 | 16 | 4.2 | 48.2 | BMRL | 3 | 1.4 | BMRL | 1.8 | 3.2 | NA | NA | NA | 6.2 | 9.4 | C19 | N | 1998-10-19 | 8:50 | 4512.5833 | 13537.75 | 7.51 | 0.2 | 21.7 | BMRL | 1.6 | 0.0155 | 0.96875 | 2.325 | 2 | 0.325 | 20 | 8.12 | 24 | 58 | 5.4 | 12 | 15 | 6.7 | 39.1 | BMRL | 5.2 | 1.6 | BMRL | 2 | 2.1 | NA | NA | NA | 8.8 | 10.9
Historical Minimum Water Temperature (oC) | 5 | Pilot column bed length, l (m) | 1.2139 | [5 empty] | A20 | N | 1998-11-04 | 8:40 | 4896.4167 | 14689.25 | 29378.5 | 8.34 | 0.34 | 61 | 20 | 103 | 98 | BMRL | 79 | 3.6 | 0.058 | 1.6111 | 3.45 | 0.9 | 2.55 | 20.2 | 8.33 | 24.3 | 192.5 | 33 | 22 | 14 | 2.3 | 71.3 | BMRL | 13 | 8.8 | BMRL | 1.8 | 6.5 | NA | NA | NA | 23.6 | 30.1 | B20 | N | 1998-09-14 | 9:30 | 3673.25 | 22039.5 | 7.4 | 0.58 | 24.8 | BMRL | 3.1 | 0.029 | 0.93548 | 2.1 | 0.9 | 1.2 | 20.4 | 8.01 | 25 | 105.5 | 16 | 14 | 16 | 5.5 | 51.5 | BMRL | 5.8 | 2 | BMRL | 2.7 | 3.8 | NA | NA | NA | 10.5 | 14.3 | C20 | N | 1998-11-04 | 8:30 | 4896.25 | 14688.75 | 7.64 | 0.17 | 20 | BMRL | 1.8 | 0.021 | 1.1667 | 2.325 | 1.28 | 1.045 | 20.3 | 8.21 | 24.3 | 62.5 | 7.3 | 9.7 | 16 | 7.3 | 40.3 | BMRL | 3.6 | 1.1 | 1.2 | 3.7 | 2.5 | NA | NA | NA | 9.6 | 12.1
Historical Average Water Temperature (oC) | 19 | Mass GAC required, m (kg) | 10.0274 | [5 empty] | A21 | N | 1998-11-16 | 9:30 | 5185.25 | 15555.75 | 31111.5 | 8.49 | 0.39 | 81 | 23.8 | 115 | 113 | BMRL | 56 | 3.65 | 0.0595 | 1.6301 | 3.45 | 0.9 | 2.55 | 20.6 | 8.38 | 23.5 | 205 | 36 | 21 | 15 | 2 | 74 | BMRL | 16 | 10 | BMRL | 2.3 | 8.4 | NA | NA | NA | 28.3 | 36.7 | B21 | N | 1998-10-19 | 9:00 | 4512.75 | 27076.5 | NA | NA | NA | NA | NA | 0.031 | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C21 | N | 1998-11-16 | 9:30 | 5185.25 | 15555.75 | 7.95 | 0.19 | 23 | BMRL | 2.2 | 0.023 | 1.0455 | 2.325 | 1.08 | 1.245 | 20.6 | 8.27 | 23.5 | 76 | 9.9 | 12 | 17 | 6.3 | 45.2 | BMRL | 5 | 1.3 | BMRL | 3.6 | 3.4 | NA | NA | NA | 9.9 | 13.3
State Approved Plant Capacity (MGD) | 420 | [7 empty] | A22 | N | 1998-11-30 | 9:00 | 5520.75 | 16562.25 | 33124.5 | 8.44 | 0.25 | 87 | 18.1 | 129 | 128 | BMRL | 57 | 3.2 | 0.0575 | 1.7969 | 3.45 | 1 | 2.45 | 20.8 | 8.36 | 24.25 | 196.5 | 44 | 34 | 14 | 2.4 | 94.4 | BMRL | 14 | 6.3 | BMRL | 2.2 | 6.1 | NA | NA | NA | 22.5 | 28.6 | B22 | N | 1998-11-17 | 9:00 | 5208.75 | 31252.5 | NA | NA | NA | NA | NA | 0.0415 | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C22 | N | 1998-11-30 | 9:00 | 5520.75 | 16562.25 | 7.78 | 0.17 | 18.5 | BMRL | 1.7 | 0.024 | 1.4118 | 2.325 | 1.2 | 1.125 | 20.6 | 7.85 | 24.25 | 68 | 9.3 | 16 | 17 | 6.3 | 48.6 | BMRL | 5 | 1.2 | BMRL | 3 | 3.2 | NA | NA | NA | 9.2 | 12.4
|  | 20-Minute EBCT Run | [6 empty] | A23 | N | 1998-12-14 | 9:00 | 5856.75 | 17570.25 | 35140.5 | 8.53 | 0.37 | 98 | 18.6 | 127 | 125 | BMRL | 64 | 3.25 | 0.063 | 1.9385 | 3.45 | 0.7 | 2.75 | 21 | 8.45 | 24.5 | 200 | 33 | 21 | 13 | 1.5 | 68.5 | BMRL | 15 | 9.7 | BMRL | 1.3 | 7.4 | NA | NA | NA | 26 | 33.4 | B23 | N | 1998-11-30 | 9:00 | 5520.75 | 33124.5 | NA | NA | NA | NA | NA | 0.0415 | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | C23 | N | 1998-12-14 | 9:00 | 5856.75 | 17570.25 | 7.96 | 0.24 | 19.2 | BMRL | 1.95 | 0.031 | 1.5897 | 2.325 | 1 | 1.325 | 21 | 8.34 | 24.5 | 86 | 18 | 23 | 17 | 5.2 | 63.2 | BMRL | 6.1 | 3.4 | BMRL | 3.5 | 6.1 | NA | NA | NA | 13 | 19.1
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | A24 | N | 1998-12-28 | 8:45 | 6192.5 | 18577.5 | 37155 | 8.63 | 0.27 | 105 | 9.8 | 146 | 130 | BMRL | nr | 3.5 | 0.069 | 1.9714 | 3.525 | 0.7 | 2.825 | 20.8 | 8.4 | 24.25 | 231 | 80 | 31 | 12 | BMRL | 123 | BMRL | 20 | 12 | BMRL | 1.3 | 6.4 | NA | NA | NA | 33.3 | 39.7 |  |  |  |  | -861584.25 | -5169505.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | C24 | N | 1998-12-28 | 8:30 | 6192.25 | 18576.75 | 8.29 | 0.32 | 14.4 | BMRL | 2.15 | 0.037 | 1.7209 | 2.325 | 1 | 1.325 | 20.9 | 8.33 | 24.25 | 114.5 | 17 | 14 | 16 | 5 | 52 | BMRL | 9.1 | 3.9 | BMRL | 2.1 | 4.7 | NA | NA | NA | 15.1 | 19.8
|  | Estimated run time, t (days) | 108.4986 | [5 empty] | 25A | N | 1999-02-15 | 10:00 | 6597.25 | 19791.75 | 39583.5 | 7.99 | 0.32 | 108 | 18.6 | 148 | 145 | BMRL | 77 | 3.35 | 0.062 | 1.8507 | 3.6 | 1.2 | 2.4 | 20.5 | 8.22 | 23.83 | 226 | 32 | 19 | 11 | 1.1 | 63.1 | BMRL | 17 | 17 | BMRL | 1.9 | 6.7 | NA | NA | NA | 35.9 | 42.6 |  |  |  |  | -861584.25 | -5169505.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | C25 | N | 1999-02-15 | 10:00 | 6597.25 | 19791.75 | 7.97 | 0.21 | 18.8 | BMRL | 2 | 0.0305 | 1.525 | 2.325 | 1.15 | 1.175 | 20.6 | 8.23 | 23.833 | 97.5 | 14 | 15 | 15 | 5.2 | 49.2 | BMRL | 7.7 | 4 | BMRL | 4.8 | 5.3 | NA | NA | NA | 16.5 | 21.8
|  | Pilot column bed length, l (m) | 2.4278 | [5 empty] | 26A | N | 1999-03-01 | 10:00 | 6933.25 | 20799.75 | 41599.5 | 8.05 | 0.41 | 108 | 16 | 152 | 150 | BMRL | NA | 3.65 | 0.0645 | 1.7671 | 3.6 | 1.5 | 2.1 | 20.4 | 8.24 | 23.83 | 227 | 29 | 16 | 11 | BMRL | 56 | BMRL | 17 | 19 | BMRL | 2.2 | 7.9 | NA | NA | NA | 38.2 | 46.1 | [36 empty] | C26 | N | 1999-03-01 | 10:00 | 6933.25 | 20799.75 | 7.71 | 0.21 | 16.5 | BMRL | 2.3 | 0.0275 | 1.1957 | 2.325 | 1.3 | 1.025 | 20.5 | 8.12 | 23.833 | 80.5 | 9.7 | 10 | 14 | 4.9 | 38.6 | BMRL | 4.6 | 2.3 | BMRL | 5.5 | 5.2 | NA | NA | NA | 12.4 | 17.6
|  | Mass GAC required, m (kg) | 20.0548 | [5 empty] | 27A | N | 1999-03-15 | 9:15 | 7268.5 | 21805.5 | 43611 | 8.38 | 0.45 | 111 | 14.8 | 158 | 155 | BMRL | 71 | 3.85 | 0.065 | 1.6883 | 3.45 | 1.1 | 2.35 | 20.4 | 8.35 | 24 | 206.5 | 33 | 19 | 13 | 1.3 | 66.3 | 2 | 17 | 20 | 1.5 | 1.9 | 7.5 | NA | NA | NA | 42.4 | 49.9 | [36 empty] | C27 | N | 1999-03-15 | 9:15 | 7268.5 | 21805.5 | 7.93 | 0.24 | 15.8 | BMRL | 2.3 | 0.0345 | 1.5 | 2.175 | 0.9 | 1.275 | 20.5 | 8.24 | 24 | 99.5 | 14 | 12 | 15 | 3.8 | 44.8 | BMRL | 6.4 | 4.9 | 1.5 | 3.8 | 5.3 | NA | NA | NA | 16.6 | 21.9
[9 empty] | 28A | N | 1999-03-29 | 8:15 | 7603.5 | 22810.5 | 45621 | 8.18 | 0.25 | 109 | 14.2 | 158 | 138 | BMRL | 74 | 3.45 | 0.0545 | 1.5797 | 3.45 | 1.1 | 2.35 | 20.3 | 8.26 | 24 | 201 | 34 | 17 | 12 | 1.9 | 64.9 | BMRL | 13 | 9.6 | BMRL | 2.7 | 8.7 | NA | NA | NA | 25.3 | 34 | [36 empty] | C28 | N | 1999-03-29 | 8:15 | 7603.5 | 22810.5 | 7.83 | 0.16 | 14.7 | BMRL | 2.65 | 0.03 | 1.1321 | 2.175 | 0.95 | 1.225 | 20.3 | 8.2 | 24 | 92 | 13 | 14 | 14 | 5.8 | 46.8 | BMRL | 5.3 | 3.7 | BMRL | 5.9 | 7.7 | NA | NA | NA | 14.9 | 22.6
[9 empty] | 29A | N | 1999-04-15 | 8:15 | 8011.5 | 24034.5 | 48069 | 7.8 | 0.35 | 105 | 18.1 | 155 | 150 | BMRL | 80 | 2.8 | 0.053 | 1.8929 | 3.45 | 1.15 | 2.3 | 20.2 | 8.13 | 25 | 175 | 30 | 21 | 13 | 2.1 | 66.1 | BMRL | 12 | 7 | BMRL | 1.5 | 6.1 | NA | NA | NA | 20.5 | 26.6 | [36 empty] | C29 | N | 1999-04-15 | 8:15 | 8011.5 | 24034.5 | 7.51 | 0.19 | 18.6 | BMRL | 1.9 | 0.025 | 1.3158 | 2.175 | 0.97 | 1.205 | 20.3 | 8.01 | 25 | 76 | 8.7 | 12 | 14 | 5.3 | 40 | BMRL | 3.3 | 1.1 | BMRL | 3.4 | 3.3 | NA | NA | NA | 7.8 | 11.1
[67 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[67 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [26 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [57 empty] | Group D, 3 duplicate effluent samples per run | [18 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A5 | Primary | 1998-05-04 | 9:00 | 480.75 | 1442.25 | 2884.5 | 8.1 | 0.34 | 127 | 22.1 | 156 | 153 | BMRL | 41 | 3 | 0.063 | 2.1 | 14.5 | 1.4 | 13.1 | 20 | 8 | 24 | 247.5 | 46 | 22 | 5.5 | BMRL | 73.5 | BMRL | 20 | 18 | BMRL | BMRL | 5.7 | NA | NA | NA | 38 | 43.7 | B3 | Primary | 1998-04-24 | 9:00 | 240.75 | 1444.5 | 8.18 | 0.26 | 20 | BMRL | BMRL | 0.004 | #VALUE! | 6.7 | 1.1 | 5.6 | 20 | 8.2 | 24 | 28.5 | 3 | 4.2 | 5.4 | 2.9 | 15.5 | BMRL | 1 | BMRL | BMRL | 1.5 | BMRL | NA | NA | NA | 2.5 | 2.5 | C4 | Primary | 1998-04-30 | 9:00 | 384.75 | 1154.25 | 8 | 0.24 | 18.8 | BMRL | 0.65 | 0.001 | 0.15385 | 2.01 | 1.55 | 0.46 | 20 | 8.2 | 24 | BMRL | 5.2 | 1.7 | 1.1 | BMRL | 8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | A5 | Duplicate | 1998-05-04 | 9:00 | 480.75 | 1442.25 | 2884.5 | 8.1 | 0.33 | 126 | 21.8 | 159 | 153 | BMRL | 41 | 2.95 | 0.063 | 2.1356 | 14.5 | 1.4 | 13.1 | 20 | 8 | 24 | 259 | 43 | 17 | 5.5 | BMRL | 65.5 | BMRL | 21 | 18 | BMRL | BMRL | 5.7 | NA | NA | NA | 39 | 44.7 | B3 | Duplicate | 1998-04-24 | 9:00 | 240.75 | 1444.5 | 8.19 | 0.21 | 20 | BMRL | BMRL | 0.0045 | #VALUE! | 6.7 | 1.1 | 5.6 | 20 | 8.2 | 24 | 30 | NR | NR | 5.2 | BMRL | 5.2 | BMRL | 1 | BMRL | BMRL | 2.6 | BMRL | NA | NA | NA | 3.6 | 3.6 | C4 | Duplicate | 1998-04-30 | 9:00 | 384.75 | 1154.25 | 8 | 0.25 | 18.8 | BMRL | 0.6 | 0.0005 | 0.083333 | 2.01 | 1.6 | 0.41 | 20 | 8.2 | 24 | BMRL | 6 | 2 | 1.2 | BMRL | 9.2 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.1 | 1.1
[9 empty] | A5 | Average | --- | --- | --- | --- | --- | 8.1 | 0.335 | 126.5 | 21.95 | 157.5 | 153 | #DIV/0! | 41 | 2.975 | 0.063 | 2.1178 | 14.5 | 1.4 | 13.1 | 20 | 8 | 24 | 253.25 | 44.5 | 19.5 | 5.5 | #DIV/0! | 69.5 | #DIV/0! | 20.5 | 18 | #DIV/0! | #DIV/0! | 5.7 | #DIV/0! | #DIV/0! | #DIV/0! | 38.5 | 44.2 | B3 | Average | --- | --- | --- | --- | 8.185 | 0.235 | 20 | #DIV/0! | #DIV/0! | 0.00425 | #VALUE! | 6.7 | 1.1 | 5.6 | 20 | 8.2 | 24 | 29.25 | 3 | 4.2 | 5.3 | 2.9 | 10.35 | #DIV/0! | 1 | #DIV/0! | #DIV/0! | 2.05 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3.05 | 3.05 | C4 | Average | --- | --- | --- | --- | 8 | 0.245 | 18.8 | #DIV/0! | 0.625 | 0.00075 | 0.11859 | 2.01 | 1.575 | 0.435 | 20 | 8.2 | 24 | #DIV/0! | 5.6 | 1.85 | 1.15 | #DIV/0! | 8.6 | #DIV/0! | 1.1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0.55 | 0.55
[9 empty] | A5 | RPD | --- | --- | --- | --- | --- | 0 | 2.9851 | 0.79051 | 1.3667 | 1.9048 | 0 | #VALUE! | 0 | 1.6807 | 0 | 1.6807 | 0 | 0 | 0 | 0 | 0 | 0 | 4.541 | 6.7416 | 25.641 | 0 | #VALUE! | 11.5108 | #VALUE! | 4.878 | 0 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 2.5974 | 2.2624 | B3 | RPD | --- | --- | --- | --- | 0.12217 | 21.2766 | 0 | #VALUE! | #VALUE! | 11.7647 | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 5.1282 | #VALUE! | #VALUE! | 3.7736 | #VALUE! | 99.5169 | #VALUE! | 0 | #VALUE! | #VALUE! | 53.6585 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 36.0656 | 36.0656 | C4 | RPD | --- | --- | --- | --- | 0 | 4.0816 | 0 | #VALUE! | 8 | 66.6667 | 59.4595 | 0 | 3.1746 | 11.4943 | 0 | 0 | 0 | #VALUE! | 14.2857 | 16.2162 | 8.6957 | #VALUE! | 13.9535 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | 200
[9 empty] | A10 | Primary | 1998-07-15 | 9:30 | 2209.25 | 6627.75 | 13255.5 | 7.95 | 0.46 | 62 | 28.8 | 90 | 88 | BMRL | 70 | 4.4 | 0.0555 | 1.2614 | 12.5 | 1 | 11.5 | 20 | 8 | 23.75 | 196 | 50 | 28 | 13 | 1 | 92 | BMRL | 18 | 14 | BMRL | 3.6 | 7.2 | NA | NA | NA | 35.6 | 42.8 | B12 | Primary | 1998-06-15 | 9:15 | 1489 | 8934 | 7.8 | 0.22 | 24.6 | BMRL | 2.15 | 0.027 | 1.2558 | 5.75 | 0.8 | 4.95 | 20 | 8 | 23.25 | NA | 14 | 13 | 13 | 3.4 | 43.4 | BMRL | 2.3 | 3.4 | BMRL | 3.2 | 3.1 | NA | NA | NA | 8.9 | 12 | C11 | Primary | 1998-07-27 | 9:00 | 2496.75 | 7490.25 | 7.66 | 0.15 | 29 | BMRL | 1.35 | 0.008 | 0.59259 | 1.65 | 1.2 | 0.45 | 20 | 8 | 25 | 29.5 | 3.3 | 5.5 | 10 | 6.6 | 25.4 | BMRL | 1.7 | BMRL | BMRL | 1 | 1.1 | NA | NA | NA | 2.7 | 3.8
[9 empty] | A10 | Duplicate | 1998-07-15 | 9:30 | 2209.25 | 6627.75 | 13255.5 | 7.94 | 0.52 | 63 | 28.6 | 94 | 92 | BMRL | 71 | 4.05 | 0.055 | 1.358 | 12.5 | 0.98 | 11.52 | 20 | 8 | 23.75 | 193 | 45 | 25 | 12 | 1 | 83 | BMRL | 22 | 16 | BMRL | 3.8 | 8.2 | NA | NA | NA | 41.8 | 50 | B12 | Duplicate | 1998-06-15 | 9:15 | 1489 | 8934 | 7.7 | 0.23 | 24.4 | BMRL | 2.1 | 0.027 | 1.2857 | 5.75 | 0.8 | 4.95 | 20 | 8 | 23.25 | 65.5 | 14 | 14 | 14 | 3.7 | 45.7 | BMRL | 2.8 | 3.4 | BMRL | 3.5 | 3.4 | NA | NA | NA | 9.7 | 13.1 | C11 | Duplicate | 1998-07-27 | 9:00 | 2496.75 | 7490.25 | 7.66 | 0.12 | 28.8 | BMRL | 1.2 | 0.0085 | 0.70833 | 1.65 | 1.3 | 0.35 | 20 | 8 | 25 | 26 | 3.2 | 5.6 | 10 | 6.5 | 25.3 | BMRL | 1.6 | BMRL | BMRL | 1 | 1.1 | NA | NA | NA | 2.6 | 3.7
[9 empty] | A10 | Average | --- | --- | --- | --- | --- | 7.945 | 0.49 | 62.5 | 28.7 | 92 | 90 | #DIV/0! | 70.5 | 4.225 | 0.05525 | 1.3097 | 12.5 | 0.99 | 11.51 | 20 | 8 | 23.75 | 194.5 | 47.5 | 26.5 | 12.5 | 1 | 87.5 | #DIV/0! | 20 | 15 | #DIV/0! | 3.7 | 7.7 | #DIV/0! | #DIV/0! | #DIV/0! | 38.7 | 46.4 |  | Average | --- | --- | --- | --- | 7.75 | 0.225 | 24.5 | #DIV/0! | 2.125 | 0.027 | 1.2708 | 5.75 | 0.8 | 4.95 | 20 | 8 | 23.25 | 65.5 | 14 | 13.5 | 13.5 | 3.55 | 44.55 | #DIV/0! | 2.55 | 3.4 | #DIV/0! | 3.35 | 3.25 | #DIV/0! | #DIV/0! | #DIV/0! | 9.3 | 12.55 | C11 | Average | --- | --- | --- | --- | 7.66 | 0.135 | 28.9 | #DIV/0! | 1.275 | 0.00825 | 0.65046 | 1.65 | 1.25 | 0.4 | 20 | 8 | 25 | 27.75 | 3.25 | 5.55 | 10 | 6.55 | 25.35 | #DIV/0! | 1.65 | #DIV/0! | #DIV/0! | 1 | 1.1 | #DIV/0! | #DIV/0! | #DIV/0! | 2.65 | 3.75
[9 empty] | A10 | RPD | --- | --- | --- | --- | --- | 0.12587 | 12.2449 | 1.6 | 0.69686 | 4.3478 | 4.4444 | #VALUE! | 1.4184 | 8.284 | 0.90498 | 7.3804 | 0 | 2.0202 | 0.17376 | 0 | 0 | 0 | 1.5424 | 10.5263 | 11.3208 | 8 | 0 | 10.2857 | #VALUE! | 20 | 13.3333 | #VALUE! | 5.4054 | 12.987 | #VALUE! | #VALUE! | #VALUE! | 16.0207 | 15.5172 |  | RPD | --- | --- | --- | --- | 1.2903 | 4.4444 | 0.81633 | #VALUE! | 2.3529 | 0 | 2.3529 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 7.4074 | 7.4074 | 8.4507 | 5.1627 | #VALUE! | 19.6078 | 0 | #VALUE! | 8.9552 | 9.2308 | #VALUE! | #VALUE! | #VALUE! | 8.6022 | 8.7649 | C11 | RPD | --- | --- | --- | --- | 0 | 22.2222 | 0.69204 | #VALUE! | 11.7647 | 6.0606 | 17.7936 | 0 | 8 | 25 | 0 | 0 | 0 | 12.6126 | 3.0769 | 1.8018 | 0 | 1.5267 | 0.39448 | #VALUE! | 6.0606 | #VALUE! | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 3.7736 | 2.6667
[9 empty] | A17 | Primary | 1998-09-21 | 9:00 | 3840.75 | 11522.25 | 23044.5 | 7.7 | 0.33 | 84 | 26.2 | 123 | 118 | BMRL | 70 | 3.35 | 0.046 | 1.3731 | 12 | 1.3 | 10.7 | 20 | 8 | 23.75 | 173.5 | 37 | 26 | 14 | 2.4 | 79.4 | BMRL | 12 | 7.1 | BMRL | 1.6 | 4.9 | NA | NA | NA | 20.7 | 25.6 | B16 | Primary | 1998-08-07 | 11:20 | 2763.0833 | 16578.5 | 7.51 | 0.3 | 28.5 | BMRL | 2.3 | 0.026 | 1.1304 | 6.5 | 0.92 | 5.58 | 21.6 | 8 | 25.5 | 81 | 13 | 15 | 16 | 4.1 | 48.1 | BMRL | 3.5 | 1 | BMRL | 2.1 | 3.1 | NA | NA | NA | 6.6 | 9.7 | C16 | Primary | 1998-09-14 | 9:10 | 3672.9167 | 11018.75 | 7.25 | 0.22 | 24.6 | BMRL | 1.8 | 0.011 | 0.61111 | 2.1 | 1.3 | 0.8 | 20 | 8 | 25 | 42.5 | 7.2 | 8.7 | 12 | 6.9 | 34.8 | BMRL | 2.9 | BMRL | BMRL | 2.1 | 1.6 | NA | NA | NA | 5 | 6.6
[9 empty] | A17 | Duplicate | 1998-09-21 | 9:00 | 3840.75 | 11522.25 | 23044.5 | 7.7 | 0.33 | 83 | 26.2 | 122 | 120 | BMRL | 70 | 3.6 | 0.0455 | 1.2639 | 12 | 1.35 | 10.65 | 20 | 8 | 23.75 | 182 | 36 | 25 | 13 | 2.3 | 76.3 | BMRL | 13 | 8.7 | BMRL | 1.6 | 5.5 | NA | NA | NA | 23.3 | 28.8 | B16 | Duplicate | 1998-08-07 | 11:20 | 2763.0833 | 16578.5 | 7.5 | 0.33 | 28.4 | BMRL | 2.1 | 0.0265 | 1.2619 | 6.5 | 0.9 | 5.6 | 24.5 | 8 | 25.5 | 80.5 | 15 | 17 | 17 | 4.3 | 53.3 | BMRL | 3.5 | 1.1 | BMRL | 2.2 | 3.3 | NA | NA | NA | 6.8 | 10.1 | C16 | Duplicate | 1998-09-14 | 9:10 | 3672.9167 | 11018.75 | 7.26 | 0.19 | 24.9 | BMRL | 1.45 | 0.011 | 0.75862 | 2.1 | 1.3 | 0.8 | 20 | 8 | 25 | 40 | 6.4 | 8.5 | 13 | 7 | 34.9 | BMRL | 2.9 | BMRL | BMRL | 2.3 | 1.8 | NA | NA | NA | 5.2 | 7
[10 empty] | Average | --- | --- | --- | --- | --- | 7.7 | 0.33 | 83.5 | 26.2 | 122.5 | 119 | #DIV/0! | 70 | 3.475 | 0.04575 | 1.3185 | 12 | 1.325 | 10.675 | 20 | 8 | 23.75 | 177.75 | 36.5 | 25.5 | 13.5 | 2.35 | 77.85 | #DIV/0! | 12.5 | 7.9 | #DIV/0! | 1.6 | 5.2 | #DIV/0! | #DIV/0! | #DIV/0! | 22 | 27.2 |  | Average | --- | --- | --- | --- | 7.505 | 0.315 | 28.45 | #DIV/0! | 2.2 | 0.02625 | 1.1962 | 6.5 | 0.91 | 5.59 | 23.05 | 8 | 25.5 | 80.75 | 14 | 16 | 16.5 | 4.2 | 50.7 | #DIV/0! | 3.5 | 1.05 | #DIV/0! | 2.15 | 3.2 | #DIV/0! | #DIV/0! | #DIV/0! | 6.7 | 9.9 |  | Average | --- | --- | --- | --- | 7.255 | 0.205 | 24.75 | #DIV/0! | 1.625 | 0.011 | 0.68487 | 2.1 | 1.3 | 0.8 | 20 | 8 | 25 | 41.25 | 6.8 | 8.6 | 12.5 | 6.95 | 34.85 | #DIV/0! | 2.9 | #DIV/0! | #DIV/0! | 2.2 | 1.7 | #DIV/0! | #DIV/0! | #DIV/0! | 5.1 | 6.8
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 1.1976 | 0 | 0.81633 | 1.6807 | #VALUE! | 0 | 7.1942 | 1.0929 | 8.2855 | 0 | 3.7736 | 0.46838 | 0 | 0 | 0 | 4.782 | 2.7397 | 3.9216 | 7.4074 | 4.2553 | 3.982 | #VALUE! | 8 | 20.2532 | #VALUE! | 0 | 11.5385 | #VALUE! | #VALUE! | #VALUE! | 11.8182 | 11.7647 |  | RPD | --- | --- | --- | --- | 0.13324 | 9.5238 | 0.35149 | #VALUE! | 9.0909 | 1.9048 | 10.9909 | 0 | 2.1978 | 0.35778 | 12.5813 | 0 | 0 | 0.6192 | 14.2857 | 12.5 | 6.0606 | 4.7619 | 10.2564 | #VALUE! | 0 | 9.5238 | #VALUE! | 4.6512 | 6.25 | #VALUE! | #VALUE! | #VALUE! | 2.9851 | 4.0404 |  | RPD | --- | --- | --- | --- | 0.13784 | 14.6341 | 1.2121 | #VALUE! | 21.5385 | 0 | 21.5385 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0606 | 11.7647 | 2.3256 | 8 | 1.4388 | 0.28694 | #VALUE! | 0 | #VALUE! | #VALUE! | 9.0909 | 11.7647 | #VALUE! | #VALUE! | #VALUE! | 3.9216 | 5.8824
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[86 empty] | Shut Down |  | 1999-01-04 | 4:30 | 6356.25 | 19068.75 | NA | NA | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[9 empty] | Shut Down | --- | 1999-01-04 | 4:30 | 867940.5 | 2603821.5 | 5207643 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | [36 empty] | Start Up | --- | 1999-02-05 | 9:00 | 6356.25 | 19068.75 | NA | NA | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[9 empty] | Start Up | --- | 1999-02-05 | 9:00 | 6356.25 | 19068.75 | 38137.5 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
Note on B7: Not Avilable. Was blank prior to correction
Note on B14: Not Avilable. Was blank prior to correction
Note on B21: Not Avilable. Was blank prior to correction
Note on E10: Manufacturer's reported bulk density is 27 lbs/ft^3.
Note on K7: Detention times have been added
Note on K8: Detention times have been added
Note on AL9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AM9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AN9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AO9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AP9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AR9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AS9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AT9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AU9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AV9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AW9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on AW10: The data is presented as reported, however, it definitely appears to be an outlier. It is more than three standard deviations greater than the average of all of the measurements.
Note on BN18: Values is "as reported" from laboratory. It appears to be and outlier but there is no known reason to "throw out" the value.
Note on BW9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on BX9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on BX57: Changed to NR because the value is apparently and outlier.
Note on BY9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on BY57: Changed to NR because the value is apparently and outlier.
Note on BZ9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CA9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CC9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CD9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CE9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CF9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CG9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CH9: Changed reading to NR since chlorine residual was less than 0.1 mg/L (as suggested by reviewer).
Note on CY17: Values is "as reported" from laboratory. It appears to be and outlier but there is no known reason to "throw out" the value.
Note on EA12: Value obtained from local engineering firm.
Note on EA13: To be filled in by USEPA (as per conversation with Steve Allgeier)
Note on EA17: Estimated. There are no known fuel oil suppliers in this area.
Note on EA18: Estimate based on local residential customer rates. We are not set up to use natural gas at the treatment plant.