## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Hillsborough Cty. Public Utilities Dept. | Carbon manufacturer | Calgon Carbon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | FL6290388 | Carbon trade name | Filtrasorb 816 | mesh size | (mm) | UV disinfection | Trojen Advantage 5 at 22,000 uW*sec/cm2 | pilot | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 |  |  |  |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 3.3 | 6 | 3.35 |  |  |  | START | --- | 1998-04-27 | 9:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-27 | 9:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-27 | 9:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 146.05 | 8 | 2.36 |  |  |  | 1.1a | N | 1998-04-28 | 8:55 | 23.9167 | 71.75 | 143.5 | 7.55 | 0.2 | 199 | 24.6 | 206 | 179 | 0.39 | 69 | 3.032 | 0.092 | 3.0343 | 9 | 1.39 | 7.61 | 25.1 | 7.51 | 24 | 300 | 53.8 | 11 | 1.42 | BMRL | 66.22 | BMRL | 17.9 | 20.9 | NR | BMRL | 2.6 | NA | NA | NA | 38.8 | 41.4 | 1.1b | N | 1998-04-28 | 8:55 | 23.9167 | 143.5 | 7.61 | 0.15 | 24.6 | 0.4 | BMRL | 0.002 | NR | 6 | 1.35 | 4.65 | 25.1 | 7.25 | 24 | BMRL | 1.21 | BMRL | BMRL | BMRL | 1.21 | BMRL | BMRL | BMRL | NR | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1.1c | N | 1998-04-28 | 8:55 | 23.9167 | 71.75 | 7.59 | 0.15 | 24.6 | 0.39 | BMRL | 0.002 | NR | 1.7 | 1.31 | 0.39 | 25.1 | 7.39 | 24 | BMRL | 1.07 | BMRL | BMRL | BMRL | 1.07 | BMRL | BMRL | BMRL | NR | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 450 | 10 | 2 |  |  |  | 1.2a | N | 1998-05-05 | 9:20 | 192.3333 | 577 | 1154 | 7.54 | 0.16 | 196 | 25.3 | 211 | 158 | 0.36 | 58 | 3.161 | 0.09 | 2.8472 | 10.7 | na | NA | 24.5 | NR | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | 1.2b | N | 1998-05-05 | 9:20 | 192.3333 | 1154 | 7.52 | 0.3 | 25.3 | 0.37 | BMRL | 0.018 | NR | 1.7 | 1.21 | 0.49 | 24.5 | 7.74 | 24 | 27 | 1.64 | BMRL | BMRL | BMRL | 1.64 | BMRL | BMRL | BMRL | NR | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1.2c | N | 1998-05-05 | 9:20 | 192.3333 | 577 | 7.55 | 0.3 | 25.4 | 0.39 | BMRL | 0 | NR | 1.7 | 1.3 | 0.4 | 24.5 | 7.73 | 24 | BMRL | 1.44 | BMRL | BMRL | BMRL | 1.44 | BMRL | BMRL | BMRL | NR | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 30
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | 1.3a | Y | 1998-05-12 | 9:10 | 360.1667 | 1080.5 | 2161 | 7.43 | 0.18 | 192.5 | 24.8 | 202 | 177.5 | 0.32 | 59.5 | 2.914 | 0.093 | 3.1915 | 9 | 1.06 | 7.94 | 25.8 | 7.43 | 24 | 290 | 54.5 | 12.4 | 1.85 | BMRL | 68.75 | 5.13 | 24.3 | 42 | BMRL | BMRL | 2.72 | NA | NA | NA | 71.43 | 74.15 | 1.3b | Y | 1998-05-12 | 9:10 | 360.1667 | 2161 | 7.36 | 0.27 | 24.9 | 0.32 | 1.189 | 0.03 | 2.5645 | 5.5 | 1.55 | 3.95 | 25.8 | 7.5 | 24 | 170 | 27.1 | 23.8 | 4.34 | BMRL | 55.24 | 2.56 | 6.08 | 7.25 | BMRL | BMRL | 1.86 | NA | NA | NA | 15.89 | 17.75 | 1.3c | Y | 1998-05-12 | 9:10 | 360.1667 | 1080.5 | 7.395 | 0.32 | 24.8 | 0.325 | 0.539 | 0.0065 | 1.2086 | 5.5 | 1.57 | NR | 25.8 | 7.39 | 24 | 65 | 7.18 | 29.7 | 5.09 | BMRL | 41.97 | 7.02 | 5.75 | 1.04 | BMRL | BMRL | BMRL | NA | NA | NA | 13.81 | 13.81 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 16 | 16 | 1.18 |  |  |  | 1.4a | N | 1998-05-19 | 9:45 | 528.75 | 1586.25 | 3172.5 | 7.59 | 0.24 | 216 | 25 | 202 | 175 | 0.36 | 41 | 2.807 | 0.095 | 3.3844 | 9 | 1.85 | 7.15 | 26.5 | 7.57 | 24 | NR | 52.3 | 9.04 | BMRL | BMRL | 61.34 | 2.67 | 25.5 | 37.7 | BMRL | BMRL | 3.1 | NA | NA | NA | 65.87 | 68.97 | 1.4b | N | 1998-05-19 | 9:45 | 528.75 | 3172.5 | 7.6 | 0.2 | 25.3 | 0.37 | 1.798 | 0.06 | 3.337 | 7 | 1.58 | 5.42 | 26.5 | 7.54 | 24 | 140 | 23.7 | 9.97 | 3.04 | BMRL | 36.71 | 2.2 | 46.7 | 13.2 | BMRL | BMRL | 3.32 | NA | NA | NA | 62.1 | 65.42 | 1.4c | N | 1998-05-19 | 9:45 | 528.75 | 1586.25 | 7.52 | 0.26 | 25.5 | 0.38 | 0.686 | 0.017 | 2.4781 | 5.5 | 1.86 | 3.64 | 26.5 | 7.55 | 24 | BMRL | 4.38 | 6.27 | 2.75 | BMRL | 13.4 | 2.15 | 42.1 | 1.22 | BMRL | BMRL | BMRL | NA | NA | NA | 45.47 | 45.47 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Flow rate, Q (L/hr) | 123.5 | 20 | 0.85 |  |  |  | 1.5a | N | 1998-05-26 | 9:20 | 696.3333 | 2089 | 4178 | 7.37 | 0.14 | 190 | 25.4 | 203 | 182 | 0.39 | 65 | 2.99 | 0.094 | 3.1438 | 10.5 | NR | #VALUE! | 24.6 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | 1.5b | N | 1998-05-26 | 9:20 | 696.3333 | 4178 | 7.5 | 0.11 | 25.3 | 0.38 | 2.116 | 0.066 | 3.1191 | 9.5 | 1.78 | 7.72 | 24.6 | 7 | 24 | 670 | 39.4 | 43.2 | 3.39 | NR | 85.99 | 21.8 | 37.1 | 39.8 | BMRL | BMRL | 3.34 | NA | NA | NA | 98.7 | 102.04 | 1.5c | N | 1998-05-26 | 9:20 | 696.3333 | 2089 | 7.48 | 0.33 | 25 | 0.37 | 1.552 | 0.038 | 2.4485 | 7 | 0.42 | 6.58 | 24.6 | 7 | 24 | 220 | NR | NR | 1.98 | BMRL | 1.98 | NR | 24.4 | 14 | BMRL | BMRL | 2 | NA | NA | NA | 38.4 | 40.4 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.5
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | 1.6a | N | 1998-06-03 | 9:00 | 888 | 2664 | 5328 | NR | 0.17 | 183 | 25.2 | 208 | 174 | 0.35 | 56 | 2.814 | 0.095 | 3.376 | 9 | 1.5 | 7.5 | 28.7 | 7.54 | 24 | 300 | 71.4 | 16.2 | 6.06 | NR | NR | 6.09 | 35 | 65.1 | BMRL | BMRL | 5.28 | NA | NA | NA | 106.19 | 111.47 | 1.6b | N | 1998-06-03 | 9:00 | 888 | 5328 | nr | 0.12 | 25.6 | 0.35 | 2.373 | 0.076 | 3.2027 | 8 | 1.41 | 6.59 | 28.7 | 7.48 | 24 | 220 | 51.6 | 16.8 | 6.67 | NR | 75.07 | 2.84 | 24.8 | 47.8 | BMRL | BMRL | 5.96 | NA | NA | NA | 75.44 | 81.4 | 1.6c | N | 1998-06-03 | 9:00 | 888 | 2664 | NR | 0.13 | 25.5 | 0.34 | 1.486 | 0.042 | 2.8264 | 7 | 1.4 | 5.6 | 28.7 | 7.48 | 24 | 110 | 29.1 | 18.9 | 8.6 | NR | 56.6 | 3.53 | 12.4 | 21.7 | BMRL | 1.6 | 5.52 | NA | NA | NA | 39.23 | 44.75 | Labor Rate + Fringe ($/work-hour) | 22
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | 1.7a | Y | 1998-06-09 | 9:15 | 1032.25 | 3096.75 | 6193.5 | 7.52 | 0.16 | 185.5 | 25.6 | 209 | 180.5 | 0.325 | 57 | 2.8885 | 0.0895 | 3.0985 | 9 | 1.75 | 7.25 | 30 | 7.52 | 24 | 290 | 73.95 | 13.8 | 2.045 | BMRL | 89.8 | 3.72 | 23.3 | 26.65 | BMRL | BMRL | 3.63 | NA | NA | NA | 51.81 | 55.44 | 1.7b | Y | 1998-06-09 | 9:15 | 1032.25 | 6193.5 | 7.48 | 0.23 | 25.7 | 0.335 | 2.5793 | 0.0725 | 2.811 | 8 | 1.67 | 6.33 | 30 | 7.565 | 24 | 220 | 44.845 | 13.6 | 3.085 | BMRL | 61.53 | 2.8 | 20.95 | 24.4 | BMRL | BMRL | 4.695 | NA | NA | NA | 46.75 | 51.445 | 1.7c | Y | 1998-06-09 | 9:15 | 1032.25 | 3096.75 | 7.45 | 0.18 | 25.7 | 0.33 | 1.4952 | 0.04 | 2.6753 | 7 | 1.57 | 5.43 | 30 | 7.585 | 24 | 130 | 25.53 | 13.135 | 5.23 | BMRL | 43.895 | 2.07 | 13.25 | 14.3 | BMRL | 1.475 | 4.905 | NA | NA | NA | 30.06 | 34.965 | Labor Overhead Factor (% of labor) | 130
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 4596.1227 | 50 | 0.3 |  |  |  | 1.8a | N | 1998-06-18 | 9:30 | 1248.5 | 3745.5 | 7491 | 7.71 | 0.33 | 183 | 25.7 | 209 | 185 | 0.29 | 36 | 2.937 | 0.094 | 3.2005 | 9 | 1.24 | 7.76 | 29.8 | 7.46 | 24 | 310 | 73.2 | 13 | 1.93 | BMRL | 88.13 | 3.08 | 26.5 | 31.7 | BMRL | BMRL | 4.83 | NA | NA | NA | 61.28 | 66.11 | 1.8b | N | 1998-06-18 | 9:30 | 1248.5 | 7491 | 7.56 | 0.28 | 25.8 | 0.3 | 2.433 | 0.076 | 3.1237 | 9 | 1.83 | 7.17 | 29.8 | 7.48 | 24 | 230 | 54.2 | 13.2 | 2.6 | BMRL | 70 | 2.81 | 25.5 | 29.9 | BMRL | BMRL | 4.28 | NA | NA | NA | 58.21 | 62.49 | 1.8c | N | 1998-06-18 | 9:30 | 1248.5 | 3745.5 | 7.5 | 0.17 | 25.9 | 0.31 | 1.7315 | 0.05 | 2.8877 | 7 | 1.25 | 5.75 | 29.8 | 7.48 | 24 | 120 | 26.8 | 12.1 | 4.22 | BMRL | 43.12 | BMRL | 12.9 | 13.2 | BMRL | 1.61 | 4.82 | NA | NA | NA | 27.71 | 32.53 | Electric Rate ($/kW-h) | 0.0662
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 9192.2454 | 60 | 0.25 |  |  |  | 1.9a | N | 1998-06-23 | 9:30 | 1368.5 | 4105.5 | 8211 | 7.3 | 0.18 | 196 | 25.6 | 203 | 187 | 0.42 | 40 | 3.105 | 0.092 | 2.963 | 10 | 1.11 | 8.89 | 30.3 | 7.5 | 24 | 330 | 70.5 | 11.4 | 1.59 | BMRL | 83.49 | 2.51 | 28 | 44.5 | BMRL | BMRL | 3.98 | NA | NA | NA | 75.01 | 78.99 | 1.9b | N | 1998-06-23 | 9:30 | 1368.5 | 8211 | 7.45 | 0.12 | 25.7 | 0.47 | 2.492 | 0.074 | 2.9695 | 9 | 1.73 | 7.27 | 25.7 | 7.65 | 24 | 230 | 50.4 | 11.7 | 2.12 | BMRL | 64.22 | 3.68 | 25.1 | 35.5 | BMRL | BMRL | 3.43 | NA | NA | NA | 64.28 | 67.71 | 1.9c | N | 1998-06-23 | 9:30 | 1368.5 | 4105.5 | 7.4 | 0.14 | 25.6 | 0.35 | 1.7115 | 0.047 | 2.7461 | 8 | 1.64 | 6.36 | 30.3 | 7.61 | 24 | 140 | 26.8 | 11.2 | 3.53 | BMRL | 41.53 | 4.32 | 15 | 18 | BMRL | 1.24 | 3.09 | NA | NA | NA | 38.56 | 41.65 | Fuel Oil Rate ($/gal) | 0.58
|  |  |  | 70 | 0.21 |  |  |  | 1.10a | N | 1998-06-30 | 9:30 | 1536.5 | 4609.5 | 9219 | 7.42 | 0.07 | 189 | 25.7 | NR | 190 | NR | NR | 2.971 | 0.097 | 3.2649 | NR | NR | NA | NR | NR | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1.10b | N | 1998-06-30 | 9:30 | 1536.5 | 9219 | NR | NR | NR | NR | 2.539 | 0.082 | 3.2296 | NR | NR | NR | NR | NR | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1.10c | N | 1998-06-30 | 9:30 | 1536.5 | 4609.5 | NR | NR | NR | NR | 2.015 | 0.07 | 3.4739 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | 1.11a | N | 1998-07-07 | 9:30 | 1704.5 | 5113.5 | 10227 | 7.51 | 0.18 | 185 | 25.7 | 200 | 196 | 0.35 | 39 | 2.953 | 0.092 | 3.1155 | 8.5 | 1.52 | 6.98 | 27.5 | 7.52 | 24 | 260 | 73.6 | 12.2 | 1.74 | BMRL | 87.54 | 2.34 | 23 | 33.6 | BMRL | BMRL | 3.29 | NA | NA | NA | 58.94 | 62.23 | 1.11b | N | 1998-07-07 | 9:30 | 1704.5 | 10227 | 7.5 | 0.2 | 26 | 0.34 | 2.565 | 0.079 | 3.0799 | 7.5 | 1.3 | 6.2 | 27.5 | 7.51 | 24 | 170 | 54.7 | 11.7 | 1.95 | BMRL | 68.35 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | 1.11c | N | 1998-07-07 | 9:30 | 1704.5 | 5113.5 | 7.49 | 0.13 | 26 | 0.35 | 1.9395 | 0.055 | 2.8358 | 7.5 | 1.61 | 5.89 | 27.5 | 7.57 | 24 | 130 | 37.2 | 12.7 | 3.46 | BMRL | 53.36 | BMRL | 16.6 | 16.9 | 1.14 | 1.09 | 4.14 | NA | NA | NA | 35.73 | 39.87 | Current Process Water Rate ($/1000 gal) | 3.5
FAX Number |  | Carbon particle diameter, d (mm) | 1.77 | [5 empty] | 1.12a | Y | 1998-07-14 | 9:30 | 1872.5 | 5617.5 | 11235 | 7.53 | 0.095 | 196.5 | 25.7 | 199.5 | 196.5 | 0.335 | 29.5 | 2.9743 | 0.091 | 3.0598 | 8.5 | 1.415 | 7.085 | 26 | 7.655 | 24 | 320 | 74.7 | 11.7 | 1.515 | BMRL | 87.9 | 2.285 | 22.85 | 34.85 | BMRL | BMRL | 3.335 | NA | NA | NA | 59.985 | 63.32 | 1.12b | Y | 1998-07-14 | 9:30 | 1872.5 | 11235 | 7.48 | 0.04 | 26.1 | 0.365 | 2.6437 | 0.0775 | 2.9318 | 8.5 | 1.765 | 6.735 | 25.9 | 7.54 | 24 | 320 | 63.25 | 11.95 | 1.795 | BMRL | 76.995 | 2.62 | 19.7 | 28.85 | BMRL | BMRL | 3.475 | NA | NA | NA | 49.86 | 53.335 | 1.12c | Y | 1998-07-14 | 9:30 | 1872.5 | 5617.5 | 7.69 | 0.06 | 25.9 | 0.37 | 2.1902 | 0.06 | 2.7396 | 7.5 | 1.835 | 5.665 | 25.9 | 7.69 | 24 | 190 | 39.15 | 11.9 | 2.915 | BMRL | 53.965 | NR | 15.85 | 19.5 | BMRL | BMRL | 3.61 | NA | NA | NA | 35.35 | 38.96 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.016753 | [5 empty] | 1.13a | N | 1998-07-21 | 10:30 | 2041.5 | 6124.5 | 12249 | 7.49 | 0.1 | 182 | 25.3 | 264 | NR | 0.36 | 28 | 2.93 | 0.091 | 3.1058 | 9.5 | 1.27 | 8.23 | 27.8 | 7.6 | 24 | 520 | 76.2 | 15.4 | 2.42 | BMRL | 94.02 | BMRL | 27.5 | 38.6 | BMRL | BMRL | 5.52 | NA | NA | NA | 66.1 | 71.62 | 1.13b | N | 1998-07-21 | 10:30 | 2041.5 | 12249 | 7.47 | 0.04 | 26.2 | 0.34 | 2.472 | 0.081 | 3.2767 | 8.5 | 1.16 | 7.34 | 27.8 | 7.61 | 24 | 450 | 64.1 | 14.4 | 2.5 | BMRL | 81 | 2.18 | 20.9 | 31.8 | BMRL | BMRL | 3.36 | NA | NA | NA | 54.88 | 58.24 | 1.13c | N | 1998-07-21 | 10:30 | 2041.5 | 6124.5 | 7.52 | 0.06 | 26.7 | 0.33 | 2.2805 | 0.069 | 3.0257 | 8.5 | 1.34 | 7.16 | 27.8 | 7.63 | 24 | 510 | 51.6 | 14.1 | 3.14 | BMRL | 68.84 | BMRL | 21.7 | 26.6 | BMRL | 1.33 | 6.19 | NA | NA | NA | 49.63 | 55.82
|  | Hydraulic loading rate1, v (m/hr) | 7.3718 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1.14a | N | 1998-07-28 | 9:30 | 2208.5 | 6625.5 | 13251 | 7.38 | 0.14 | 201 | 25.7 | 282 | NR | 0.33 | 25 | 2.952 | 0.098 | 3.3198 | 10 | 1.87 | 8.13 | 28.7 | 7.52 | 24 | 390 | 78.5 | 12.6 | 1.62 | BMRL | 92.72 | 2.09 | 55 | 47 | BMRL | BMRL | 5.8 | NA | NA | NA | 104.09 | 109.89 | 1.14b | N | 1998-07-28 | 9:30 | 2208.5 | 13251 | 7.4 | 0.18 | 26.1 | 0.32 | 2.54 | 0.082 | 3.2283 | 9 | 2.1 | 6.9 | 28.7 | 7.54 | 24 | 600 | 56.3 | 11.3 | 1.85 | BMRL | 69.45 | BMRL | 22.6 | 32.2 | BMRL | BMRL | 5.01 | NA | NA | NA | 54.8 | 59.81 | 1.14c | N | 1998-07-28 | 9:30 | 2208.5 | 6625.5 | 7.41 | 0.14 | 26.5 | 0.32 | 2.0745 | 0.068 | 3.2779 | 9 | 1.98 | 7.02 | 28.7 | 7.59 | 24 | 580 | 40.2 | 11.3 | 2.63 | BMRL | 54.13 | BMRL | 29.8 | 37.7 | BMRL | BMRL | 5.55 | NA | NA | NA | 67.5 | 73.05
Plant Name | Northwest Potable WTP | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1.15a | N | 1998-08-04 | 9:30 | 2376.5 | 7129.5 | 14259 | 7.41 | 0.22 | 194 | 25.7 | 272 | 188 | 0.4 | 21 | 3.14 | 0.095 | 3.0255 | 10 | 1.89 | 8.11 | 29.4 | 7.43 | 26 | 310 | 80.2 | 11.4 | 1.35 | BMRL | 92.95 | 7.67 | 27.2 | 42.4 | BMRL | BMRL | 4.19 | NA | NA | NA | 77.27 | 81.46 | 1.15b | N | 1998-08-04 | 9:30 | 2376.5 | 14259 | 7.46 | 0.13 | 25.8 | 0.39 | 3.017 | 0.083 | 2.7511 | 9 | 1.72 | 7.28 | 29.4 | 7.22 | 26 | 730 | 71 | 12.6 | 1.82 | BMRL | 85.42 | BMRL | 27.2 | 36.6 | BMRL | BMRL | 4.92 | NA | NA | NA | 63.8 | 68.72 | 1.15c | N | 1998-08-04 | 9:30 | 2376.5 | 7129.5 | 7.52 | 0.14 | 26.1 | 0.38 | 2.1045 | 0.062 | 2.9461 | 8.5 | 1.99 | 6.51 | 29.4 | 7.32 | 26 | 320 | 47.4 | 12.3 | 2.61 | BMRL | 62.31 | 3.7 | 24 | 27.1 | 1.38 | 1.54 | 5.46 | NA | NA | NA | 57.72 | 63.18
Treatment Plant Category | Groundwater |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | 1.16a | N | 1998-08-11 | 9:30 | 2544.5 | 7633.5 | 15267 | 7.39 | 0.15 | 197 | 25.7 | 217 | 183 | 0.38 | 30 | 3.498 | 0.105 | 3.0017 | 10 | 2.6 | 7.4 | 29 | 7.29 | 24 | NR | 84.2 | 13 | 1.66 | BMRL | 98.86 | 7.89 | 27.6 | 44.6 | BMRL | BMRL | 5.06 | NA | NA | NA | 80.09 | 85.15 | 1.16b | N | 1998-08-11 | 9:30 | 2544.5 | 15267 | 7.31 | 0.14 | 25.8 | 0.39 | 3.175 | 0.098 | 3.0866 | 9.5 | 2.42 | 7.08 | 29 | 7.31 | 24 | 580 | 72.6 | 13.2 | 1.93 | BMRL | 87.73 | 7.32 | 27.4 | 43.9 | BMRL | BMRL | 4.83 | NA | NA | NA | 78.62 | 83.45 | 1.16c | N | 1998-08-11 | 9:30 | 2544.5 | 7633.5 | 7.34 | 0.16 | 26.2 | 0.4 | 2.385 | 0.08 | 3.3543 | 8 | 2.46 | 5.54 | 29 | 7.34 | 24 | 250 | 49.8 | 13.1 | 2.82 | BMRL | 65.72 | 5.82 | 20 | 32 | BMRL | 1.02 | 5.14 | NA | NA | NA | 58.84 | 63.98
Process Train Name | Northwest Potable WTP | 10-Minute EBCT Run | [6 empty] | 1.17a | N | 1998-08-18 | 9:30 | 2712.5 | 8137.5 | 16275 | 7.43 | 0.28 | 186 | 25.7 | 212 | 179 | 0.39 | 23 | 2.891 | 0.091 | 3.1477 | 9.5 | 1.4 | 8.1 | 29.4 | 7.48 | 24 | 290 | 75.8 | 11.6 | 1.7 | BMRL | 89.1 | 3.17 | 19.7 | 28.9 | BMRL | BMRL | 3.46 | NA | NA | NA | 51.77 | 55.23 | 1.17b | N | 1998-08-18 | 9:30 | 2712.5 | 16275 | 7.36 | 0.32 | 26.1 | 0.41 | 2.654 | 0.086 | 3.2404 | 8.5 | 1.39 | 7.11 | 29.4 | 7.46 | 24 | 280 | 62.6 | 11.7 | 2.1 | BMRL | 76.4 | 8.45 | 30.8 | 53.8 | BMRL | BMRL | 5.08 | NA | NA | NA | 93.05 | 98.13 | 1.17c | N | 1998-08-18 | 9:30 | 2712.5 | 8137.5 | 7.41 | 0.36 | 26.1 | 0.4 | 2.164 | 0.068 | 3.1423 | 7 | 1.48 | 5.52 | 29.4 | 7.44 | 24 | 270 | 49.9 | 12.4 | 2.79 | BMRL | 65.09 | 2.34 | 13.9 | 19.2 | BMRL | BMRL | 3.74 | NA | NA | NA | 35.44 | 39.18
ICR Treatment Plant Identification Number | 312 | Empty bed contact time, EBCT (min) | 10
PWSID Number of Plant (if assigned) | NA | Estimated run time, t (days) | 63.835
Historical Minimum Water Temperature (oC) | 22 | Pilot column bed length, l (m) | 1.2286
Historical Average Water Temperature (oC) | 23 | Mass GAC required, m (kg) | 9.2625
State Approved Plant Capacity (MGD) | 13.26
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 127.6701
|  | Pilot column bed length, l (m) | 2.4573 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 18.525 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | 1.3a | Primary | 1998-05-12 | 9:10 | 360.1667 | 1080.5 | 2161 | 7.44 | 0.2 | 193 | 24.8 | 202 | 177 | 0.32 | 59 | 2.942 | 0.094 | 3.1951 | 9 | 1.06 | 7.94 | 25.8 | 7.44 | 24 | 290 | 54.5 | 12.4 | 1.85 | BMRL | 68.75 | 5.13 | 24.3 | 42 | BMRL | BMRL | 2.72 | na | na | na | 71.43 | 74.15 | 1.3b | Primary | 1998-05-12 | 9:10 | 360.1667 | 2161 | 7.36 | 0.24 | 24.9 | 0.32 | 1.038 | 0.03 | 2.8902 | 5.5 | 1.55 | 3.95 | 25.8 | 7.5 | 24 | 170 | 27.1 | 23.8 | 4.34 | BMRL | 55.24 | 2.56 | 6.08 | 7.25 | bmrl | bmrl | 1.86 | na | na | na | 15.89 | 17.75 | 1.3c | Primary | 1998-05-12 | 9:10 | 360.1667 | 1080.5 | 7.39 | 0.36 | 24.8 | 0.32 | 0.534 | 0.008 | 1.4981 | 5.5 | 1.57 | 3.93 | 25.8 | 7.39 | 24 | 65 | 7.18 | 29.7 | 5.09 | BMRL | 41.97 | 7.02 | 5.75 | 1.04 | BMRL | BMRL | BMRL | na | na | na | 13.81 | 13.81
[9 empty] | 1.3a-d | Duplicate | 1998-05-12 | 9:10 | 360.1667 | 1080.5 | 2161 | 7.42 | 0.16 | 192 | 24.8 | 202 | 178 | 0.32 | 60 | 2.886 | 0.092 | 3.1878 | 9 | bmrl | nr | 25.8 | 7.42 | 24 | na | na | na | na | na | nr | na | na | na | na | na | na | na | na | na | NR | NR | 1.3b-d | Duplicate | 1998-05-12 | 9:10 | 360.1667 | 2161 | 7.36 | 0.3 | 24.9 | 0.32 | 1.34 | 0.03 | 2.2388 | 5.5 | NR | NR | 25.8 | 7.5 | 24 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | na | na | na | NR | NR | 1.3c-d | Duplicate | 1998-05-12 | 9:10 | 360.1667 | 1080.5 | 7.4 | 0.28 | 24.8 | 0.33 | 0.544 | 0.005 | 0.91912 | 5.5 | -- | NR | 25.8 | 7.39 | 24 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | na | na | na | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 7.43 | 0.18 | 192.5 | 24.8 | 202 | 177.5 | 0.32 | 59.5 | 2.914 | 0.093 | 3.1915 | 9 | 1.06 | 7.94 | 25.8 | 7.43 | 24 | 290 | 54.5 | 12.4 | 1.85 | nr | 68.75 | 5.13 | 24.3 | 42 | nr | nr | 2.72 | na | na | na | 71.43 | 74.15 |  | Average | --- | --- | --- | --- | 7.36 | 0.27 | 24.9 | 0.32 | 1.189 | 0.03 | 2.5645 | 5.5 | 1.55 | 3.95 | 25.8 | 7.5 | 24 | 170 | 27.1 | 23.8 | 4.34 | NR | 55.24 | 2.56 | 6.08 | 7.25 | NR | NR | 1.86 | na | na | na | 15.89 | 17.75 |  | Average | --- | --- | --- | --- | 7.395 | 0.32 | 24.8 | 0.325 | 0.539 | 0.0065 | 1.2086 | 5.5 | 1.57 | NR | 25.8 | 7.39 | 24 | 65 | 7.18 | 29.7 | 5.09 | NR | 41.97 | 7.02 | 5.75 | 1.04 | NR | NR | NR | na | na | na | 13.81 | 13.81
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.26918 | 22.2222 | 0.51948 | 0 | 0 | 0.56338 | 0 | 1.6807 | 1.9218 | 2.1505 | 0.2288 | 0 | nr | nr | 0 | 0.26918 | 0 | nr | nr | nr | nr | nr | nr | nr | nr | nr | nr | nr | nr | na | na | na | NR | NR |  | RPD | --- | --- | --- | --- | 0 | 22.2222 | 0 | 0 | 25.3995 | 0 | 25.3995 | 0 | NR | NR | 0 | 0 | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | na | na | na | NR | NR |  | RPD | --- | --- | --- | --- | 0.13523 | 25 | 0 | 3.0769 | 1.8553 | 46.1538 | 47.9066 | 0 | NR | NR | 0 | 0 | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | na | na | na | NR | NR
[9 empty] | 1.7a | Primary | 1998-06-09 | 9:15 | 1032.25 | 3096.75 | 6193.5 | 7.53 | 0.14 | 182 | 25.6 | 209 | 182 | 0.32 | 60 | 2.866 | 0.089 | 3.1054 | 9 | 1.77 | 7.23 | 30 | 7.53 | 24 | 290 | 74.8 | 14 | 2.07 | BMRL | 90.87 | BMRL | 19.9 | 21 | BMRL | BMRL | 3.01 | na | na | na | 40.9 | 43.91 | 1.7b | Primary | 1998-06-09 | 9:15 | 1032.25 | 6193.5 | 7.48 | 0.22 | 25.7 | 0.33 | 2.6375 | 0.074 | 2.8057 | 8 | 1.71 | 6.29 | 30 | 7.58 | 24 | 220 | 40.4 | 13.2 | 3.13 | BMRL | 56.73 | bmrl | 20.3 | 23.2 | bmrl | bmrl | NR | na | na | na | 43.5 | 43.5 | 1.7c | Primary | 1998-06-09 | 9:15 | 1032.25 | 3096.75 | 7.45 | 0.18 | 25.7 | 0.33 | 1.482 | 0.04 | 2.6991 | 7 | 1.65 | 5.35 | 30 | 7.55 | 24 | 130 | 22 | 12.75 | 5.58 | BMRL | 40.33 | 2.07 | 12 | 12 | BMRL | 1.84 | 4.99 | na | na | na | 27.91 | 32.9
[9 empty] | 1.7a-d | Duplicate | 1998-06-09 | 9:15 | 1032.25 | 3096.75 | 6193.5 | 7.51 | 0.18 | 189 | 25.6 | 209 | 179 | 0.33 | 54 | 2.911 | 0.09 | 3.0917 | 9 | 1.73 | 7.27 | 30 | 7.51 | 24 | na | 73.1 | 13.6 | 2.02 | BMRL | 88.72 | 3.72 | 26.7 | 32.3 | BMRL | BMRL | 4.25 | na | na | na | 62.72 | 66.97 | 1.7b-d | Duplicate | 1998-06-09 | 9:15 | 1032.25 | 6193.5 | 7.48 | 0.24 | 25.7 | 0.34 | 2.521 | 0.071 | 2.8163 | 8 | 1.63 | 6.37 | 30 | 7.55 | 24 | NA | 49.29 | 14 | 3.04 | BMRL | 66.33 | 2.8 | 21.6 | 25.6 | bmrl | bmrl | 4.63 | na | na | na | 50 | 54.63 | 1.7c-d | Duplicate | 1998-06-09 | 9:15 | 1032.25 | 3096.75 | 7.45 | 0.18 | 25.7 | 0.33 | 1.5085 | 0.04 | 2.6516 | 7 | 1.49 | 5.51 | 30 | 7.62 | 24 | na | 29.06 | 13.52 | 4.88 | BMRL | 47.46 | BMRL | 14.5 | 16.6 | BMRL | 1.11 | 4.82 | na | na | na | 32.21 | 37.03
[10 empty] | Average | --- | --- | --- | --- | --- | 7.52 | 0.16 | 185.5 | 25.6 | 209 | 180.5 | 0.325 | 57 | 2.8885 | 0.0895 | 3.0985 | 9 | 1.75 | 7.25 | 30 | 7.52 | 24 | 290 | 73.95 | 13.8 | 2.045 | nr | 89.795 | 3.72 | 23.3 | 26.65 | nr | nr | 3.63 | na | na | na | 51.81 | 55.44 |  | Average | --- | --- | --- | --- | 7.48 | 0.23 | 25.7 | 0.335 | 2.5793 | 0.0725 | 2.811 | 8 | 1.67 | 6.33 | 30 | 7.565 | 24 | 220 | 44.845 | 13.6 | 3.085 | NR | 61.53 | 2.8 | 20.95 | 24.4 | NR | NR | 4.63 | na | na | na | 46.75 | 49.065 |  | Average | --- | --- | --- | --- | 7.45 | 0.18 | 25.7 | 0.33 | 1.4952 | 0.04 | 2.6753 | 7 | 1.57 | 5.43 | 30 | 7.585 | 24 | 130 | 25.53 | 13.135 | 5.23 | NR | 43.895 | 2.07 | 13.25 | 14.3 | NR | 1.475 | 4.905 | na | na | na | 30.06 | 34.965
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.26596 | 25 | 3.7736 | 0 | 0 | 1.662 | 3.0769 | 10.5263 | 1.5579 | 1.1173 | 0.4406 | 0 | 2.2857 | 0.55172 | 0 | 0.26596 | 0 | nr | 2.2989 | 2.8986 | 2.445 | nr | 2.3943 | nr | 29.1845 | 42.4015 | nr | nr | 34.1598 | na | na | na | 42.1154 | 41.5945 |  | RPD | --- | --- | --- | --- | 0 | 8.6957 | 0 | 2.9851 | 4.5168 | 4.1379 | 0.37906 | 0 | 4.7904 | 1.2638 | 0 | 0.39656 | 0 | NR | 19.8238 | 5.8824 | 2.9173 | NR | 15.6021 | NR | 6.2053 | 9.8361 | NR | NR | #VALUE! | na | na | na | 13.9037 | 22.6842 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 1.7723 | 0 | 1.7723 | 0 | 10.1911 | 2.9466 | 0 | 0.92287 | 0 | NR | 27.6537 | 5.8622 | 13.3843 | NR | 16.2433 | NR | 18.8679 | 32.1678 | NR | 49.4915 | 3.4659 | na | na | na | 14.3047 | 11.8118
[9 empty] | 1.12a | Primary | 07/14/98 | 9:30 | 1872.5 | 5617.5 | 11235 | 7.54 | 0.1 | 197 | 25.7 | 199 | 197 | 0.32 | 31 | 3 | 0.091 | 3.0333 | 8.5 | 1.41 | 7.09 | 25.9 | 7.69 | 24 | 320 | 73 | 11.6 | 1.51 | bmrl | 86.11 | 2.23 | 23 | 35.4 | BMRL | BMRL | 3.38 | na | na | na | 60.63 | 64.01 | 1.12b | Primary | 07/14/98 | 9:30 | 1872.5 | 11235 | 7.44 | 0.03 | 26.1 | 0.36 | 2.6235 | 0.078 | 2.9731 | 8.5 | 1.89 | 6.61 | 25.9 | 7.44 | 24 | 320 | 61.1 | 12.1 | 1.92 | BMRL | 75.12 | BMRL | 17.4 | 25.7 | bmrl | bmrl | 3.34 | na | na | na | 43.1 | 46.44 | 1.12c | Primary | 07/14/98 | 9:30 | 1872.5 | 5617.5 | 7.72 | 0.05 | 25.9 | 0.37 | 2.21 | 0.06 | 2.7149 | 7.5 | 2 | 5.5 | 25.9 | 7.72 | 24 | 190 | 40.9 | 12 | 2.84 | BMRL | 55.74 | BMRL | 17.2 | 20.7 | BMRL | BMRL | 3.67 | na | na | na | 37.9 | 41.57
[9 empty] | 1.12a-d | Duplicate | 07/14/98 | 9:30 | 1872.5 | 5617.5 | 11235 | 7.52 | 0.09 | 196 | 25.7 | 200 | 196 | 0.35 | 28 | 2.9485 | 0.091 | 3.0863 | 8.5 | 1.42 | 7.08 | 26.1 | 7.62 | 24 | na | 76.4 | 11.8 | 1.52 | BMRL | 89.72 | 2.34 | 22.7 | 34.3 | BMRL | BMRL | 3.29 | na | na | na | 59.34 | 62.63 | 1.12b-d | Duplicate | 07/14/98 | 9:30 | 1872.5 | 11235 | 7.52 | 0.05 | 26.1 | 0.37 | 2.664 | 0.077 | 2.8904 | 8.5 | 1.64 | 6.86 | 25.9 | 7.64 | 24 | na | 65.4 | 11.8 | 1.67 | BMRL | 78.87 | 2.62 | 22 | 32 | bmrl | bmrl | 3.61 | na | na | na | 56.62 | 60.23 | 1.12c-d | Duplicate | 07/14/98 | 9:30 | 1872.5 | 5617.5 | 7.66 | 0.07 | 25.9 | 0.37 | 2.1705 | 0.06 | 2.7643 | 7.5 | 1.67 | 5.83 | 25.9 | 7.66 | 24 | na | 37.4 | 11.8 | 2.99 | BMRL | 52.19 | BMRL | 14.5 | 18.3 | BMRL | BMRL | 3.55 | na | na | na | 32.8 | 36.35
[10 empty] | Average | --- | --- | --- | --- | --- | 7.53 | 0.095 | 196.5 | 25.7 | 199.5 | 196.5 | 0.335 | 29.5 | 2.9743 | 0.091 | 3.0598 | 8.5 | 1.415 | 7.085 | 26 | 7.655 | 24 | 320 | 74.7 | 11.7 | 1.515 | nr | 87.915 | 2.285 | 22.85 | 34.85 | nr | nr | 3.335 | na | na | na | 59.985 | 63.32 |  | Average | --- | --- | --- | --- | 7.48 | 0.04 | 26.1 | 0.365 | 2.6437 | 0.0775 | 2.9318 | 8.5 | 1.765 | 6.735 | 25.9 | 7.54 | 24 | 320 | 63.25 | 11.95 | 1.795 | NR | 76.995 | 2.62 | 19.7 | 28.85 | NR | NR | 3.475 | na | na | na | 49.86 | 53.335 |  | Average | --- | --- | --- | --- | 7.69 | 0.06 | 25.9 | 0.37 | 2.1902 | 0.06 | 2.7396 | 7.5 | 1.835 | 5.665 | 25.9 | 7.69 | 24 | 190 | 39.15 | 11.9 | 2.915 | NR | 53.965 | NR | 15.85 | 19.5 | NR | NR | 3.61 | na | na | na | 35.35 | 38.96
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.2656 | 10.5263 | 0.50891 | 0 | 0.50125 | 0.50891 | 8.9552 | 10.1695 | 1.7315 | 0 | 1.7315 | 0 | 0.70671 | 0.14114 | 0.76923 | 0.91444 | 0 | nr | 4.5515 | 1.7094 | 0.66007 | nr | 4.1062 | 4.814 | 1.3129 | 3.1564 | nr | nr | 2.6987 | na | na | na | 2.1505 | 2.1794 |  | RPD | --- | --- | --- | --- | 1.0695 | 50 | 0 | 2.7397 | 1.5319 | 1.2903 | 2.8221 | 0 | 14.1643 | 3.712 | 0 | 2.6525 | 0 | NR | 6.7984 | 2.5105 | 13.9276 | NR | 4.8704 | NR | 23.3503 | 21.8371 | NR | NR | 7.7698 | na | na | na | 27.1159 | 25.8554 |  | RPD | --- | --- | --- | --- | 0.78023 | 33.3333 | 0 | 0 | 1.8034 | 0 | 1.8034 | 0 | 17.9837 | 5.8252 | 0 | 0.78023 | 0 | NR | 8.94 | 1.6807 | 5.1458 | NR | 6.5783 | NR | 17.0347 | 12.3077 | NR | NR | 3.3241 | na | na | na | 14.4272 | 13.3984
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AM13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AN13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AO13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AP13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AR13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AS13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AT13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AU13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AV13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on AW13: Reviewer M.H. (10/11/99): Reviewer changed DBP results to NR since chlorine residual was changed to NR by consultant.
Note on BA49: M.H. (8/5): Consultant verified high RPD results.
Note on BB49: M.H. (8/5): Consultant verified high RPD results.
Note on BN45: M.H. (8/5): Consultant verified high RPD results.
Note on BT17: M.H. (8/5): Consultant verified chlorination temperature drop.
Note on BY11: M.H. (8/5): Consultant verified result.
Note on BY13: M.H. (8/5): Consultant verified result.
Note on CC13: M.H. (8/5): Consultant verified result.
Note on CD12: M.H. (8/5): Consultant verified result.
Note on CD13: M.H. (8/5): Consultant verified result.
Note on CD53: M.H. (8/5): Consultant verified high RPD results.
Note on CE13: M.H. (8/5): Consultant verified result.
Note on CE14: M.H. (8/5): Consultant verified result.
Note on CE53: M.H. (8/5): Consultant verified high RPD results.
Note on CV9: M.H. (8/5): Consultant verified high effluent turbidity values, relative to influent turbidity values.
Note on DO12: M.H. (8/5): Consultant verified result.
Note on DO13: M.H. (8/5): Consultant verified result.

## Sheet2. 2nd Pilot Study
FIELD-SET 2: RESULTS FROM 2nd PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 2-3: Pretreatment Used Prior To GAC1 |  |  | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 2-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 2-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 2-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 2-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 2-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 2-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Hillsborough Cty. Public Utilities Dept. | Carbon manufacturer | Calgon Carbon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | FL6290388 | Carbon trade name | Filtrasorb 816 | mesh size | (mm) | UV disinfection | Trojen Advantage 5 and 44,000 uW*sec/cm2 | pilot | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 |  |  |  |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 3.3 | 6 | 3.35 |  |  |  | START | --- | 1998-09-13 | 10:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-09-13 | 10:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-09-13 | 10:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 146.05 | 8 | 2.36 |  |  |  | 2.1a | N | 1998-09-14 | 10:00 | 24 | 72 | 144 | 7.22 | 0.45 | 194 | 25 | 212 | 180 | 0.3 | 57 | 2.832 | 0.092 | 3.2486 | 9.5 | 1.52 | 7.98 | 28.2 | 7.4 | 24 | 290 | 92 | 19 | 3 | BMRL | 114 | BMRL | 35 | 39.6 | BMRL | BMRL | 5.9 | NA | NA | NA | 74.6 | 80.5 | 2.1b | N | 1998-09-14 | 10:00 | 24 | 144 | 7.16 | 0.26 | 26 | 0.31 | 0.3985 | 0.011 | 2.7604 | 3.5 | 0.38 | 3.12 | 28.2 | 7.42 | 24 | BMRL | 3 | 5 | 6 | 1 | 15 | BMRL | 28.7 | 32.8 | BMRL | BMRL | 4.83 | NA | NA | NA | 61.5 | 66.33 | 2.1c | N | 1998-09-14 | 10:00 | 24 | 72 | 7.17 | 0.28 | 26 | 0.31 | 0.25 | 0.000 | 0 | 3.5 | 0.51 | 2.99 | 28.2 | 7.46 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BCAA* | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 450 | 10 | 2 |  |  |  | 2.2a | N | 1998-09-17 | 9:00 | 95 | 285 | 570 | 7.62 | 0.44 | 202 | 25.7 | 223 | 188 | 0.33 | 40 | 2.9725 | 0.09 | 3.0278 | 9.5 | 1.79 | 7.71 | 27.2 | 7.61 | 24 | 280 | 99 | 17 | 2 | BMRL | 118 | BMRL | 40.6 | 41 | BMRL | BMRL | 5.12 | NA | NA | NA | 81.6 | 86.72 | 2.2b | N | 1998-09-17 | 9:00 | 95 | 570 | 7.57 | 0.24 | 25.9 | 0.32 | 1.342 | 0.039 | 2.9061 | 6.5 | 2.3 | 4.2 | 27.2 | 7.6 | 24 | 44 | 11 | 9 | 6 | BMRL | 26 | BMRL | 17.6 | 6.12 | BMRL | BMRL | 3.69 | NA | NA | NA | 23.72 | 27.41 | 2.2c | N | 1998-09-17 | 9:00 | 95 | 285 | 7.51 | 0.26 | 25.9 | 0.32 | 0.3495 | 0.000 | 0 | 5 | 1.79 | 3.21 | 27.2 | 7.49 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 5.8 | BMRL | BMRL | BMRL | BCAA* | NA | NA | NA | 5.8 | 5.8 | Construction Contingencies (% of construction costs) | 30
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | 2.3a | n | 1998-09-21 | 9:00 | 191 | 573 | 1146 | 7.46 | 0.41 | 202 | 25.7 | 214 | 190 | 0.36 | NR | 2.97 | 0.098 | 3.2997 | 9 | 1.57 | 7.43 | 27.3 | 7.51 | 24 | 290 | 90 | 9.7 | 0.96 | BMRL | 100.66 | BMRL | 29.3 | 33.7 | BMRL | BMRL | 4.07 | NA | NA | NA | 63 | 67.07 | 2.3b | N | 1998-09-21 | 9:00 | 191 | 1146 | 7.38 | 0.31 | 25.8 | 0.36 | 1.815 | 0.064 | 3.5262 | 6 | 1.49 | 4.51 | 27.3 | 7.47 | 24 | 130 | 31 | 8.4 | 2.2 | BMRL | 41.6 | BMRL | 17.2 | 14.3 | BMRL | BMRL | 4.2 | NA | NA | NA | 49.44 | 49.44 | 2.3c | N | 1998-09-21 | 9:00 | 191 | 573 | 7.39 | 0.27 | 25.8 | 0.35 | 0.509 | 0.011 | 2.1611 | 5 | 1.68 | 3.32 | 27.3 | 7.46 | 24 | 28 | 1.8 | 1.9 | 1.7 | BMRL | 5.4 | BMRL | 7.12 | 1.67 | BMRL | 1.33 | 1.66 | NA | NA | NA | 17.7 | 20.24 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 16 | 16 | 1.18 |  |  |  | 2.4a | NR | 1998-09-28 | 9:30 | 359.5 | 1078.5 | 2157 | 7.36 | 0.08 | 197 | 25.7 | 218 | 184 | 0.38 | 30 | 3.0565 | 0.091 | 2.9773 | 9.5 | 1.59 | 7.91 | 27.1 | 7.47 | 24 | 440 | 62.5 | 9.45 | 1.03 | BMRL | 72.98 | BMRL | 32.8 | 43.4 | BMRL | BMRL | 4 | NA | NA | NA | 76.2 | 80.2 | 2.4b | Y | 1998-09-28 | 9:30 | 359.5 | 2157 | 7.41 | 0.071 | 25.7 | 0.35 | 1.906 | 0.068 | 3.5677 | 6.5 | 1.31 | 5.19 | 27.1 | 7.46 | 24 | 240 | 41 | 10 | 1.5 | BMRL | 52.5 | BMRL | 19.4 | 26 | BMRL | BMRL | 3.91 | NA | NA | NA | 45.4 | 49.31 | 2.4c | Y | 1998-09-28 | 9:30 | 359.5 | 1078.5 | 7.37 | 0.089 | 25.9 | 0.38 | 0.553 | 0.019 | 3.4358 | 5.5 | 1.5 | 4 | 27.1 | 7.35 | 24 | 76 | 8.1 | 5.8 | 4 | BMRL | 17.9 | 2.12 | 11.6 | 6 | BMRL | 2.13 | 3.51 | NA | NA | NA | 21.85 | 25.36 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Flow rate, Q (L/hr) | 123.5 | 20 | 0.85 |  |  |  | 2.5a | N | 1998-10-01 | 9:30 | 431.5 | 1294.5 | 2589 | 7.43 | 0.08 | 195 | 25.7 | 210 | 190 | 0.34 | 29 | 2.941 | 0.085 | 2.8902 | 9 | 1.47 | 7.53 | 27.3 | 7.4 | 24 | 270 | 53 | 8 | 0.89 | BMRL | 61.89 | BMRL | 29 | 39.8 | BMRL | BMRL | 3.92 | NA | NA | NA | 68.8 | 72.72 | 2.5b | N | 1998-10-01 | 9:30 | 431.5 | 2589 | 7.38 | 0.07 | 25.8 | 0.44 | 2.039 | 0.05 | 2.4522 | 7 | 1.47 | 5.53 | 27.3 | 7.41 | 24 | NR | 42 | 8.2 | 1.3 | BMRL | 51.5 | BMRL | 25.3 | 27.6 | BMRL | BMRL | 4.13 | NA | NA | NA | 52.9 | 57.03 | 2.5c | N | 1998-10-01 | 9:30 | 431.5 | 1294.5 | 7.39 | 0.06 | 26 | 0.34 | 0.604 | 0.002 | 0.33113 | 5.5 | 1.43 | 4.07 | 27.3 | 7.35 | 24 | 90 | 5.6 | 4.7 | 3.5 | BMRL | 13.8 | 3 | 8.71 | 4.71 | BMRL | 1.48 | 2.83 | NA | NA | NA | 17.9 | 20.73 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.5
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | 2.6a | N | 1998-10-05 | 10:30 | 528.5 | 1585.5 | 3171 | 7.45 | 0.17 | 188 | 25.6 | 217 | 183 | 0.372 | 42 | 3.1655 | 0.087 | 2.7484 | 9 | 1.64 | 7.36 | 28.3 | 7.41 | 24 | 270 | 86 | 7.4 | 0.83 | BMRL | 94.23 | BMRL | 33.9 | 36 | BMRL | BMRL | 3.44 | NA | NA | NA | 69.9 | 73.34 | 2.6b | N | 1998-10-05 | 10:30 | 528.5 | 3171 | 7.44 | 0.18 | 25.8 | 0.391 | 2.2585 | 0.066 | 2.9223 | 7 | 1.47 | 5.53 | 28.3 | 7.39 | 24 | 180 | 43 | 8.6 | 1.5 | BMRL | 53.1 | BMRL | 32.8 | 25.4 | 1.06 | 1.06 | 4.38 | NA | NA | NA | 60.32 | 64.7 | 2.6c | N | 1998-10-05 | 10:30 | 528.5 | 1585.5 | 7.39 | 0.1 | 26.1 | 0.359 | 0.8985 | 0.013 | 1.4469 | 6 | 1.59 | 4.41 | 28.3 | 7.37 | 24 | 89 | 14 | 8.2 | 3.7 | BMRL | 25.9 | BMRL | NR | 8.77 | BMRL | 1.76 | 4.06 | NA | NA | NA | NR | NR | Labor Rate + Fringe ($/work-hour) | 22
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | 2.7a | N | 1998-10-12 | 9:30 | 695.5 | 2086.5 | 4173 | 7.29 | 0.08 | 196 | 25.7 | 209 | 187 | 0.39 | 41 | 3.2695 | 0.099 | 3.028 | 9.5 | 1.56 | 7.94 | 27.3 | 7.57 | 24 | 260 | 79 | 7.9 | BMRL | BMRL | 86.9 | BMRL | 56.2 | 39.4 | BMRL | BMRL | 3.86 | NA | NA | NA | 95.6 | 99.46 | 2.7b | N | 1998-10-12 | 9:30 | 695.5 | 4173 | 7.33 | 0.1 | 25.7 | 0.386 | 2.465 | 0.077 | 3.1237 | 7.5 | 1.12 | 6.38 | 27.3 | 7.59 | 24 | 150 | 47 | 7.2 | 0.81 | BMRL | 55.01 | BMRL | 27.3 | 22.6 | BMRL | BMRL | 3.92 | NA | NA | NA | 49.9 | 53.82 | 2.7c | N | 1998-10-12 | 9:30 | 695.5 | 2086.5 | 7.35 | 0.04 | 25.9 | 0.378 | 1.7705 | 0.038 | 2.1463 | 6.5 | 1.82 | 4.68 | 27.3 | 7.71 | 24 | 97 | 22 | 7.8 | 1.6 | BMRL | 31.4 | 2.53 | NR | 14.3 | BMRL | BMRL | 3.94 | NA | NA | NA | NR | NR | Labor Overhead Factor (% of labor) | 130
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 4596.1227 | 50 | 0.3 |  |  |  | 2.8a | Y | 1998-10-15 | 9:30 | 767.5 | 2302.5 | 4605 | 7.535 | 0.12 | 190 | 25.7 | 209.5 | 184 | 0.372 | 26 | 2.9497 | 0.093 | 3.1528 | 9 | 1.51 | 7.49 | 27.6 | 7.51 | 24 | 320 | 69.5 | 10.5 | 0.57 | BMRL | 80.57 | BMRL | 27.7 | 31.1 | 3.63 | 37.7 | 3.12 | NA | NA | NA | 64.915 | 66.475 | 2.8b | Y | 1998-10-15 | 9:30 | 767.5 | 4605 | 7.49 | 0.08 | 25.6 | 0.363 | 2.276 | 0.064 | 2.812 | 8.5 | 1.445 | 7.055 | 27.6 | 7.44 | 24 | 260 | 56 | 9.55 | 0.91 | BMRL | 66.46 | BMRL | BMRL | 30.75 | 3.525 | 29.2 | BMRL | NA | NA | NA | 63.475 | 63.475 | 2.8c | Y | 1998-10-15 | 9:30 | 767.5 | 2302.5 | 7.5 | 0.065 | 25.9 | 0.363 | 1.4505 | 0.032 | 2.2061 | 6 | 1.485 | 4.515 | 27.6 | 7.51 | 24 | 180 | 24.5 | 9.5 | 2.5 | BMRL | 36.5 | BMRL | 20.75 | 13.7 | BMRL | 1.56 | 3.825 | NA | NA | NA | 35.23 | 39.055 | Electric Rate ($/kW-h) | 0.0662
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 9192.2454 | 60 | 0.25 |  |  |  | 2.9a | N | 1998-10-19 | 9:30 | 863.5 | 2590.5 | 5181 | 7.47 | 0.1 | 201 | 26.2 | 218 | 190 | 0.381 | 29 | 3.1955 | 0.099 | 3.0981 | 9 | 2.04 | 6.96 | 27.9 | 7.52 | 24 | 470 | 66 | 13 | 1 | BMRL | 80 | BMRL | 66.3 | 37.4 | BMRL | BMRL | 3.62 | NA | NA | NA | 103.7 | 107.32 | 2.9b | N | 1998-10-19 | 9:30 | 863.5 | 5181 | 7.47 | 0.12 | 26.1 | 0.423 | 2.511 | 0.072 | 2.8674 | 8.5 | 2.42 | 6.08 | 27.9 | 7.46 | 24 | 320 | 40 | 12 | 2.1 | BMRL | 54.1 | BMRL | 115 | 24 | BMRL | BMRL | 3.83 | NA | NA | NA | 139 | 142.83 | 2.9c | N | 1998-10-19 | 9:30 | 863.5 | 2590.5 | 7.46 | 0.12 | 26.1 | 0.389 | 1.9145 | 0.047 | 2.4549 | 7 | 2.45 | 4.55 | 27.9 | 7.51 | 24 | 180 | 22 | 11 | 3 | BMRL | 36 | 3.89 | NR | 16.2 | BMRL | BMRL | 3.8 | NA | NA | NA | 20.09 | 23.89 | Fuel Oil Rate ($/gal) | 0.58
|  |  |  | 70 | 0.21 |  |  |  | 2.10a | N | 1998-10-22 | 9:45 | 935.75 | 2807.25 | 5614.5 | 7.52 | 0.1 | 197 | 25.9 | 223 | 186 | 0.374 | 31 | 2.889 | 0.092 | 3.1845 | 8.5 | 2.16 | 6.34 | 25.8 | 7.55 | 24 | 220 | 53 | 12 | 1.7 | BMRL | 66.7 | BMRL | 67 | 31.3 | BMRL | BMRL | 4.59 | NA | NA | NA | 98.3 | 102.89 | 2.10b | N | 1998-10-22 | 9:45 | 935.75 | 5614.5 | 7.5 | 0.05 | 25.9 | 0.338 | 2.527 | 0.074 | 2.9284 | 7.5 | 1.86 | 5.64 | 25.8 | 7.51 | 24 | 190 | 46 | 13 | 2 | BMRL | 61 | BMRL | 41.9 | 25.4 | BMRL | BMRL | 4.48 | NA | NA | NA | 67.3 | 71.78 | 2.10c | N | 1998-10-22 | 9:45 | 935.75 | 2807.25 | 7.41 | 0.14 | 26.1 | 0.351 | 1.922 | 0.06 | 3.1217 | 6 | 1.79 | 4.21 | 25.8 | 7.47 | 24 | 260 | 26 | 10 | 2.6 | BMRL | 38.6 | BMRL | 24.1 | 20 | BMRL | 1.29 | 4.54 | NA | NA | NA | 45.39 | 49.93 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | 2.11a | N | 1998-10-26 | 9:15 | 1031.25 | 3093.75 | 6187.5 | 7.46 | 0.15 | NR | 25.7 | 223 | 189 | 0.37 | 30 | 2.933 | 0.098 | 3.3413 | 8 | 1.43 | 6.57 | 26.5 | 7.49 | 24 | 270 | 65 | 12 | 1.2 | BMRL | 78.2 | BMRL | 27.3 | 38.6 | BMRL | BMRL | 3.56 | NA | NA | NA | 65.9 | 69.46 | 2.11b | N | 1998-10-26 | 9:15 | 1031.25 | 6187.5 | 7.41 | 0.14 | 25.7 | 0.367 | 2.4515 | 0.088 | 3.5896 | 7.5 | 1.72 | 5.78 | 26.5 | 7.61 | 24 | 180 | 40 | 12 | 2.1 | BMRL | 54.1 | BMRL | 25.1 | 28.1 | BMRL | BMRL | 3.75 | NA | NA | NA | 53.2 | 56.95 | 2.11c | N | 1998-10-26 | 9:15 | 1031.25 | 3093.75 | 7.4 | 0.15 | 26.2 | 0.359 | 1.994 | 0.069 | 3.4604 | 6.5 | 1.94 | 4.56 | 26.5 | 7.64 | 24 | 190 | 27 | 13 | 3.4 | BMRL | 43.4 | BMRL | NR | NR | BMRL | BMRL | 3.1 | NA | NA | NA | NR | NR | Current Process Water Rate ($/1000 gal) | 3.5
FAX Number |  | Carbon particle diameter, d (mm) | 1.77 | [5 empty] | 2.12a | N | 1998-10-29 | 9:20 | 1103.3333 | 3310 | 6620 | 7.55 | 0.08 | 195 | 25.7 | 215 | 189 | 0.361 | 37 | 3.0275 | 0.095 | 3.1379 | 8.5 | 1.59 | 6.91 | 27.1 | 7.56 | 24 | 310 | 77 | 13 | 0.94 | BMRL | 90.94 | BMRL | 28.9 | 40 | BMRL | BMRL | 3.25 | NA | NA | NA | 68.9 | 72.15 | 2.12b | N | 1998-10-29 | 9:20 | 1103.3333 | 6620 | 7.47 | 0.04 | 26 | 0.371 | 2.415 | 0.075 | 3.1056 | 7.5 | 1.64 | 5.86 | 27.1 | 7.5 | 24 | 190 | 46 | 11 | 1.8 | BMRL | 58.8 | BMRL | 22.2 | 28.3 | BMRL | BMRL | 3.54 | NA | NA | NA | 50.5 | 54.04 | 2.12c | N | 1998-10-29 | 9:20 | 1103.3333 | 3310 | 7.47 | 0.05 | 26 | 0.357 | 1.93 | 0.073 | 3.7824 | 6 | 1.51 | 4.49 | 27.1 | 7.48 | 24 | 140 | 27 | 13 | 2.7 | BMRL | 42.7 | BMRL | 17 | 16.8 | BMRL | BMRL | 3.46 | NA | NA | NA | 33.8 | 37.26 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.016753 | [5 empty] | 2.13a | Y | 1998-11-02 | 9:15 | 1199.25 | 3597.75 | 7195.5 | 7.505 | 0.12 | 195 | 25.8 | 219.5 | 183 | 0.3535 | 45 | 2.9697 | 0.09 | 3.0306 | 8.5 | 1.825 | 6.675 | 27 | 7.52 | 24 | 310 | 63.5 | 12.5 | 1.7 | BMRL | 77.7 | BMRL | 25.75 | 29.65 | 3.58 | 37.8 | 3.25 | NA | NA | NA | 64.79 | 66.415 | 2.13b | Y | 1998-11-02 | 9:15 | 1199.25 | 7195.5 | 7.475 | 0.0625 | 25.7 | 0.384 | 2.4745 | 0.072 | 2.9097 | 7.5 | 1.6 | 5.9 | 27 | 7.49 | 24 | 240 | 41.5 | 13.5 | 2.75 | BMRL | 57.75 | BMRL | BMRL | 19.45 | 4.39 | 28.25 | BMRL | NA | NA | NA | 52.09 | 52.09 | 2.13c | Y | 1998-11-02 | 9:15 | 1199.25 | 3597.75 | 7.48 | 0.045 | 26.1 | 0.3535 | 1.9027 | 0.0505 | 2.654 | 6.5 | 1.485 | 5.015 | 27 | 7.485 | 24 | 190 | 27 | 13 | 4 | BMRL | 44 | BMRL | 11.335 | 16.75 | BMRL | 1.04 | 4.315 | NA | NA | NA | 28.605 | 32.92
|  | Hydraulic loading rate1, v (m/hr) | 7.3718 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 2.14a | N | 1998-11-05 | 9:30 | 1271.5 | 3814.5 | 7629 | 7.6 | 0.26 | 198 | 26 | 218 | 191 | 0.356 | 51 | 3.063 | 0.094 | 3.0689 | 8.5 | 1.22 | 7.28 | 24.1 | 7.64 | 24 | 260 | 52 | 10 | 1.2 | BMRL | 63.2 | BMRL | 19.3 | 37.8 | BMRL | BMRL | 3.58 | NA | NA | NA | 57.1 | 60.68 | 2.14b | N | 1998-11-05 | 9:30 | 1271.5 | 7629 | 7.51 | 0.12 | 26.1 | 0.37 | 2.814 | 0.077 | 2.7363 | 7.5 | 1.34 | 6.16 | 24.1 | 7.66 | 24 | 200 | 35 | 9.1 | 1.6 | BMRL | 45.7 | BMRL | 15.1 | 27.2 | BMRL | BMRL | 3.7 | NA | NA | NA | 42.3 | 46 | 2.14c | N | 1998-11-05 | 9:30 | 1271.5 | 3814.5 | 7.5 | 0.12 | 26 | 0.365 | 2.0915 | 0.047 | 2.2472 | 6.5 | 1.52 | 4.98 | 24.1 | 7.63 | 24 | 140 | 20 | 9.8 | 2.6 | BMRL | 32.4 | BMRL | 11.2 | 17.5 | BMRL | BMRL | 3.78 | NA | NA | NA | 28.7 | 32.48
Plant Name | Northwest Potable WTP | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 2.15a | N | 1998-11-12 | 9:20 | 1439.3333 | 4318 | 8636 | 7.59 | 0.25 | 199 | 25.7 | 220 | 198 | 0.373 | 55 | 2.9675 | 0.09 | 3.0329 | 8 | 1.69 | 6.31 | 26.7 | 7.61 | 24 | 300 | 53 | 11 | 1.3 | BMRL | 65.3 | 2.68 | 18.5 | 22.4 | BMRL | BMRL | 2.88 | NA | NA | NA | 43.58 | 46.46 | 2.15b | N | 1998-11-12 | 9:20 | 1439.3333 | 8636 | 7.53 | 0.13 | 25.9 | 0.36 | 2.567 | 0.077 | 2.9996 | 7.5 | 1.52 | 5.98 | 26.7 | 7.59 | 24 | 240 | 46 | 12 | 1.8 | BMRL | 59.8 | 2.68 | 12.5 | 20.6 | 1.15 | 1.03 | 3.86 | NA | NA | NA | 37.96 | 41.82 | 2.15c | N | 1998-11-12 | 9:20 | 1439.3333 | 4318 | 7.51 | 0.12 | 26.1 | 0.366 | 1.84 | 0.042 | 2.2826 | 6.5 | 1.44 | 5.06 | 26.7 | 7.6 | 24 | 170 | 33 | 11 | 2.5 | BMRL | 46.5 | 2.68 | 12.5 | 13.4 | 1.15 | 1.03 | 3.86 | NA | NA | NA | 30.76 | 34.62
Treatment Plant Category | Groundwater |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run.
Process Train Name | Northwest Potable WTP | 10-Minute EBCT Run
ICR Treatment Plant Identification Number | 312 | Empty bed contact time, EBCT (min) | 10
PWSID Number of Plant (if assigned) | NA | Estimated run time, t (days) | 63.835
Historical Minimum Water Temperature (oC) | 22 | Pilot column bed length, l (m) | 1.2286
Historical Average Water Temperature (oC) | 23 | Mass GAC required, m (kg) | 9.2625
State Approved Plant Capacity (MGD) | 13.26
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 127.6701
|  | Pilot column bed length, l (m) | 2.4573 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 18.525 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | 2.4a | Primary | 1998-09-28 | 9:30 | 359.5 | 1078.5 | 2157 | 7.36 | 0.08 | 197 | 25.7 | 218 | 184 | 0.38 | 30 | 3.0565 | 0.091 | 2.9773 | 9.5 | 1.59 | 7.91 | 27.1 | 7.47 | 24 | 440 | 77 | 9 | 0.86 | BMRL | 86.86 | BMRL | 32.8 | 43.4 | BMRL | BMRL | 4 | NA | NA | NA | 76.2 | 80.2 | 2.4b | Primary | 1998-09-28 | 9:30 | 359.5 | 2157 | 7.41 | 0.071 | 25.7 | 0.35 | 1.906 | 0.068 | 3.5677 | 6.5 | 1.31 | 5.19 | 27.1 | 7.46 | 24 | 240 | 41 | 10 | 1.5 | bmrl | 52.5 | bmrl | 19.4 | 26 | BMRL | BMRL | 3.91 | NA | NA | NA | 45.4 | 49.31 | 2.4c | Primary | 1998-09-28 | 9:30 | 359.5 | 1078.5 | 7.37 | 0.089 | 25.9 | 0.38 | 0.553 | 0.019 | 3.4358 | 5.5 | 1.5 | 4 | 27.1 | 7.35 | 24 | 76 | 8.1 | 5.8 | 4 | bmrl | 17.9 | 2.12 | 11.6 | 6 | bmrl | 2.13 | 3.51 | NA | NA | NA | 21.85 | 25.36
[9 empty] | 2.4a-d | Duplicate | 1998-09-28 | 9:30 | 359.5 | 1078.5 | 2157 | 7.36 | 0.08 | 198 | 25.7 | 218 | 185 | NR | NR | NR | 0.091 | NR | 9.5 | 1.64 | 7.86 | 27.1 | NR | 24 | na | 48 | 9.9 | 1.2 | BMRL | 59.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | NR | NR | 2.4b-d | Duplicate | 1998-09-28 | 9:30 | 359.5 | 2157 | 7.41 | 0.071 | 25.7 | nr | nr | nr | NR | 6.5 | 1.43 | 5.07 | 27.1 | NR | 24 | na | 38 | 8.2 | 1.7 | bmrl | 47.9 | bmrl | 23.1 | 22.4 | BMRL | BMRL | 4.07 | NA | NA | NA | 45.5 | 49.57 | 2.4c-d | Duplicate | 1998-09-28 | 9:30 | 359.5 | 1078.5 | 7.37 | 0.089 | 25.9 | nr | nr | nr | NR | 5.5 | 1.61 | 3.89 | 27.1 | NR | 24 | na | 2.2 | 1.9 | 1.5 | bmrl | 5.6 | bmrl | 11.4 | 2.15 | bmrl | bmrl | 1.57 | NA | NA | NA | 13.55 | 15.12
[10 empty] | Average | --- | --- | --- | --- | --- | 7.36 | 0.08 | 197.5 | 25.7 | 218 | 184.5 | 0.38 | 30 | 3.0565 | 0.091 | NR | 9.5 | 1.615 | 7.885 | 27.1 | 7.47 | 24 | 440 | 62.5 | 9.45 | 1.03 | NR | 72.98 | nr | 32.8 | 43.4 | NR | #DIV/0! | 4 | NA | NA | NA | 76.2 | 80.2 |  | Average | --- | --- | --- | --- | 7.41 | 0.071 | 25.7 | 0.35 | 1.906 | 0.068 | NR | 6.5 | 1.37 | 5.13 | 27.1 | 7.46 | 24 | 240 | 39.5 | 9.1 | 1.6 | NR | 50.2 | NR | NR | 24.2 | #DIV/0! | #DIV/0! | NR | NA | NA | NA | 45.45 | 49.44 |  | Average | --- | --- | --- | --- | 7.37 | 0.089 | 25.9 | 0.38 | 0.553 | 0.019 | NR | 5.5 | 1.555 | 3.945 | 27.1 | 7.35 | 24 | 76 | 5.15 | 3.85 | 2.75 | NR | 11.75 | 2.12 | 11.5 | 4.075 | NR | 2.13 | 2.54 | NA | NA | NA | 17.7 | 20.24
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0.50633 | 0 | 0 | 0.54201 | NR | NR | NR | 0 | NR | 0 | 3.096 | 0.63412 | 0 | NR | 0 | NR | 46.4 | 9.5238 | 33.0097 | NR | 38.0378 | nr | NR | nr | NR | NR | NR | NA | NA | NA | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | NR | nr | nr | NR | 0 | 8.7591 | 2.3392 | 0 | NR | 0 | NR | 7.5949 | 19.7802 | 12.5 | NR | 9.1633 | NR | NR | 14.876 | #VALUE! | #VALUE! | NR | NA | NA | NA | 0.22002 | 0.52589 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | NR | NR | NR | NR | 0 | 7.074 | 2.7883 | 0 | NR | 0 | NR | 114.5631 | 101.2987 | 90.9091 | NR | 104.6809 | NR | 1.7391 | 94.4785 | NR | NR | 76.378 | NA | NA | NA | 46.8927 | 50.5929
[9 empty] | 2.8a | Primary | 1998-10-15 | 9:30 | 767.5 | 2302.5 | 4605 | 7.54 | 0.13 | 190 | 25.7 | 209 | 185 | 0.381 | 5.2 | 3.011 | 0.093 | 3.0887 | 9 | 1.49 | 7.51 | 27.6 | 7.51 | 24 | 320 | 63 | 10 | 0.54 | BMRL | 73.54 | BMRL | 26.3 | 33.1 | BMRL | BMRL | 3.12 | NA | NA | NA | 59.4 | 62.52 | 2.8b | Primary | 1998-10-15 | 9:30 | 767.5 | 4605 | 7.49 | 0.08 | 25.6 | 0.366 | 2.276 | 0.064 | 2.812 | 8.5 | 1.55 | 6.95 | 27.6 | 7.44 | 24 | 260 | 55 | 9.4 | 0.87 | bmrl | 65.27 | bmrl | 30.6 | 28.2 | BMRL | BMRL | 3.43 | NA | NA | NA | 58.8 | 62.23 | 2.8c | Primary | 1998-10-15 | 9:30 | 767.5 | 2302.5 | 7.51 | 0.07 | 25.9 | 0.36 | 1.4505 | 0.032 | 2.2061 | 6 | 1.52 | 4.48 | 27.6 | NR | 24 | na | 26 | 10 | 2.4 | bmrl | 38.4 | bmrl | 19 | 12.9 | bmrl | 1.56 | 4.02 | NA | NA | NA | 33.46 | 37.48
[9 empty] | 2.8a-d | Duplicate | 1998-10-15 | 9:30 | 767.5 | 2302.5 | 4605 | 7.53 | 0.11 | 190 | NR | 210 | 183 | 0.363 | 0.047 | 2.8885 | NR | NR | 9 | 1.53 | 7.47 | 27.6 | NR | 24 | na | 76 | 11 | 0.6 | BMRL | 87.6 | BMRL | 29.1 | 37.7 | BMRL | BMRL | 3.63 | NA | NA | NA | 66.8 | 70.43 | 2.8b-d | Duplicate | 1998-10-15 | 9:30 | 767.5 | 4605 | 7.49 | 0.08 | nr | 0.36 | nr | nr | NR | 8.5 | 1.34 | 7.16 | 27.6 | NR | 24 | na | 57 | 9.7 | 0.95 | bmrl | 67.65 | bmrl | 30.9 | 30.2 | BMRL | BMRL | 3.62 | NA | NA | NA | 61.1 | 64.72 | 2.8c-d | Duplicate | 1998-10-15 | 9:30 | 767.5 | 2302.5 | 7.49 | 0.06 | nr | 0.366 | nr | nr | NR | 6 | 1.45 | 4.55 | 27.6 | 7.51 | 24 | 180 | 23 | 9 | 2.6 | bmrl | 34.6 | bmrl | 22.5 | 14.5 | bmrl | bmrl | 3.63 | NA | NA | NA | 37 | 40.63
[10 empty] | Average | --- | --- | --- | --- | --- | 7.535 | 0.12 | 190 | 25.7 | 209.5 | 184 | 0.372 | 2.6235 | 2.9497 | 0.093 | NR | 9 | 1.51 | 7.49 | 27.6 | 7.51 | 24 | 320 | 69.5 | 10.5 | 0.57 | NR | 80.57 | nr | 27.7 | 35.4 | #DIV/0! | #DIV/0! | 3.375 | NA | NA | NA | 63.1 | 66.475 |  | Average | --- | --- | --- | --- | 7.49 | 0.08 | 25.6 | 0.363 | 2.276 | 0.064 | NR | 8.5 | 1.445 | 7.055 | 27.6 | 7.44 | 24 | 260 | 56 | 9.55 | 0.91 | NR | 66.46 | NR | NR | 29.2 | #DIV/0! | #DIV/0! | NR | NA | NA | NA | 59.95 | 63.475 |  | Average | --- | --- | --- | --- | 7.5 | 0.065 | 25.9 | 0.363 | 1.4505 | 0.032 | NR | 6 | 1.485 | 4.515 | 27.6 | 7.51 | 24 | 180 | 24.5 | 9.5 | 2.5 | NR | 36.5 | NR | 20.75 | 13.7 | NR | 1.56 | 3.825 | NA | NA | NA | 35.23 | 39.055
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.13271 | 16.6667 | 0 | NR | 0.47733 | 1.087 | 4.8387 | 196.417 | 4.1529 | NR | NR | 0 | 2.649 | 0.53405 | 0 | NR | 0 | NR | 18.705 | 9.5238 | 10.5263 | NR | 17.4507 | nr | nr | 12.9944 | NR | NR | NR | NA | NA | NA | 11.7274 | 11.8992 |  | RPD | --- | --- | --- | --- | 0 | 0 | nr | 1.6529 | NR | nr | NR | 0 | 14.5329 | 2.9766 | 0 | NR | 0 | NR | 3.5714 | 3.1414 | 8.7912 | NR | 3.5811 | NR | NR | 6.8493 | #VALUE! | #VALUE! | NR | NA | NA | NA | 3.8365 | 3.9228 |  | RPD | --- | --- | --- | --- | 0.26667 | 15.3846 | NR | 1.6529 | NR | NR | NR | 0 | 4.7138 | 1.5504 | 0 | NR | 0 | NR | 12.2449 | 10.5263 | 8 | NR | 10.411 | NR | 16.8675 | 11.6788 | NR | NR | 10.1961 | NA | NA | NA | 10.0483 | 8.0655
[9 empty] | 2.12a-d | Primary | 1998-11-02 | 9:15 | 1199.25 | 3597.75 | 7195.5 | 7.5 | 0.12 | 194 | 25.8 | 220 | 183 | 0.351 | 4.4 | 2.9675 | 0.09 | 3.0329 | 8.5 | 1.85 | 6.65 | 27 | 7.52 | 24 | 310 | 60 | 13 | 1.7 | BMRL | 74.7 | BMRL | 26 | 39.9 | BMRL | BMRL | 4.51 | NA | NA | NA | 65.9 | 70.41 | 2.12b-d | Primary | 1998-11-02 | 9:15 | 1199.25 | 7195.5 | 7.47 | 0.065 | 25.7 | 0.374 | 2.472 | 0.072 | 2.9126 | 7.5 | 1.61 | 5.89 | 27 | 7.49 | 24 | 240 | 40 | 13 | 2.9 | bmrl | 55.9 | bmrl | 20.7 | 26.3 | BMRL | BMRL | 4.37 | NA | NA | NA | 47 | 51.37 | 2.12c-d | Primary | 1998-11-02 | 9:15 | 1199.25 | 3597.75 | 7.48 | 0.045 | 26.1 | 0.344 | 1.896 | 0.05 | 2.6371 | 6.5 | 1.47 | 5.03 | 27 | 7.49 | 24 | 190 | 20 | 11 | 4.1 | bmrl | 35.1 | bmrl | 9.97 | 15.1 | bmrl | 1.04 | 4.28 | NA | NA | NA | 26.11 | 30.39
[9 empty] | 2.12a | Duplicate | 1998-11-02 | 9:15 | 1199.25 | 3597.75 | 7195.5 | 7.51 | 0.12 | 196 | NR | 219 | 183 | 0.356 | 4.5 | 2.972 | 0.09 | 3.0283 | 8.5 | 1.8 | 6.7 | 27 | 7.52 | 24 | na | 67 | 12 | 1.7 | BMRL | 80.7 | BMRL | 22.6 | 42.3 | BMRL | BMRL | 4.38 | NA | NA | NA | 64.9 | 69.28 | 2.12b-d | Duplicate | 1998-11-02 | 9:15 | 1199.25 | 7195.5 | 7.48 | 0.06 | nr | 0.394 | 2.477 | 0.072 | 2.9067 | 7.5 | 1.59 | 5.91 | 27 | 7.49 | 24 | na | 43 | 14 | 2.6 | bmrl | 59.6 | bmrl | 18.2 | 30.2 | BMRL | BMRL | 4.41 | NA | NA | NA | 48.4 | 52.81 | 2.12c | Duplicate | 1998-11-02 | 9:15 | 1199.25 | 3597.75 | 7.48 | 0.045 | nr | 0.363 | 1.9095 | 0.051 | 2.6709 | 6.5 | 1.5 | 5 | 27 | 7.48 | 24 | na | 34 | 15 | 3.9 | bmrl | 52.9 | bmrl | 12.7 | 18.4 | bmrl | bmrl | 4.35 | NA | NA | NA | 31.1 | 35.45
[10 empty] | Average | --- | --- | --- | --- | --- | 7.505 | 0.12 | 195 | 25.8 | 219.5 | 183 | 0.3535 | 4.45 | 2.9697 | 0.09 | 3.0306 | 8.5 | 1.825 | 6.675 | 27 | 7.52 | 24 | 310 | 63.5 | 12.5 | 1.7 | NR | 77.7 | nr | 24.3 | 41.1 | #DIV/0! | #DIV/0! | 4.445 | NA | NA | NA | 65.4 | 69.845 |  | Average | --- | --- | --- | --- | 7.475 | 0.0625 | 25.7 | 0.384 | 2.4745 | 0.072 | 2.9097 | 7.5 | 1.6 | 5.9 | 27 | 7.49 | 24 | 240 | 41.5 | 13.5 | 2.75 | NR | 57.75 | NR | NR | 28.25 | #DIV/0! | #DIV/0! | NR | NA | NA | NA | 47.7 | 52.09 |  | Average | --- | --- | --- | --- | 7.48 | 0.045 | 26.1 | 0.3535 | 1.9027 | 0.0505 | 2.654 | 6.5 | 1.485 | 5.015 | 27 | 7.485 | 24 | 190 | 27 | 13 | 4 | NR | 44 | NR | 11.335 | 16.75 | NR | 1.04 | 4.315 | NA | NA | NA | 28.605 | 32.92
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.13324 | 0 | 1.0256 | NR | 0.45558 | 0 | 1.4144 | 2.2472 | 0.15153 | 0 | 0.15153 | 0 | 2.7397 | 0.74906 | 0 | 0 | 0 | NR | 11.0236 | 8 | 0 | NR | 7.722 | nr | nr | 5.8394 | NR | NR | NR | NA | NA | NA | 1.5291 | 1.6179 |  | RPD | --- | --- | --- | --- | 0.13378 | 8 | NR | 5.2083 | 0.20206 | 0 | 0.20206 | 0 | 1.25 | 0.33898 | 0 | 0 | 0 | NR | 7.2289 | 7.4074 | 10.9091 | NR | 6.4069 | NR | NR | 13.8053 | #VALUE! | #VALUE! | NR | NA | NA | NA | 2.935 | 2.7644 |  | RPD | --- | --- | --- | --- | 0 | 0 | NR | 5.3748 | 0.7095 | 1.9802 | 1.2707 | 0 | 2.0202 | 0.59821 | 0 | 0.1336 | 0 | NR | 51.8519 | 30.7692 | 5 | NR | 40.4545 | NR | 24.0847 | 19.7015 | NR | NR | 1.6222 | NA | NA | NA | 17.4445 | 15.3706
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AL11: M.H. (8/5/99): Consultant verified result.
Note on AL12: M.H. (8/5/99): Consultant verified result.
Note on AL17: M.H. (8/5/99): Consultant verified result.
Note on AM45: M.H. (8/5): Consultant verified high RPD results.
Note on CD9: M.H. (8/5): Consultant verified result.
Note on CE9: M.H. (8/5): Consultant verified result.
Note on CL9: M.H. (8/5): Consultant verified result.
Note on CM9: M.H. (8/5): Consultant verified result.
Note on DI53: M.H. (8/5): Consultant verified high RPD results.
Note on DJ53: M.H. (8/5): Consultant verified high RPD results.
Note on DO53: M.H. (8/5): Consultant verified high RPD results.
Note on DP53: M.H. (8/5): Consultant verified high RPD results.