## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Pinellas County Utilities | Membrane manufacturer | DOW USA, (FilmTec) | Average yearly temperature of feed water, TavgoC (oC) | 24 | Alkalinity (mg/L as CaCO3) | 215 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.55 | [6 empty] | System recovery during sample collection (decimal) | 0.73 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 | [6 empty] | System recovery during sample collection (decimal) | 0.79 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.79 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.77 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.59 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL6521405 | Membrane trade name | NF-70 | Temperature normalized MTCW (gfd/psi) | 0.33981 | Calcium Hardness (mg/L as CaCO3) | 208 | Cartridge filtration | 5 mm exclusion size | Pilot-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 12.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 6.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 12.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 6 | [6 empty] | System feed flow rate during sample collection (gpm) | 12.1 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 7.29 | [6 empty] | System feed flow rate during sample collection (gpm) | 10.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 6.72 | [6 empty] | System feed flow rate during sample collection (gpm) | 12.06 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 7.06 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) |  | Membrane element model number | NF-70, 4040 |  |  | LSI | 0.02 | Sulfuric acid addition | approx. = 110 mg/L to pH = 6.0 | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 12.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.1 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.1 | [6 empty] | System influent flow rate during sample collection (gpm) | 10.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 10.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.06 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.06 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.13 | (or) Flocon 100, anti-scalent | 2 ppm | Pilot-scale | 1989-07-19 |  | 12 | 24 | 130 | 75 | 58 | 0 | 10 | 3 |  | 13 | 13 | 0.76923 | 0 | 20 | 20 | 5.5733 | 38.9267 | 0.51379 | 7.2 | 5.8 | 113 | 264 | 322 | 999 | 1018.6667 | -1.9686 | 64.9068 | 670.3333 | 83.1427 | 130 | 92 | 64 | 6.8 | 6 | 12.8 | 12.8 | 0.34905 | 0.53125 | 20.4 | 20.4 | 3.2273 | 43.7727 | 0.46604 | 5.8 | 6 | 116 | 322 | 584 | 555.4667 | 4.8858 | 63.9752 | 438.7333 | 73.5602 | 92 | 75 | 52 | 2.3 | 3 | 5.3 | 5.3 | 0.30821 | 0.43396 | 13.8 | 13.8 | 5.9622 | 25.5378 | 0.54037 | 6 | 6.1 | 153 | 584 | 999 | 914.4333 | 8.4651 | 52.4845 | 749.2167 | 79.5787 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 250
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.13 |  |  |  | 1989-07-20 |  | 22.8 | 24 | 119 | 68 | 50.5 | 0 | 9 | 3.1 |  | 12.1 | 12.1 | 0.7438 | 0 | 18 | 18 | 5.1239 | 37.8761 | 0.47523 | 7.2 | 5.8 | 113 | 264 | 322 | 999 | 928.7742 | 7.0296 | 64.9068 | 625.3871 | 81.9312 | 119 | 117 | 56 | 6.8 | 5.3 | 12.1 | 12.1 | 0.32306 | 0.56198 | 20.4 | 20.4 | 3.3815 | 58.6185 | 0.34801 | 5.8 | 6 | 116 | 322 | 584 | 586.3019 | -0.39416 | 63.9752 | 454.1509 | 74.4578 | 117 | 68 | 45 | 2.3 | 3.1 | 5.4 | 5.4 | 0.31563 | 0.42593 | 13.8 | 13.8 | 5.9089 | 41.5911 | 0.3318 | 6 | 6.1 | 153 | 584 | 999 | 903.7742 | 9.5321 | 52.4845 | 743.8871 | 79.4324 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1989-07-21 |  | 47.6 | 24 | 120 | 70 | 51.5 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 5.3643 | 38.1357 | 0.49298 | 7.2 | 5.8 | 113 | 264 | 322 | 999 | 976.8667 | 2.2155 | 64.9068 | 649.4333 | 82.6002 | 120 | 98 | 58 | 6.8 | 5.5 | 12.3 | 12.3 | 0.33049 | 0.55285 | 20.4 | 20.4 | 3.3335 | 47.6665 | 0.42797 | 5.8 | 6 | 116 | 322 | 584 | 576.6909 | 1.2516 | 63.9752 | 449.3455 | 74.1847 | 98 | 70 | 45 | 2.3 | 3 | 5.3 | 5.3 | 0.30821 | 0.43396 | 13.8 | 13.8 | 5.9622 | 33.0378 | 0.4177 | 6 | 6.1 | 153 | 584 | 999 | 914.4333 | 8.4651 | 52.4845 | 749.2167 | 79.5787 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | NA |  |  |  | 1989-07-24 |  | 114.9 | 24 | 130 | 75 | 56 | 0 | 10 | 3.3 |  | 13.3 | 13.3 | 0.75188 | 0 | 20 | 20 | 5.2567 | 41.2433 | 0.48493 | 7.2 | 5.8 | 113 | 264 | 322 | 999 | 955.3333 | 4.371 | 64.9068 | 638.6667 | 82.3069 | 130 | 91 | 62 | 6.8 | 5.9 | 12.7 | 12.7 | 0.34534 | 0.53543 | 20.4 | 20.4 | 3.2471 | 45.2529 | 0.4508 | 5.8 | 6 | 116 | 322 | 584 | 559.4237 | 4.2083 | 63.9752 | 440.7119 | 73.6789 | 91 | 75 | 50 | 2.3 | 3.3 | 5.6 | 5.6 | 0.33049 | 0.41071 | 13.8 | 13.8 | 5.812 | 27.188 | 0.50758 | 6 | 6.1 | 153 | 584 | 999 | 884.3939 | 11.4721 | 52.4845 | 734.197 | 79.1609 | Sampling date | MM/DD/YY | 725/89 | 1989-07-25 | 1989-07-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-07-25 | 1989-07-25 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-09-07 | 1989-09-07 | 1989-09-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-09-07 | 1989-09-07 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-09-27 | 1989-09-27 | 1989-09-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-09-27 | 1989-09-27 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-11-02 | 1989-11-02 | 1989-11-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1989-11-02 | 1989-11-02 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-01-10 | 1990-01-10 | 1990-01-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-01-10 | 1990-01-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.2 |  |  |  | 1989-07-25 |  | 137.4 | 24 | 130 | 75 | 55 | 0 | 9.5 | 3 |  | 12.5 | 12.5 | 0.76 | 0 | 19 | 19 | 5.3992 | 42.1008 | 0.4513 | 7.2 | 5.8 | 113 | 264 | 322 | 999 | 983.8333 | 1.5182 | 64.9068 | 652.9167 | 82.693 | 130 | 92 | 60 | 6.8 | 5.5 | 12.3 | 12.3 | 0.33049 | 0.55285 | 20.4 | 20.4 | 3.3335 | 47.6665 | 0.42797 | 5.8 | 6 | 116 | 322 | 584 | 576.6909 | 1.2516 | 63.9752 | 449.3455 | 74.1847 | 92 | 75 | 50 | 2.3 | 3 | 5.3 | 5.3 | 0.30821 | 0.43396 | 13.8 | 13.8 | 5.9622 | 27.5378 | 0.50113 | 6 | 6.1 | 153 | 584 | 999 | 914.4333 | 8.4651 | 52.4845 | 749.2167 | 79.5787 | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | NA |  |  |  | 1989-07-26 |  | 163.4 | 24 | 130 | 75 | 57.5 | 0 | 9.8 | 3.5 |  | 13.3 | 13.3 | 0.73684 | 0 | 19.6 | 19.6 | 4.08 | 40.92 | 0.47898 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 776 | 16.1081 | 56.6667 | 538 | 75.8364 | 130 | 92 | 64 | 6.8 | 5.8 | 12.6 | 12.6 | 0.34163 | 0.53968 | 20.4 | 20.4 | 3.2359 | 43.7641 | 0.46614 | 6.4 | 6.4 | 96 | 300 | 627 | 539.1724 | 14.0076 | 68 | 419.5862 | 77.1203 | 92 | 75 | 51 | 2.3 | 3.5 | 5.8 | 5.8 | 0.34534 | 0.39655 | 13.8 | 13.8 | 5.394 | 27.106 | 0.50911 | 6.4 | 6.6 | 221 | 627 | 925 | 893.8 | 3.373 | 26.3333 | 760.4 | 70.9363 | Operation time | hh.hh | 137.4 | 137.4 | 137.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 137.4 | 137.4 | --- | --- | --- | --- | Operation time | hh.hh | 1176.2 | 1176.2 | 1176.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1176.2 | 1176.2 | --- | --- | --- | --- | Operation time | hh.hh | 1497.3 | 1497.3 | 1497.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1497.3 | 1497.3 | --- | --- | --- | --- | Operation time | hh.hh | 2339.9 | 2339.9 | 2339.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2339.9 | 2339.9 | --- | --- | --- | --- | Operation time | hh.hh | 3904.4 | 3904.4 | 3904.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3904.4 | 3904.4 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.83333 | Sulfate (mg/L) | 2.2 |  |  |  | 1989-07-27 |  | 182.7 | 24 | 130 | 75 | 56 | 0 | 9.2 | 3 |  | 12.2 | 12.2 | 0.7541 | 0 | 18.4 | 18.4 | 4.3067 | 42.1933 | 0.43609 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 821.3333 | 11.2072 | 56.6667 | 560.6667 | 76.8133 | 130 | 90 | 62 | 5.9 | 5.6 | 11.5 | 11.5 | 0.31749 | 0.51304 | 17.7 | 17.7 | 3.1146 | 44.8854 | 0.39434 | 6.4 | 6.4 | 96 | 300 | 627 | 514.9286 | 17.8742 | 68 | 407.4643 | 76.4397 | 90 | 75 | 50 | 2.1 | 3 | 5.1 | 5.1 | 0.30078 | 0.41176 | 12.6 | 12.6 | 5.481 | 27.019 | 0.46634 | 6.4 | 6.6 | 221 | 627 | 925 | 911.2 | 1.4919 | 26.3333 | 769.1 | 71.2651 | pH | --- | 5.3 | 5.8 | 6.1 | --- | --- | --- | --- | --- | pH | --- | 5.3 | 5.8 | --- | --- | --- | --- | pH | --- | 5.6 | 6.4 | 6.6 | --- | --- | --- | --- | --- | pH | --- | 5.6 | 6.4 | --- | --- | --- | --- | pH | --- | 5.6 | 6 | 6.2 | --- | --- | --- | --- | --- | pH | --- | 5.5 | 6 | --- | --- | --- | --- | pH | --- | 5.8 | 6.2 | 6.6 | --- | --- | --- | --- | --- | pH | --- | 5.8 | 6.2 | --- | --- | --- | --- | pH | --- | 5.2 | 5.9 | 6.3 | --- | --- | --- | --- | --- | pH | --- | 5.4 | 5.9 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.5 | Calcium (mg/L) | 83.2 |  |  |  | 1989-07-28 |  | 207.3 | 24 | 130 | 75 | 56 | 0 | 9.6 | 3 |  | 12.6 | 12.6 | 0.7619 | 0 | 19.2 | 19.2 | 4.42 | 42.08 | 0.45627 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 844 | 8.7568 | 56.6667 | 572 | 77.2727 | 130 | 91 | 62 | 5.9 | 5.3 | 11.2 | 11.2 | 0.30635 | 0.52679 | 17.7 | 17.7 | 3.1755 | 45.3245 | 0.39052 | 6.4 | 6.4 | 96 | 300 | 627 | 527.0943 | 15.9339 | 68 | 413.5472 | 76.7862 | 91 | 75 | 50 | 2.1 | 3 | 5.1 | 5.1 | 0.30078 | 0.41176 | 12.6 | 12.6 | 5.481 | 27.519 | 0.45787 | 6.4 | 6.6 | 221 | 627 | 925 | 911.2 | 1.4919 | 26.3333 | 769.1 | 71.2651 | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5 | Barium (mg/L) | NA |  |  |  | 1989-07-29 |  | 234.4 | 24 | 130 | 75 | 55.5 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 4.3633 | 42.6367 | 0.44094 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 832.6667 | 9.982 | 56.6667 | 566.3333 | 77.0453 | 130 | 90 | 61 | 5.9 | 5.3 | 11.2 | 11.2 | 0.30635 | 0.52679 | 17.7 | 17.7 | 3.1755 | 45.8245 | 0.38626 | 6.4 | 6.4 | 96 | 300 | 627 | 527.0943 | 15.9339 | 68 | 413.5472 | 76.7862 | 90 | 75 | 50 | 2.1 | 3 | 5.1 | 5.1 | 0.30078 | 0.41176 | 12.6 | 12.6 | 5.481 | 27.019 | 0.46634 | 6.4 | 6.6 | 221 | 627 | 925 | 911.2 | 1.4919 | 26.3333 | 769.1 | 71.2651 | Alkalinity | mg/L as CaCO3 | 62 | 95 | 180 | 199.5 | -10.8333 | 34.7368 | 147.25 | 57.8947 | Alkalinity | mg/L as CaCO3 | 63 | 95 | 134.5636 | 33.6842 | 114.7818 | 45.1133 | Alkalinity | mg/L as CaCO3 | 72 | 159 | 346 | 394.2222 | -13.9371 | 54.717 | 276.6111 | 73.9707 | Alkalinity | mg/L as CaCO3 | 53 | 159 | 274.6364 | 66.6667 | 216.8182 | 75.5556 | Alkalinity | mg/L as CaCO3 | 89 | 158 | 220 | 417.5714 | -89.8052 | 43.6709 | 287.7857 | 69.0742 | Alkalinity | mg/L as CaCO3 | 29 | 158 | 353.5114 | 81.6456 | 255.7557 | 88.6611 | Alkalinity | mg/L as CaCO3 | 40 | 95 | 278 | 301.9048 | -8.5988 | 57.8947 | 198.4524 | 79.844 | Alkalinity | mg/L as CaCO3 | 28 | 95 | 205.3529 | 70.5263 | 150.1765 | 81.3553 | Alkalinity | mg/L as CaCO3 | 40 | 120 | 380 | 387.8261 | -2.0595 | 66.6667 | 253.913 | 84.2466 | Alkalinity | mg/L as CaCO3 | 28 | 120 | 249.904 | 76.6667 | 184.952 | 84.8609 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.075
Mailing Address |  | Design flux, FW (gfd) | 15 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.5 | Strontium (mg/L) | NA |  |  |  | 1989-07-30 |  | 256.8 | 24 | 130 | 75 | 56 | 0 | 9.2 | 3 |  | 12.2 | 12.2 | 0.7541 | 0 | 18.4 | 18.4 | 4.3067 | 42.1933 | 0.43609 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 821.3333 | 11.2072 | 56.6667 | 560.6667 | 76.8133 | 130 | 89 | 62 | 5.9 | 5.6 | 11.5 | 11.5 | 0.31749 | 0.51304 | 17.7 | 17.7 | 3.1146 | 44.3854 | 0.39878 | 6.4 | 6.4 | 96 | 300 | 627 | 514.9286 | 17.8742 | 68 | 407.4643 | 76.4397 | 89 | 75 | 50 | 2.1 | 3 | 5.1 | 5.1 | 0.30078 | 0.41176 | 12.6 | 12.6 | 5.481 | 26.519 | 0.47513 | 6.4 | 6.6 | 221 | 627 | 925 | 911.2 | 1.4919 | 26.3333 | 769.1 | 71.2651 | Total dissolved solids | mg/L | 113 | 322 | 999 | 983.8333 | 1.5182 | 64.9068 | 652.9167 | 82.693 | Total dissolved solids | mg/L | 116 | 322 | 576.6909 | 63.9752 | 449.3455 | 74.1847 | Total dissolved solids | mg/L | 130 | 300 | 925 | 759.6296 | 17.8779 | 56.6667 | 529.8148 | 75.4631 | Total dissolved solids | mg/L | 96 | 300 | 522.5455 | 68 | 411.2727 | 76.6578 | Total dissolved solids | mg/L | 88 | 347 | 1069 | 1321.3333 | -23.6046 | 74.6398 | 834.1667 | 89.4505 | Total dissolved solids | mg/L | 68 | 347 | 769.8503 | 80.4035 | 558.4252 | 87.8229 | Total dissolved solids | mg/L | 70 | 309 | 1031 | 1208.0952 | -17.177 | 77.3463 | 758.5476 | 90.7718 | Total dissolved solids | mg/L | 48 | 309 | 738.8824 | 84.466 | 523.9412 | 90.8387 | Total dissolved solids | mg/L | 84 | 340 | 1100 | 1197.0435 | -8.8221 | 75.2941 | 768.5217 | 89.0699 | Total dissolved solids | mg/L | 62 | 340 | 732.536 | 81.7647 | 536.268 | 88.4386 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | 1.25
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 7.5 | Reactive silica (mg/L as SiO2) | 14.6 |  |  |  | 1989-07-31 |  | 277.4 | 24 | 130 | 75 | 55 | 0 | 9.5 | 3 |  | 12.5 | 12.5 | 0.76 | 0 | 19 | 19 | 4.3917 | 43.1083 | 0.44075 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 838.3333 | 9.3694 | 56.6667 | 569.1667 | 77.1596 | 130 | 80 | 60 | 6 | 5.5 | 11.5 | 11.5 | 0.31563 | 0.52174 | 18 | 18 | 3.1527 | 41.8473 | 0.43014 | 6.4 | 6.4 | 96 | 300 | 627 | 522.5455 | 16.6594 | 68 | 411.2727 | 76.6578 | 80 | 75 | 50 | 2.2 | 3 | 5.2 | 5.2 | 0.30449 | 0.42308 | 13.2 | 13.2 | 5.5487 | 21.9513 | 0.60133 | 6.4 | 6.6 | 221 | 627 | 925 | 924.7333 | 0.028829 | 26.3333 | 775.8667 | 71.5157 | Total hardness | mg/L as CaCO3 | 74 | 218 | 681 | 674 | 1.0279 | 66.055 | 446 | 83.4081 | Total hardness | mg/L as CaCO3 | 54 | 218 | 420.7636 | 75.2294 | 319.3818 | 83.0923 | Total hardness | mg/L as CaCO3 | 81 | 222 | 633 | 603.2222 | 4.7042 | 63.5135 | 412.6111 | 80.3689 | Total hardness | mg/L as CaCO3 | 80 | 222 | 376.9091 | 63.964 | 299.4545 | 73.2848 | Total hardness | mg/L as CaCO3 | 80 | 238 | 670 | 832.381 | -24.236 | 66.3866 | 535.1905 | 85.0521 | Total hardness | mg/L as CaCO3 | 35 | 238 | 545.6653 | 85.2941 | 391.8326 | 91.0676 | Total hardness | mg/L as CaCO3 | 51 | 229 | 728 | 898.619 | -23.4367 | 77.7293 | 563.8095 | 90.9544 | Total hardness | mg/L as CaCO3 | 36 | 229 | 546.8824 | 84.2795 | 387.9412 | 90.7202 | Total hardness | mg/L as CaCO3 | 50 | 230 | 780 | 832.6087 | -6.7447 | 78.2609 | 531.3043 | 90.5892 | Total hardness | mg/L as CaCO3 | 35 | 230 | 505.34 | 84.7826 | 367.67 | 90.4806 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.35 | Feed flow rate to system, QF-sys (gpm) | 10 | Turbidity (ntu) | 0.3 |  |  |  | 1989-08-01 |  | 301.5 | 24 | 130 | 75 | 55 | 0 | 9.5 | 3 |  | 12.5 | 12.5 | 0.76 | 0 | 19 | 19 | 4.3917 | 43.1083 | 0.44075 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 838.3333 | 9.3694 | 56.6667 | 569.1667 | 77.1596 | 130 | 90 | 60 | 6 | 5.5 | 11.5 | 11.5 | 0.31563 | 0.52174 | 18 | 18 | 3.1527 | 46.8473 | 0.38423 | 6.4 | 6.4 | 96 | 300 | 627 | 522.5455 | 16.6594 | 68 | 411.2727 | 76.6578 | 90 | 75 | 50 | 2.3 | 3 | 5.3 | 5.3 | 0.30821 | 0.43396 | 13.8 | 13.8 | 5.6163 | 26.8837 | 0.51332 | 6.4 | 6.6 | 221 | 627 | 925 | 938.2667 | -1.4342 | 26.3333 | 782.6333 | 71.762 | Calcium hardness | mg/L as CaCO3 | 62 | 200 | 600 | 637 | -6.1667 | 69 | 418.5 | 85.1852 | Calcium hardness | mg/L as CaCO3 | 45 | 200 | 391.6364 | 77.5 | 295.8182 | 84.788 | Calcium hardness | mg/L as CaCO3 | 72 | 201 | 559 | 549.7778 | 1.6498 | 64.1791 | 375.3889 | 80.8199 | Calcium hardness | mg/L as CaCO3 | 73 | 201 | 340.6364 | 63.6816 | 270.8182 | 73.0446 | Calcium hardness | mg/L as CaCO3 | 44 | 213 | 577 | 848.7619 | -47.0991 | 79.3427 | 530.881 | 91.7119 | Calcium hardness | mg/L as CaCO3 | 32 | 213 | 487.3222 | 84.9765 | 350.1611 | 90.8613 | Calcium hardness | mg/L as CaCO3 | 38 | 200 | 657 | 809.4286 | -23.2007 | 81 | 504.7143 | 92.471 | Calcium hardness | mg/L as CaCO3 | 32 | 200 | 476.7059 | 84 | 338.3529 | 90.5424 | Calcium hardness | mg/L as CaCO3 | 42 | 200 | 680 | 728.9565 | -7.1995 | 79 | 464.4783 | 90.9576 | Calcium hardness | mg/L as CaCO3 | 30 | 200 | 440.04 | 85 | 320.02 | 90.6256 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 1.31
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.5 | SDI | 2.0 & 2.3 |  |  |  | 1989-08-02 |  | 325.6 | 24 | 130 | 75 | 55.5 | 0 | 9.3 | 3 |  | 12.3 | 12.3 | 0.7561 | 0 | 18.6 | 18.6 | 4.335 | 42.665 | 0.43595 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 827 | 10.5946 | 56.6667 | 563.5 | 76.9299 | 130 | 90 | 61 | 6 | 5.5 | 11.5 | 11.5 | 0.31563 | 0.52174 | 18 | 18 | 3.1527 | 45.8473 | 0.39261 | 6.4 | 6.4 | 96 | 300 | 627 | 522.5455 | 16.6594 | 68 | 411.2727 | 76.6578 | 90 | 75 | 50 | 2.2 | 3 | 5.2 | 5.2 | 0.30449 | 0.42308 | 13.2 | 13.2 | 5.5487 | 26.9513 | 0.48977 | 6.4 | 6.6 | 221 | 627 | 925 | 924.7333 | 0.028829 | 26.3333 | 775.8667 | 71.5157 | Turbidity | ntu | 0.16 | 0.18 | 0.72 | 0.24333 | 66.2037 | 11.1111 | 0.21167 | 24.4094 | Turbidity | ntu | 0.15 | 0.18 | 0.21709 | 16.6667 | 0.19855 | 24.4505 | Turbidity | ntu | 0.23 | 1 | 0.26 | 3.0819 | -1085.3276 | 77 | 2.0409 | 88.7306 | Turbidity | ntu | 0.08 | 1 | 2.0036 | 92 | 1.5018 | 94.6731 | Turbidity | ntu | 0.9 | 0.2 | 0.42 | -2.4333 | 679.3651 | -350 | -1.1167 | 180.597 | Turbidity | ntu | 1.13 | 0.2 | -1.2095 | -465 | -0.50475 | 323.873 | Turbidity | ntu | 0.31 | 0.66 | 0.82 | 1.9767 | -141.0569 | 53.0303 | 1.3183 | 76.4855 | Turbidity | ntu | 0.22 | 0.66 | 1.3847 | 66.6667 | 1.0224 | 78.481 | Turbidity | ntu | 0.13 | 0.18 | 0.27 | 0.34739 | -28.6634 | 27.7778 | 0.2637 | 50.7007 | Turbidity | ntu | 0.32 | 0.18 | -0.01768 | -77.7778 | 0.08116 | -294.2829 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI |  |  |  |  | 1989-08-03 |  | 351.7 | 24 | 130 | 75 | 55 | 0 | 9 | 3 |  | 12 | 12 | 0.75 | 0 | 18 | 18 | 4.25 | 43.25 | 0.41618 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 810 | 12.4324 | 56.6667 | 555 | 76.5766 | 130 | 89 | 60 | 5.7 | 5.3 | 11 | 11 | 0.30264 | 0.51818 | 17.1 | 17.1 | 3.137 | 46.363 | 0.36883 | 6.4 | 6.4 | 96 | 300 | 627 | 519.3962 | 17.1617 | 68 | 409.6981 | 76.5681 | 89 | 75 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 26.5867 | 0.45135 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.2 | 3.5 | 7.1 | 94.2857 | 5.3 | 96.2264 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.2 | 3.7 | 9.4647 | 94.5946 | 6.5824 | 96.9616 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.9 | 8.9832 | 92.3077 | 6.4416 | 95.3428 | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1989-08-04 |  | 373 | 24 | 130 | 75 | 55 | 0 | 9.5 | 3 |  | 12.5 | 12.5 | 0.76 | 0 | 19 | 19 | 4.3917 | 43.1083 | 0.44075 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 838.3333 | 9.3694 | 56.6667 | 569.1667 | 77.1596 | 130 | 90 | 60 | 6 | 5.4 | 11.4 | 11.4 | 0.31192 | 0.52632 | 18 | 18 | 3.1733 | 46.8267 | 0.3844 | 6.4 | 6.4 | 96 | 300 | 627 | 526.6667 | 16.0021 | 68 | 413.3333 | 76.7742 | 90 | 75 | 50 | 2.2 | 3 | 5.2 | 5.2 | 0.30449 | 0.42308 | 13.2 | 13.2 | 5.5487 | 26.9513 | 0.48977 | 6.4 | 6.6 | 221 | 627 | 925 | 924.7333 | 0.028829 | 26.3333 | 775.8667 | 71.5157 | Total organic carbon | mg/L | 0.3 | 3.4 | 12.5 | 13.2167 | -5.7333 | 91.1765 | 8.3083 | 96.3892 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.2 | 3.5 | 14.1 | 12.4222 | 11.8991 | 94.2857 | 7.9611 | 97.4878 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.4 | 11.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.1 | 3.7 | 14.3 | 17.2429 | -20.5794 | 97.2973 | 10.4714 | 99.045 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.9 | 15 | 15.9522 | -6.3478 | 92.3077 | 9.9261 | 96.9777 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Keller Plant 1 | Total width of all membrane envelopes in the element, w (ft) | 12 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 6.6667 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1989-08-07 |  | 443.6 | 24 | 131 | 75 | 55 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 4.3633 | 43.6367 | 0.43083 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 832.6667 | 9.982 | 56.6667 | 566.3333 | 77.0453 | 131 | 91 | 60 | 5.9 | 5.5 | 11.4 | 11.4 | 0.31378 | 0.51754 | 17.7 | 17.7 | 3.1342 | 47.8658 | 0.36978 | 6.4 | 6.4 | 96 | 300 | 627 | 518.8364 | 17.251 | 68 | 409.4182 | 76.5521 | 91 | 75 | 50 | 2.1 | 3 | 5.1 | 5.1 | 0.30078 | 0.41176 | 12.6 | 12.6 | 5.481 | 27.519 | 0.45787 | 6.4 | 6.6 | 221 | 627 | 925 | 911.2 | 1.4919 | 26.3333 | 769.1 | 71.2651 | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | (11) Other/GW | Feed spacer thickness, T (ft) | 0.0025 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 3.3333 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1989-08-08 |  | 467.6 | 24 | 129 | 75 | 54 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 4.3633 | 43.6367 | 0.43083 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 832.6667 | 9.982 | 56.6667 | 566.3333 | 77.0453 | 129 | 90 | 58 | 5.8 | 5.4 | 11.2 | 11.2 | 0.30821 | 0.51786 | 17.4 | 17.4 | 3.1356 | 48.3644 | 0.35977 | 6.4 | 6.4 | 96 | 300 | 627 | 519.1111 | 17.2072 | 68 | 409.5556 | 76.56 | 90 | 75 | 50 | 2.2 | 3 | 5.2 | 5.2 | 0.30449 | 0.42308 | 13.2 | 13.2 | 5.5487 | 26.9513 | 0.48977 | 6.4 | 6.6 | 221 | 627 | 925 | 924.7333 | 0.028829 | 26.3333 | 775.8667 | 71.5157 | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | Induced Aeration | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1989-08-09 |  | 490.4 | 24 | 130 | 75 | 55 | 0 | 9.5 | 3 |  | 12.5 | 12.5 | 0.76 | 0 | 19 | 19 | 4.3917 | 43.1083 | 0.44075 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 838.3333 | 9.3694 | 56.6667 | 569.1667 | 77.1596 | 130 | 90 | 60 | 5.7 | 5.6 | 11.3 | 11.3 | 0.31378 | 0.50442 | 17.1 | 17.1 | 3.0782 | 46.9218 | 0.36444 | 6.4 | 6.4 | 96 | 300 | 627 | 507.6429 | 19.0362 | 68 | 403.8214 | 76.2271 | 90 | 75 | 50 | 2.2 | 3 | 5.2 | 5.2 | 0.30449 | 0.42308 | 13.2 | 13.2 | 5.5487 | 26.9513 | 0.48977 | 6.4 | 6.6 | 221 | 627 | 925 | 924.7333 | 0.028829 | 26.3333 | 775.8667 | 71.5157 | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 317 | Purchase price for an equivalent 8" x 40 " element ($) | 500 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1989-08-10 |  | 514.2 | 24 | 131 | 75 | 55 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 4.3633 | 43.6367 | 0.43083 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 832.6667 | 9.982 | 56.6667 | 566.3333 | 77.0453 | 131 | 90 | 60 | 5.8 | 5.3 | 11.1 | 11.1 | 0.30449 | 0.52252 | 17.4 | 17.4 | 3.1562 | 47.3438 | 0.36752 | 6.4 | 6.4 | 96 | 300 | 627 | 523.2453 | 16.5478 | 68 | 411.6226 | 76.6777 | 90 | 75 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 27.0867 | 0.44302 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL6521405 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1.3333 | [5 empty] | 1989-08-11 |  | 538.5 | 24 | 131 | 75 | 55 | 0 | 9.1 | 3 |  | 12.1 | 12.1 | 0.75207 | 0 | 18.2 | 18.2 | 4.2783 | 43.7217 | 0.41627 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 815.6667 | 11.8198 | 56.6667 | 557.8333 | 76.6955 | 131 | 91 | 60 | 5.8 | 5.4 | 11.2 | 11.2 | 0.30821 | 0.51786 | 17.4 | 17.4 | 3.1356 | 47.8644 | 0.36353 | 6.4 | 6.4 | 96 | 300 | 627 | 519.1111 | 17.2072 | 68 | 409.5556 | 76.56 | 91 | 75 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 27.5867 | 0.43499 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-Free Cl2 residual | mg/L | 0.74 | 1.28 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.43 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 2.1 | 3.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.37 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.7 | 4.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.6 | 4.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.44 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.2 | 4.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.43 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 22 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 0.66667 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1989-08-12 |  | 564 | 24 | 130 | 75 | 55 | 0 | 9.2 | 3 |  | 12.2 | 12.2 | 0.7541 | 0 | 18.4 | 18.4 | 4.3067 | 43.1933 | 0.42599 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 821.3333 | 11.2072 | 56.6667 | 560.6667 | 76.8133 | 130 | 91 | 60 | 5.8 | 5.4 | 11.2 | 11.2 | 0.30821 | 0.51786 | 17.4 | 17.4 | 3.1356 | 47.3644 | 0.36736 | 6.4 | 6.4 | 96 | 300 | 627 | 519.1111 | 17.2072 | 68 | 409.5556 | 76.56 | 91 | 75 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 27.5867 | 0.43499 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-Cl2 demand | mg/L | 4.26 | 11.22 | --- | 33.26 | --- | 62.0321 | 22.24 | 80.8453 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.3 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.9 | 9 | --- | 25.4926 | --- | 67.7778 | 17.2463 | 83.1848 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.3 | 8.3 | --- | 27.1095 | --- | 60.241 | 17.7048 | 81.3609 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.4 | 8.4 | --- | 23.4476 | --- | 47.619 | 15.9238 | 72.3684 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 1.78 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.8 | 8 | --- | 18.713 | --- | 40 | 13.3565 | 64.0625 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.17 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 24 | Design cross-flow velocity (fps) | 0.257 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1989-08-13 |  | 588.9 | 24 | 130 | 74 | 55 | 0 | 9.1 | 3 |  | 12.1 | 12.1 | 0.75207 | 0 | 18.2 | 18.2 | 4.2783 | 42.7217 | 0.42601 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 815.6667 | 11.8198 | 56.6667 | 557.8333 | 76.6955 | 130 | 90 | 60 | 5.8 | 5.4 | 11.2 | 11.2 | 0.30821 | 0.51786 | 17.4 | 17.4 | 3.1356 | 46.8644 | 0.37128 | 6.4 | 6.4 | 96 | 300 | 627 | 519.1111 | 17.2072 | 68 | 409.5556 | 76.56 | 90 | 74 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 26.5867 | 0.45135 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 5.3 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 5.4 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 4.81 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 4.08 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 5 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 25 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1989-08-14 |  | 609 | 24 | 130 | 75 | 55 | 0 | 9 | 3 |  | 12 | 12 | 0.75 | 0 | 18 | 18 | 4.25 | 43.25 | 0.41618 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 810 | 12.4324 | 56.6667 | 555 | 76.5766 | 130 | 91 | 60 | 5.7 | 5.4 | 11.1 | 11.1 | 0.30635 | 0.51351 | 17.1 | 17.1 | 3.1167 | 47.3833 | 0.36089 | 6.4 | 6.4 | 96 | 300 | 627 | 515.3333 | 17.8097 | 68 | 407.6667 | 76.4513 | 91 | 75 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 27.5867 | 0.43499 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 1989-08-15 |  | 632.1 | 24 | 129 | 74 | 55 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 4.3633 | 42.1367 | 0.44617 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 832.6667 | 9.982 | 56.6667 | 566.3333 | 77.0453 | 129 | 92 | 60 | 5.8 | 5.4 | 11.2 | 11.2 | 0.30821 | 0.51786 | 17.4 | 17.4 | 3.1356 | 47.3644 | 0.36736 | 6.4 | 6.4 | 96 | 300 | 627 | 519.1111 | 17.2072 | 68 | 409.5556 | 76.56 | 92 | 74 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 27.5867 | 0.43499 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) |  | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1989-08-16 |  | 656.6 | 24 | 132 | 72 | 55 | 0 | 9.4 | 3 |  | 12.4 | 12.4 | 0.75806 | 0 | 18.8 | 18.8 | 4.3633 | 42.6367 | 0.44094 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 832.6667 | 9.982 | 56.6667 | 566.3333 | 77.0453 | 132 | 92 | 60 | 5.7 | 5.4 | 11.1 | 11.1 | 0.30635 | 0.51351 | 17.1 | 17.1 | 3.1167 | 48.8833 | 0.34981 | 6.4 | 6.4 | 96 | 300 | 627 | 515.3333 | 17.8097 | 68 | 407.6667 | 76.4513 | 92 | 72 | 50 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 26.5867 | 0.45135 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-TOX | mg Cl- /L | 27 | 599 | --- | 2410.3333 | --- | 95.4925 | 1504.6667 | 98.2056 | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 33 | 567 | --- | 2010.7778 | --- | 94.1799 | 1288.8889 | 97.4397 | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 26 | 494 | --- | 2254.5714 | --- | 94.7368 | 1374.2857 | 98.1081 | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 42 | 444 | --- | 1956.2857 | --- | 90.5405 | 1200.1429 | 96.5004 | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 45 | 600 | --- | 2458.0435 | --- | 92.5 | 1529.0217 | 97.0569 | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95 % at 2000 ppm | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 22 | [5 empty] | 1989-08-17 |  | 679.1 | 24 | 130 | 73 | 55 | 0 | 9.5 | 3.5 |  | 13 | 13 | 0.73077 | 0 | 19 | 19 | 4.0071 | 42.4929 | 0.44713 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 761.4286 | 17.6834 | 56.6667 | 530.7143 | 75.5047 | 130 | 92 | 60 | 6.4 | 5.7 | 12.1 | 12.1 | 0.33049 | 0.52893 | 19.2 | 19.2 | 3.1853 | 47.8147 | 0.40155 | 6.4 | 6.4 | 96 | 300 | 627 | 529.0526 | 15.6216 | 68 | 414.5263 | 76.841 | 92 | 73 | 50 | 2.2 | 3.5 | 5.7 | 5.7 | 0.34163 | 0.38596 | 13.2 | 13.2 | 5.336 | 27.164 | 0.48594 | 6.4 | 6.6 | 221 | 627 | 925 | 882.2 | 4.627 | 26.3333 | 754.6 | 70.713 | SDS-CHCl3 | mg/L | 17 | 201 | --- | 783.6667 | --- | 91.5423 | 492.3333 | 96.5471 | Sampling date | MM/DD/YY | 1989-07-25 | 1989-07-25 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 9 | 84 | --- | 286.7778 | --- | 89.2857 | 185.3889 | 95.1453 | Sampling date | MM/DD/YY | 1989-09-07 | 1989-09-07 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1989-09-27 | 1989-09-27 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 9 | 107 | --- | 475.6667 | --- | 91.5888 | 291.3333 | 96.9108 | Sampling date | MM/DD/YY | 1989-11-02 | 1989-11-02 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 108 | --- | 459.5217 | --- | 97.2222 | 283.7609 | 98.9428 | Sampling date | MM/DD/YY | 1990-01-10 | 1990-01-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | MgSO4 solution | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 11 | [5 empty] | 1989-08-18 |  | 705.2 | 24 | 129 | 72 | 53 | 0 | 9.1 | 3 |  | 12.1 | 12.1 | 0.75207 | 0 | 18.2 | 18.2 | 4.2783 | 43.2217 | 0.42109 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 815.6667 | 11.8198 | 56.6667 | 557.8333 | 76.6955 | 129 | 92 | 58 | 5.7 | 5.2 | 10.9 | 10.9 | 0.29892 | 0.52294 | 17.1 | 17.1 | 3.1581 | 49.3419 | 0.34656 | 6.4 | 6.4 | 96 | 300 | 627 | 523.6154 | 16.4888 | 68 | 411.8077 | 76.6881 | 92 | 72 | 48 | 2 | 3 | 5 | 5 | 0.29707 | 0.4 | 12 | 12 | 5.4133 | 28.5867 | 0.41978 | 6.4 | 6.6 | 221 | 627 | 925 | 897.6667 | 2.955 | 26.3333 | 762.3333 | 71.0101 | SDS-BDCM | mg/L | 8 | 41 | --- | 145.5 | --- | 80.4878 | 93.25 | 91.4209 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 6 | 14 | --- | 35.6296 | --- | 57.1429 | 24.8148 | 75.8209 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 9 | 22 | --- | 70.9048 | --- | 59.0909 | 46.4524 | 80.6253 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 9 | 19 | --- | 56.619 | --- | 52.6316 | 37.8095 | 76.1965 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 4 | 27 | --- | 104 | --- | 85.1852 | 65.5 | 93.8931 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | [8 empty] | 1989-08-21 |  | 777 | 24 | 130 | 70 | 52 | 0 | 9.5 | 3.5 |  | 13 | 13 | 0.73077 | 0 | 19 | 19 | 4.0071 | 43.9929 | 0.43189 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 761.4286 | 17.6834 | 56.6667 | 530.7143 | 75.5047 | 130 | 93 | 57 | 6.4 | 5.5 | 11.9 | 11.9 | 0.32306 | 0.53782 | 19.2 | 19.2 | 3.2269 | 51.2731 | 0.37447 | 6.4 | 6.4 | 96 | 300 | 627 | 537.3818 | 14.2932 | 68 | 418.6909 | 77.0714 | 93 | 70 | 47 | 2.2 | 3.5 | 5.7 | 5.7 | 0.34163 | 0.38596 | 13.2 | 13.2 | 5.336 | 29.164 | 0.45261 | 6.4 | 6.6 | 221 | 627 | 925 | 882.2 | 4.627 | 26.3333 | 754.6 | 70.713 | SDS-DBCM | mg/L | 5 | 4.6 | --- | 3.3333 | --- | -8.6957 | 3.9667 | -26.0504 | Operation time | hh.hh | 137.4 | 137.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | 6.4 | 2.2 | --- | -9.1556 | --- | -190.9091 | -3.4778 | 284.0256 | Operation time | hh.hh | 1176.2 | 1176.2 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.7 | 3.6 | --- | -4.3 | --- | -58.3333 | -0.35 | 1728.5714 | Operation time | hh.hh | 1497.3 | 1497.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.9 | 1.8 | --- | -13.6238 | --- | -227.7778 | -5.9119 | 199.7986 | Operation time | hh.hh | 2339.9 | 2339.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.8 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3904.4 | 3904.4 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1989-08-22 |  | 799.6 | 24 | 130 | 70 | 52.5 | 0 | 9.5 | 3.5 |  | 13 | 13 | 0.73077 | 0 | 19 | 19 | 4.0071 | 43.4929 | 0.43685 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 761.4286 | 17.6834 | 56.6667 | 530.7143 | 75.5047 | 130 | 92 | 60 | 6.2 | 5.5 | 11.7 | 11.7 | 0.31935 | 0.52991 | 18.6 | 18.6 | 3.1898 | 47.8102 | 0.38904 | 6.4 | 6.4 | 96 | 300 | 627 | 529.9636 | 15.4763 | 68 | 414.9818 | 76.8665 | 92 | 70 | 45 | 2 | 3.5 | 5.5 | 5.5 | 0.3342 | 0.36364 | 12 | 12 | 5.22 | 30.78 | 0.38986 | 6.4 | 6.6 | 221 | 627 | 925 | 859 | 7.1351 | 26.3333 | 743 | 70.2557 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.5 | 6 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6 | 6.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.4 | 0.2 | --- | -4.3143 | --- | -600 | -2.0571 | 168.0556 | pH | --- | 5.7 | 6.1 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.4 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.1 | 6.5 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.7 | 6.2 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1.3333 | [5 empty] | 1989-08-23 |  | 824.2 | 24 | 130 | 68 | 51.5 | 0 | 9 | 3 |  | 12 | 12 | 0.75 | 0 | 18 | 18 | 4.25 | 43.25 | 0.41618 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 810 | 12.4324 | 56.6667 | 555 | 76.5766 | 130 | 91 | 58 | 5.6 | 5.8 | 11.4 | 11.4 | 0.31935 | 0.49123 | 16.8 | 16.8 | 3.0248 | 49.4752 | 0.33956 | 6.4 | 6.4 | 96 | 300 | 627 | 496.9655 | 20.7392 | 68 | 398.4828 | 75.9086 | 91 | 68 | 45 | 1.9 | 3 | 4.9 | 4.9 | 0.29335 | 0.38776 | 11.4 | 11.4 | 5.3457 | 29.1543 | 0.39102 | 6.4 | 6.6 | 221 | 627 | 925 | 884.1333 | 4.418 | 26.3333 | 755.5667 | 70.7504 | SDS-THM4 | mg/L | 30 | 246.6 | --- | 932.5 | --- | 87.8345 | 589.55 | 94.9114 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 23.6 | 100.2 | --- | 307.3037 | --- | 76.4471 | 203.7519 | 88.4173 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 16.1 | 92.8 | --- | 381.3381 | --- | 82.6509 | 237.069 | 93.2087 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 25.3 | 127.8 | --- | 513.3952 | --- | 80.2034 | 320.5976 | 92.1085 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 12.8 | 135 | --- | 544.1043 | --- | 90.5185 | 339.5522 | 96.2303 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 - 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 11 | [5 empty] | 1989-08-24 |  | 846.2 | 24 | 130 | 70 | 52.5 | 0 | 9.4 | 3.5 |  | 12.9 | 12.9 | 0.72868 | 0 | 18.8 | 18.8 | 3.9829 | 43.5171 | 0.43201 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 756.5714 | 18.2085 | 56.6667 | 528.2857 | 75.3921 | 130 | 93 | 59 | 6.3 | 5.5 | 11.8 | 11.8 | 0.3212 | 0.5339 | 18.9 | 18.9 | 3.2084 | 49.2916 | 0.38343 | 6.4 | 6.4 | 96 | 300 | 627 | 533.6727 | 14.8847 | 68 | 416.8364 | 76.9694 | 93 | 70 | 46 | 3.1 | 3.5 | 6.6 | 6.6 | 0.37505 | 0.4697 | 18.6 | 18.6 | 5.858 | 29.642 | 0.62749 | 6.4 | 6.6 | 221 | 627 | 925 | 986.6 | -6.6595 | 26.3333 | 806.8 | 72.6078 | SDS-MCAA* | mg/L | 5 | 4 | --- | 0.83333 | --- | -25 | 2.4167 | -106.8966 | Alkalinity | mg/L as CaCO3 | 85 | 129 | 162.7333 | 10.5263 | 145.8667 | 41.7276 | SDS-MCAA* | mg/L | 6 | 10 | --- | 20.8148 | --- | 40 | 15.4074 | 61.0577 | Alkalinity | mg/L as CaCO3 | 129 | 255 | 329.1176 | 18.8679 | 292.0588 | 55.8308 | SDS-MCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 65 | 169 | 265.096 | 58.8608 | 217.048 | 70.0527 | SDS-MCAA* | mg/L | 1 | 2 | --- | 5.7619 | --- | 50 | 3.881 | 74.2331 | Alkalinity | mg/L as CaCO3 | 90 | 208 | 299.3217 | 5.2632 | 253.6609 | 64.5196 | SDS-MCAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 94 | 270 | 404.9541 | 21.6667 | 337.477 | 72.1463 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 3 - 9 | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1989-08-25 |  | 871.7 | 24 | 127 | 68 | 50.5 | 0 | 9 | 3 |  | 12 | 12 | 0.75 | 0 | 18 | 18 | 4.25 | 42.75 | 0.42105 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 810 | 12.4324 | 56.6667 | 555 | 76.5766 | 127 | 91 | 56 | 5.7 | 5 | 10.7 | 10.7 | 0.2915 | 0.53271 | 17.1 | 17.1 | 3.2028 | 49.7972 | 0.34339 | 6.4 | 6.4 | 96 | 300 | 627 | 532.56 | 15.0622 | 68 | 416.28 | 76.9386 | 91 | 68 | 45 | 1.8 | 3 | 4.8 | 4.8 | 0.28964 | 0.375 | 10.8 | 10.8 | 5.278 | 29.222 | 0.36958 | 6.4 | 6.6 | 221 | 627 | 925 | 870.6 | 5.8811 | 26.3333 | 748.8 | 70.4861 | SDS-DCAA* | mg/L | 3 | 26 | --- | 98.8333 | --- | 88.4615 | 62.4167 | 95.1936 | Total dissolved solids | mg/L | 153 | 584 | 914.4333 | 52.4845 | 749.2167 | 79.5787 | SDS-DCAA* | mg/L | 5 | 41 | --- | 138.3333 | --- | 87.8049 | 89.6667 | 94.4238 | Total dissolved solids | mg/L | 221 | 627 | 865.8235 | 26.3333 | 746.4118 | 70.3917 | SDS-DCAA* | mg/L | BMRL | 45 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 156 | 649 | 1104.532 | 55.0432 | 876.766 | 82.2073 | SDS-DCAA* | mg/L | 2 | 36 | --- | 163.9048 | --- | 94.4444 | 99.9524 | 97.999 | Total dissolved solids | mg/L | 152 | 641 | 1019.4435 | 50.8091 | 830.2217 | 81.6916 | SDS-DCAA* | mg/L | 2 | 17 | --- | 67.2174 | --- | 88.2353 | 42.1087 | 95.2504 | Total dissolved solids | mg/L | 200 | 700 | 1083.3922 | 41.1765 | 891.6961 | 77.5708 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 10 | [5 empty] | 1989-08-26 |  | 871.7 | 24 | 125 | 67 | 51.5 | 0 | 9 | 3.1 |  | 12.1 | 12.1 | 0.7438 | 0 | 18 | 18 | 4.1677 | 40.3323 | 0.44629 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 793.5484 | 14.211 | 56.6667 | 546.7742 | 76.2242 | 125 | 79 | 57 | 5.5 | 5 | 10.5 | 10.5 | 0.28778 | 0.52381 | 16.5 | 16.5 | 3.162 | 41.838 | 0.39438 | 6.4 | 6.4 | 96 | 300 | 627 | 524.4 | 16.3636 | 68 | 412.2 | 76.7103 | 79 | 67 | 46 | 1.7 | 3.1 | 4.8 | 4.8 | 0.29335 | 0.35417 | 10.2 | 10.2 | 5.1732 | 21.8268 | 0.46732 | 6.4 | 6.6 | 221 | 627 | 925 | 849.6452 | 8.1465 | 26.3333 | 738.3226 | 70.0673 | SDS-TCAA* | mg/L | 2 | 27 | --- | 106.1667 | --- | 92.5926 | 66.5833 | 96.9962 | Total hardness | mg/L as CaCO3 | 102 | 392 | 614.3333 | 53.211 | 503.1667 | 79.7284 | SDS-TCAA* | mg/L | 2 | 45 | --- | 161.2593 | --- | 95.5556 | 103.1296 | 98.0607 | Total hardness | mg/L as CaCO3 | 181 | 428 | 573.2941 | 18.4685 | 500.6471 | 63.8468 | SDS-TCAA* | mg/L | BMRL | 47 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 86 | 430 | 747.856 | 63.8655 | 588.928 | 85.3972 | SDS-TCAA* | mg/L | 1 | 31 | --- | 143.8571 | --- | 96.7742 | 87.4286 | 98.8562 | Total hardness | mg/L as CaCO3 | 108 | 470 | 750.1565 | 52.8384 | 610.0783 | 82.2974 | SDS-TCAA* | mg/L | 1 | 21 | --- | 87.9565 | --- | 95.2381 | 54.4783 | 98.1644 | Total hardness | mg/L as CaCO3 | 123 | 500 | 789.0777 | 46.5217 | 644.5389 | 80.9166 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [5 empty] | 1989-08-27 |  | 916.1 | 24 | 125 | 66 | 44 | 0 | 8.9 | 3 |  | 11.9 | 11.9 | 0.7479 | 0 | 17.8 | 17.8 | 4.2217 | 47.2783 | 0.37649 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 804.3333 | 13.045 | 56.6667 | 552.1667 | 76.4564 | 125 | 76 | 58 | 7.8 | 5.2 | 13 | 13 | 0.33791 | 0.6 | 23.4 | 23.4 | 3.57 | 38.93 | 0.60108 | 6.4 | 6.4 | 96 | 300 | 627 | 606 | 3.3493 | 68 | 453 | 78.8079 | 76 | 66 | 30 | 2.8 | 3 | 5.8 | 5.8 | 0.32677 | 0.48276 | 16.8 | 16.8 | 5.9547 | 35.0453 | 0.47938 | 6.4 | 6.6 | 221 | 627 | 925 | 1005.9333 | -8.7495 | 26.3333 | 816.4667 | 72.9321 | SDS-MBAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 95 | 355 | 554.3333 | 52.5 | 454.6667 | 79.1056 | SDS-MBAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 172 | 392 | 521.4118 | 14.4279 | 456.7059 | 62.339 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 76 | 347 | 597.404 | 64.3192 | 472.202 | 83.9052 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 94 | 424 | 679.3913 | 53 | 551.6957 | 82.9616 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 110 | 470 | 746.0424 | 45 | 608.0212 | 81.9085 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | not reported | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1989-08-28 |  | 940.1 | 24 | 129 | 67 | 50.5 | 0 | 9 | 2.9 |  | 11.9 | 11.9 | 0.7563 | 0 | 18 | 18 | 4.3379 | 43.1621 | 0.41703 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 827.5862 | 10.5312 | 56.6667 | 563.7931 | 76.9419 | 129 | 91 | 56 | 5.6 | 5 | 10.6 | 10.6 | 0.28964 | 0.5283 | 16.8 | 16.8 | 3.1824 | 50.8176 | 0.33059 | 6.4 | 6.4 | 96 | 300 | 627 | 528.48 | 15.7129 | 68 | 414.24 | 76.825 | 91 | 67 | 45 | 2.8 | 2.9 | 5.7 | 5.7 | 0.31935 | 0.49123 | 16.8 | 16.8 | 6.02 | 27.98 | 0.60043 | 6.4 | 6.6 | 221 | 627 | 925 | 1019 | -10.1622 | 26.3333 | 823 | 73.147 | SDS-DBAA* | mg/L | 1 | 1 | --- | 1 | --- | 0 | 1 | 0 | Turbidity | ntu | 0.16 | 1.52 | 2.5627 | 11.1111 | 2.0413 | 92.162 | SDS-DBAA* | mg/L | 2 | 1 | --- | -1.7037 | --- | -100 | -0.35185 | 668.4211 | Turbidity | ntu | 0.17 | 0.54 | 0.75765 | 83 | 0.64882 | 73.7987 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 1.9 | 0.48 | -0.83208 | -850 | -0.17604 | 1179.3002 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.49 | 1.9 | 2.9912 | 25.7576 | 2.4456 | 79.9641 | SDS-DBAA* | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 1.7 | 0.22 | -0.91484 | -844.4444 | -0.34742 | 589.3206 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 free chlorine | maximum system recycle flow rates. | [6 empty] | 1989-08-29 |  | 966.3 | 24 | 127 | 67 | 50 | 0 | 8.7 | 3 |  | 11.7 | 11.7 | 0.74359 | 0 | 17.4 | 17.4 | 4.165 | 42.835 | 0.40621 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 793 | 14.2703 | 56.6667 | 546.5 | 76.2123 | 127 | 90 | 55 | 5.7 | 5 | 10.7 | 10.7 | 0.2915 | 0.53271 | 17.1 | 17.1 | 3.2028 | 50.2972 | 0.33998 | 6.4 | 6.4 | 96 | 300 | 627 | 532.56 | 15.0622 | 68 | 416.28 | 76.9386 | 90 | 67 | 45 | 2.8 | 3 | 5.8 | 5.8 | 0.32677 | 0.48276 | 16.8 | 16.8 | 5.9547 | 27.5453 | 0.6099 | 6.4 | 6.6 | 221 | 627 | 925 | 1005.9333 | -8.7495 | 26.3333 | 816.4667 | 72.9321 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 7 | 12.06 | 88.2353 | 9.53 | 95.8027 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 8 | 12.5294 | 91.4286 | 10.2647 | 97.0774 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 8.4 | 14.6687 | 91.8919 | 11.5343 | 97.3991 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.9 | 8.9 | 15.0343 | 76.9231 | 11.9671 | 92.4794 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1989-08-31 |  | 1014.1 | 24 | 129 | 68 | 51 | 0 | 9.3 | 3.5 |  | 12.8 | 12.8 | 0.72656 | 0 | 18.6 | 18.6 | 3.9586 | 43.5414 | 0.42718 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 751.7143 | 18.7336 | 56.6667 | 525.8571 | 75.2785 | 129 | 91 | 57 | 6.2 | 5.5 | 11.7 | 11.7 | 0.31935 | 0.52991 | 18.6 | 18.6 | 3.1898 | 49.8102 | 0.37342 | 6.4 | 6.4 | 96 | 300 | 627 | 529.9636 | 15.4763 | 68 | 414.9818 | 76.8665 | 91 | 68 | 45 | 2 | 3.5 | 5.5 | 5.5 | 0.3342 | 0.36364 | 12 | 12 | 5.22 | 29.28 | 0.40984 | 6.4 | 6.6 | 221 | 627 | 925 | 859 | 7.1351 | 26.3333 | 743 | 70.2557 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1989-09-01 |  | 1036.9 | 24 | 129 | 64 | 51.5 | 0 | 9 | 3 |  | 12 | 12 | 0.75 | 0 | 18 | 18 | 4.25 | 40.75 | 0.44172 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 810 | 12.4324 | 56.6667 | 555 | 76.5766 | 129 | 91 | 58 | 5.5 | 5 | 10.5 | 10.5 | 0.28778 | 0.52381 | 16.5 | 16.5 | 3.162 | 48.838 | 0.33785 | 6.4 | 6.4 | 96 | 300 | 627 | 524.4 | 16.3636 | 68 | 412.2 | 76.7103 | 91 | 64 | 45 | 1.8 | 3 | 4.8 | 4.8 | 0.28964 | 0.375 | 10.8 | 10.8 | 5.278 | 27.222 | 0.39674 | 6.4 | 6.6 | 221 | 627 | 925 | 870.6 | 5.8811 | 26.3333 | 748.8 | 70.4861 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 10 | [5 empty] | 1989-09-05 |  | 1132.4 | 24 | 125 | 73 | 50 | 0 | 9 | 3 |  | 12 | 12 | 0.75 | 0 | 18 | 18 | 4.25 | 44.75 | 0.40223 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 810 | 12.4324 | 56.6667 | 555 | 76.5766 | 125 | 90 | 55 | 5.8 | 5.5 | 11.3 | 11.3 | 0.31192 | 0.51327 | 17.4 | 17.4 | 3.1156 | 49.3844 | 0.35234 | 6.4 | 6.4 | 96 | 300 | 627 | 515.1273 | 17.8425 | 68 | 407.5636 | 76.4454 | 90 | 73 | 45 | 1.8 | 3 | 4.8 | 4.8 | 0.28964 | 0.375 | 10.8 | 10.8 | 5.278 | 31.222 | 0.34591 | 6.4 | 6.6 | 221 | 627 | 925 | 870.6 | 5.8811 | 26.3333 | 748.8 | 70.4861 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5 | [5 empty] | 1989-09-06 |  | 1153.4 | 24 | 125 | 70 | 50 | 0 | 9 | 3.5 |  | 12.5 | 12.5 | 0.72 | 0 | 18 | 18 | 3.8857 | 43.6143 | 0.41271 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 737.1429 | 20.3089 | 56.6667 | 518.5714 | 74.9311 | 125 | 93 | 55 | 5.8 | 5 | 10.8 | 10.8 | 0.29335 | 0.53704 | 17.4 | 17.4 | 3.2232 | 50.7768 | 0.34268 | 6.4 | 6.4 | 96 | 300 | 627 | 536.64 | 14.4115 | 68 | 418.32 | 77.0511 | 93 | 70 | 45 | 1.8 | 3.5 | 5.3 | 5.3 | 0.32677 | 0.33962 | 10.8 | 10.8 | 5.104 | 31.396 | 0.34399 | 6.4 | 6.6 | 221 | 627 | 925 | 835.8 | 9.6432 | 26.3333 | 731.4 | 69.784 | SDS-HAA5 | mg/L | 11 | 59 | --- | 211 | --- | 81.3559 | 135 | 91.8519 | [8 empty] | SDS-HAA5 | mg/L | 15 | 99 | --- | 326.1111 | --- | 84.8485 | 212.5556 | 92.943 | [8 empty] | SDS-HAA5 | mg/L | 0 | 108 | --- | 514.2857 | --- | 100 | 311.1429 | 100 | [8 empty] | SDS-HAA5 | mg/L | 4 | 69 | --- | 313.5238 | --- | 94.2029 | 191.2619 | 97.9086 | [8 empty] | SDS-HAA5 | mg/L | 4 | 39 | --- | 156.1739 | --- | 89.7436 | 97.587 | 95.9011 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 5 | [5 empty] | 1989-09-07 |  | 1176.2 | 24 | 129 | 69 | 50.5 | 0 | 9.2 | 3.4 |  | 12.6 | 12.6 | 0.73016 | 0 | 18.4 | 18.4 | 4 | 44.5 | 0.41348 | 7.5 | 6.4 | 130 | 282 | 300 | 925 | 760 | 17.8378 | 56.6667 | 530 | 75.4717 | 129 | 91 | 56 | 6 | 5.5 | 11.5 | 11.5 | 0.31563 | 0.52174 | 18 | 18 | 3.1527 | 50.8473 | 0.354 | 6.4 | 6.4 | 96 | 300 | 627 | 522.5455 | 16.6594 | 68 | 411.2727 | 76.6578 | 91 | 69 | 45 | 2 | 3.4 | 5.4 | 5.4 | 0.32677 | 0.37037 | 12 | 12 | 5.2541 | 29.7459 | 0.40342 | 6.4 | 6.6 | 221 | 627 | 925 | 865.8235 | 6.3975 | 26.3333 | 746.4118 | 70.3917 | SDS-HAA6 | mg/L | 11 | 59 | --- | 211 | --- | 81.3559 | 135 | 91.8519 | [8 empty] | SDS-HAA6 | mg/L | 15 | 99 | --- | 326.1111 | --- | 84.8485 | 212.5556 | 92.943 | [8 empty] | SDS-HAA6 | mg/L | 0 | 108 | --- | 514.2857 | --- | 100 | 311.1429 | 100 | [8 empty] | SDS-HAA6 | mg/L | 4 | 69 | --- | 313.5238 | --- | 94.2029 | 191.2619 | 97.9086 | [8 empty] | SDS-HAA6 | mg/L | 4 | 39 | --- | 156.1739 | --- | 89.7436 | 97.587 | 95.9011 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 5 | [5 empty] | 1989-09-08 |  | 1202.6 | 24 | 127 | 66 | 48.5 | 0 | 9.2 | 3.4 |  | 12.6 | 12.6 | 0.73016 | 0 | 18.4 | 18.4 | 6.0941 | 41.9059 | 0.43908 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1047.8235 | 1.981 | 74.6398 | 697.4118 | 87.3819 | 127 | 90 | 55 | 6 | 5.5 | 11.5 | 11.5 | 0.31563 | 0.52174 | 18 | 18 | 4.3118 | 49.1882 | 0.36594 | 6 | 6.1 | 68 | 347 | 649 | 651.3636 | -0.3642 | 80.4035 | 499.1818 | 86.3777 | 90 | 66 | 42 | 2 | 3.4 | 5.4 | 5.4 | 0.32677 | 0.37037 | 12 | 12 | 6.38 | 29.62 | 0.40513 | 6.1 | 6.2 | 156 | 649 | 1069 | 939 | 12.1609 | 55.0432 | 794 | 80.3526 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.5 | [5 empty] | 1989-09-12 |  | 1206.6 | 24 | 128 | 66 | 49.5 | 0 | 9 | 3.5 |  | 12.5 | 12.5 | 0.72 | 0 | 18 | 18 | 5.92 | 41.58 | 0.4329 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1013 | 5.2385 | 74.6398 | 680 | 87.0588 | 128 | 90 | 55 | 6 | 5.7 | 11.7 | 11.7 | 0.32306 | 0.51282 | 18 | 18 | 4.2584 | 49.7416 | 0.36187 | 6 | 6.1 | 68 | 347 | 649 | 640.6842 | 1.2813 | 80.4035 | 493.8421 | 86.2304 | 90 | 66 | 44 | 1.9 | 3.5 | 5.4 | 5.4 | 0.33049 | 0.35185 | 11.4 | 11.4 | 6.2681 | 27.7319 | 0.41108 | 6.1 | 6.2 | 156 | 649 | 1069 | 916.6286 | 14.2536 | 55.0432 | 782.8143 | 80.0719 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 2.5 | [5 empty] | 1989-09-12 |  | 1206.6 | 24 | 136 | 71 | 50.5 | 0 | 9.3 | 3.6 |  | 12.9 | 12.9 | 0.72093 | 0 | 18.6 | 18.6 | 5.9354 | 47.0646 | 0.3952 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1016.0833 | 4.9501 | 74.6398 | 681.5417 | 87.0881 | 136 | 96 | 56 | 6.2 | 6 | 12.2 | 12.2 | 0.33791 | 0.5082 | 18.6 | 18.6 | 4.2315 | 55.7685 | 0.33352 | 6 | 6.1 | 68 | 347 | 649 | 635.3 | 2.1109 | 80.4035 | 491.15 | 86.1549 | 96 | 71 | 45 | 2.1 | 3.6 | 5.7 | 5.7 | 0.34534 | 0.36842 | 12.6 | 12.6 | 6.3679 | 32.1321 | 0.39213 | 6.1 | 6.2 | 156 | 649 | 1069 | 936.5833 | 12.387 | 55.0432 | 792.7917 | 80.3227
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1989-09-13 |  | 1211.8 | 24 | 130 | 70 | 50.5 | 0 | 9.4 | 3.5 |  | 12.9 | 12.9 | 0.72868 | 0 | 18.8 | 18.8 | 6.068 | 43.432 | 0.43286 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1042.6 | 2.4696 | 74.6398 | 694.8 | 87.3345 | 130 | 90 | 56 | 6.2 | 6 | 12.2 | 12.2 | 0.33791 | 0.5082 | 18.6 | 18.6 | 4.2315 | 49.7685 | 0.37373 | 6 | 6.1 | 68 | 347 | 649 | 635.3 | 2.1109 | 80.4035 | 491.15 | 86.1549 | 90 | 70 | 45 | 2.1 | 3.5 | 5.6 | 5.6 | 0.33791 | 0.375 | 12.6 | 12.6 | 6.409 | 28.591 | 0.4407 | 6.1 | 6.2 | 156 | 649 | 1069 | 944.8 | 11.6183 | 55.0432 | 796.9 | 80.4241 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 2.5 | [5 empty] | 1989-09-14 |  | 1235.2 | 24 | 135 | 70 | 52.5 | 0 | 9 | 3.5 |  | 12.5 | 12.5 | 0.72 | 0 | 18 | 18 | 5.92 | 44.08 | 0.40835 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1013 | 5.2385 | 74.6398 | 680 | 87.0588 | 135 | 90 | 60 | 7 | 5.5 | 12.5 | 12.5 | 0.3342 | 0.56 | 21 | 21 | 4.5655 | 47.9345 | 0.4381 | 6 | 6.1 | 68 | 347 | 649 | 702.0909 | -8.1804 | 80.4035 | 524.5455 | 87.0364 | 90 | 70 | 45 | 1.8 | 3.5 | 5.3 | 5.3 | 0.32677 | 0.33962 | 10.8 | 10.8 | 6.1977 | 28.8023 | 0.37497 | 6.1 | 6.2 | 156 | 649 | 1069 | 902.5429 | 15.5713 | 55.0432 | 775.7714 | 79.891 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 7.5 | [5 empty] | 1989-09-15 |  | 1258.6 | 24 | 140 | 70 | 52.5 | 0 | 9.1 | 3.5 |  | 12.6 | 12.6 | 0.72222 | 0 | 18.2 | 18.2 | 5.957 | 46.543 | 0.39104 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1020.4 | 4.5463 | 74.6398 | 683.7 | 87.1289 | 140 | 88 | 60 | 7 | 5.5 | 12.5 | 12.5 | 0.3342 | 0.56 | 21 | 21 | 4.5655 | 49.4345 | 0.4248 | 6 | 6.1 | 68 | 347 | 649 | 702.0909 | -8.1804 | 80.4035 | 524.5455 | 87.0364 | 88 | 70 | 45 | 2 | 3.5 | 5.5 | 5.5 | 0.3342 | 0.36364 | 12 | 12 | 6.3386 | 27.6614 | 0.43382 | 6.1 | 6.2 | 156 | 649 | 1069 | 930.7143 | 12.936 | 55.0432 | 789.8571 | 80.2496 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 10 | [5 empty] | 1989-09-18 |  | 1288.7 | 24 | 135 | 68 | 51.5 | 0 | 9 | 3.3 |  | 12.3 | 12.3 | 0.73171 | 0 | 18 | 18 | 6.1218 | 43.8782 | 0.41023 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1053.3636 | 1.4627 | 74.6398 | 700.1818 | 87.4318 | 135 | 95 | 58 | 6 | 6 | 12 | 12 | 0.3342 | 0.5 | 18 | 18 | 4.185 | 52.815 | 0.34081 | 6 | 6.1 | 68 | 347 | 649 | 626 | 3.5439 | 80.4035 | 486.5 | 86.0226 | 95 | 68 | 45 | 2 | 3.3 | 5.3 | 5.3 | 0.31935 | 0.37736 | 12 | 12 | 6.4239 | 30.0761 | 0.39899 | 6.1 | 6.2 | 156 | 649 | 1069 | 947.7879 | 11.3388 | 55.0432 | 798.3939 | 80.4608 | Qp/QT (THM4), % | 80.6094 | 97.2299 |  | Qp/QT (HAA5), % | 10.4167 | 66.6667 | [11 empty] | Qp/QT (THM4), % | 36.8146 | 83.812 |  | Qp/QT (HAA5), % | 53.5714 | 85.7143 | [11 empty] | Qp/QT (THM4), % | 27.1186 | 74.0548 |  | Qp/QT (HAA5), % | 50 | 75 | [11 empty] | Qp/QT (THM4), % | 54.439 | 89.561 |  | Qp/QT (HAA5), % | 23.0769 | 64.6154 | [11 empty] | Qp/QT (THM4), % | 51.5548 | 81.0147 |  | Qp/QT (HAA5), % | -42.8571 | 34.2857 | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[11 empty] | 1989-09-19 |  | 1311.5 | 24 | 134 | 69 | 49 | 0 | 9.6 | 3.6 |  | 13.2 | 13.2 | 0.72727 | 0 | 19.2 | 19.2 | 6.0433 | 46.4567 | 0.41329 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1037.6667 | 2.9311 | 74.6398 | 692.3333 | 87.2894 | 134 | 94 | 56 | 6.4 | 6.3 | 12.7 | 12.7 | 0.35277 | 0.50394 | 19.2 | 19.2 | 4.2071 | 53.7929 | 0.35692 | 6 | 6.1 | 68 | 347 | 649 | 630.4286 | 2.8615 | 80.4035 | 488.7143 | 86.0859 | 94 | 69 | 42 | 2.2 | 3.6 | 5.8 | 5.8 | 0.34905 | 0.37931 | 13.2 | 13.2 | 6.4364 | 33.0636 | 0.39923 | 6.1 | 6.2 | 156 | 649 | 1069 | 950.2778 | 11.1059 | 55.0432 | 799.6389 | 80.4912 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 224.0375 | 102.2 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 59.1643 | 34.5429 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 54.45 | 35.275 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 104.1462 | 61.5692 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 93.1029 | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1989-09-20 |  | 1336.8 | 24 | 135 | 65 | 50 | 0 | 9.5 | 3.2 |  | 12.7 | 12.7 | 0.74803 | 0 | 19 | 19 | 6.4345 | 43.5655 | 0.43613 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1115.9062 | -4.3879 | 74.6398 | 731.4531 | 87.9692 | 135 | 90 | 60 | 6 | 5.8 | 11.8 | 11.8 | 0.32677 | 0.50847 | 18 | 18 | 4.2331 | 48.2669 | 0.37293 | 6 | 6.1 | 68 | 347 | 649 | 635.6207 | 2.0615 | 80.4035 | 491.3103 | 86.1595 | 90 | 65 | 40 | 2 | 3.2 | 5.2 | 5.2 | 0.31192 | 0.38462 | 12 | 12 | 6.4706 | 31.0294 | 0.38673 | 6.1 | 6.2 | 156 | 649 | 1069 | 957.125 | 10.4654 | 55.0432 | 803.0625 | 80.5744 | SDS-HAA5b, mg/L | 20.3075 | 12.3296 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 68.0757 | 28.5979 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 78.7119 | 28.0209 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 33.6146 | 10.7854 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 20.9558 | 10.6448 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.3 | [5 empty] | 1989-09-21 |  | 1358.1 | 24 | 135 | 65 | 50 | 0 | 9.5 | 3.1 |  | 12.6 | 12.6 | 0.75397 | 0 | 19 | 19 | 6.5585 | 43.4415 | 0.43737 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1140.7097 | -6.7081 | 74.6398 | 743.8548 | 88.1697 | 135 | 90 | 60 | 6 | 5.8 | 11.8 | 11.8 | 0.32677 | 0.50847 | 18 | 18 | 4.2331 | 48.2669 | 0.37293 | 6 | 6.1 | 68 | 347 | 649 | 635.6207 | 2.0615 | 80.4035 | 491.3103 | 86.1595 | 90 | 65 | 40 | 2 | 3.1 | 5.1 | 5.1 | 0.30449 | 0.39216 | 12 | 12 | 6.5203 | 30.9797 | 0.38735 | 6.1 | 6.2 | 156 | 649 | 1069 | 967.0645 | 9.5356 | 55.0432 | 808.0323 | 80.6938 | SDS-TOXb, mg Cl- /L | 137.9141 | 42.8449 |  | SDS-TOXb, mg Cl- /L | 539.4167 | 217.6667 | [11 empty] | SDS-TOXb, mg Cl- /L | 370.4099 | 119.4439 |  | SDS-TOXb, mg Cl- /L | 280.9286 | 109.2857 | [11 empty] | SDS-TOXb, mg Cl- /L | 367.0847 | 147.4237 |  | SDS-TOXb, mg Cl- /L | 260 | 143 | [11 empty] | SDS-TOXb, mg Cl- /L | 225.1551 | 83.9649 |  | SDS-TOXb, mg Cl- /L | 351.2308 | 184.2462 | [11 empty] | SDS-TOXb, mg Cl- /L | 313.8707 | 150.3682 |  | SDS-TOXb, mg Cl- /L | NA | 409.7143 | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 7 | [5 empty] | 1989-09-22 |  | 1380.9 | 24 | 135 | 63 | 47.5 | 0 | 9.6 | 3.3 |  | 12.9 | 12.9 | 0.74419 | 0 | 19.2 | 19.2 | 6.3573 | 45.1427 | 0.42532 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1100.4545 | -2.9424 | 74.6398 | 723.7273 | 87.8407 | 135 | 93 | 55 | 7.2296 | 5.6704 | 12.9 | 12.9 | 0.34479 | 0.56044 | 21.6889 | 21.6889 | 4.5686 | 54.4314 | 0.39846 | 6 | 6.1 | 68 | 347 | 649 | 702.7204 | -8.2774 | 80.4035 | 524.8602 | 87.0442 | 93 | 63 | 40 | 2.3704 | 3.3 | 5.6704 | 5.6704 | 0.3331 | 0.41803 | 14.2222 | 14.2222 | 6.7006 | 31.2994 | 0.45439 | 6.1 | 6.2 | 156 | 649 | 1069 | 1003.119 | 6.1629 | 55.0432 | 826.0595 | 81.1152 | SDS-CDb, mg/L | 5.6096 | 4.4528 |  | SDS-CDb, mg/L | 10.495 | 6.58 | [11 empty] | SDS-CDb, mg/L | 6.7543 | 3.8875 |  | SDS-CDb, mg/L | 5.7321 | 3.7714 | [11 empty] | SDS-CDb, mg/L | 6.9441 | 4.5973 |  | SDS-CDb, mg/L | 5.8 | 4.55 | [11 empty] | SDS-CDb, mg/L | 6.2224 | 4.8176 |  | SDS-CDb, mg/L | 7.4769 | 5.8154 | [11 empty] | SDS-CDb, mg/L | 6.3502 | 5.4075 |  | SDS-CDb, mg/L | NA | 6.9029 | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 15 | [5 empty] | 1989-09-25 |  | 1452.2 | 24 | 135 | 63 | 50 | 0 | 10.4 | 3.3 |  | 13.7 | 13.7 | 0.75912 | 0 | 20.8 | 20.8 | 6.6712 | 42.3288 | 0.49139 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1163.2424 | -8.8159 | 74.6398 | 755.1212 | 88.3462 | 135 | 93 | 60 | 8 | 5.7 | 13.7 | 13.7 | 0.36019 | 0.58394 | 24 | 24 | 4.7479 | 49.2521 | 0.48729 | 6 | 6.1 | 68 | 347 | 649 | 738.5789 | -13.8026 | 80.4035 | 542.7895 | 87.4721 | 93 | 63 | 40 | 2.4 | 3.3 | 5.7 | 5.7 | 0.3342 | 0.42105 | 14.4 | 14.4 | 6.7227 | 31.2773 | 0.4604 | 6.1 | 6.2 | 156 | 649 | 1069 | 1007.5455 | 5.7488 | 55.0432 | 828.2727 | 81.1656 | TOCb, mg/L | 0.90111 | 0.38587 |  | TOCb, mg/L | 3.0771 | 1.3333 | [11 empty] | TOCb, mg/L | 2.2851 | 0.7342 |  | TOCb, mg/L | 1.7321 | 0.67143 | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 1.7402 | 0.4758 |  | TOCb, mg/L | 2.8692 | 1.3738 | [11 empty] | TOCb, mg/L | 2.044 | 0.98347 |  | TOCb, mg/L | NA | 2.6657 | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1989-09-26 |  | 1475.3 | 24 | 130 | 65 | 47.5 | 0 | 9.2 | 2.4 |  | 11.6 | 11.6 | 0.7931 | 0 | 18.4 | 18.4 | 7.5542 | 42.4458 | 0.43349 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1339.8333 | -25.3352 | 74.6398 | 843.4167 | 89.5662 | 130 | 94 | 55 | 7.0769 | 4.5231 | 11.6 | 11.6 | 0.29935 | 0.61008 | 21.2308 | 21.2308 | 4.9727 | 52.0273 | 0.40807 | 6 | 6.1 | 68 | 347 | 649 | 783.5306 | -20.7289 | 80.4035 | 565.2653 | 87.9703 | 94 | 65 | 40 | 2.1231 | 2.4 | 4.5231 | 4.5231 | 0.25708 | 0.46939 | 12.7385 | 12.7385 | 7.1106 | 32.3894 | 0.39329 | 6.1 | 6.2 | 156 | 649 | 1069 | 1085.1154 | -1.5075 | 55.0432 | 867.0577 | 82.0081 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 50 | [5 empty] | 1989-09-27 |  | 1497.3 | 24 | 135 | 65 | 47.5 | 0 | 9.6 | 2.5 |  | 12.1 | 12.1 | 0.79339 | 0 | 19.2 | 19.2 | 7.5628 | 44.9372 | 0.42726 | 7.5 | 6 | 88 | 270 | 347 | 1069 | 1341.56 | -25.4967 | 74.6398 | 844.28 | 89.5769 | 135 | 92 | 55 | 7.2911 | 4.8089 | 12.1 | 12.1 | 0.31394 | 0.60257 | 21.8734 | 21.8734 | 4.9051 | 53.5949 | 0.40812 | 6 | 6.1 | 68 | 347 | 649 | 770.0166 | -18.6466 | 80.4035 | 558.5083 | 87.8247 | 92 | 65 | 40 | 2.3089 | 2.5 | 4.8089 | 4.8089 | 0.2714 | 0.48013 | 13.8532 | 13.8532 | 7.2065 | 31.2935 | 0.44269 | 6.1 | 6.2 | 156 | 649 | 1069 | 1104.3073 | -3.3028 | 55.0432 | 876.6537 | 82.2051 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 24 | [5 empty] | 1989-09-28 |  | 1522.3 | 24 | 135 | 65 | 48.5 | 0 | 9.6 | 2.4 |  | 12 | 12 | 0.8 | 0 | 19.2 | 19.2 | 7.17 | 44.33 | 0.43312 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1265 | -22.6964 | 77.3463 | 787 | 91.1055 | 135 | 90 | 60 | 7.3846 | 4.6154 | 12 | 12 | 0.30849 | 0.61538 | 22.1538 | 22.1538 | 4.698 | 47.802 | 0.46345 | 6 | 6.5 | 48 | 309 | 641 | 726.6 | -13.3541 | 84.466 | 517.8 | 90.73 | 90 | 65 | 37 | 2.2154 | 2.4 | 4.6154 | 4.6154 | 0.26051 | 0.48 | 13.2923 | 13.2923 | 7.1469 | 33.3531 | 0.39853 | 6.5 | 6.6 | 152 | 641 | 1031 | 1092.3846 | -5.9539 | 50.8091 | 866.6923 | 82.4621 | Alkb, mg/L CaCO3 | 68.3989 | 62.9141 |  | Alkb, mg/L CaCO3 | 91.5625 | 73 | [11 empty] | Alkb, mg/L CaCO3 | 126.9713 | 86.0836 |  | Alkb, mg/L CaCO3 | 112.3929 | 84.4286 | [11 empty] | Alkb, mg/L CaCO3 | 139.2881 | 106.9022 |  | Alkb, mg/L CaCO3 | 123.5 | 106.25 | [11 empty] | Alkb, mg/L CaCO3 | 65.0585 | 45.7415 |  | Alkb, mg/L CaCO3 | 82.3077 | 59.4615 | [11 empty] | Alkb, mg/L CaCO3 | 78.7561 | 55.1882 |  | Alkb, mg/L CaCO3 | NA | 92.5714 | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 44.1429 | [5 empty] | 1989-09-29 |  | 1547.7 | 24 | 135 | 64 | 46.5 | 0 | 9.6 | 2.4 |  | 12 | 12 | 0.8 | 0 | 19.2 | 19.2 | 7.17 | 45.83 | 0.41894 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1265 | -22.6964 | 77.3463 | 787 | 91.1055 | 135 | 95 | 55 | 7.3846 | 4.6154 | 12 | 12 | 0.30849 | 0.61538 | 22.1538 | 22.1538 | 4.698 | 55.302 | 0.4006 | 6 | 6.5 | 48 | 309 | 641 | 726.6 | -13.3541 | 84.466 | 517.8 | 90.73 | 95 | 64 | 38 | 2.2154 | 2.4 | 4.6154 | 4.6154 | 0.26051 | 0.48 | 13.2923 | 13.2923 | 7.1469 | 34.3531 | 0.38693 | 6.5 | 6.6 | 152 | 641 | 1031 | 1092.3846 | -5.9539 | 50.8091 | 866.6923 | 82.4621 | T-Hdb, mg/L CaCO3 | 101.9224 | 77.9889 |  | T-Hdb, mg/L CaCO3 | 203 | 122 | [11 empty] | T-Hdb, mg/L CaCO3 | 170.0914 | 103.8251 |  | T-Hdb, mg/L CaCO3 | 146.4643 | 101.1429 | [11 empty] | T-Hdb, mg/L CaCO3 | 195.1525 | 120.9935 |  | T-Hdb, mg/L CaCO3 | 159 | 119.5 | [11 empty] | T-Hdb, mg/L CaCO3 | 132.0985 | 69.5815 |  | T-Hdb, mg/L CaCO3 | 187.9231 | 113.9846 | [11 empty] | T-Hdb, mg/L CaCO3 | 137.2013 | 84.1735 |  | T-Hdb, mg/L CaCO3 | NA | 168.2857 | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 33.2 | [5 empty] | 1989-10-02 |  | 1612.7 | 24 | 135 | 65 | 42.5 | 0 | 9.7 | 2.3 |  | 12 | 12 | 0.80833 | 0 | 19.4 | 19.4 | 7.4298 | 50.0702 | 0.38746 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1316.9565 | -27.7358 | 77.3463 | 812.9783 | 91.3897 | 135 | 93 | 55 | 7.4026 | 4.5974 | 12 | 12 | 0.30816 | 0.61689 | 22.2079 | 22.2079 | 4.7113 | 54.2887 | 0.40907 | 6 | 6.5 | 48 | 309 | 641 | 729.2593 | -13.769 | 84.466 | 519.1297 | 90.7538 | 93 | 65 | 30 | 2.2974 | 2.3 | 4.5974 | 4.5974 | 0.25612 | 0.49971 | 13.7842 | 13.7842 | 7.3322 | 41.6678 | 0.33081 | 6.5 | 6.6 | 152 | 641 | 1031 | 1129.4405 | -9.5481 | 50.8091 | 885.2203 | 82.8291 | Ca-Hdb, mg/L CaCO3 | 88.759 | 65.8227 |  | Ca-Hdb, mg/L CaCO3 | 185.625 | 108 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 153.5091 | 92.8825 |  | Ca-Hdb, mg/L CaCO3 | 131.8929 | 90.4286 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 167.1695 | 87.8475 |  | Ca-Hdb, mg/L CaCO3 | 128.5 | 86.25 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 111.8088 | 54.9112 |  | Ca-Hdb, mg/L CaCO3 | 162.6154 | 95.3231 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 118.5434 | 71.9967 |  | Ca-Hdb, mg/L CaCO3 | NA | 145.8286 | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 127.3429 | [5 empty] | 1989-10-03 |  | 1637.1 | 24 | 136 | 63 | 45 | 0 | 9.6 | 2.4 |  | 12 | 12 | 0.8 | 0 | 19.2 | 19.2 | 7.17 | 47.33 | 0.40566 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1265 | -22.6964 | 77.3463 | 787 | 91.1055 | 136 | 95 | 55 | 7.3846 | 4.6154 | 12 | 12 | 0.30849 | 0.61538 | 22.1538 | 22.1538 | 4.698 | 55.802 | 0.39701 | 6 | 6.5 | 48 | 309 | 641 | 726.6 | -13.3541 | 84.466 | 517.8 | 90.73 | 95 | 63 | 35 | 2.2154 | 2.4 | 4.6154 | 4.6154 | 0.26051 | 0.48 | 13.2923 | 13.2923 | 7.1469 | 36.8531 | 0.36068 | 6.5 | 6.6 | 152 | 641 | 1031 | 1092.3846 | -5.9539 | 50.8091 | 866.6923 | 82.4621 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1989-10-04 |  | 1658.8 | 24 | 136 | 62 | 46 | 0 | 8.8 | 3.2 |  | 12 | 12 | 0.73333 | 0 | 17.6 | 17.6 | 5.6762 | 47.3237 | 0.37191 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 966.25 | 6.2803 | 77.3463 | 637.625 | 89.0218 | 136 | 95 | 55 | 6.8053 | 5.1947 | 12 | 12 | 0.31925 | 0.56711 | 20.416 | 20.416 | 4.3196 | 56.1804 | 0.3634 | 6 | 6.5 | 48 | 309 | 641 | 650.9261 | -1.5485 | 84.466 | 479.963 | 89.9992 | 95 | 62 | 37 | 1.9947 | 3.2 | 5.1947 | 5.1947 | 0.31172 | 0.38398 | 11.968 | 11.968 | 6.414 | 35.0859 | 0.34111 | 6.5 | 6.6 | 152 | 641 | 1031 | 945.81 | 8.2629 | 50.8091 | 793.405 | 80.8421 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1989-10-05 |  | 1680.4 | 24 | 136 | 63 | 46.5 | 0 | 9.1 | 3.1 |  | 12.2 | 12.2 | 0.7459 | 0 | 18.2 | 18.2 | 5.8979 | 47.1021 | 0.38639 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1010.5806 | 1.9805 | 77.3463 | 659.7903 | 89.3906 | 136 | 96 | 56 | 7.15 | 5.05 | 12.2 | 12.2 | 0.32028 | 0.58607 | 21.45 | 21.45 | 4.4577 | 55.5423 | 0.38619 | 6 | 6.5 | 48 | 309 | 641 | 678.5347 | -5.8556 | 84.466 | 493.7673 | 90.2788 | 96 | 63 | 37 | 1.95 | 3.1 | 5.05 | 5.05 | 0.30264 | 0.38614 | 11.7 | 11.7 | 6.428 | 36.072 | 0.32435 | 6.5 | 6.6 | 152 | 641 | 1031 | 948.5968 | 7.9926 | 50.8091 | 794.7984 | 80.8757 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1989-10-06 |  | 1701.9 | 24 | 136 | 62 | 45.5 | 0 | 9.3 | 3.1 |  | 12.4 | 12.4 | 0.75 | 0 | 18.6 | 18.6 | 5.975 | 47.525 | 0.39137 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1026 | 0.48497 | 77.3463 | 667.5 | 89.5131 | 136 | 95 | 55 | 7.1185 | 5.2815 | 12.4 | 12.4 | 0.32829 | 0.57407 | 21.3556 | 21.3556 | 4.3689 | 56.1311 | 0.38046 | 6 | 6.5 | 48 | 309 | 641 | 660.7826 | -3.0862 | 84.466 | 484.8913 | 90.1009 | 95 | 62 | 36 | 2.1815 | 3.1 | 5.2815 | 5.2815 | 0.31123 | 0.41304 | 13.0889 | 13.0889 | 6.6106 | 35.8894 | 0.3647 | 6.5 | 6.6 | 152 | 641 | 1031 | 985.1111 | 4.4509 | 50.8091 | 813.0556 | 81.3051 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1989-10-09 |  | 1771.8 | 24 | 137 | 63 | 46.5 | 0 | 9 | 3.1 |  | 12.1 | 12.1 | 0.7438 | 0 | 18 | 18 | 5.8594 | 47.6406 | 0.37783 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1002.871 | 2.7283 | 77.3463 | 655.9355 | 89.3282 | 137 | 96 | 55 | 6.9398 | 5.1602 | 12.1 | 12.1 | 0.32047 | 0.57353 | 20.8193 | 20.8193 | 4.365 | 57.135 | 0.36439 | 6 | 6.5 | 48 | 309 | 641 | 660.0063 | -2.9651 | 84.466 | 484.5032 | 90.0929 | 96 | 63 | 38 | 2.0602 | 3.1 | 5.1602 | 5.1602 | 0.30673 | 0.39925 | 12.3614 | 12.3614 | 6.5149 | 34.9851 | 0.35333 | 6.5 | 6.6 | 152 | 641 | 1031 | 965.9864 | 6.3059 | 50.8091 | 803.4932 | 81.0826 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1989-10-10 |  | 1797.1 | 24 | 137 | 63 | 46 | 0 | 9.1 | 3.2 |  | 12.3 | 12.3 | 0.73984 | 0 | 18.2 | 18.2 | 5.7883 | 48.2117 | 0.3775 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 988.6562 | 4.1071 | 77.3463 | 648.8281 | 89.2113 | 137 | 95 | 55 | 7.0169 | 5.2831 | 12.3 | 12.3 | 0.32646 | 0.57048 | 21.0506 | 21.0506 | 4.3433 | 56.6567 | 0.37155 | 6 | 6.5 | 48 | 309 | 641 | 655.6509 | -2.2856 | 84.466 | 482.3254 | 90.0482 | 95 | 63 | 37 | 2.0831 | 3.2 | 5.2831 | 5.2831 | 0.31501 | 0.3943 | 12.4988 | 12.4988 | 6.4816 | 35.5184 | 0.3519 | 6.5 | 6.6 | 152 | 641 | 1031 | 959.3287 | 6.9516 | 50.8091 | 800.1643 | 81.0039 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1989-10-11 |  | 1819.2 | 24 | 137 | 62 | 45.5 | 0 | 9.3 | 3.1 |  | 12.4 | 12.4 | 0.75 | 0 | 18.6 | 18.6 | 5.975 | 48.025 | 0.3873 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1026 | 0.48497 | 77.3463 | 667.5 | 89.5131 | 137 | 95 | 55 | 7.1711 | 5.2289 | 12.4 | 12.4 | 0.32731 | 0.57831 | 21.5133 | 21.5133 | 4.3997 | 56.6003 | 0.38009 | 6 | 6.5 | 48 | 309 | 641 | 666.9429 | -4.0472 | 84.466 | 487.9714 | 90.1634 | 95 | 62 | 36 | 2.1289 | 3.1 | 5.2289 | 5.2289 | 0.30928 | 0.40714 | 12.7735 | 12.7735 | 6.5691 | 35.9309 | 0.3555 | 6.5 | 6.6 | 152 | 641 | 1031 | 976.8193 | 5.2552 | 50.8091 | 808.9096 | 81.2093 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1989-10-12 |  | 1843.6 | 24 | 137 | 64 | 45.5 | 0 | 9 | 3.1 |  | 12.1 | 12.1 | 0.7438 | 0 | 18 | 18 | 5.8594 | 49.1406 | 0.3663 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1002.871 | 2.7283 | 77.3463 | 655.9355 | 89.3282 | 137 | 95 | 54 | 7.0244 | 5.0756 | 12.1 | 12.1 | 0.3189 | 0.58053 | 21.0732 | 21.0732 | 4.4161 | 57.5839 | 0.36596 | 6 | 6.5 | 48 | 309 | 641 | 670.211 | -4.5571 | 84.466 | 489.6055 | 90.1962 | 95 | 64 | 37 | 1.9756 | 3.1 | 5.0756 | 5.0756 | 0.30359 | 0.38924 | 11.8537 | 11.8537 | 6.4482 | 36.0518 | 0.3288 | 6.5 | 6.6 | 152 | 641 | 1031 | 952.6365 | 7.6007 | 50.8091 | 796.8183 | 80.9241 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1989-10-13 |  | 1867.9 | 24 | 137 | 62 | 45 | 0 | 9.2 | 3.1 |  | 12.3 | 12.3 | 0.74797 | 0 | 18.4 | 18.4 | 5.9365 | 48.5635 | 0.37888 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1018.2903 | 1.2328 | 77.3463 | 663.6452 | 89.4522 | 137 | 95 | 55 | 7.094 | 5.206 | 12.3 | 12.3 | 0.32503 | 0.57675 | 21.2819 | 21.2819 | 4.3883 | 56.6117 | 0.37593 | 6 | 6.5 | 48 | 309 | 641 | 664.651 | -3.6897 | 84.466 | 486.8255 | 90.1402 | 95 | 62 | 35 | 2.106 | 3.1 | 5.206 | 5.206 | 0.30843 | 0.40454 | 12.6361 | 12.6361 | 6.551 | 36.949 | 0.34199 | 6.5 | 6.6 | 152 | 641 | 1031 | 973.2083 | 5.6054 | 50.8091 | 807.1042 | 81.1672 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1989-10-16 |  | 1937.6 | 24 | 138 | 62 | 45 | 0 | 9 | 3.1 |  | 12.1 | 12.1 | 0.7438 | 0 | 18 | 18 | 5.8594 | 49.1406 | 0.3663 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1002.871 | 2.7283 | 77.3463 | 655.9355 | 89.3282 | 138 | 95 | 55 | 7.0244 | 5.0756 | 12.1 | 12.1 | 0.3189 | 0.58053 | 21.0732 | 21.0732 | 4.4161 | 57.0839 | 0.36916 | 6 | 6.5 | 48 | 309 | 641 | 670.211 | -4.5571 | 84.466 | 489.6055 | 90.1962 | 95 | 62 | 35 | 1.9756 | 3.1 | 5.0756 | 5.0756 | 0.30359 | 0.38924 | 11.8537 | 11.8537 | 6.4482 | 37.0518 | 0.31992 | 6.5 | 6.6 | 152 | 641 | 1031 | 952.6365 | 7.6007 | 50.8091 | 796.8183 | 80.9241 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1989-10-17 |  | 1961.9 | 24 | 137 | 62 | 44.5 | 0 | 9 | 3.1 |  | 12.1 | 12.1 | 0.7438 | 0 | 18 | 18 | 5.8594 | 49.1406 | 0.3663 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1002.871 | 2.7283 | 77.3463 | 655.9355 | 89.3282 | 137 | 95 | 54 | 7 | 5.1 | 12.1 | 12.1 | 0.31935 | 0.57851 | 21 | 21 | 4.4012 | 57.5988 | 0.36459 | 6 | 6.5 | 48 | 309 | 641 | 667.2353 | -4.0929 | 84.466 | 488.1176 | 90.1663 | 95 | 62 | 35 | 2 | 3.1 | 5.1 | 5.1 | 0.30449 | 0.39216 | 12 | 12 | 6.4674 | 37.0326 | 0.32404 | 6.5 | 6.6 | 152 | 641 | 1031 | 956.4839 | 7.2276 | 50.8091 | 798.7419 | 80.9701 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1989-10-18 |  | 1984.6 | 24 | 138 | 60 | 45 | 0 | 9.3 | 3 |  | 12.3 | 12.3 | 0.7561 | 0 | 18.6 | 18.6 | 6.0945 | 47.9055 | 0.38826 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1049.9 | -1.8332 | 77.3463 | 679.45 | 89.6975 | 138 | 95 | 55 | 7.2585 | 5.0415 | 12.3 | 12.3 | 0.32197 | 0.59012 | 21.7756 | 21.7756 | 4.4889 | 57.0111 | 0.38195 | 6 | 6.5 | 48 | 309 | 641 | 684.7794 | -6.8299 | 84.466 | 496.8897 | 90.3399 | 95 | 60 | 35 | 2.0415 | 3 | 5.0415 | 5.0415 | 0.29861 | 0.40493 | 12.2488 | 12.2488 | 6.5538 | 35.9462 | 0.34075 | 6.5 | 6.6 | 152 | 641 | 1031 | 973.7585 | 5.552 | 50.8091 | 807.3793 | 81.1737
[11 empty] | 1989-10-19 |  | 2007.5 | 24 | 137 | 62 | 45 | 0 | 9.1 | 3.1 |  | 12.2 | 12.2 | 0.7459 | 0 | 18.2 | 18.2 | 5.8979 | 48.6021 | 0.37447 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1010.5806 | 1.9805 | 77.3463 | 659.7903 | 89.3906 | 137 | 95 | 55 | 7.1024 | 5.0976 | 12.2 | 12.2 | 0.32116 | 0.58217 | 21.3073 | 21.3073 | 4.4283 | 56.5717 | 0.37664 | 6 | 6.5 | 48 | 309 | 641 | 672.6517 | -4.9379 | 84.466 | 490.8258 | 90.2206 | 95 | 62 | 35 | 1.9976 | 3.1 | 5.0976 | 5.0976 | 0.3044 | 0.39187 | 11.9854 | 11.9854 | 6.4655 | 37.0345 | 0.32363 | 6.5 | 6.6 | 152 | 641 | 1031 | 956.0991 | 7.2649 | 50.8091 | 798.5496 | 80.9655
[11 empty] | 1989-10-20 |  | 2029 | 24 | 138 | 62 | 45 | 0 | 8.8 | 3 |  | 11.8 | 11.8 | 0.74576 | 0 | 17.6 | 17.6 | 5.8953 | 49.1047 | 0.35842 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1010.0667 | 2.0304 | 77.3463 | 659.5333 | 89.3864 | 138 | 96 | 55 | 6.8683 | 4.9317 | 11.8 | 11.8 | 0.31065 | 0.58206 | 20.6049 | 20.6049 | 4.4274 | 57.5726 | 0.35789 | 6 | 6.5 | 48 | 309 | 641 | 672.4896 | -4.9126 | 84.466 | 490.7448 | 90.2189 | 96 | 62 | 35 | 1.9317 | 3 | 4.9317 | 4.9317 | 0.29453 | 0.39169 | 11.5902 | 11.5902 | 6.4643 | 37.5357 | 0.30878 | 6.5 | 6.6 | 152 | 641 | 1031 | 955.8683 | 7.2873 | 50.8091 | 798.4341 | 80.9627
[11 empty] | 1989-10-23 |  | 2101.1 | 24 | 139 | 60 | 45 | 0 | 8.8 | 3 |  | 11.8 | 11.8 | 0.74576 | 0 | 17.6 | 17.6 | 5.8953 | 48.6047 | 0.36211 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1010.0667 | 2.0304 | 77.3463 | 659.5333 | 89.3864 | 139 | 96 | 55 | 6.8683 | 4.9317 | 11.8 | 11.8 | 0.31065 | 0.58206 | 20.6049 | 20.6049 | 4.4274 | 58.0726 | 0.35481 | 6 | 6.5 | 48 | 309 | 641 | 672.4896 | -4.9126 | 84.466 | 490.7448 | 90.2189 | 96 | 60 | 35 | 1.9317 | 3 | 4.9317 | 4.9317 | 0.29453 | 0.39169 | 11.5902 | 11.5902 | 6.4643 | 36.5357 | 0.31723 | 6.5 | 6.6 | 152 | 641 | 1031 | 955.8683 | 7.2873 | 50.8091 | 798.4341 | 80.9627
[11 empty] | 1989-10-24 |  | 2125.3 | 24 | 139 | 58 | 44 | 0 | 9 | 2.9 |  | 11.9 | 11.9 | 0.7563 | 0 | 18 | 18 | 6.0986 | 48.4014 | 0.37189 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1050.7241 | -1.9131 | 77.3463 | 679.8621 | 89.7038 | 139 | 96 | 54 | 7.0633 | 4.8367 | 11.9 | 11.9 | 0.31075 | 0.59355 | 21.1899 | 21.1899 | 4.5158 | 58.9842 | 0.35925 | 6 | 6.5 | 48 | 309 | 641 | 690.1515 | -7.6679 | 84.466 | 499.5758 | 90.3918 | 96 | 58 | 34 | 1.9367 | 2.9 | 4.8367 | 4.8367 | 0.28729 | 0.40042 | 11.6203 | 11.6203 | 6.5228 | 36.4772 | 0.31856 | 6.5 | 6.6 | 152 | 641 | 1031 | 967.5692 | 6.1524 | 50.8091 | 804.2846 | 81.1012
[11 empty] | 1989-10-25 |  | 2150 | 24 | 139 | 57 | 43.5 | 0 | 8.8 | 2.9 |  | 11.7 | 11.7 | 0.75214 | 0 | 17.6 | 17.6 | 6.0162 | 48.4838 | 0.36301 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1034.2414 | -0.31439 | 77.3463 | 671.6207 | 89.5775 | 139 | 96 | 53 | 6.9531 | 4.7469 | 11.7 | 11.7 | 0.30537 | 0.59428 | 20.8593 | 20.8593 | 4.5215 | 59.9785 | 0.34778 | 6 | 6.5 | 48 | 309 | 641 | 691.3022 | -7.8475 | 84.466 | 500.1511 | 90.4029 | 96 | 57 | 34 | 1.8469 | 2.9 | 4.7469 | 4.7469 | 0.28396 | 0.38908 | 11.0815 | 11.0815 | 6.4471 | 36.0529 | 0.30737 | 6.5 | 6.6 | 152 | 641 | 1031 | 952.4278 | 7.621 | 50.8091 | 796.7139 | 80.9216
[11 empty] | 1989-10-26 |  | 2173.4 | 24 | 139 | 58 | 44 | 0 | 9.1 | 2.9 |  | 12 | 12 | 0.75833 | 0 | 18.2 | 18.2 | 6.1398 | 48.3602 | 0.37634 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1058.9655 | -2.7125 | 77.3463 | 683.9828 | 89.7658 | 139 | 95 | 54 | 7.2333 | 4.7667 | 12 | 12 | 0.3113 | 0.60278 | 21.7 | 21.7 | 4.5903 | 58.4097 | 0.37151 | 6 | 6.5 | 48 | 309 | 641 | 705.0629 | -9.9942 | 84.466 | 507.0315 | 90.5331 | 95 | 58 | 34 | 1.8667 | 2.9 | 4.7667 | 4.7667 | 0.28469 | 0.39161 | 11.2 | 11.2 | 6.4638 | 36.0362 | 0.3108 | 6.5 | 6.6 | 152 | 641 | 1031 | 955.7586 | 7.2979 | 50.8091 | 798.3793 | 80.9614
[11 empty] | 1989-10-27 |  | 2196.3 | 24 | 140 | 59 | 41.5 | 0 | 9.1 | 2.9 |  | 12 | 12 | 0.75833 | 0 | 18.2 | 18.2 | 6.1398 | 51.8602 | 0.35094 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1058.9655 | -2.7125 | 77.3463 | 683.9828 | 89.7658 | 140 | 97 | 50 | 7.28 | 4.72 | 12 | 12 | 0.31044 | 0.60667 | 21.84 | 21.84 | 4.6228 | 63.8772 | 0.34191 | 6 | 6.5 | 48 | 309 | 641 | 711.5593 | -11.0077 | 84.466 | 510.2797 | 90.5934 | 97 | 59 | 33 | 1.82 | 2.9 | 4.72 | 4.72 | 0.28296 | 0.38559 | 10.92 | 10.92 | 6.4244 | 38.5756 | 0.28308 | 6.5 | 6.6 | 152 | 641 | 1031 | 947.8897 | 8.0611 | 50.8091 | 794.4448 | 80.8671
[11 empty] | 1989-10-30 |  | 2266.4 | 24 | 140 | 59 | 42.5 | 0 | 9.6 | 2.8 |  | 12.4 | 12.4 | 0.77419 | 0 | 19.2 | 19.2 | 6.4871 | 50.5129 | 0.3801 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1128.4286 | -9.4499 | 77.3463 | 718.7143 | 90.2604 | 140 | 99 | 50 | 7.6274 | 4.7726 | 12.4 | 12.4 | 0.31884 | 0.61511 | 22.8822 | 22.8822 | 4.6956 | 64.8044 | 0.3531 | 6 | 6.5 | 48 | 309 | 641 | 726.1206 | -13.2793 | 84.466 | 517.5603 | 90.7257 | 99 | 59 | 35 | 1.9726 | 2.8 | 4.7726 | 4.7726 | 0.2812 | 0.41332 | 11.8356 | 11.8356 | 6.6125 | 37.3875 | 0.31657 | 6.5 | 6.6 | 152 | 641 | 1031 | 985.501 | 4.4131 | 50.8091 | 813.2505 | 81.3096
[11 empty] | 1989-10-31 |  | 2292.1 | 24 | 140 | 57 | 43 | 0 | 8.8 | 2.9 |  | 11.7 | 11.7 | 0.75214 | 0 | 17.6 | 17.6 | 6.0162 | 49.4838 | 0.35567 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1034.2414 | -0.31439 | 77.3463 | 671.6207 | 89.5775 | 140 | 97 | 53 | 6.9063 | 4.7937 | 11.7 | 11.7 | 0.30623 | 0.59028 | 20.719 | 20.719 | 4.4901 | 61.0099 | 0.3396 | 6 | 6.5 | 48 | 309 | 641 | 685.0275 | -6.8686 | 84.466 | 497.0137 | 90.3423 | 97 | 57 | 33 | 1.8937 | 2.9 | 4.7937 | 4.7937 | 0.28569 | 0.39504 | 11.362 | 11.362 | 6.4866 | 37.5134 | 0.30288 | 6.5 | 6.6 | 152 | 641 | 1031 | 960.3121 | 6.8562 | 50.8091 | 800.656 | 81.0156
[11 empty] | 1989-11-01 |  | 2314.2 | 24 | 141 | 57 | 43 | 0 | 9.1 | 3.5 |  | 12.6 | 12.6 | 0.72222 | 0 | 18.2 | 18.2 | 5.497 | 50.503 | 0.36037 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 930.4 | 9.7575 | 77.3463 | 619.7 | 88.7042 | 141 | 98 | 52 | 7.1418 | 5.4582 | 12.6 | 12.6 | 0.33528 | 0.56681 | 21.4253 | 21.4253 | 4.3175 | 63.1825 | 0.3391 | 6 | 6.5 | 48 | 309 | 641 | 650.5032 | -1.4826 | 84.466 | 479.7516 | 89.9948 | 98 | 57 | 34 | 1.9582 | 3.5 | 5.4582 | 5.4582 | 0.33265 | 0.35877 | 11.7494 | 11.7494 | 6.258 | 37.242 | 0.31549 | 6.5 | 6.6 | 152 | 641 | 1031 | 914.5924 | 11.2907 | 50.8091 | 777.7962 | 80.4576
[11 empty] | 1989-11-02 |  | 2339.9 | 24 | 139 | 60 | 44 | 0 | 8.5 | 2.3 |  | 10.8 | 10.8 | 0.78704 | 0 | 17 | 17 | 6.8063 | 48.6937 | 0.34912 | 7.5 | 6 | 70 | 264 | 309 | 1031 | 1192.2609 | -15.6412 | 77.3463 | 750.6304 | 90.6745 | 139 | 97 | 53 | 6.716 | 4.084 | 10.8 | 10.8 | 0.27635 | 0.62186 | 20.1481 | 20.1481 | 4.7561 | 60.2439 | 0.33444 | 6 | 6.5 | 48 | 309 | 641 | 738.214 | -15.166 | 84.466 | 523.607 | 90.8328 | 97 | 60 | 35 | 1.784 | 2.3 | 4.084 | 4.084 | 0.23706 | 0.43682 | 10.7037 | 10.7037 | 6.7864 | 36.7136 | 0.29155 | 6.5 | 6.6 | 152 | 641 | 1031 | 1020.2834 | 1.0394 | 50.8091 | 830.6417 | 81.7009
[11 empty] | 1989-11-03 |  | 2363.4 | 24 | 139 | 57 | 42 | 0 | 8.8 | 2.9 |  | 11.7 | 11.7 | 0.75214 | 0 | 17.6 | 17.6 | 6.4441 | 49.5559 | 0.35515 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1116.8276 | -1.5298 | 75.2941 | 728.4138 | 88.4681 | 139 | 97 | 51 | 6.93 | 4.77 | 11.7 | 11.7 | 0.30579 | 0.59231 | 20.79 | 20.79 | 4.5059 | 62.4941 | 0.33267 | 5.9 | 6.2 | 48 | 309 | 641 | 688.1887 | -7.3617 | 85.8824 | 498.5943 | 90.3729 | 97 | 57 | 33 | 1.87 | 2.9 | 4.77 | 4.77 | 0.28481 | 0.39203 | 11.22 | 11.22 | 5.8318 | 38.1682 | 0.29396 | 6.2 | 6.3 | 200 | 641 | 1100 | 925.369 | 15.8755 | 41.1765 | 783.1845 | 74.4632
[11 empty] | 1989-11-06 |  | 2434.1 | 24 | 140 | 57 | 42 | 0 | 9 | 2.7 |  | 11.7 | 11.7 | 0.76923 | 0 | 18 | 18 | 6.8267 | 49.6733 | 0.36237 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1193.3333 | -8.4848 | 75.2941 | 766.6667 | 89.0435 | 140 | 98 | 52 | 7.0633 | 4.6367 | 11.7 | 11.7 | 0.30332 | 0.6037 | 21.1899 | 21.1899 | 4.598 | 62.402 | 0.33957 | 5.9 | 6.2 | 48 | 309 | 641 | 706.5921 | -10.2328 | 85.8824 | 507.7961 | 90.5474 | 98 | 57 | 32 | 1.9367 | 2.7 | 4.6367 | 4.6367 | 0.27244 | 0.41769 | 11.6203 | 11.6203 | 5.9916 | 39.5084 | 0.29412 | 6.2 | 6.3 | 200 | 641 | 1100 | 957.3291 | 12.9701 | 41.1765 | 799.1646 | 74.9739
[11 empty] | 1989-11-07 |  | 2458.3 | 24 | 140 | 57 | 41.5 | 0 | 8.6 | 2.75 |  | 11.35 | 11.35 | 0.75771 | 0 | 17.2 | 17.2 | 6.5629 | 50.4371 | 0.34102 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1140.5818 | -3.6893 | 75.2941 | 740.2909 | 88.6531 | 140 | 98 | 51 | 6.7951 | 4.5549 | 11.35 | 11.35 | 0.2953 | 0.59868 | 20.3852 | 20.3852 | 4.8536 | 63.1464 | 0.32282 | 5.9 | 6.2 | 62 | 340 | 700 | 754.7207 | -7.8172 | 81.7647 | 547.3603 | 88.6729 | 98 | 57 | 32 | 1.8049 | 2.75 | 4.5549 | 4.5549 | 0.27126 | 0.39626 | 10.8296 | 10.8296 | 5.8572 | 39.6428 | 0.27318 | 6.2 | 6.3 | 200 | 641 | 1100 | 930.4465 | 15.414 | 41.1765 | 785.7232 | 74.5457
[11 empty] | 1989-11-08 |  | 2479.8 | 24 | 140 | 57 | 42.5 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 49.363 | 0.34844 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 140 | 97 | 52 | 6.7951 | 4.5049 | 11.3 | 11.3 | 0.29345 | 0.60133 | 20.3852 | 20.3852 | 4.8766 | 61.6234 | 0.3308 | 5.9 | 6.2 | 62 | 340 | 700 | 759.3237 | -8.4748 | 81.7647 | 549.6618 | 88.7203 | 97 | 57 | 33 | 1.8049 | 2.7 | 4.5049 | 4.5049 | 0.26754 | 0.40066 | 10.8296 | 10.8296 | 5.884 | 38.116 | 0.28412 | 6.2 | 6.3 | 200 | 641 | 1100 | 935.8066 | 14.9267 | 41.1765 | 788.4033 | 74.6323
[11 empty] | 1989-11-09 |  | 2506.6 | 24 | 140 | 57 | 41.5 | 0 | 8.8 | 2.8 |  | 11.6 | 11.6 | 0.75862 | 0 | 17.6 | 17.6 | 6.5829 | 50.4171 | 0.34909 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1144.5714 | -4.0519 | 75.2941 | 742.2857 | 88.6836 | 140 | 98 | 51 | 6.9531 | 4.6469 | 11.6 | 11.6 | 0.30165 | 0.5994 | 20.8593 | 20.8593 | 4.8598 | 63.1402 | 0.33036 | 5.9 | 6.2 | 62 | 340 | 700 | 755.966 | -7.9951 | 81.7647 | 547.983 | 88.6858 | 98 | 57 | 32 | 1.8469 | 2.8 | 4.6469 | 4.6469 | 0.27653 | 0.39745 | 11.0815 | 11.0815 | 5.8644 | 39.6356 | 0.27958 | 6.2 | 6.3 | 200 | 641 | 1100 | 931.8889 | 15.2828 | 41.1765 | 786.4444 | 74.5691
[11 empty] | 1989-11-13 |  | 2598.2 | 24 | 140 | 56 | 41.5 | 0 | 8.5 | 2.75 |  | 11.25 | 11.25 | 0.75556 | 0 | 17 | 17 | 6.5164 | 49.9836 | 0.34011 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1131.2727 | -2.843 | 75.2941 | 735.6364 | 88.5813 | 140 | 98 | 51 | 6.716 | 4.534 | 11.25 | 11.25 | 0.29306 | 0.59698 | 20.1481 | 20.1481 | 4.839 | 63.161 | 0.319 | 5.9 | 6.2 | 62 | 340 | 700 | 751.7958 | -7.3994 | 81.7647 | 545.8979 | 88.6426 | 98 | 56 | 32 | 1.784 | 2.75 | 4.534 | 4.534 | 0.27048 | 0.39346 | 10.7037 | 10.7037 | 5.8404 | 39.1596 | 0.27334 | 6.2 | 6.3 | 200 | 641 | 1100 | 927.0808 | 15.7199 | 41.1765 | 784.0404 | 74.4911
[11 empty] | 1989-11-15 |  | 2647.1 | 24 | 140 | 56 | 40.5 | 0 | 8.8 | 2.7 |  | 11.5 | 11.5 | 0.76522 | 0 | 17.6 | 17.6 | 6.7319 | 50.7681 | 0.34667 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1174.3704 | -6.7609 | 75.2941 | 757.1852 | 88.9063 | 140 | 98 | 50 | 7.04 | 4.46 | 11.5 | 11.5 | 0.29633 | 0.61217 | 21.12 | 21.12 | 4.9741 | 64.0259 | 0.32987 | 5.9 | 6.2 | 62 | 340 | 700 | 778.8161 | -11.2594 | 81.7647 | 559.4081 | 88.9169 | 98 | 56 | 31 | 1.76 | 2.7 | 4.46 | 4.46 | 0.26588 | 0.39462 | 10.56 | 10.56 | 5.8473 | 40.1527 | 0.263 | 6.2 | 6.3 | 200 | 641 | 1100 | 928.4667 | 15.5939 | 41.1765 | 784.7333 | 74.5136
[11 empty] | 1989-11-16 |  | 2669.4 | 24 | 140 | 56 | 41 | 0 | 8.4 | 2.7 |  | 11.1 | 11.1 | 0.75676 | 0 | 16.8 | 16.8 | 6.5422 | 50.4578 | 0.33295 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1136.4444 | -3.3131 | 75.2941 | 738.2222 | 88.6213 | 140 | 98 | 50 | 6.6769 | 4.4231 | 11.1 | 11.1 | 0.28821 | 0.60152 | 20.0308 | 20.0308 | 4.8783 | 64.1217 | 0.31239 | 5.9 | 6.2 | 62 | 340 | 700 | 759.6591 | -8.5227 | 81.7647 | 549.8296 | 88.7238 | 98 | 56 | 32 | 1.7231 | 2.7 | 4.4231 | 4.4231 | 0.2645 | 0.38957 | 10.3385 | 10.3385 | 5.8172 | 39.1828 | 0.26385 | 6.2 | 6.3 | 200 | 641 | 1100 | 922.4359 | 16.1422 | 41.1765 | 781.7179 | 74.4153
[11 empty] | 1989-11-17 |  | 2691.9 | 24 | 140 | 55 | 42.5 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 48.363 | 0.35564 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 140 | 97 | 50 | 6.8386 | 4.4614 | 11.3 | 11.3 | 0.29264 | 0.60518 | 20.5157 | 20.5157 | 4.9106 | 63.5894 | 0.32263 | 5.9 | 6.2 | 62 | 340 | 700 | 766.1215 | -9.4459 | 81.7647 | 553.0608 | 88.7897 | 97 | 55 | 35 | 1.7614 | 2.7 | 4.4614 | 4.4614 | 0.26593 | 0.39482 | 10.5687 | 10.5687 | 5.8485 | 35.1515 | 0.30066 | 6.2 | 6.3 | 200 | 641 | 1100 | 928.7028 | 15.5725 | 41.1765 | 784.8514 | 74.5175
[11 empty] | 1989-11-20 |  | 2765.4 | 24 | 141 | 56 | 40 | 0 | 8.8 | 2.9 |  | 11.7 | 11.7 | 0.75214 | 0 | 17.6 | 17.6 | 6.4441 | 52.0559 | 0.3381 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1116.8276 | -1.5298 | 75.2941 | 728.4138 | 88.4681 | 141 | 98 | 50 | 7.0857 | 4.6143 | 11.7 | 11.7 | 0.3029 | 0.60562 | 21.2571 | 21.2571 | 4.9145 | 64.5855 | 0.32913 | 5.9 | 6.2 | 62 | 340 | 700 | 766.8978 | -9.5568 | 81.7647 | 553.4489 | 88.7975 | 98 | 56 | 30 | 1.7143 | 2.9 | 4.6143 | 4.6143 | 0.27903 | 0.37152 | 10.2857 | 10.2857 | 5.7134 | 41.2866 | 0.24913 | 6.2 | 6.3 | 200 | 641 | 1100 | 901.6897 | 18.0282 | 41.1765 | 771.3448 | 74.0713
[11 empty] | 1989-11-21 |  | 2787.5 | 24 | 142 | 57 | 39.5 | 0 | 8.7 | 2.7 |  | 11.4 | 11.4 | 0.76316 | 0 | 17.4 | 17.4 | 6.6844 | 53.3156 | 0.32636 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1164.8889 | -5.899 | 75.2941 | 752.4444 | 88.8364 | 142 | 100 | 49 | 6.6841 | 4.7159 | 11.4 | 11.4 | 0.29922 | 0.58633 | 20.0524 | 20.0524 | 4.7502 | 67.2498 | 0.29818 | 5.9 | 6.2 | 62 | 340 | 700 | 734.031 | -4.8616 | 81.7647 | 537.0155 | 88.4547 | 100 | 57 | 30 | 2.0159 | 2.7 | 4.7159 | 4.7159 | 0.27538 | 0.42746 | 12.0951 | 12.0951 | 6.0563 | 42.4437 | 0.28497 | 6.2 | 6.3 | 200 | 641 | 1100 | 970.2561 | 11.7949 | 41.1765 | 805.628 | 75.1746
[11 empty] | 1989-11-22 |  | 2811.6 | 24 | 140 | 55 | 40 | 0 | 8.7 | 2.7 |  | 11.4 | 11.4 | 0.76316 | 0 | 17.4 | 17.4 | 6.6844 | 50.8156 | 0.34241 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1164.8889 | -5.899 | 75.2941 | 752.4444 | 88.8364 | 140 | 98 | 50 | 7.0315 | 4.3685 | 11.4 | 11.4 | 0.29277 | 0.6168 | 21.0945 | 21.0945 | 5.0173 | 63.9827 | 0.32969 | 5.9 | 6.2 | 62 | 340 | 700 | 787.4675 | -12.4954 | 81.7647 | 563.7338 | 89.0019 | 98 | 55 | 30 | 1.6685 | 2.7 | 4.3685 | 4.3685 | 0.26248 | 0.38194 | 10.011 | 10.011 | 5.7726 | 40.7274 | 0.2458 | 6.2 | 6.3 | 200 | 641 | 1100 | 913.5205 | 16.9527 | 41.1765 | 777.2603 | 74.2686
[11 empty] | 1989-11-27 |  | 2931.1 | 24 | 141 | 55 | 39.5 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 51.863 | 0.33164 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 141 | 97 | 49 | 6.9462 | 4.3538 | 11.3 | 11.3 | 0.29064 | 0.6147 | 20.8385 | 20.8385 | 4.9976 | 65.0024 | 0.32058 | 5.9 | 6.2 | 62 | 340 | 700 | 783.523 | -11.9319 | 81.7647 | 561.7615 | 88.9633 | 97 | 55 | 30 | 1.6538 | 2.7 | 4.3538 | 4.3538 | 0.26193 | 0.37986 | 9.9231 | 9.9231 | 5.7606 | 40.2394 | 0.2466 | 6.2 | 6.3 | 200 | 641 | 1100 | 911.1282 | 17.1702 | 41.1765 | 776.0641 | 74.2289
[11 empty] | 1989-11-28 |  | 2956 | 24 | 140 | 56 | 40 | 0 | 8.7 | 3 |  | 11.7 | 11.7 | 0.74359 | 0 | 17.4 | 17.4 | 6.272 | 51.728 | 0.33637 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1082.4 | 1.6 | 75.2941 | 711.2 | 88.189 | 140 | 99 | 50 | 6.96 | 4.74 | 11.7 | 11.7 | 0.30524 | 0.59487 | 20.88 | 20.88 | 4.821 | 64.679 | 0.32283 | 5.9 | 6.2 | 62 | 340 | 700 | 748.2025 | -6.8861 | 81.7647 | 544.1013 | 88.6051 | 99 | 56 | 30 | 1.74 | 3 | 4.74 | 4.74 | 0.28741 | 0.36709 | 10.44 | 10.44 | 5.6889 | 41.8111 | 0.24969 | 6.2 | 6.3 | 200 | 641 | 1100 | 896.78 | 18.4745 | 41.1765 | 768.89 | 73.9885
[11 empty] | 1989-11-29 |  | 2979.5 | 24 | 141 | 54 | 39.5 | 0 | 8.5 | 2.8 |  | 11.3 | 11.3 | 0.75221 | 0 | 17 | 17 | 6.4457 | 51.5543 | 0.32975 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1117.1429 | -1.5584 | 75.2941 | 728.5714 | 88.4706 | 141 | 98 | 49 | 6.8442 | 4.4558 | 11.3 | 11.3 | 0.29253 | 0.60568 | 20.5325 | 20.5325 | 4.915 | 65.585 | 0.31307 | 5.9 | 6.2 | 62 | 340 | 700 | 767.0067 | -9.5724 | 81.7647 | 553.5034 | 88.7986 | 98 | 54 | 30 | 1.6558 | 2.8 | 4.4558 | 4.4558 | 0.26943 | 0.37161 | 9.9351 | 9.9351 | 5.714 | 40.286 | 0.24661 | 6.2 | 6.3 | 200 | 641 | 1100 | 901.7955 | 18.0186 | 41.1765 | 771.3977 | 74.073
[11 empty] | 1989-11-30 |  | 3004 | 24 | 141 | 55 | 40 | 0 | 8.6 | 2.75 |  | 11.35 | 11.35 | 0.75771 | 0 | 17.2 | 17.2 | 6.5629 | 51.4371 | 0.33439 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1140.5818 | -3.6893 | 75.2941 | 740.2909 | 88.6531 | 141 | 97 | 50 | 6.9247 | 4.4253 | 11.35 | 11.35 | 0.2929 | 0.6101 | 20.774 | 20.774 | 4.955 | 64.045 | 0.32437 | 5.9 | 6.2 | 62 | 340 | 700 | 775.0098 | -10.7157 | 81.7647 | 557.5049 | 88.879 | 97 | 55 | 30 | 1.6753 | 2.75 | 4.4253 | 4.4253 | 0.26644 | 0.37858 | 10.0519 | 10.0519 | 5.7533 | 40.2467 | 0.24976 | 6.2 | 6.3 | 200 | 641 | 1100 | 909.6612 | 17.3035 | 41.1765 | 775.3306 | 74.2046
[11 empty] | 1989-12-01 |  | 3025.1 | 24 | 141 | 54 | 40 | 0 | 8.8 | 2.8 |  | 11.6 | 11.6 | 0.75862 | 0 | 17.6 | 17.6 | 6.5829 | 50.9171 | 0.34566 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1144.5714 | -4.0519 | 75.2941 | 742.2857 | 88.6836 | 141 | 97 | 50 | 7.1789 | 4.4211 | 11.6 | 11.6 | 0.29746 | 0.61887 | 21.5368 | 21.5368 | 5.0371 | 63.9629 | 0.33671 | 5.9 | 6.2 | 62 | 340 | 700 | 791.419 | -13.0599 | 81.7647 | 565.7095 | 89.0403 | 97 | 54 | 30 | 1.6211 | 2.8 | 4.4211 | 4.4211 | 0.26814 | 0.36667 | 9.7263 | 9.7263 | 5.6866 | 39.8134 | 0.2443 | 6.2 | 6.3 | 200 | 641 | 1100 | 896.3158 | 18.5167 | 41.1765 | 768.6579 | 73.9806
[11 empty] | 1989-12-04 |  | 3097.3 | 24 | 130 | 53 | 41 | 0 | 8.3 | 2.6 |  | 10.9 | 10.9 | 0.76147 | 0 | 16.6 | 16.6 | 6.6462 | 43.8538 | 0.37853 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1157.2308 | -5.2028 | 75.2941 | 748.6154 | 88.7793 | 130 | 98 | 50 | 6.7711 | 4.1289 | 10.9 | 10.9 | 0.27904 | 0.6212 | 20.3132 | 20.3132 | 5.0595 | 58.9405 | 0.34464 | 5.9 | 6.2 | 62 | 340 | 700 | 795.8917 | -13.6988 | 81.7647 | 567.9458 | 89.0835 | 98 | 53 | 32 | 1.5289 | 2.6 | 4.1289 | 4.1289 | 0.24987 | 0.3703 | 9.1737 | 9.1737 | 5.7067 | 37.7933 | 0.24273 | 6.2 | 6.3 | 200 | 641 | 1100 | 900.333 | 18.1515 | 41.1765 | 770.6665 | 74.0484
[11 empty] | 1989-12-05 |  | 3122 | 24 | 140 | 53 | 38 | 0 | 8.5 | 2.6 |  | 11.1 | 11.1 | 0.76577 | 0 | 17 | 17 | 6.7446 | 51.7554 | 0.32847 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1176.9231 | -6.993 | 75.2941 | 758.4615 | 88.9249 | 140 | 96 | 48 | 6.8442 | 4.2558 | 11.1 | 11.1 | 0.28511 | 0.61659 | 20.5325 | 20.5325 | 5.0154 | 64.9846 | 0.31596 | 5.9 | 6.2 | 62 | 340 | 700 | 787.0735 | -12.4391 | 81.7647 | 563.5368 | 88.9981 | 96 | 53 | 28 | 1.6558 | 2.6 | 4.2558 | 4.2558 | 0.25458 | 0.38908 | 9.9351 | 9.9351 | 5.8143 | 40.6857 | 0.24419 | 6.2 | 6.3 | 200 | 641 | 1100 | 921.8566 | 16.1949 | 41.1765 | 781.4283 | 74.4058
[11 empty] | 1989-12-06 |  | 3144.5 | 24 | 141 | 53 | 40 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 50.363 | 0.34152 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 141 | 97 | 50 | 7.0158 | 4.2842 | 11.3 | 11.3 | 0.28935 | 0.62087 | 21.0474 | 21.0474 | 5.0563 | 63.9437 | 0.32915 | 5.9 | 6.2 | 62 | 340 | 700 | 795.2506 | -13.6072 | 81.7647 | 567.6253 | 89.0773 | 97 | 53 | 30 | 1.5842 | 2.7 | 4.2842 | 4.2842 | 0.25935 | 0.36978 | 9.5053 | 9.5053 | 5.7038 | 39.2962 | 0.24189 | 6.2 | 6.3 | 200 | 641 | 1100 | 899.7544 | 18.2041 | 41.1765 | 770.3772 | 74.0387
[11 empty] | 1989-12-07 |  | 3169.5 | 24 | 140 | 53 | 38.5 | 0 | 8.6 | 2.6 |  | 11.2 | 11.2 | 0.76786 | 0 | 17.2 | 17.2 | 6.7938 | 51.2062 | 0.3359 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1186.7692 | -7.8881 | 75.2941 | 763.3846 | 88.9964 | 140 | 97 | 48 | 6.9247 | 4.2753 | 11.2 | 11.2 | 0.28733 | 0.61827 | 20.774 | 20.774 | 5.0314 | 65.4686 | 0.31731 | 5.9 | 6.2 | 62 | 340 | 700 | 790.2722 | -12.896 | 81.7647 | 565.1361 | 89.0292 | 97 | 53 | 29 | 1.6753 | 2.6 | 4.2753 | 4.2753 | 0.2553 | 0.39186 | 10.0519 | 10.0519 | 5.8308 | 40.1692 | 0.25024 | 6.2 | 6.3 | 200 | 641 | 1100 | 925.1608 | 15.8945 | 41.1765 | 783.0804 | 74.4598
[11 empty] | 1989-12-08 |  | 3193.2 | 24 | 145 | 55 | 41 | 0 | 8.7 | 2.9 |  | 11.6 | 11.6 | 0.75 | 0 | 17.4 | 17.4 | 6.4 | 52.6 | 0.3308 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1108 | -0.72727 | 75.2941 | 724 | 88.3978 | 145 | 101 | 52 | 7.0974 | 4.5026 | 11.6 | 11.6 | 0.29897 | 0.61184 | 21.2921 | 21.2921 | 4.971 | 66.029 | 0.32247 | 5.9 | 6.2 | 62 | 340 | 700 | 778.2034 | -11.1719 | 81.7647 | 559.1017 | 88.9108 | 101 | 55 | 30 | 1.6026 | 2.9 | 4.5026 | 4.5026 | 0.27489 | 0.35593 | 9.6158 | 9.6158 | 5.6286 | 42.3714 | 0.22694 | 6.2 | 6.3 | 200 | 641 | 1100 | 884.7105 | 19.5718 | 41.1765 | 762.8553 | 73.7827
[11 empty] | 1989-12-11 |  | 3263.1 | 24 | 145 | 55 | 40 | 0 | 8.5 | 2.6 |  | 11.1 | 11.1 | 0.76577 | 0 | 17 | 17 | 6.7446 | 53.2554 | 0.31922 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1176.9231 | -6.993 | 75.2941 | 758.4615 | 88.9249 | 145 | 102 | 50 | 6.9342 | 4.1658 | 11.1 | 11.1 | 0.28344 | 0.6247 | 20.8026 | 20.8026 | 5.0937 | 68.4063 | 0.3041 | 5.9 | 6.2 | 62 | 340 | 700 | 802.7479 | -14.6783 | 81.7647 | 571.374 | 89.149 | 102 | 55 | 30 | 1.5658 | 2.6 | 4.1658 | 4.1658 | 0.25124 | 0.37587 | 9.3947 | 9.3947 | 5.7379 | 42.7621 | 0.2197 | 6.2 | 6.3 | 200 | 641 | 1100 | 906.582 | 17.5835 | 41.1765 | 773.791 | 74.1532
[11 empty] | 1989-12-13 |  | 3311.6 | 24 | 149 | 57 | 36.5 | 0 | 8.5 | 2.7 |  | 11.2 | 11.2 | 0.75893 | 0 | 17 | 17 | 6.5896 | 59.9104 | 0.28376 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1145.9259 | -4.1751 | 75.2941 | 742.963 | 88.6939 | 149 | 105 | 45 | 6.9342 | 4.2658 | 11.2 | 11.2 | 0.28715 | 0.61913 | 20.8026 | 20.8026 | 5.0395 | 76.9605 | 0.2703 | 5.9 | 6.2 | 62 | 340 | 700 | 791.9001 | -13.1286 | 81.7647 | 565.95 | 89.045 | 105 | 57 | 28 | 1.5658 | 2.7 | 4.2658 | 4.2658 | 0.25866 | 0.36706 | 9.3947 | 9.3947 | 5.6887 | 47.3113 | 0.19857 | 6.2 | 6.3 | 200 | 641 | 1100 | 896.7456 | 18.4777 | 41.1765 | 768.8728 | 73.9879
[11 empty] | 1989-12-14 |  | 3335.4 | 24 | 146 | 55 | 40 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 53.863 | 0.31933 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 146 | 101 | 50 | 7.0158 | 4.2842 | 11.3 | 11.3 | 0.28935 | 0.62087 | 21.0474 | 21.0474 | 5.0563 | 68.4437 | 0.30751 | 5.9 | 6.2 | 62 | 340 | 700 | 795.2506 | -13.6072 | 81.7647 | 567.6253 | 89.0773 | 101 | 55 | 30 | 1.5842 | 2.7 | 4.2842 | 4.2842 | 0.25935 | 0.36978 | 9.5053 | 9.5053 | 5.7038 | 42.2962 | 0.22473 | 6.2 | 6.3 | 200 | 641 | 1100 | 899.7544 | 18.2041 | 41.1765 | 770.3772 | 74.0387
[11 empty] | 1989-12-15 |  | 3357.2 | 24 | 145 | 55 | 40 | 0 | 8.6 | 2.6 |  | 11.2 | 11.2 | 0.76786 | 0 | 17.2 | 17.2 | 6.7938 | 53.2062 | 0.32327 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1186.7692 | -7.8881 | 75.2941 | 763.3846 | 88.9964 | 145 | 100 | 50 | 6.9247 | 4.2753 | 11.2 | 11.2 | 0.28733 | 0.61827 | 20.774 | 20.774 | 5.0314 | 67.4686 | 0.30791 | 5.9 | 6.2 | 62 | 340 | 700 | 790.2722 | -12.896 | 81.7647 | 565.1361 | 89.0292 | 100 | 55 | 30 | 1.6753 | 2.6 | 4.2753 | 4.2753 | 0.2553 | 0.39186 | 10.0519 | 10.0519 | 5.8308 | 41.6692 | 0.24123 | 6.2 | 6.3 | 200 | 641 | 1100 | 925.1608 | 15.8945 | 41.1765 | 783.0804 | 74.4598
[11 empty] | 1989-12-18 |  | 3428.1 | 24 | 146 | 56 | 39 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 55.363 | 0.31068 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 146 | 102 | 48 | 6.9462 | 4.3538 | 11.3 | 11.3 | 0.29064 | 0.6147 | 20.8385 | 20.8385 | 4.9976 | 71.0024 | 0.29349 | 5.9 | 6.2 | 62 | 340 | 700 | 783.523 | -11.9319 | 81.7647 | 561.7615 | 88.9633 | 102 | 56 | 30 | 1.6538 | 2.7 | 4.3538 | 4.3538 | 0.26193 | 0.37986 | 9.9231 | 9.9231 | 5.7606 | 43.2394 | 0.22949 | 6.2 | 6.3 | 200 | 641 | 1100 | 911.1282 | 17.1702 | 41.1765 | 776.0641 | 74.2289
[11 empty] | 1989-12-20 |  | 3466.7 | 24 | 148 | 58 | 39.5 | 0 | 8.7 | 2.8 |  | 11.5 | 11.5 | 0.75652 | 0 | 17.4 | 17.4 | 6.5371 | 56.9629 | 0.30546 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1135.4286 | -3.2208 | 75.2941 | 737.7143 | 88.6135 | 148 | 101 | 49 | 7.0052 | 4.4948 | 11.5 | 11.5 | 0.29697 | 0.60915 | 21.0156 | 21.0156 | 4.9463 | 70.5537 | 0.29787 | 5.9 | 6.2 | 62 | 340 | 700 | 773.2655 | -10.4665 | 81.7647 | 556.6328 | 88.8616 | 101 | 58 | 30 | 1.6948 | 2.8 | 4.4948 | 4.4948 | 0.27088 | 0.37706 | 10.1688 | 10.1688 | 5.7447 | 43.7553 | 0.2324 | 6.2 | 6.3 | 200 | 641 | 1100 | 907.9318 | 17.4607 | 41.1765 | 774.4659 | 74.1758
[11 empty] | 1989-12-21 |  | 3488 | 24 | 146 | 56 | 39 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 55.363 | 0.31068 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 146 | 101 | 48 | 6.9247 | 4.3753 | 11.3 | 11.3 | 0.29104 | 0.6128 | 20.774 | 20.774 | 4.9799 | 70.5201 | 0.29458 | 5.9 | 6.2 | 62 | 340 | 700 | 779.981 | -11.4259 | 81.7647 | 559.9905 | 88.9284 | 101 | 56 | 30 | 1.6753 | 2.7 | 4.3753 | 4.3753 | 0.26273 | 0.3829 | 10.0519 | 10.0519 | 5.7782 | 42.7218 | 0.23529 | 6.2 | 6.3 | 200 | 641 | 1100 | 914.6364 | 16.8512 | 41.1765 | 777.8182 | 74.2871
[11 empty] | 1989-12-22 |  | 3512.9 | 24 | 148 | 56 | 40 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 55.363 | 0.31068 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 148 | 101 | 50 | 6.9247 | 4.3753 | 11.3 | 11.3 | 0.29104 | 0.6128 | 20.774 | 20.774 | 4.9799 | 69.5201 | 0.29882 | 5.9 | 6.2 | 62 | 340 | 700 | 779.981 | -11.4259 | 81.7647 | 559.9905 | 88.9284 | 101 | 56 | 30 | 1.6753 | 2.7 | 4.3753 | 4.3753 | 0.26273 | 0.3829 | 10.0519 | 10.0519 | 5.7782 | 42.7218 | 0.23529 | 6.2 | 6.3 | 200 | 641 | 1100 | 914.6364 | 16.8512 | 41.1765 | 777.8182 | 74.2871
[11 empty] | 1989-12-26 |  | 3566.7 | 24 | 145 | 56 | 40 | 0 | 8.7 | 2.8 |  | 11.5 | 11.5 | 0.75652 | 0 | 17.4 | 17.4 | 6.5371 | 53.9629 | 0.32244 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1135.4286 | -3.2208 | 75.2941 | 737.7143 | 88.6135 | 145 | 101 | 48 | 7.0269 | 4.4731 | 11.5 | 11.5 | 0.29657 | 0.61104 | 21.0808 | 21.0808 | 4.9636 | 70.0364 | 0.301 | 5.9 | 6.2 | 62 | 340 | 700 | 776.7206 | -10.9601 | 81.7647 | 558.3603 | 88.8961 | 101 | 56 | 32 | 1.6731 | 2.8 | 4.4731 | 4.4731 | 0.27007 | 0.37403 | 10.0385 | 10.0385 | 5.7275 | 40.7725 | 0.24621 | 6.2 | 6.3 | 200 | 641 | 1100 | 904.5096 | 17.7719 | 41.1765 | 772.7548 | 74.1186
[11 empty] | 1989-12-28 |  | 3615.7 | 24 | 145 | 56 | 39 | 0 | 8.7 | 2.7 |  | 11.4 | 11.4 | 0.76316 | 0 | 17.4 | 17.4 | 6.6844 | 54.8156 | 0.31743 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1164.8889 | -5.899 | 75.2941 | 752.4444 | 88.8364 | 145 | 102 | 48 | 7.0269 | 4.3731 | 11.4 | 11.4 | 0.29285 | 0.6164 | 21.0808 | 21.0808 | 5.0135 | 70.4865 | 0.29908 | 5.9 | 6.2 | 62 | 340 | 700 | 786.7071 | -12.3867 | 81.7647 | 563.3536 | 88.9945 | 102 | 56 | 30 | 1.6731 | 2.7 | 4.3731 | 4.3731 | 0.26265 | 0.38259 | 10.0385 | 10.0385 | 5.7763 | 43.2237 | 0.23224 | 6.2 | 6.3 | 200 | 641 | 1100 | 914.2692 | 16.8846 | 41.1765 | 777.6346 | 74.281
[11 empty] | 1989-12-29 |  | 3639 | 24 | 145 | 56 | 41 | 0 | 8.6 | 2.6 |  | 11.2 | 11.2 | 0.76786 | 0 | 17.2 | 17.2 | 6.7938 | 52.7062 | 0.32634 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1186.7692 | -7.8881 | 75.2941 | 763.3846 | 88.9964 | 145 | 101 | 50 | 6.9462 | 4.2538 | 11.2 | 11.2 | 0.28693 | 0.62019 | 20.8385 | 20.8385 | 5.0497 | 67.9503 | 0.30667 | 5.9 | 6.2 | 62 | 340 | 700 | 793.9494 | -13.4213 | 81.7647 | 566.9747 | 89.0648 | 101 | 56 | 32 | 1.6538 | 2.6 | 4.2538 | 4.2538 | 0.25451 | 0.38879 | 9.9231 | 9.9231 | 5.8126 | 40.6874 | 0.24389 | 6.2 | 6.3 | 200 | 641 | 1100 | 921.5178 | 16.2257 | 41.1765 | 781.2589 | 74.4003
[11 empty] | 1990-01-02 |  | 3710.7 | 24 | 146 | 56 | 41 | 0 | 8.7 | 2.7 |  | 11.4 | 11.4 | 0.76316 | 0 | 17.4 | 17.4 | 6.6844 | 53.3156 | 0.32636 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1164.8889 | -5.899 | 75.2941 | 752.4444 | 88.8364 | 146 | 100 | 50 | 7.0052 | 4.3948 | 11.4 | 11.4 | 0.29326 | 0.61449 | 21.0156 | 21.0156 | 4.9956 | 68.0044 | 0.30903 | 5.9 | 6.2 | 62 | 340 | 700 | 783.1241 | -11.8749 | 81.7647 | 561.5621 | 88.9594 | 100 | 56 | 32 | 1.6948 | 2.7 | 4.3948 | 4.3948 | 0.26345 | 0.38564 | 10.1688 | 10.1688 | 5.7941 | 40.2059 | 0.25292 | 6.2 | 6.3 | 200 | 641 | 1100 | 917.8182 | 16.562 | 41.1765 | 779.4091 | 74.3395
[11 empty] | 1990-01-04 |  | 3782.8 | 24 | 146 | 56 | 39.5 | 0 | 8.6 | 2.7 |  | 11.3 | 11.3 | 0.76106 | 0 | 17.2 | 17.2 | 6.637 | 54.863 | 0.31351 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1155.4074 | -5.037 | 75.2941 | 747.7037 | 88.7656 | 146 | 102 | 48 | 6.9247 | 4.3753 | 11.3 | 11.3 | 0.29104 | 0.6128 | 20.774 | 20.774 | 4.9799 | 71.0201 | 0.29251 | 5.9 | 6.2 | 62 | 340 | 700 | 779.981 | -11.4259 | 81.7647 | 559.9905 | 88.9284 | 102 | 56 | 31 | 1.6753 | 2.7 | 4.3753 | 4.3753 | 0.26273 | 0.3829 | 10.0519 | 10.0519 | 5.7782 | 42.2218 | 0.23807 | 6.2 | 6.3 | 200 | 641 | 1100 | 914.6364 | 16.8512 | 41.1765 | 777.8182 | 74.2871
[11 empty] | 1990-01-05 |  | 3805.8 | 24 | 145 | 56 | 39.5 | 0 | 8.7 | 2.8 |  | 11.5 | 11.5 | 0.75652 | 0 | 17.4 | 17.4 | 6.5371 | 54.4629 | 0.31948 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1135.4286 | -3.2208 | 75.2941 | 737.7143 | 88.6135 | 145 | 101 | 49 | 7.0052 | 4.4948 | 11.5 | 11.5 | 0.29697 | 0.60915 | 21.0156 | 21.0156 | 4.9463 | 69.0537 | 0.30434 | 5.9 | 6.2 | 62 | 340 | 700 | 773.2655 | -10.4665 | 81.7647 | 556.6328 | 88.8616 | 101 | 56 | 30 | 1.6948 | 2.8 | 4.4948 | 4.4948 | 0.27088 | 0.37706 | 10.1688 | 10.1688 | 5.7447 | 42.7553 | 0.23784 | 6.2 | 6.3 | 200 | 641 | 1100 | 907.9318 | 17.4607 | 41.1765 | 774.4659 | 74.1758
[11 empty] | 1990-01-08 |  | 3880.6 | 24 | 146 | 56 | 40.5 | 0 | 8.7 | 2.7 |  | 11.4 | 11.4 | 0.76316 | 0 | 17.4 | 17.4 | 6.6844 | 53.8156 | 0.32333 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1164.8889 | -5.899 | 75.2941 | 752.4444 | 88.8364 | 146 | 100 | 50 | 7.0052 | 4.3948 | 11.4 | 11.4 | 0.29326 | 0.61449 | 21.0156 | 21.0156 | 4.9956 | 68.0044 | 0.30903 | 5.9 | 6.2 | 62 | 340 | 700 | 783.1241 | -11.8749 | 81.7647 | 561.5621 | 88.9594 | 100 | 56 | 31 | 1.6948 | 2.7 | 4.3948 | 4.3948 | 0.26345 | 0.38564 | 10.1688 | 10.1688 | 5.7941 | 41.2059 | 0.24678 | 6.2 | 6.3 | 200 | 641 | 1100 | 917.8182 | 16.562 | 41.1765 | 779.4091 | 74.3395
[11 empty] | 1990-01-09 |  | 3898.6 | 24 | 145 | 56 | 39 | 0 | 8.6 | 2.5 |  | 11.1 | 11.1 | 0.77477 | 0 | 17.2 | 17.2 | 6.9632 | 54.5368 | 0.31538 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1220.64 | -10.9673 | 75.2941 | 780.32 | 89.2352 | 145 | 102 | 48 | 6.9247 | 4.1753 | 11.1 | 11.1 | 0.28361 | 0.62384 | 20.774 | 20.774 | 5.0853 | 70.4147 | 0.29502 | 5.9 | 6.2 | 62 | 340 | 700 | 801.0563 | -14.4366 | 81.7647 | 570.5281 | 89.1329 | 102 | 56 | 30 | 1.6753 | 2.5 | 4.1753 | 4.1753 | 0.24788 | 0.40124 | 10.0519 | 10.0519 | 5.8876 | 43.1124 | 0.23316 | 6.2 | 6.3 | 200 | 641 | 1100 | 936.5273 | 14.8612 | 41.1765 | 788.7636 | 74.6439
[11 empty] | 1990-01-10 |  | 3900.9 | 24 | 144 | 56 | 38 | 0 | 8.51 | 2.54 |  | 11.05 | 11.05 | 0.77014 | 0 | 17.02 | 17.02 | 6.8485 | 55.1515 | 0.3086 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1197.7008 | -8.8819 | 75.2941 | 768.8504 | 89.0746 | 144 | 101 | 45 | 6.9424 | 4.1076 | 11.05 | 11.05 | 0.28143 | 0.62827 | 20.8271 | 20.8271 | 5.1293 | 72.3707 | 0.28778 | 5.9 | 6.2 | 62 | 340 | 700 | 809.8519 | -15.6931 | 81.7647 | 574.9259 | 89.216 | 101 | 56 | 31 | 1.5676 | 2.54 | 4.1076 | 4.1076 | 0.24685 | 0.38164 | 9.4058 | 9.4058 | 5.7709 | 41.7291 | 0.2254 | 6.2 | 6.3 | 200 | 641 | 1100 | 913.1754 | 16.9841 | 41.1765 | 777.0877 | 74.2629
[11 empty] | 1990-01-10 |  | 3904.4 | 24 | 141 | 69 | 43.5 | 0 | 9.23 | 2.83 |  | 12.06 | 12.06 | 0.76534 | 0 | 18.46 | 18.46 | 6.7347 | 54.7653 | 0.33707 | 6.8 | 5.9 | 84 | 300 | 340 | 1100 | 1174.9399 | -6.8127 | 75.2941 | 757.47 | 88.9105 | 141 | 102 | 50 | 7.0649 | 4.9951 | 12.06 | 12.06 | 0.31666 | 0.58582 | 21.1948 | 21.1948 | 4.746 | 66.754 | 0.31751 | 5.9 | 6.2 | 62 | 340 | 700 | 733.1989 | -4.7427 | 81.7647 | 536.5995 | 88.4458 | 102 | 69 | 37 | 2.1651 | 2.83 | 4.9951 | 4.9951 | 0.29057 | 0.43344 | 12.9904 | 12.9904 | 6.0969 | 42.4031 | 0.30635 | 6.2 | 6.3 | 200 | 641 | 1100 | 978.3824 | 11.0561 | 41.1765 | 809.6912 | 75.2992
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on T8: C. Hill (9/7/99): These values are not measured, but are the average temperature. This utility uses groundwater which generally has stable temperatures.
Note on AA14: TSC_ADM: Reviewer removed "X" because it was noted in the Summary Report that no cleanings occurred during this study.
Note on AA58: TSC_ADM: Reviewer removed "X" because it was noted in the Summary Report that no cleanings occurred during this study.
Note on AJ41: C. Hill (9/7/99): The consultant stated, "The system permeate pressure (at 916 hrs) was verified. Modifications to the permeate discharge piping caused a decrease in permeate pressure but not the feed pressure. There was only a small increase in the overall system permeate stream flow. These results caused a decrease in the system MTCw."
Note on CW33: The consultant stated, " The CHCl3 values were verified as 17 ug/L for the 7/25/89 sample event and below the reported detection limit of 1 ug/L for 9/27/89. The 7/25/89 sample event produced the highest individual species and total THMs recorded for all process streams. The 9/27/89 sample event produced the lowest chloroform concentrations recorded for all process streams."
Note on CX33: C. Hill (9/7/99): The consultant stated, "The CHCl3 value was verified as 201 ug/L for the 7/25/89 sample date. This sample event produced the highest individual species and total THMs recorded for all process streams."
Note on EK33: The consultant stated, " The CHCl3 values were verified as 17 ug/L for the 7/25/89 sample event and below the reported detection limit of 1 ug/L for 9/27/89. The 7/25/89 sample event produced the highest individual species and total THMs recorded for all process streams. The 9/27/89 sample event produced the lowest chloroform concentrations recorded for all process streams.
Note on EK38: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."
Note on EK39: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."
Note on EK40: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."
Note on EK41: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."
Note on EK42: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."
Note on EL41: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."
Note on EL42: The consultant stated, " The HAA values recorded for 9/27/89 were verified as below the analytical detection limit of 1 ug/L for the individual species in the permeate sample and the SDS-MBAA and SDS-DBAA species in the feed stream."