## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM "1st" PILOT-SCALE STUDY WITH CHEMICAL DOSES SIMILAR TO FULL-SCALE PLANT
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot Scale GAC Contactors | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Dallas Water Utilities Department | Carbon manufacturer | Calgon Carbon Corporation | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0570004 | Carbon trade name | GAC Filtrasorb 820 | mesh size | (mm) | Primary Coagulation | Ferric Sulfate (Fe2(SO4)3), avg=20 mg/L (10-30 mg/L) | Pilot | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6.6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal | 4 | 4.75 | Primary Coagulation | Calcium Hydroxide (Ca(OH)2), avg=52 mg/L (40-60 mg/L) | Pilot |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 11.9
|  | Pilot GAC influent TOC (mg/L) | 4.7 | 6 | 3.35 | Primary Flocculation | three-stage, 12 minutes/stage | Pilot | START | --- | 1998-04-13 | 15:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-13 | 15:25 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-13 | 15:15 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 101.6 | 8 | 2.36 | Primary Sedimentation | tube settler, 23 minutes detention | Pilot | BAICR-IN1 | N | 1998-04-14 | 15:00 | 24 | 72 | 144 | 8.6 | 0.17 | 49 | 19.7 | 77 | 57 | BMRL | 110 | 3.9 | 0.079 | 2.0256 | 4.5 | 1 | 3.5 | 22 | 8.6 | 24 | NR | 68 | 36 | 17 | BMRL | 121 | 2.5 | 22 | 11 | BMRL | 2.7 | 12 | NA | NA | NA | 38.2 | 50.2 | BAICR-101 | N | 1998-04-14 | 15:25 | 24 | 144 | 9 | 0.18 | 19.5 | BMRL | BMRL | BMRL | NR | 1.5 | 1.1 | 0.4 | 22.3 | 8.8 | 24 | BMRL | BMRL | BMRL | 3.1 | 5.7 | 8.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | BAICR-201 | N | 1998-04-14 | 15:15 | 24 | 72 | 9.2 | 0.3 | 20 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 1 | 0.5 | 22 | 9.2 | 24 | BMRL | BMRL | BMRL | 1.9 | 3.4 | 5.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 549.1 | 10 | 2 | Secondary Coagulation | Ferric Sulfate (Fe2(SO4)3), 7 - 10 mg/L | Pilot | BAICR-IN2 | N | 1998-04-20 | 15:30 | 168.5 | 505.5 | 1011 | 8.5 | 0.23 | 47 | 20.9 | 73 | 56 | BMRL | 110 | 3.7 | 0.089 | 2.4054 | 4.5 | 1.1 | 3.4 | 19.7 | 8.8 | 24 | 250 | 58 | 30 | 15 | 2 | 105 | 3.1 | 20 | 7.5 | BMRL | 2.8 | 11 | NA | NA | NA | 33.4 | 44.4 | BAICR-102 | N | 1998-04-16 | 15:00 | 71.5833 | 429.5 | 8.3 | 0.21 | 20.6 | BMRL | 0.73 | 0.011 | 1.5068 | 1.5 | 0.9 | 0.6 | 21.7 | 8.6 | 24 | 77 | 1.3 | 3.3 | 11 | 15 | 30.6 | BMRL | BMRL | 1 | BMRL | 2.8 | 1.4 | NA | NA | NA | 3.8 | 5.2 | BAICR-202 | N | 1998-04-20 | 15:45 | 168.5 | 505.5 | 9.6 | 0.22 | 21.8 | BMRL | BMRL | 0.01 | #VALUE! | 1.5 | 1.1 | 0.4 | 19.8 | 8.7 | 24 | 26 | BMRL | 1 | 3.5 | 5.8 | 10.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 | Secondary Flocculation | three-stage, 12 minutes/stage | Pilot | BAICR-IN3 | Y | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | BMRL | 115 | 3.8 | 0.084 | 2.2105 | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 60 | 36 | 19.5 | 2.45 | 117.95 | 3.55 | 20 | 9.35 | BMRL | 3.15 | 12.5 | NA | NA | NA | 36.05 | 48.55 | BAICR-103 | Y | 1998-04-20 | 16:00 | 168.5833 | 1011.5 | 8.6 | 0.22 | 21.3 | BMRL | 1.5 | 0.03 | 2 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 6.1 | 12 | 21 | 14.5 | 53.6 | BMRL | 2.4 | 1.45 | BMRL | 5.05 | 3.45 | NA | NA | NA | 8.9 | 12.35 | BAICR-203 | Y | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | BMRL | 0.615 | 0.01 | 1.626 | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | 1 | 1.8 | 6.5 | 8.95 | 18.25 | BMRL | BMRL | BMRL | BMRL | 2 | BMRL | NA | NA | NA | 2 | 2 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 20 | 16 | 1.18 | Secondary Sedimentation | tube settler, 23 minutes detention | Pilot | BAICR-IN4 | N | 1998-04-30 | 11:16 | 404.2667 | 1212.8 | 2425.6 | 8.7 | 0.16 | 59 | 20.6 | 88 | 69 | BMRL | 120 | 3.8 | 0.085 | 2.2368 | 4.3 | 0.95 | 3.35 | 22 | 8.6 | 24 | 260 | 56 | 35 | 19 | 2.5 | 112.5 | 2.3 | 19 | 10 | BMRL | 3.2 | 13 | NA | NA | NA | 34.5 | 47.5 | BAICR-104 | N | 1998-04-22 | 14:00 | 214.5833 | 1287.5 | 8.8 | 0.17 | 20.7 | BMRL | 1.6 | 0.031 | 1.9375 | 2.4 | 1 | 1.4 | 21.1 | 8.5 | 24 | 96 | 11 | 18 | 25 | 11 | 65 | BMRL | 5.7 | 2.4 | BMRL | 5.6 | 5.2 | NA | NA | NA | 13.7 | 18.9 | BAICR-204 | N | 1998-04-30 | 11:36 | 404.35 | 1213.05 | 8.2 | 0.21 | 21 | BMRL | 1 | 0.025 | 2.5 | 1.9 | 0.97 | 0.93 | 22 | 8.1 | 24 | BMRL | 2.3 | 6.6 | 17 | 15 | 40.9 | BMRL | 1.2 | 1.6 | BMRL | 3.9 | 2.5 | NA | NA | NA | 6.7 | 9.2 | 1998 ENR Construction Cost Index (CCI base year 1913) | 3941.46
FAX Number |  | Flow rate, Q (L/hr) | 45.42 | 18 | 1 | Dual Media Filtration | sand/anthracite | Pilot | BAICR-IN5 | N | 1998-05-06 | 12:30 | 549.5 | 1648.5 | 3297 | 8.4 | 0.23 | 55 | 24.6 | 96 | 74 | BMRL | 140 | 3.7 | 0.081 | 2.1892 | 4.3 | 0.83 | 3.47 | 25.3 | 8.3 | 24 | 310 | 54 | 40 | 27 | 4.9 | 125.9 | 2.3 | 18 | 11 | BMRL | 6 | 15 | NA | NA | NA | 37.3 | 52.3 | BAICR-105 | N | 1998-04-23 | 13:00 | 237.5833 | 1425.5 | 8.6 | 0.19 | 20.9 | BMRL | 1.9 | 0.034 | 1.7895 | 2.3 | 0.85 | 1.45 | 22.6 | 8.7 | 24 | 92 | 10 | 17 | 22 | 9.8 | 58.8 | BMRL | 4.2 | 2.4 | BMRL | 6 | 5.5 | NA | NA | NA | 12.6 | 18.1 | BAICR-205 | N | 1998-05-06 | 13:00 | 549.75 | 1649.25 | 7.8 | 0.18 | 26 | BMRL | 1.2 | 0.018 | 1.5 | 1.9 | 0.96 | 0.94 | 25.4 | 7.8 | 24 | 54 | 2.1 | 6.7 | 18 | 17 | 43.8 | BMRL | 1.3 | 2 | BMRL | 6.2 | 3 | NA | NA | NA | 9.5 | 12.5 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | 20 | 0.85 |  |  |  | BAICR-IN6 | N | 1998-05-11 | 13:00 | 670 | 2010 | 4020 | 8.2 | 0.15 | 61 | 25 | 106 | 80 | BMRL | 150 | 3.8 | 0.08 | 2.1053 | 4.3 | 0.93 | 3.37 | 26 | 8.2 | 24 | NR | 53 | 42 | 28 | 5.1 | 128.1 | 3.3 | 17 | 12 | BMRL | 4.2 | 14 | NA | NA | NA | 36.5 | 50.5 | BAICR-106 | N | 1998-04-27 | 13:15 | 333.8333 | 2003 | 7.9 | 0.52 | 21.4 | BMRL | 1.9 | NR | NR | 2.3 | 0.7 | 1.6 | 20 | 7.8 | 24 | 120 | 11 | 20 | 25 | 8.6 | 64.6 | BMRL | 4.8 | 3.7 | BMRL | 5.9 | 6.6 | NA | NA | NA | 14.4 | 21 | BAICR-206 | N | 1998-05-11 | 13:30 | 670.25 | 2010.75 | 7.7 | 0.12 | 26 | BMRL | 1.4 | 0.021 | 1.5 | 1.9 | 0.95 | 0.95 | 26 | 7.8 | 24 | 65 | 2 | 7.5 | 22 | 19 | 50.5 | BMRL | 1.1 | 1.9 | BMRL | 4.6 | 3.1 | NA | NA | NA | 7.6 | 10.7 | Labor Rate + Fringe ($/work-hour) | 20
|  | Estimated Run Length |  | 30 | 0.6 |  |  |  | BAICR-IN7 | Y | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.8 | 0.077 | 2.0263 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 295 | 55 | 46 | 33 | 6.7 | 140.7 | 3.5 | 18 | 13 | 1 | 4.65 | 15 | NA | NA | NA | 40.15 | 55.15 | BAICR-107 | Y | 1998-04-30 | 11:55 | 404.5 | 2427 | 8.5 | 0.19 | 20.6 | BMRL | 2.15 | 0.0415 | 1.9302 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16.5 | 22.5 | 25 | 8 | 72 | BMRL | 5.9 | 3.85 | BMRL | 5.6 | 7.55 | NA | NA | NA | 15.35 | 22.9 | BAICR-207 | Y | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.45 | 0.0195 | 1.3448 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 68.5 | 2.85 | 9.6 | 23 | 17 | 52.45 | BMRL | 1.7 | 2.35 | BMRL | 5.5 | 3.95 | NA | NA | NA | 9.55 | 13.5 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 2902.2346 | 40 | 0.425 |  |  |  | BAICR-IN8 | N | 1998-05-21 | 11:00 | 908 | 2724 | 5448 | 7.9 | 0.25 | 80 | 27 | 124 | 102 | BMRL | 150 | 3.8 | 0.083 | 2.1842 | 5 | 0.97 | 4.03 | 26 | 7.9 | 24 | 340 | 59 | 44 | 29 | 5.3 | 137.3 | 4 | 24 | 17 | 1.4 | 4.7 | 16 | NA | NA | NA | 51.1 | 67.1 | BAICR-108 | N | 1998-05-04 | 13:22 | 501.95 | 3011.7 | 8.2 | 0.14 | 23 | BMRL | 2.3 | 0.041 | 1.7826 | 2.6 | 0.85 | 1.75 | 24 | 8.1 | 24 | 140 | 17 | 24 | 28 | 11 | 80 | BMRL | 5.7 | 4.4 | BMRL | 8.4 | 8.1 | NA | NA | NA | 18.5 | 26.6 | BAICR-208 | N | 1998-05-21 | 11:25 | 908.1667 | 2724.5 | 7.7 | 0.16 | 28 | BMRL | 1.8 | 0.024 | 1.3333 | 2.3 | 0.83 | 1.47 | 26 | 7.8 | 24 | BMRL | 4.2 | 11 | 24 | 15 | 54.2 | BMRL | 2.3 | 2.8 | 1.1 | 5.6 | 4.7 | NA | NA | NA | 11.8 | 16.5 | Electric Rate ($/kW-h) | 0.05273
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 5804.4692 | 50 | 0.3 |  |  |  | BAICR-IN9 | N | 1998-05-27 | 10:25 | 1051.4167 | 3154.25 | 6308.5 | 7.9 | 0.22 | 85 | 26 | 129 | 101 | BMRL | 160 | 3.8 | 0.097 | 2.5526 | 4.8 | 0.98 | 3.82 | 27 | 7.8 | 24 | NR | 46 | 38 | 27 | 4.7 | 115.7 | 5.2 | 23 | 12 | 1.6 | 4.9 | 10 | NA | NA | NA | 46.7 | 56.7 | BAICR-109 | N | 1998-05-06 | 13:20 | 549.9167 | 3299.5 | 8.1 | 0.21 | 25.3 | BMRL | 2.2 | 0.041 | 1.8636 | 2.8 | 0.9 | 1.9 | 25.6 | 8 | 24 | 140 | 16 | 25 | 30 | 12 | 83 | BMRL | 6.4 | 4.5 | BMRL | 6 | 8.2 | NA | NA | NA | 16.9 | 25.1 | BAICR-209 | N | 1998-05-27 | 10:45 | 1051.5 | 3154.5 | 7.5 | 0.17 | 26 | BMRL | 1.7 | 0.029 | 1.7059 | 2.4 | 0.98 | 1.42 | 27 | 7.8 | 24 | BMRL | 5 | 14 | 28 | 16 | 63 | BMRL | 2.6 | 2.9 | 1.1 | 6.4 | 5.3 | NA | NA | NA | 13 | 18.3 | Fuel Oil Rate ($/gal)
|  |  |  | 60 | 0.25 |  |  |  | BAICR-IN10 | N | 1998-06-02 | 13:00 | 1198 | 3594 | 7188 | 8 | 0.32 | 78 | 29 | 111 | 91 | BMRL | 140 | 3.8 | 0.093 | 2.4474 | 5.5 | 0.85 | 4.65 | 29 | 7.9 | 24 | 360 | 68 | 44 | 26 | 3.6 | 141.6 | 5.6 | 30 | 17 | BMRL | 3.5 | 17 | NA | NA | NA | 56.1 | 73.1 | BAICR-1010 | N | 1998-05-11 | 14:00 | 670.5833 | 4023.5 | 7.9 | 0.11 | 24.6 | BMRL | 2.5 | 0.042 | 1.68 | 2.9 | 0.97 | 1.93 | 26 | 7.9 | 24 | 96 | 14 | 23 | 29 | 11 | 77 | BMRL | 6.2 | 4.5 | BMRL | 4.8 | 7.6 | NA | NA | NA | 15.5 | 23.1 | BAICR-2010 | N | 1998-06-02 | 13:20 | 1198.0833 | 3594.25 | 7.3 | 0.2 | 31 | BMRL | 1.9 | 0.032 | 1.6842 | 2.6 | 0.9 | 1.7 | 29 | 7.9 | 24 | 130 | 8.6 | 19 | 29 | 13 | 69.6 | BMRL | 4.5 | 4.2 | 1.1 | 6.1 | 7.5 | NA | NA | NA | 15.9 | 23.4 | Natural Gas Rate ($/ft3)
|  | General Pilot Design Parameters |  | 70 | 0.21 | [44 empty] | BAICR-1011 | N | 1998-05-13 | 10:30 | 715.0833 | 4290.5 | 7.9 | 0.14 | 25 | BMRL | 2.6 | 0.047 | 1.8077 | 3 | 1 | 2 | 25.1 | 7.9 | 24 | 150 | 18 | 27 | 31 | 11 | 87 | BMRL | 8.2 | 6.2 | 1 | 7.7 | 10 | NA | NA | NA | 23.1 | 33.1 | [36 empty] | Current Process Water Rate ($/1000 gal) | 0.1
Phone Number |  | Carbon particle diameter, d (mm) | 1.605 | 80 | 0.18 | [44 empty] | BAICR-1012 | Y | 1998-05-18 | 15:50 | 840.4167 | 5042.5 | 7.9 | 0.16 | 27 | BMRL | 2.45 | 0.041 | 1.6735 | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 155 | 17.5 | 28 | 35.5 | 13.5 | 94.5 | BMRL | 6.1 | 5.3 | 1 | 6.25 | 8.85 | NA | NA | NA | 18.65 | 27.5 | [36 empty] | Modifications to Existing Plant (% of construction costs) | 30
FAX Number |  | Column cross-sectional area, A (m2) | 0.0081073 | [46 empty] | BAICR-1013 | N | 1998-05-21 | 11:50 | 908.4167 | 5450.5 | 7.8 | 0.16 | 27 | BMRL | 2.6 | 0.045 | 1.7308 | 3.5 | 1.05 | 2.45 | 26 | 7.9 | 24 | 180 | 18 | 24 | 28 | 8.8 | 78.8 | BMRL | 9.3 | 7.5 | 1.3 | 6.2 | 11 | NA | NA | NA | 24.3 | 35.3
E-Mail Address (optional) |  | Hydraulic loading rate1, v (m/hr) | 5.6023 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [43 empty] | BAICR-1014 | N | 1998-05-26 | 11:30 | 1028.0833 | 6168.5 | 7.4 | 0.17 | 26 | BMRL | 2.8 | 0.057 | 2.0357 | 3.2 | 0.93 | 2.27 | 26 | 7.8 | 24 | NR | 19 | 27 | 31 | 10 | 87 | BMRL | 8.2 | 4.6 | 1.1 | 7.6 | 9.7 | NA | NA | NA | 21.5 | 31.2
|  | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [43 empty] | BAICR-1015 | N | 1998-06-02 | 13:45 | 1198.3333 | 7190 | 7.5 | 0.24 | 30 | BMRL | 2.8 | 0.061 | 2.1786 | 3.8 | 0.82 | 2.98 | 29 | 7.8 | 24 | 220 | 28 | 32 | 30 | 6.9 | 96.9 | 2.9 | 14 | 10 | 1 | 5.7 | 13 | NA | NA | NA | 33.6 | 46.6
Plant Name | Bachman Water Treatment Plant |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. | [43 empty] | BAICR-1016 | N | 1998-06-23 | 11:40 | 1700.25 | 10201.5 | 7.2 | 0.16 | 30 | BMRL | NR | NR | NR | 4.2 | 1.2 | 3 | 29 | 7.3 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
Treatment Plant Category | TS/SOFT | 10-Minute EBCT Run | [47 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Process Train Name | Two-stage softening | Empty bed contact time, EBCT (min) | 10 | [46 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
ICR Treatment Plant Identification Number | 620 | Estimated run time, t (days) | 40.3088 | [46 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
PWSID Number of Plant (if assigned) | TX0570004 | Pilot column bed length, l (m) | 0.93372
Historical Minimum Water Temperature (oC) | 5 | Mass GAC required, m (kg) | 4.1567
Historical Average Water Temperature (oC) | 20
State Approved Plant Capacity (MGD) | 115 | 20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 80.6176 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [76 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Pilot column bed length, l (m) | 1.8674 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [76 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  | Mass GAC required, m (kg) | 8.3134 | [5 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [76 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | BAICR-IN3 | Primary | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | BMRL | 110 | 3.7 | NR | #VALUE! | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 62 | 37 | 20 | 2.6 | 121.6 | 3.6 | 20 | 9.1 | BMRL | 2.9 | 12 | NA | NA | NA | 35.6 | 47.6 | BAICR-103 | Primary | 1998-04-20 | 16:00 | 168.5833 | 1011.5 | 8.6 | 0.22 | 21.3 | BMRL | 1.4 | 0.03 | 2.1429 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 6.6 | 13 | 22 | 15 | 56.6 | BMRL | 2.4 | 1.4 | BMRL | 5 | 3.4 | NA | NA | NA | 8.8 | 12.2 | BAICR-203 | Primary | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | BMRL | 0.62 | NR | #VALUE! | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | 1 | 2 | 7 | 9.3 | 19.3 | BMRL | BMRL | BMRL | BMRL | 2 | BMRL | NA | NA | NA | 2 | 2
[9 empty] | BAICR-IN3 D | Duplicate | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | NA | 120 | 3.9 | 0.084 | 2.1538 | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 58 | 35 | 19 | 2.3 | 114.3 | 3.5 | 20 | 9.6 | BMRL | 3.4 | 13 | NA | NA | NA | 36.5 | 49.5 | BAICR-103 D | Duplicate | 1998-04-20 | 16:00 | 168.5833 | 1011.5 | 8.6 | 0.22 | 21.3 | BMRL | 1.6 | 0.03 | 1.875 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 5.6 | 11 | 20 | 14 | 50.6 | BMRL | 2.4 | 1.5 | BMRL | 5.1 | 3.5 | NA | NA | NA | 9 | 12.5 | BAICR-203 D | Duplicate | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | NA | 0.61 | 0.01 | 1.6393 | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | BMRL | 1.6 | 6 | 8.6 | 16.2 | BMRL | BMRL | BMRL | BMRL | NR | BMRL | NA | NA | NA | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 8.5 | 0.19 | 51 | 21 | 79 | 61 | #DIV/0! | 115 | 3.8 | 0.084 | #VALUE! | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 60 | 36 | 19.5 | 2.45 | 117.95 | 3.55 | 20 | 9.35 | #DIV/0! | 3.15 | 12.5 | #DIV/0! | #DIV/0! | #DIV/0! | 36.05 | 48.55 |  | Average | --- | --- | --- | --- | 8.6 | 0.22 | 21.3 | #DIV/0! | 1.5 | 0.03 | 2.0089 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | #DIV/0! | 6.1 | 12 | 21 | 14.5 | 53.6 | #DIV/0! | 2.4 | 1.45 | #DIV/0! | 5.05 | 3.45 | #DIV/0! | #DIV/0! | #DIV/0! | 8.9 | 12.35 |  | Average | --- | --- | --- | --- | 7.8 | 0.55 | 21.8 | #DIV/0! | 0.615 | 0.01 | #VALUE! | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | #DIV/0! | 1 | 1.8 | 6.5 | 8.95 | 17.75 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | 2
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 8.6957 | 5.2632 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6667 | 5.5556 | 5.1282 | 12.2449 | 6.1891 | 2.8169 | 0 | 5.3476 | #VALUE! | 15.873 | 8 | #VALUE! | #VALUE! | #VALUE! | 2.4965 | 3.9135 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 13.3333 | 0 | 13.3333 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 16.3934 | 16.6667 | 9.5238 | 6.8966 | 11.194 | #VALUE! | 0 | 6.8966 | #VALUE! | 1.9802 | 2.8986 | #VALUE! | #VALUE! | #VALUE! | 2.2472 | 2.4291 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 1.626 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 22.2222 | 15.3846 | 7.8212 | 17.4648 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | BAICR-IN7 | Primary | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.7 | 0.076 | 2.0541 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 290 | 56 | 46 | 33 | 6.6 | 141.6 | 3.5 | 18 | 13 | BMRL | 4.8 | 15 | NA | NA | NA | 39.3 | 54.3 | BAICR-107 | Primary | 1998-04-30 | 11:55 | 404.5 | 2427 | 8.5 | 0.19 | 20.6 | BMRL | 2.1 | 0.041 | 1.9524 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 17 | 23 | 25 | 8.1 | 73.1 | BMRL | 5.7 | 3.9 | BMRL | 5.8 | 7.7 | NA | NA | NA | 15.4 | 23.1 | BAICR-207 | Primary | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.5 | 0.019 | 1.2667 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 71 | 2.7 | 9.2 | 22 | 16 | 49.9 | BMRL | 1.7 | 2.3 | BMRL | 5.2 | 3.9 | NA | NA | NA | 9.2 | 13.1
[9 empty] | BAICR-IN7 D | Duplicate | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.9 | 0.078 | 2 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 300 | 54 | 46 | 33 | 6.8 | 139.8 | NR | 18 | 13 | 1 | 4.5 | 15 | NA | NA | NA | NR | NR | BAICR-107 D | Duplicate | 1998-04-30 | 11:55 | 404.5 | 2427 | 8.5 | 0.19 | 20.6 | BMRL | 2.2 | 0.042 | 1.9091 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16 | 22 | 25 | 7.9 | 70.9 | BMRL | 6.1 | 3.8 | BMRL | 5.4 | 7.4 | NA | NA | NA | 15.3 | 22.7 | BAICR-207 D | Duplicate | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.4 | 0.02 | 1.4286 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 66 | 3 | 10 | 24 | 18 | 55 | BMRL | 1.7 | 2.4 | BMRL | 5.8 | 4 | NA | NA | NA | 9.9 | 13.9
[10 empty] | Average | --- | --- | --- | --- | --- | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | #DIV/0! | 160 | 3.8 | 0.077 | 2.027 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 295 | 55 | 46 | 33 | 6.7 | 140.7 | 3.5 | 18 | 13 | 1 | 4.65 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | 39.3 | 54.3 |  | Average | --- | --- | --- | --- | 8.5 | 0.19 | 20.6 | #DIV/0! | 2.15 | 0.0415 | 1.9307 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16.5 | 22.5 | 25 | 8 | 72 | #DIV/0! | 5.9 | 3.85 | #DIV/0! | 5.6 | 7.55 | #DIV/0! | #DIV/0! | #DIV/0! | 15.35 | 22.9 |  | Average | --- | --- | --- | --- | 7.5 | 0.09 | 28.5 | #DIV/0! | 1.45 | 0.0195 | 1.3476 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 68.5 | 2.85 | 9.6 | 23 | 17 | 52.45 | #DIV/0! | 1.7 | 2.35 | #DIV/0! | 5.5 | 3.95 | #DIV/0! | #DIV/0! | #DIV/0! | 9.55 | 13.5
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 5.2632 | 2.5974 | 2.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3898 | 3.6364 | 0 | 0 | 2.9851 | 1.2793 | #VALUE! | 0 | 0 | #VALUE! | 6.4516 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 4.6512 | 2.4096 | 2.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0606 | 4.4444 | 0 | 2.5 | 3.0556 | #VALUE! | 6.7797 | 2.5974 | #VALUE! | 7.1429 | 3.9735 | #VALUE! | #VALUE! | #VALUE! | 0.65147 | 1.7467 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 6.8966 | 5.1282 | 12.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2993 | 10.5263 | 8.3333 | 8.6957 | 11.7647 | 9.7235 | #VALUE! | 0 | 4.2553 | #VALUE! | 10.9091 | 2.5316 | #VALUE! | #VALUE! | #VALUE! | 7.3298 | 5.9259
[9 empty] | BAICR-IN12 | Primary | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | NA | 2.9 | 0.061 | 2.1034 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 | Primary | 1998-05-18 | 15:50 | 840.4167 | 5042.5 | 7.9 | 0.16 | 27 | BMRL | 2.5 | BMRL | #VALUE! | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 150 | 17 | 28 | 35 | 13 | 93 | NR | 6 | 5.2 | BMRL | 6.4 | 8.8 | NA | NA | NA | NR | NR | BAICR-2012 | Primary | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.4 | 0.02 | 1.4286 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[9 empty] | BAICR-IN12 D | Duplicate | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | 130 | 2.9 | 0.066 | 2.2759 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 D | Duplicate | 1998-05-18 | 15:50 | 840.4167 | 5042.5 | 7.9 | 0.16 | 27 | BMRL | 2.4 | 0.041 | 1.7083 | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 160 | 18 | 28 | 36 | 14 | 96 | BMRL | 6.2 | 5.4 | 1 | 6.1 | 8.9 | NA | NA | NA | 18.7 | 27.6 | BAICR-2012 D | Duplicate | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.2 | 0.018 | 1.5 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 6.8 | 0.23 | 90 | 29 | 144 | 120 | #DIV/0! | 130 | 2.9 | 0.0635 | 2.1897 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | Average | --- | --- | --- | --- | 7.9 | 0.16 | 27 | #DIV/0! | 2.45 | 0.041 | #VALUE! | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 155 | 17.5 | 28 | 35.5 | 13.5 | 94.5 | #DIV/0! | 6.1 | 5.3 | 1 | 6.25 | 8.85 | #DIV/0! | #DIV/0! | #DIV/0! | 18.7 | 27.6 |  | Average | --- | --- | --- | --- | 6.8 | 0.14 | 30 | #DIV/0! | 1.3 | 0.019 | 1.4643 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 0 | 7.874 | 7.874 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 4.0816 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 6.4516 | 5.7143 | 0 | 2.8169 | 7.4074 | 3.1746 | #VALUE! | 3.2787 | 3.7736 | #VALUE! | 4.8 | 1.1299 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 15.3846 | 10.5263 | 4.878 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on A1: Reviewer M.H. (2/2/00): 2. The data in the Data Collection Spreadsheets have been separated to differentiate between the two halves of the run (in terms of pretreatment). The "first" run (up to 51 days of operation) utilized chemical pretreatment doses similar to the full-scale plant. The weighted average ferric sulfate dose was 20 mg/L (range: 10 to 30 mg/L). The weighted average calcium hydroxide dose was 52 mg/L (range: 40 to 60 mg/L). During the "second" run (changing pretreatment conditions which affected the second half of the 20 minute EBCT run, after 51 days of operation), the average ferric sulfate dose was 39 mg/L (range: 20 to 100 mg/L) and the average calcium hydroxide dose was 11 mg/L (range: 0 to 120 mg/L). The original data has been included as a third sheet for reference, but should not be used for further data analysis. It should be noted when interpreting the results of the second half of the run in terms of pretreatment, that the first half of the run was conducted under conventional coagulant doses (similar to the full-scale plant). The GAC influent data collected during the entire run has been included with the GAC effluent data from the second half of the run.
Note on E11: Reviewer M.H. (11/13/99): Per Utility: "This has been corrected to calculate the correct value. Note that size 18 mesh was added since this was not provided. If size 16 and 20 mesh are used in the calculation, the effective size calculated is smaller than that provided to us by the manufacturer."
Note on E12: Reviewer M.H. (11/13/99): Per Utility: "This has been corrected to calculate the correct value. Note that size 18 mesh was added since this was not provided. If size 16 and 20 mesh are used in the calculation, the effective size calculated is smaller than that provided to us by the manufacturer."
Note on K6: Reviewer M.H. (1/10/00): Reviewer changed results by calculating a weighted average of the dosages as reported in Table 4-1 in the summary report, per consultant's request.
Note on K7: Reviewer M.H. (1/10/00): Reviewer changed results by calculating a weighted average of the dosages as reported in Table 4-1 in the summary report, per consultant's request.
Note on AF39: Reviewer M.H. (11/13/99): Per utility "The reported duplicates SDS chlorination conditions are correct as shown. These are the measured values."
Note on AG39: Reviewer M.H. (11/13/99): Per utility "The reported duplicates SDS chlorination conditions are correct as shown. These are the measured values."
Note on AI39: Reviewer M.H. (11/13/99): Per utility "The reported duplicates SDS chlorination conditions are correct as shown. These are the measured values."
Note on AJ39: Reviewer M.H. (11/13/99): Per utility "The reported duplicates SDS chlorination conditions are correct as shown. These are the measured values."
Note on AK39: Reviewer M.H. (11/13/99): Per utility "The reported duplicates SDS chlorination conditions are correct as shown. These are the measured values."
Note on BV5: Reviewer M.H. (11/13/99): Per Utility: "The measured incubation time is reported on the spreadsheets."
Note on DG5: Reviewer M.H. (11/13/99): Per Utility: "The measured incubation time is reported on the spreadsheets."

## Sheet2. 2nd Pilot Study
FIELD-SET 1: RESULTS FROM "2nd" PILOT-SCALE STUDY WITH VARYING CHEMICAL SCHEMES (AS APPROVED BY USEPA IN THE STUDY PLAN)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot Scale GAC Contactors | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Dallas Water Utilities Department | Carbon manufacturer | Calgon Carbon Corporation | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0570004 | Carbon trade name | GAC Filtrasorb 820 | mesh size | (mm) | Primary Coagulation | Ferric Sulfate (Fe2(SO4)3), avg=39 mg/L (20-100 mg/L) | Pilot | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6.6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal | 4 | 4.75 | Primary Coagulation | Calcium Hydroxide (Ca(OH)2), avg=11 mg/L (0 - 120 mg/L) | Pilot |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 11.9
|  | Pilot GAC influent TOC (mg/L) | 4.7 | 6 | 3.35 | Primary Flocculation | three-stage, 12 minutes/stage | Pilot | START | --- | 1998-04-13 | 15:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | [36 empty] | START | --- | 1998-04-13 | 15:15 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 101.6 | 8 | 2.36 | Primary Sedimentation | tube settler, 23 minutes detention | Pilot | BAICR-IN1 | N | 1998-04-14 | 15:00 | 24 | 72 | 144 | 8.6 | 0.17 | 49 | 19.7 | 77 | 57 | BMRL | 110 | 3.9 | 0.079 | 2.0256 | 4.5 | 1 | 3.5 | 22 | 8.6 | 24 | NR | 68 | 36 | 17 | BMRL | 121 | 2.5 | 22 | 11 | BMRL | 2.7 | 12 | NA | NA | NA | 38.2 | 50.2 | [36 empty] | BAICR-2011 | N | 1998-06-11 | 13:45 | 1414.5 | 4243.5 | 7.1 | 0.11 | 27 | BMRL | 1.6 | 0.026 | 1.625 | 2.4 | 1.05 | 1.35 | 29 | 7.4 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 549.1 | 10 | 2 | Secondary Coagulation | Ferric Sulfate (Fe2(SO4)3), 7 - 10 mg/L | Pilot | BAICR-IN2 | N | 1998-04-20 | 15:30 | 168.5 | 505.5 | 1011 | 8.5 | 0.23 | 47 | 20.9 | 73 | 56 | BMRL | 110 | 3.7 | 0.089 | 2.4054 | 4.5 | 1.1 | 3.4 | 19.7 | 8.8 | 24 | 250 | 58 | 30 | 15 | 2 | 105 | 3.1 | 20 | 7.5 | BMRL | 2.8 | 11 | NA | NA | NA | 33.4 | 44.4 | [36 empty] | BAICR-2012 | Y | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.3 | 0.019 | 1.4615 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Construction Contingencies (% of construction costs) | 15
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 | Secondary Flocculation | three-stage, 12 minutes/stage | Pilot | BAICR-IN3 | Y | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | BMRL | 115 | 3.8 | 0.084 | 2.2105 | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 60 | 36 | 19.5 | 2.45 | 117.95 | 3.55 | 20 | 9.35 | BMRL | 3.15 | 12.5 | NA | NA | NA | 36.05 | 48.55 | [36 empty] | BAICR-2013 | N | 1998-06-25 | 13:40 | 1750.4167 | 5251.25 | 7.1 | 0.21 | 31.5 | BMRL | 1.6 | 0.024 | 1.5 | 2.5 | 0.91 | 1.59 | 30 | 7.4 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 20 | 16 | 1.18 | Secondary Sedimentation | tube settler, 23 minutes detention | Pilot | BAICR-IN4 | N | 1998-04-30 | 11:16 | 404.2667 | 1212.8 | 2425.6 | 8.7 | 0.16 | 59 | 20.6 | 88 | 69 | BMRL | 120 | 3.8 | 0.085 | 2.2368 | 4.3 | 0.95 | 3.35 | 22 | 8.6 | 24 | 260 | 56 | 35 | 19 | 2.5 | 112.5 | 2.3 | 19 | 10 | BMRL | 3.2 | 13 | NA | NA | NA | 34.5 | 47.5 | [36 empty] | BAICR-2014 | N | 1998-07-07 | 15:30 | 2040.25 | 6120.75 | 9.2 | 0.05 | 32.5 | BMRL | NR | NR | NR | 4 | 0.75 | 3.25 | 31.5 | 8.8 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | 1998 ENR Construction Cost Index (CCI base year 1913) | 3941.46
FAX Number |  | Flow rate, Q (L/hr) | 45.42 | 18 | 1 | Dual Media Filtration | sand/anthracite | Pilot | BAICR-IN5 | N | 1998-05-06 | 12:30 | 549.5 | 1648.5 | 3297 | 8.4 | 0.23 | 55 | 24.6 | 96 | 74 | BMRL | 140 | 3.7 | 0.081 | 2.1892 | 4.3 | 0.83 | 3.47 | 25.3 | 8.3 | 24 | 310 | 54 | 40 | 27 | 4.9 | 125.9 | 2.3 | 18 | 11 | BMRL | 6 | 15 | NA | NA | NA | 37.3 | 52.3 | [36 empty] | BAICR-2015 | N | 1998-07-21 | 15:10 | 2375.9167 | 7127.75 | 6.3 | 0.06 | 32.5 | BMRL | NR | NR | NR | 2.6 | 1 | 1.6 | 31.5 | 6.5 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | 20 | 0.85 |  |  |  | BAICR-IN6 | N | 1998-05-11 | 13:00 | 670 | 2010 | 4020 | 8.2 | 0.15 | 61 | 25 | 106 | 80 | BMRL | 150 | 3.8 | 0.08 | 2.1053 | 4.3 | 0.93 | 3.37 | 26 | 8.2 | 24 | NR | 53 | 42 | 28 | 5.1 | 128.1 | 3.3 | 17 | 12 | BMRL | 4.2 | 14 | NA | NA | NA | 36.5 | 50.5 | [36 empty] | BAICR-2016 | N | 1998-08-04 | 11:15 | 2708 | 8124 | 6.4 | 0.1 | 32 | BMRL | 0.79 | 0.01 | 1.2658 | 2.4 | 0.9 | 1.5 | 29 | 8.3 | 24 | BMRL | 2.5 | 7.7 | 18 | 14 | 42.2 | 3.6 | NR | NR | BMRL | 3.4 | 2.5 | NA | NA | NA | NR | NR | Labor Rate + Fringe ($/work-hour) | 20
|  | Estimated Run Length |  | 30 | 0.6 |  |  |  | BAICR-IN7 | Y | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.8 | 0.077 | 2.0263 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 295 | 55 | 46 | 33 | 6.7 | 140.7 | 3.5 | 18 | 13 | 1 | 4.65 | 15 | NA | NA | NA | 40.15 | 55.15 | [36 empty] | BAICR-2017 | N | 1998-08-18 | 15:20 | 3048.0833 | 9144.25 | 6.5 | 0.15 | 31 | BMRL | 1.1 | 0.015 | 1.3636 | 2.2 | 0.61 | 1.59 | 31 | 8 | 24 | NR | 2.5 | 8.6 | 20 | 17 | 48.1 | 3.8 | 1.4 | 1.7 | BMRL | 4.8 | 2.7 | NA | NA | NA | 11.7 | 14.4 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 2902.2346 | 40 | 0.425 |  |  |  | BAICR-IN8 | N | 1998-05-21 | 11:00 | 908 | 2724 | 5448 | 7.9 | 0.25 | 80 | 27 | 124 | 102 | BMRL | 150 | 3.8 | 0.083 | 2.1842 | 5 | 0.97 | 4.03 | 26 | 7.9 | 24 | 340 | 59 | 44 | 29 | 5.3 | 137.3 | 4 | 24 | 17 | 1.4 | 4.7 | 16 | NA | NA | NA | 51.1 | 67.1 | [36 empty] | BAICR-2018 | N | 1998-09-01 | 13:40 | 3382.4167 | 10147.25 | 6.6 | 0.12 | 31 | BMRL | 1.3 | 0.015 | 1.1538 | 2.6 | 0.77 | 1.83 | 30 | 8.3 | 24 | 60 | 2.4 | 9.8 | 19 | 15 | 46.2 | BMRL | 1.8 | 1.3 | BMRL | 5.3 | 3.1 | NA | NA | NA | 8.4 | 11.5 | Electric Rate ($/kW-h) | 0.05273
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 5804.4692 | 50 | 0.3 |  |  |  | BAICR-IN9 | N | 1998-05-27 | 10:25 | 1051.4167 | 3154.25 | 6308.5 | 7.9 | 0.22 | 85 | 26 | 129 | 101 | BMRL | 160 | 3.8 | 0.097 | 2.5526 | 4.8 | 0.98 | 3.82 | 27 | 7.8 | 24 | NR | 46 | 38 | 27 | 4.7 | 115.7 | 5.2 | 23 | 12 | 1.6 | 4.9 | 10 | NA | NA | NA | 46.7 | 56.7 | [36 empty] | BAICR-2019 | N | 1998-09-15 | 13:45 | 3718.5 | 11155.5 | 6.6 | 0.11 | 27 | BMRL | 1.6 | 0.02 | 1.25 | 2.4 | 0.87 | 1.53 | 26 | 8.1 | 24 | 73 | 3.2 | 10 | 19 | 13 | 45.2 | NR | 1.3 | 1.4 | BMRL | 5.1 | 3.2 | NA | NA | NA | NR | NR | Fuel Oil Rate ($/gal)
|  |  |  | 60 | 0.25 |  |  |  | BAICR-IN10 | N | 1998-06-02 | 13:00 | 1198 | 3594 | 7188 | 8 | 0.32 | 78 | 29 | 111 | 91 | BMRL | 140 | 3.8 | 0.093 | 2.4474 | 5.5 | 0.85 | 4.65 | 29 | 7.9 | 24 | 360 | 68 | 44 | 26 | 3.6 | 141.6 | 5.6 | 30 | 17 | BMRL | 3.5 | 17 | NA | NA | NA | 56.1 | 73.1 | [36 empty] | BAICR-2020 | N | 1998-09-29 | 11:25 | 4052.1667 | 12156.5 | 6.6 | 0.13 | 30 | BMRL | 1.9 | 0.021 | 1.1053 | 2.6 | 0.65 | 1.95 | 29 | 8.2 | 24 | 88 | 4.3 | 12 | 21 | 15 | 52.3 | 3.5 | 2.6 | 2.7 | BMRL | 8.7 | 5 | NA | NA | NA | 17.5 | 22.5 | Natural Gas Rate ($/ft3)
|  | General Pilot Design Parameters |  | 70 | 0.21 |  |  |  | BAICR-IN11 | N | 1998-06-11 | 13:00 | 1414 | 4242 | 8484 | 7.5 | 0.11 | 100 | 26.5 | 182 | 164 | BMRL | 130 | 3.2 | 0.076 | 2.375 | 4.5 | 1.25 | 3.25 | 28.3 | 7.8 | 24 | 270 | 39 | 27 | 16 | 3 | 85 | 6.1 | 20 | 15 | BMRL | 3.3 | 12 | NA | NA | NA | 44.4 | 56.4 | [36 empty] | BAICR-2021 | N | 1998-10-13 | 14:55 | 4391.6667 | 13175 | 7.1 | 0.09 | 25 | 0.15 | 1.9 | 0.027 | 1.4211 | 2.7 | 0.78 | 1.92 | 24 | 8.1 | 24 | 92 | 6 | 11 | 14 | 7.2 | 38.2 | BMRL | 3.3 | 2.6 | BMRL | 6.2 | 5.3 | NA | NA | NA | 12.1 | 17.4 | Current Process Water Rate ($/1000 gal) | 0.1
Phone Number |  | Carbon particle diameter, d (mm) | 1.605 | 80 | 0.18 |  |  |  | BAICR-IN12 | Y | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | 130 | 2.9 | 0.0635 | 2.1897 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | [36 empty] | BAICR-2022 | N | 1998-10-27 | 14:35 | 4727.3333 | 14182 | 6.9 | 0.09 | 23 | BMRL | 2.3 | 0.03 | 1.3043 | 3 | 1.11 | 1.89 | 22 | 8.2 | 24 | 120 | 8.1 | 13 | 17 | 8.7 | 46.8 | 3.1 | 3.7 | 3 | BMRL | 5.6 | 5.9 | NA | NA | NA | 15.4 | 21.3 | Modifications to Existing Plant (% of construction costs) | 30
FAX Number |  | Column cross-sectional area, A (m2) | 0.0081073 | [5 empty] | BAICR-IN13 | N | 1998-06-25 | 13:00 | 1750 | 5250 | 10500 | 7 | 0.23 | 97 | 30.3 | 136 | 116 | BMRL | 140 | 3.2 | 0.061 | 1.9062 | 4.4 | 0.85 | 3.55 | 29.5 | 7.4 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | [36 empty] | BAICR-2023 | N | 1998-11-10 | 13:55 | 5062.6667 | 15188 | 6.8 | 0.1 | 18 | BMRL | NR | 0.018 | NR | 2.4 | 1.08 | 1.32 | 18 | 8 | 24 | 80 | 2.5 | 6.3 | 9.5 | 5.3 | 23.6 | BMRL | 1.9 | 2.5 | BMRL | 3.3 | 3.5 | NA | NA | NA | 7.7 | 11.2
E-Mail Address (optional) |  | Hydraulic loading rate1, v (m/hr) | 5.6023 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | BAICR-IN14 | N | 1998-07-07 | 15:00 | 2040 | 6120 | 12240 | 10.6 | 0.06 | 45 | 31.7 | 109 | 98 | BMRL | 130 | 2.8 | 0.05 | 1.7857 | 5 | 0.82 | 4.18 | 31.5 | 10.5 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | [36 empty] | BAICR-2024 | N | 1998-12-15 | 19:15 | 5779 | 17337 | 7.4 | 0.13 | 19 | BMRL | 2.6 | 0.05 | 1.9231 | 2.5 | 1.14 | 1.36 | 19 | 8.2 | 24 | 130 | 12 | 14 | 11 | 2.3 | 39.3 | BMRL | 5.6 | 5.4 | BMRL | 2.5 | 5.8 | NA | NA | NA | 13.5 | 19.3
|  | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | BAICR-IN15 | N | 1998-07-21 | 14:35 | 2375.5833 | 7126.75 | 14253.5 | 6 | 0.07 | 35 | 31.5 | 123 | 102 | BMRL | 160 | 2.2 | 0.033 | 1.5 | 4.3 | 1.2 | 3.1 | 31.5 | 6.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
Plant Name | Bachman Water Treatment Plant |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | BAICR-IN16 | N | 1998-08-04 | 10:30 | 2707.5 | 8122.5 | 16245 | 6 | 0.09 | 38 | 31 | 118 | 96 | BMRL | 140 | 2.1 | 0.031 | 1.4762 | 4 | 0.79 | 3.21 | 29 | 7.8 | 24 | 140 | 19 | 24 | 23 | 7.3 | 73.3 | 3.6 | 12 | 10 | BMRL | 1.5 | 7.2 | NA | NA | NA | 27.1 | 34.3
Treatment Plant Category | TS/SOFT | 10-Minute EBCT Run | [6 empty] | BAICR-IN17 | N | 1998-08-18 | 14:30 | 3047.5 | 9142.5 | 18285 | 6.3 | 0.1 | 57 | 30 | 118 | 98 | BMRL | 140 | 2.1 | 0.04 | 1.9048 | 4.1 | 0.63 | 3.47 | 30 | 8 | 24 | NR | 23 | 25 | 23 | 8 | 79 | 3.4 | 7.3 | 4.3 | BMRL | 5.5 | 7.5 | NA | NA | NA | 20.5 | 28 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Process Train Name | Two-stage softening | Empty bed contact time, EBCT (min) | 10 | [5 empty] | BAICR-IN18 | N | 1998-09-01 | 12:45 | 3381.75 | 10145.25 | 20290.5 | 6.3 | 0.08 | 51 | 30 | 112 | 90 | BMRL | 130 | 2.3 | 0.04 | 1.7391 | 4.5 | 0.81 | 3.69 | 30 | 8.1 | 24 | 150 | 21 | 24 | 22 | 8.4 | 75.4 | BMRL | 6.7 | 3.6 | BMRL | 4.5 | 6.3 | NA | NA | NA | 14.8 | 21.1 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
ICR Treatment Plant Identification Number | 620 | Estimated run time, t (days) | 40.3088 | [5 empty] | BAICR-IN19 | N | 1998-09-15 | 13:05 | 3718.0833 | 11154.25 | 22308.5 | 6.5 | 0.1 | 51 | 26 | 113 | 93 | BMRL | 160 | 2.2 | 0.04 | 1.8182 | 4 | 0.86 | 3.14 | 26 | 8 | 24 | 170 | 21 | 25 | 23 | 8.3 | 77.3 | 2.1 | 5.6 | 4.5 | BMRL | 5.2 | 7.2 | NA | NA | NA | 17.4 | 24.6 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
PWSID Number of Plant (if assigned) | TX0570004 | Pilot column bed length, l (m) | 0.93372 | [5 empty] | BAICR-IN20 | N | 1998-09-29 | 10:45 | 4051.75 | 12155.25 | 24310.5 | 6.5 | 0.11 | 54 | 29 | 108 | 87 | BMRL | 150 | 2.7 | 0.05 | 1.8519 | 4.1 | 0.68 | 3.42 | 28 | 8 | 24 | 180 | 16 | NR | 19 | 7.3 | NR | 2.4 | 8.5 | 6.4 | BMRL | 8.7 | 10 | NA | NA | NA | 26 | 36
Historical Minimum Water Temperature (oC) | 5 | Mass GAC required, m (kg) | 4.1567 | [5 empty] | BAICR-IN21 | N | 1998-10-13 | 13:50 | 4390.8333 | 13172.5 | 26345 | 6.9 | 0.09 | 69 | 24 | 121 | 103 | BMRL | 140 | 2.9 | 0.052 | 1.7931 | 3.9 | 0.79 | 3.11 | 23 | 8.1 | 24 | 200 | 17 | 16 | 13 | 3.7 | 49.7 | 3 | 9.2 | 6.4 | BMRL | 4.9 | 8.8 | NA | NA | NA | 23.5 | 32.3
Historical Average Water Temperature (oC) | 20 | [7 empty] | BAICR-IN22 | N | 1998-10-27 | 14:00 | 4727 | 14181 | 28362 | 6.8 | 0.1 | 69 | 23 | 129 | 109 | BMRL | 95 | 3.1 | 0.052 | 1.6774 | 4 | 0.85 | 3.15 | 22 | 8.3 | 24 | 190 | 20 | 20 | 18 | 5.5 | 63.5 | 3.8 | 9.4 | 5.7 | BMRL | 5.3 | 9 | NA | NA | NA | 24.2 | 33.2
State Approved Plant Capacity (MGD) | 115 | 20-Minute EBCT Run | [6 empty] | BAICR-IN23 | N | 1998-11-10 | 13:10 | 5062.1667 | 15186.5 | 30373 | 6.7 | 0.1 | 51 | 18 | 119 | 101 | 0.11 | 130 | NR | 0.034 | #VALUE! | 3.6 | 1.05 | 2.55 | 18 | 8 | 24 | 130 | 7.4 | 12 | 13 | 5.1 | 37.5 | 2.3 | 5.1 | 4.6 | BMRL | 4 | 5.6 | NA | NA | NA | 16 | 21.6
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | BAICR-IN24 | N | 1998-12-16 | 19:15 | 5803.25 | 17409.75 | 34819.5 | 8.3 | 0.18 | 37 | 17.1 | 100 | 84 | BMRL | 97 | 2.9 | 0.077 | 2.6552 | 3.5 | 1.21 | 2.29 | 17.2 | 8.3 | 24 | 260 | 26 | 18 | 9 | 1.5 | 54.5 | 2.1 | 12 | 14 | BMRL | 1.7 | 7.1 | NA | NA | NA | 29.8 | 36.9
|  | Estimated run time, t (days) | 80.6176 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [76 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Pilot column bed length, l (m) | 1.8674 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [76 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  | Mass GAC required, m (kg) | 8.3134 | [5 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [76 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | BAICR-IN3 | Primary | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | BMRL | 110 | 3.7 | NR | #VALUE! | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 62 | 37 | 20 | 2.6 | 121.6 | 3.6 | 20 | 9.1 | BMRL | 2.9 | 12 | NA | NA | NA | 35.6 | 47.6 | BAICR-103 | Primary | 1998-04-20 | 16:00 | 861736 | 5170416 | 8.6 | 0.22 | 21.3 | BMRL | 1.4 | 0.03 | 2.1429 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 6.6 | 13 | 22 | 15 | 56.6 | BMRL | 2.4 | 1.4 | BMRL | 5 | 3.4 | NA | NA | NA | 8.8 | 12.2 | BAICR-203 | Primary | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | BMRL | 0.62 | NR | NA | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | 1 | 2 | 7 | 9.3 | 19.3 | BMRL | BMRL | BMRL | BMRL | 2 | BMRL | NA | NA | NA | 2 | 2
[9 empty] | BAICR-IN3 D | Duplicate | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | NA | 120 | 3.9 | 0.084 | 2.1538 | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 58 | 35 | 19 | 2.3 | 114.3 | 3.5 | 20 | 9.6 | BMRL | 3.4 | 13 | NA | NA | NA | 36.5 | 49.5 | BAICR-103 D | Duplicate | 1998-04-20 | 16:00 | 861736 | 5170416 | 8.6 | 0.22 | 21.3 | BMRL | 1.6 | 0.03 | 1.875 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 5.6 | 11 | 20 | 14 | 50.6 | BMRL | 2.4 | 1.5 | BMRL | 5.1 | 3.5 | NA | NA | NA | 9 | 12.5 | BAICR-203 D | Duplicate | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | NA | 0.61 | 0.01 | 1.6393 | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | BMRL | 1.6 | 6 | 8.6 | 16.2 | BMRL | BMRL | BMRL | BMRL | NR | BMRL | NA | NA | NA | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 8.5 | 0.19 | 51 | 21 | 79 | 61 | #DIV/0! | 115 | 3.8 | 0.084 | #VALUE! | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 60 | 36 | 19.5 | 2.45 | 117.95 | 3.55 | 20 | 9.35 | #DIV/0! | 3.15 | 12.5 | #DIV/0! | #DIV/0! | #DIV/0! | 36.05 | 48.55 |  | Average | --- | --- | --- | --- | 8.6 | 0.22 | 21.3 | #DIV/0! | 1.5 | 0.03 | 2.0089 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | #DIV/0! | 6.1 | 12 | 21 | 14.5 | 53.6 | #DIV/0! | 2.4 | 1.45 | #DIV/0! | 5.05 | 3.45 | #DIV/0! | #DIV/0! | #DIV/0! | 8.9 | 12.35 |  | Average | --- | --- | --- | --- | 7.8 | 0.55 | 21.8 | #DIV/0! | 0.615 | 0.01 | 1.64 | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | #DIV/0! | 1 | 1.8 | 6.5 | 8.95 | 17.75 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | 2
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 8.6957 | 5.2632 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6667 | 5.5556 | 5.1282 | 12.2449 | 6.1891 | 2.8169 | 0 | 5.3476 | #VALUE! | 15.873 | 8 | #VALUE! | #VALUE! | #VALUE! | 2.4965 | 3.9135 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 13.3333 | 0 | 13.3333 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 16.3934 | 16.6667 | 9.5238 | 6.8966 | 11.194 | #VALUE! | 0 | 6.8966 | #VALUE! | 1.9802 | 2.8986 | #VALUE! | #VALUE! | #VALUE! | 2.2472 | 2.4291 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 1.626 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 22.2222 | 15.3846 | 7.8212 | 17.4648 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | BAICR-IN7 | Primary | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.7 | 0.076 | 2.0541 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 290 | 56 | 46 | 33 | 6.6 | 141.6 | 3.5 | 18 | 13 | BMRL | 4.8 | 15 | NA | NA | NA | 39.3 | 54.3 | BAICR-107 | Primary | 1998-04-30 | 11:55 | 861971.9167 | 5171831.5 | 8.5 | 0.19 | 20.6 | BMRL | 2.1 | 0.041 | 1.9524 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 17 | 23 | 25 | 8.1 | 73.1 | BMRL | 5.7 | 3.9 | BMRL | 5.8 | 7.7 | NA | NA | NA | 15.4 | 23.1 | BAICR-207 | Primary | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.5 | 0.019 | 1.2667 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 71 | 2.7 | 9.2 | 22 | 16 | 49.9 | BMRL | 1.7 | 2.3 | BMRL | 5.2 | 3.9 | NA | NA | NA | 9.2 | 13.1
[9 empty] | BAICR-IN7 D | Duplicate | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.9 | 0.078 | 2 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 300 | 54 | 46 | 33 | 6.8 | 139.8 | NR | 18 | 13 | 1 | 4.5 | 15 | NA | NA | NA | NR | NR | BAICR-107 D | Duplicate | 1998-04-30 | 11:55 | 861971.9167 | 5171831.5 | 8.5 | 0.19 | 20.6 | BMRL | 2.2 | 0.042 | 1.9091 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16 | 22 | 25 | 7.9 | 70.9 | BMRL | 6.1 | 3.8 | BMRL | 5.4 | 7.4 | NA | NA | NA | 15.3 | 22.7 | BAICR-207 D | Duplicate | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.4 | 0.02 | 1.4286 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 66 | 3 | 10 | 24 | 18 | 55 | BMRL | 1.7 | 2.4 | BMRL | 5.8 | 4 | NA | NA | NA | 9.9 | 13.9
[10 empty] | Average | --- | --- | --- | --- | --- | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | #DIV/0! | 160 | 3.8 | 0.077 | 2.027 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 295 | 55 | 46 | 33 | 6.7 | 140.7 | 3.5 | 18 | 13 | 1 | 4.65 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | 39.3 | 54.3 |  | Average | --- | --- | --- | --- | 8.5 | 0.19 | 20.6 | #DIV/0! | 2.15 | 0.0415 | 1.9307 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16.5 | 22.5 | 25 | 8 | 72 | #DIV/0! | 5.9 | 3.85 | #DIV/0! | 5.6 | 7.55 | #DIV/0! | #DIV/0! | #DIV/0! | 15.35 | 22.9 |  | Average | --- | --- | --- | --- | 7.5 | 0.09 | 28.5 | #DIV/0! | 1.45 | 0.0195 | 1.3476 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 68.5 | 2.85 | 9.6 | 23 | 17 | 52.45 | #DIV/0! | 1.7 | 2.35 | #DIV/0! | 5.5 | 3.95 | #DIV/0! | #DIV/0! | #DIV/0! | 9.55 | 13.5
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 5.2632 | 2.5974 | 2.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3898 | 3.6364 | 0 | 0 | 2.9851 | 1.2793 | #VALUE! | 0 | 0 | #VALUE! | 6.4516 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 4.6512 | 2.4096 | 2.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0606 | 4.4444 | 0 | 2.5 | 3.0556 | #VALUE! | 6.7797 | 2.5974 | #VALUE! | 7.1429 | 3.9735 | #VALUE! | #VALUE! | #VALUE! | 0.65147 | 1.7467 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 6.8966 | 5.1282 | 12.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2993 | 10.5263 | 8.3333 | 8.6957 | 11.7647 | 9.7235 | #VALUE! | 0 | 4.2553 | #VALUE! | 10.9091 | 2.5316 | #VALUE! | #VALUE! | #VALUE! | 7.3298 | 5.9259
[9 empty] | BAICR-IN12 | Primary | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | NA | 2.9 | 0.061 | 2.1034 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 | Primary | 1998-05-18 | 15:50 | 862407.8333 | 5174447 | 7.9 | 0.16 | 27 | BMRL | 2.5 | BMRL | #VALUE! | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 150 | 17 | 28 | 35 | 13 | 93 | NR | 6 | 5.2 | BMRL | 6.4 | 8.8 | NA | NA | NA | NR | NR | BAICR-2012 | Primary | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.4 | 0.02 | 1.4286 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[9 empty] | BAICR-IN12 D | Duplicate | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | 130 | 2.9 | 0.066 | 2.2759 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 D | Duplicate | 1998-05-18 | 15:50 | 862407.8333 | 5174447 | 7.9 | 0.16 | 27 | BMRL | 2.4 | 0.041 | 1.7083 | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 160 | 18 | 28 | 36 | 14 | 96 | BMRL | 6.2 | 5.4 | 1 | 6.1 | 8.9 | NA | NA | NA | 18.7 | 27.6 | BAICR-2012 D | Duplicate | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.2 | 0.018 | 1.5 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 6.8 | 0.23 | 90 | 29 | 144 | 120 | #DIV/0! | 130 | 2.9 | 0.0635 | 2.1897 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | Average | --- | --- | --- | --- | 7.9 | 0.16 | 27 | #DIV/0! | 2.45 | 0.041 | #VALUE! | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 155 | 17.5 | 28 | 35.5 | 13.5 | 94.5 | #DIV/0! | 6.1 | 5.3 | 1 | 6.25 | 8.85 | #DIV/0! | #DIV/0! | #DIV/0! | 18.7 | 27.6 |  | Average | --- | --- | --- | --- | 6.8 | 0.14 | 30 | #DIV/0! | 1.3 | 0.019 | 1.4643 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 0 | 7.874 | 7.874 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 4.0816 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 6.4516 | 5.7143 | 0 | 2.8169 | 7.4074 | 3.1746 | #VALUE! | 3.2787 | 3.7736 | #VALUE! | 4.8 | 1.1299 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 15.3846 | 10.5263 | 4.878 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on A1: Reviewer M.H. (2/2/00): 2. The data in the Data Collection Spreadsheets have been separated to differentiate between the two halves of the run (in terms of pretreatment). The "first" run (up to 51 days of operation) utilized chemical pretreatment doses similar to the full-scale plant. The weighted average ferric sulfate dose was 20 mg/L (range: 10 to 30 mg/L). The weighted average calcium hydroxide dose was 52 mg/L (range: 40 to 60 mg/L). During the "second" run (changing pretreatment conditions which affected the second half of the 20 minute EBCT run, after 51 days of operation), the average ferric sulfate dose was 39 mg/L (range: 20 to 100 mg/L) and the average calcium hydroxide dose was 11 mg/L (range: 0 to 120 mg/L). The original data has been included as a third sheet for reference, but should not be used for further data analysis. It should be noted when interpreting the results of the second half of the run in terms of pretreatment, that the first half of the run was conducted under conventional coagulant doses (similar to the full-scale plant). The GAC influent data collected during the entire run has been included with the GAC effluent data from the second half of the run.
Note on K6: Reviewer M.H. (1/10/00): Reviewer changed results by calculating a weighted average of the dosages as reported in Table 4-1 in the summary report, per consultant's request.
Note on K7: Reviewer M.H. (1/10/00): Reviewer changed results by calculating a weighted average of the dosages as reported in Table 4-1 in the summary report, per consultant's request.
Note on N42: Reviewer M.H. (11/13/99): No duplicates taken during this session.
Note on U23: Reviewer M.H. (11/13/99): According to summary report, lime dosage was terminated after day 70, as a result the pH decreased.
Note on AA31: Reviewer M.H. (11/13/99): Per Utility: "We believe the Ammonia spike in the influent water to be valid. The MRL for ammonia is 0.10mg/L. Thus, a value of 0.11mg/L is not much of a spike. Additionally, the source water experiences spikes in ammonia from time to time."
Note on AK5: Reviewer M.H. (11/13/99): Per Utility: "The measured incubation time is reported on the spreadsheets."
Note on BD42: Reviewer M.H. (11/13/99): No duplicates taken during this session.
Note on CO8: Reviewer M.H. (11/13/99): Moved 1 row to sheet 1.
Note on CO42: Reviewer M.H. (11/13/99): No duplicates taken during this session.
Note on DB10: Reviewer M.H. (11/13/99): Per consultant "The high chlorine dose is a result of the high SDS pH which caused an increase in chlorine demand. The reported duplicates SDS chlorination conditions are correct as shown. These are the measured values."
Note on DG5: Reviewer M.H. (11/13/99): Per Utility: "The measured incubation time is reported on the spreadsheets."

## Sheet3. 3rd Pilot Study
FIELD-SET 1: OVERALL RESULTS FROM BOTH PILOT-SCALE STUDIES (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot Scale GAC Contactors | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Dallas Water Utilities Department | Carbon manufacturer | Calgon Carbon Corporation | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0570004 | Carbon trade name | GAC Filtrasorb 820 | mesh size | (mm) | Primary Coagulation | Ferric Sulfate (Fe2(SO4)3), avg=35 mg/L (10-100 mg/L) | Pilot | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6.6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal | 4 | 4.75 | Primary Coagulation | Calcium Hydroxide (Ca(OH)2), avg=19 mg/L (0 - 120 mg/L) | Pilot |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 11.9
|  | Pilot GAC influent TOC (mg/L) | 4.7 | 6 | 3.35 | Primary Flocculation | three-stage, 12 minutes/stage | Pilot | START | --- | 1998-04-13 | 15:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-13 | 15:25 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-13 | 15:15 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 101.6 | 8 | 2.36 | Primary Sedimentation | tube settler, 23 minutes detention | Pilot | BAICR-IN1 | N | 1998-04-14 | 15:00 | 24 | 72 | 144 | 8.6 | 0.17 | 49 | 19.7 | 77 | 57 | BMRL | 110 | 3.9 | 0.079 | 2.0256 | 4.5 | 1 | 3.5 | 22 | 8.6 | 24 | NR | 68 | 36 | 17 | BMRL | 121 | 2.5 | 22 | 11 | BMRL | 2.7 | 12 | NA | NA | NA | 38.2 | 50.2 | BAICR-101 | N | 1998-04-14 | 15:25 | 24 | 144 | 9 | 0.18 | 19.5 | BMRL | BMRL | BMRL | NR | 1.5 | 1.1 | 0.4 | 22.3 | 8.8 | 24 | BMRL | BMRL | BMRL | 3.1 | 5.7 | 8.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | BAICR-201 | N | 1998-04-14 | 15:15 | 24 | 72 | 9.2 | 0.3 | 20 | BMRL | BMRL | BMRL | #VALUE! | 1.5 | 1 | 0.5 | 22 | 9.2 | 24 | BMRL | BMRL | BMRL | 1.9 | 3.4 | 5.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 549.1 | 10 | 2 | Secondary Coagulation | Ferric Sulfate (Fe2(SO4)3), 7 - 10 mg/L | Pilot | BAICR-IN2 | N | 1998-04-20 | 15:30 | 168.5 | 505.5 | 1011 | 8.5 | 0.23 | 47 | 20.9 | 73 | 56 | BMRL | 110 | 3.7 | 0.089 | 2.4054 | 4.5 | 1.1 | 3.4 | 19.7 | 8.8 | 24 | 250 | 58 | 30 | 15 | 2 | 105 | 3.1 | 20 | 7.5 | BMRL | 2.8 | 11 | NA | NA | NA | 33.4 | 44.4 | BAICR-102 | N | 1998-04-16 | 15:00 | 71.5833 | 429.5 | 8.3 | 0.21 | 20.6 | BMRL | 0.73 | 0.011 | 1.5068 | 1.5 | 0.9 | 0.6 | 21.7 | 8.6 | 24 | 77 | 1.3 | 3.3 | 11 | 15 | 30.6 | BMRL | BMRL | 1 | BMRL | 2.8 | 1.4 | NA | NA | NA | 3.8 | 5.2 | BAICR-202 | N | 1998-04-20 | 15:45 | 168.5 | 505.5 | 9.6 | 0.22 | 21.8 | BMRL | BMRL | 0.01 | #VALUE! | 1.5 | 1.1 | 0.4 | 19.8 | 8.7 | 24 | 26 | BMRL | 1 | 3.5 | 5.8 | 10.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 | Secondary Flocculation | three-stage, 12 minutes/stage | Pilot | BAICR-IN3 | Y | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | BMRL | 115 | 3.8 | 0.084 | 2.2105 | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 60 | 36 | 19.5 | 2.45 | 117.95 | 3.55 | 20 | 9.35 | BMRL | 3.15 | 12.5 | NA | NA | NA | 36.05 | 48.55 | BAICR-103 | Y | 1998-04-20 | 16:00 | 168.5833 | 1011.5 | 8.6 | 0.22 | 21.3 | BMRL | 1.5 | 0.03 | 2 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 6.1 | 12 | 21 | 14.5 | 53.6 | BMRL | 2.4 | 1.45 | BMRL | 5.05 | 3.45 | NA | NA | NA | 8.9 | 12.35 | BAICR-203 | Y | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | BMRL | 0.615 | 0.01 | 1.626 | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | 1 | 1.8 | 6.5 | 8.95 | 18.25 | BMRL | BMRL | BMRL | BMRL | 2 | BMRL | NA | NA | NA | 2 | 2 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 20 | 16 | 1.18 | Secondary Sedimentation | tube settler, 23 minutes detention | Pilot | BAICR-IN4 | N | 1998-04-30 | 11:16 | 404.2667 | 1212.8 | 2425.6 | 8.7 | 0.16 | 59 | 20.6 | 88 | 69 | BMRL | 120 | 3.8 | 0.085 | 2.2368 | 4.3 | 0.95 | 3.35 | 22 | 8.6 | 24 | 260 | 56 | 35 | 19 | 2.5 | 112.5 | 2.3 | 19 | 10 | BMRL | 3.2 | 13 | NA | NA | NA | 34.5 | 47.5 | BAICR-104 | N | 1998-04-22 | 14:00 | 214.5833 | 1287.5 | 8.8 | 0.17 | 20.7 | BMRL | 1.6 | 0.031 | 1.9375 | 2.4 | 1 | 1.4 | 21.1 | 8.5 | 24 | 96 | 11 | 18 | 25 | 11 | 65 | BMRL | 5.7 | 2.4 | BMRL | 5.6 | 5.2 | NA | NA | NA | 13.7 | 18.9 | BAICR-204 | N | 1998-04-30 | 11:36 | 404.35 | 1213.05 | 8.2 | 0.21 | 21 | BMRL | 1 | 0.025 | 2.5 | 1.9 | 0.97 | 0.93 | 22 | 8.1 | 24 | BMRL | 2.3 | 6.6 | 17 | 15 | 40.9 | BMRL | 1.2 | 1.6 | BMRL | 3.9 | 2.5 | NA | NA | NA | 6.7 | 9.2 | 1998 ENR Construction Cost Index (CCI base year 1913) | 3941.46
FAX Number |  | Flow rate, Q (L/hr) | 45.42 | 18 | 1 | Dual Media Filtration | sand/anthracite | Pilot | BAICR-IN5 | N | 1998-05-06 | 12:30 | 549.5 | 1648.5 | 3297 | 8.4 | 0.23 | 55 | 24.6 | 96 | 74 | BMRL | 140 | 3.7 | 0.081 | 2.1892 | 4.3 | 0.83 | 3.47 | 25.3 | 8.3 | 24 | 310 | 54 | 40 | 27 | 4.9 | 125.9 | 2.3 | 18 | 11 | BMRL | 6 | 15 | NA | NA | NA | 37.3 | 52.3 | BAICR-105 | N | 1998-04-23 | 13:00 | 237.5833 | 1425.5 | 8.6 | 0.19 | 20.9 | BMRL | 1.9 | 0.034 | 1.7895 | 2.3 | 0.85 | 1.45 | 22.6 | 8.7 | 24 | 92 | 10 | 17 | 22 | 9.8 | 58.8 | BMRL | 4.2 | 2.4 | BMRL | 6 | 5.5 | NA | NA | NA | 12.6 | 18.1 | BAICR-205 | N | 1998-05-06 | 13:00 | 549.75 | 1649.25 | 7.8 | 0.18 | 26 | BMRL | 1.2 | 0.018 | 1.5 | 1.9 | 0.96 | 0.94 | 25.4 | 7.8 | 24 | 54 | 2.1 | 6.7 | 18 | 17 | 43.8 | BMRL | 1.3 | 2 | BMRL | 6.2 | 3 | NA | NA | NA | 9.5 | 12.5 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | 20 | 0.85 |  |  |  | BAICR-IN6 | N | 1998-05-11 | 13:00 | 670 | 2010 | 4020 | 8.2 | 0.15 | 61 | 25 | 106 | 80 | BMRL | 150 | 3.8 | 0.08 | 2.1053 | 4.3 | 0.93 | 3.37 | 26 | 8.2 | 24 | NR | 53 | 42 | 28 | 5.1 | 128.1 | 3.3 | 17 | 12 | BMRL | 4.2 | 14 | NA | NA | NA | 36.5 | 50.5 | BAICR-106 | N | 1998-04-27 | 13:15 | 333.8333 | 2003 | 7.9 | 0.52 | 21.4 | BMRL | 1.9 | NR | NR | 2.3 | 0.7 | 1.6 | 20 | 7.8 | 24 | 120 | 11 | 20 | 25 | 8.6 | 64.6 | BMRL | 4.8 | 3.7 | BMRL | 5.9 | 6.6 | NA | NA | NA | 14.4 | 21 | BAICR-206 | N | 1998-05-11 | 13:30 | 670.25 | 2010.75 | 7.7 | 0.12 | 26 | BMRL | 1.4 | 0.021 | 1.5 | 1.9 | 0.95 | 0.95 | 26 | 7.8 | 24 | 65 | 2 | 7.5 | 22 | 19 | 50.5 | BMRL | 1.1 | 1.9 | BMRL | 4.6 | 3.1 | NA | NA | NA | 7.6 | 10.7 | Labor Rate + Fringe ($/work-hour) | 20
|  | Estimated Run Length |  | 30 | 0.6 |  |  |  | BAICR-IN7 | Y | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.8 | 0.077 | 2.0263 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 295 | 55 | 46 | 33 | 6.7 | 140.7 | 3.5 | 18 | 13 | 1 | 4.65 | 15 | NA | NA | NA | 40.15 | 55.15 | BAICR-107 | Y | 1998-04-30 | 11:55 | 404.5 | 2427 | 8.5 | 0.19 | 20.6 | BMRL | 2.15 | 0.0415 | 1.9302 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16.5 | 22.5 | 25 | 8 | 72 | BMRL | 5.9 | 3.85 | BMRL | 5.6 | 7.55 | NA | NA | NA | 15.35 | 22.9 | BAICR-207 | Y | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.45 | 0.0195 | 1.3448 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 68.5 | 2.85 | 9.6 | 23 | 17 | 52.45 | BMRL | 1.7 | 2.35 | BMRL | 5.5 | 3.95 | NA | NA | NA | 9.55 | 13.5 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 2902.2346 | 40 | 0.425 |  |  |  | BAICR-IN8 | N | 1998-05-21 | 11:00 | 908 | 2724 | 5448 | 7.9 | 0.25 | 80 | 27 | 124 | 102 | BMRL | 150 | 3.8 | 0.083 | 2.1842 | 5 | 0.97 | 4.03 | 26 | 7.9 | 24 | 340 | 59 | 44 | 29 | 5.3 | 137.3 | 4 | 24 | 17 | 1.4 | 4.7 | 16 | NA | NA | NA | 51.1 | 67.1 | BAICR-108 | N | 1998-05-04 | 13:22 | 501.95 | 3011.7 | 8.2 | 0.14 | 23 | BMRL | 2.3 | 0.041 | 1.7826 | 2.6 | 0.85 | 1.75 | 24 | 8.1 | 24 | 140 | 17 | 24 | 28 | 11 | 80 | BMRL | 5.7 | 4.4 | BMRL | 8.4 | 8.1 | NA | NA | NA | 18.5 | 26.6 | BAICR-208 | N | 1998-05-21 | 11:25 | 908.1667 | 2724.5 | 7.7 | 0.16 | 28 | BMRL | 1.8 | 0.024 | 1.3333 | 2.3 | 0.83 | 1.47 | 26 | 7.8 | 24 | BMRL | 4.2 | 11 | 24 | 15 | 54.2 | BMRL | 2.3 | 2.8 | 1.1 | 5.6 | 4.7 | NA | NA | NA | 11.8 | 16.5 | Electric Rate ($/kW-h) | 0.05273
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 5804.4692 | 50 | 0.3 |  |  |  | BAICR-IN9 | N | 1998-05-27 | 10:25 | 1051.4167 | 3154.25 | 6308.5 | 7.9 | 0.22 | 85 | 26 | 129 | 101 | BMRL | 160 | 3.8 | 0.097 | 2.5526 | 4.8 | 0.98 | 3.82 | 27 | 7.8 | 24 | NR | 46 | 38 | 27 | 4.7 | 115.7 | 5.2 | 23 | 12 | 1.6 | 4.9 | 10 | NA | NA | NA | 46.7 | 56.7 | BAICR-109 | N | 1998-05-06 | 13:20 | 549.9167 | 3299.5 | 8.1 | 0.21 | 25.3 | BMRL | 2.2 | 0.041 | 1.8636 | 2.8 | 0.9 | 1.9 | 25.6 | 8 | 24 | 140 | 16 | 25 | 30 | 12 | 83 | BMRL | 6.4 | 4.5 | BMRL | 6 | 8.2 | NA | NA | NA | 16.9 | 25.1 | BAICR-209 | N | 1998-05-27 | 10:45 | 1051.5 | 3154.5 | 7.5 | 0.17 | 26 | BMRL | 1.7 | 0.029 | 1.7059 | 2.4 | 0.98 | 1.42 | 27 | 7.8 | 24 | BMRL | 5 | 14 | 28 | 16 | 63 | BMRL | 2.6 | 2.9 | 1.1 | 6.4 | 5.3 | NA | NA | NA | 13 | 18.3 | Fuel Oil Rate ($/gal)
|  |  |  | 60 | 0.25 |  |  |  | BAICR-IN10 | N | 1998-06-02 | 13:00 | 1198 | 3594 | 7188 | 8 | 0.32 | 78 | 29 | 111 | 91 | BMRL | 140 | 3.8 | 0.093 | 2.4474 | 5.5 | 0.85 | 4.65 | 29 | 7.9 | 24 | 360 | 68 | 44 | 26 | 3.6 | 141.6 | 5.6 | 30 | 17 | BMRL | 3.5 | 17 | NA | NA | NA | 56.1 | 73.1 | BAICR-1010 | N | 1998-05-11 | 14:00 | 670.5833 | 4023.5 | 7.9 | 0.11 | 24.6 | BMRL | 2.5 | 0.042 | 1.68 | 2.9 | 0.97 | 1.93 | 26 | 7.9 | 24 | 96 | 14 | 23 | 29 | 11 | 77 | BMRL | 6.2 | 4.5 | BMRL | 4.8 | 7.6 | NA | NA | NA | 15.5 | 23.1 | BAICR-2010 | N | 1998-06-02 | 13:20 | 1198.0833 | 3594.25 | 7.3 | 0.2 | 31 | BMRL | 1.9 | 0.032 | 1.6842 | 2.6 | 0.9 | 1.7 | 29 | 7.9 | 24 | 130 | 8.6 | 19 | 29 | 13 | 69.6 | BMRL | 4.5 | 4.2 | 1.1 | 6.1 | 7.5 | NA | NA | NA | 15.9 | 23.4 | Natural Gas Rate ($/ft3)
|  | General Pilot Design Parameters |  | 70 | 0.21 |  |  |  | BAICR-IN11 | N | 1998-06-11 | 13:00 | 1414 | 4242 | 8484 | 7.5 | 0.11 | 100 | 26.5 | 182 | 164 | BMRL | 130 | 3.2 | 0.076 | 2.375 | 4.5 | 1.25 | 3.25 | 28.3 | 7.8 | 24 | 270 | 39 | 27 | 16 | 3 | 85 | 6.1 | 20 | 15 | BMRL | 3.3 | 12 | NA | NA | NA | 44.4 | 56.4 | BAICR-1011 | N | 1998-05-13 | 10:30 | 715.0833 | 4290.5 | 7.9 | 0.14 | 25 | BMRL | 2.6 | 0.047 | 1.8077 | 3 | 1 | 2 | 25.1 | 7.9 | 24 | 150 | 18 | 27 | 31 | 11 | 87 | BMRL | 8.2 | 6.2 | 1 | 7.7 | 10 | NA | NA | NA | 23.1 | 33.1 | BAICR-2011 | N | 1998-06-11 | 13:45 | 1414.5 | 4243.5 | 7.1 | 0.11 | 27 | BMRL | 1.6 | 0.026 | 1.625 | 2.4 | 1.05 | 1.35 | 29 | 7.4 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Current Process Water Rate ($/1000 gal) | 0.1
Phone Number |  | Carbon particle diameter, d (mm) | 1.605 | 80 | 0.18 |  |  |  | BAICR-IN12 | Y | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | 130 | 2.9 | 0.0635 | 2.1897 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 | Y | 1998-05-18 | 15:50 | 840.4167 | 5042.5 | 7.9 | 0.16 | 27 | BMRL | 2.45 | 0.041 | 1.6735 | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 155 | 17.5 | 28 | 35.5 | 13.5 | 94.5 | BMRL | 6.1 | 5.3 | 1 | 6.25 | 8.85 | NA | NA | NA | 18.65 | 27.5 | BAICR-2012 | Y | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.3 | 0.019 | 1.4615 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Modifications to Existing Plant (% of construction costs) | 30
FAX Number |  | Column cross-sectional area, A (m2) | 0.0081073 | [5 empty] | BAICR-IN13 | N | 1998-06-25 | 13:00 | 1750 | 5250 | 10500 | 7 | 0.23 | 97 | 30.3 | 136 | 116 | BMRL | 140 | 3.2 | 0.061 | 1.9062 | 4.4 | 0.85 | 3.55 | 29.5 | 7.4 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1013 | N | 1998-05-21 | 11:50 | 908.4167 | 5450.5 | 7.8 | 0.16 | 27 | BMRL | 2.6 | 0.045 | 1.7308 | 3.5 | 1.05 | 2.45 | 26 | 7.9 | 24 | 180 | 18 | 24 | 28 | 8.8 | 78.8 | BMRL | 9.3 | 7.5 | 1.3 | 6.2 | 11 | NA | NA | NA | 24.3 | 35.3 | BAICR-2013 | N | 1998-06-25 | 13:40 | 1750.4167 | 5251.25 | 7.1 | 0.21 | 31.5 | BMRL | 1.6 | 0.024 | 1.5 | 2.5 | 0.91 | 1.59 | 30 | 7.4 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
E-Mail Address (optional) |  | Hydraulic loading rate1, v (m/hr) | 5.6023 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | BAICR-IN14 | N | 1998-07-07 | 15:00 | 2040 | 6120 | 12240 | 10.6 | 0.06 | 45 | 31.7 | 109 | 98 | BMRL | 130 | 2.8 | 0.05 | 1.7857 | 5 | 0.82 | 4.18 | 31.5 | 10.5 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1014 | N | 1998-05-26 | 11:30 | 1028.0833 | 6168.5 | 7.4 | 0.17 | 26 | BMRL | 2.8 | 0.057 | 2.0357 | 3.2 | 0.93 | 2.27 | 26 | 7.8 | 24 | NR | 19 | 27 | 31 | 10 | 87 | BMRL | 8.2 | 4.6 | 1.1 | 7.6 | 9.7 | NA | NA | NA | 21.5 | 31.2 | BAICR-2014 | N | 1998-07-07 | 15:30 | 2040.25 | 6120.75 | 9.2 | 0.05 | 32.5 | BMRL | NR | NR | #VALUE! | 4 | 0.75 | 3.25 | 31.5 | 8.8 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
|  | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | BAICR-IN15 | N | 1998-07-21 | 14:35 | 2375.5833 | 7126.75 | 14253.5 | 6 | 0.07 | 35 | 31.5 | 123 | 102 | BMRL | 160 | 2.2 | 0.033 | 1.5 | 4.3 | 1.2 | 3.1 | 31.5 | 6.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1015 | N | 1998-06-02 | 13:45 | 1198.3333 | 7190 | 7.5 | 0.24 | 30 | BMRL | 2.8 | 0.061 | 2.1786 | 3.8 | 0.82 | 2.98 | 29 | 7.8 | 24 | 220 | 28 | 32 | 30 | 6.9 | 96.9 | 2.9 | 14 | 10 | 1 | 5.7 | 13 | NA | NA | NA | 33.6 | 46.6 | BAICR-2015 | N | 1998-07-21 | 15:10 | 2375.9167 | 7127.75 | 6.3 | 0.06 | 32.5 | BMRL | NR | NR | #VALUE! | 2.6 | 1 | 1.6 | 31.5 | 6.5 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
Plant Name | Bachman Water Treatment Plant |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | BAICR-IN16 | N | 1998-08-04 | 10:30 | 2707.5 | 8122.5 | 16245 | 6 | 0.09 | 38 | 31 | 118 | 96 | BMRL | 140 | 2.1 | 0.031 | 1.4762 | 4 | 0.79 | 3.21 | 29 | 7.8 | 24 | 140 | 19 | 24 | 23 | 7.3 | 73.3 | 3.6 | 12 | 10 | BMRL | 1.5 | 7.2 | NA | NA | NA | 27.1 | 34.3 | BAICR-1016 | N | 1998-06-23 | 11:40 | 1700.25 | 10201.5 | 7.2 | 0.16 | 30 | BMRL | NR | NR | NR | 4.2 | 1.2 | 3 | 29 | 7.3 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-2016 | N | 1998-08-04 | 11:15 | 2708 | 8124 | 6.4 | 0.1 | 32 | BMRL | 0.79 | 0.01 | 1.2658 | 2.4 | 0.9 | 1.5 | 29 | 8.3 | 24 | BMRL | 2.5 | 7.7 | 18 | 14 | 42.2 | 3.6 | NR | NR | BMRL | 3.4 | 2.5 | NA | NA | NA | NR | NR
Treatment Plant Category | TS/SOFT | 10-Minute EBCT Run | [6 empty] | BAICR-IN17 | N | 1998-08-18 | 14:30 | 3047.5 | 9142.5 | 18285 | 6.3 | 0.1 | 57 | 30 | 118 | 98 | BMRL | 140 | 2.1 | 0.04 | 1.9048 | 4.1 | 0.63 | 3.47 | 30 | 8 | 24 | NR | 23 | 25 | 23 | 8 | 79 | 3.4 | 7.3 | 4.3 | BMRL | 5.5 | 7.5 | NA | NA | NA | 20.5 | 28 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [35 empty] | BAICR-2017 | N | 1998-08-18 | 15:20 | 3048.0833 | 9144.25 | 6.5 | 0.15 | 31 | BMRL | 1.1 | 0.015 | 1.3636 | 2.2 | 0.61 | 1.59 | 31 | 8 | 24 | NR | 2.5 | 8.6 | 20 | 17 | 48.1 | 3.8 | 1.4 | 1.7 | BMRL | 4.8 | 2.7 | NA | NA | NA | 11.7 | 14.4
Process Train Name | Two-stage softening | Empty bed contact time, EBCT (min) | 10 | [5 empty] | BAICR-IN18 | N | 1998-09-01 | 12:45 | 3381.75 | 10145.25 | 20290.5 | 6.3 | 0.08 | 51 | 30 | 112 | 90 | BMRL | 130 | 2.3 | 0.04 | 1.7391 | 4.5 | 0.81 | 3.69 | 30 | 8.1 | 24 | 150 | 21 | 24 | 22 | 8.4 | 75.4 | BMRL | 6.7 | 3.6 | BMRL | 4.5 | 6.3 | NA | NA | NA | 14.8 | 21.1 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [35 empty] | BAICR-2018 | N | 1998-09-01 | 13:40 | 3382.4167 | 10147.25 | 6.6 | 0.12 | 31 | BMRL | 1.3 | 0.015 | 1.1538 | 2.6 | 0.77 | 1.83 | 30 | 8.3 | 24 | 60 | 2.4 | 9.8 | 19 | 15 | 46.2 | BMRL | 1.8 | 1.3 | BMRL | 5.3 | 3.1 | NA | NA | NA | 8.4 | 11.5
ICR Treatment Plant Identification Number | 620 | Estimated run time, t (days) | 40.3088 | [5 empty] | BAICR-IN19 | N | 1998-09-15 | 13:05 | 3718.0833 | 11154.25 | 22308.5 | 6.5 | 0.1 | 51 | 26 | 113 | 93 | BMRL | 160 | 2.2 | 0.04 | 1.8182 | 4 | 0.86 | 3.14 | 26 | 8 | 24 | 170 | 21 | 25 | 23 | 8.3 | 77.3 | 2.1 | 5.6 | 4.5 | BMRL | 5.2 | 7.2 | NA | NA | NA | 17.4 | 24.6 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | BAICR-2019 | N | 1998-09-15 | 13:45 | 3718.5 | 11155.5 | 6.6 | 0.11 | 27 | BMRL | 1.6 | 0.02 | 1.25 | 2.4 | 0.87 | 1.53 | 26 | 8.1 | 24 | 73 | 3.2 | 10 | 19 | 13 | 45.2 | NR | 1.3 | 1.4 | BMRL | 5.1 | 3.2 | NA | NA | NA | NR | NR
PWSID Number of Plant (if assigned) | TX0570004 | Pilot column bed length, l (m) | 0.93372 | [5 empty] | BAICR-IN20 | N | 1998-09-29 | 10:45 | 4051.75 | 12155.25 | 24310.5 | 6.5 | 0.11 | 54 | 29 | 108 | 87 | BMRL | 150 | 2.7 | 0.05 | 1.8519 | 4.1 | 0.68 | 3.42 | 28 | 8 | 24 | 180 | 16 | NR | 19 | 7.3 | NR | 2.4 | 8.5 | 6.4 | BMRL | 8.7 | 10 | NA | NA | NA | 26 | 36 | [36 empty] | BAICR-2020 | N | 1998-09-29 | 11:25 | 4052.1667 | 12156.5 | 6.6 | 0.13 | 30 | BMRL | 1.9 | 0.021 | 1.1053 | 2.6 | 0.65 | 1.95 | 29 | 8.2 | 24 | 88 | 4.3 | 12 | 21 | 15 | 52.3 | 3.5 | 2.6 | 2.7 | BMRL | 8.7 | 5 | NA | NA | NA | 17.5 | 22.5
Historical Minimum Water Temperature (oC) | 5 | Mass GAC required, m (kg) | 4.1567 | [5 empty] | BAICR-IN21 | N | 1998-10-13 | 13:50 | 4390.8333 | 13172.5 | 26345 | 6.9 | 0.09 | 69 | 24 | 121 | 103 | BMRL | 140 | 2.9 | 0.052 | 1.7931 | 3.9 | 0.79 | 3.11 | 23 | 8.1 | 24 | 200 | 17 | 16 | 13 | 3.7 | 49.7 | 3 | 9.2 | 6.4 | BMRL | 4.9 | 8.8 | NA | NA | NA | 23.5 | 32.3 | [36 empty] | BAICR-2021 | N | 1998-10-13 | 14:55 | 4391.6667 | 13175 | 7.1 | 0.09 | 25 | 0.15 | 1.9 | 0.027 | 1.4211 | 2.7 | 0.78 | 1.92 | 24 | 8.1 | 24 | 92 | 6 | 11 | 14 | 7.2 | 38.2 | BMRL | 3.3 | 2.6 | BMRL | 6.2 | 5.3 | NA | NA | NA | 12.1 | 17.4
Historical Average Water Temperature (oC) | 20 | [7 empty] | BAICR-IN22 | N | 1998-10-27 | 14:00 | 4727 | 14181 | 28362 | 6.8 | 0.1 | 69 | 23 | 129 | 109 | BMRL | 95 | 3.1 | 0.052 | 1.6774 | 4 | 0.85 | 3.15 | 22 | 8.3 | 24 | 190 | 20 | 20 | 18 | 5.5 | 63.5 | 3.8 | 9.4 | 5.7 | BMRL | 5.3 | 9 | NA | NA | NA | 24.2 | 33.2 | [36 empty] | BAICR-2022 | N | 1998-10-27 | 14:35 | 4727.3333 | 14182 | 6.9 | 0.09 | 23 | BMRL | 2.3 | 0.03 | 1.3043 | 3 | 1.11 | 1.89 | 22 | 8.2 | 24 | 120 | 8.1 | 13 | 17 | 8.7 | 46.8 | 3.1 | 3.7 | 3 | BMRL | 5.6 | 5.9 | NA | NA | NA | 15.4 | 21.3
State Approved Plant Capacity (MGD) | 115 | 20-Minute EBCT Run | [6 empty] | BAICR-IN23 | N | 1998-11-10 | 13:10 | 5062.1667 | 15186.5 | 30373 | 6.7 | 0.1 | 51 | 18 | 119 | 101 | 0.11 | 130 | NR | 0.034 | #VALUE! | 3.6 | 1.05 | 2.55 | 18 | 8 | 24 | 130 | 7.4 | 12 | 13 | 5.1 | 37.5 | 2.3 | 5.1 | 4.6 | BMRL | 4 | 5.6 | NA | NA | NA | 16 | 21.6 | [36 empty] | BAICR-2023 | N | 1998-11-10 | 13:55 | 5062.6667 | 15188 | 6.8 | 0.1 | 18 | BMRL | NR | 0.018 | #VALUE! | 2.4 | 1.08 | 1.32 | 18 | 8 | 24 | 80 | 2.5 | 6.3 | 9.5 | 5.3 | 23.6 | BMRL | 1.9 | 2.5 | BMRL | 3.3 | 3.5 | NA | NA | NA | 7.7 | 11.2
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | BAICR-IN24 | N | 1998-12-16 | 19:15 | 5803.25 | 17409.75 | 34819.5 | 8.3 | 0.18 | 37 | 17.1 | 100 | 84 | BMRL | 97 | 2.9 | 0.077 | 2.6552 | 3.5 | 1.21 | 2.29 | 17.2 | 8.3 | 24 | 260 | 26 | 18 | 9 | 1.5 | 54.5 | 2.1 | 12 | 14 | BMRL | 1.7 | 7.1 | NA | NA | NA | 29.8 | 36.9 | [36 empty] | BAICR-2024 | N | 1998-12-15 | 19:15 | 5779 | 17337 | 7.4 | 0.13 | 19 | BMRL | 2.6 | 0.05 | 1.9231 | 2.5 | 1.14 | 1.36 | 19 | 8.2 | 24 | 130 | 12 | 14 | 11 | 2.3 | 39.3 | BMRL | 5.6 | 5.4 | BMRL | 2.5 | 5.8 | NA | NA | NA | 13.5 | 19.3
|  | Estimated run time, t (days) | 80.6176 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [76 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Pilot column bed length, l (m) | 1.8674 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [76 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  | Mass GAC required, m (kg) | 8.3134 | [5 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [76 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | BAICR-IN3 | Primary | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | BMRL | 110 | 3.7 | NR | #VALUE! | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 62 | 37 | 20 | 2.6 | 121.6 | 3.6 | 20 | 9.1 | BMRL | 2.9 | 12 | NA | NA | NA | 35.6 | 47.6 | BAICR-103 | Primary | 1998-04-20 | 16:00 | 168.5833 | 1011.5 | 8.6 | 0.22 | 21.3 | BMRL | 1.4 | 0.03 | 2.1429 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 6.6 | 13 | 22 | 15 | 56.6 | BMRL | 2.4 | 1.4 | BMRL | 5 | 3.4 | NA | NA | NA | 8.8 | 12.2 | BAICR-203 | Primary | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | BMRL | 0.62 | NR | #VALUE! | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | 1 | 2 | 7 | 9.3 | 19.3 | BMRL | BMRL | BMRL | BMRL | 2 | BMRL | NA | NA | NA | 2 | 2
[9 empty] | BAICR-IN3 D | Duplicate | 1998-04-27 | 12:45 | 333.75 | 1001.25 | 2002.5 | 8.5 | 0.19 | 51 | 21 | 79 | 61 | NA | 120 | 3.9 | 0.084 | 2.1538 | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 58 | 35 | 19 | 2.3 | 114.3 | 3.5 | 20 | 9.6 | BMRL | 3.4 | 13 | NA | NA | NA | 36.5 | 49.5 | BAICR-103 D | Duplicate | 1998-04-20 | 16:00 | 168.5833 | 1011.5 | 8.6 | 0.22 | 21.3 | BMRL | 1.6 | 0.03 | 1.875 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | BMRL | 5.6 | 11 | 20 | 14 | 50.6 | BMRL | 2.4 | 1.5 | BMRL | 5.1 | 3.5 | NA | NA | NA | 9 | 12.5 | BAICR-203 D | Duplicate | 1998-04-27 | 13:00 | 333.75 | 1001.25 | 7.8 | 0.55 | 21.8 | NA | 0.61 | 0.01 | 1.6393 | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | BMRL | BMRL | 1.6 | 6 | 8.6 | 16.2 | BMRL | BMRL | BMRL | BMRL | NR | BMRL | NA | NA | NA | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 8.5 | 0.19 | 51 | 21 | 79 | 61 | #DIV/0! | 115 | 3.8 | 0.084 | #VALUE! | 4.2 | 0.9 | 3.3 | 19.9 | 8.7 | 24 | 270 | 60 | 36 | 19.5 | 2.45 | 117.95 | 3.55 | 20 | 9.35 | #DIV/0! | 3.15 | 12.5 | #DIV/0! | #DIV/0! | #DIV/0! | 36.05 | 48.55 |  | Average | --- | --- | --- | --- | 8.6 | 0.22 | 21.3 | #DIV/0! | 1.5 | 0.03 | 2.0089 | 1.5 | 0.6 | 0.9 | 20 | 8.7 | 24 | #DIV/0! | 6.1 | 12 | 21 | 14.5 | 53.6 | #DIV/0! | 2.4 | 1.45 | #DIV/0! | 5.05 | 3.45 | #DIV/0! | #DIV/0! | #DIV/0! | 8.9 | 12.35 |  | Average | --- | --- | --- | --- | 7.8 | 0.55 | 21.8 | #DIV/0! | 0.615 | 0.01 | #VALUE! | 1.5 | 0.75 | 0.75 | 19.8 | 7.9 | 24 | #DIV/0! | 1 | 1.8 | 6.5 | 8.95 | 17.75 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 2 | 2
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 8.6957 | 5.2632 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6667 | 5.5556 | 5.1282 | 12.2449 | 6.1891 | 2.8169 | 0 | 5.3476 | #VALUE! | 15.873 | 8 | #VALUE! | #VALUE! | #VALUE! | 2.4965 | 3.9135 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 13.3333 | 0 | 13.3333 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 16.3934 | 16.6667 | 9.5238 | 6.8966 | 11.194 | #VALUE! | 0 | 6.8966 | #VALUE! | 1.9802 | 2.8986 | #VALUE! | #VALUE! | #VALUE! | 2.2472 | 2.4291 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 1.626 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 22.2222 | 15.3846 | 7.8212 | 17.4648 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | BAICR-IN7 | Primary | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.7 | 0.076 | 2.0541 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 290 | 56 | 46 | 33 | 6.6 | 141.6 | 3.5 | 18 | 13 | BMRL | 4.8 | 15 | NA | NA | NA | 39.3 | 54.3 | BAICR-107 | Primary | 1998-04-30 | 11:55 | 404.5 | 2427 | 8.5 | 0.19 | 20.6 | BMRL | 2.1 | 0.041 | 1.9524 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 17 | 23 | 25 | 8.1 | 73.1 | BMRL | 5.7 | 3.9 | BMRL | 5.8 | 7.7 | NA | NA | NA | 15.4 | 23.1 | BAICR-207 | Primary | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.5 | 0.019 | 1.2667 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 71 | 2.7 | 9.2 | 22 | 16 | 49.9 | BMRL | 1.7 | 2.3 | BMRL | 5.2 | 3.9 | NA | NA | NA | 9.2 | 13.1
[9 empty] | BAICR-IN7 D | Duplicate | 1998-05-18 | 14:45 | 839.75 | 2519.25 | 5038.5 | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | BMRL | 160 | 3.9 | 0.078 | 2 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 300 | 54 | 46 | 33 | 6.8 | 139.8 | NR | 18 | 13 | 1 | 4.5 | 15 | NA | NA | NA | NR | NR | BAICR-107 D | Duplicate | 1998-04-30 | 11:55 | 404.5 | 2427 | 8.5 | 0.19 | 20.6 | BMRL | 2.2 | 0.042 | 1.9091 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16 | 22 | 25 | 7.9 | 70.9 | BMRL | 6.1 | 3.8 | BMRL | 5.4 | 7.4 | NA | NA | NA | 15.3 | 22.7 | BAICR-207 D | Duplicate | 1998-05-18 | 15:30 | 840.25 | 2520.75 | 7.5 | 0.09 | 28.5 | BMRL | 1.4 | 0.02 | 1.4286 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 66 | 3 | 10 | 24 | 18 | 55 | BMRL | 1.7 | 2.4 | BMRL | 5.8 | 4 | NA | NA | NA | 9.9 | 13.9
[10 empty] | Average | --- | --- | --- | --- | --- | 7.9 | 0.18 | 80 | 26.8 | 130 | 106 | #DIV/0! | 160 | 3.8 | 0.077 | 2.027 | 4.7 | 0.78 | 3.92 | 29 | 8 | 24 | 295 | 55 | 46 | 33 | 6.7 | 140.7 | 3.5 | 18 | 13 | 1 | 4.65 | 15 | #DIV/0! | #DIV/0! | #DIV/0! | 39.3 | 54.3 |  | Average | --- | --- | --- | --- | 8.5 | 0.19 | 20.6 | #DIV/0! | 2.15 | 0.0415 | 1.9307 | 2.6 | 0.95 | 1.65 | 22 | 8.4 | 24 | 120 | 16.5 | 22.5 | 25 | 8 | 72 | #DIV/0! | 5.9 | 3.85 | #DIV/0! | 5.6 | 7.55 | #DIV/0! | #DIV/0! | #DIV/0! | 15.35 | 22.9 |  | Average | --- | --- | --- | --- | 7.5 | 0.09 | 28.5 | #DIV/0! | 1.45 | 0.0195 | 1.3476 | 2.3 | 1.05 | 1.25 | 29 | 7.8 | 24 | 68.5 | 2.85 | 9.6 | 23 | 17 | 52.45 | #DIV/0! | 1.7 | 2.35 | #DIV/0! | 5.5 | 3.95 | #DIV/0! | #DIV/0! | #DIV/0! | 9.55 | 13.5
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 5.2632 | 2.5974 | 2.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3898 | 3.6364 | 0 | 0 | 2.9851 | 1.2793 | #VALUE! | 0 | 0 | #VALUE! | 6.4516 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 4.6512 | 2.4096 | 2.2422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0606 | 4.4444 | 0 | 2.5 | 3.0556 | #VALUE! | 6.7797 | 2.5974 | #VALUE! | 7.1429 | 3.9735 | #VALUE! | #VALUE! | #VALUE! | 0.65147 | 1.7467 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 6.8966 | 5.1282 | 12.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2993 | 10.5263 | 8.3333 | 8.6957 | 11.7647 | 9.7235 | #VALUE! | 0 | 4.2553 | #VALUE! | 10.9091 | 2.5316 | #VALUE! | #VALUE! | #VALUE! | 7.3298 | 5.9259
[9 empty] | BAICR-IN12 | Primary | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | NA | 2.9 | 0.061 | 2.1034 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 | Primary | 1998-05-18 | 15:50 | 840.4167 | 5042.5 | 7.9 | 0.16 | 27 | BMRL | 2.5 | BMRL | #VALUE! | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 150 | 17 | 28 | 35 | 13 | 93 | NR | 6 | 5.2 | BMRL | 6.4 | 8.8 | NA | NA | NA | NR | NR | BAICR-2012 | Primary | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.4 | 0.02 | 1.4286 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[9 empty] | BAICR-IN12 D | Duplicate | 1998-06-18 | 12:35 | 1581.5833 | 4744.75 | 9489.5 | 6.8 | 0.23 | 90 | 29 | 144 | 120 | BMRL | 130 | 2.9 | 0.066 | 2.2759 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | BAICR-1012 D | Duplicate | 1998-05-18 | 15:50 | 840.4167 | 5042.5 | 7.9 | 0.16 | 27 | BMRL | 2.4 | 0.041 | 1.7083 | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 160 | 18 | 28 | 36 | 14 | 96 | BMRL | 6.2 | 5.4 | 1 | 6.1 | 8.9 | NA | NA | NA | 18.7 | 27.6 | BAICR-2012 D | Duplicate | 1998-06-18 | 13:25 | 1582.1667 | 4746.5 | 6.8 | 0.14 | 30 | BMRL | 1.2 | 0.018 | 1.5 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[10 empty] | Average | --- | --- | --- | --- | --- | 6.8 | 0.23 | 90 | 29 | 144 | 120 | #DIV/0! | 130 | 2.9 | 0.0635 | 2.1897 | 4.4 | 0.97 | 3.43 | 29 | 7 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | Average | --- | --- | --- | --- | 7.9 | 0.16 | 27 | #DIV/0! | 2.45 | 0.041 | #VALUE! | 3.2 | 0.88 | 2.32 | 29 | 7.9 | 24 | 155 | 17.5 | 28 | 35.5 | 13.5 | 94.5 | #DIV/0! | 6.1 | 5.3 | 1 | 6.25 | 8.85 | #DIV/0! | #DIV/0! | #DIV/0! | 18.7 | 27.6 |  | Average | --- | --- | --- | --- | 6.8 | 0.14 | 30 | #DIV/0! | 1.3 | 0.019 | 1.4643 | 2.4 | 0.81 | 1.59 | 29.5 | 7.2 | 24 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 0 | 7.874 | 7.874 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 4.0816 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 6.4516 | 5.7143 | 0 | 2.8169 | 7.4074 | 3.1746 | #VALUE! | 3.2787 | 3.7736 | #VALUE! | 4.8 | 1.1299 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 15.3846 | 10.5263 | 4.878 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on A1: Reviewer M.H. (2/2/00): 2. The data in the Data Collection Spreadsheets have been separated to differentiate between the two halves of the run (in terms of pretreatment). The "first" run (up to 51 days of operation) utilized chemical pretreatment doses similar to the full-scale plant. The weighted average ferric sulfate dose was 20 mg/L (range: 10 to 30 mg/L). The weighted average calcium hydroxide dose was 52 mg/L (range: 40 to 60 mg/L). During the "second" run (changing pretreatment conditions which affected the second half of the 20 minute EBCT run, after 51 days of operation), the average ferric sulfate dose was 39 mg/L (range: 20 to 100 mg/L) and the average calcium hydroxide dose was 11 mg/L (range: 0 to 120 mg/L). The original data has been included as a third sheet for reference, but should not be used for further data analysis. It should be noted when interpreting the results of the second half of the run in terms of pretreatment, that the first half of the run was conducted under conventional coagulant doses (similar to the full-scale plant). The GAC influent data collected during the entire run has been included with the GAC effluent data from the second half of the run.
Note on K6: Reviewer M.H. (1/10/00): Reviewer changed results by calculating a weighted average of the dosages as reported in Table 4-1 in the summary report, per consultant's request.
Note on K7: Reviewer M.H. (1/10/00): Reviewer changed results by calculating a weighted average of the dosages as reported in Table 4-1 in the summary report, per consultant's request.
Note on U23: Reviewer M.H. (11/13/99): According to summary report, lime dosage was terminated after day 70, as a result the pH decreased.
Note on AA31: Reviewer M.H. (11/13/99): Per Utility: "We believe the Ammonia spike in the influent water to be valid. The MRL for ammonia is 0.10mg/L. Thus, a value of 0.11mg/L is not much of a spike. Additionally, the source water experiences spikes in ammonia from time to time."