## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Topeka | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 2.8 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-02-12 | [12 empty] | 20-min. EBCT Start Date | 1998-02-12 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | KS2017701 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 8 | mesh size | (mm) | Rapid mix | 8 mg/L polymer | Full-Scale | 10-min. EBCT Start Time | 15:00 | [12 empty] | 20-min. EBCT Start Time | 15:00 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.3056 | 4 | 4.75 | Primary presedimentation | 382 minutes | Full-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 10
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 4 | 6 | 3.35 | Polymer addition | 2 mg/L polymer | Full-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-02-13 | 00:16 | 9.2667 | 698.892 | 9.19 | 20.3 | 0.31 | 0.0025 | 0.80645 | 2.13 | 0.79 | 1.34 | 3.6 | 9.1747 | 47.7 | 4.8 | BMRL | 1.2706 | BMRL | 2.38 | 3.6506 | BMRL | BMRL | BMRL | BMRL | 1.0298 | BMRL | BMRL | BMRL | BMRL | 1.0298 | 1.0298 | C1-20 | N | 1998-02-12 | 15:59 | 0.98333 | 74.163 | 9.33 | 20.1 | 0.3 | 0.00205 | 0.68333 | 2.21 | 0.85 | 1.36 | 3.6 | 9.2343 | 48 | 2.25 | BMRL | BMRL | BMRL | 1.42 | 1.42 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Secondary presedimentation | 220 minutes | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-02-13 | 11:16 | 20.2667 | 1528.512 | 8.8 | 20.8 | 0.53 | 0.0051 | 0.96226 | 2.3 | 0.85 | 1.45 | 3.6 | 9.1595 | 47.7 | 14.45 | BMRL | 4.0427 | 1.5981 | 5.37 | 11.0108 | BMRL | 1.5212 | BMRL | BMRL | 1.7022 | 1.0859 | BMRL | BMRL | BMRL | 3.2233 | 4.3093 | C2-20 | N | 1998-02-14 | 14:54 | 47.9 | 3612.618 | 8.65 | 22.5 | 0.52 | 0.00615 | 1.1827 | 2.3 | 0.89 | 1.41 | 3.6 | 9.1895 | 48 | 19.8 | BMRL | 5.4987 | 1.9207 | 6.73 | 14.1494 | BMRL | 1.8913 | BMRL | BMRL | 1.9616 | 1.2637 | BMRL | BMRL | BMRL | 3.8529 | 5.1166 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.524 | 10 | 2 | Softening | 130 mg/L lime; 8.6 mg/L alum | Full-Scale | Sampling date | MM/DD/YY | 1998-02-12 | 1998-02-23 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-02-12 | 1998-02-23 | [7 empty] | --- | --- |  | C3-10 | N | 1998-02-13 | 16:19 | 25.3167 | 1909.383 | 8.91 | 22.3 | 0.75 | 0.0077 | 1.0267 | 2.39 | 0.86 | 1.53 | 3.6 | 9.2495 | 47.8 | 25.1 | 1.39 | 7.0199 | 3.1222 | 7.36 | 18.8922 | BMRL | 4.191 | BMRL | BMRL | 2.3485 | 1.6001 | BMRL | BMRL | BMRL | 6.5395 | 8.1395 | C3-20 | N | 1998-02-15 | 01:24 | 58.4 | 4404.528 | 8.63 | 21 | 0.71 | 0.0074 | 1.0423 | 2.37 | 0.88 | 1.49 | 3.6 | 9.2395 | 48 | 29.8 | 1.38 | 7.6429 | 3.1086 | 8.07 | 20.2015 | BMRL | 6.0053 | BMRL | BMRL | 2.5706 | 1.6659 | BMRL | BMRL | BMRL | 8.5759 | 10.2419 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 140 | 12 | 1.68 | Primary sedimentation | 439 minutes | Full-Scale | Sampling time | hh:mm | 18:40 | 11:10 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 18:40 | 11:10 | [7 empty] | --- | --- |  | C4-10 | N | 1998-02-13 | 19:54 | 28.9 | 2179.638 | 8.99 | 21.4 | 0.845 | 0.0099 | 1.1716 | 2.43 | 0.85 | 1.58 | 3.6 | 9.2647 | 47.8 | 32.05 | 2.3 | 9.4032 | 4.7106 | 8.82 | 25.2337 | BMRL | 5.6684 | BMRL | BMRL | 2.8791 | 2.0862 | BMRL | BMRL | 1.1456 | 8.5476 | 10.6337 | Avg-C4-20 | Y | 1998-02-15 | 15:25 | 72.4167 | 5461.665 | 8.745 | 22.5 | 0.895 | 0.01165 | 1.3017 | 2.45 | 0.845 | 1.605 | 3.6 | 9.1721 | 48.05 | 39.425 | 2.035 | 11.0319 | 4.9222 | 9.485 | 27.4741 | BMRL | 5.8053 | BMRL | 1.0045 | 3.0374 | 2.517 | BMRL | BMRL | 1.2022 | 9.8472 | 12.3642 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 230 | 16 | 1.18 | Chemical addition | 28 mg/L soda ash | Full-Scale | Operation time | hh.hh | 3.6667 | 260.1667 | [7 empty] | --- | --- |  | Operation time | hh.hh | 3.6667 | 260.1667 | [7 empty] | --- | --- |  | Avg-C5-10 | Y | 1998-02-14 | 03:00 | 36 | 2715.12 | 7.305 | 20.75 | 1.105 | 0.0137 | 1.2398 | 2.535 | 0.8 | 1.735 | 3.6 | 9.2043 | 47.8 | 48.4 | 3.785 | 13.5291 | 7.9239 | 10.075 | 35.313 | BMRL | 5.4781 | 1.0038 | 1.168 | 3.3051 | 3.06 | BMRL | BMRL | 1.363 | 10.955 | 14.015 | C5-20 | N | 1998-02-16 | 05:18 | 86.3 | 6508.746 | 8.81 | 21.3 | 1.045 | 0.01375 | 1.3158 | 2.51 | 0.83 | 1.68 | 3.6 | 9.195 | 48.1 | 48.25 | 2.92 | 13.559 | 6.8589 | 9.91 | 33.2479 | BMRL | 5.1217 | BMRL | 1.0464 | 3.1519 | 3.0761 | BMRL | BMRL | 1.2532 | 9.32 | 12.396 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 | Secondary sedimentation | 189 minutes | Full-Scale | Bed volumes | (10 minutes) | 276.54 | 19621.77 | [7 empty] | --- | --- |  | Bed volumes | (10 minutes) | 138.27 | 9810.885 | [7 empty] | --- | --- |  | C6-10 | N | 1998-02-14 | 10:06 | 43.1 | 3250.602 | 8.69 | 21.2 | 1.35 | 0.0174 | 1.2889 | 2.63 | 0.83 | 1.8 | 3.6 | 9.249 | 47.8 | 75.05 | 5.705 | 16.2094 | 10.8642 | 10.075 | 42.8536 | BMRL | 6.1435 | 1.2243 | BMRL | 3.6881 | 3.8471 | BMRL | BMRL | 1.4547 | 11.0559 | 14.9031 | C6-20 | N | 1998-02-16 | 20:57 | 101.95 | 7689.069 | 8.84 | 22 | 1.2 | 0.01755 | 1.4625 | 2.55 | 0.94 | 1.61 | 3.2 | 9.2047 | 48 | 53.75 | 4.14 | 15.5468 | 9.2657 | 10.3 | 39.2525 | BMRL | 5.3139 | 1.1821 | BMRL | 3.7356 | 3.5048 | BMRL | BMRL | 1.4582 | 10.2315 | 13.7363 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Alkalinity | mg/L as CaCO3 | 40.9 | 45.75 | [7 empty] | 43.325 | 7.9157 |  | Alkalinity | mg/L as CaCO3 | 40.9 | 45.75 | [7 empty] | 43.325 | 7.9157 |  | C7-10 | N | 1998-02-14 | 22:04 | 55.0667 | 4153.128 | 7.28 | 20.8 | 1.485 | 0.0213 | 1.4343 | 2.69 | 0.77 | 1.92 | 3.6 | 9.2443 | 47.9 | 80.6 | 7.4 | 18.9671 | 14.02 | 9.49 | 49.8771 | BMRL | 6.2698 | 2.539 | 1.0721 | 4.2607 | 4.4688 | BMRL | BMRL | 1.8899 | 14.1417 | 18.6105 | Avg-C7-20 | Y | 1998-02-17 | 16:00 | 121 | 9125.82 | 8.855 | 23.15 | 1.305 | 0.0211 | 1.6169 | 2.6 | 0.89 | 1.71 | 3.2 | 9.1947 | 48.05 | 70.8 | 5.845 | 18.4224 | 12.0659 | 9.91 | 46.2432 | BMRL | 5.6423 | 2.7917 | 1.0428 | 3.9424 | 3.7929 | BMRL | BMRL | 1.6249 | 13.4192 | 17.2121 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 5690.5508 | 40 | 0.425 | pH adjustment | 29 mg/L sulfuric acid (from pH 10.4 to 9.2) | Bench-Scale | Total hardness | mg/L as CaCO3 | 80.8 | 85.05 | [7 empty] | 82.925 | 3.624 |  | Total hardness | mg/L as CaCO3 | 80.8 | 85.05 | [7 empty] | 82.925 | 3.624 |  | Avg-C8-10 | Y | 1998-02-15 | 08:30 | 65.5 | 4940.01 | 8.02 | 21.3 | 1.6475 | 0.0245 | 1.4871 | 2.755 | 0.79 | 1.965 | 3.6 | 9.2395 | 47.9 | 97.15 | 10.37 | 21.5611 | 17.6947 | 9.115 | 58.7408 | BMRL | 6.2119 | 3.1891 | BMRL | 4.1024 | 4.5114 | BMRL | BMRL | 1.9646 | 13.5034 | 18.0148 | C8-20 | N | 1998-02-18 | 12:58 | 141.9667 | 10707.126 | 8.85 | 22 | 1.51 | 0.0231 | 1.5298 | 2.7 | 0.91 | 1.79 | 3.2 | 9.185 | 48.1 | 76.5 | 7.21 | 19.3824 | 13.7952 | 9.64 | 50.0276 | BMRL | 5.6308 | 4.1756 | 1.0159 | 3.8279 | 3.8532 | BMRL | BMRL | 1.8316 | 14.6503 | 18.5035 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 11381.1015 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 69.45 | 75 | [7 empty] | 72.225 | 5.4336 |  | Calcium hardness | mg/L as CaCO3 | 69.45 | 75 | [7 empty] | 72.225 | 5.4336 |  | C9-10 | N | 1998-02-16 | 01:15 | 82.25 | 6203.295 | 8.49 | 21 | 1.815 | 0.0286 | 1.5758 | 2.82 | 0.8 | 2.02 | 3.6 | 9.2443 | 48 | 105 | 11.36 | 18.9144 | 17.3629 | 6.48 | 54.1173 | BMRL | 7.4978 | 3.6705 | 1.0428 | 4.1677 | 5.1919 | BMRL | BMRL | 2.3142 | 16.3787 | 21.5707 | C9-20 | N | 1998-02-20 | 06:14 | 183.2333 | 13819.458 | 8.91 | 21.1 | 1.74 | 0.02705 | 1.5546 | 2.76 | 0.91 | 1.85 | 3 | 9.2295 | 48 | 84.5 | 10.5 | 20.829 | 17.76 | 8.01 | 57.099 | BMRL | 6.1401 | 4.0886 | BMRL | 4.2962 | 4.6645 | BMRL | 2.0668 | 2.4508 | 14.525 | 19.1895 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 14795.432 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.1 | 0.12 | [7 empty] | 0.11 | 12.8565 |  | Ammonia | mg NH3-N / L | 0.1 | 0.12 | [7 empty] | 0.11 | 12.8565 |  | Avg-C10-10 | Y | 1998-02-16 | 16:52 | 97.8667 | 7381.104 | 8.945 | 22.95 | 2.0275 | 0.0333 | 1.6424 | 2.935 | 0.88 | 2.055 | 3.2 | 9.1819 | 47.9 | 118.175 | 13.75 | 18.7154 | 19.1306 | 5.65 | 57.246 | BMRL | 7.9038 | 4.2836 | 1.0425 | 4.1043 | 5.4061 | BMRL | BMRL | 2.6378 | 17.3342 | 22.7403 | Avg-C10-20 | Y | 1998-02-21 | 19:33 | 220.55 | 16633.881 | 7.76 | 21.05 | 1.885 | 0.0309 | 1.6393 | 2.82 | 0.84 | 1.98 | 3 | 9.2049 | 48 | 97.875 | 13.375 | 21.722 | 20.2887 | 7.15 | 62.5357 | BMRL | 6.7896 | 4.4119 | 1.1023 | 4.9023 | 5.8032 | BMRL | 2.2778 | 2.952 | 17.2062 | 23.0093 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 86 | 81 | [7 empty] | 83.5 | 4.2342 |  | Bromide | mg/L | 86 | 81 | [7 empty] | 83.5 | 4.2342 |  | C11-10 | N | 1998-02-18 | 11:48 | 140.8 | 10619.136 | 8.95 | 21.8 | 2.175 | 0.0384 | 1.7655 | 3.01 | 0.87 | 2.14 | 3.2 | 9.2247 | 47.9 | 143.25 | 21.4 | 21.9524 | 25.1497 | 5.46 | 73.9621 | BMRL | 8.4771 | 3.9388 | BMRL | 3.6375 | 5.2864 | BMRL | BMRL | 2.7163 | 16.0533 | 21.3398 | C11-20 | N | 1998-02-23 | 18:35 | 267.5833 | 20181.135 | 8.48 | 21.3 | 2.105 | 0.03365 | 1.5986 | 2.89 | 0.76 | 2.13 | 3.3 | 9.19 | 48.1 | 109.85 | 15.4 | 20.8451 | 21.347 | 6.12 | 63.7121 | BMRL | 5.0656 | 4.0008 | BMRL | 4.1684 | 5.3429 | BMRL | 2.1357 | 2.91 | 13.2348 | 18.5777 | Natural Gas Rate ($/ft3) | 0.0058
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-02-19 | 06:43 | 159.7167 | 12045.831 | 8.87 | 21.3 | 2.36 | 0.04005 | 1.697 | 3.09 | 0.82 | 2.27 | 3.2 | 9.215 | 48 | 145.35 | 20.9 | 20.0767 | 23.6016 | 4.95 | 69.5283 | BMRL | 10.07 | 5.8881 | 1.2438 | 4.7446 | 7.0189 | BMRL | 2.5056 | 4.1645 | 21.9465 | 28.9653 | C12-20 | N | 1998-02-27 | 02:27 | 347.45 | 26204.679 | 9.01 | 21.5 | 2.275 | 0.03665 | 1.611 | 2.98 | 0.77 | 2.21 | 3.3 | 9.195 | 48.1 | 122.85 | 19.6 | 20.8783 | 24.1575 | 5.55 | 70.1858 | BMRL | 6.0552 | 4.5358 | 1.0565 | 3.7709 | 5.4302 | BMRL | 2.3251 | 3.3195 | 15.4184 | 20.8486 | Current Process Water Rate ($/1000 gal) | 0.43
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.5524e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-02-20 | 10:33 | 187.55 | 14145.021 | 9.14 | 21.1 | 2.48 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C13-20 | N | 1998-03-01 | 20:02 | 413.0333 | 31150.974 | 9.17 | 21.7 | 2.34 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.084 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | [34 empty] | C14-20 | N | 1998-03-03 | 07:58 | 448.9667 | 33861.066 | 8.9 | 21.6 | 2.34 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
|  |  |  | Scaling factor, SF | 12.57 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-02-12 | 1998-02-15 | 1998-02-17 | 1998-02-20 | 1998-02-24 | 1998-02-27 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-02-12 | 1998-02-15 | 1998-02-17 | 1998-02-20 | 1998-02-24 | 1998-02-27 |  |  |  |  | --- | ---
Plant Name | West End Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 9.1497 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 18:45 | 13:50 | 13:08 | 09:20 | 09:15 | 08:25 |  |  |  |  | --- | --- | Sampling time | hh:mm | 18:45 | 13:50 | 13:08 | 09:20 | 09:15 | 08:25 |  |  |  |  | --- | ---
Treatment Plant Category | TS/SOFT |  |  | RSSCT flow rate, QSC (mL/min) | 7.6652 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 3.75 | 70.8333 | 118.1333 | 186.3333 | 282.25 | 353.4167 |  |  |  |  | --- | --- | Operation time | hh.hh | 3.75 | 70.8333 | 118.1333 | 186.3333 | 282.25 | 353.4167 |  |  |  |  | --- | ---
Process Train Name | North/South Train |  |  | Estimated total influent volume required, VSCT (L) | 270.6681 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 282.825 | 5342.25 | 8909.616 | 14053.26 | 21287.295 | 26654.685 |  |  |  |  | --- | --- | Bed volumes | (10 minute) | 141.4125 | 2671.125 | 4454.808 | 7026.63 | 10643.6475 | 13327.3425 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 383 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 9.23 | 9.23 | 9.24 | 9.23 | 9.22 | 9.23 |  |  |  |  | 9.23 | 0.068522 | pH | --- | 9.23 | 9.23 | 9.24 | 9.23 | 9.22 | 9.23 |  |  |  |  | 9.23 | 0.068522 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.15 | NA | NA | 0.15 | NA | 0.15 |  |  |  |  | 0.15 | 0 | Turbidity | ntu | 0.15 | NA | NA | 0.15 | NA | 0.15 |  |  |  |  | 0.15 | 0 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 0.5 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 12.5 | 17.6 | 17.3 | 17.4 | 18.2 | 19.3 |  |  |  |  | 17.05 | 13.7736 | Temperature | oC | 12.5 | 17.6 | 17.3 | 17.4 | 18.2 | 19.3 |  |  |  |  | 17.05 | 13.7736
Historical Average Water Temperature (oC) | 17 |  |  | Estimated full-scale run time, tLCT (days) | 102.7461 | [5 empty] | Total organic carbon | mg/L | 3.255 | 3.17 | 3.085 | 3.135 | 3.25 | 3.165 |  |  |  |  | 3.1767 | 2.0802 | Total organic carbon | mg/L | 3.255 | 3.17 | 3.085 | 3.135 | 3.25 | 3.165 |  |  |  |  | 3.1767 | 2.0802 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.79554 | [5 empty] | UV254 | cm-1 | 0.06005 | NA | NA | 0.0614 | NA | 0.0604 |  |  |  |  | 0.060617 | 1.1558 | UV254 | cm-1 | 0.06005 | NA | NA | 0.0614 | NA | 0.0604 |  |  |  |  | 0.060617 | 1.1558 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.1739 | [5 empty] | SUVA | L/(mg*m) | 1.8449 | NR | NR | 1.9585 | NR | 1.9084 |  |  |  |  | 1.9039 | 2.9922 | SUVA | L/(mg*m) | 1.8449 | NR | NR | 1.9585 | NR | 1.9084 |  |  |  |  | 1.9039 | 2.9922 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 12.1316 | [5 empty] | SDS-Cl2 dose | mg/L | 3.71 | NA | NA | 3.65 | NA | 3.55 |  |  |  |  | 3.6367 | 2.2226 | SDS-Cl2 dose | mg/L | 3.71 | NA | NA | 3.65 | NA | 3.55 |  |  |  |  | 3.6367 | 2.2226 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 90.2227 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.86 | NA | NA | 0.86 | NA | 0.76 |  |  |  |  | 0.82667 | 6.9841 | SDS-Free Cl2 residual | mg/L | 0.86 | NA | NA | 0.86 | NA | 0.76 |  |  |  |  | 0.82667 | 6.9841 | C5-10 | Primary | 1998-02-14 | 03:00 | 36 | 2715.12 | 7.09 | 20.7 | 1.115 | 0.01375 | 1.2332 | 2.54 | 0.81 | 1.73 | 3.6 | 9.2343 | 47.8 | 48.6 | 3.7 | 13.4899 | 7.7357 | 10.2 | 35.1256 | BMRL | 5.4661 | 1.0082 | 1.2582 | 3.4365 | 3.1281 | BMRL | BMRL | 1.4 | 11.169 | 14.2971 | C4-20 | Primary | 1998-02-15 | 15:25 | 72.4167 | 5461.665 | 8.8 | 22.5 | 0.89 | 0.0114 | 1.2809 | 2.45 | 0.84 | 1.61 | 3.6 | 9.1547 | 48 | 39.8 | 2.03 | 11.2018 | 4.9794 | 9.85 | 28.0612 | BMRL | 5.7488 | BMRL | 1.0045 | 2.8799 | 2.4417 | BMRL | BMRL | 1.2069 | 9.6332 | 12.0749
|  |  |  | Mass GAC required, mSC (g) | 3.1954 | [5 empty] | SDS-Cl2 demand | mg/L | 2.85 | NR | NR | 2.79 | NR | 2.79 |  |  |  |  | 2.81 | 1.2328 | SDS-Cl2 demand | mg/L | 2.85 | NR | NR | 2.79 | NR | 2.79 |  |  |  |  | 2.81 | 1.2328 | D-C5-10 | Duplicate | 1998-02-14 | 03:00 | 36 | 2715.12 | 7.52 | 20.8 | 1.095 | 0.01365 | 1.2466 | 2.53 | 0.79 | 1.74 | 3.6 | 9.1743 | 47.8 | 48.2 | 3.87 | 13.5682 | 8.1121 | 9.95 | 35.5004 | BMRL | 5.4902 | BMRL | 1.0778 | 3.1737 | 2.9919 | BMRL | BMRL | 1.3259 | 9.7417 | 12.7336 | D-C4-10 | Duplicate | 1998-02-15 | 15:25 | 72.4167 | 5461.665 | 8.69 | NR | 0.9 | 0.0119 | 1.3222 | 2.45 | 0.85 | 1.6 | 3.6 | 9.1895 | 48.1 | 39.05 | 2.04 | 10.8621 | 4.865 | 9.12 | 26.887 | BMRL | 5.8618 | BMRL | BMRL | 3.195 | 2.5922 | BMRL | BMRL | 1.1974 | 9.0567 | 11.649
[11 empty] | SDS-Chlorination temp. | oC | 3.6 | NA | NA | 3 | NA | 3.3 |  |  |  |  | 3.3 | 9.0909 | SDS-Chlorination temp. | oC | 3.6 | NA | NA | 3 | NA | 3.3 |  |  |  |  | 3.3 | 9.0909 | Avg-C5-10 | Average | --- | --- | --- | --- | 7.305 | 20.75 | 1.105 | 0.0137 | 1.2399 | 2.535 | 0.8 | 1.735 | 3.6 | 9.2043 | 47.8 | 48.4 | 3.785 | 13.5291 | 7.9239 | 10.075 | 35.313 | BMRL | 5.4781 | 1.0082 | 1.168 | 3.3051 | 3.06 | BMRL | BMRL | 1.363 | 10.4553 | 13.5154 | Avg-C4-20 | Average | --- | --- | --- | --- | 8.745 | 22.5 | 0.895 | 0.01165 | 1.3016 | 2.45 | 0.845 | 1.605 | 3.6 | 9.1721 | 48.05 | 39.425 | 2.035 | 11.0319 | 4.9222 | 9.485 | 27.4741 | BMRL | 5.8053 | BMRL | 1.0045 | 3.0374 | 2.517 | BMRL | BMRL | 1.2022 | 9.3449 | 11.8619
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9.185 | NA | NA | 9.3095 | NA | 9.24 |  |  |  |  | 9.2448 | 0.67524 | SDS-Chlorination pH | --- | 9.185 | NA | NA | 9.3095 | NA | 9.24 |  |  |  |  | 9.2448 | 0.67524 | RPD-C5-10 | RPD | --- | --- | --- | --- | 5.8864 | 0.48193 | 1.81 | 0.72993 | 1.0801 | 0.39448 | 2.5 | 0.57637 | 0 | 0.65187 | 0 | 0.82645 | 4.4914 | 0.57941 | 4.7506 | 2.4814 | 1.0614 |  | 0.44081 |  | 15.4499 | 7.9511 | 4.4514 |  |  | 5.4425 | 13.6518 | 11.5687 | RPD-C4-20 | RPD | --- | --- | --- | --- | 1.2579 |  | 1.1173 | 4.2918 | 3.1749 | 0 | 1.1834 | 0.62305 | 0 | 0.37939 | 0.20812 | 1.9023 | 0.4914 | 3.0796 | 2.3255 | 7.6964 | 4.2738 |  | 1.9465 |  |  | 10.374 | 5.9807 |  |  | 0.79245 | 6.1684 | 3.5905
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 48.1 | NA | NA | 48 | NA | 48.1 |  |  |  |  | 48.0667 | 0.12011 | SDS-Incubation time | hours | 48.1 | NA | NA | 48 | NA | 48.1 |  |  |  |  | 48.0667 | 0.12011 | C8-10 | Primary | 1998-02-15 | 08:30 | 65.5 | 4940.01 | 7.99 | 21.3 | 1.66 | 0.02455 | 1.4789 | 2.76 | 0.81 | 1.95 | 3.6 | 9.2595 | 47.9 | 91.9 | 11.2 | 22.8984 | 18.8849 | 9.67 | 62.6533 | BMRL | 5.7246 | 2.8216 | BMRL | 3.5971 | 4.036 | BMRL | BMRL | 1.7999 | 12.1433 | 16.1793 | C7-20 | Primary | 1998-02-17 | 16:00 | 121 | 9125.82 | 8.85 | 23.1 | 1.31 | 0.02115 | 1.6145 | 2.6 | 0.88 | 1.72 | 3.2 | 9.1999 | 48 | 71.4 | 6.05 | 18.6234 | 12.5163 | 10.2 | 47.3897 | BMRL | 5.4875 | 2.6252 | BMRL | 3.8861 | 3.7647 | BMRL | BMRL | 1.59 | 11.9989 | 15.7635
|  |  |  | Estimated full-scale run time, tLCT (days) | 205.4921 | [5 empty] | SDS-TOX | mg Cl- /L | 218.4 | NA | NA | 204.55 | NA | 201.65 |  |  |  |  | 208.2 | 4.2996 | SDS-TOX | mg Cl- /L | 218.4 | NA | NA | 204.55 | NA | 201.65 |  |  |  |  | 208.2 | 4.2996 | D-C8-10 | Duplicate | 1998-02-15 | 08:30 | 65.5 | 4940.01 | 8.05 | 21.3 | 1.635 | 0.02445 | 1.4954 | 2.75 | 0.77 | 1.98 | 3.6 | 9.2195 | 47.9 | 102.4 | 9.54 | 20.2238 | 16.5045 | 8.56 | 54.8283 | BMRL | 6.6991 | 3.5566 | BMRL | 4.6077 | 4.9868 | BMRL | BMRL | 2.1293 | 14.8635 | 19.8502 | D-C7-20 | Duplicate | 1998-02-17 | 16:00 | 121 | 9125.82 | 8.86 | 23.2 | 1.3 | 0.02105 | 1.6192 | 2.6 | 0.9 | 1.7 | 3.2 | 9.1895 | 48.1 | 70.2 | 5.64 | 18.2213 | 11.6154 | 9.62 | 45.0968 | BMRL | 5.7971 | 2.9581 | 1.0428 | 3.9986 | 3.8212 | BMRL | BMRL | 1.6597 | 13.7966 | 17.6178
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5911 | [5 empty] | SDS-CHCl3 | mg/L | 39.9 | NA | NA | 46.1 | NA | 43.4 |  |  |  |  | 43.1333 | 7.2069 | SDS-CHCl3 | mg/L | 39.9 | NA | NA | 46.1 | NA | 43.4 |  |  |  |  | 43.1333 | 7.2069 | Avg-C8-10 | Average | --- | --- | --- | --- | 8.02 | 21.3 | 1.6475 | 0.0245 | 1.4872 | 2.755 | 0.79 | 1.965 | 3.6 | 9.2395 | 47.9 | 97.15 | 10.37 | 21.5611 | 17.6947 | 9.115 | 58.7408 | BMRL | 6.2119 | 3.1891 | BMRL | 4.1024 | 4.5114 | BMRL | BMRL | 1.9646 | 13.5034 | 18.0148 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.855 | 23.15 | 1.305 | 0.0211 | 1.6169 | 2.6 | 0.89 | 1.71 | 3.2 | 9.1947 | 48.05 | 70.8 | 5.845 | 18.4224 | 12.0659 | 9.91 | 46.2432 | BMRL | 5.6423 | 2.7917 | 1.0428 | 3.9424 | 3.7929 | BMRL | BMRL | 1.6249 | 12.8978 | 16.6907
|  |  |  | Estimated RSSCT run time, tSCT (days) | 16.3478 | [5 empty] | SDS-BDCM | mg/L | 15.7068 | NA | NA | 18.2313 | NA | 17.9876 |  |  |  |  | 17.3086 | 8.0451 | SDS-BDCM | mg/L | 15.7068 | NA | NA | 18.2313 | NA | 17.9876 |  |  |  |  | 17.3086 | 8.0451 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.74813 | 0 | 1.5175 | 0.40816 | 1.1093 | 0.36298 | 5.0633 | 1.5267 | 0 | 0.43292 | 0 | 10.808 | 16.0077 | 12.4046 | 13.453 | 12.1777 | 13.3213 |  | 15.6873 | 23.0497 |  | 24.634 | 21.0746 |  |  | 16.766 | 20.1442 | 20.3772 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.11293 | 0.43197 | 0.76628 | 0.47393 | 0.29235 | 0 | 2.2472 | 1.1696 | 0 | 0.11251 | 0.20812 | 1.6949 | 7.0145 | 2.1825 | 7.4664 | 5.8527 | 4.9585 |  | 5.4876 | 11.924 |  | 2.8519 | 1.4902 |  |  | 4.288 | 13.9385 | 11.1096
|  |  |  | RSSCT bed length, lSC (cm) | 24.2632 | [5 empty] | SDS-DBCM | mg/L | 29.2084 | NA | NA | 32.414 | NA | 32.4157 |  |  |  |  | 31.346 | 5.9059 | SDS-DBCM | mg/L | 29.2084 | NA | NA | 32.414 | NA | 32.4157 |  |  |  |  | 31.346 | 5.9059 | C10-10 | Primary | 1998-02-16 | 16:52 | 97.8667 | 7381.104 | 8.94 | 23 | 2.035 | 0.0334 | 1.6413 | 2.94 | 0.9 | 2.04 | 3.2 | 9.1747 | 47.9 | 119.85 | 13.8 | 18.679 | 19.3288 | 5.62 | 57.4279 | BMRL | 7.9922 | 4.2202 | BMRL | 3.92 | 5.2086 | BMRL | BMRL | 2.5803 | 16.1323 | 21.3409 | C10-20 | Primary | 1998-02-21 | 19:33 | 220.55 | 16633.881 | 7.73 | 21.1 | 1.86 | 0.03035 | 1.6317 | 2.81 | 0.81 | 2 | 3 | 9.2147 | 48 | 97.85 | 13.55 | 21.9714 | 20.4176 | 7.29 | 63.229 | BMRL | 7.113 | 4.7273 | 1.0646 | 5.2941 | 6.0574 | BMRL | 2.3458 | 3.1935 | 18.199 | 24.2564
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 180.4454 | [5 empty] | SDS-CHBr3 | mg/L | 2.46 | NA | NA | 2.95 | NA | 2.91 |  |  |  |  | 2.7733 | 9.811 | SDS-CHBr3 | mg/L | 2.46 | NA | NA | 2.95 | NA | 2.91 |  |  |  |  | 2.7733 | 9.811 | D-C10-10 | Duplicate | 1998-02-16 | 16:52 | 97.8667 | 7381.104 | 8.95 | 22.9 | 2.02 | 0.0332 | 1.6436 | 2.93 | 0.86 | 2.07 | 3.2 | 9.189 | 47.9 | 116.5 | 13.7 | 18.7518 | 18.9323 | 5.68 | 57.064 | BMRL | 7.8154 | 4.3471 | 1.0425 | 4.2886 | 5.6036 | BMRL | BMRL | 2.6954 | 17.4935 | 23.0971 | D-C10-20 | Duplicate | 1998-02-21 | 19:33 | 220.55 | 16633.881 | 7.79 | 21 | 1.91 | 0.03145 | 1.6466 | 2.83 | 0.87 | 1.96 | 3 | 9.195 | 48 | 97.9 | 13.2 | 21.4726 | 20.1599 | 7.01 | 61.8424 | BMRL | 6.4661 | 4.0966 | 1.14 | 4.5106 | 5.5489 | BMRL | 2.2098 | 2.7104 | 16.2134 | 21.7623
|  |  |  | Mass GAC required, mSC (g) | 6.3907 | [5 empty] | SDS-THM4 | mg/L | 87.2752 | NA | NA | 99.6953 | NA | 96.7133 |  |  |  |  | 94.5612 | 6.8566 | SDS-THM4 | mg/L | 87.2752 | NA | NA | 99.6953 | NA | 96.7133 |  |  |  |  | 94.5612 | 6.8566 | Avg-C10-10 | Average | --- | --- | --- | --- | 8.945 | 22.95 | 2.0275 | 0.0333 | 1.6424 | 2.935 | 0.88 | 2.055 | 3.2 | 9.1819 | 47.9 | 118.175 | 13.75 | 18.7154 | 19.1306 | 5.65 | 57.246 | BMRL | 7.9038 | 4.2836 | 1.0425 | 4.1043 | 5.4061 | BMRL | BMRL | 2.6378 | 16.8129 | 22.219 | Avg-C10-20 | Average | --- | --- | --- | --- | 7.76 | 21.05 | 1.885 | 0.0309 | 1.6392 | 2.82 | 0.84 | 1.98 | 3 | 9.2049 | 48 | 97.875 | 13.375 | 21.722 | 20.2887 | 7.15 | 62.5357 | BMRL | 6.7896 | 4.4119 | 1.1023 | 4.9023 | 5.8032 | BMRL | 2.2778 | 2.952 | 17.2062 | 23.0093
[11 empty] | SDS-MCAA* | mg/L | 3.576 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 3.576 | #DIV/0! | SDS-MCAA* | mg/L | 3.576 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 3.576 | #DIV/0! | RPD-C10-10 | RPD | --- | --- | --- | --- | 0.11179 | 0.43573 | 0.73983 | 0.6006 | 0.13923 | 0.34072 | 4.5455 | 1.4599 | 0 | 0.15491 | 0 | 2.8348 | 0.72727 | 0.38869 | 2.073 | 1.0619 | 0.63555 |  | 2.2376 | 2.9626 |  | 8.9804 | 7.3081 |  |  | 4.3627 | 8.0958 | 7.9041 | RPD-C10-20 | RPD | --- | --- | --- | --- | 0.7732 | 0.47506 | 2.6525 | 3.5599 | 0.90756 | 0.70922 | 7.1429 | 2.0202 | 0 | 0.21478 | 0 | 0.051086 | 2.6168 | 2.2963 | 1.2704 | 3.9161 | 2.2172 |  | 9.5278 | 14.2952 | 6.8413 | 15.9811 | 8.7624 |  | 5.9693 | 16.365 | 11.5402 | 10.8396
[11 empty] | SDS-DCAA* | mg/L | 14.5856 | NA | NA | 14.5476 | NA | 13.8931 |  |  |  |  | 14.3421 | 2.7146 | SDS-DCAA* | mg/L | 14.5856 | NA | NA | 14.5476 | NA | 13.8931 |  |  |  |  | 14.3421 | 2.7146 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 7.3545 | NA | NA | 8.3344 | NA | 7.1664 |  |  |  |  | 7.6184 | 8.2318 | SDS-TCAA* | mg/L | 7.3545 | NA | NA | 8.3344 | NA | 7.1664 |  |  |  |  | 7.6184 | 8.2318 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.252 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 1.252 | #DIV/0! | SDS-MBAA* | mg/L | 1.252 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 1.252 | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 3.0632 | NA | NA | 3.4167 | NA | 3.1794 |  |  |  |  | 3.2198 | 5.5966 | SDS-DBAA* | mg/L | 3.0632 | NA | NA | 3.4167 | NA | 3.1794 |  |  |  |  | 3.2198 | 5.5966
[11 empty] | SDS-BCAA* | mg/L | 7.197 | NA | NA | 7.5443 | NA | 7.0783 |  |  |  |  | 7.2732 | 3.3296 | SDS-BCAA* | mg/L | 7.197 | NA | NA | 7.5443 | NA | 7.0783 |  |  |  |  | 7.2732 | 3.3296
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | BMRL | NA | NA | 2.0147 | NA | 2.0334 |  |  |  |  | 2.024 | 0.65434 | SDS-CDBAA | mg/L | BMRL | NA | NA | 2.0147 | NA | 2.0334 |  |  |  |  | 2.024 | 0.65434
[11 empty] | SDS-DCBAA | mg/L | 4.0629 | NA | NA | 4.2912 | NA | 4.3028 |  |  |  |  | 4.219 | 3.2065 | SDS-DCBAA | mg/L | 4.0629 | NA | NA | 4.2912 | NA | 4.3028 |  |  |  |  | 4.219 | 3.2065
[11 empty] | SDS-HAA5 | mg/L | 29.8314 | NA | NA | 26.2987 | NA | 24.2389 |  |  |  |  | 26.7897 | 10.5578 | SDS-HAA5 | mg/L | 29.8314 | NA | NA | 26.2987 | NA | 24.2389 |  |  |  |  | 26.7897 | 10.5578
[11 empty] | SDS-HAA6 | mg/L | 37.0284 | NA | NA | 33.843 | NA | 31.3172 |  |  |  |  | 34.0629 | 8.402 | SDS-HAA6 | mg/L | 37.0284 | NA | NA | 33.843 | NA | 31.3172 |  |  |  |  | 34.0629 | 8.402
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on A1: S&H Comments: 1. Very rapid breakthrough of SDS-DCAA occurred during quarters 1, 2 and 4 (in the 3rd quarter, SDS-DCAA breakthrough followed the breakthrough pattern of other DBPs). This rapid breakthrough of SDS-DCAA can be indicative of preformed DCAA. Recarbonation feeds, which contained plant chlorinated finished water were not utilized during the first sampling session. However, the recarbonation feeds were left on during the 2nd, 3rd, and 4th quarters of testing. Note that the plant does not return filter washwater to the head of the plant, so this is not a potential source of preformed DBPs. Also, breakthrough of SDS-DCAA exhibited a “peak” curve during the 2nd quarter – 20- minute EBCT and a “peak-valley-peak” curve during the 4th quarter – 20-minute EBCT. 2. For the analysis of UV-254, TOC and TOX, values below the MRL of 0.009 1/cm, 0.50 mg/L and 25ug/L as Cl-, respectively, have been reported and should be considered estimates.
Note on H22: S&H Comment: Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS.
Note on BS5: S&H Comment: Based on the breakthrough of SDS-DCAA, preformed DCAA may have been present in the influent water. This was not confirmed through analysis of instantaneous DBPs or chlorine residual monitoring of the treatment study influent . Recarbonation feeds (which contain chlorinated plant finished water) were not on during quarter 1 sampling, and filter washwater is not returned to the head of the plant.
Note on DB5: S&H Comment: DCAA in the influent was possible, but not confirmed through instantaneous DBP's or chlorine residual of the sample influent. Based on the plant schematic, the sample was collected from a train with no washwater return.

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Topeka | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 2.4 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-06-01 | [12 empty] | 20-min. EBCT Start Date | 1998-06-01 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | KS2017701 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 8 | mesh size | (mm) | Rapid mix | 4 mg/L polymer | Full-Scale | 10-min. EBCT Start Time | 15:20 | [12 empty] | 20-min. EBCT Start Time | 15:20 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Primary presedimentation | 636 minutes | Full-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 10
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 20 | 6 | 3.35 | Polymer addition | 2 mg/L polymer | Full-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-06-01 | 20:37 | 5.2833 | 398.469 | 8.63 | 22.5 | 0.195 | 0.0018 | 0.92308 | 2 | 0.77 | 1.23 | 20.2 | 9.1799 | 48.3 | 6.1 | BMRL | 3.282 | BMRL | 6.8032 | 10.0852 | BMRL | BMRL | BMRL | BMRL | 1.1602 | BMRL | BMRL | BMRL | BMRL | 1.1602 | 1.1602 | C1-20 | N | 1998-06-01 | 19:55 | 4.5833 | 345.675 | 8.76 | 23.2 | 0.19 | 0.00145 | 0.76316 | 2 | 0.96 | 1.04 | 20.2 | 9.2599 | 48.4 | 5.65 | BMRL | 2.5208 | BMRL | 5.497 | 8.0178 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Secondary presedimentation | 367 minutes | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-06-02 | 15:21 | 24.0167 | 1811.337 | 8.56 | 23.1 | 0.32 | 0.00355 | 1.1094 | 2.09 | 0.81 | 1.28 | 20.2 | 9.205 | 48.4 | 16.15 | BMRL | 6.3418 | 1.6535 | 15.9522 | 23.9475 | BMRL | BMRL | BMRL | BMRL | 2.3885 | BMRL | BMRL | BMRL | BMRL | 2.3885 | 2.3885 | C2-20 | N | 1998-06-04 | 19:32 | 76.2 | 5747.004 | 8.49 | 21.5 | 0.42 | 0.0048 | 1.1429 | 2.16 | 0.77 | 1.39 | 19.6 | 9.1959 | 48.3 | 36.95 | BMRL | 8.171 | 2.3967 | 19.3622 | 29.9298 | BMRL | 8.0075 | BMRL | BMRL | 3.7842 | 1.4114 | BMRL | BMRL | BMRL | 11.7917 | 13.203 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5155 | 10 | 2 | Softening | 137 mg/L lime; 11.5 mg/L alum | Full-Scale | Sampling date | MM/DD/YY | 1998-06-01 | 1998-06-09 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-06-01 | 1998-06-09 | [7 empty] | --- | --- |  | Avg-C3-10 | Y | 1998-06-03 | 02:09 | 34.8167 | 2625.873 | 8.69 | 21.55 | 0.465 | 0.005725 | 1.2312 | 2.2 | 0.815 | 1.385 | 20.2 | 9.2271 | 48.3 | 31.925 | BMRL | 10.2259 | 2.9523 | 22.2342 | 35.4124 | BMRL | 7.5416 | BMRL | BMRL | 3.9018 | 1.6221 | BMRL | BMRL | BMRL | 11.4433 | 13.0654 | Avg-C3-20 | Y | 1998-06-05 | 13:32 | 94.2 | 7104.564 | 8.635 | 22.35 | 0.6325 | 0.007 | 1.1067 | 2.365 | 0.765 | 1.6 | 19.6 | 9.1973 | 48.3 | 43.675 | BMRL | 13.1968 | 4.0453 | 25.0382 | 42.2803 | BMRL | 7.5794 | BMRL | BMRL | 4.4084 | 2.9302 | BMRL | BMRL | BMRL | 11.9878 | 14.918 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 140 | 12 | 1.68 | Primary sedimentation | 732 minutes | Full-Scale | Sampling time | hh:mm | 17:15 | 16:40 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 17:15 | 16:40 | [7 empty] | --- | --- |  | C4-10 | N | 1998-06-03 | 07:36 | 40.2667 | 3036.912 | 8.66 | 22.7 | 0.585 | 0.0071 | 1.2137 | 2.29 | 0.77 | 1.52 | 20.2 | 9.2195 | 48.4 | 41.45 | BMRL | 13.5647 | 3.9372 | 28.1698 | 45.6717 | BMRL | 7.9461 | BMRL | BMRL | 4.1045 | 2.2503 | BMRL | BMRL | BMRL | 12.0506 | 14.3009 | C4-20 | N | 1998-06-06 | 07:31 | 112.1833 | 8460.867 | 8.73 | 20.4 | 0.745 | 0.009 | 1.2081 | 2.47 | 0.78 | 1.69 | 19.6 | 9.2259 | 48.3 | 55.5 | 1.8019 | 16.4225 | 5.7458 | 27.2025 | 51.1727 | BMRL | 6.341 | BMRL | BMRL | 5.1722 | 4.0802 | BMRL | BMRL | BMRL | 11.5133 | 15.5935 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 230 | 16 | 1.18 | Recarbonation | 14 mg/L carbon dioxide | Full-Scale | Operation time | hh.hh | 1.9167 | 193.3333 | [7 empty] | --- | --- |  | Operation time | hh.hh | 1.9167 | 193.3333 | [7 empty] | --- | --- |  | C5-10 | N | 1998-06-03 | 21:18 | 53.9667 | 4070.166 | 8.58 | 21.5 | 0.805 | 0.01055 | 1.3106 | 2.46 | 0.69 | 1.77 | 20.2 | 9.225 | 48.4 | 62.5 | 2.3521 | 19.7824 | 6.979 | 31.1988 | 60.3123 | BMRL | 7.0524 | BMRL | BMRL | 6.921 | 4.9186 | BMRL | BMRL | 1.0351 | 13.9735 | 18.8921 | C5-20 | N | 1998-06-07 | 01:22 | 130.0333 | 9807.114 | 8.73 | 21.4 | 0.87 | 0.01215 | 1.3966 | 2.59 | 0.77 | 1.82 | 19.6 | 9.2159 | 48.3 | 65.2 | 3.1182 | 22.6671 | 8.7518 | 32.3384 | 66.8754 | BMRL | 5.6171 | BMRL | BMRL | 5.6918 | 3.921 | BMRL | BMRL | BMRL | 11.3089 | 15.2299 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 | Secondary sedimentation | 314 minutes | Full-Scale | Bed volumes | (10 minutes) | 144.555 | 14581.2 | [7 empty] | --- | --- |  | Bed volumes | (10 minutes) | 72.2775 | 7290.6 | [7 empty] | --- | --- |  | C6-10 | N | 1998-06-04 | 04:55 | 61.5833 | 4644.615 | 8.58 | 21.5 | 0.92 | 0.0123 | 1.337 | 2.54 | 0.73 | 1.81 | 20.2 | 9.215 | 48.5 | 69.15 | 2.7101 | 22.5581 | 8.4483 | 31.7971 | 65.5137 | BMRL | 6.4361 | BMRL | BMRL | 6.6924 | 4.6168 | BMRL | BMRL | 1.0034 | 13.1285 | 17.7453 | C6-20 | N | 1998-06-07 | 13:17 | 141.95 | 10705.869 | 8.79 | 22.3 | 0.98 | 0.0137 | 1.398 | 2.69 | 0.74 | 1.95 | 20 | 9.1695 | 47.9 | 68.3 | 2.6126 | 22.2603 | 8.8031 | 27.8 | 61.476 | BMRL | 4.9859 | BMRL | BMRL | 5.9559 | 3.785 | BMRL | BMRL | 1.0526 | 10.9418 | 14.7269 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Alkalinity | mg/L as CaCO3 | 37.2 | 38 | [7 empty] | 37.6 | 1.5045 |  | Alkalinity | mg/L as CaCO3 | 37.2 | 38 | [7 empty] | 37.6 | 1.5045 |  | Avg-C7-10 | Y | 1998-06-04 | 17:31 | 74.1833 | 5594.907 | 8.535 | 22.25 | 1.1025 | 0.01525 | 1.3832 | 2.82 | 1.17 | 1.65 | 19.6 | 9.1427 | 48.1 | 85.225 | 4.4822 | 28.3096 | 13.3649 | 28.4556 | 74.6123 | BMRL | 6.782 | 1.1492 | BMRL | 7.3254 | 5.4507 | BMRL | BMRL | 1.2444 | 15.2566 | 20.7073 | Avg-C7-20 | Y | 1998-06-08 | 13:00 | 165.6667 | 12494.58 | 8.555 | 23.6 | 1.1375 | 0.015225 | 1.3385 | 2.85 | 0.765 | 2.085 | 20 | 9.1395 | 47.95 | 81.825 | 3.5073 | 25.7493 | 11.0167 | 28.25 | 68.5233 | BMRL | 4.2679 | 1.1605 | BMRL | 5.9011 | 3.8537 | BMRL | BMRL | 1.1608 | 11.3294 | 15.1831 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 6953.206 | 40 | 0.425 | pH adjustment | Sulfuric acid to pH 9.2 | Bench-Scale | Total hardness | mg/L as CaCO3 | 166 | 166 | [7 empty] | 166 | 0 |  | Total hardness | mg/L as CaCO3 | 166 | 166 | [7 empty] | 166 | 0 |  | C8-10 | N | 1998-06-05 | 08:03 | 88.7167 | 6691.011 | 8.42 | 21.7 | 1.285 | 0.01755 | 1.3658 | 2.99 | 1.38 | 1.61 | 19.6 | 9.1667 | 48.1 | 94.85 | 6.2094 | 32.1184 | 17.2282 | 27.701 | 83.257 | BMRL | 7.6337 | 1.4818 | BMRL | 7.887 | 6.015 | BMRL | BMRL | 1.532 | 17.0025 | 23.0175 | C8-20 | N | 1998-06-11 | 00:43 | 225.3833 | 16998.411 | 8.61 | 22.8 | 1.31 | 0.0187 | 1.4275 | 2.98 | 0.77 | 2.21 | 19.7 | 9.2047 | 48 | 93.95 | 5.2072 | 29.6819 | 14.7483 | 28.1 | 77.7373 | BMRL | 2.9316 | 2.044 | BMRL | 9.0682 | 5.1783 | BMRL | BMRL | 1.7102 | 14.0438 | 19.2221 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 13906.412 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 125 | 125 | [7 empty] | 125 | 0 |  | Calcium hardness | mg/L as CaCO3 | 125 | 125 | [7 empty] | 125 | 0 |  | C9-10 | N | 1998-06-05 | 20:54 | 101.5667 | 7660.158 | 8.38 | 23 | 1.415 | 0.01945 | 1.3746 | 3.12 | 0.89 | 2.23 | 19.6 | 9.1786 | 48.2 | 106.25 | 7.7402 | 33.5154 | 19.1396 | 27.9701 | 88.3654 | BMRL | 8.0687 | 1.7421 | BMRL | 8.9681 | 6.7479 | BMRL | 2.2975 | 1.7855 | 18.779 | 25.5268 | C9-20 | N | 1998-06-13 | 00:24 | 273.0667 | 20594.688 | 8.6 | 23 | 1.435 | 0.02065 | 1.439 | 3.09 | 0.72 | 2.37 | 19.7 | 9.2299 | 48 | 100.7 | 6.5746 | 32.4255 | 18.066 | 26.4 | 83.4661 | BMRL | 3.4134 | 2.218 | BMRL | 10.5513 | 6.4581 | BMRL | 2.3536 | 2.2105 | 16.1827 | 22.6408 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 18078.3356 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.15 | 0.16 | [7 empty] | 0.155 | 4.562 |  | Ammonia | mg NH3-N / L | 0.15 | 0.16 | [7 empty] | 0.155 | 4.562 |  | Avg-C10-10 | Y | 1998-06-06 | 13:37 | 118.2833 | 8920.929 | 8.69 | 22.35 | 1.52 | 0.021425 | 1.4095 | 3.215 | 0.895 | 2.32 | 19.6 | 9.1714 | 48.2 | 114.525 | 9.6319 | 36.0011 | 22.4844 | 27.821 | 95.9384 | BMRL | 7.7876 | 1.4694 | BMRL | 7.8356 | 6.3856 | BMRL | 2.1415 | 1.7724 | 17.0925 | 23.4782 | Avg-C10-20 | Y | 1998-06-14 | 12:14 | 308.9 | 23297.238 | 8.615 | 23.4 | 1.53 | 0.02275 | 1.4869 | 3.19 | 0.735 | 2.455 | 20 | 9.2147 | 48.75 | 112.875 | 8.3569 | 32.9437 | 20.2894 | 25.518 | 87.108 | BMRL | 3.7874 | 1.999 | BMRL | 9.1271 | 6.1524 | BMRL | 2.0755 | 1.9151 | 14.9135 | 21.066 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 110 | 110 | [7 empty] | 110 | 0 |  | Bromide | mg/L | 110 | 110 | [7 empty] | 110 | 0 |  | C11-10 | N | 1998-06-07 | 11:33 | 140.2167 | 10575.141 | 8.79 | 22.3 | 1.67 | 0.0243 | 1.4551 | 3.36 | 0.87 | 2.49 | 19.6 | 9.2202 | 48.2 | 123.35 | 13.1759 | 39.208 | 26.8636 | 27.9553 | 107.2028 | BMRL | 8.5144 | 1.8739 | BMRL | 8.2695 | 7.0216 | BMRL | 2.0227 | 2.1671 | 18.6577 | 25.6794 | C11-20 | N | 1998-06-17 | 00:05 | 368.75 | 27811.125 | 8.71 | 23.1 | 1.665 | 0.0244 | 1.4655 | 3.32 | 0.31 | 3.01 | 20.3 | 9.1547 | 48 | 118.9 | 9.1799 | 32.6097 | 21.6398 | 21.4 | 84.8294 | BMRL | 3.6309 | 2.0141 | BMRL | 9.8421 | 7.0369 | BMRL | 2.5506 | 2.2113 | 15.4871 | 22.524 | Natural Gas Rate ($/ft3) | 0.0058
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-06-08 | 17:04 | 169.7333 | 12801.288 | 8.59 | 24.4 | 1.83 | 0.02645 | 1.4454 | 3.45 | 0.88 | 2.57 | 19.7 | 9.1247 | 47.9 | 129 | 13.1416 | 34.9567 | 26.1037 | 20.9 | 95.102 | BMRL | 8.4047 | 3.059 | BMRL | 11.3172 | 8.8625 | BMRL | 3.2224 | 3.3865 | 22.7809 | 31.6434 | C12-20 | N | 1998-06-20 | 13:02 | 453.7 | 34218.054 | 8.75 | 24.1 | 1.84 | 0.0276 | 1.5 | 3.47 | 0.62 | 2.85 | 20.3 | 9.1436 | 48 | 131.45 | 13.1621 | 36.0303 | 26.3963 | 24.857 | 100.4456 | BMRL | 4.918 | 2.4533 | BMRL | 9.4671 | 7.2082 | BMRL | 2.5955 | 2.6411 | 16.8384 | 24.0465 | Current Process Water Rate ($/1000 gal) | 0.43
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.0266e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-06-09 | 22:14 | 198.9 | 15001.038 | 8.62 | 23.4 | 1.88 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C13-20 | N | 1998-06-21 | 17:24 | 482.0667 | 36357.468 | 8.76 | 22.3 | 1.8 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.084 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD
|  |  |  | Scaling factor, SF | 12.57 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-06-01 | 1998-06-04 | 1998-06-06 | 1998-06-09 | 1998-06-12 | 1998-06-21 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-06-01 | 1998-06-04 | 1998-06-06 | 1998-06-09 | 1998-06-12 | 1998-06-21 |  |  |  |  | --- | ---
Plant Name | West End Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 9.8996 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 17:20 | 09:10 | 09:05 | 16:35 | 11:00 | 17:30 |  |  |  |  | --- | --- | Sampling time | hh:mm | 17:20 | 09:10 | 09:05 | 16:35 | 11:00 | 17:30 |  |  |  |  | --- | ---
Treatment Plant Category | TS/SOFT |  |  | RSSCT flow rate, QSC (mL/min) | 8.2934 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 2 | 65.8333 | 113.75 | 193.25 | 259.6667 | 482.1667 |  |  |  |  | --- | --- | Operation time | hh.hh | 2 | 65.8333 | 113.75 | 193.25 | 259.6667 | 482.1667 |  |  |  |  | --- | ---
Process Train Name | North/South Train |  |  | Estimated total influent volume required, VSCT (L) | 357.8322 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 150.84 | 4965.15 | 8579.025 | 14574.915 | 19584.06 | 36365.01 |  |  |  |  | --- | --- | Bed volumes | (10 minute) | 75.42 | 2482.575 | 4289.5125 | 7287.4575 | 9792.03 | 18182.505 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 383 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.98 | NA | NA | 8.98 | NA | 8.97 |  |  |  |  | 8.9767 | 0.064317 | pH | --- | 8.98 | NA | NA | 8.98 | NA | 8.97 |  |  |  |  | 8.9767 | 0.064317 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.1 | NA | NA | 0.1 | NA | 0.1 |  |  |  |  | 0.1 | 0 | Turbidity | ntu | 0.1 | NA | NA | 0.1 | NA | 0.1 |  |  |  |  | 0.1 | 0 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 0.5 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 16.3 | NA | NA | 18.1 | NA | 19.4 |  |  |  |  | 17.9333 | 8.6805 | Temperature | oC | 16.3 | NA | NA | 18.1 | NA | 19.4 |  |  |  |  | 17.9333 | 8.6805
Historical Average Water Temperature (oC) | 17 |  |  | Estimated full-scale run time, tLCT (days) | 125.544 | [5 empty] | Total organic carbon | mg/L | 2.57 | 2.535 | 2.57 | 2.605 | 2.56 | 2.56 |  |  |  |  | 2.5667 | 0.8856 | Total organic carbon | mg/L | 2.57 | 2.535 | 2.57 | 2.605 | 2.56 | 2.56 |  |  |  |  | 2.5667 | 0.8856 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.79554 | [5 empty] | UV254 | cm-1 | 0.04555 | NA | NA | 0.04555 | NA | 0.047 |  |  |  |  | 0.046033 | 1.8186 | UV254 | cm-1 | 0.04555 | NA | NA | 0.04555 | NA | 0.047 |  |  |  |  | 0.046033 | 1.8186 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 9.9876 | [5 empty] | SUVA | L/(mg*m) | 1.7724 | NR | NR | 1.7486 | NR | 1.8359 |  |  |  |  | 1.7856 | 2.5297 | SUVA | L/(mg*m) | 1.7724 | NR | NR | 1.7486 | NR | 1.8359 |  |  |  |  | 1.7856 | 2.5297 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.1259 | [5 empty] | SDS-Cl2 dose | mg/L | 4.2 | NA | NA | 4.14 | NA | 4.18 |  |  |  |  | 4.1733 | 0.73204 | SDS-Cl2 dose | mg/L | 4.2 | NA | NA | 4.14 | NA | 4.18 |  |  |  |  | 4.1733 | 0.73204 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 119.2774 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.82 | NA | NA | 0.76 | NA | 0.4 |  |  |  |  | 0.66 | 34.4176 | SDS-Free Cl2 residual | mg/L | 0.82 | NA | NA | 0.76 | NA | 0.4 |  |  |  |  | 0.66 | 34.4176 | C3-10 | Primary | 1998-06-03 | 02:09 | 34.8167 | 2625.873 | 8.69 | 21.6 | 0.46 | 0.0059 | 1.2826 | 2.2 | 0.85 | 1.35 | 20.2 | 9.2295 | 48.3 | 34.7 | BMRL | 10.6153 | 3.0177 | 23.2809 | 36.9139 | BMRL | 7.8186 | BMRL | BMRL | 3.9666 | 1.6653 | BMRL | BMRL | BMRL | 11.7852 | 13.4505 | C3-20 | Primary | 1998-06-05 | 13:32 | 94.2 | 7104.564 | 8.64 | 22.3 | 0.625 | 0.0069 | 1.104 | 2.36 | 0.81 | 1.55 | 19.6 | 9.2044 | 48.3 | 44.3 | BMRL | 12.8281 | 3.8872 | 24.4872 | 41.2025 | BMRL | 7.7738 | BMRL | BMRL | 4.4574 | 2.9936 | BMRL | BMRL | BMRL | 12.2312 | 15.2248
|  |  |  | Mass GAC required, mSC (g) | 3.4012 | [5 empty] | SDS-Cl2 demand | mg/L | 3.38 | NR | NR | 3.38 | NR | 3.78 |  |  |  |  | 3.5133 | 6.5732 | SDS-Cl2 demand | mg/L | 3.38 | NR | NR | 3.38 | NR | 3.78 |  |  |  |  | 3.5133 | 6.5732 | D-C3-10 | Duplicate | 1998-06-03 | 02:09 | 34.8167 | 2625.873 | 8.69 | 21.5 | 0.47 | 0.00555 | 1.1809 | 2.2 | 0.78 | 1.42 | 20.2 | 9.2247 | 48.3 | 29.15 | BMRL | 9.8365 | 2.8869 | 21.1875 | 33.9108 | BMRL | 7.2645 | BMRL | BMRL | 3.837 | 1.5788 | BMRL | BMRL | BMRL | 11.1015 | 12.6803 | D-C3-10 | Duplicate | 1998-06-05 | 13:32 | 94.2 | 7104.564 | 8.63 | 22.4 | 0.64 | 0.0071 | 1.1094 | 2.37 | 0.72 | 1.65 | 19.6 | 9.1902 | 48.3 | 43.05 | BMRL | 13.5656 | 4.2034 | 25.5891 | 43.3581 | BMRL | 7.3851 | BMRL | BMRL | 4.3593 | 2.8669 | BMRL | BMRL | BMRL | 11.7444 | 14.6113
[11 empty] | SDS-Chlorination temp. | oC | 20.2 | NA | NA | 19.7 | NA | 20.3 |  |  |  |  | 20.0667 | 1.6019 | SDS-Chlorination temp. | oC | 20.2 | NA | NA | 19.7 | NA | 20.3 |  |  |  |  | 20.0667 | 1.6019 | Avg-C3-10 | Average | --- | --- | --- | --- | 8.69 | 21.55 | 0.465 | 0.005725 | 1.2317 | 2.2 | 0.815 | 1.385 | 20.2 | 9.2271 | 48.3 | 31.925 | BMRL | 10.2259 | 2.9523 | 22.2342 | 35.4124 | BMRL | 7.5416 | BMRL | BMRL | 3.9018 | 1.6221 | BMRL | BMRL | BMRL | 11.4433 | 13.0654 | Avg-C3-20 | Average | --- | --- | --- | --- | 8.635 | 22.35 | 0.6325 | 0.007 | 1.1067 | 2.365 | 0.765 | 1.6 | 19.6 | 9.1973 | 48.3 | 43.675 | BMRL | 13.1968 | 4.0453 | 25.0382 | 42.2803 | BMRL | 7.5794 | BMRL | BMRL | 4.4084 | 2.9302 | BMRL | BMRL | BMRL | 11.9878 | 14.918
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9.2699 | NA | NA | 9.2747 | NA | 9.199 |  |  |  |  | 9.2479 | 0.45867 | SDS-Chlorination pH | --- | 9.2699 | NA | NA | 9.2747 | NA | 9.199 |  |  |  |  | 9.2479 | 0.45867 | RPD-C3-10 | RPD | --- | --- | --- | --- | 0 | 0.46404 | 2.1505 | 6.1135 | 8.2614 | 0 | 8.589 | 5.0542 | 0 | 0.052006 | 0 | 17.3845 |  | 7.6162 | 4.4296 | 9.4155 | 8.4803 |  | 7.3478 |  |  | 3.3216 | 5.3293 |  |  |  | 5.975 | 5.8948 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0.11581 | 0.44743 | 2.3715 | 2.8571 | 0.48568 | 0.42283 | 11.7647 | 6.25 | 0 | 0.15471 | 0 | 2.862 |  | 5.5887 | 7.8164 | 4.4007 | 5.0983 |  | 5.1282 |  |  | 2.2258 | 4.3219 |  |  |  | 4.0609 | 4.1121
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 48.5 | NA | NA | 48 | NA | 47.9 |  |  |  |  | 48.1333 | 0.66784 | SDS-Incubation time | hours | 48.5 | NA | NA | 48 | NA | 47.9 |  |  |  |  | 48.1333 | 0.66784 | C7-10 | Primary | 1998-06-04 | 17:31 | 74.1833 | 5594.907 | 8.52 | 22.3 | 1.09 | 0.01555 | 1.4266 | 2.8 | 1.18 | 1.62 | 19.6 | 9.1486 | 48.1 | 87.9 | 4.6115 | 28.3868 | 13.4219 | 28.6589 | 75.079 | BMRL | 7.2968 | 1.1492 | BMRL | 8.0948 | 5.946 | BMRL | BMRL | 1.3014 | 16.5408 | 22.4868 | C7-20 | Primary | 1998-06-08 | 13:00 | 165.6667 | 12494.58 | 8.55 | 23.6 | 1.14 | 0.0153 | 1.3421 | 2.85 | 0.77 | 2.08 | 20 | 9.1495 | 47.9 | 83.95 | 3.4568 | 25.6798 | 11.0945 | 28.3 | 68.5312 | BMRL | 4.5075 | 1.1891 | BMRL | 6.1605 | 3.9648 | BMRL | BMRL | 1.1261 | 11.8571 | 15.8218
|  |  |  | Estimated full-scale run time, tLCT (days) | 251.088 | [5 empty] | SDS-TOX | mg Cl- /L | 219.8 | NA | NA | 222.1 | NA | 220.05 |  |  |  |  | 220.65 | 0.57192 | SDS-TOX | mg Cl- /L | 219.8 | NA | NA | 222.1 | NA | 220.05 |  |  |  |  | 220.65 | 0.57192 | D-C7-10 | Duplicate | 1998-06-04 | 17:31 | 74.1833 | 5594.907 | 8.55 | 22.2 | 1.115 | 0.01495 | 1.3408 | 2.84 | 1.16 | 1.68 | 19.6 | 9.1367 | 48.1 | 82.55 | 4.3529 | 28.2325 | 13.3079 | 28.2524 | 74.1457 | BMRL | 6.2672 | BMRL | BMRL | 6.556 | 4.9555 | BMRL | BMRL | 1.1874 | 12.8232 | 17.7786 | D-C7-20 | Duplicate | 1998-06-08 | 13:00 | 165.6667 | 12494.58 | 8.56 | 23.6 | 1.135 | 0.01515 | 1.3348 | 2.85 | 0.76 | 2.09 | 20 | 9.1295 | 48 | 79.7 | 3.5577 | 25.8188 | 10.939 | 28.2 | 68.5154 | BMRL | 4.0282 | 1.1318 | BMRL | 5.6417 | 3.7427 | BMRL | BMRL | 1.1955 | 10.8017 | 14.5443
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5911 | [5 empty] | SDS-CHCl3 | mg/L | 50.6557 | NA | NA | 42.2445 | NA | 37.2698 |  |  |  |  | 43.39 | 15.5937 | SDS-CHCl3 | mg/L | 50.6557 | NA | NA | 42.2445 | NA | 37.2698 |  |  |  |  | 43.39 | 15.5937 | Avg-C7-10 | Average | --- | --- | --- | --- | 8.535 | 22.25 | 1.1025 | 0.01525 | 1.3837 | 2.82 | 1.17 | 1.65 | 19.6 | 9.1427 | 48.1 | 85.225 | 4.4822 | 28.3096 | 13.3649 | 28.4556 | 74.6123 | BMRL | 6.782 | 1.1492 | BMRL | 7.3254 | 5.4507 | BMRL | BMRL | 1.2444 | 14.682 | 20.1327 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.555 | 23.6 | 1.1375 | 0.015225 | 1.3385 | 2.85 | 0.765 | 2.085 | 20 | 9.1395 | 47.95 | 81.825 | 3.5073 | 25.7493 | 11.0167 | 28.25 | 68.5233 | BMRL | 4.2679 | 1.1605 | BMRL | 5.9011 | 3.8537 | BMRL | BMRL | 1.1608 | 11.3294 | 15.1831
|  |  |  | Estimated RSSCT run time, tSCT (days) | 19.9752 | [5 empty] | SDS-BDCM | mg/L | 41.0069 | NA | NA | 36.5051 | NA | 33.8774 |  |  |  |  | 37.1298 | 9.7108 | SDS-BDCM | mg/L | 41.0069 | NA | NA | 36.5051 | NA | 33.8774 |  |  |  |  | 37.1298 | 9.7108 | RPD-C7-10 | RPD | --- | --- | --- | --- | 0.35149 | 0.44944 | 2.2676 | 3.9344 | 6.2006 | 1.4184 | 1.7094 | 3.6364 | 0 | 0.12964 | 0 | 6.2775 | 5.7687 | 0.54511 | 0.85272 | 1.4285 | 1.2509 |  | 15.1808 |  |  | 21.0072 | 18.1723 |  |  | 9.1625 | 25.3208 | 23.3855 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.11689 | 0 | 0.43956 | 0.98522 | 0.54567 | 0 | 1.3072 | 0.47962 | 0 | 0.21883 | 0.20855 | 5.194 | 2.8755 | 0.53946 | 1.4115 | 0.35398 | 0.022976 |  | 11.2287 | 4.9444 |  | 8.7912 | 5.7636 |  |  | 5.9731 | 9.3154 | 8.4139
|  |  |  | RSSCT bed length, lSC (cm) | 26.2518 | [5 empty] | SDS-DBCM | mg/L | 48.0349 | NA | NA | 41.2538 | NA | 37.6928 |  |  |  |  | 42.3272 | 12.4127 | SDS-DBCM | mg/L | 48.0349 | NA | NA | 41.2538 | NA | 37.6928 |  |  |  |  | 42.3272 | 12.4127 | C10-10 | Primary | 1998-06-06 | 13:37 | 118.2833 | 8920.929 | 8.7 | 22.4 | 1.515 | 0.0214 | 1.4125 | 3.21 | 0.89 | 2.32 | 19.6 | 9.1527 | 48.2 | 111.85 | 9.8121 | 37.657 | 23.0538 | 29.5731 | 100.096 | BMRL | 8.1249 | 1.5744 | BMRL | 8.6428 | 6.8829 | BMRL | 2.1415 | 1.7818 | 18.3421 | 25.225 | C10-20 | Primary | 1998-06-14 | 12:14 | 308.9 | 23297.238 | 8.59 | 23.4 | 1.545 | 0.0229 | 1.4822 | 3.19 | 0.78 | 2.41 | 20 | 9.2195 | 48.7 | 111.65 | 8.2997 | 32.3174 | 20.0089 | 25.7884 | 86.4144 | BMRL | 3.8171 | 1.9569 | BMRL | 9.1632 | 6.2224 | BMRL | 2.1054 | 1.9037 | 14.9372 | 21.1596
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 238.5548 | [5 empty] | SDS-CHBr3 | mg/L | 14.02 | NA | NA | 12 | NA | 12.2 |  |  |  |  | 12.74 | 8.7364 | SDS-CHBr3 | mg/L | 14.02 | NA | NA | 12 | NA | 12.2 |  |  |  |  | 12.74 | 8.7364 | D-C10-10 | Duplicate | 1998-06-06 | 13:37 | 118.2833 | 8920.929 | 8.68 | 22.3 | 1.525 | 0.02145 | 1.4066 | 3.22 | 0.9 | 2.32 | 19.6 | 9.1902 | 48.2 | 117.2 | 9.4518 | 34.3451 | 21.9149 | 26.0689 | 91.7807 | BMRL | 7.4502 | 1.3644 | BMRL | 7.0283 | 5.8884 | BMRL | BMRL | 1.763 | 15.843 | 21.7314 | D-C10-20 | Duplicate | 1998-06-14 | 12:14 | 308.9 | 23297.238 | 8.64 | 23.4 | 1.515 | 0.0226 | 1.4917 | 3.19 | 0.69 | 2.5 | 20 | 9.2099 | 48.8 | 114.1 | 8.414 | 33.5701 | 20.5699 | 25.2476 | 87.8016 | BMRL | 3.7577 | 2.0411 | BMRL | 9.091 | 6.0825 | BMRL | 2.0455 | 1.9264 | 14.8898 | 20.9723
|  |  |  | Mass GAC required, mSC (g) | 6.8023 | [5 empty] | SDS-THM4 | mg/L | 153.7175 | NA | NA | 132.0033 | NA | 121.0399 |  |  |  |  | 135.5869 | 12.2659 | SDS-THM4 | mg/L | 153.7175 | NA | NA | 132.0033 | NA | 121.0399 |  |  |  |  | 135.5869 | 12.2659 | Avg-C10-10 | Average | --- | --- | --- | --- | 8.69 | 22.35 | 1.52 | 0.021425 | 1.4095 | 3.215 | 0.895 | 2.32 | 19.6 | 9.1714 | 48.2 | 114.525 | 9.6319 | 36.0011 | 22.4844 | 27.821 | 95.9384 | BMRL | 7.7876 | 1.4694 | BMRL | 7.8356 | 6.3856 | BMRL | 2.1415 | 1.7724 | 17.0925 | 23.4782 | Avg-C10-20 | Average | --- | --- | --- | --- | 8.615 | 23.4 | 1.53 | 0.02275 | 1.487 | 3.19 | 0.735 | 2.455 | 20 | 9.2147 | 48.75 | 112.875 | 8.3569 | 32.9437 | 20.2894 | 25.518 | 87.108 | BMRL | 3.7874 | 1.999 | BMRL | 9.1271 | 6.1524 | BMRL | 2.0755 | 1.9151 | 14.9135 | 21.066
[11 empty] | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | RPD-C10-10 | RPD | --- | --- | --- | --- | 0.23015 | 0.44743 | 0.65789 | 0.23337 | 0.42452 | 0.31104 | 1.1173 | 0 | 0 | 0.40867 | 0 | 4.6715 | 3.7404 | 9.1995 | 5.065 | 12.5954 | 8.6672 |  | 8.6636 | 14.2893 |  | 20.6045 | 15.5731 |  |  | 1.0603 | 14.6212 | 14.8801 | RPD-C10-20 | RPD | --- | --- | --- | --- | 0.58038 | 0 | 1.9608 | 1.3187 | 0.64214 | 0 | 12.2449 | 3.666 | 0 | 0.10478 | 0.20513 | 2.1705 | 1.3666 | 3.8027 | 2.7652 | 2.1191 | 1.5925 |  | 1.5697 | 4.2142 |  | 0.79131 | 2.2727 |  | 2.8871 | 1.1869 | 0.31806 | 0.88892
[11 empty] | SDS-DCAA* | mg/L | 17.5587 | NA | NA | 15.5022 | NA | 13.0595 |  |  |  |  | 15.3735 | 14.6511 | SDS-DCAA* | mg/L | 17.5587 | NA | NA | 15.5022 | NA | 13.0595 |  |  |  |  | 15.3735 | 14.6511 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 3.3185 | NA | NA | 3.9348 | NA | 3.8744 |  |  |  |  | 3.7092 | 9.1595 | SDS-TCAA* | mg/L | 3.3185 | NA | NA | 3.9348 | NA | 3.8744 |  |  |  |  | 3.7092 | 9.1595 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-DBAA* | mg/L | 9.6614 | NA | NA | 9.2238 | NA | 9.5344 |  |  |  |  | 9.4732 | 2.3767 | SDS-DBAA* | mg/L | 9.6614 | NA | NA | 9.2238 | NA | 9.5344 |  |  |  |  | 9.4732 | 2.3767
[11 empty] | SDS-BCAA* | mg/L | 13.2544 | NA | NA | 10.9856 | NA | 11.5207 |  |  |  |  | 11.9203 | 9.9495 | SDS-BCAA* | mg/L | 13.2544 | NA | NA | 10.9856 | NA | 11.5207 |  |  |  |  | 11.9203 | 9.9495
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | 2.8398 | NA | NA | 2.6353 | NA | 2.6119 |  |  |  |  | 2.6957 | 4.6495 | SDS-CDBAA | mg/L | 2.8398 | NA | NA | 2.6353 | NA | 2.6119 |  |  |  |  | 2.6957 | 4.6495
[11 empty] | SDS-DCBAA | mg/L | 3.8522 | NA | NA | 3.5993 | NA | 3.3914 |  |  |  |  | 3.6143 | 6.3844 | SDS-DCBAA | mg/L | 3.8522 | NA | NA | 3.5993 | NA | 3.3914 |  |  |  |  | 3.6143 | 6.3844
[11 empty] | SDS-HAA5 | mg/L | 30.5387 | NA | NA | 28.6608 | NA | 26.4682 |  |  |  |  | 28.5559 | 7.1342 | SDS-HAA5 | mg/L | 30.5387 | NA | NA | 28.6608 | NA | 26.4682 |  |  |  |  | 28.5559 | 7.1342
[11 empty] | SDS-HAA6 | mg/L | 43.7931 | NA | NA | 39.6464 | NA | 37.9889 |  |  |  |  | 40.4761 | 7.3864 | SDS-HAA6 | mg/L | 43.7931 | NA | NA | 39.6464 | NA | 37.9889 |  |  |  |  | 40.4761 | 7.3864
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H22: S&H Comment: Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS.
Note on BS5: S&H Comment: Based on the breakthrough of SDS-DCAA, preformed DCAA may have been present in the influent water. This was not confirmed through analysis of instantaneous DBPs or chlorine residual monitoring of the treatment study influent . Recarbonation feeds (which contain chlorinated plant finished water) were on during quarter 2 sampling, and filter washwater is not returned to the head of the plant.
Note on CY12: S&H Comment: Bromoform spike result verified.
Note on DB5: S&H Comment: Based on the breakthrough of SDS-DCAA, preformed DCAA may have been present in the influent water. This was not confirmed through analysis of instantaneous DBPs or chlorine residual monitoring of the treatment study influent . Recarbonation feeds (which contain chlorinated plant finished water) were on during quarter 2 sampling, and filter washwater is not returned to the head of the plant.

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Topeka | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 2.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-09-08 | [12 empty] | 20-min. EBCT Start Date | 1998-09-08 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | KS2017701 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 10 | mesh size | (mm) | Rapid mix | 6 mg/L polymer | Full-Scale | 10-min. EBCT Start Time | 13:00 | [12 empty] | 20-min. EBCT Start Time | 13:00 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.5 | 4 | 4.75 | Primary presedimentation | 382 minutes | Full-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 10
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 28 | 6 | 3.35 | Polymer addition | 4 mg/L polymer | Full-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-09-08 | 16:39 | 3.65 | 275.283 | 8.9 | 21.1 | 0.08 | 0.0008 | 1 | 1.5 | 0.72 | 0.78 | 26.2 | 9.12 | 47.8 | 6.15 | BMRL | 2.4834 | BMRL | 5.8918 | 8.3752 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | C1-20 | N | 1998-09-08 | 16:43 | 3.7167 | 280.311 | 9.06 | 21.3 | 0.075 | 0.0006 | 0.8 | 1.5 | 0.73 | 0.77 | 26.2 | 9.1847 | 47.8 | 4.85 | BMRL | 2.0133 | BMRL | 4.8144 | 6.8277 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Secondary presedimentation | 220 minutes | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-09-09 | 18:25 | 29.4167 | 2218.605 | 8.58 | 21.2 | 0.2 | 0.00205 | 1.025 | 1.72 | 0.79 | 0.93 | 26.2 | 9.1499 | 47.8 | 16.05 | BMRL | 6.0972 | 1.2461 | 15.5839 | 22.9273 | BMRL | BMRL | BMRL | BMRL | 1.8921 | BMRL | BMRL | BMRL | BMRL | 1.8921 | 1.8921 | C2-20 | N | 1998-09-11 | 19:27 | 78.45 | 5916.699 | 8.54 | 22.2 | 0.295 | 0.00265 | 0.89831 | 1.83 | 0.76 | 1.07 | 26.1 | 9.1547 | 48.3 | 22.85 | BMRL | 8.2451 | 1.6371 | 17.7356 | 27.6178 | BMRL | BMRL | BMRL | BMRL | 3.8452 | 1.2227 | BMRL | BMRL | BMRL | 3.8452 | 5.0679 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.449 | 10 | 2 | Softening | 98 mg/L lime; 5.8 mg/L alum | Full-Scale | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-21 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-21 | [7 empty] | --- | --- |  | C3-10 | N | 1998-09-10 | 04:47 | 39.7833 | 3000.459 | 8.82 | 21.4 | 0.355 | 0.00395 | 1.1127 | 1.99 | 0.91 | 1.08 | 26.2 | 9.1747 | 47.8 | 27.5 | BMRL | 10.1959 | 2.5339 | 21.4152 | 34.145 | BMRL | BMRL | BMRL | BMRL | 3.2347 | 1.1611 | BMRL | BMRL | BMRL | 3.2347 | 4.3958 | Avg-C3-20 | Y | 1998-09-12 | 11:43 | 94.7167 | 7143.531 | 8.725 | 21.7 | 0.4 | 0.00465 | 1.1625 | 1.96 | 0.815 | 1.145 | 26.1 | 9.1623 | 48.3 | 29.65 | BMRL | 11.4582 | 2.5576 | 21.6074 | 35.6232 | BMRL | BMRL | BMRL | BMRL | 4.2156 | 1.4822 | BMRL | BMRL | 1.0553 | 4.2156 | 5.6977 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 140 | 12 | 1.68 | Primary sedimentation | 439 minutes | Full-Scale | Sampling time | hh:mm | 14:10 | 10:20 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 14:10 | 10:20 | [7 empty] | --- | --- |  | Avg-C4-10 | Y | 1998-09-10 | 09:56 | 44.9333 | 3388.872 | 8.535 | 21.35 | 0.46 | 0.00495 | 1.0761 | 2.02 | 0.74 | 1.28 | 26.1 | 9.115 | 48.3 | 37.775 | BMRL | 14.8373 | 3.6911 | 24.9145 | 43.4428 | BMRL | BMRL | BMRL | BMRL | 4.5554 | 1.7987 | BMRL | BMRL | 1.0699 | 4.5554 | 6.3541 | C4-20 | N | 1998-09-13 | 03:51 | 110.85 | 8360.307 | 8.72 | 21.5 | 0.525 | 0.00615 | 1.1714 | 2.09 | 0.76 | 1.33 | 26.1 | 9.1747 | 48.3 | 36.9 | 1.1251 | 16.5876 | 4.2339 | 27.5516 | 49.4982 | BMRL | BMRL | BMRL | BMRL | 4.7268 | 1.7913 | BMRL | BMRL | 1.1099 | 4.7268 | 6.5181 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 230 | 16 | 1.18 | Recarbonation | 24 mg/L carbon dioxide | Full-Scale | Operation time | hh.hh | 1.1667 | 309.3333 | [7 empty] | --- | --- |  | Operation time | hh.hh | 1.1667 | 309.3333 | [7 empty] | --- | --- |  | C5-10 | N | 1998-09-11 | 01:25 | 60.4167 | 4556.625 | 8.6 | 21 | 0.665 | 0.00825 | 1.2406 | 2.25 | 0.8 | 1.45 | 26.1 | 9.1299 | 48.3 | 53.15 | 1.6487 | 21.6202 | 6.6527 | 29.7131 | 59.6347 | BMRL | 1.0532 | BMRL | BMRL | 7.5322 | 3.1364 | BMRL | BMRL | 1.1987 | 8.5854 | 11.7218 | C5-20 | N | 1998-09-13 | 19:55 | 126.9167 | 9572.055 | 8.49 | 22.6 | 0.61 | 0.0074 | 1.2131 | 2.2 | 0.77 | 1.43 | 26.2 | 9.155 | 48.1 | 43.95 | 1.2469 | 17.8426 | 4.7925 | 27.122 | 51.004 | BMRL | BMRL | BMRL | BMRL | 4.5792 | 1.8367 | BMRL | BMRL | 1.0765 | 4.5792 | 6.4159 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 | Secondary sedimentation | 189 minutes | Full-Scale | Bed volumes | (10 minutes) | 87.99 | 23329.92 | [7 empty] | --- | --- |  | Bed volumes | (10 minutes) | 43.995 | 11664.96 | [7 empty] | --- | --- |  | C6-10 | N | 1998-09-11 | 11:50 | 70.8333 | 5342.25 | 8.39 | 21.1 | 0.785 | 0.0111 | 1.414 | 2.38 | 0.74 | 1.64 | 26.1 | 9.1399 | 48.3 | 62.7 | 2.7163 | 25.81 | 8.9238 | 30.3507 | 67.8009 | BMRL | 1.3791 | BMRL | BMRL | 7.6323 | 3.558 | BMRL | BMRL | 1.2036 | 9.0114 | 12.5694 | C6-20 | N | 1998-09-14 | 17:32 | 148.5333 | 11202.384 | 8.36 | 22.7 | 0.785 | 0.00985 | 1.2548 | 2.4 | 0.83 | 1.57 | 26.2 | 9.15 | 48.2 | 55.55 | 1.8741 | 23.9598 | 7.4526 | 30.1158 | 63.4024 | BMRL | BMRL | BMRL | BMRL | 6.5312 | 2.7174 | BMRL | BMRL | 1.2486 | 6.5312 | 9.2486 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Alkalinity | mg/L as CaCO3 | 29.5 | 29.55 | [7 empty] | 29.525 | 0.11975 |  | Alkalinity | mg/L as CaCO3 | 29.5 | 29.55 | [7 empty] | 29.525 | 0.11975 |  | Avg-C7-10 | Y | 1998-09-12 | 03:22 | 86.3667 | 6513.774 | 8.625 | 21.25 | 0.935 | 0.013625 | 1.4572 | 2.55 | 0.785 | 1.765 | 26.1 | 9.1163 | 48.3 | 76.35 | 3.4192 | 30.2291 | 12.0852 | 29.199 | 74.9325 | BMRL | 1.5415 | BMRL | BMRL | 6.8734 | 3.4809 | BMRL | BMRL | 1.3088 | 8.4149 | 11.8958 | Avg-C7-20 | Y | 1998-09-16 | 07:26 | 186.4333 | 14060.802 | 8.41 | 21.15 | 0.925 | 0.013175 | 1.4243 | 2.56 | 0.765 | 1.795 | 26.2 | 9.1675 | 48.2 | 70.8 | 2.6893 | 27.64 | 9.8123 | 29.4863 | 69.6279 | BMRL | 1.5749 | BMRL | BMRL | 7.851 | 3.608 | BMRL | BMRL | BMRL | 9.4259 | 13.0339 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 6593.8296 | 40 | 0.425 | pH adjustment | Sulfuric acid to pH 9.2 | Bench-Scale | Total hardness | mg/L as CaCO3 | 133 | 133 | [7 empty] | 133 | 0 |  | Total hardness | mg/L as CaCO3 | 133 | 133 | [7 empty] | 133 | 0 |  | C8-10 | N | 1998-09-12 | 21:43 | 104.7167 | 7897.731 | 8.66 | 21.6 | 1.085 | 0.0163 | 1.5023 | 2.72 | 0.81 | 1.91 | 26.1 | 9.165 | 48.3 | 91 | 5.0577 | 33.6776 | 15.8272 | 26.6733 | 81.2358 | BMRL | 2.1518 | 1.2841 | BMRL | 7.9045 | 4.3582 | BMRL | BMRL | 1.5191 | 11.3405 | 15.6986 | C8-20 | N | 1998-09-18 | 13:59 | 240.9833 | 18174.963 | 8.3 | 21.7 | 1.03 | 0.01555 | 1.5097 | 2.71 | 0.87 | 1.84 | 26 | 9.1299 | 48 | 83.55 | 4.2 | 30.0892 | 13.8985 | 27.9448 | 76.1326 | BMRL | 2.4702 | 2.0376 | BMRL | 12.1705 | 5.7592 | BMRL | BMRL | 1.2598 | 16.6783 | 22.4375 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 13187.6593 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 95 | 95 | [7 empty] | 95 | 0 |  | Calcium hardness | mg/L as CaCO3 | 95 | 95 | [7 empty] | 95 | 0 |  | C9-10 | N | 1998-09-14 | 09:53 | 140.8833 | 10625.421 | 8.4 | 21.7 | 1.285 | 0.01895 | 1.4747 | 2.96 | 0.79 | 2.17 | 26.2 | 9.125 | 48.1 | 99.35 | 7.8591 | 35.4508 | 20.2594 | 22.8707 | 86.44 | BMRL | 3.298 | 1.4521 | BMRL | 8.7819 | 5.6726 | BMRL | BMRL | 1.8012 | 13.532 | 19.2046 | C9-20 | N | 1998-09-19 | 17:02 | 268.0333 | 20215.074 | 8.5 | 23 | 1.21 | 0.0178 | 1.4711 | 2.87 | 0.88 | 1.99 | 26 | 9.1399 | 47.9 | 99.85 | 6.0799 | 32.5503 | 17.5486 | 26.4931 | 82.6719 | BMRL | 3.7016 | 2.3887 | BMRL | 14.2073 | 7.8615 | BMRL | 2.5102 | 1.9128 | 20.2976 | 28.159 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 17143.9571 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | [7 empty] | BMRL |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | [7 empty] | BMRL |  |  | Avg-C10-10 | Y | 1998-09-15 | 22:08 | 177.1333 | 13359.396 | 8.385 | 21.6 | 1.4375 | 0.02225 | 1.5478 | 3.14 | 0.81 | 2.33 | 26.2 | 9.1525 | 48.1 | 126.725 | 13.4617 | 38.6856 | 26.0661 | 21.8405 | 100.0539 | BMRL | 4.3649 | 1.4773 | BMRL | 7.8653 | 5.8678 | BMRL | BMRL | 1.8523 | 13.7075 | 19.5753 | Avg-C10-20 | Y | 1998-09-25 | 02:43 | 397.7167 | 29995.791 | 8.595 | 21.5 | 1.4025 | 0.021175 | 1.5098 | 3.07 | 0.79 | 2.28 | 26 | 9.2199 | 48 | 121.875 | 11.8773 | 33.9412 | 23.2677 | 23.7693 | 92.8554 | BMRL | 5.4042 | 2.5256 | BMRL | 11.1867 | 7.4152 | BMRL | 2.9363 | 3.1607 | 19.1165 | 26.5317 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 140 | 160 | [7 empty] | 150 | 9.4281 |  | Bromide | mg/L | 140 | 160 | [7 empty] | 150 | 9.4281 |  | C11-10 | N | 1998-09-17 | 10:43 | 213.7167 | 16118.511 | 8.36 | 21.2 | 1.54 | 0.0252 | 1.6364 | 3.26 | 0.9 | 2.36 | 26.2 | 9.1547 | 47.7 | 138.9 | 18.0381 | 38.7359 | 30.346 | 23.0636 | 110.1835 | BMRL | 6.4223 | 2.5505 | BMRL | 9.9783 | 7.6935 | BMRL | BMRL | 2.0002 | 18.9511 | 26.6446 | C11-20 | N | 1998-09-26 | 15:28 | 434.4667 | 32767.476 | 8.55 | 23 | 1.51 | 0.0237 | 1.5695 | 3.17 | 0.64 | 2.53 | 25.7 | 9.1795 | 47.7 | 127.65 | 15.3748 | 35.9531 | 26.7214 | 21.9515 | 100.0008 | BMRL | 5.8251 | 1.8975 | BMRL | 9.2319 | 6.9529 | BMRL | BMRL | 1.9054 | 16.9545 | 23.9073 | Natural Gas Rate ($/ft3) | 0.0058
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-09-19 | 20:30 | 271.5 | 20476.53 | 8.52 | 22.4 | 1.815 | 0.03015 | 1.6612 | 3.54 | 0.92 | 2.62 | 26 | 9.145 | 48 | 160.5 | 26.5402 | 36.8659 | 33.7598 | 18.806 | 115.9719 | BMRL | 10.3989 | 4.0784 | BMRL | 13.6439 | 11.0438 | BMRL | BMRL | 3.4306 | 28.1212 | 39.165 | C12-20 | N | 1998-09-28 | 04:54 | 471.9 | 35590.698 | 8.68 | 22 | 1.52 | 0.0236 | 1.5526 | 3.19 | 0.86 | 2.33 | 24.3 | 9.1799 | 48 | 131.95 | 14.4456 | 34.8039 | 25.8106 | 22.4789 | 97.539 | BMRL | 6.1662 | 1.3973 | BMRL | 9.3139 | 7.0642 | BMRL | BMRL | 1.3806 | 16.8773 | 23.9415 | Current Process Water Rate ($/1000 gal) | 0.43
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 8.4872e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-09-21 | 03:27 | 302.45 | 22810.779 | 8.52 | 21 | 1.85 | 0.03055 | 1.6514 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | [34 empty] | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.084 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD
|  |  |  | Scaling factor, SF | 12.57 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-10 | 1998-09-13 | 1998-09-20 | 1998-09-25 | 1998-09-28 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-09-08 | 1998-09-10 | 1998-09-13 | 1998-09-20 | 1998-09-25 | 1998-09-28 |  |  |  |  | --- | ---
Plant Name | West End Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 8.1841 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 14:15 | 16:28 | 08:30 | 14:50 | 18:13 | 16:00 |  |  |  |  | --- | --- | Sampling time | hh:mm | 14:15 | 16:28 | 08:30 | 14:50 | 18:13 | 16:00 |  |  |  |  | --- | ---
Treatment Plant Category | TS/SOFT |  |  | RSSCT flow rate, QSC (mL/min) | 10.713 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1.25 | 51.4667 | 115.5 | 289.8333 | 413.2167 | 483 |  |  |  |  | --- | --- | Operation time | hh.hh | 1.25 | 51.4667 | 115.5 | 289.8333 | 413.2167 | 483 |  |  |  |  | --- | ---
Process Train Name | North/South Train |  |  | Estimated total influent volume required, VSCT (L) | 438.3351 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 94.275 | 3881.616 | 8711.01 | 21859.23 | 31164.801 | 36427.86 |  |  |  |  | --- | --- | Bed volumes | (10 minute) | 47.1375 | 1940.808 | 4355.505 | 10929.615 | 15582.4005 | 18213.93 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 383 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.97 | 8.92 | 9.12 | 8.97 | 9.01 | NA |  |  |  |  | 8.998 | 0.83685 | pH | --- | 8.97 | 8.92 | 9.12 | 8.97 | 9.01 | NA |  |  |  |  | 8.998 | 0.83685 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.15 | NA | NA | 0.15 | NA | 0.15 |  |  |  |  | 0.15 | 0 | Turbidity | ntu | 0.15 | NA | NA | 0.15 | NA | 0.15 |  |  |  |  | 0.15 | 0 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 0.5 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 16.5 | 17.3 | 17.1 | 17.2 | 18.1 | NA |  |  |  |  | 17.24 | 3.322 | Temperature | oC | 16.5 | 17.3 | 17.1 | 17.2 | 18.1 | NA |  |  |  |  | 17.24 | 3.322
Historical Average Water Temperature (oC) | 17 |  |  | Estimated full-scale run time, tLCT (days) | 119.0553 | [5 empty] | Total organic carbon | mg/L | 2.34 | 2.495 | 2.345 | 2.31 | 2.32 | 2.3 |  |  |  |  | 2.3517 | 3.0742 | Total organic carbon | mg/L | 2.34 | 2.495 | 2.345 | 2.31 | 2.32 | 2.3 |  |  |  |  | 2.3517 | 3.0742 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.79554 | [5 empty] | UV254 | cm-1 | 0.04855 | NA | NA | 0.04755 | NA | 0.04735 |  |  |  |  | 0.047817 | 1.3445 | UV254 | cm-1 | 0.04855 | NA | NA | 0.04755 | NA | 0.04735 |  |  |  |  | 0.047817 | 1.3445 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 9.4714 | [5 empty] | SUVA | L/(mg*m) | 2.0748 | NR | NR | 2.0584 | NR | 2.0587 |  |  |  |  | 2.064 | 0.4537 | SUVA | L/(mg*m) | 2.0748 | NR | NR | 2.0584 | NR | 2.0587 |  |  |  |  | 2.064 | 0.4537 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 10.8514 | [5 empty] | SDS-Cl2 dose | mg/L | 4.6 | NA | NA | 4.3 | NA | 4.2 |  |  |  |  | 4.3667 | 4.7672 | SDS-Cl2 dose | mg/L | 4.6 | NA | NA | 4.3 | NA | 4.2 |  |  |  |  | 4.3667 | 4.7672 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 146.1117 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.1 | NA | NA | 0.91 | NA | 0.83 |  |  |  |  | 0.94667 | 14.6497 | SDS-Free Cl2 residual | mg/L | 1.1 | NA | NA | 0.91 | NA | 0.83 |  |  |  |  | 0.94667 | 14.6497 | C4-10 | Primary | 1998-09-10 | 09:56 | 44.9333 | 3388.872 | 8.55 | 21.4 | 0.455 | 0.00495 | 1.0879 | 2.02 | 0.75 | 1.27 | 26.1 | 9.095 | 48.3 | 38 | BMRL | 14.1085 | 3.5492 | 24.2976 | 41.9553 | BMRL | BMRL | BMRL | BMRL | 5.091 | 1.9874 | BMRL | BMRL | 1.0782 | 5.091 | 7.0784 | C3-20 | Primary | 1998-09-12 | 11:43 | 94.7167 | 7143.531 | 8.73 | 21.7 | 0.405 | 0.0047 | 1.1605 | 1.96 | 0.82 | 1.14 | 26.1 | 9.1547 | 48.3 | 30.6 | BMRL | 11.8215 | 2.6388 | 22.1752 | 36.6355 | BMRL | BMRL | BMRL | BMRL | 4.6788 | 1.6646 | BMRL | BMRL | 1.0624 | 4.6788 | 6.3434
|  |  |  | Mass GAC required, mSC (g) | 3.8267 | [5 empty] | SDS-Cl2 demand | mg/L | 3.5 | NR | NR | 3.39 | NR | 3.37 |  |  |  |  | 3.42 | 2.0468 | SDS-Cl2 demand | mg/L | 3.5 | NR | NR | 3.39 | NR | 3.37 |  |  |  |  | 3.42 | 2.0468 | D-C4-10 | Duplicate | 1998-09-10 | 09:56 | 44.9333 | 3388.872 | 8.52 | 21.3 | 0.465 | 0.00495 | 1.0645 | 2.02 | 0.73 | 1.29 | 26.1 | 9.135 | 48.3 | 37.55 | BMRL | 15.566 | 3.833 | 25.5314 | 44.9303 | BMRL | BMRL | BMRL | BMRL | 4.0198 | 1.61 | BMRL | BMRL | 1.0616 | 4.0198 | 5.6298 | D-C3-10 | Duplicate | 1998-09-12 | 11:43 | 94.7167 | 7143.531 | 8.72 | 21.7 | 0.395 | 0.0046 | 1.1646 | 1.96 | 0.81 | 1.15 | 26.1 | 9.1699 | 48.3 | 28.7 | BMRL | 11.095 | 2.4764 | 21.0396 | 34.611 | BMRL | BMRL | BMRL | BMRL | 3.7523 | 1.2998 | BMRL | BMRL | 1.0481 | 3.7523 | 5.0521
[11 empty] | SDS-Chlorination temp. | oC | 26.2 | NA | NA | 26 | NA | 24.3 |  |  |  |  | 25.5 | 4.0942 | SDS-Chlorination temp. | oC | 26.2 | NA | NA | 26 | NA | 24.3 |  |  |  |  | 25.5 | 4.0942 | Avg-C4-10 | Average | --- | --- | --- | --- | 8.535 | 21.35 | 0.46 | 0.00495 | 1.0762 | 2.02 | 0.74 | 1.28 | 26.1 | 9.115 | 48.3 | 37.775 | BMRL | 14.8373 | 3.6911 | 24.9145 | 43.4428 | BMRL | BMRL | BMRL | BMRL | 4.5554 | 1.7987 | BMRL | BMRL | 1.0699 | 4.5554 | 6.3541 | Avg-C3-20 | Average | --- | --- | --- | --- | 8.725 | 21.7 | 0.4 | 0.00465 | 1.1625 | 1.96 | 0.815 | 1.145 | 26.1 | 9.1623 | 48.3 | 29.65 | BMRL | 11.4582 | 2.5576 | 21.6074 | 35.6232 | BMRL | BMRL | BMRL | BMRL | 4.2156 | 1.4822 | BMRL | BMRL | 1.0553 | 4.2156 | 5.6977
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9.1799 | NA | NA | 9.1599 | NA | 9.11 |  |  |  |  | 9.1499 | 0.39335 | SDS-Chlorination pH | --- | 9.1799 | NA | NA | 9.1599 | NA | 9.11 |  |  |  |  | 9.1499 | 0.39335 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0.35149 | 0.46838 | 2.1739 | 0 | 2.1739 | 0 | 2.7027 | 1.5625 | 0 | 0.43884 | 0 | 1.1913 |  | 9.8234 | 7.6884 | 4.9519 | 6.8482 |  |  |  |  | 23.5144 | 20.9827 |  |  | 1.5504 | 23.5144 | 22.7977 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0.11461 | 0 | 2.5 | 2.1505 | 0.34951 | 0 | 1.227 | 0.87336 | 0 | 0.16528 | 0 | 6.4081 |  | 6.3407 | 6.3479 | 5.2558 | 5.6831 |  |  |  |  | 21.9778 | 24.6159 |  |  | 1.3543 | 21.9778 | 22.6641
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 47.9 | NA | NA | 47.9 | NA | 47.9 |  |  |  |  | 47.9 | 0 | SDS-Incubation time | hours | 47.9 | NA | NA | 47.9 | NA | 47.9 |  |  |  |  | 47.9 | 0 | C7-10 | Primary | 1998-09-12 | 03:22 | 86.3667 | 6513.774 | 8.62 | 21.3 | 0.925 | 0.0136 | 1.4703 | 2.55 | 0.79 | 1.76 | 26.1 | 9.0927 | 48.3 | 76.8 | 3.5462 | 31.1282 | 12.4858 | 30.2013 | 77.3614 | BMRL | 1.5271 | BMRL | BMRL | 7.2092 | 3.6205 | BMRL | BMRL | 1.3275 | 8.7363 | 12.3569 | C7-20 | Primary | 1998-09-16 | 07:26 | 186.4333 | 14060.802 | 8.41 | 21.2 | 0.925 | 0.0131 | 1.4162 | 2.56 | 0.8 | 1.76 | 26.2 | 9.175 | 48.2 | 69.1 | 2.7994 | 29.0959 | 10.2674 | 31.4522 | 73.6149 | BMRL | 1.5686 | BMRL | BMRL | 7.8116 | 3.4267 | BMRL | BMRL | BMRL | 9.3802 | 12.8069
|  |  |  | Estimated full-scale run time, tLCT (days) | 238.1105 | [5 empty] | SDS-TOX | mg Cl- /L | 247.85 | NA | NA | 251 | NA | 265.1 |  |  |  |  | 254.65 | 3.6073 | SDS-TOX | mg Cl- /L | 247.85 | NA | NA | 251 | NA | 265.1 |  |  |  |  | 254.65 | 3.6073 | D-C7-10 | Duplicate | 1998-09-12 | 03:22 | 86.3667 | 6513.774 | 8.63 | 21.2 | 0.945 | 0.01365 | 1.4444 | 2.55 | 0.78 | 1.77 | 26.1 | 9.1399 | 48.3 | 75.9 | 3.2923 | 29.33 | 11.6845 | 28.1967 | 72.5035 | BMRL | 1.5559 | BMRL | BMRL | 6.5375 | 3.3413 | BMRL | BMRL | 1.2901 | 8.0934 | 11.4348 | D-C7-20 | Duplicate | 1998-09-16 | 07:26 | 186.4333 | 14060.802 | 8.41 | 21.1 | 0.925 | 0.01325 | 1.4324 | 2.56 | 0.73 | 1.83 | 26.2 | 9.16 | 48.2 | 72.5 | 2.5791 | 26.1841 | 9.3572 | 27.5204 | 65.6409 | BMRL | 1.5812 | BMRL | BMRL | 7.8904 | 3.7894 | BMRL | BMRL | BMRL | 9.4716 | 13.2609
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5911 | [5 empty] | SDS-CHCl3 | mg/L | 70.9576 | NA | NA | 56.6004 | NA | 53.2822 |  |  |  |  | 60.2801 | 15.5851 | SDS-CHCl3 | mg/L | 70.9576 | NA | NA | 56.6004 | NA | 53.2822 |  |  |  |  | 60.2801 | 15.5851 | Avg-C7-10 | Average | --- | --- | --- | --- | 8.625 | 21.25 | 0.935 | 0.013625 | 1.4574 | 2.55 | 0.785 | 1.765 | 26.1 | 9.1163 | 48.3 | 76.35 | 3.4192 | 30.2291 | 12.0852 | 29.199 | 74.9325 | BMRL | 1.5415 | BMRL | BMRL | 6.8734 | 3.4809 | BMRL | BMRL | 1.3088 | 8.4149 | 11.8958 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.41 | 21.15 | 0.925 | 0.013175 | 1.4243 | 2.56 | 0.765 | 1.795 | 26.2 | 9.1675 | 48.2 | 70.8 | 2.6893 | 27.64 | 9.8123 | 29.4863 | 69.6279 | BMRL | 1.5749 | BMRL | BMRL | 7.851 | 3.608 | BMRL | BMRL | BMRL | 9.4259 | 13.0339
|  |  |  | Estimated RSSCT run time, tSCT (days) | 18.9428 | [5 empty] | SDS-BDCM | mg/L | 38.7549 | NA | NA | 35.7445 | NA | 34.0574 |  |  |  |  | 36.1856 | 6.5761 | SDS-BDCM | mg/L | 38.7549 | NA | NA | 35.7445 | NA | 34.0574 |  |  |  |  | 36.1856 | 6.5761 | RPD-C7-10 | RPD | --- | --- | --- | --- | 0.11594 | 0.47059 | 2.139 | 0.36697 | 1.7721 | 0 | 1.2739 | 0.56657 | 0 | 0.51789 | 0 | 1.1788 | 7.425 | 5.9486 | 6.6302 | 6.8652 | 6.4831 |  | 1.8669 |  |  | 9.7722 | 8.0203 |  |  | 2.8591 | 7.64 | 7.7513 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0 | 0.47281 | 0 | 1.1385 | 1.1385 | 0 | 9.1503 | 3.8997 | 0 | 0.16331 | 0 | 4.8023 | 8.1894 | 10.5347 | 9.2761 | 13.3344 | 11.4523 |  | 0.80233 |  |  | 1.0034 | 10.052 |  |  |  | 0.9698 | 3.4839
|  |  |  | RSSCT bed length, lSC (cm) | 21.7027 | [5 empty] | SDS-DBCM | mg/L | 49.1394 | NA | NA | 42.9604 | NA | 41.3217 |  |  |  |  | 44.4738 | 9.2701 | SDS-DBCM | mg/L | 49.1394 | NA | NA | 42.9604 | NA | 41.3217 |  |  |  |  | 44.4738 | 9.2701 | C10-10 | Primary | 1998-09-15 | 22:08 | 177.1333 | 13359.396 | 8.34 | 21.6 | 1.44 | 0.0223 | 1.5486 | 3.14 | 0.84 | 2.3 | 26.2 | 9.165 | 48.1 | 125.7 | 12.9908 | 37.4589 | 25.4631 | 21.459 | 97.3718 | BMRL | 4.5464 | 1.4667 | BMRL | 7.8472 | 5.9081 | BMRL | BMRL | 1.9034 | 13.8603 | 19.7684 | C10-20 | Primary | 1998-09-25 | 02:43 | 397.7167 | 29995.791 | 8.6 | 21.5 | 1.405 | 0.02125 | 1.5125 | 3.07 | 0.81 | 2.26 | 26 | 9.2199 | 48 | 119.55 | 11.8798 | 33.5742 | 23.0792 | 24.9933 | 93.5265 | BMRL | 6.6313 | 3.4592 | BMRL | 15.3592 | 9.6664 | BMRL | 2.9363 | 3.1607 | 25.4497 | 35.1161
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 292.2234 | [5 empty] | SDS-CHBr3 | mg/L | 12.9823 | NA | NA | 13.0775 | NA | 12.8733 |  |  |  |  | 12.9777 | 0.78738 | SDS-CHBr3 | mg/L | 12.9823 | NA | NA | 13.0775 | NA | 12.8733 |  |  |  |  | 12.9777 | 0.78738 | D-C10-10 | Duplicate | 1998-09-15 | 22:08 | 177.1333 | 13359.396 | 8.43 | 21.6 | 1.435 | 0.0222 | 1.547 | 3.14 | 0.78 | 2.36 | 26.2 | 9.14 | 48.1 | 127.75 | 13.9327 | 39.9123 | 26.669 | 22.222 | 102.736 | BMRL | 4.1835 | 1.488 | BMRL | 7.8834 | 5.8274 | BMRL | BMRL | 1.8013 | 13.5548 | 19.3823 | D-C10-20 | Duplicate | 1998-09-25 | 02:43 | 397.7167 | 29995.791 | 8.59 | 21.5 | 1.4 | 0.0211 | 1.5071 | 3.07 | 0.77 | 2.3 | 26 | 9.22 | 48 | 124.2 | 11.8747 | 34.3082 | 23.4561 | 22.5453 | 92.1843 | BMRL | 4.177 | 1.5919 | BMRL | 7.0143 | 5.164 | BMRL | BMRL | BMRL | 12.7832 | 17.9472
|  |  |  | Mass GAC required, mSC (g) | 7.6533 | [5 empty] | SDS-THM4 | mg/L | 171.8342 | NA | NA | 148.3828 | NA | 141.5346 |  |  |  |  | 153.9172 | 10.3237 | SDS-THM4 | mg/L | 171.8342 | NA | NA | 148.3828 | NA | 141.5346 |  |  |  |  | 153.9172 | 10.3237 | Avg-C10-10 | Average | --- | --- | --- | --- | 8.385 | 21.6 | 1.4375 | 0.02225 | 1.5478 | 3.14 | 0.81 | 2.33 | 26.2 | 9.1525 | 48.1 | 126.725 | 13.4617 | 38.6856 | 26.0661 | 21.8405 | 100.0539 | BMRL | 4.3649 | 1.4773 | BMRL | 7.8653 | 5.8678 | BMRL | BMRL | 1.8523 | 13.7075 | 19.5753 | Avg-C10-20 | Average | --- | --- | --- | --- | 8.595 | 21.5 | 1.4025 | 0.021175 | 1.5098 | 3.07 | 0.79 | 2.28 | 26 | 9.2199 | 48 | 121.875 | 11.8773 | 33.9412 | 23.2677 | 23.7693 | 92.8554 | BMRL | 5.4042 | 2.5256 | BMRL | 11.1867 | 7.4152 | BMRL | 2.9363 | 3.1607 | 19.1165 | 26.5317
[11 empty] | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | RPD-C10-10 | RPD | --- | --- | --- | --- | 1.0733 | 0 | 0.34783 | 0.44944 | 0.10161 | 0 | 7.4074 | 2.5751 | 0 | 0.27284 | 0 | 1.6177 | 6.9972 | 6.3417 | 4.6264 | 3.4937 | 5.3613 |  | 8.3132 | 1.4407 |  | 0.45971 | 1.3754 |  |  | 5.5116 | 2.2281 | 1.9725 | RPD-C10-20 | RPD | --- | --- | --- | --- | 0.11635 | 0 | 0.35651 | 0.70838 | 0.35188 | 0 | 5.0633 | 1.7544 | 0 | 0.0012486 | 0 | 3.8154 | 0.043397 | 2.1626 | 1.6201 | 10.299 | 1.4455 |  | 45.4154 | 73.9362 |  | 74.5961 | 60.7178 |  |  |  | 66.2596 | 64.7108
[11 empty] | SDS-DCAA* | mg/L | 13.2804 | NA | NA | 19.4155 | NA | 14.8543 |  |  |  |  | 15.8501 | 20.1038 | SDS-DCAA* | mg/L | 13.2804 | NA | NA | 19.4155 | NA | 14.8543 |  |  |  |  | 15.8501 | 20.1038 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 3.0025 | NA | NA | 8.3717 | NA | 4.0079 |  |  |  |  | 5.1274 | 55.6682 | SDS-TCAA* | mg/L | 3.0025 | NA | NA | 8.3717 | NA | 4.0079 |  |  |  |  | 5.1274 | 55.6682 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-DBAA* | mg/L | 7.0501 | NA | NA | 14.1908 | NA | 8.4266 |  |  |  |  | 9.8891 | 38.3081 | SDS-DBAA* | mg/L | 7.0501 | NA | NA | 14.1908 | NA | 8.4266 |  |  |  |  | 9.8891 | 38.3081
[11 empty] | SDS-BCAA* | mg/L | 9.6131 | NA | NA | 16.7019 | NA | 11.0466 |  |  |  |  | 12.4539 | 30.0956 | SDS-BCAA* | mg/L | 9.6131 | NA | NA | 16.7019 | NA | 11.0466 |  |  |  |  | 12.4539 | 30.0956
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | 2.0794 | NA | NA | 3.0176 | NA | BMRL |  |  |  |  | 2.5485 | 26.0309 | SDS-CDBAA | mg/L | 2.0794 | NA | NA | 3.0176 | NA | BMRL |  |  |  |  | 2.5485 | 26.0309
[11 empty] | SDS-DCBAA | mg/L | 2.5964 | NA | NA | 5.7665 | NA | 2.6626 |  |  |  |  | 3.6752 | 49.29 | SDS-DCBAA | mg/L | 2.5964 | NA | NA | 5.7665 | NA | 2.6626 |  |  |  |  | 3.6752 | 49.29
[11 empty] | SDS-HAA5 | mg/L | 23.333 | NA | NA | 41.9781 | NA | 27.2888 |  |  |  |  | 30.8666 | 31.8271 | SDS-HAA5 | mg/L | 23.333 | NA | NA | 41.9781 | NA | 27.2888 |  |  |  |  | 30.8666 | 31.8271
[11 empty] | SDS-HAA6 | mg/L | 32.9461 | NA | NA | 58.6799 | NA | 38.3354 |  |  |  |  | 43.3205 | 31.329 | SDS-HAA6 | mg/L | 32.9461 | NA | NA | 58.6799 | NA | 38.3354 |  |  |  |  | 43.3205 | 31.329
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H22: S&H Comment: Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS.
Note on V53: S&H Comment: HAA results for influent B4-20 verified. No reason can be given for the relatively high results.
Note on V54: S&H Comment: HAA results for influent B4-20 verified. No reason can be given for the relatively high results.
Note on AK53: S&H Comment: HAA results for influent B4-20 verified. No reason can be given for the relatively high results.
Note on AK54: S&H Comment: HAA results for influent B4-20 verified. No reason can be given for the relatively high results.
Note on BV5: S&H Comment: It is possible that the high Bromide levels for the 3rd quarter study influenced the high formation of DBAA for this quarter. However, no reason for the higher HAA influent can be given.
Note on DB44: S&H Comment: HAA results verified.
Note on DC44: S&H Comment: HAA results verified.
Note on DE5: S&H Comment: It is possible that the high Bromide levels for the 3rd quarter study influenced the high formation of DBAA for this quarter. However, no reason for the higher HAA influent can be given.
Note on DE44: S&H Comment: HAA results verified.
Note on DF44: S&H Comment: HAA results verified.

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Topeka | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 3.2 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-11-19 | [12 empty] | 20-min. EBCT Start Date | 1998-11-19 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | KS2017701 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 8 | mesh size | (mm) | Rapid mix | 4 mg/L polymer | Full-Scale | 10-min. EBCT Start Time | 15:30 | [12 empty] | 20-min. EBCT Start Time | 15:30 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.395 | 4 | 4.75 | Primary presedimentation | 477 minutes | Full-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 10
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 11 | 6 | 3.35 | Polymer addition | 2 mg/L polymer | Full-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-11-19 | 20:09 | 4.65 | 350.703 | 8.92 | 22.2 | 0.215 | 0.00165 | 0.76744 | 1.52 | 0.82 | 0.7 | 11 | 9.2 | 48 | 2.75 | BMRL | 1.0627 | BMRL | 1.61 | 2.6727 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | C1-20 | N | 1998-11-19 | 20:05 | 4.5833 | 345.675 | 9.05 | 22.2 | 0.125 | 0.00195 | 1.56 | 1.47 | 0.85 | 0.62 | 11 | 9.24 | 48 | 3.55 | BMRL | BMRL | BMRL | 1.16 | 1.16 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Secondary presedimentation | 275 minutes | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-11-21 | 03:43 | 36.2167 | 2731.461 | 8.91 | 21 | 0.405 | 0.00515 | 1.2716 | 1.66 | 0.81 | 0.85 | 11 | 9.2399 | 48 | 19.65 | BMRL | 6.7205 | 2.5623 | 7.6 | 16.8827 | BMRL | 2.2819 | BMRL | BMRL | 2.4298 | 1.273 | BMRL | BMRL | BMRL | 4.7117 | 5.9847 | C2-20 | N | 1998-11-22 | 19:00 | 75.5 | 5694.21 | 8.79 | 21.7 | 0.355 | 0.0054 | 1.5211 | 1.63 | 0.83 | 0.8 | 11.1 | 9.1999 | 48 | 18.05 | BMRL | 6.1172 | 1.9886 | 7.25 | 15.3559 | BMRL | BMRL | BMRL | BMRL | 1.9572 | BMRL | BMRL | BMRL | BMRL | 1.9572 | 1.9572 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.455 | 10 | 2 | Softening | 115 mg/L lime; 8.6 mg/L alum | Full-Scale | Sampling date | MM/DD/YY | 1998-11-19 | 1998-11-30 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-11-19 | 1998-11-30 | [7 empty] | --- | --- |  | Avg-C3-10 | Y | 1998-11-21 | 10:44 | 43.2333 | 3260.658 | 8.83 | 21.2 | 0.5475 | 0.0084 | 1.5342 | 1.75 | 0.745 | 1.005 | 11 | 9.2199 | 48 | 33.75 | 1.531 | 9.8127 | 4.2008 | 9.11 | 24.6545 | BMRL | 6.9094 | BMRL | BMRL | 2.8916 | 1.7425 | BMRL | BMRL | BMRL | 9.801 | 11.5434 | C3-20 | N | 1998-11-23 | 09:07 | 89.6167 | 6758.889 | 8.77 | 21.8 | 0.54 | 0.0082 | 1.5185 | 1.74 | 0.83 | 0.91 | 11.1 | 9.2 | 48 | 33 | 1.1133 | 9.3646 | 3.6036 | 8.98 | 23.0614 | BMRL | 10.1873 | BMRL | BMRL | 3.183 | 1.6995 | BMRL | BMRL | BMRL | 13.3704 | 15.0699 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 140 | 12 | 1.68 | Primary sedimentation | 549 minutes | Full-Scale | Sampling time | hh:mm | 16:45 | 11:15 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 16:45 | 11:15 | [7 empty] | --- | --- |  | C4-10 | N | 1998-11-21 | 17:42 | 50.2 | 3786.084 | 8.8 | 21.4 | 0.67 | 0.0107 | 1.597 | 1.83 | 0.73 | 1.1 | 11.1 | 9.185 | 47.8 | 44.05 | 2.0906 | 13.1321 | 5.9659 | 10.7 | 31.8885 | BMRL | 7.6089 | BMRL | BMRL | 3.2513 | 2.2673 | BMRL | BMRL | 0.81965 | 10.8602 | 13.1275 | Avg-C4-20 | Y | 1998-11-24 | 07:07 | 111.6167 | 8418.129 | 8.795 | 21.9 | 0.745 | 0.011575 | 1.5537 | 1.88 | 0.82 | 1.06 | 11 | 9.1797 | 48.1 | 44.95 | 2.0305 | 12.6699 | 6.1002 | 9.55 | 30.3506 | BMRL | 7.0804 | BMRL | BMRL | 3.8598 | 2.8162 | BMRL | BMRL | BMRL | 10.9402 | 13.7564 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 230 | 16 | 1.18 | Recarbonation | 19 mg/L carbon dioxide | Full-Scale | Operation time | hh.hh | 1.25 | 259.75 | [7 empty] | --- | --- |  | Operation time | hh.hh | 1.25 | 259.75 | [7 empty] | --- | --- |  | C5-10 | N | 1998-11-22 | 00:34 | 57.0667 | 4303.968 | 8.86 | 21.3 | 0.825 | 0.01325 | 1.6061 | 1.94 | 0.85 | 1.09 | 11.1 | 9.205 | 47.9 | 53.25 | 3.2148 | 15.4986 | 8.2658 | 10.2 | 37.1792 | BMRL | 7.4864 | BMRL | BMRL | 4.0754 | 3.4944 | BMRL | BMRL | BMRL | 11.5618 | 15.0562 | C5-20 | N | 1998-11-25 | 13:05 | 141.5833 | 10678.215 | 8.71 | 22.1 | 0.895 | 0.0145 | 1.6201 | 1.97 | 0.84 | 1.13 | 11 | 9.1747 | 48.2 | 55.45 | 3.4976 | 15.764 | 9.097 | 9.57 | 37.9286 | BMRL | 5.3698 | BMRL | BMRL | 4.8001 | 4.0565 | BMRL | BMRL | BMRL | 10.17 | 14.2265 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 | Secondary sedimentation | 236 minutes | Full-Scale | Bed volumes | (10 minutes) | 94.275 | 19590.345 | [7 empty] | --- | --- |  | Bed volumes | (10 minutes) | 47.1375 | 9795.1725 | [7 empty] | --- | --- |  | C6-10 | N | 1998-11-22 | 13:54 | 70.4 | 5309.568 | 8.84 | 21.8 | 1.03 | 0.0172 | 1.6699 | 2.07 | 0.81 | 1.26 | 11.1 | 9.225 | 47.9 | 67.8 | 5.2251 | 17.2313 | 11.1948 | 8.59 | 42.2412 | BMRL | 7.0976 | BMRL | BMRL | 4.7756 | 4.6392 | BMRL | BMRL | 1.2505 | 11.8732 | 16.5124 | C6-20 | N | 1998-11-26 | 11:40 | 164.1667 | 12381.45 | 8.86 | 22.1 | 0.995 | 0.0173 | 1.7387 | 2.05 | 0.87 | 1.18 | 11 | 9.2099 | 48.2 | 65.5 | 5.0331 | 17.5439 | 11.5076 | 8.82 | 42.9046 | BMRL | 6.2194 | BMRL | BMRL | 5.1971 | 4.5704 | BMRL | BMRL | 1.0015 | 11.4165 | 15.9869 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Alkalinity | mg/L as CaCO3 | 51.6 | 52.55 | [7 empty] | 52.075 | 1.29 |  | Alkalinity | mg/L as CaCO3 | 51.6 | 52.55 | [7 empty] | 52.075 | 1.29 |  | C7-10 | N | 1998-11-23 | 03:09 | 83.65 | 6308.883 | 8.9 | 21.6 | 1.21 | 0.0203 | 1.6777 | 2.18 | 0.95 | 1.23 | 11 | 9.2143 | 48.1 | 83 | 7.9037 | 18.0785 | 14.197 | 7.06 | 47.2392 | BMRL | 7.4397 | 2.5703 | BMRL | 5.881 | 5.4508 | BMRL | BMRL | 1.1796 | 15.891 | 21.3418 | Avg-C7-20 | Y | 1998-11-28 | 14:20 | 214.8333 | 16202.73 | 8.665 | 23.15 | 1.205 | 0.021275 | 1.7656 | 2.15 | 0.87 | 1.28 | 11.1 | 9.1821 | 48 | 84.9 | 8.5577 | 18.9376 | 15.0565 | 7.495 | 50.0468 | BMRL | 4.0461 | 6.45 | BMRL | 5.2466 | 4.7842 | BMRL | BMRL | 1.1719 | 15.7428 | 20.527 | Labor Rate + Fringe ($/work-hour) | 21
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 4783.709 | 40 | 0.425 | pH adjustment | 4 mg/L sulfuric acid to pH 9.2 | Bench-Scale | Total hardness | mg/L as CaCO3 | 100 | 101 | [7 empty] | 100.5 | 0.70359 |  | Total hardness | mg/L as CaCO3 | 100 | 101 | [7 empty] | 100.5 | 0.70359 |  | Avg-C8-10 | Y | 1998-11-24 | 00:31 | 105.0167 | 7920.357 | 8.825 | 21.3 | 1.3125 | 0.02335 | 1.779 | 2.26 | 0.79 | 1.47 | 11 | 9.2073 | 48.1 | 96.625 | 10.7177 | 18.2912 | 16.2426 | 6.205 | 51.4565 | BMRL | 8.1253 | 5.9032 | BMRL | 5.6858 | 6.0665 | BMRL | BMRL | 1.671 | 19.7143 | 25.7807 | C8-20 | N | 1998-11-30 | 23:30 | 272 | 20514.24 | 8.62 | 22.5 | 1.36 | 0.0239 | 1.7574 | 2.2 | 0.93 | 1.27 | 11 | 9.1195 | 47.5 | 99.05 | 10.566 | 17.409 | 15.9313 | 5.15 | 49.0564 | BMRL | 5.1864 | 5.9803 | BMRL | 5.8378 | 6.0933 | BMRL | BMRL | 2.4916 | 17.0046 | 23.0979 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 9567.418 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 62 | 63 | [7 empty] | 62.5 | 1.1314 |  | Calcium hardness | mg/L as CaCO3 | 62 | 63 | [7 empty] | 62.5 | 1.1314 |  | C9-10 | N | 1998-11-24 | 15:00 | 119.5 | 9012.69 | 8.73 | 23.9 | 1.52 | 0.02725 | 1.7928 | 2.39 | 0.85 | 1.54 | 11 | 9.205 | 48.1 | 111.85 | 16.4284 | 19.8768 | 19.8405 | 5.11 | 61.2557 | BMRL | 9.1325 | 5.7091 | BMRL | 5.0454 | 6.4552 | BMRL | BMRL | 1.8982 | 19.887 | 26.3422 | C9-20 | N | 1998-12-03 | 09:40 | 330.1667 | 24901.17 | 8.66 | 22.7 | 1.56 | 0.0277 | 1.7756 | 2.27 | 0.55 | 1.72 | 11.1 | 9.1536 | 48.1 | 102.3 | 13.246 | 17.0522 | 16.5705 | 4.38 | 51.2487 | BMRL | 5.8002 | 5.3163 | BMRL | 5.6796 | 6.1074 | BMRL | BMRL | 2.4887 | 16.7961 | 22.9035 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 12437.6434 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | [7 empty] | BMRL |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | [7 empty] | BMRL |  |  | C10-10 | N | 1998-11-26 | 02:11 | 154.6833 | 11666.217 | 8.92 | 21.2 | 1.715 | 0.03155 | 1.8397 | 2.51 | 0.84 | 1.67 | 11 | 9.2095 | 48.1 | 126.5 | 19.2035 | 16.7942 | 19.9659 | 3.51 | 59.4736 | BMRL | 10.4051 | 5.4317 | BMRL | 4.923 | 6.8409 | BMRL | BMRL | 2.7446 | 20.7598 | 27.6006 | Avg-C10-20 | Y | 1998-12-05 | 12:31 | 381.0167 | 28736.277 | 8.76 | 23.2 | 1.6525 | 0.031125 | 1.8835 | 2.32 | 1.175 | 1.145 | 11.1 | 9.2159 | 48.15 | 124.3 | 18.4564 | 16.7233 | 19.1729 | 3.82 | 58.1726 | BMRL | 6.8655 | 5.5465 | BMRL | 4.8901 | 6.4507 | BMRL | BMRL | 2.4531 | 17.3021 | 23.7528 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 81 | 78 | [7 empty] | 79.5 | 2.6683 |  | Bromide | mg/L | 81 | 78 | [7 empty] | 79.5 | 2.6683 |  | Avg-C11-10 | Y | 1998-11-27 | 20:25 | 196.9167 | 14851.455 | 8.74 | 21.85 | 1.91 | 0.0367 | 1.9215 | 2.59 | 0.865 | 1.725 | 11.1 | 9.1943 | 48.1 | 149.25 | 23.936 | 17.4847 | 21.9423 | 3.605 | 66.968 | BMRL | 10.4063 | 6.5362 | BMRL | 4.7346 | 7.5586 | BMRL | BMRL | 2.7067 | 21.6771 | 29.2357 | C11-20 | N | 1998-12-07 | 20:55 | 437.4167 | 32989.965 | 8.62 | 21.4 | 1.875 | 0.03395 | 1.8107 | 2.44 | 1.2 | 1.24 | 11.1 | 9.1647 | 47.9 | 135.25 | 18.9638 | 14.7968 | 18.1889 | 3.31 | 55.2594 | BMRL | 8.8085 | 5.635 | BMRL | 4.4094 | 6.7505 | BMRL | BMRL | 2.8465 | 18.8529 | 25.6034 | Natural Gas Rate ($/ft3) | 0.0058
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-11-29 | 00:21 | 224.85 | 16958.187 | 8.78 | 21.7 | 2.065 | 0.0398 | 1.9274 | 2.7 | 0.8 | 1.9 | 11.1 | 9.2147 | 48.1 | 154.75 | 27.0902 | 17.0793 | 22.7511 | 3.07 | 69.9906 | BMRL | 11.2354 | 7.0313 | BMRL | 4.7859 | 7.9717 | BMRL | BMRL | 2.9511 | 23.0526 | 31.0242 | C12-20 | N | 1998-12-10 | 04:51 | 493.35 | 37208.457 | 8.69 | 22.1 | 2.055 | 0.0396 | 1.927 | 2.05 | 0.82 | 1.23 | 11.2 | 9.2082 | 48.6 | 148.65 | 23.1424 | 14.7858 | 19.9977 | 3.27 | 61.196 | BMRL | 10.1711 | 5.8185 | BMRL | 4.0878 | 7.0995 | BMRL | BMRL | 2.9601 | 20.0773 | 27.1768 | Current Process Water Rate ($/1000 gal) | 0.43
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.2881e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-11-30 | 04:31 | 253.0167 | 19082.517 | 8.85 | 21.4 | 2.18 | 0.04245 | 1.9472 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C13-20 | N | 1998-12-11 | 08:49 | 521.3167 | 39317.703 | 8.55 | 22 | 2.1 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.084 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD
|  |  |  | Scaling factor, SF | 12.57 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-11-19 | 1998-11-21 | 1998-11-25 | 1998-11-30 | 1998-12-06 | 1998-12-10 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-11-19 | 1998-11-21 | 1998-11-25 | 1998-11-30 | 1998-12-06 | 1998-12-10 |  |  |  |  | --- | ---
Plant Name | West End Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 9.8126 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:40 | 13:30 | 13:10 | 11:10 | 14:50 | 10:30 |  |  |  |  | --- | --- | Sampling time | hh:mm | 16:40 | 13:30 | 13:10 | 11:10 | 14:50 | 10:30 |  |  |  |  | --- | ---
Treatment Plant Category | TS/SOFT |  |  | RSSCT flow rate, QSC (mL/min) | 8.2206 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1.1667 | 46 | 141.6667 | 259.6667 | 407.3333 | 499 |  |  |  |  | --- | --- | Operation time | hh.hh | 1.1667 | 46 | 141.6667 | 259.6667 | 407.3333 | 499 |  |  |  |  | --- | ---
Process Train Name | North/South Train |  |  | Estimated total influent volume required, VSCT (L) | 244.0199 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 87.99 | 3469.32 | 10684.5 | 19584.06 | 30721.08 | 37634.58 |  |  |  |  | --- | --- | Bed volumes | (10 minute) | 43.995 | 1734.66 | 5342.25 | 9792.03 | 15360.54 | 18817.29 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 383 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 9.03 | 8.99 | 9.06 | 9.04 | 8.97 | 9.03 |  |  |  |  | 9.02 | 0.37102 | pH | --- | 9.03 | 8.99 | 9.06 | 9.04 | 8.97 | 9.03 |  |  |  |  | 9.02 | 0.37102 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.15 | NA | NA | 0.1 | NA | 0.1 |  |  |  |  | 0.11667 | 24.7436 | Turbidity | ntu | 0.15 | NA | NA | 0.1 | NA | 0.1 |  |  |  |  | 0.11667 | 24.7436 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 0.5 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 19.6 | 17.4 | 18 | 18 | 19.2 | 18.3 |  |  |  |  | 18.4167 | 4.4831 | Temperature | oC | 19.6 | 17.4 | 18 | 18 | 19.2 | 18.3 |  |  |  |  | 18.4167 | 4.4831
Historical Average Water Temperature (oC) | 17 |  |  | Estimated full-scale run time, tLCT (days) | 86.3725 | [5 empty] | Total organic carbon | mg/L | 2.975 | 2.84 | 2.85 | 2.855 | 2.81 | 2.79 |  |  |  |  | 2.8533 | 2.265 | Total organic carbon | mg/L | 2.975 | 2.84 | 2.85 | 2.855 | 2.81 | 2.79 |  |  |  |  | 2.8533 | 2.265 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 60 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.79554 | [5 empty] | UV254 | cm-1 | 0.0645 | NA | NA | 0.0641 | NA | 0.06365 |  |  |  |  | 0.064083 | 0.66358 | UV254 | cm-1 | 0.0645 | NA | NA | 0.0641 | NA | 0.06365 |  |  |  |  | 0.064083 | 0.66358 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 6.8713 | [5 empty] | SUVA | L/(mg*m) | 2.1681 | NR | NR | 2.2452 | NR | 2.2814 |  |  |  |  | 2.2315 | 2.5931 | SUVA | L/(mg*m) | 2.1681 | NR | NR | 2.2452 | NR | 2.2814 |  |  |  |  | 2.2315 | 2.5931 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.0106 | [5 empty] | SDS-Cl2 dose | mg/L | 3.39 | NA | NA | 3.25 | NA | 3.3 |  |  |  |  | 3.3133 | 2.1412 | SDS-Cl2 dose | mg/L | 3.39 | NA | NA | 3.25 | NA | 3.3 |  |  |  |  | 3.3133 | 2.1412 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 81.34 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.86 | NA | NA | 0.68 | NA | 0.91 |  |  |  |  | 0.81667 | 14.8124 | SDS-Free Cl2 residual | mg/L | 0.86 | NA | NA | 0.68 | NA | 0.91 |  |  |  |  | 0.81667 | 14.8124 | C3-10 | Primary | 1998-11-21 | 10:44 | 43.2333 | 3260.658 | 8.83 | 21.2 | 0.555 | 0.0081 | 1.4595 | 1.75 | 0.77 | 0.98 | 11 | 9.2299 | 48 | 34.45 | 1.4915 | 9.7162 | 4.1318 | 9 | 24.3395 | BMRL | 6.8577 | BMRL | BMRL | 2.964 | 1.8068 | BMRL | BMRL | BMRL | 9.8217 | 11.6285 | C4-20 | Primary | 1998-11-24 | 07:07 | 111.6167 | 8418.129 | 8.8 | 21.9 | 0.745 | 0.0115 | 1.5436 | 1.88 | 0.75 | 1.13 | 11 | 9.1847 | 48.1 | 45.85 | 2.0718 | 12.9673 | 6.3582 | 9.52 | 30.9173 | BMRL | 7.3098 | BMRL | BMRL | 4.0313 | 3.0612 | BMRL | BMRL | BMRL | 11.341 | 14.4022
|  |  |  | Mass GAC required, mSC (g) | 2.9756 | [5 empty] | SDS-Cl2 demand | mg/L | 2.53 | NR | NR | 2.57 | NR | 2.39 |  |  |  |  | 2.4967 | 3.7857 | SDS-Cl2 demand | mg/L | 2.53 | NR | NR | 2.57 | NR | 2.39 |  |  |  |  | 2.4967 | 3.7857 | D-C3-10 | Duplicate | 1998-11-21 | 10:44 | 43.2333 | 3260.658 | 8.83 | 21.2 | 0.54 | 0.0087 | 1.6111 | 1.75 | 0.72 | 1.03 | 11 | 9.2099 | 48 | 33.05 | 1.5705 | 9.9092 | 4.2698 | 9.22 | 24.9695 | BMRL | 6.9611 | BMRL | BMRL | 2.8191 | 1.6781 | BMRL | BMRL | BMRL | 9.7803 | 11.4584 | D-C4-10 | Duplicate | 1998-11-24 | 07:07 | 111.6167 | 8418.129 | 8.79 | 21.9 | 0.745 | 0.01165 | 1.5638 | 1.88 | 0.89 | 0.99 | 11 | 9.1747 | 48.1 | 44.05 | 1.9893 | 12.3725 | 5.8422 | 9.58 | 29.784 | BMRL | 6.8511 | BMRL | BMRL | 3.6883 | 2.5713 | BMRL | BMRL | BMRL | 10.5393 | 13.1107
[11 empty] | SDS-Chlorination temp. | oC | 11 | NA | NA | 11.1 | NA | 11.2 |  |  |  |  | 11.1 | 0.9009 | SDS-Chlorination temp. | oC | 11 | NA | NA | 11.1 | NA | 11.2 |  |  |  |  | 11.1 | 0.9009 | Avg-C3-10 | Average | --- | --- | --- | --- | 8.83 | 21.2 | 0.5475 | 0.0084 | 1.5353 | 1.75 | 0.745 | 1.005 | 11 | 9.2199 | 48 | 33.75 | 1.531 | 9.8127 | 4.2008 | 9.11 | 24.6545 | BMRL | 6.9094 | BMRL | BMRL | 2.8916 | 1.7425 | BMRL | BMRL | BMRL | 9.801 | 11.5434 | Avg-C4-20 | Average | --- | --- | --- | --- | 8.795 | 21.9 | 0.745 | 0.011575 | 1.5537 | 1.88 | 0.82 | 1.06 | 11 | 9.1797 | 48.1 | 44.95 | 2.0305 | 12.6699 | 6.1002 | 9.55 | 30.3506 | BMRL | 7.0804 | BMRL | BMRL | 3.8598 | 2.8162 | BMRL | BMRL | BMRL | 10.9402 | 13.7564
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 9.215 | NA | NA | 9.245 | NA | 9.2636 |  |  |  |  | 9.2412 | 0.26545 | SDS-Chlorination pH | --- | 9.215 | NA | NA | 9.245 | NA | 9.2636 |  |  |  |  | 9.2412 | 0.26545 | RPD-C3-10 | RPD | --- | --- | --- | --- | 0 | 0 | 2.7397 | 7.1429 | 9.8778 | 0 | 6.7114 | 4.9751 | 0 | 0.21692 | 0 | 4.1481 | 5.1575 | 1.9663 | 3.2864 | 2.4149 | 2.5552 |  | 1.497 |  |  | 5.0093 | 7.3846 |  |  |  | 0.42255 | 1.4735 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0.1137 | 0 | 0 | 1.2959 | 1.2959 | 0 | 17.0732 | 13.2075 | 0 | 0.10894 | 0 | 4.0044 | 4.0631 | 4.6943 | 8.4592 | 0.62827 | 3.734 |  | 6.4779 |  |  | 8.8868 | 17.3948 |  |  |  | 7.3278 | 9.3887
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 48 | NA | NA | 48.1 | NA | 48.6 |  |  |  |  | 48.2333 | 0.66646 | SDS-Incubation time | hours | 48 | NA | NA | 48.1 | NA | 48.6 |  |  |  |  | 48.2333 | 0.66646 | C8-10 | Primary | 1998-11-24 | 00:31 | 105.0167 | 7920.357 | 8.79 | 21.3 | 1.31 | 0.0233 | 1.7786 | 2.26 | 0.81 | 1.45 | 11 | 9.2199 | 48.1 | 96.05 | 10.6557 | 18.3239 | 16.1433 | 5.84 | 50.9629 | BMRL | 7.8903 | 5.8813 | BMRL | 5.845 | 6.1117 | BMRL | BMRL | 1.8032 | 19.6167 | 25.7283 | C7-20 | Primary | 1998-11-28 | 14:20 | 214.8333 | 16202.73 | 8.66 | 23.1 | 1.205 | 0.0213 | 1.7676 | 2.15 | 0.9 | 1.25 | 11.1 | 9.1895 | 48 | 86.55 | 8.8263 | 19.2593 | 15.3477 | 7.55 | 50.9832 | BMRL | 4.114 | 6.4618 | BMRL | 5.2359 | 4.8358 | BMRL | BMRL | 1.2221 | 15.8117 | 20.6476
|  |  |  | Estimated full-scale run time, tLCT (days) | 172.745 | [5 empty] | SDS-TOX | mg Cl- /L | 263.15 | NA | NA | 245.9 | NA | 249.45 |  |  |  |  | 252.8333 | 3.6028 | SDS-TOX | mg Cl- /L | 263.15 | NA | NA | 245.9 | NA | 249.45 |  |  |  |  | 252.8333 | 3.6028 | D-C8-10 | Duplicate | 1998-11-24 | 00:31 | 105.0167 | 7920.357 | 8.86 | 21.3 | 1.315 | 0.0234 | 1.7795 | 2.26 | 0.77 | 1.49 | 11 | 9.1947 | 48.1 | 97.2 | 10.7797 | 18.2586 | 16.3419 | 6.57 | 51.9502 | BMRL | 8.3602 | 5.9251 | BMRL | 5.5266 | 6.0212 | BMRL | BMRL | 1.5387 | 19.8119 | 25.8331 | D-C7-20 | Duplicate | 1998-11-28 | 14:20 | 214.8333 | 16202.73 | 8.67 | 23.2 | 1.205 | 0.02125 | 1.7635 | 2.15 | 0.84 | 1.31 | 11.1 | 9.1747 | 48 | 83.25 | 8.2892 | 18.6159 | 14.7653 | 7.44 | 49.1104 | BMRL | 3.9782 | 6.4382 | BMRL | 5.2573 | 4.7326 | BMRL | BMRL | 1.1217 | 15.6738 | 20.4064
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5911 | [5 empty] | SDS-CHCl3 | mg/L | 51.5912 | NA | NA | 59.1799 | NA | 48.3483 |  |  |  |  | 53.0398 | 10.4812 | SDS-CHCl3 | mg/L | 51.5912 | NA | NA | 59.1799 | NA | 48.3483 |  |  |  |  | 53.0398 | 10.4812 | Avg-C8-10 | Average | --- | --- | --- | --- | 8.825 | 21.3 | 1.3125 | 0.02335 | 1.779 | 2.26 | 0.79 | 1.47 | 11 | 9.2073 | 48.1 | 96.625 | 10.7177 | 18.2912 | 16.2426 | 6.205 | 51.4565 | BMRL | 8.1253 | 5.9032 | BMRL | 5.6858 | 6.0665 | BMRL | BMRL | 1.671 | 19.7143 | 25.7807 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.665 | 23.15 | 1.205 | 0.021275 | 1.7656 | 2.15 | 0.87 | 1.28 | 11.1 | 9.1821 | 48 | 84.9 | 8.5577 | 18.9376 | 15.0565 | 7.495 | 50.0468 | BMRL | 4.0461 | 6.45 | BMRL | 5.2466 | 4.7842 | BMRL | BMRL | 1.1719 | 15.7428 | 20.527
|  |  |  | Estimated RSSCT run time, tSCT (days) | 13.7426 | [5 empty] | SDS-BDCM | mg/L | 13.3969 | NA | NA | 14.4268 | NA | 12.2525 |  |  |  |  | 13.3587 | 8.1418 | SDS-BDCM | mg/L | 13.3969 | NA | NA | 14.4268 | NA | 12.2525 |  |  |  |  | 13.3587 | 8.1418 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.7932 | 0 | 0.38095 | 0.42827 | 0.047313 | 0 | 5.0633 | 2.7211 | 0 | 0.27309 | 0 | 1.1902 | 1.1573 | 0.35716 | 1.2231 | 11.7647 | 1.9188 |  | 5.7827 | 0.74073 |  | 5.5998 | 1.4911 |  |  | 15.8264 | 0.99015 | 0.40627 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.11541 | 0.43197 | 0 | 0.23502 | 0.23502 | 0 | 6.8966 | 4.6875 | 0 | 0.16117 | 0 | 3.8869 | 6.2764 | 3.3973 | 3.8677 | 1.4676 | 3.7421 |  | 3.3565 | 0.36515 |  | 0.40754 | 2.1569 |  |  | 8.5646 | 0.87645 | 1.1749
|  |  |  | RSSCT bed length, lSC (cm) | 26.0211 | [5 empty] | SDS-DBCM | mg/L | 28.9569 | NA | NA | 31.5932 | NA | 25.1875 |  |  |  |  | 28.5792 | 11.2651 | SDS-DBCM | mg/L | 28.9569 | NA | NA | 31.5932 | NA | 25.1875 |  |  |  |  | 28.5792 | 11.2651 | C11-10 | Primary | 1998-11-27 | 20:25 | 196.9167 | 14851.455 | 8.76 | 21.9 | 1.92 | 0.03675 | 1.9141 | 2.59 | 0.88 | 1.71 | 11.1 | 9.1943 | 48.1 | 153.7 | 24.3424 | 17.7439 | 22.3314 | 3.71 | 68.1277 | BMRL | 10.4453 | 6.6073 | BMRL | 4.9289 | 7.8336 | BMRL | BMRL | 2.7472 | 21.9814 | 29.815 | C10-20 | Primary | 1998-12-05 | 12:31 | 381.0167 | 28736.277 | 8.77 | 23.2 | 1.65 | 0.0311 | 1.8848 | 2.32 | 1.19 | 1.13 | 11.1 | 9.2136 | 48.1 | 125.65 | 19.1396 | 16.744 | 19.8669 | 3.99 | 59.7405 | BMRL | 6.9029 | 5.5601 | BMRL | 4.8799 | 6.4123 | BMRL | BMRL | 2.5213 | 17.3429 | 23.7551
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 162.6799 | [5 empty] | SDS-CHBr3 | mg/L | 1.64 | NA | NA | 1.81 | NA | 1.65 |  |  |  |  | 1.7 | 5.6114 | SDS-CHBr3 | mg/L | 1.64 | NA | NA | 1.81 | NA | 1.65 |  |  |  |  | 1.7 | 5.6114 | D-C11-10 | Duplicate | 1998-11-27 | 20:25 | 196.9167 | 14851.455 | 8.72 | 21.8 | 1.9 | 0.03665 | 1.9289 | 2.59 | 0.85 | 1.74 | 11.1 | 9.1943 | 48.1 | 144.8 | 23.5297 | 17.2254 | 21.5532 | 3.5 | 65.8083 | BMRL | 10.3672 | 6.4652 | BMRL | 4.5404 | 7.2837 | BMRL | BMRL | 2.6663 | 21.3728 | 28.6564 | D-C10-20 | Duplicate | 1998-12-05 | 12:31 | 381.0167 | 28736.277 | 8.75 | 23.2 | 1.655 | 0.03115 | 1.8822 | 2.32 | 1.16 | 1.16 | 11.1 | 9.2182 | 48.2 | 122.95 | 17.7732 | 16.7026 | 18.479 | 3.65 | 56.6047 | BMRL | 6.828 | 5.5329 | BMRL | 4.9004 | 6.4891 | BMRL | BMRL | 2.3848 | 17.2613 | 23.7504
|  |  |  | Mass GAC required, mSC (g) | 5.9512 | [5 empty] | SDS-THM4 | mg/L | 95.585 | NA | NA | 107.0099 | NA | 87.4384 |  |  |  |  | 96.6778 | 10.1693 | SDS-THM4 | mg/L | 95.585 | NA | NA | 107.0099 | NA | 87.4384 |  |  |  |  | 96.6778 | 10.1693 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.74 | 21.85 | 1.91 | 0.0367 | 1.9215 | 2.59 | 0.865 | 1.725 | 11.1 | 9.1943 | 48.1 | 149.25 | 23.936 | 17.4847 | 21.9423 | 3.605 | 66.968 | BMRL | 10.4063 | 6.5362 | BMRL | 4.7346 | 7.5586 | BMRL | BMRL | 2.7067 | 21.6771 | 29.2357 | Avg-C10-20 | Average | --- | --- | --- | --- | 8.76 | 23.2 | 1.6525 | 0.031125 | 1.8835 | 2.32 | 1.175 | 1.145 | 11.1 | 9.2159 | 48.15 | 124.3 | 18.4564 | 16.7233 | 19.1729 | 3.82 | 58.1726 | BMRL | 6.8655 | 5.5465 | BMRL | 4.8901 | 6.4507 | BMRL | BMRL | 2.4531 | 17.3021 | 23.7528
[11 empty] | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.45767 | 0.45767 | 1.0471 | 0.27248 | 0.77465 | 0 | 3.4682 | 1.7391 | 0 | 0 | 0 | 5.9631 | 3.3954 | 2.965 | 3.5469 | 5.8252 | 3.4635 |  | 0.74992 | 2.1742 |  | 8.205 | 7.2753 |  |  | 2.9907 | 2.8077 | 3.9627 | RPD-C10-20 | RPD | --- | --- | --- | --- | 0.22831 | 0 | 0.30257 | 0.16064 | 0.14193 | 0 | 2.5532 | 2.6201 | 0 | 0.049581 | 0.20768 | 2.1722 | 7.4036 | 0.24731 | 7.239 | 8.9005 | 5.3904 |  | 1.0902 | 0.49026 |  | 0.41987 | 1.1913 |  |  | 5.565 | 0.4711 | 0.019638
[11 empty] | SDS-DCAA* | mg/L | 21.0631 | NA | NA | 21.3685 | NA | 19.982 |  |  |  |  | 20.8045 | 3.5016 | SDS-DCAA* | mg/L | 21.0631 | NA | NA | 21.3685 | NA | 19.982 |  |  |  |  | 20.8045 | 3.5016 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 9.6351 | NA | NA | 10.6077 | NA | 8.1533 |  |  |  |  | 9.4653 | 13.058 | SDS-TCAA* | mg/L | 9.6351 | NA | NA | 10.6077 | NA | 8.1533 |  |  |  |  | 9.4653 | 13.058 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-DBAA* | mg/L | 2.8758 | NA | NA | 3.3961 | NA | 2.8264 |  |  |  |  | 3.0327 | 10.4069 | SDS-DBAA* | mg/L | 2.8758 | NA | NA | 3.3961 | NA | 2.8264 |  |  |  |  | 3.0327 | 10.4069
[11 empty] | SDS-BCAA* | mg/L | 8.5572 | NA | NA | 9.3489 | NA | 8.0547 |  |  |  |  | 8.6536 | 7.5401 | SDS-BCAA* | mg/L | 8.5572 | NA | NA | 9.3489 | NA | 8.0547 |  |  |  |  | 8.6536 | 7.5401
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-CDBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-DCBAA | mg/L | 3.7982 | NA | NA | 3.9002 | NA | 3.7131 |  |  |  |  | 3.8038 | 2.4616 | SDS-DCBAA | mg/L | 3.7982 | NA | NA | 3.9002 | NA | 3.7131 |  |  |  |  | 3.8038 | 2.4616
[11 empty] | SDS-HAA5 | mg/L | 33.5739 | NA | NA | 35.3723 | NA | 30.9617 |  |  |  |  | 33.3026 | 6.6594 | SDS-HAA5 | mg/L | 33.5739 | NA | NA | 35.3723 | NA | 30.9617 |  |  |  |  | 33.3026 | 6.6594
[11 empty] | SDS-HAA6 | mg/L | 42.1312 | NA | NA | 44.7212 | NA | 39.0164 |  |  |  |  | 41.9563 | 6.8081 | SDS-HAA6 | mg/L | 42.1312 | NA | NA | 44.7212 | NA | 39.0164 |  |  |  |  | 41.9563 | 6.8081
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H22: S&H Comment: Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS.
Note on BS5: S&H Comment: Based on the breakthrough of SDS-DCAA, preformed DCAA may have been present in the influent water. This was not confirmed through analysis of instantaneous DBPs or chlorine residual monitoring of the treatment study influent . Recarbonation feeds (which contain chlorinated plant finished water) were on during quarter 3 sampling, and filter washwater is not returned to the head of the plant.
Note on DB5: S&H Comment: Based on the breakthrough of SDS-DCAA, preformed DCAA may have been present in the influent water. This was not confirmed through analysis of instantaneous DBPs or chlorine residual monitoring of the treatment study influent . Recarbonation feeds (which contain chlorinated plant finished water) were on during quarter 3 sampling, and filter washwater is not returned to the head of the plant.