## NF70. 1st Quarter
FIELD-SET 1: Membrane A, Run 1 (FILE: Margate1.xls) | [70 empty] | 0.69
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [21 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) |  | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.86384 | [45 empty] | Recovery during sample collection (decimal) | 0.689 | [10 empty] | Recovery during sample collection (decimal) | 0.882 | [7 empty] | Recovery during sample collection (decimal) | 0.47 | [7 empty] | Recovery during sample collection (decimal) | 0.298 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | NF70 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 15.8 | [10 empty] | Feed flow rate during sample collection (mL/min) | 12.3 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 36.5 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 226.5485 | 226.5485 | 226.5485 | 226.5485 | SDS-THM4F, ug/L | 226.5485 | 226.5485 | 226.5485 | 226.5485 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 135.2 | 135.2 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 18.4265 | 32.86 | 12.344 | 7.299 | SDS-THM4p, ug/L | 18.4265 | 32.86 | 12.344 | 7.299 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.59 | 6.79 | 6.69 | 2.9895 | 1998-11-17 | 10:55 | 0.5 | 24.2 | 84.9 | 84.3 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.1947 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 83.9232 | 0.27638 | 1998-11-23 | 0:00 | [47 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 116.903 | 116.903 | 116.903 | 116.903 | SDS-HAA5F, ug/L | 116.903 | 116.903 | 116.903 | 116.903 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32671 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1998-11-17 | 17:55 | 6.5 | 25.8 | 66.5 | 65.8 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.1232 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.4732 | 0.3379 | 1998-11-23 | 17:05 | 2 | 25.3 | 72 | 70.9 | 600 | 9.9252 | 4.9015 |  | 14.8268 | 0.45405 | 0.66941 | 39.4674 | 22.6538 | 20.5484 | 1127.4136 | 151.3127 | 1111.2669 | 9.6803 | 61.7697 | 0.33266 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.312 | 6.646 | 3.738 | 0 | SDS-HAA5p, ug/L | 2.312 | 6.646 | 3.738 | 0 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative charge | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 147 | 148 | 147.5 | 0.67797 | 1998-11-17 | 19:35 | 9.1 | 24.3 | 68.8 | 66.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.1262 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 66.8232 | 0.34608 | 1998-11-24 | 9:00 | 17.8 | 26.2 | 97.1 | 96.5 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 21.8632 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 86.7214 | 0.25211 | 6.46 | 6.91 | 7.39 | 136.75 | 460.92 | 1654.45 | 1220.1877 | 26.2481 | 71.1498 | 1210.3962 | 88.702 | 0.009 | 0.018 | 0.09 | 0.87639 | -873.7697 | 96.7742 | 0.86855 | 98.9638 | [8 empty] | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-01 | --- | --- | 1998-12-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-02 | 1998-12-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-03 | 1998-12-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-08 | 1998-12-08 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 722.25 | 722.25 | 722.25 | 722.25 | SDS-TOXF, ug Cl- /L | 722.25 | 722.25 | 722.25 | 722.25 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 469 | 479 | 474 | 2.1097 | 1998-11-18 | 9:30 | 23.2 | 25.4 | 72.8 | 72.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3864 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 71.8232 | 0.31169 | 1998-11-24 | 15:05 | 23.8 | 26.5 | 90.2 | 89.9 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 21.6702 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 79.9714 | 0.27097 | 6.39 | 6.95 | 7.4 | 138.938 | 467.13 | 1711.5 | 1215.3467 | 28.9894 | 70.6882 | 1205.6186 | 88.4758 | 0.009 | 0.018 | 0.09 | 0.87639 | -873.7697 | 96.7742 | 0.86855 | 98.9638 | [8 empty] | Sampling time | hh:mm | 8:40 | 8:40 | --- | --- | 8:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 21:15 | 21:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:55 | 17:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:30 | 11:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 32.15 | 68.9 | 29.8 | BMRL | SDS-TOXp, ug Cl- /L | 32.15 | 68.9 | 29.8 | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 295 | 295 | 295 | 0 | 1998-11-18 | 13:40 | 27.1 | 24.9 | 71.7 | 71 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.7197 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 70.6732 | 0.32148 | 1998-11-24 | 17:05 | 25.8 | 26.2 | 96.6 | 96.1 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 21.8632 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 86.2714 | 0.25342 | [27 empty] | Operation time | hh.hh | 65.4 | 65.4 | --- | --- | 65.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101.4 | 101.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 121.9 | 121.9 | --- | --- | --- | --- | --- | Cumulative time | hr | 161.5 | 157.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 10.685 | 10.685 | 10.685 | 10.685 | SDS-CDF, mg/L | 10.685 | 10.685 | 10.685 | 10.685 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 25 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 279 | 279 | 279 | 0 | 1998-11-18 | 16:30 | 30 | 25.5 | 71.8 | 71.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3203 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 70.8232 | 0.31516 | 1998-11-25 | 9:10 | 41.9 | 25.7 | 102.1 | 101.4 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.1887 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 91.6714 | 0.24205 | 6.36 | 7.02 | 7.36 | 132.921 | 517.5 | 1858.2 | 1228.6597 | 33.879 | 71.9576 | 1218.7569 | 89.0937 | 0.009 | 0.018 | 0.09 | 0.87639 | -873.7697 | 96.7742 | 0.86855 | 98.9638 | [8 empty] | pH | --- | 7.45 | 7.6 | 7.525 | 1.9934 | 7.99 | --- | --- | --- | --- | --- | pH | --- | 7.26 | 8.01 | --- | --- | --- | --- | --- | pH | --- | 6.38 | 6.86 | --- | --- | --- | --- | --- | pH | --- | 5.96 | 6.95 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.86 | 3.35 | 1.89 | 1.33 | SDS-CDp, mg/L | 3.86 | 3.35 | 1.89 | 1.33 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 25 | 14.3517 | 90.8732 | 531.2481 | 10.952 | 15.6457 | 4.6937 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.4 | 0.36 | 0.38 | 10.5263 | 1998-11-19 | 10:30 | 48 | 24.5 | 62.8 | 61.9 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.9899 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 61.6732 | 0.37277 | 1998-11-25 | 14:00 | 46.6 | 25.5 | 102.1 | 101.6 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3203 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 91.7714 | 0.24322 | 6.38 | 7.04 | 7.36 | 132.921 | 547.86 | 1638.15 | 1228.6597 | 24.9971 | 71.9576 | 1218.7569 | 89.0937 | 0.009 | 0.018 | 0.045 | 0.87639 | -1847.5394 | 96.7742 | 0.86855 | 98.9638 | [8 empty] | Temperature | oC | 24.4 | 24.4 | 24.4 | 0 | 24.4 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 26.3 | 26.3 | --- | --- | --- | --- | --- | Temperature | oC | 23.2 | 23.2 | --- | --- | --- | --- | --- | TOCF, mg/L | 9.695 | 9.695 | 9.695 | 9.695 | TOCF, mg/L | 9.695 | 9.695 | 9.695 | 9.695 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.357 | 2 | 0.9 | 25 | 39.785 | 116.3065 | 531.2481 | 10.952 | 12.1689 | 1.2169 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.63 | 0.64 | 0.635 | 1.5748 | 1998-11-19 | 12:20 | 49.8 | 24.6 | 68.5 | 67.8 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.922 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.4732 | 0.33972 | 1998-11-25 | 15:00 | 47.7 | 26.3 | 102.6 | 101.8 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 21.7987 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 92.1214 | 0.23663 | [27 empty] | Alkalinity | mg/L as CaCO3 | 130 | 131 | 130.5 | 0.76628 | 577 | 185.1624 | 67.9095 | 11.5254 | 184.6665 | 29.3321 | Alkalinity | mg/L as CaCO3 | 66 | 1080 | 756.678 | 29.9372 | 55.2542 | 750.4339 | 91.2051 | Alkalinity | mg/L as CaCO3 | 28.5 | 263 | 253.0283 | 3.7915 | 80.678 | 251.164 | 88.6528 | Alkalinity | mg/L as CaCO3 | 19 | 197 | 202.0484 | -2.5627 | 87.1186 | 200.3893 | 90.5185 | TOCp, mg/L | 0.755 | 1.14 | 0.52 | 0.6 | TOCp, mg/L | 0.755 | 1.14 | 0.52 | 0.6 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 25 | 9.265 | 85.7865 | 531.2481 | 10.952 | 21.9039 | 10.952 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 9.72 | 9.67 | 9.695 | 0.51573 | 1998-11-19 | 15:55 | 53.1 | 25 | 68.6 | 67.4 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.6526 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.3232 | 0.33648 | 1998-11-30 | 16:30 | 49.2 | 24.8 | 97.9 | 97 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.7869 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 87.3714 | 0.26081 | [27 empty] | Total dissolved solids | mg/L | 339 | 337 | 338 | 0.59172 | 1826 | 775.299 | 57.5411 | 28.692 | 771.3319 | 56.1797 | Total dissolved solids | mg/L | 260 | NA | 2073.5593 | #VALUE! | 45.1477 | 2057.1638 | 87.3612 | Total dissolved solids | mg/L | 87 | NA | 817.1887 | #VALUE! | 81.6456 | 811.1257 | 89.2742 | Total dissolved solids | mg/L | 51.5 | NR | 653.3519 | #VALUE! | 89.135 | 647.8966 | 92.0512 | UV254 F, cm-1 | 0.279 | 0.279 | 0.279 | 0.279 | UV254 F, cm-1 | 0.279 | 0.279 | 0.279 | 0.279 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 25 | 7.085 | 83.6065 | 531.2481 | 10.952 | 36.5066 | 25.5546 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.28 | 0.278 | 0.279 | 0.71685 | 1998-11-20 | 9:15 | 70.3 | 24.5 | 66.5 | 65.7 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.9899 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.4232 | 0.3514 | 1998-12-01 | 0:00 | 57 | 24.8 | 99 | 98.2 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.7869 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 88.5214 | 0.25742 | [27 empty] | Total hardness | mg/L as CaCO3 | 222 | 213 | 217.5 | 4.1379 | 1010 | 466.6961 | 53.7925 | 26.2712 | 464.4355 | 53.169 | Total hardness | mg/L as CaCO3 | 121 | 2160 | 1595.5763 | 26.1307 | 58.9831 | 1582.2454 | 92.3526 | Total hardness | mg/L as CaCO3 | 46 | 512 | 515.8113 | -0.7444 | 84.4068 | 511.9103 | 91.0141 | Total hardness | mg/L as CaCO3 | 21.5 | 378 | 411.1011 | -8.7569 | 92.7119 | 407.5697 | 94.7248 | UV254 p, cm-1 | 0.01 | 0.025 | 0.012 | BMRL | UV254 p, cm-1 | 0.01 | 0.025 | 0.012 | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 600 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 2.8807 | 2.8749 | 2.8778 | 0.20112 | 1998-11-20 | 11:30 | 72.6 | 25.2 | 66.9 | 66.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.5191 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.8732 | 0.34186 | 1998-12-01 | 8:40 | 65.4 | 24.4 | 98 | 97.3 | 600 | 10.845 | 4.9015 |  | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.058 | 1174.4654 | 157.4148 | 1156.0822 | 10.0786 | 87.5714 | 0.2633 | 7.45 |  | 7.99 | 338.046 |  | 1825.6 | 774.8071 | 57.5588 | 28.6823 | 770.8599 | 56.1469 | 0.01 |  | 1.116 | 0.87418 | 21.6684 | 96.4158 | 0.86637 | 98.8458 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 214 | 206 | 210 | 3.8095 | 958 | 431.865 | 54.9202 | 24.7312 | 429.8522 | 51.146 | Calcium hardness | mg/L as CaCO3 | 115 | 2040 | 1504.8305 | 26.2338 | 58.7814 | 1492.2657 | 92.2936 | Calcium hardness | mg/L as CaCO3 | 43.4 | 484 | 487.9283 | -0.81163 | 84.4444 | 484.2372 | 91.0375 | Calcium hardness | mg/L as CaCO3 | 19.5 | 357 | 389.1581 | -9.0079 | 93.0108 | 385.8075 | 94.9457 | BromideF, ug/L | 184.5 | 184.5 | 184.5 | 184.5 | BromideF, ug/L | 184.5 | 184.5 | 184.5 | 184.5 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 185 | 184 | 184.5 | 0.54201 | 1998-11-20 | 14:00 | 75.1 | 25.4 | 66.5 | 66 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3864 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.5732 | 0.3414 | 1998-12-01 | 15:25 | 71.7 | 25.1 | 89.7 | 89.2 | 600 | 10.845 | 1.4506 |  | 12.2956 | 0.45405 | 0.88202 | 47.7981 | 24.7531 | 22.5858 | 2006.8258 | 268.977 | 1975.4142 | 17.2214 | 72.2286 | 0.3127 | [27 empty] | Turbidity | ntu | 0.03 | 0.05 | 0.04 | 50 | 0.23 | 1.1332 | -392.7163 | 89.4737 | 1.1233 | 96.4392 | Turbidity | ntu | 0.17 | 3 | 1.9497 | 35.0113 | 55.2632 | 1.9336 | 91.208 | Turbidity | ntu | 0.01 | 0.32 | 0.70811 | -121.2854 | 97.3684 | 0.70232 | 98.5761 | Turbidity | ntu | BMRL | 0.28 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 171 | 137 | 50.2 | 38.1 | Bromidep, ug/L | 171 | 137 | 50.2 | 38.1 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 24.7 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12 | 12 | 12 | 0 | 1998-11-21 | 14:25 | 99.2 | 24.2 | 68.6 | 68.1 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.1947 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.6732 | 0.34275 | 1998-12-01 | 18:20 | 74.5 | 24.7 | 116.4 | 115.6 | 600 | 10.845 | 1.4506 |  | 12.2956 | 0.45405 | 0.88202 | 47.7981 | 24.7531 | 22.8544 | 2006.8258 | 268.977 | 1975.4142 | 17.2214 | 98.7786 | 0.23137 | [27 empty] | Ammonia | mg NH3-N / L | 0.55 | 0.64 | 0.595 | 15.1261 | 1.2 | 0.72362 | 39.6986 | 6.2992 | 0.72245 | 17.6414 | Ammonia | mg NH3-N / L | 0.43 | NA | 2.1673 | #VALUE! | 32.2835 | 2.1516 | 80.0147 | Ammonia | mg NH3-N / L | 0.24 | NA | 0.98528 | #VALUE! | 62.2047 | 0.97909 | 75.4876 | Ammonia | mg NH3-N / L | 0.19 | 0.44 | 0.8239 | -87.2507 | 70.0787 | 0.81816 | 76.7771 | AlkF, mg/L CaCO3 | 147.5 | 147.5 | 147.5 | 147.5 | AlkF, mg/L CaCO3 | 147.5 | 147.5 | 147.5 | 147.5
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.33 | 1.3 | 1.315 | 2.2814 | 1998-11-22 | 9:40 | 118.4 | 23.9 | 68.4 | 67.7 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.4013 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.3732 | 0.34734 | 1998-12-02 | 9:30 | 89.8 | 25.4 | 132.1 | 131.5 | 600 | 10.845 | 1.4506 |  | 12.2956 | 0.45405 | 0.88202 | 47.7981 | 24.7531 | 22.3864 | 2006.8258 | 268.977 | 1975.4142 | 17.2214 | 114.5786 | 0.19538 | 6.63 |  |  | 324.8 |  |  | 1589.4728 |  | 31.4768 | 1578.0434 | 79.4175 | 0.036 |  |  | 2.0958 |  | 87.0968 | 2.0771 | 98.2668 | [8 empty] | Total organic carbon | mg/L | 0.5 | 1.01 | 0.755 | 67.5497 | 36.4 | 29.501 | 18.9533 | 92.2125 | 29.2402 | 97.4179 | Total organic carbon | mg/L | 1.14 | 53.5 | 73.64 | -37.6449 | 88.2414 | 72.9846 | 98.438 | Total organic carbon | mg/L | 0.52 | 19.5 | 17.8313 | 8.5573 | 94.6364 | 17.6876 | 97.0601 | Total organic carbon | mg/L | 0.6 | 12.8 | 13.5558 | -5.905 | 93.8112 | 13.4384 | 95.5352 | Alkp, mg/L CaCO3 | 130.5 | 66 | 28.5 | 19 | Alkp, mg/L CaCO3 | 130.5 | 66 | 28.5 | 19
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 10.67 | 10.7 | 10.685 | 0.28077 | [21 empty] | 1998-12-02 | 12:15 | 92.4 | 25.9 | 133.3 | 132.8 | 600 | 10.845 | 1.4506 |  | 12.2956 | 0.45405 | 0.88202 | 47.7981 | 24.7531 | 22.0579 | 2006.8258 | 268.977 | 1975.4142 | 17.2214 | 115.8286 | 0.19044 | 6.68 | 7.3 | 7.91 | 340.8 | 496.11 | 3219.25 | 1469.8511 | 54.3418 | 28.1013 | 1459.6473 | 76.6519 | 0.051 | 0.274 | 3.66 | 1.9836 | 45.803 | 81.7204 | 1.9661 | 97.4061 | [8 empty] | UV254 | cm-1 | 0.01 | 0.01 | 0.01 | 0 | 1.116 | 0.87495 | 21.5993 | 96.4158 | 0.86711 | 98.8467 | UV254 | cm-1 | 0.025 | 3.325 | 2.1775 | 34.51 | 91.0394 | 2.1581 | 98.8416 | UV254 | cm-1 | 0.012 | 0.559 | 0.51577 | 7.7328 | 95.6989 | 0.51159 | 97.6544 | UV254 | cm-1 | BMRL | 0.381 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 23 | 23 | 23 | 0 | [21 empty] | 1998-12-02 | 16:20 | 96.5 | 24.7 | 148.1 | 147.5 | 600 | 10.845 | 1.4506 |  | 12.2956 | 0.45405 | 0.88202 | 47.7981 | 24.7531 | 22.8544 | 2006.8258 | 268.977 | 1975.4142 | 17.2214 | 130.5786 | 0.17502 | 6.84 |  |  | 274.4 |  |  | 1966.2814 |  | 42.1097 | 1950.991 | 85.9354 | 0.028 |  |  | 2.1556 |  | 89.9642 | 2.1363 | 98.6893 | [8 empty] | SUVA | L/(mg*m) | 2 | 0.9901 | 1.495 | 67.5497 | 3.0659 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.193 | 6.215 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.3077 | 2.8667 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.9766 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 217.5 | 121 | 46 | 21.5 | T-Hdp, mg/L CaCO3 | 217.5 | 121 | 46 | 21.5
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.54 | 7.52 | 7.53 | 0.2656 | [21 empty] | 1998-12-02 | 21:15 | 101.4 | [19 empty] | 7.26 |  | 8.01 | 260 |  | 3235.55 | 474 | 85.3502 | 45.1477 |  |  | 0.025 |  | 3.32 | 0.279 | 91.5964 | 91.0394 | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L | 167 | 175 | 171 | 4.6784 | --- | 214.4084 | --- | 7.3171 | 214.0146 | 20.0989 | Bromide | mg/L | 137 | --- | 539.5424 | --- | 25.7453 | 535.9032 | 74.4357 | Bromide | mg/L | 50.2 | --- | 303.5962 | --- | 72.7913 | 301.4922 | 83.3495 | Bromide | mg/L | 38.1 | --- | 246.647 | --- | 79.3496 | 244.7567 | 84.4335 | Ca-HdF, mg/L CaCO3 | 279 | 279 | 279 | 279 | Ca-HdF, mg/L CaCO3 | 279 | 279 | 279 | 279
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 23.6333 | 23.6167 | 23.625 | 0.070547 | [21 empty] | 1998-12-02 | 22:20 | 102.7 | 24.5 | 148.7 | 148 | 600 | 10.845 | 1.4506 |  | 12.2956 | 0.45405 | 0.88202 | 47.7981 | 24.7531 | 22.9899 | 2006.8258 | 268.977 | 1975.4142 | 17.2214 | 131.1286 | 0.17532 | [27 empty] | SDS-Cl2 dose | mg/L | 4.5 | 4.5 | 4.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 210 | 115 | 43.4 | 19.5 | Ca-Hdp, mg/L CaCO3 | 210 | 115 | 43.4 | 19.5
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.54 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 731.5 | 713 | 722.25 | 2.5614 | [21 empty] | 1998-12-02 | 22:30 | 102.8 | 24.5 | 135.1 | 134 | 600 | 10.845 | 11.2676 |  | 22.1126 | 0.45405 | 0.49044 | 26.1338 | 24.7531 | 22.9899 | 823.9303 | 110.4323 | 811.0339 | 7.0705 | 127.4795 | 0.18034 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.7 | 0.58 | 0.64 | 18.75 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.15 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.61 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.17 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 15 | [14 empty] | SDS-CHCl3 | mg/L | 165.737 | 167.04 | 166.3885 | 0.78311 | [21 empty] | 1998-12-03 | 8:50 | 113 | 25.7 | 138.5 | 137.6 | 600 | 10.845 | 11.2676 |  | 22.1126 | 0.45405 | 0.49044 | 26.1338 | 24.7531 | 22.1887 | 823.9303 | 110.4323 | 811.0339 | 7.0705 | 130.9795 | 0.16941 | 6.35 |  |  | 63.8979 |  |  | 868.7192 |  | 86.5194 | 861.4456 | 92.5825 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 3.8 | 3.92 | 3.86 | 3.1088 | --- | 25.8053 | --- | 63.8746 | 25.6063 | 84.9256 | SDS-Cl2 demand | mg/L | 3.35 | --- | 65.511 | --- | 68.6476 | 64.9491 | 94.8421 | SDS-Cl2 demand | mg/L | 1.89 | --- | 18.4843 | --- | 82.3117 | 18.3466 | 89.6983 | SDS-Cl2 demand | mg/L | 1.33 | --- | 14.6562 | --- | 87.5526 | 14.5354 | 90.8499 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | 10 | [14 empty] | SDS-BDCM | mg/L | 47.693 | 52.154 | 49.9235 | 8.9357 | [21 empty] | 1998-12-03 | 12:55 | 117.2 | 26.1 | 142.8 | 142.2 | 600 | 10.845 | 11.2676 |  | 22.1126 | 0.45405 | 0.49044 | 26.1338 | 24.7531 | 21.9279 | 823.9303 | 110.4323 | 811.0339 | 7.0705 | 135.4295 | 0.16191 | 6.43 | 7.17 | 7.02 | 61.3734 | 496.8 | 1022.01 | 871.149 | 14.7612 | 87.052 | 863.8306 | 92.8952 | BMRL | 0.303 | 0.565 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 23 | 23 | 23 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 74.2586 | 79.7923 | 72.15 | 70.4898 | Qp/QT (THM4), % | 91.5562 | 98.3788 | 88.9563 | 86.9094
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | 95% | [14 empty] | SDS-DBCM | mg/L | 9.871 | 10.602 | 10.2365 | 7.1411 | [21 empty] | 1998-12-03 | 15:15 | 119.5 | 26.3 | 165.7 | 143 | 600 | 10.845 | 11.2676 |  | 22.1126 | 0.45405 | 0.49044 | 26.1338 | 24.7531 | 21.7987 | 823.9303 | 110.4323 | 811.0339 | 7.0705 | 147.2795 | 0.14801 | 6.44 |  |  | 89.8161 |  |  | 843.7732 |  | 81.0515 | 836.9593 | 89.2688 | 0.011 |  |  | 0.53695 |  | 96.0573 | 0.53219 | 97.9331 | [8 empty] | SDS-Chlorination pH | --- | 7.49 | 7.55 | 7.52 | 0.79787 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.46 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.51 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 2000 ppm MgSO4 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [21 empty] | 1998-12-03 | 17:55 | 121.9 | [19 empty] | 6.38 |  | 6.86 | 86.955 |  | 1010.6 | 474 | 53.0972 | 81.6551 |  |  | 0.012 |  | 0.559 | 0.279 | 50.0894 | 95.6989 | #DIV/0! | #DIV/0! | [8 empty] | SDS-Incubation time | hours | 23.6167 | 23.6 | 23.6083 | 0.070597 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.5833 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.5833 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.6 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 31.8093 | 28.9264 | 35.2545 | 34.4983 | SDS-HAA5b, ug/L | 11.9879 | 8.4334 | 16.2355 | 15.3033
|  | Variability of rejection of reference solute (%) | 3 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 223.301 | 229.796 | 226.5485 | 2.8669 | [21 empty] | 1998-12-03 | 22:00 | 126.1 | 24.2 | 144.2 | 143.9 | 600 | 9.9252 | 11.2676 |  | 21.1929 | 0.45405 | 0.46833 | 27.3114 | 22.6538 | 21.2275 | 797.272 | 107.0036 | 785.8536 | 6.8456 | 137.2044 | 0.15471 | [27 empty] | SDS-TOX | mg Cl- /L | 31 | 33.3 | 32.15 | 7.154 | --- | 2251.1211 | --- | 95.5486 | 2230.9909 | 98.5589 | SDS-TOX | mg Cl- /L | 68.9 | --- | 5605.7644 | --- | 90.4604 | 5555.7084 | 98.7598 | SDS-TOX | mg Cl- /L | 29.8 | --- | 1336.3094 | --- | 95.874 | 1325.4611 | 97.7517 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 209.7913 | 200.927 | 222.6475 | #VALUE! | SDS-TOXb, ug Cl- /L | 90.421 | 79.4918 | 106.2718 | #VALUE!
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 2.694 | 5.838 | 4.266 | 73.699 | [21 empty] | 1998-12-07 | 16:00 | 138 | 23.2 | 91.9 | 91.1 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 23.8905 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 86.0204 | 0.27773 | [27 empty] | SDS-CHCl3 | mg/L | 1.699 | 1.682 | 1.6905 | 1.0056 | --- | 531.2661 | --- | 98.984 | 526.4618 | 99.6789 | SDS-CHCl3 | mg/L | 7.333 | --- | 1355.261 | --- | 95.5928 | 1343.075 | 99.454 | SDS-CHCl3 | mg/L | 3.311 | --- | 311.0044 | --- | 98.0101 | 308.4495 | 98.9266 | SDS-CHCl3 | mg/L | 2.234 | --- | 236.0723 | --- | 98.6574 | 233.9528 | 99.0451 | SDS-CDb, mg/L | 5.6169 | 4.8322 | 4.3394 | 4.0907 | SDS-CDb, mg/L | 4.4363 | 3.4689 | 2.8613 | 2.5546
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 38.838 | 33.604 | 36.221 | 14.4502 | [21 empty] | 1998-12-08 | 9:00 | 155 | 23.2 | 88.8 | 88 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 23.8905 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 82.9204 | 0.28811 |  |  |  | 55.6592 |  |  | 651.2183 |  | 88.2576 | 645.8359 | 91.3818 | [16 empty] | SDS-BDCM | mg/L | 3.926 | 3.914 | 3.92 | 0.30612 | --- | 151.8412 | --- | 92.148 | 150.4993 | 97.3953 | SDS-BDCM | mg/L | 11.574 | --- | 336.5698 | --- | 76.8165 | 333.6316 | 96.5309 | SDS-BDCM | mg/L | 4.596 | --- | 90.1196 | --- | 90.7939 | 89.4095 | 94.8596 | SDS-BDCM | mg/L | 2.866 | --- | 69.8995 | --- | 94.2592 | 69.2919 | 95.8639 | TOCb, mg/L | 3.0563 | 2.8688 | 3.0752 | 3.284 | TOCb, mg/L | 1.5099 | 1.2787 | 1.5333 | 1.7906
|  | Acceptable range of operating pressures | <250 psi | [14 empty] | SDS-TCAA* | mg/L | 72.51 | 76.17 | 74.34 | 4.9233 | [21 empty] | 1998-12-08 |  | 159.1 | [22 empty] | 67.9056 |  | 730.24 | 474 | 35.0898 | 85.6739 | [18 empty] | SDS-DBCM | mg/L | 7.492 | 8.151 | 7.8215 | 8.4255 | --- | 15.5868 | --- | 23.592 | 15.5163 | 49.5918 | SDS-DBCM | mg/L | 12.014 | --- | -3.0496 | --- | -17.3643 | -2.9134 | 512.3737 | SDS-DBCM | mg/L | 4.437 | --- | 15.3795 | --- | 56.6551 | 15.2886 | 70.9784 | SDS-DBCM | mg/L | 2.199 | --- | 13.6484 | --- | 78.518 | 13.5447 | 83.7648 | UV254 b, cm-1 | 0.079244 | 0.076328 | 0.08636 | #VALUE! | UV254 b, cm-1 | 0.032714 | 0.029118 | 0.041487 | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [14 empty] | SDS-MBAA* | mg/L | BMRL | 1.294 | 1.294 | #VALUE! | [21 empty] | 1998-12-08 | 15:00 | 161 | 23.1 | 90.3 | 89.5 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 23.9612 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 84.4204 | 0.28383 |  |  |  | 56.2784 |  |  | 650.956 |  | 88.1269 | 645.5816 | 91.2825 | [16 empty] | SDS-CHBr3 | mg/L | 4.371 | 5.618 | 4.9945 | 24.9675 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.939 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 174.4751 | 146.5987 | 87.6026 | 81.303 | Bromideb, ug/L | 172.1399 | 137.7701 | 65.0316 | 57.2646
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | 1.44 | 1.418 | 1.429 | 1.5395 | [21 empty] | 1998-12-08 | 15:30 | 161.5 |  |  |  |  | . | . | [13 empty] | 5.96 |  | 6.95 | 51.5312 |  | 650.37 | 474 | 27.1184 | 89.1284 |  |  | BMRL |  | 0.381 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 17.488 | 19.365 | 18.4265 | 10.1864 | --- | 687.6291 | --- | 91.8664 | 681.5582 | 97.2964 | SDS-THM4 | mg/L | 32.86 | --- | 1674.288 | --- | 85.4954 | 1659.4486 | 98.0198 | SDS-THM4 | mg/L | 12.344 | --- | 416.5034 | --- | 94.5513 | 413.1476 | 97.0122 | SDS-THM4 | mg/L | 7.299 | --- | 319.6202 | --- | 96.7782 | 316.7893 | 97.6959 | Alkb, mg/L CaCO3 | 134.876 | 82.4693 | 61.6415 | 56.9206 | Alkb, mg/L CaCO3 | 131.9355 | 67.3212 | 41.6419 | 35.8214
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.477 | 8.214 | 8.3455 | 3.1514 | [21 empty] | 1998-12-15 | 19:05 | 167.5 | 20 | 115.6 | 114.9 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 26.2606 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 109.7704 | 0.23923 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 237.4496 | 156.1614 | 115.3466 | 102.2104 | T-Hdb, mg/L CaCO3 | 224.044 | 123.8208 | 73.4987 | 57.3027
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [21 empty] | 1998-12-15 | 23:59 | 172.5 | 22.6 | 134.7 | 134.6 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 24.318 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 129.1704 | 0.18826 | [27 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 2.281 | --- | 289.9081 | --- | 93.7025 | 287.3078 | 99.2061 | SDS-DCAA* | mg/L | 1.428 | --- | 67.0752 | --- | 96.0575 | 66.5301 | 97.8536 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 227.7616 | 148.1406 | 109.0147 | 96.079 | Ca-Hdb, mg/L CaCO3 | 215.8263 | 117.6587 | 69.4188 | 53.47
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hrs | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [21 empty] | 1998-12-16 | 8:20 | 180.8 | 22.8 | 136.2 | 135.4 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 24.1747 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 130.3204 | 0.1855 |  |  |  | 48.5728 |  |  | 654.2202 |  | 89.7526 | 648.7467 | 92.5128 | BMDL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 2.408 | --- | 612.0012 | --- | 96.7608 | 606.4902 | 99.603 | SDS-TCAA* | mg/L | 1.207 | --- | 139.1938 | --- | 98.3764 | 138.048 | 99.1257 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [23 empty] | 183.9 | [6 empty] | X | [15 empty] | 46.9904 |  |  | 474 |  | 90.0864 |  |  | BMDL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 115.482 | 118.324 | 116.903 | 2.4311 | [21 empty] | 1998-12-16 | 13:40 | 186.1 | 24.3 | 116.4 | 115.9 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 23.1262 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 110.6704 | 0.20896 |  |  |  | 49.8112 |  |  | 653.6956 |  | 89.4913 | 648.238 | 92.3159 | BMDL | 0.29 | 0.409 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | 2.162 | 2.462 | 2.312 | 12.9758 | --- | -0.52723 | --- | -61.7915 | -0.50147 | 561.0433 | SDS-DBAA* | mg/L | 1.957 | --- | -2.5176 | --- | -36.9489 | -2.4771 | 179.0029 | SDS-DBAA* | mg/L | 1.103 | --- | 1.7181 | --- | 22.8132 | 1.713 | 35.6096 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 123.959 | 126.538 | 125.2485 | 2.0591 | [21 empty] | 1998-12-16 | 15:30 | 188 | [22 empty] | 37.7024 | 491.28 | 719.645 | 474 | 34.1342 | 92.0459 |  |  | BMDL |  | 0.427 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | 1.444 | 1.456 | 1.45 | 0.82759 | --- | 23.622 | --- | 82.6254 | 23.4209 | 93.8089 | SDS-BCAA* | mg/L | 2.517 | --- | 51.9111 | --- | 69.84 | 51.4645 | 95.1093 | SDS-BCAA* | mg/L | 1.529 | --- | 14.3903 | --- | 81.6787 | 14.2835 | 89.2954 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 54.8935 | 57.0513 | 55.5852 | 53.8079 | Qp/QT (HAA5), % | 78.4556 | 81.5395 | 79.4442 | 76.9039
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [26 empty] | 1998-12-16 | 19:50 | 192.2 | 24.5 | 118.1 | 117.3 | 600 | 10.845 | 25.6007 |  | 36.4457 | 0.45405 | 0.29757 | 15.4629 | 24.7531 | 22.9899 | 638.5413 | 85.5844 | 628.5466 | 5.4796 | 112.2204 | 0.20486 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 112.3031 | 116.0468 | 107.4825 | 108.575 | SDS-THM4b, ug/L | 63.2652 | 68.6159 | 56.3755 | 57.937
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 343.43 | 349.5056 | 337.3502 | #VALUE! | SDS-TOXb, ug Cl- /L | 180.8282 | 189.5117 | 172.1388 | #VALUE!
[94 empty] | SDS-HAA5 | mg/L | 2.162 | 2.462 | 2.312 | 12.9758 | --- | 370.7718 | --- | 98.0223 | 367.4292 | 99.3708 | SDS-HAA5 | mg/L | 6.646 | --- | 941.0274 | --- | 94.3149 | 932.5801 | 99.2874 | SDS-HAA5 | mg/L | 3.738 | --- | 217.2569 | --- | 96.8025 | 215.4839 | 98.2653 | SDS-HAA5 | mg/L | 0 | --- | 166.5285 | --- | 100 | 165.019 | 100 | SDS-CDb, mg/L | 6.9385 | 6.5003 | 5.7963 | 5.6513 | SDS-CDb, mg/L | 5.3304 | 4.7041 | 3.6979 | 3.4906
[94 empty] | SDS-HAA6 | mg/L | 3.606 | 3.918 | 3.762 | 8.2935 | --- | 394.3938 | --- | 96.9964 | 390.8501 | 99.0375 | SDS-HAA6 | mg/L | 9.163 | --- | 992.9384 | --- | 92.6841 | 984.0446 | 99.0688 | SDS-HAA6 | mg/L | 5.267 | --- | 231.6472 | --- | 95.7948 | 229.7675 | 97.7077 | SDS-HAA6 | mg/L | 0 | --- | 178.4167 | --- | 100 | 176.7995 | 100 | TOCb, mg/L | 4.7875 | 4.8143 | 4.5951 | 4.8012 | TOCb, mg/L | 2.6811 | 2.7193 | 2.406 | 2.7006
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.13134 | 0.13409 | 0.13059 | #VALUE! | UV254 b, cm-1 | 0.067955 | 0.07189 | 0.066884 | #VALUE!
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 177.0894 | 157.4007 | 109.8491 | 105.7253 | Bromideb, ug/L | 173.9085 | 145.7687 | 77.8065 | 71.9126
[133 empty] | Alkb, mg/L CaCO3 | 138.1681 | 101.0032 | 81.3536 | 78.3569 | Alkb, mg/L CaCO3 | 134.1626 | 81.0453 | 52.9614 | 48.6785
[133 empty] | T-Hdb, mg/L CaCO3 | 252.4575 | 195.7308 | 156.5928 | 147.8355 | T-Hdb, mg/L CaCO3 | 234.1969 | 153.1213 | 97.184 | 84.6678
[133 empty] | Ca-Hdb, mg/L CaCO3 | 241.1235 | 185.4359 | 148.0413 | 139.3686 | Ca-Hdb, mg/L CaCO3 | 224.8657 | 145.2752 | 91.8295 | 79.4343
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on CD7: TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Note on CY16: C. Rice: Consultant stated that the TDS, alkalinity, calcium hardness, total hardness and bromide data for the 70% run was verified by the laboratory.
Note on CY17: C. Rice: Consultant stated that the TDS, alkalinity, calcium hardness, total hardness and bromide data for the 70% run was verified by the laboratory.
Note on CY18: C. Rice: Consultant stated that the TDS, alkalinity, calcium hardness, total hardness and bromide data for the 70% run was verified by the laboratory.
Note on CY19: C. Rice: Consultant stated that the TDS, alkalinity, calcium hardness, total hardness and bromide data for the 70% run was verified by the laboratory.
Note on CY25: C. Rice: Consultant stated that the TDS, alkalinity, calcium hardness, total hardness and bromide data for the 70% run was verified by the laboratory.
Print All Fields

## NF200. 1st Quarter
FIELD-SET 2: Membrane B, Run 1 (FILE: Margate1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.6103 | [45 empty] | Recovery during sample collection (decimal) | 0.708 | [10 empty] | Recovery during sample collection (decimal) | 0.873 | [7 empty] | Recovery during sample collection (decimal) | 0.479 | [7 empty] | Recovery during sample collection (decimal) | 0.298 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 12.8 | [10 empty] | Feed flow rate during sample collection (mL/min) | 10.4 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 30.3 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 226.5485 | 226.5485 | 226.5485 | 226.5485 | SDS-THM4F, ug/L | 226.5485 | 226.5485 | 226.5485 | 226.5485 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 135.2 | 135.2 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 20.199 | 52.694 | 29.327 | 23.472 | SDS-THM4p, ug/L | 20.199 | 52.694 | 29.327 | 23.472 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.59 | 6.79 | 6.69 | 2.9895 | 1998-11-17 | 10:55 | 0.5 | 24.2 | 84.9 | 84.3 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.1947 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 83.9232 | 0.27638 | 1998-11-23 | 15:05 | 0 |  |  |  |  | . | . | [40 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 116.903 | 116.903 | 116.903 | 116.903 | SDS-HAA5F, ug/L | 116.903 | 116.903 | 116.903 | 116.903 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.2599 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1998-11-17 | 17:55 | 6.5 | 25.8 | 66.5 | 65.8 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.1232 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.4732 | 0.3379 | 1998-11-23 | 17:05 | 2.1 | 24.7 | 91.8 | 90.9 | 600 | 8.6954 | 3.7259 |  | 12.4213 | 0.45405 | 0.70004 | 47.3043 | 19.8468 | 18.3244 | 831.0872 | 320.9928 | 823.6948 | 5.064 | 86.286 | 0.21237 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 7.2785 | 12.511 | 6.886 | 5.196 | SDS-HAA5p, ug/L | 7.2785 | 12.511 | 6.886 | 5.196 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Highly Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 147 | 148 | 147.5 | 0.67797 | 1998-11-17 | 19:35 | 9.1 | 24.3 | 68.8 | 66.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.1262 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 66.8232 | 0.34608 | 1998-11-24 | 9:00 | 17.8 | 24.8 | 106 | 105.1 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 18.9932 | 838.526 | 323.7502 | 830.7705 | 5.109 | 100.441 | 0.1891 | 7 | 6.91 | 7.29 | 263.704 | 460.92 | 1263.15 | 984.2061 | 22.0832 | 44.3662 | 978.7787 | 73.0579 | 0.009 | 0.018 | 0.09 | 0.93406 | -937.8399 | 96.7742 | 0.92709 | 99.0292 | [8 empty] | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-01 | --- | --- | 1998-12-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-02 | 1998-12-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-03 | 1998-12-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-08 | 1998-12-08 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 722.25 | 722.25 | 722.25 | 722.25 | SDS-TOXF, ug Cl- /L | 722.25 | 722.25 | 722.25 | 722.25 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 469 | 479 | 474 | 2.1097 | 1998-11-18 | 9:30 | 23.2 | 25.4 | 72.8 | 72.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3864 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 71.8232 | 0.31169 | 1998-11-24 | 15:05 | 23.9 | 25.6 | 102.5 | 101.8 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 18.5493 | 838.526 | 323.7502 | 830.7705 | 5.109 | 97.041 | 0.19115 | 6.81 | 6.95 | 7.34 | 257.516 | 467.13 | 1108.364 | 999.219 | 9.8474 | 45.6717 | 993.6319 | 74.0834 | 0.009 | 0.018 | 0.09 | 0.93406 | -937.8399 | 96.7742 | 0.92709 | 99.0292 | [8 empty] | Sampling time | hh:mm | 8:40 | 8:40 | --- | --- | 8:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:02 | 19:02 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:40 | 17:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:30 | 11:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 51.275 | 110 | 62.35 | 41.3 | SDS-TOXp, ug Cl- /L | 51.275 | 110 | 62.35 | 41.3 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 295 | 295 | 295 | 0 | 1998-11-18 | 13:40 | 27.1 | 24.9 | 71.7 | 71 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.7197 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 70.6732 | 0.32148 | 1998-11-24 | 17:05 | 25.9 | 25.2 | 98.9 | 98.1 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 18.7699 | 838.526 | 323.7502 | 830.7705 | 5.109 | 93.391 | 0.20098 | [27 empty] | Operation time | hh.hh | 65.5 | 65.5 | --- | --- | 65.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101.6 | 101.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122.1 | 122.1 | --- | --- | --- | --- | --- | Cumulative time | hr | 161.8 | 157.7 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 10.685 | 10.685 | 10.685 | 10.685 | SDS-CDF, mg/L | 10.685 | 10.685 | 10.685 | 10.685 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 279 | 279 | 279 | 0 | 1998-11-18 | 16:30 | 30 | 25.5 | 71.8 | 71.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3203 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 70.8232 | 0.31516 | 1998-11-25 | 9:10 | 42 | 24.9 | 99 | 98.4 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 18.9371 | 838.526 | 323.7502 | 830.7705 | 5.109 | 93.591 | 0.20234 | 6.72 | 7.02 | 7.4 | 279.888 | 517.5 | 1163.702 | 944.9416 | 18.7987 | 40.9519 | 939.9318 | 70.2225 | 0.009 | 0.018 | 0.09 | 0.93406 | -937.8399 | 96.7742 | 0.92709 | 99.0292 | [8 empty] | pH | --- | 7.31 | 7.34 | 7.325 | 0.40956 | 8.07 | --- | --- | --- | --- | --- | pH | --- | 7.32 | 7.81 | --- | --- | --- | --- | --- | pH | --- | 6.65 | 6.95 | --- | --- | --- | --- | --- | pH | --- | 6.63 | 6.96 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.445 | 4.39 | 3.97 | 3.56 | SDS-CDp, mg/L | 3.445 | 4.39 | 3.97 | 3.56 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 21.1 | 14.3517 | 95.5367 | 344.1283 | 9.2435 | 13.2049 | 3.9615 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.4 | 0.36 | 0.38 | 10.5263 | 1998-11-19 | 10:30 | 48 | 24.5 | 62.8 | 61.9 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.9899 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 61.6732 | 0.37277 | 1998-11-25 | 14:00 | 46.7 | 24.7 | 105.9 | 105.5 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 19.0494 | 838.526 | 323.7502 | 830.7705 | 5.109 | 100.591 | 0.18937 | 6.75 | 7.04 | 7.4 | 276.556 | 547.86 | 1055.432 | 953.0254 | 9.7028 | 41.6549 | 947.9297 | 70.8253 | 0.009 | 0.018 | 0.09 | 0.93406 | -937.8399 | 96.7742 | 0.92709 | 99.0292 | [8 empty] | Temperature | oC | 24.2 | 24.2 | 24.2 | 0 | 24.2 | --- | --- | --- | --- | --- | Temperature | oC | 25.2 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 26.9 | 26.9 | --- | --- | --- | --- | --- | Temperature | oC | 23.2 | 23.2 | --- | --- | --- | --- | --- | TOCF, mg/L | 9.695 | 9.695 | 9.695 | 9.695 | TOCF, mg/L | 9.695 | 9.695 | 9.695 | 9.695 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 21.1 | 39.785 | 120.97 | 344.1283 | 9.2435 | 10.2705 | 1.0271 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.63 | 0.64 | 0.635 | 1.5748 | 1998-11-19 | 12:20 | 49.8 | 24.6 | 68.5 | 67.8 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.922 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.4732 | 0.33972 | 1998-11-25 | 15:00 | 47.8 | 25.2 | 106 | 105.5 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 18.7699 | 838.526 | 323.7502 | 830.7705 | 5.109 | 100.641 | 0.1865 | [27 empty] | Alkalinity | mg/L as CaCO3 | 45 | 44 | 44.5 | 2.2472 | 400 | 397.2397 | 0.69007 | 69.8305 | 394.5758 | 88.7221 | Alkalinity | mg/L as CaCO3 | 134 | 320 | 240.2992 | 24.9065 | 9.1525 | 239.495 | 44.0489 | Alkalinity | mg/L as CaCO3 | 120 | 203 | 172.7831 | 14.8852 | 18.6441 | 172.3849 | 30.3883 | Alkalinity | mg/L as CaCO3 | 86 | 179.5 | 173.6068 | 3.2831 | 41.6949 | 172.9476 | 50.274 | TOCp, mg/L | 0.825 | 1.88 | 1.16 | 0.85 | TOCp, mg/L | 0.825 | 1.88 | 1.16 | 0.85 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 21.1 | 9.265 | 90.45 | 344.1283 | 9.2435 | 18.4869 | 9.2435 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 9.72 | 9.67 | 9.695 | 0.51573 | 1998-11-19 | 1555 | 53.1 | 25 | 68.6 | 67.4 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.6526 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.3232 | 0.33648 | 1998-11-30 | 16:30 | 49.4 | 23.7 | 103.1 | 102.7 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 19.6209 | 838.526 | 323.7502 | 830.7705 | 5.109 | 97.791 | 0.20064 | [27 empty] | Total dissolved solids | mg/L | 116 | 127 | 121.5 | 9.0535 | 1236 | 1328.6918 | -7.4993 | 74.3671 | 1319.5751 | 90.7925 | Total dissolved solids | mg/L | 374 | NA | 1161.4016 | #VALUE! | 21.097 | 1155.4441 | 67.6315 | Total dissolved solids | mg/L | 414 | NA | 529.1631 | #VALUE! | 12.6582 | 528.2943 | 21.6346 | Total dissolved solids | mg/L | 200 | 235 | 590.3134 | -151.1972 | 57.8059 | 587.3765 | 65.9503 | UV254 F, cm-1 | 0.279 | 0.279 | 0.279 | 0.279 | UV254 F, cm-1 | 0.279 | 0.279 | 0.279 | 0.279 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 21.1 | 7.085 | 88.27 | 344.1283 | 9.2435 | 30.8115 | 21.5681 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.28 | 0.278 | 0.279 | 0.71685 | 1998-11-20 | 21960:00 | 70.3 | 24.5 | 66.5 | 65.7 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.9899 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.4232 | 0.3514 | 1998-12-01 | 0:00 | 57.1 | 24.3 | 114.8 | 114.3 | 600 | 9.9252 | 3.7259 |  | 13.6511 | 0.45405 | 0.72706 | 42.9526 | 22.6538 | 21.1648 | 856.5348 | 330.3988 | 847.8314 | 5.2178 | 109.3322 | 0.19358 | [27 empty] | Total hardness | mg/L as CaCO3 | 76.4 | 76 | 76.2 | 0.52493 | 783 | 825.5151 | -5.4298 | 74.1695 | 819.8562 | 90.7057 | Total hardness | mg/L as CaCO3 | 238 | 832 | 686.8189 | 17.4497 | 19.322 | 683.4231 | 65.1753 | Total hardness | mg/L as CaCO3 | 215 | 418 | 368.5509 | 11.8299 | 27.1186 | 367.3924 | 41.4795 | Total hardness | mg/L as CaCO3 | 102 | 366 | 376.9288 | -2.986 | 65.4237 | 374.8601 | 72.7898 | UV254 p, cm-1 | 0.0175 | 0.038 | 0.018 | 0.016 | UV254 p, cm-1 | 0.0175 | 0.038 | 0.018 | 0.016 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 2.8807 | 2.8749 | 2.8778 | 0.20112 | 1998-11-20 | 1130 | 72.6 | 25.2 | 66.9 | 66.2 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.5191 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.8732 | 0.34186 | 1998-12-01 | 8:40 | 65.5 | 24.2 | 111.3 | 110.9 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 19.333 | 838.526 | 323.7502 | 830.7705 | 5.109 | 105.991 | 0.1824 | 7.31 |  | 8.07 | 121.38 |  | 1235.882 | 1329.5031 | -7.5752 | 74.3924 | 1320.4024 | 90.8073 | 0.017 |  | 1.71 | 0.91465 | 46.5119 | 93.9068 | 0.90789 | 98.1275 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 72.4 | 72.1 | 72.25 | 0.41522 | 716 | 780.2979 | -8.9802 | 74.1039 | 774.9508 | 90.6768 | Calcium hardness | mg/L as CaCO3 | 227 | 751 | 636.4488 | 15.2532 | 18.638 | 633.3509 | 64.1589 | Calcium hardness | mg/L as CaCO3 | 206 | 392 | 346.1152 | 11.7053 | 26.1649 | 345.0581 | 40.2999 | Calcium hardness | mg/L as CaCO3 | 99.3 | 344 | 355.2829 | -3.2799 | 64.4086 | 353.3568 | 71.8981 | BromideF, ug/L | 184.5 | 184.5 | 184.5 | 184.5 | BromideF, ug/L | 184.5 | 184.5 | 184.5 | 184.5 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 185 | 184 | 184.5 | 0.54201 | 1998-11-20 | 1400 | 75.1 | 25.4 | 66.5 | 66 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 22.3864 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 65.5732 | 0.3414 | 1998-12-01 | 15:25 | 72 | 24.9 | 111.5 | 111.2 | 600 | 9.0394 | 3.7259 |  | 12.7653 | 0.45405 | 0.70813 | 46.0024 | 20.632 | 18.9371 | 838.526 | 323.7502 | 830.7705 | 5.109 | 106.241 | 0.17825 | [27 empty] | Turbidity | ntu | 0.01 | 0.05 | 0.03 | 133.3333 | 0.44 | 1.2286 | -179.2341 | 92.1053 | 1.2196 | 97.5401 | Turbidity | ntu | 0.14 | 0.59 | 2.0298 | -244.0278 | 63.1579 | 2.0155 | 93.0537 | Turbidity | ntu | 0.04 | 0.36 | 0.69259 | -92.3864 | 89.4737 | 0.68767 | 94.1832 | Turbidity | ntu | BMRL | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 78.081 | 181 | 175 | 173.6 | Bromidep, ug/L | 78.081 | 181 | 175 | 173.6 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12 | 12 | 12 | 0 | 1998-11-21 | 1425 | 99.2 | 24.2 | 68.6 | 68.1 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.1947 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.6732 | 0.34275 | 1998-12-01 | 18:20 | 74.7 | 24.6 | 106.6 | 106.1 | 600 | 9.0394 | 1.3191 |  | 10.3585 | 0.45405 | 0.87266 | 56.9233 | 20.632 | 19.1058 | 1020.9539 | 394.1846 | 1011.5111 | 6.2205 | 100.1295 | 0.19081 | [27 empty] | Ammonia | mg NH3-N / L | 0.42 | 0.48 | 0.45 | 13.3333 | 0.75 | 1.0836 | -44.4749 | 29.1339 | 1.0788 | 58.2861 | Ammonia | mg NH3-N / L | 0.54 | NA | 1.288 | #VALUE! | 14.9606 | 1.2824 | 57.8905 | Ammonia | mg NH3-N / L | 0.51 | NA | 0.74992 | #VALUE! | 19.685 | 0.74811 | 31.8285 | Ammonia | mg NH3-N / L | 0.44 | NA | 0.71778 | #VALUE! | 30.7087 | 0.71569 | 38.5207 | AlkF, mg/L CaCO3 | 147.5 | 147.5 | 147.5 | 147.5 | AlkF, mg/L CaCO3 | 147.5 | 147.5 | 147.5 | 147.5
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.33 | 1.3 | 1.315 | 2.2814 | 1998-11-22 | 22560:00 | 118.4 | 23.9 | 68.4 | 67.7 | 600 | 10.845 | 4.9015 | 15.7465 | 0.45405 | 0.68872 | 37.1036 | 24.7531 | 23.4013 | 97.0373 | 28.7408 | 95.8028 | 0.67679 | 67.3732 | 0.34734 | 1998-12-02 | 9:30 | 90 | 24.5 | 136.8 | 136.1 | 600 | 9.0394 | 1.3191 |  | 10.3585 | 0.45405 | 0.87266 | 56.9233 | 20.632 | 19.1624 | 1020.9539 | 394.1846 | 1011.5111 | 6.2205 | 130.2295 | 0.14714 | 6.91 |  |  | 413.036 |  |  | 891.7704 |  | 12.8616 | 888.1641 | 53.4955 | 0.025 |  |  | 2.0196 |  | 91.0394 | 2.0046 | 98.7529 | [8 empty] | Total organic carbon | mg/L | 0.93 | 0.72 | 0.825 | 25.4545 | 61 | 31.2017 | 48.8497 | 91.4905 | 30.9723 | 97.3363 | Total organic carbon | mg/L | 1.88 | 108 | 63.4154 | 41.282 | 80.6086 | 62.9499 | 97.0135 | Total organic carbon | mg/L | 1.16 | 23.5 | 17.542 | 25.3534 | 88.0351 | 17.4184 | 93.3404 | Total organic carbon | mg/L | 0.85 | 12.4 | 13.4497 | -8.4654 | 91.2326 | 13.3549 | 93.6353 | Alkp, mg/L CaCO3 | 44.5 | 134 | 120 | 86 | Alkp, mg/L CaCO3 | 44.5 | 134 | 120 | 86
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 10.67 | 10.7 | 10.685 | 0.28077 | [21 empty] | 1998-12-02 | 12:15 | 92.7 | 25.1 | 138.7 | 139.1 | 600 | 9.0394 | 1.3191 |  | 10.3585 | 0.45405 | 0.87266 | 56.9233 | 20.632 | 18.8255 | 1020.9539 | 394.1846 | 1011.5111 | 6.2205 | 132.6795 | 0.14189 | 7.1 | 7.3 | 7.8 | 448.188 | 496.11 | 1346.558 | 650.8829 | 51.6632 | 5.4456 | 649.356 | 30.9796 | 0.035 | 0.274 | 4.17 | 1.9511 | 53.2118 | 87.4552 | 1.9366 | 98.1927 | [8 empty] | UV254 | cm-1 | 0.017 | 0.018 | 0.0175 | 5.7143 | 1.708 | 0.91305 | 46.5429 | 93.7276 | 0.90628 | 98.069 | UV254 | cm-1 | 0.038 | 3.206 | 1.9356 | 39.6245 | 86.3799 | 1.9213 | 98.0222 | UV254 | cm-1 | 0.018 | 0.676 | 0.51896 | 23.2308 | 93.5484 | 0.51518 | 96.5061 | UV254 | cm-1 | 0.016 | 0.409 | 0.39064 | 4.4881 | 94.2652 | 0.38782 | 95.8744 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 23 | 23 | 23 | 0 | [21 empty] | 1998-12-02 | 16:20 | 96.8 | 25.3 | 145.2 | 144.5 | 600 | 9.0394 | 1.3191 |  | 10.3585 | 0.45405 | 0.87266 | 56.9233 | 20.632 | 18.7145 | 1020.9539 | 394.1846 | 1011.5111 | 6.2205 | 138.6295 | 0.135 | 7.23 |  |  | 421.148 |  |  | 836.181 |  | 11.1502 | 833.0546 | 49.4453 | 0.042 |  |  | 1.9031 |  | 84.9462 | 1.8891 | 97.7767 | [8 empty] | SUVA | L/(mg*m) | 1.828 | 2.5 | 2.164 | 31.0559 | 2.8 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.0213 | 2.9685 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.5517 | 2.8766 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8824 | 3.2984 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 76.2 | 238 | 215 | 102 | T-Hdp, mg/L CaCO3 | 76.2 | 238 | 215 | 102
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.54 | 7.52 | 7.53 | 0.2656 | [21 empty] | 1998-12-02 | 19:02 | 101.6 | [19 empty] | 7.32 |  | 7.81 | 373.828 |  | 1283.2 | 474 | 63.0611 | 21.1333 |  |  | 0.038 |  | 3.21 | 0.279 | 91.3084 | 86.3799 | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L | 77.153 | 79.009 | 78.081 | 2.377 | --- | 442.5296 | --- | 57.6797 | 439.7773 | 82.2453 | Bromide | mg/L | 181 | --- | 208.5591 | --- | 1.897 | 208.3505 | 13.1272 | Bromide | mg/L | 175 | --- | 193.2342 | --- | 5.1491 | 193.0966 | 9.3718 | Bromide | mg/L | 173.6 | --- | 189.1271 | --- | 5.9079 | 189.0102 | 8.1531 | Ca-HdF, mg/L CaCO3 | 279 | 279 | 279 | 279 | Ca-HdF, mg/L CaCO3 | 279 | 279 | 279 | 279
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | - | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 23.6333 | 23.6167 | 23.625 | 0.070547 | [21 empty] | 1998-12-02 | 20:20 | 102.9 | 25.2 | 144.4 | 143.4 | 600 | 9.0394 | 1.3191 |  | 10.3585 | 0.45405 | 0.87266 | 56.9233 | 20.632 | 18.7699 | 1020.9539 | 394.1846 | 1011.5111 | 6.2205 | 137.6795 | 0.13633 | [27 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 72.25 | 227 | 206 | 99.3 | Ca-Hdp, mg/L CaCO3 | 72.25 | 227 | 206 | 99.3
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | - | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 731.5 | 713 | 722.25 | 2.5614 | [21 empty] | 1998-12-02 | 20:30 | 103 | 25.2 | 168 | 167.4 | 600 | 9.0394 | 9.829 |  | 18.8684 | 0.45405 | 0.47908 | 30.7991 | 20.632 | 18.7699 | 671.491 | 259.259 | 665.2804 | 4.0913 | 163.6087 | 0.11472 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.54 | 1.57 | 1.555 | 1.9293 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.11 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.53 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.44 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 19 | [14 empty] | SDS-CHCl3 | mg/L | 165.737 | 167.04 | 166.3885 | 0.78311 | [21 empty] | 1998-12-03 | 8:50 | 113.3 | 26 | 167.6 | 167.1 | 600 | 9.0394 | 9.829 |  | 18.8684 | 0.45405 | 0.47908 | 30.7991 | 20.632 | 18.3313 | 671.491 | 259.259 | 665.2804 | 4.0913 | 163.2587 | 0.11228 | 6.56 |  |  | 347.82 |  |  | 590.044 |  | 26.6203 | 588.2194 | 40.869 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 3.46 | 3.43 | 3.445 | 0.87083 | --- | 28.2395 | --- | 67.7585 | 28.0523 | 87.7194 | SDS-Cl2 demand | mg/L | 4.39 | --- | 53.9569 | --- | 58.9144 | 53.5819 | 91.8069 | SDS-Cl2 demand | mg/L | 3.97 | --- | 16.8587 | --- | 62.8451 | 16.7614 | 76.3147 | SDS-Cl2 demand | mg/L | 3.56 | --- | 13.7096 | --- | 66.6823 | 13.6332 | 73.8873 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | -10%, +25% | [14 empty] | SDS-BDCM | mg/L | 47.693 | 52.154 | 49.9235 | 8.9357 | [21 empty] | 1998-12-03 | 12:55 | 117.4 | 27.1 | 164.5 | 164.1 | 600 | 9.0394 | 9.829 |  | 18.8684 | 0.45405 | 0.47908 | 30.7991 | 20.632 | 17.7448 | 671.491 | 259.259 | 665.2804 | 4.0913 | 160.2087 | 0.11076 | 6.67 | 7.17 | 7.04 | 346.456 | 496.8 | 824.456 | 591.2985 | 28.2802 | 26.908 | 589.4541 | 41.2243 | BMRL | 0.774 | 0.298 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 23 | 23 | 23 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 74.8965 | 88.8953 | 78.3629 | 76.1036 | Qp/QT (THM4), % | 92.3426 | 109.6023 | 96.6165 | 93.8309
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | >99% of 2,000 ppm MgSO4 | [14 empty] | SDS-DBCM | mg/L | 9.871 | 10.602 | 10.2365 | 7.1411 | [21 empty] | 1998-12-03 | 15:15 | 119.7 | 26.9 | 165.5 | 164.7 | 600 | 9.0394 | 9.829 |  | 18.8684 | 0.45405 | 0.47908 | 30.7991 | 20.632 | 17.8501 | 671.491 | 259.259 | 665.2804 | 4.0913 | 161.0087 | 0.11086 | 6.73 |  |  | 404.426 |  |  | 537.9852 |  | 14.6781 | 536.9791 | 24.685 | 0.008 |  |  | 0.52823 |  | 97.1326 | 0.52431 | 98.4742 | [8 empty] | SDS-Chlorination pH | --- | 7.47 | 7.49 | 7.48 | 0.26738 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.49 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.49 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | 36 | 36
|  | (e.g., solute type and concentration) | <50% 500 ppm CaCl2 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [21 empty] | 1998-12-03 | 17:40 | 122.1 | [19 empty] | 6.65 |  | 6.95 | 413.974 |  | 756.286 | 474 | 37.3253 | 12.6637 |  |  | 0.018 |  | 0.676 | 0.279 | 58.7278 | 93.5484 | #DIV/0! | #DIV/0! | [8 empty] | SDS-Incubation time | hours | 23.6167 | 23.7167 | 23.6667 | 0.42254 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.6167 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.65 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.6833 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 34.7981 | 24.1034 | 30.6905 | 31.89 | SDS-HAA5b, ug/L | 15.6729 | NA | 10.6084 | 12.0873
|  | Variability of rejection of reference solute (%) | - | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 223.301 | 229.796 | 226.5485 | 2.8669 | [21 empty] | 1998-12-03 | 22:00 | 126.3 | 23.5 | 164.8 | 164.3 | 600 | 9.0394 | 9.829 |  | 18.8684 | 0.45405 | 0.47908 | 30.7991 | 20.632 | 19.7372 | 671.491 | 259.259 | 665.2804 | 4.0913 | 160.4587 | 0.123 | [27 empty] | SDS-TOX | mg Cl- /L | 52.55 | 50 | 51.275 | 4.9732 | --- | 2349.1346 | --- | 92.9007 | 2331.7812 | 97.801 | SDS-TOX | mg Cl- /L | 110 | --- | 4930.8661 | --- | 84.7698 | 4894.3915 | 97.7525 | SDS-TOX | mg Cl- /L | 62.35 | --- | 1328.9527 | --- | 91.3673 | 1319.3971 | 95.2744 | SDS-TOX | mg Cl- /L | 41.3 | --- | 1011.3142 | --- | 94.2818 | 1004.0154 | 95.8865 | SDS-TOXb, ug Cl- /L | 219.7134 | 177.9885 | 205.1332 | 204.0226 | SDS-TOXb, ug Cl- /L | 102.6542 | NA | 84.6778 | 83.3085
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 2.694 | 5.838 | 4.266 | 73.699 | [21 empty] | 1998-12-07 | 16:00 | 138.2 | 21.5 | 121.1 | 120.3 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 20.9392 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 117.1645 | 0.17872 | [27 empty] | SDS-CHCl3 | mg/L | 5.564 | 5.985 | 5.7745 | 7.2907 | --- | 555.8224 | --- | 96.5295 | 551.6685 | 98.9533 | SDS-CHCl3 | mg/L | 10.074 | --- | 1240.8968 | --- | 93.9455 | 1231.5844 | 99.182 | SDS-CHCl3 | mg/L | 4.351 | --- | 315.3635 | --- | 97.385 | 313.0171 | 98.61 | SDS-CHCl3 | mg/L | 2.724 | --- | 235.8643 | --- | 98.3629 | 234.11 | 98.8364 | SDS-CDb, mg/L | 5.2625 | 5.089 | 5.4229 | 5.2626 | SDS-CDb, mg/L | 3.9994 | NA | 4.1972 | 3.9995
|  | Standard testing pH | 6.7-7.3 | [14 empty] | SDS-DCAA* | mg/L | 38.838 | 33.604 | 36.221 | 14.4502 | [21 empty] | 1998-12-08 | 9:00 | 155.2 | 23.2 | 117.5 | 116.7 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 19.913 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 113.5645 | 0.17535 |  |  |  | 165.704 |  |  | 605.0662 |  | 65.0414 | 601.7566 | 72.4633 | [16 empty] | SDS-BDCM | mg/L | 7.338 | 7.645 | 7.4915 | 4.098 | --- | 152.8066 | --- | 84.994 | 151.7091 | 95.0619 | SDS-BDCM | mg/L | 17.468 | --- | 273.0231 | --- | 65.0105 | 271.0896 | 93.5564 | SDS-BDCM | mg/L | 8.666 | --- | 87.8551 | --- | 82.6414 | 87.2576 | 90.0685 | SDS-BDCM | mg/L | 6.527 | --- | 68.3454 | --- | 86.926 | 67.8802 | 90.3845 | TOCb, mg/L | 3.0517 | 2.7478 | 3.0067 | 2.9636 | TOCb, mg/L | 1.5042 | NA | 1.4488 | 1.3957
|  | Acceptable range of operating pressures | <105 psi | [14 empty] | SDS-TCAA* | mg/L | 72.51 | 76.17 | 74.34 | 4.9233 | [21 empty] | 1998-12-08 | 11:30 | 159.4 | [22 empty] | 200.136 |  | 690.522 | 474 | 31.3563 | 57.7772 | [18 empty] | SDS-DBCM | mg/L | 6.864 | 7.002 | 6.933 | 1.9905 | --- | 18.2464 | --- | 32.2718 | 18.1609 | 61.8246 | SDS-DBCM | mg/L | 19.932 | --- | -56.4105 | --- | -94.715 | -55.8329 | 135.6994 | SDS-DBCM | mg/L | 12.34 | --- | 8.3026 | --- | -20.549 | 8.333 | -48.0854 | SDS-DBCM | mg/L | 10.554 | --- | 10.1017 | --- | -3.1016 | 10.1051 | -4.4421 | UV254 b, cm-1 | 0.083146 | 0.064762 | 0.074473 | 0.078848 | UV254 b, cm-1 | 0.037524 | NA | 0.026831 | 0.032225
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | 1.294 | 1.294 | #VALUE! | [21 empty] | 1998-12-08 | 15:00 | 161.3 | 23 | 120.5 | 119.9 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 20.0311 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 116.6645 | 0.1717 |  |  |  | 167.318 |  |  | 604.3801 |  | 64.7008 | 601.0877 | 72.1641 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 5.22 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.97 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.667 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 104.7959 | 181.3887 | 177.0555 | 176.2047 | Bromideb, ug/L | 86.2299 | NA | 175.3214 | 174.2724
|  | Typical pressure drop across a single element (psi) | 3 | [14 empty] | SDS-DBAA* | mg/L | 1.44 | 1.418 | 1.429 | 1.5395 | [21 empty] | 1998-12-08 | 15:30 | 161.8 |  |  |  |  | . | . | [13 empty] | 6.63 |  | 6.96 | 154.406 |  | 605.51 | 474 | 21.7189 | 67.4249 |  |  | 0.016 |  | 0.409 | 0.279 | 31.7848 | 94.2652 | #DIV/0! | #DIV/0! | [8 empty] | SDS-THM4 | mg/L | 19.766 | 20.632 | 20.199 | 4.2873 | --- | 726.8754 | --- | 91.084 | 721.5385 | 97.2006 | SDS-THM4 | mg/L | 52.694 | --- | 1421.6271 | --- | 76.7405 | 1411.2697 | 96.2662 | SDS-THM4 | mg/L | 29.327 | --- | 407.8711 | --- | 87.0549 | 405.0153 | 92.759 | SDS-THM4 | mg/L | 23.472 | --- | 312.7548 | --- | 89.6393 | 310.5781 | 92.4425 | Alkb, mg/L CaCO3 | 70.3566 | 135.4991 | 125.9502 | 100.6963 | Alkb, mg/L CaCO3 | 52.3871 | NA | 120.9305 | 89.794
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.477 | 8.214 | 8.3455 | 3.1514 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 131.1265 | 244.3297 | 232.3097 | 148.1201 | T-Hdb, mg/L CaCO3 | 92.9544 | NA | 217.7068 | 113.9064
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [21 empty] | 1998-12-15 | 19:05 | 167.8 | 21.4 | 128.3 | 126.1 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 21.0012 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 123.6645 | 0.16982 | [27 empty] | SDS-DCAA* | mg/L | 2.689 | 2.791 | 2.74 | 3.7226 | --- | 117.401 | --- | 92.4353 | 116.535 | 97.6488 | SDS-DCAA* | mg/L | 4.132 | --- | 256.8013 | --- | 88.5923 | 254.8896 | 98.3789 | SDS-DCAA* | mg/L | 2.03 | --- | 67.6557 | --- | 94.3955 | 67.1606 | 96.9774 | SDS-DCAA* | mg/L | 1.402 | --- | 51.0017 | --- | 96.1293 | 50.6285 | 97.2308 | Ca-Hdb, mg/L CaCO3 | 124.1515 | 232.7744 | 221.7951 | 142.2419 | Ca-Hdb, mg/L CaCO3 | 88.0817 | NA | 208.47 | 110.3859
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hr | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [21 empty] | 1998-12-15 | 23:59 | 172.7 | 23.4 | 126.4 | 125.6 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 19.7957 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 122.4645 | 0.16164 | [27 empty] | SDS-TCAA* | mg/L | 2.93 | 3.036 | 2.983 | 3.5535 | --- | 247.3563 | --- | 95.9874 | 245.5108 | 98.785 | SDS-TCAA* | mg/L | 4.146 | --- | 556.8547 | --- | 94.4229 | 552.6729 | 99.2498 | SDS-TCAA* | mg/L | 2.038 | --- | 140.8134 | --- | 97.2585 | 139.7665 | 98.5419 | SDS-TCAA* | mg/L | 1.172 | --- | 105.3999 | --- | 98.4235 | 104.6157 | 98.8797
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [21 empty] | 1998-12-16 | 8:20 | 181 | 23.6 | 123.8 | 123.2 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 19.679 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 119.9645 | 0.16404 |  |  |  | 148.488 |  |  | 612.3853 |  | 68.6734 | 608.8908 | 75.6134 | 0.01 |  |  | 0.39336 |  | 96.4158 | 0.39047 | 97.439 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 115.482 | 118.324 | 116.903 | 2.4311 | [23 empty] | 184.1 | [6 empty] | X | [15 empty] | 151.716 |  |  | 474 |  | 67.9924 |  |  | 0.01 |  |  | 0.279 |  | 96.4158 | #DIV/0! | #DIV/0! | [8 empty] | SDS-DBAA* | mg/L | 1.542 | 1.569 | 1.5555 | 1.7358 | --- | 1.1223 | --- | -8.8523 | 1.1256 | -38.1988 | SDS-DBAA* | mg/L | 4.233 | --- | -17.8457 | --- | -196.2211 | -17.6787 | 123.9441 | SDS-DBAA* | mg/L | 2.818 | --- | 0.15197 | --- | -97.2008 | 0.17209 | -1537.5504 | SDS-DBAA* | mg/L | 2.622 | --- | 0.92257 | --- | -83.485 | 0.93536 | -180.3207 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 123.959 | 126.538 | 125.2485 | 2.0591 | [21 empty] | 1998-12-16 | 13:45 | 186.4 | 24.1 | 123.5 | 123 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 19.3903 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 119.7145 | 0.16197 |  |  |  | 149.026 |  |  | 612.1566 |  | 68.5599 | 608.6679 | 75.516 | 0.01 | 0.298 | 0.418 | 0.39336 | 5.8947 | 96.4158 | 0.39047 | 97.439 | [8 empty] | SDS-BCAA* | mg/L | 2.609 | 2.653 | 2.631 | 1.6724 | --- | 22.2012 | --- | 68.474 | 22.0534 | 88.0699 | SDS-BCAA* | mg/L | 5.186 | --- | 30.064 | --- | 37.8587 | 29.8757 | 82.6414 | SDS-BCAA* | mg/L | 2.909 | --- | 13.3437 | --- | 65.1429 | 13.265 | 78.0701 | SDS-BCAA* | mg/L | 2.395 | --- | 10.8715 | --- | 71.3019 | 10.8077 | 77.8399 | Qp/QT (HAA5), % | 57.3804 | 60.2565 | 57.1757 | 56.3107 | Qp/QT (HAA5), % | 82.01 | 86.1206 | 81.7174 | 80.4811
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [26 empty] | 1998-12-16 | 17:20 | 190 | [22 empty] | 139.88 | 491.28 | 676.888 | 474 | 29.9736 | 70.4895 |  |  | 0.01 |  | 0.416 | 0.279 | 32.9327 | 96.4158 | #DIV/0! | #DIV/0! | [8 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 108.1443 | 121.7898 | 113.7857 | 112.1947 | SDS-THM4b, ug/L | 57.3214 | 76.824 | 65.3843 | 63.1103
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [26 empty] | 1998-12-16 | 19:50 | 192.5 | 24.2 | 122.6 | 122 | 600 | 9.0394 | 21.2627 |  | 30.3021 | 0.45405 | 0.29831 | 18.8006 | 20.632 | 19.333 | 580.2667 | 224.0378 | 574.8999 | 3.5355 | 118.7645 | 0.16278 | [27 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 337.2417 | 353.3294 | 344.9475 | 338.8022 | SDS-TOXb, ug Cl- /L | 171.9837 | 194.9767 | 182.9971 | 174.2141
[94 empty] | SDS-HAA5 | mg/L | 7.161 | 7.396 | 7.2785 | 3.2287 | --- | 382.7049 | --- | 93.7739 | 379.8696 | 98.0839 | SDS-HAA5 | mg/L | 12.511 | --- | 834.4953 | --- | 89.298 | 828.2761 | 98.4895 | SDS-HAA5 | mg/L | 6.886 | --- | 218.0511 | --- | 94.1096 | 216.458 | 96.8188 | SDS-HAA5 | mg/L | 5.196 | --- | 164.3228 | --- | 95.5553 | 163.1254 | 96.8147 | SDS-CDb, mg/L | 6.5307 | 6.8919 | 6.8457 | 6.6729 | SDS-CDb, mg/L | 4.7475 | 5.2637 | 5.1977 | 4.9507
[94 empty] | SDS-HAA6 | mg/L | 9.77 | 10.049 | 9.9095 | 2.8155 | --- | 404.9061 | --- | 92.0881 | 401.9231 | 97.5345 | SDS-HAA6 | mg/L | 17.697 | --- | 864.5592 | --- | 85.8705 | 858.1518 | 97.9378 | SDS-HAA6 | mg/L | 9.795 | --- | 231.3948 | --- | 92.1795 | 229.723 | 95.7362 | SDS-HAA6 | mg/L | 7.591 | --- | 175.1943 | --- | 93.9392 | 173.9331 | 95.6357 | TOCb, mg/L | 4.6054 | 4.986 | 4.8151 | 4.7143 | TOCb, mg/L | 2.4207 | 2.9647 | 2.7204 | 2.5764
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.12895 | 0.13378 | 0.12977 | 0.1309 | UV254 b, cm-1 | 0.064544 | 0.071449 | 0.065718 | 0.067335
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 123.4363 | 182.391 | 179.0683 | 178.3621 | Bromideb, ug/L | 97.2258 | 181.4858 | 176.7368 | 175.7276
[133 empty] | Alkb, mg/L CaCO3 | 88.3982 | 139.3654 | 131.7767 | 112.8689 | Alkb, mg/L CaCO3 | 63.0297 | 135.8737 | 125.0277 | 98.0041
[133 empty] | T-Hdb, mg/L CaCO3 | 169.4516 | 260.6538 | 249.2594 | 186.3203 | T-Hdb, mg/L CaCO3 | 115.5622 | 245.9113 | 229.6261 | 139.6715
[133 empty] | Ca-Hdb, mg/L CaCO3 | 160.366 | 247.6666 | 237.2617 | 177.8097 | Ca-Hdb, mg/L CaCO3 | 109.4444 | 234.2173 | 219.3463 | 134.3755
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on CD7: TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Note on CY16: C. Rice: Consultant verified the permeate TDS, alkalinity, total hardness, calcium hardness and bromide concentrations but did not provide an explanation for the "zigzag" trend that results.
Note on CY17: C. Rice: Consultant verified the permeate TDS, alkalinity, total hardness, calcium hardness and bromide concentrations but did not provide an explanation for the "zigzag" trend that results.
Note on CY18: C. Rice: Consultant verified the permeate TDS, alkalinity, total hardness, calcium hardness and bromide concentrations but did not provide an explanation for the "zigzag" trend that results.
Note on CY19: C. Rice: Consultant verified the permeate TDS, alkalinity, total hardness, calcium hardness and bromide concentrations but did not provide an explanation for the "zigzag" trend that results.
Note on CY22: C. Rice: Consultant verified the dip in TOC, UV, THM and HAA concentrations at 70% recovery; no explanation was provided.
Note on CY23: C. Rice: Consultant verified the dip in TOC, UV, THM and HAA concentrations at 70% recovery; no explanation was provided.
Note on CY25: C. Rice: Consultant verified the permeate TDS, alkalinity, total hardness, calcium hardness and bromide concentrations but did not provide an explanation for the "zigzag" trend that results.
Note on CY37: C. Rice: Consultant verified the dip in TOC, UV, THM and HAA concentrations at 70% recovery; no explanation was provided.
Note on CY47: C. Rice: Consultant verified the dip in TOC, UV, THM and HAA concentrations at 70% recovery; no explanation was provided.
Note on DL22: C. Rice: Consultant verified the TOC and UV data at 70%, 90% and 50% recovery; no explanation was given for the high MB closure errors.
Note on DL23: C. Rice: Consultant verified the TOC and UV data at 70%, 90% and 50% recovery; no explanation was given for the high MB closure errors.
Note on DV22: C. Rice: Consultant verified the TOC and UV data at 70%, 90% and 50% recovery; no explanation was given for the high MB closure errors.
Note on DV23: C. Rice: Consultant verified the TOC and UV data at 70%, 90% and 50% recovery; no explanation was given for the high MB closure errors.
Note on EI17: Gregg Thompson: ?
Print All Fields

## ESNA. 1st Quarter
FIELD-SET 3: Membrane C, Run 1 (FILE: Margate1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Hydranautics | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.93778 | [45 empty] | Recovery during sample collection (decimal) | 0.67 | [10 empty] | Recovery during sample collection (decimal) | 0.83 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.27 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | ESNA1 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-02-26 | 1999-03-01 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 19.8 | [10 empty] | Feed flow rate during sample collection (mL/min) | 12.7 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 36.6 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 180 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 9:20 | 10:55 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 410 | [10 empty] | Influent flow rate during sample collection (mL/min) | 410 | [7 empty] | Influent flow rate during sample collection (mL/min) | 410 | [7 empty] | Influent flow rate during sample collection (mL/min) | 410 | [6 empty] | SDS-THM4F, ug/L | 210.245 | 210.245 | 210.245 | 210.245 | SDS-THM4F, ug/L | 210.245 | 210.245 | 210.245 | 210.245 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 46.48 | 119.95 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 5.663 | 9.509 | 3.621 | 1.044 | SDS-THM4p, ug/L | 5.663 | 9.509 | 3.621 | 1.044 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.33 | 6.37 | 6.35 | 0.62992 | 1999-02-12 | 13:50 | 0 | 20 | 92 | 91 | 411 | 11.7949 | 5.3141 | 17.109 | 0.31102 | 0.6894 | 23.0225 | 26.9212 | 28.5607 | 97.422 | 28.6344 | 95.4479 | 0.67801 | 90.822 | 0.31447 | 1999-02-24 | 10:56 | 0 | 24.3 | 127 | 127 | 410 | 11.7949 | 5.3141 |  | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.1517 | 1664.6092 | 100.7658 | 1619.6206 | 15.4135 | 111.5865 | 0.2254 | 5.57 |  |  | 77.131 |  |  | 1717.0677 |  | 86.8489 | 1693.4789 | 95.4454 | 0.01 |  |  | 1.1739 |  | 97.3082 | 1.1571 | 99.1358 | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 161.0335 | 161.0335 | 161.0335 | 161.0335 | SDS-HAA5F, ug/L | 161.0335 | 161.0335 | 161.0335 | 161.0335 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32945 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1999-02-12 | 16:25 | 2.5 | 23.7 | 92 | 91 | 411 | 11.7949 | 5.3141 | 17.109 | 0.31102 | 0.6894 | 23.0225 | 26.9212 | 25.6018 | 97.422 | 28.6344 | 95.4479 | 0.67801 | 90.822 | 0.28189 | 1999-02-24 | 14:28 | 3.6 | 24.8 | 121 | 121 | 410 | 11.7949 | 5.3141 |  | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 24.7828 | 1664.6092 | 100.7658 | 1619.6206 | 15.4135 | 105.5865 | 0.23472 | 5.54 | 6.45 | 6.81 | 86.139 | 556.14 | 1465.793 | 1697.074 | -15.7786 | 85.313 | 1673.9024 | 94.854 | 0.011 | 0.372 | 1.158 | 1.1716 | -1.1784 | 97.039 | 1.155 | 99.0476 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 2.218 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 2.218 | 0 | 0 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 66.3 | 73 | 69.65 | 9.6195 | 1999-02-13 | 10:00 | 20 | 23.4 | 92 | 92 | 411 | 11.7949 | 5.3141 | 17.109 | 0.31102 | 0.6894 | 23.0225 | 26.9212 | 25.8298 | 97.422 | 28.6344 | 95.4479 | 0.67801 | 91.322 | 0.28284 | 1999-02-25 | 7:46 | 20.9 | 23.7 | 122 | 121 | 410 | 11.7949 | 5.3141 |  | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.6018 | 1664.6092 | 100.7658 | 1619.6206 | 15.4135 | 106.0865 | 0.24133 | 5.58 |  |  | 84.45 |  |  | 1700.8228 |  | 85.601 | 1677.5729 | 94.9659 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1999-02-26 | 1999-02-26 | --- | --- | 1999-02-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-27 | 1999-02-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-28 | 1999-02-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-01 | 1999-03-01 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 924.25 | 924.25 | 924.25 | 924.25 | SDS-TOXF, ug Cl- /L | 924.25 | 924.25 | 924.25 | 924.25 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 571 | 602 | 586.5 | 5.2856 | 1999-02-14 | 12:30 | 46.7 | 23.6 | 99 | 99 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.6776 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 98.322 | 0.26116 | 1999-02-25 | 13:09 | 26.3 | 24.2 | 139 | 139 | 410 | 11.7949 | 5.3141 |  | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.2262 | 1664.6092 | 100.7658 | 1619.6206 | 15.4135 | 123.5865 | 0.20412 | 5.58 |  |  | 76.568 |  |  | 1718.3173 |  | 86.9449 | 1694.7024 | 95.4819 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 18:48 | 18:48 | --- | --- | NR | --- | --- | --- | --- | --- | Sampling time | hh:mm | 0:05 | 0:05 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 0:50 | 0:50 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 3:55 | 3:55 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | 32.05 | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | 32.05 | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 284 | 286 | 285 | 0.70175 | 1999-02-15 | 9:20 | 67.4 | 24 | 100 | 99 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.3758 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 98.822 | 0.25678 | 1999-02-26 | 9:15 | 46.4 | 24.1 | 152 | 152 | 410 | 13.1661 | 6.6033 |  | 19.7694 | 0.31026 | 0.66598 | 19.7391 | 30.0509 | 28.2422 | 1567.337 | 94.5705 | 1520.0429 | 14.4912 | 137.5088 | 0.20538 | 5.63 | 6.42 | 6.89 | 81.072 | 510.6 | 1572.9 | 1594.2511 | -1.3574 | 86.177 | 1569.9552 | 94.836 | BMRL | 0.39 | 1.376 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 32 | 32 | --- | --- | 32 | --- | --- | --- | --- | --- | Operation time | hh.hh | 62.1 | 62.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 86.4 | 86.4 | --- | --- | --- | --- | --- | Cumulative time | hr | 92.1 | 92.1 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 12.3 | 12.3 | 12.3 | 12.3 | SDS-CDF, mg/L | 12.3 | 12.3 | 12.3 | 12.3 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 27 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 267 | 269 | 268 | 0.74627 | 1999-02-15 | 14:45 | 72.9 | 24.2 | 102 | 101 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.2262 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 100.822 | 0.25021 | 1999-02-26 | 11:37 | 48.7 | 24.7 | 158 | 158 | 410 | 10.2892 | 2.3331 |  | 12.6223 | 0.31026 | 0.81516 | 31.4822 | 23.4847 | 21.6832 | 2502.5894 | 152.0302 | 2443.6004 | 23.2106 | 134.7894 | 0.16087 | [27 empty] | pH | --- | 6.05 | 6.12 | 6.085 | 1.1504 | 6.75 | --- | --- | --- | --- | --- | pH | --- | 5.96 | 7.91 | --- | --- | --- | --- | --- | pH | --- | 5.8 | 6.66 | --- | --- | --- | --- | --- | pH | --- | 5.79 | 6.66 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.55 | 3.75 | 1.88 | 1.32 | SDS-CDp, mg/L | 2.55 | 3.75 | 1.88 | 1.32 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 68 | 1 | 0.7 | 27 | 14.3517 | 96.3062 | 411.456 | 11.8281 | 16.8973 | 5.0692 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.49 | 1.24 | 0.865 | 86.7052 | 1999-02-15 | 16:45 | 74.9 | 24.4 | 99 | 99 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.0775 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 98.322 | 0.25505 | 1999-02-26 | 14:44 | 51.8 | 25 | 158 | 158 | 410 | 9.3894 | 2.1755 |  | 11.5649 | 0.31026 | 0.81189 | 34.4521 | 21.4309 | 19.6123 | 2469.1142 | 150.3137 | 2416.0111 | 22.9225 | 135.0775 | 0.14519 | 5.61 |  |  | 217.5 |  |  | 2179.133 |  | 62.9156 | 2156.6713 | 89.915 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24.1 | 24.1 | 24.1 | 0 | 24.1 | --- | --- | --- | --- | --- | Temperature | oC | 24.9 | 24.9 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- | --- | TOCF, mg/L | 11 | 11 | 11 | 11 | TOCF, mg/L | 11 | 11 | 11 | 11 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.36 | 2 | 0.9 | 27 | 39.785 | 121.7395 | 411.456 | 11.8281 | 13.1424 | 1.3142 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.4 | 0.3 | 0.35 | 28.5714 | 1999-02-16 | 9:10 | 91.3 | 23.5 | 107 | 106 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.7536 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 105.822 | 0.24337 | 1999-02-26 | 15:55 | 53 | 25.1 | 158 | 158 | 410 | 10.4732 | 2.1755 |  | 12.6487 | 0.31026 | 0.82801 | 31.4144 | 23.9046 | 21.8115 | 2638.6855 | 160.2286 | 2575.3746 | 24.468 | 133.532 | 0.16334 | 5.57 | 6.2 | 7.82 | 198 | 520.26 | 4010.8 | 2456.844 | 38.7443 | 66.2404 | 2427.9935 | 91.8451 | BMRL | 0.342 | 2.506 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 11.5 | 13 | 12.25 | 12.2449 | 196 | 186.1894 | 5.0054 | 82.4121 | 183.3754 | 93.3197 | Alkalinity | mg/L as CaCO3 | 17.1 | 425 | 326.2176 | 23.2429 | 75.4487 | 322.244 | 94.6935 | Alkalinity | mg/L as CaCO3 | 10.1 | 138 | 129.2 | 6.3768 | 85.4989 | 127.6604 | 92.0884 | Alkalinity | mg/L as CaCO3 | 10 | 100 | 91.7123 | 8.2877 | 85.6425 | 90.7276 | 88.978 | TOCp, mg/L | 0.43 | 0.53 | 0.34 | 0.31 | TOCp, mg/L | 0.43 | 0.53 | 0.34 | 0.31 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 27 | 9.265 | 91.2195 | 411.456 | 11.8281 | 23.6562 | 11.8281 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 10.6 | 11.4 | 11 | 7.2727 | 1999-02-16 | 13:35 | 95.7 | 23.6 | 106 | 105 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.6776 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 104.822 | 0.24496 | 1999-02-27 | 10:10 | 71.2 | 24.6 | 170 | 170 | 410 | 10.4732 | 2.1755 |  | 12.6487 | 0.31026 | 0.82801 | 31.4144 | 23.9046 | 22.1363 | 2638.6855 | 160.2286 | 2575.3746 | 24.468 | 145.532 | 0.15211 | [27 empty] | Total dissolved solids | mg/L | 93.7 | 68.5 | 81.1 | 31.0727 | 1572.5 | 1612.6152 | -2.551 | 86.1722 | 1587.8382 | 94.8924 | Total dissolved solids | mg/L | 198 | 4010 | 2483.2941 | 38.0725 | 66.2404 | 2453.9169 | 91.9313 | Total dissolved solids | mg/L | 54 | 1120 | 1119 | 0.089286 | 90.7928 | 1105.2329 | 95.1142 | Total dissolved solids | mg/L | 58 | 758 | 781.9726 | -3.1626 | 90.1108 | 773.2478 | 92.4992 | UV254 F, cm-1 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | UV254 F, cm-1 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 27 | 7.085 | 89.0395 | 411.456 | 11.8281 | 39.4271 | 27.599 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.387 | 0.356 | 0.3715 | 8.3445 | 1999-02-16 | 16:35 | 98.7 | 23.2 | 106 | 105 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.983 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 104.822 | 0.24788 | 1999-02-27 | 12:30 | 73.6 | 24.6 | 146 | 146 | 410 | 12.7701 | 12.2358 |  | 25.0059 | 0.31026 | 0.51068 | 15.3961 | 29.1471 | 26.991 | 1127.5399 | 68.0977 | 1094.5419 | 10.4294 | 135.5706 | 0.19909 | 5.35 |  |  | 54.998 |  |  | 1141.2116 |  | 90.6227 | 1124.2957 | 95.1082 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 32.9 | 33.4 | 33.15 | 1.5083 | 808 | 796.3318 | 1.4441 | 88.3684 | 783.985 | 95.7716 | Total hardness | mg/L as CaCO3 | 68 | 1940 | 1344.4706 | 30.6974 | 76.1404 | 1328.0617 | 94.8798 | Total hardness | mg/L as CaCO3 | 22.5 | 511 | 547.5 | -7.1429 | 92.1053 | 540.7134 | 95.8388 | Total hardness | mg/L as CaCO3 | 17.9 | 385 | 383.7904 | 0.31418 | 93.7193 | 379.381 | 95.2818 | UV254 p, cm-1 | 0.0048125 | 0.0065 | 0.002625 | 0.0025 | UV254 p, cm-1 | 0.0048125 | 0.0065 | 0.002625 | 0.0025 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 875 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.6509 | 3.1228 | 3.3869 | 15.5936 | 1999-02-17 | 8:50 | 115 | 23 | 105 | 104 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 26.137 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 103.822 | 0.25175 | 1999-02-27 | 11:00 | 79 | 24.5 | 146 | 146 | 410 | 9.8 | 10.7 |  | 20.5 | 0.31026 | 0.47805 | 19 | 22.368 | 20.7746 | 1064.3787 | 64.7345 | 1040.4848 | 9.877 | 136.123 | 0.15262 | 5.35 | 6.2 | 6.42 | 53.97 | 521.64 | 1120.14 | 1074.2378 | 4.0979 | 90.798 | 1062.0443 | 94.9183 | BMRL | 0.387 | 0.656 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 32.9 | 33.4 | 33.15 | 1.5083 | 756 | 744.8167 | 1.4793 | 87.6306 | 733.3033 | 95.4794 | Calcium hardness | mg/L as CaCO3 | 64.4 | 1810 | 1262.0471 | 30.2736 | 75.9701 | 1246.6515 | 94.8342 | Calcium hardness | mg/L as CaCO3 | 22.5 | 479 | 513.5 | -7.2025 | 91.6045 | 507.1529 | 95.5635 | Calcium hardness | mg/L as CaCO3 | 17.9 | 362 | 360.5027 | 0.41361 | 93.3209 | 356.374 | 94.9772 | BromideF, ug/L | 176.508 | 176.508 | 176.508 | 176.508 | BromideF, ug/L | 176.508 | 176.508 | 176.508 | 176.508 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 174.064 | 178.952 | 176.508 | 2.7693 | 1999-02-17 | 15:00 | 121.1 | 23.9 | 105 | 104 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.4509 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 103.822 | 0.24514 | 1999-02-28 | 8:50 | 93.8 | 24.5 | 150 | 150 | 410 | 10.7 | 10.5 |  | 21.2 | 0.31026 | 0.50472 | 18.3396 | 24.4222 | 22.6825 | 1115.2002 | 67.6821 | 1087.8625 | 10.3385 | 139.6615 | 0.16241 | 5.33 |  | 6.38 | 54.484 |  | 1166.368 | 1128.6496 | 3.2338 | 90.7103 | 1114.6331 | 95.1119 | BMRL |  | 0.735 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.02 | 0.02 | 0.02 | 0 | 0.51 | 2.5806 | -406.0012 | 97.6879 | 2.5392 | 99.2123 | Turbidity | ntu | BMRL | 0.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.32 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.84 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 51.5155 | 76.818 | 32.055 | 24.347 | Bromidep, ug/L | 51.5155 | 76.818 | 32.055 | 24.347 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 13 | 13 | 13 | 0 | 1999-02-18 | 10:00 | 140.2 | 24 | 110 | 109 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.3758 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 108.822 | 0.23319 | 1999-02-28 | 9:40 | 94.7 | 24.2 | 158 | 158 | 410 | 10.5 | 27 |  | 37.5 | 0.31026 | 0.28 | 9.9333 | 23.9657 | 22.4568 | 795.7923 | 48.3198 | 776.6497 | 7.379 | 150.621 | 0.14909 | 5.4 |  |  | 57.97 |  |  | 792.0394 |  | 90.1159 | 782.6398 | 92.593 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.22 | 0.21 | 0.215 | 4.6512 | 0.67 | 0.62409 | 6.8521 | 38.5714 | 0.61747 | 65.1806 | Ammonia | mg NH3-N / L | 0.24 | 0.71 | 0.88706 | -24.9379 | 31.4286 | 0.87874 | 72.6882 | Ammonia | mg NH3-N / L | 0.17 | 0.67 | 0.53 | 20.8955 | 51.4286 | 0.52535 | 67.6404 | Ammonia | mg NH3-N / L | 0.14 | 0.49 | 0.42767 | 12.7202 | 60 | 0.4242 | 66.997 | AlkF, mg/L CaCO3 | 69.65 | 69.65 | 69.65 | 69.65 | AlkF, mg/L CaCO3 | 69.65 | 69.65 | 69.65 | 69.65
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 76.667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.81 | 0.59 | 0.7 | 31.4286 | 1999-02-18 | 14:06 | 144.2 | 24.2 | 113 | 112 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.2262 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 111.822 | 0.22559 | 1999-02-28 | 13:45 | 98.8 | 24.3 | 158 | 158 | 410 | 10.2 | 26.6 |  | 36.8 | 0.31026 | 0.27717 | 10.1413 | 23.281 | 21.7508 | 792.9236 | 48.1796 | 774.3959 | 7.3548 | 150.6452 | 0.14438 | 5.39 |  |  | 66.154 |  |  | 786.0312 |  | 88.7205 | 777.0766 | 91.4868 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | 0.29 | 0.57 | 0.43 | 65.1163 | 34.9 | 32.4603 | 6.9905 | 96.0909 | 31.9421 | 98.6538 | Total organic carbon | mg/L | 0.53 | 93.3 | 62.1182 | 33.421 | 95.1818 | 61.3265 | 99.1358 | Total organic carbon | mg/L | 0.34 | 21 | 21.66 | -3.1429 | 96.9091 | 21.3844 | 98.4101 | Total organic carbon | mg/L | 0.31 | 15 | 14.9538 | 0.30776 | 97.1818 | 14.7774 | 97.9022 | Alkp, mg/L CaCO3 | 12.25 | 17.1 | 10.1 | 10 | Alkp, mg/L CaCO3 | 12.25 | 17.1 | 10.1 | 10
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 12.19 | 12.41 | 12.3 | 1.7886 | 1999-02-18 | 17:09 | 147.3 | 24.5 | 111 | 110 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.0035 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 109.822 | 0.22767 | 1999-02-28 | 19:00 | 104.1 | 24.2 | 158 | 158 | 410 | 10.1 | 26.5 |  | 36.6 | 0.31026 | 0.27596 | 10.2022 | 23.0527 | 21.6013 | 791.6953 | 48.1162 | 773.3779 | 7.3442 | 150.6558 | 0.14338 | 5.37 | 6.29 | 6.39 | 57.97 | 514.05 | 758.313 | 787.9397 | -3.9069 | 90.1159 | 778.9486 | 92.5579 | BMRL | 0.389 | 0.565 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | 0.005 | 0.004625 | 0.0048125 | 7.7922 | 1.202 | 1.116 | 7.1558 | 98.7046 | 1.098 | 99.5617 | UV254 | cm-1 | 0.0065 | 3.11 | 2.1536 | 30.7537 | 98.2503 | 2.126 | 99.6943 | UV254 | cm-1 | 0.002625 | 0.729 | 0.74038 | -1.5604 | 99.2934 | 0.73084 | 99.6408 | UV254 | cm-1 | 0.0025 | 0.483 | 0.50798 | -5.1717 | 99.3271 | 0.50189 | 99.5019 | T-HdF, mg/L CaCO3 | 285 | 285 | 285 | 285 | T-HdF, mg/L CaCO3 | 285 | 285 | 285 | 285
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | 1999-02-19 | 7:24 | 161.6 | 24.9 | 112 | 112 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 24.7096 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 111.322 | 0.22197 | 1999-03-01 | 10:10 | 119.2 | 24.8 | 155 | 155 | 410 | 9.9 | 26.7 |  | 36.6 | 0.31026 | 0.27049 | 10.2022 | 22.5962 | 20.8014 | 786.2401 | 47.8071 | 768.4096 | 7.2952 | 147.7048 | 0.14083 | [27 empty] | SUVA | L/(mg*m) | 1.7241 | 0.8114 | 1.2678 | 71.9952 | 3.4441 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.2264 | 3.3333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 0.77206 | 3.4714 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 0.80645 | 3.22 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 33.15 | 68 | 22.5 | 17.9 | T-Hdp, mg/L CaCO3 | 33.15 | 68 | 22.5 | 17.9
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.6 | 7.43 | 7.515 | 2.2621 | 1999-02-19 | 12:03 | 166.2 | 24.5 | 115 | 114 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 25.0035 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 113.822 | 0.21967 | 1999-03-05 | 8:50 | 143.2 | [6 empty] | X | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Bromide | mg/L | 44.881 | 58.15 | 51.5155 | 25.7573 | --- | 430.2807 | --- | 70.8141 | 424.153 | 87.8545 | Bromide | mg/L | 76.818 | --- | 663.2298 | --- | 56.479 | 655.6915 | 88.2844 | Bromide | mg/L | 32.055 | --- | 320.961 | --- | 81.8394 | 317.2264 | 89.8952 | Bromide | mg/L | 24.347 | --- | 232.7867 | --- | 86.2063 | 230.2748 | 89.427 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 23.52 | 23 | 23.26 | 2.2356 | 1999-02-19 | 15:23 | 169.5 | 25.1 | 111 | 110 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 24.564 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 109.822 | 0.22367 | 1999-03-05 | 10:45 | 145.1 | 25.4 | 158 | 158 | 410 |  |  |  | 0 | 0.31026 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.25 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.75 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 33.15 | 64.4 | 22.5 | 17.9 | Ca-Hdp, mg/L CaCO3 | 33.15 | 64.4 | 22.5 | 17.9
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | 5 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 891.5 | 957 | 924.25 | 7.0868 | 1999-02-23 | 17:13 | 170.4 | 21.4 | 117 | 117 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 27.4029 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 116.322 | 0.23558 | 1999-03-05 | 14:00 | 148.3 | 25.4 | 158 | 158 | 410 | 10.4732 | 26.4241 |  | 36.8973 | 0.31026 | 0.28385 | 10.1119 | 23.9046 | 21.619 | 799.7131 | 48.5609 | 780.5253 | 7.4156 | 150.5844 | 0.14357 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.43 | 1.47 | 1.45 | 2.7586 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.37 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.43 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 20 | [14 empty] | SDS-CHCl3 | mg/L | 148.418 | 155.362 | 151.89 | 4.5717 | 1999-02-24 | 8:48 | 186 | 24.6 | 112 | 111 | 410 | 11.7949 | 5.3141 | 17.109 | 0.31026 | 0.6894 | 22.964 | 26.9212 | 24.9297 | 97.4239 | 28.6335 | 95.445 | 0.67801 | 110.822 | 0.22495 | 1999-03-05 | 16:00 | 150.4 | 25.2 | 158 | 158 | 410 | 9.3894 | 24.3378 |  | 33.7273 | 0.31026 | 0.27839 | 11.1563 | 21.4309 | 19.4967 | 794.1187 | 48.344 | 777.0397 | 7.3724 | 150.6276 | 0.12944 | [27 empty] | SDS-Cl2 demand | mg/L | 2.57 | 2.53 | 2.55 | 1.5686 | --- | 32.0955 | --- | 79.2683 | 31.6175 | 91.9348 | SDS-Cl2 demand | mg/L | 3.75 | --- | 54.0441 | --- | 69.5122 | 53.3976 | 92.9772 | SDS-Cl2 demand | mg/L | 1.88 | --- | 22.72 | --- | 84.7154 | 22.4506 | 91.6261 | SDS-Cl2 demand | mg/L | 1.32 | --- | 16.3611 | --- | 89.2683 | 16.1798 | 91.8417 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 49.194 | 52.654 | 50.924 | 6.7944 | [21 empty] | 1999-03-05 | 16:00 | 150.4 | 25.2 | 158 | 158 | 410 | 9.3894 | 24.3378 |  | 33.7273 | 0.31026 | 0.27839 | 11.1563 | 21.4309 | 19.4967 | 794.1187 | 48.344 | 777.0397 | 7.3724 | 150.6276 | 0.12944 | [27 empty] | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 67.5744 | 68.8691 | 66.9066 | 66.0824 | Qp/QT (THM4), % | 85.1712 | 86.8031 | 84.3295 | 83.2907
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | min 70% avg 80% | [14 empty] | SDS-DBCM | mg/L | 7.511 | 7.351 | 7.431 | 2.1531 | [70 empty] | SDS-Chlorination pH | --- | 7.55 | 7.54 | 7.545 | 0.13254 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.52 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.53 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.46 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 500 ppm NaCl | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 23.97 | 23.9 | 23.935 | 0.29246 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.42 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.27 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.03 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 52.2161 | 51.6588 | 53.2915 | 54.6187 | SDS-HAA5b, ug/L | 23.8793 | 23.1768 | 25.2347 | 26.9076
|  | Variability of rejection of reference solute (%) | 10 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 205.123 | 215.367 | 210.245 | 4.8724 | [70 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | 32.05 | --- | 5280.2853 | --- | 96.5323 | 5212.8199 | 99.3852 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 309.8002 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 149.7931 | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.903 | 9.018 | 7.9605 | 26.5687 | [70 empty] | SDS-CHCl3 | mg/L | 1.943 | 1.722 | 1.8325 | 12.06 | --- | 456.5522 | --- | 98.7935 | 449.1957 | 99.592 | SDS-CHCl3 | mg/L | 1.932 | --- | 884.0379 | --- | 98.728 | 872.6985 | 99.7786 | SDS-CHCl3 | mg/L | 1.261 | --- | 302.519 | --- | 99.1698 | 298.6247 | 99.5777 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 5.7115 | 6.4117 | 5.3283 | 5.0442 | SDS-CDb, mg/L | 3.9958 | 4.8783 | 3.5129 | 3.1547
|  | Standard testing pH | 6.5-7 | [14 empty] | SDS-DCAA* | mg/L | 56.34 | 59.54 | 57.94 | 5.523 | [70 empty] | SDS-BDCM | mg/L | 2.138 | 1.9 | 2.019 | 11.788 | --- | 150.216 | --- | 96.0353 | 147.8184 | 98.6341 | SDS-BDCM | mg/L | 2.913 | --- | 285.3306 | --- | 94.2797 | 281.7002 | 98.9659 | SDS-BDCM | mg/L | 1.257 | --- | 100.591 | --- | 97.5316 | 99.3069 | 98.7342 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | 3.8574 | 3.7894 | 3.8678 | 3.9358 | TOCb, mg/L | 1.9974 | 1.9117 | 2.0105 | 2.0962
|  | Acceptable range of operating pressures | <400 psi | [14 empty] | SDS-TCAA* | mg/L | 88.66 | 95.87 | 92.265 | 7.8144 | [70 empty] | SDS-DBCM | mg/L | 1.874 | 1.749 | 1.8115 | 6.9004 | --- | 18.8403 | --- | 75.6224 | 18.5648 | 90.2423 | SDS-DBCM | mg/L | 3.58 | --- | 26.2329 | --- | 51.8234 | 25.9417 | 86.1998 | SDS-DBCM | mg/L | 1.103 | --- | 13.759 | --- | 85.1568 | 13.5954 | 91.887 | SDS-DBCM | mg/L | 1.044 | --- | 9.7933 | --- | 85.9507 | 9.6879 | 89.2236 | UV254 b, cm-1 | 0.12371 | 0.12013 | 0.1247 | 0.12766 | UV254 b, cm-1 | 0.059188 | 0.054669 | 0.06043 | 0.064157
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | 1.135 | 1.37 | 1.2525 | 18.7625 | [70 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.084 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 92.0451 | 107.8524 | 79.8595 | 75.9564 | Bromideb, ug/L | 70.0504 | 89.974 | 54.6915 | 49.772
|  | Typical pressure drop across a single element (psi) | 3-5 | [14 empty] | SDS-DBAA* | mg/L | 1.567 | 1.664 | 1.6155 | 6.0043 | [70 empty] | SDS-THM4 | mg/L | 5.955 | 5.371 | 5.663 | 10.3126 | --- | 625.6085 | --- | 97.3065 | 615.5789 | 99.0801 | SDS-THM4 | mg/L | 9.509 | --- | 1190.309 | --- | 95.4772 | 1175.13 | 99.1908 | SDS-THM4 | mg/L | 3.621 | --- | 416.869 | --- | 98.2777 | 411.527 | 99.1201 | SDS-THM4 | mg/L | 1.044 | --- | 287.6207 | --- | 99.5034 | 284.1671 | 99.6326 | Alkb, mg/L CaCO3 | 30.8623 | 33.4593 | 29.8071 | 30.2319 | Alkb, mg/L CaCO3 | 20.7617 | 24.035 | 19.4318 | 19.9671
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 12.951 | 14.618 | 13.7845 | 12.0933 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 114.8139 | 135.5541 | 109.3703 | 108.494 | T-Hdb, mg/L CaCO3 | 70.4963 | 96.6373 | 63.635 | 62.5305
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 1.157 | --- | 335.1746 | --- | 98.0031 | 330.8809 | 99.6503 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 109.3016 | 127.7826 | 103.7444 | 102.728 | Ca-Hdb, mg/L CaCO3 | 67.9754 | 91.269 | 60.9711 | 59.6899
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 154.605 | 167.462 | 161.0335 | 7.9841 | [70 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.061 | --- | 4.3228 | --- | 34.3237 | 4.2808 | 75.2151 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 167.556 | 182.08 | 174.818 | 8.3081 | [70 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.245 | --- | 75.0068 | --- | 90.9681 | 74.0586 | 98.3189 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 66.4666 | 67.3949 | 66.4666 | 66.4666 | Qp/QT (HAA5), % | 83.2333 | 84.3957 | 83.2333 | 83.2333
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 74.2663 | 74.9592 | 72.909 | 71.1962 | SDS-THM4b, ug/L | 39.9646 | 40.8324 | 38.265 | 36.1201
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | #DIV/0! | 322.953 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 171.2713 | #VALUE! | #VALUE!
[94 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 487.9803 | --- | 100 | 480.0857 | 100 | SDS-HAA5 | mg/L | 2.218 | --- | 936.4268 | --- | 98.6226 | 924.4177 | 99.7601 | SDS-HAA5 | mg/L | 0 | --- | 322.067 | --- | 100 | 317.9037 | 100 | SDS-HAA5 | mg/L | 0 | --- | 220.5938 | --- | 100 | 217.9354 | 100 | SDS-CDb, mg/L | 5.8195 | 6.5377 | 5.3742 | 5.002 | SDS-CDb, mg/L | 4.1848 | 5.0842 | 3.6271 | 3.161
[94 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 529.7515 | --- | 100 | 521.1812 | 100 | SDS-HAA6 | mg/L | 3.463 | --- | 1011.4336 | --- | 98.0191 | 998.4762 | 99.6532 | SDS-HAA6 | mg/L | 0 | --- | 349.636 | --- | 100 | 345.1163 | 100 | SDS-HAA6 | mg/L | 0 | --- | 239.4767 | --- | 100 | 236.5907 | 100 | TOCb, mg/L | 3.9745 | 3.9438 | 3.9147 | 3.8947 | TOCb, mg/L | 2.2022 | 2.1638 | 2.1273 | 2.1024
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.12778 | 0.12551 | 0.12632 | 0.12624 | UV254 b, cm-1 | 0.066294 | 0.063456 | 0.064473 | 0.064369
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 93.4297 | 109.3221 | 80.495 | 75.3717 | Bromideb, ug/L | 72.4726 | 92.3739 | 56.275 | 49.8594
[133 empty] | Alkb, mg/L CaCO3 | 31.4982 | 34.234 | 30.0691 | 30.0027 | Alkb, mg/L CaCO3 | 21.8741 | 25.3 | 20.0846 | 20.0013
[133 empty] | T-Hdb, mg/L CaCO3 | 117.6039 | 138.7531 | 110.5252 | 107.4677 | T-Hdb, mg/L CaCO3 | 75.3769 | 101.8613 | 66.5126 | 62.6838
[133 empty] | Ca-Hdb, mg/L CaCO3 | 111.9032 | 130.784 | 104.8245 | 101.767 | Ca-Hdb, mg/L CaCO3 | 72.5266 | 96.1703 | 63.6622 | 59.8335
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on AA10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on BJ26: TSC_ADM: Permeate and concentrate flow rates were not reported at 145.1 hours because of the corresponding cleaning event.
Note on CD7: TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Print All Fields

## TFC. 1st Quarter
FIELD-SET 4: Membrane D, Run 1 (FILE: Margate1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.82566 | [45 empty] | Recovery during sample collection (decimal) | 0.74 | [10 empty] | Recovery during sample collection (decimal) | 0.87 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.31 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | TFC 8921S-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-02-26 | 1999-03-01 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.8 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.5 | [7 empty] | Feed flow rate during sample collection (mL/min) | 12 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 9:20 | 10:55 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 300 | [10 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [7 empty] | Influent flow rate during sample collection (mL/min) | 300 | [6 empty] | SDS-THM4F, ug/L | 210.245 | 210.245 | 210.245 | 210.245 | SDS-THM4F, ug/L | 210.245 | 210.245 | 210.245 | 210.245 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 46.2 | 119.2 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 30.5025 | 49.598 | 13.272 | 8.916 | SDS-THM4p, ug/L | 30.5025 | 49.598 | 13.272 | 8.916 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.33 | 6.37 | 6.35 | 0.62992 | 1999-02-12 | 13:50 | 0 | 20 |  |  | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 16.0176 | 100.5166 | 29.6864 | 98.9548 | 0.70049 |  |  | 1999-02-24 | 10:44 | 0 | 24.4 | 113.6 | 113.2 | 300 | 6.6149 | 2.66 |  | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.0642 | 1434.4731 | 245.5156 | 1408.257 | 11.7585 | 101.6415 | 0.13837 | 5.91 |  |  | 219.504 |  |  | 1499.1598 |  | 62.5739 | 1485.0518 | 85.2191 | 0.039 |  |  | 1.1984 |  | 89.502 | 1.1856 | 96.7105 | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 161.0335 | 161.0335 | 161.0335 | 161.0335 | SDS-HAA5F, ug/L | 161.0335 | 161.0335 | 161.0335 | 161.0335 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.24251 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1999-02-12 | 16:25 | 2.5 | 22.5 | 78.5 | 78.2 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.8767 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 77.6495 | 0.19159 | 1999-02-24 | 14:29 | 3.8 | 24.9 | 125.6 | 125.3 | 300 | 6.6149 | 2.66 |  | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 13.8579 | 1434.4731 | 245.5156 | 1408.257 | 11.7585 | 113.6915 | 0.12189 | 6 |  |  | 289.713 |  |  | 1324.5614 |  | 50.6031 | 1313.1523 | 77.9376 | 0.055 |  |  | 1.1586 |  | 85.1952 | 1.1464 | 95.2024 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 9.647 | 15.407 | 3.978 | 3.001 | SDS-HAA5p, ug/L | 9.647 | 15.407 | 3.978 | 3.001 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 66.3 | 73 | 69.65 | 9.6195 | 1999-02-13 | 10:00 | 20 | 22.5 | 77.5 | 77.2 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.8767 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 76.6495 | 0.19409 | 1999-02-24 | 16:32 | 5.8 | 25.1 | 130.2 | 130 | 300 | 6.6149 | 2.66 |  | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 13.7762 | 1434.4731 | 245.5156 | 1408.257 | 11.7585 | 118.3415 | 0.11641 | 6.02 | 6.45 | 6.92 | 289.713 | 556.14 | 1830.84 | 1324.5614 | 27.6528 | 50.6031 | 1313.1523 | 77.9376 | 0.056 | 0.372 | 1.473 | 1.1561 | 21.5141 | 84.926 | 1.144 | 95.1048 | [8 empty] | Sampling date | MM/DD/YY | 1999-02-26 | 1999-02-26 | --- | --- | 1999-02-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-27 | 1999-02-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-28 | 1999-02-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-28 | 1999-02-28 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 924.25 | 924.25 | 924.25 | 924.25 | SDS-TOXF, ug Cl- /L | 924.25 | 924.25 | 924.25 | 924.25 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 571 | 602 | 586.5 | 5.2856 | 1999-02-14 | 12:30 | 46.7 | 22.8 | 77.3 | 77 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.7453 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 76.4495 | 0.19288 | 1999-02-25 | 7:58 | 12.3 | 24.2 | 140 | 139.6 | 300 | 6.6149 | 2.66 |  | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.1476 | 1434.4731 | 245.5156 | 1408.257 | 11.7585 | 128.0415 | 0.11049 | 6.12 |  |  | 339.747 |  |  | 1200.1349 |  | 42.0721 | 1190.6492 | 71.4654 | 0.066 |  |  | 1.1312 |  | 82.2342 | 1.1195 | 94.1044 | [8 empty] | Sampling time | hh:mm | 2:00 | 2:00 | --- | --- | 2:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 0:05 | 0:05 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 0:50 | 0:50 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:54 | 15:54 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 85.525 | 146.5 | 34.6 | 28.5 | SDS-TOXp, ug Cl- /L | 85.525 | 146.5 | 34.6 | 28.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 284 | 286 | 285 | 0.70175 | 1999-02-15 | 9:20 | 67.5 | 23.2 | 78.7 | 78.5 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.572 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 77.8995 | 0.18706 | 1999-02-25 | 13:06 | 26.4 | 25.1 | 139.2 | 138.9 | 300 | 6.6149 | 2.66 |  | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 13.7762 | 1434.4731 | 245.5156 | 1408.257 | 11.7585 | 127.2915 | 0.10823 | 6.1 |  |  | 283.257 |  |  | 1340.6164 |  | 51.7038 | 1328.9592 | 78.6858 | 0.044 |  |  | 1.1859 |  | 88.1561 | 1.1733 | 96.2501 | [8 empty] | Operation time | hh.hh | 32.2 | 32.2 | --- | --- | 32.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 62.3 | 62.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 86.6 | 86.6 | --- | --- | --- | --- | --- | Cumulative time | hr | 101.3 | 101.3 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 12.3 | 12.3 | 12.3 | 12.3 | SDS-CDF, mg/L | 12.3 | 12.3 | 12.3 | 12.3 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 15 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 267 | 269 | 268 | 0.74627 | 1999-02-15 | 14:45 | 72.9 | 23.7 | 78.8 | 78.6 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.3582 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 77.9995 | 0.18408 | 1999-02-26 | 9:19 | 46.6 | 23.7 | 122.9 | 122.7 | 300 | 5.751 | 2.66 |  | 8.411 | 0.24449 | 0.68375 | 34.6676 | 13.1264 | 12.4831 | 1352.7524 | 232.0936 | 1331.2692 | 11.0992 | 111.7008 | 0.11176 | 6.02 | 6.42 | 6.98 | 267.117 | 510.6 | 1988.52 | 1277.0292 | 35.7799 | 54.4558 | 1267.3491 | 78.9232 | 0.038 | 0.39 | 1.76 | 1.0926 | 37.9232 | 89.7712 | 1.0824 | 96.4894 | [8 empty] | pH | --- | 6.34 | 6.35 | 6.345 | 0.1576 | 7.15 | --- | --- | --- | --- | --- | pH | --- | 6.5 | 8.22 | --- | --- | --- | --- | --- | pH | --- | 5.91 | 6.99 | --- | --- | --- | --- | --- | pH | --- | 6.14 | 6.83 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.905 | 4.92 | 2.82 | 1.91 | SDS-CDp, mg/L | 3.905 | 4.92 | 2.82 | 1.91 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 56.5 | 1 | 0.7 | 15 | 14.3517 | 76.2041 | 299.4788 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.49 | 1.24 | 0.865 | 86.7052 | 1999-02-15 | 16:45 | 74.9 | 23.9 | 79 | 78.7 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.2736 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 78.1495 | 0.18264 | 1999-02-26 | 11:40 | 49 | 24.2 | 125.5 | 124.9 | 300 | 5.751 | 2.0219 |  | 7.7729 | 0.24449 | 0.73988 | 37.5955 | 13.1264 | 12.3 | 1515.2604 | 259.9753 | 1491.1964 | 12.4325 | 112.7675 | 0.10907 | [27 empty] | Temperature | oC | 23.9 | 23.9 | 23.9 | 0 | 23.9 | --- | --- | --- | --- | --- | Temperature | oC | 24.3 | 24.3 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.4 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 11 | 11 | 11 | 11 | TOCF, mg/L | 11 | 11 | 11 | 11 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.265 | 2 | 0.9 | 15 | 39.785 | 101.6375 | 299.4788 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.4 | 0.3 | 0.35 | 28.5714 | 1999-02-16 | 9:10 | 91.3 | 23.2 | 80.9 | 80.5 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.572 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 79.9995 | 0.18215 | 1999-02-26 | 14:49 | 52.1 | 24.5 | 126.6 | 126.5 | 300 | 5.751 | 2.0219 |  | 7.7729 | 0.24449 | 0.73988 | 37.5955 | 13.1264 | 12.1914 | 1515.2604 | 259.9753 | 1491.1964 | 12.4325 | 114.1175 | 0.10683 | 5.82 |  |  | 381.672 |  |  | 1169.1087 |  | 34.9238 | 1161.561 | 67.1415 | 0.033 |  |  | 1.3343 |  | 91.1171 | 1.3218 | 97.5035 | [8 empty] | Alkalinity | mg/L as CaCO3 | 27.6 | 28.8 | 28.2 | 4.2553 | 246.9 | 187.6231 | 24.0085 | 59.5118 | 186.0894 | 84.846 | Alkalinity | mg/L as CaCO3 | 39 | 398.8 | 274.7692 | 31.101 | 44.0057 | 272.5471 | 85.6905 | Alkalinity | mg/L as CaCO3 | 15.9 | 143.8 | 123.4 | 14.1864 | 77.1716 | 122.325 | 87.0018 | Alkalinity | mg/L as CaCO3 | 12 | 85 | 95.5507 | -12.4126 | 82.771 | 94.6442 | 87.3209 | TOCp, mg/L | 1.09 | 2.04 | 0.53 | 0.4 | TOCp, mg/L | 1.09 | 2.04 | 0.53 | 0.4 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 9.265 | 71.1175 | 299.4788 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 10.6 | 11.4 | 11 | 7.2727 | 1999-02-16 | 13:40 | 95.8 | 23.5 | 80.7 | 80.5 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.4434 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 79.8995 | 0.18077 | 1999-02-26 | 15:57 | 53.3 | 24.6 | 127.3 | 127.1 | 300 | 5.751 | 0.84252 |  | 6.5936 | 0.24449 | 0.87222 | 44.499 | 13.1264 | 12.1554 | 2114.069 | 362.7137 | 2080.4953 | 17.3457 | 109.8543 | 0.11065 | 5.84 | 6.1 | 7.88 | 391.932 | 520.26 | 3381 | 1914.6245 | 43.3711 | 33.1744 | 1900.0294 | 79.3723 | 0.036 | 0.342 | 1.85 | 2.6616 | -43.8718 | 90.3096 | 2.6365 | 98.6345 | [8 empty] | Total dissolved solids | mg/L | 240.5 | 294 | 267.25 | 20.0187 | 1988 | 1495.1346 | 24.792 | 54.4331 | 1483.3224 | 81.983 | Total dissolved solids | mg/L | 392 | 3380 | 1888.1538 | 44.1375 | 33.1628 | 1874.0526 | 79.0828 | Total dissolved solids | mg/L | 112 | 1020 | 1061 | -4.0196 | 80.9037 | 1051.51 | 89.3487 | Total dissolved solids | mg/L | 94 | 702 | 807.7681 | -15.0667 | 83.9727 | 800.0237 | 88.2503 | UV254 F, cm-1 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | UV254 F, cm-1 | 0.3715 | 0.3715 | 0.3715 | 0.3715 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 7.085 | 68.9375 | 299.4788 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.387 | 0.356 | 0.3715 | 8.3445 | 1999-02-16 | 16:35 | 98.7 | 23.3 | 81.9 | 81.7 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.529 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 81.0995 | 0.17915 | 1999-02-27 | 10:10 | 71.4 | 24 | 139.2 | 139 | 300 | 5.6132 | 0.84252 |  | 6.4557 | 0.24449 | 0.86949 | 45.4707 | 12.8118 | 12.0763 | 2096.5473 | 359.8471 | 2064.0527 | 17.2045 | 121.8955 | 0.099071 | [27 empty] | Total hardness | mg/L as CaCO3 | 111 | 111 | 111 | 0 | 956 | 780.2308 | 18.3859 | 61.0526 | 773.7928 | 85.6551 | Total hardness | mg/L as CaCO3 | 180 | 1680 | 987.6923 | 41.2088 | 36.8421 | 980.0798 | 81.6341 | Total hardness | mg/L as CaCO3 | 51.4 | 522 | 518.6 | 0.65134 | 81.9649 | 513.928 | 89.9986 | Total hardness | mg/L as CaCO3 | 37 | 395 | 396.4203 | -0.35957 | 87.0175 | 392.5206 | 90.5737 | UV254 p, cm-1 | 0.032 | 0.053 | 0.012 | 0.009 | UV254 p, cm-1 | 0.032 | 0.053 | 0.012 | 0.009 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 846 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.6509 | 3.1228 | 3.3869 | 15.5936 | 1999-02-17 | 8:50 | 115 | 22.8 | 82.9 | 82.7 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.7453 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 82.0995 | 0.1796 | 1999-02-27 | 10:20 | 73.8 | 24.9 | 116.6 | 116.4 | 300 | 5.751 | 7.048 |  | 12.799 | 0.24449 | 0.44933 | 22.4393 | 13.1264 | 12.0481 | 934.2763 | 160.2951 | 919.439 | 7.6656 | 108.8344 | 0.1107 | 5.54 |  |  | 88.308 |  |  | 993.0165 |  | 84.9432 | 984.3448 | 91.0288 | 0.018 |  |  | 0.65995 |  | 95.1548 | 0.6538 | 97.2469 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 104 | 104 | 104 | 0 | 893 | 734.7692 | 17.719 | 61.194 | 728.7012 | 85.728 | Calcium hardness | mg/L as CaCO3 | 171 | 1580 | 917.1538 | 41.9523 | 36.194 | 910.1213 | 81.2113 | Calcium hardness | mg/L as CaCO3 | 48.1 | 489 | 487.9 | 0.22495 | 82.0522 | 483.502 | 90.0517 | Calcium hardness | mg/L as CaCO3 | 34.7 | 372 | 372.8159 | -0.21934 | 87.0522 | 369.1474 | 90.6 | BromideF, ug/L | 176.508 | 176.508 | 176.508 | 176.508 | BromideF, ug/L | 176.508 | 176.508 | 176.508 | 176.508 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 174.064 | 178.952 | 176.508 | 2.7693 | 1999-02-17 | 15:00 | 121.1 | 23.7 | 83.8 | 83.5 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.3582 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 82.9495 | 0.1731 | 1999-02-27 | 18:00 | 79.2 | 24.7 | 115.1 | 114.8 | 300 | 6.2 | 3.3 |  | 9.5 | 0.24449 | 0.65263 | 30.5789 | 14.1512 | 13.0657 | 1277.222 | 218.8577 | 1255.3491 | 10.4743 | 104.4757 | 0.12506 | 5.61 | 6.2 | 6.8 | 111.946 | 521.64 | 1020.76 | 1478.0863 | -44.8025 | 80.9129 | 1463.9695 | 92.3533 | 0.018 | 0.387 | 1.039 | 1.0357 | 0.32228 | 95.1548 | 1.0251 | 98.2441 | [8 empty] | Turbidity | ntu | 0.02 | 0.02 | 0.02 | 0 | 0.45 | 3.27 | -626.6667 | 97.6879 | 3.2387 | 99.3825 | Turbidity | ntu | 0.2 | 0.91 | 5.3154 | -484.1082 | 76.8786 | 5.2672 | 96.2029 | Turbidity | ntu | 0.02 | 0.38 | 1.71 | -350 | 97.6879 | 1.6931 | 98.8187 | Turbidity | ntu | 0.04 | 0.24 | 1.2357 | -414.8551 | 95.3757 | 1.2227 | 96.7285 | Bromidep, ug/L | 132.2435 | 133.716 | 52.797 | 42.309 | Bromidep, ug/L | 132.2435 | 133.716 | 52.797 | 42.309 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 15 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 13 | 13 | 13 | 0 | 1999-02-18 | 10:00 | 140.2 | 23.7 | 90.2 | 90 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.3582 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 89.3995 | 0.16061 | 1999-02-28 | 8:50 | 94 | 24.5 | 115.4 | 115.2 | 300 | 6.5 | 5.5 |  | 12 | 0.24449 | 0.54167 | 24 | 14.8359 | 13.7791 | 1064.2897 | 182.2164 | 1045.1781 | 8.7252 | 106.5748 | 0.12929 | 5.72 |  | 6.77 | 91.43 |  | 797.28 | 1171.5827 | -46.9475 | 84.4109 | 1159.8811 | 92.1173 | 0.013 |  | 0.72 | 0.79518 | -10.4419 | 96.5007 | 0.78671 | 98.3475 | [8 empty] | Ammonia | mg NH3-N / L | 0.31 | 0.28 | 0.295 | 10.1695 | 0.8 | 0.50654 | 36.6827 | 15.7143 | 0.5045 | 41.5267 | Ammonia | mg NH3-N / L | 0.32 | 0.66 | 0.55077 | 16.5501 | 8.5714 | 0.54859 | 41.6691 | Ammonia | mg NH3-N / L | 0.21 | 0.61 | 0.49 | 19.6721 | 40 | 0.4872 | 56.8966 | Ammonia | mg NH3-N / L | 0.16 | 0.52 | 0.43536 | 16.2765 | 54.2857 | 0.43237 | 62.9951 | AlkF, mg/L CaCO3 | 69.65 | 69.65 | 69.65 | 69.65 | AlkF, mg/L CaCO3 | 69.65 | 69.65 | 69.65 | 69.65
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 63.2 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.81 | 0.59 | 0.7 | 31.4286 | 1999-02-18 | 14:16 | 144.2 | 24.1 | 86.1 | 85.9 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.1895 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 85.2995 | 0.16635 | 1999-02-28 | 9:50 | 95 | 24.5 | 116.2 | 115.9 | 300 | 5.8907 | 15.1491 |  | 21.0398 | 0.24449 | 0.27998 | 13.2587 | 13.4451 | 12.4874 | 763.6322 | 130.9659 | 751.2095 | 6.2645 | 109.7855 | 0.11374 | 5.72 |  |  | 97.79 |  |  | 776.5325 |  | 83.3265 | 769.8688 | 87.2978 | 0.011 |  |  | 0.51168 |  | 97.039 | 0.50676 | 97.8294 | [8 empty] | Total organic carbon | mg/L | 1.11 | 1.07 | 1.09 | 3.6697 | 51.1 | 39.2054 | 23.2771 | 90.0909 | 38.8387 | 97.1935 | Total organic carbon | mg/L | 2.04 | 101.8 | 70.9631 | 30.2917 | 81.4545 | 70.3135 | 97.0987 | Total organic carbon | mg/L | 0.53 | 22.6 | 21.47 | 5 | 95.1818 | 21.2606 | 97.5071 | Total organic carbon | mg/L | 0.4 | 15.2 | 15.7623 | -3.6995 | 96.3636 | 15.5956 | 97.4352 | Alkp, mg/L CaCO3 | 28.2 | 39 | 15.9 | 12 | Alkp, mg/L CaCO3 | 28.2 | 39 | 15.9 | 12
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0021667 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 12.19 | 12.41 | 12.3 | 1.7886 | 1999-02-18 | 17:07 | 147.3 | 24.1 | 90.8 | 90.5 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.1895 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 89.9495 | 0.15775 | 1999-02-28 | 13:45 | 99 | 24.6 | 115.1 | 114.9 | 300 | 6.8 | 15.5 |  | 22.3 | 0.24449 | 0.30493 | 12.4529 | 15.5206 | 14.3725 | 784.8985 | 134.2682 | 770.1509 | 6.4326 | 108.5674 | 0.13238 | 5.42 |  |  | 93.345 |  |  | 802.8519 |  | 84.0844 | 794.8108 | 88.2557 | 0.01 |  |  | 0.53009 |  | 97.3082 | 0.5242 | 98.0923 | [8 empty] | UV254 | cm-1 | 0.032 | 0.032 | 0.032 | 0 | 1.787 | 1.3378 | 25.1388 | 91.3863 | 1.3252 | 97.5853 | UV254 | cm-1 | 0.053 | 3.3345 | 2.503 | 24.9363 | 85.7335 | 2.4799 | 97.8628 | UV254 | cm-1 | 0.012 | 0.372 | 0.731 | -96.5054 | 96.7699 | 0.72381 | 98.3421 | UV254 | cm-1 | 0.009 | 0.504 | 0.53436 | -6.0243 | 97.5774 | 0.52866 | 98.2976 | T-HdF, mg/L CaCO3 | 285 | 285 | 285 | 285 | T-HdF, mg/L CaCO3 | 285 | 285 | 285 | 285
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | 1999-02-19 | 7:14 | 161.4 | 23.7 | 90.7 | 90.5 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.3582 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 89.8995 | 0.15971 | 1999-02-28 | 19:00 | 104.4 | 24.5 | 115 | 114.8 | 300 | 6.7 | 15.2 |  | 21.9 | 0.24449 | 0.30594 | 12.6986 | 15.2924 | 14.2031 | 785.7575 | 134.4531 | 771.2117 | 6.4403 | 108.4597 | 0.13095 | 5.46 | 6.29 | 6.38 | 93.98 | 514.05 | 702.033 | 803.5976 | -14.4672 | 83.9761 | 795.6736 | 88.1886 | 0.01 | 0.389 | 0.506 | 0.53085 | -4.9102 | 97.3082 | 0.52503 | 98.0953 | [8 empty] | SUVA | L/(mg*m) | 2.8829 | 2.9907 | 2.9368 | 3.6697 | 3.4971 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.598 | 3.2755 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.2642 | 1.646 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.25 | 3.3158 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 111 | 180 | 51.4 | 37 | T-Hdp, mg/L CaCO3 | 111 | 180 | 51.4 | 37
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.6 | 7.43 | 7.515 | 2.2621 | 36210 | 0.50347 | 166.2 | 23.7 | 94.4 | 94.2 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.3582 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 93.5995 | 0.1534 | 1999-03-01 | 10:55 | 119.2 | 23.5 | 107 | 106.8 | 300 | 6.6 | 14.4 |  | 21 | 0.24449 | 0.31429 | 13.2857 | 15.0641 | 14.4108 | 793.0951 | 135.747 | 778.6335 | 6.5012 | 100.3988 | 0.14354 | [27 empty] | Bromide | mg/L | 98.434 | 166.053 | 132.2435 | 51.1322 | --- | 302.4916 | --- | 25.0779 | 300.8538 | 56.0439 | Bromide | mg/L | 133.716 | --- | 462.8852 | --- | 24.2437 | 459.7828 | 70.9176 | Bromide | mg/L | 52.797 | --- | 300.219 | --- | 70.088 | 297.7448 | 82.2677 | Bromide | mg/L | 42.309 | --- | 236.8003 | --- | 76.03 | 234.6901 | 81.9724 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | .7 ft/sec @ 15 gfd, 10% recovery | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 23.52 | 23 | 23.26 | 2.2356 | 36210 | 0.62361 | 169.1 | 24 | 94.2 | 94 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.2315 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 93.3995 | 0.15237 | 1999-03-04 | 9:55 | 119.2 | [6 empty] | X | [39 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 104 | 171 | 48.1 | 34.7 | Ca-Hdp, mg/L CaCO3 | 104 | 171 | 48.1 | 34.7
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 891.5 | 957 | 924.25 | 7.0868 | 36214 | 0.71806 | 170.4 | 17.3 | 99.3 | 99.1 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 17.3484 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 98.4995 | 0.17613 | 1999-03-04 | 12:19 | 123 | 23.2 | 105 | 104.7 | 300 | 6.8 | 15.4 |  | 22.2 | 0.24449 | 0.30631 | 12.5135 | 15.5206 | 14.9798 | 786.0963 | 134.4731 | 771.3262 | 6.4424 | 98.4076 | 0.15222 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.09 | 1.1 | 1.095 | 0.91324 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.83 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.93 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.59 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 17 | [14 empty] | SDS-CHCl3 | mg/L | 148.418 | 155.362 | 151.89 | 4.5717 | 36215 | 0.36944 | 186 | 24.4 | 91.7 | 91.4 | 300 | 6.6149 | 2.66 | 9.2749 | 0.24449 | 0.71321 | 31.3455 | 15.0982 | 14.0642 | 100.5166 | 29.6864 | 98.9548 | 0.70049 | 90.8495 | 0.15481 | 1999-03-05 | 8:25 | 143 | 23.5 | 105.8 | 105.6 | 300 | 5.751 | 15.1491 |  | 20.9001 | 0.24449 | 0.27517 | 13.354 | 13.1264 | 12.5571 | 759.6722 | 130.338 | 747.6078 | 6.233 | 99.467 | 0.12624 | [27 empty] | SDS-Cl2 demand | mg/L | 3.91 | 3.9 | 3.905 | 0.25608 | --- | 36.1935 | --- | 68.252 | 35.8828 | 89.1174 | SDS-Cl2 demand | mg/L | 4.92 | --- | 61.6892 | --- | 60 | 61.1542 | 91.9548 | SDS-Cl2 demand | mg/L | 2.82 | --- | 21.78 | --- | 77.0732 | 21.5904 | 86.9386 | SDS-Cl2 demand | mg/L | 1.91 | --- | 16.968 | --- | 84.4715 | 16.8046 | 88.6341 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 49.194 | 52.654 | 50.924 | 6.7944 | [70 empty] | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 76.9128 | 86.0551 | 70.1847 | 68.6662 | Qp/QT (THM4), % | 96.9415 | 108.4645 | 88.4614 | 86.5474
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | 0.85 | [14 empty] | SDS-DBCM | mg/L | 7.511 | 7.351 | 7.431 | 2.1531 | [70 empty] | SDS-Chlorination pH | --- | 7.44 | 7.57 | 7.505 | 1.7322 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.45 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.57 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | 36 | 36
|  | (e.g., solute type and concentration) | 500 mg/L NaCl @ 80 psi | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 23.83 | 23.73 | 23.78 | 0.42052 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.33 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.17 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.08 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 44.5979 | 35.7144 | 50.8045 | 52.5186 | SDS-HAA5b, ug/L | 14.2772 | NA | 22.1001 | 24.2605
|  | Variability of rejection of reference solute (%) | 5 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 205.123 | 215.367 | 210.245 | 4.8724 | [70 empty] | SDS-TOX | mg Cl- /L | 85.65 | 85.4 | 85.525 | 0.29231 | --- | 3311.3904 | --- | 90.7466 | 3280.3576 | 97.3928 | SDS-TOX | mg Cl- /L | 146.5 | --- | 6129.1923 | --- | 84.1493 | 6072.8054 | 97.5876 | SDS-TOX | mg Cl- /L | 34.6 | --- | 1813.9 | --- | 96.2564 | 1796.107 | 98.0736 | SDS-TOX | mg Cl- /L | 28.5 | --- | 1326.6884 | --- | 96.9164 | 1312.6031 | 97.8287 | SDS-TOXb, ug Cl- /L | 279.1631 | 254.9562 | 299.8514 | 309.1724 | SDS-TOXb, ug Cl- /L | 111.1778 | NA | 137.2535 | 149.0017
|  | Standard testing recovery (%) | 10 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.903 | 9.018 | 7.9605 | 26.5687 | [70 empty] | SDS-CHCl3 | mg/L | 7.786 | 7.855 | 7.8205 | 0.8823 | --- | 561.934 | --- | 94.8512 | 556.6034 | 98.595 | SDS-CHCl3 | mg/L | 14.107 | --- | 1073.9762 | --- | 90.7124 | 1063.987 | 98.6741 | SDS-CHCl3 | mg/L | 3.12 | --- | 300.66 | --- | 97.9459 | 297.6846 | 98.9519 | SDS-CHCl3 | mg/L | 2.742 | --- | 218.8985 | --- | 98.1947 | 216.5532 | 98.7338 | SDS-CDb, mg/L | 5.8432 | 5.9491 | 5.6465 | 5.1656 | SDS-CDb, mg/L | 4.1618 | NA | 3.9139 | 3.3077
|  | Standard testing pH | 7.5 | [14 empty] | SDS-DCAA* | mg/L | 56.34 | 59.54 | 57.94 | 5.523 | [70 empty] | SDS-BDCM | mg/L | 10.828 | 10.996 | 10.912 | 1.5396 | --- | 164.8043 | --- | 78.572 | 163.3239 | 93.3188 | SDS-BDCM | mg/L | 18.035 | --- | 271.0273 | --- | 64.5845 | 268.6429 | 93.2866 | SDS-BDCM | mg/L | 4.543 | --- | 97.305 | --- | 91.0789 | 96.3774 | 95.2862 | SDS-BDCM | mg/L | 3.334 | --- | 72.305 | --- | 93.453 | 71.5567 | 95.3408 | TOCb, mg/L | 3.3779 | 3.2895 | 3.6517 | 3.7214 | TOCb, mg/L | 1.3931 | NA | 1.7381 | 1.826
|  | Acceptable range of operating pressures | 0-350 | [14 empty] | SDS-TCAA* | mg/L | 88.66 | 95.87 | 92.265 | 7.8144 | [70 empty] | SDS-DBCM | mg/L | 10.225 | 10.061 | 10.143 | 1.6169 | --- | -0.28777 | --- | -36.4958 | -0.18743 | 5511.758 | SDS-DBCM | mg/L | 15.236 | --- | -44.8025 | --- | -105.033 | -44.2366 | 134.4421 | SDS-DBCM | mg/L | 4.592 | --- | 10.27 | --- | 38.2048 | 10.2132 | 55.0387 | SDS-DBCM | mg/L | 2.84 | --- | 9.4936 | --- | 61.7817 | 9.4214 | 69.856 | UV254 b, cm-1 | 0.11038 | 0.097414 | 0.11919 | 0.12258 | UV254 b, cm-1 | 0.042384 | NA | 0.053481 | 0.057766
|  | Acceptable range of operating pH values | 4-11 | [14 empty] | SDS-MBAA* | mg/L | 1.135 | 1.37 | 1.2525 | 18.7625 | [70 empty] | SDS-CHBr3 | mg/L | 1.724 | 1.53 | 1.627 | 11.9238 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.22 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.017 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 142.4629 | 139.6833 | 89.6817 | 84.3586 | Bromideb, ug/L | 133.5973 | NA | 67.0716 | 60.3623
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | 1.567 | 1.664 | 1.6155 | 6.0043 | [70 empty] | SDS-THM4 | mg/L | 30.563 | 30.442 | 30.5025 | 0.39669 | --- | 721.8198 | --- | 85.4919 | 715.1693 | 95.7349 | SDS-THM4 | mg/L | 49.598 | --- | 1285.3442 | --- | 76.4094 | 1273.6972 | 96.106 | SDS-THM4 | mg/L | 13.272 | --- | 407.218 | --- | 93.6874 | 403.2785 | 96.709 | SDS-THM4 | mg/L | 8.916 | --- | 300.6972 | --- | 95.7592 | 297.5313 | 97.0033 | Alkb, mg/L CaCO3 | 37.7696 | 43.2741 | 31.9257 | 30.0639 | Alkb, mg/L CaCO3 | 29.4678 | NA | 22.102 | 19.7554
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 12.951 | 14.618 | 13.7845 | 12.0933 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 151.1717 | 194.6421 | 121.0484 | 114.7078 | T-Hdb, mg/L CaCO3 | 116.3219 | NA | 78.3543 | 70.3625
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 3.485 | 3.608 | 3.5465 | 3.4682 | --- | 212.7523 | --- | 93.879 | 210.7397 | 98.3171 | SDS-DCAA* | mg/L | 5.742 | --- | 407.2651 | --- | 90.0897 | 403.4807 | 98.5769 | SDS-DCAA* | mg/L | 1.532 | --- | 114.348 | --- | 97.3559 | 113.2198 | 98.6469 | SDS-DCAA* | mg/L | 1.633 | --- | 83.2373 | --- | 97.1816 | 82.3519 | 98.017 | Ca-Hdb, mg/L CaCO3 | 141.863 | 184.5265 | 113.6637 | 107.8017 | Ca-Hdb, mg/L CaCO3 | 109.016 | NA | 73.4735 | 66.0849
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L extended | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 3.28 | 3.535 | 3.4075 | 7.4835 | --- | 345.1671 | --- | 96.3068 | 341.8794 | 99.0033 | SDS-TCAA* | mg/L | 5.615 | --- | 672.1535 | --- | 93.9143 | 665.8713 | 99.1567 | SDS-TCAA* | mg/L | 1.177 | --- | 183.353 | --- | 98.7243 | 181.5312 | 99.3516 | SDS-TCAA* | mg/L | 1.368 | --- | 133.1028 | --- | 98.5173 | 131.6735 | 98.9611
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 154.605 | 167.462 | 161.0335 | 7.9841 | [70 empty] | SDS-DBAA* | mg/L | 2.728 | 2.658 | 2.693 | 2.5993 | --- | -1.4512 | --- | -66.6976 | -1.4114 | 290.8084 | SDS-DBAA* | mg/L | 4.05 | --- | -14.6769 | --- | -150.6964 | -14.5004 | 127.9302 | SDS-DBAA* | mg/L | 1.269 | --- | 1.962 | --- | 21.4485 | 1.9551 | 35.0918 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 167.556 | 182.08 | 174.818 | 8.3081 | [70 empty] | SDS-BCAA* | mg/L | 4.076 | 4.064 | 4.07 | 0.29484 | --- | 41.4335 | --- | 70.4741 | 41.074 | 90.0911 | SDS-BCAA* | mg/L | 6.399 | --- | 63.2105 | --- | 53.5783 | 62.6751 | 89.7902 | SDS-BCAA* | mg/L | 1.73 | --- | 25.839 | --- | 87.4497 | 25.5979 | 93.2416 | SDS-BCAA* | mg/L | 1.483 | --- | 19.3113 | --- | 89.2415 | 19.1178 | 92.2428 | Qp/QT (HAA5), % | 70.7021 | 73.4986 | 68.1501 | 67.7288 | Qp/QT (HAA5), % | 88.5373 | 92.0392 | 85.3415 | 84.8139
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 83.1632 | 92.1716 | 76.0077 | 73.8873 | SDS-THM4b, ug/L | 51.1059 | 62.3867 | 42.1453 | 39.4901
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 331.2534 | 352.6143 | 317.9525 | 317.5694 | SDS-TOXb, ug Cl- /L | 181.6656 | 208.4149 | 165.0095 | 164.5296
[94 empty] | SDS-HAA5 | mg/L | 9.493 | 9.801 | 9.647 | 3.1927 | --- | 591.9028 | --- | 94.0093 | 586.3015 | 98.3546 | SDS-HAA5 | mg/L | 15.407 | --- | 1135.6108 | --- | 90.4324 | 1125.0529 | 98.6306 | SDS-HAA5 | mg/L | 3.978 | --- | 318.089 | --- | 97.5297 | 314.9479 | 98.7369 | SDS-HAA5 | mg/L | 3.001 | --- | 232.0336 | --- | 98.1364 | 229.5486 | 98.6927 | SDS-CDb, mg/L | 6.3646 | 6.8758 | 5.8394 | 5.263 | SDS-CDb, mg/L | 4.8673 | 5.5075 | 4.2096 | 3.4878
[94 empty] | SDS-HAA6 | mg/L | 13.569 | 13.865 | 13.717 | 2.1579 | --- | 633.3362 | --- | 92.1536 | 627.3755 | 97.8136 | SDS-HAA6 | mg/L | 21.806 | --- | 1198.8214 | --- | 87.5265 | 1187.728 | 98.1641 | SDS-HAA6 | mg/L | 5.708 | --- | 343.928 | --- | 96.7349 | 340.5458 | 98.3239 | SDS-HAA6 | mg/L | 4.484 | --- | 251.3449 | --- | 97.435 | 248.6664 | 98.1968 | TOCb, mg/L | 3.9934 | 4.4145 | 3.8647 | 3.8207 | TOCb, mg/L | 2.226 | 2.7533 | 2.0647 | 2.0097
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.13147 | 0.13741 | 0.1265 | 0.12598 | UV254 b, cm-1 | 0.070916 | 0.078355 | 0.064697 | 0.06405
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 145.212 | 145.0565 | 92.1988 | 85.6166 | Bromideb, ug/L | 137.3174 | 137.1226 | 70.9312 | 62.6886
[133 empty] | Alkb, mg/L CaCO3 | 40.344 | 47.1227 | 33.0193 | 30.6044 | Alkb, mg/L CaCO3 | 32.9513 | 41.44 | 23.779 | 20.7548
[133 empty] | T-Hdb, mg/L CaCO3 | 161.9783 | 207.8264 | 125.8013 | 117.0326 | T-Hdb, mg/L CaCO3 | 130.9451 | 188.3588 | 85.6423 | 74.6616
[133 empty] | Ca-Hdb, mg/L CaCO3 | 152.0485 | 196.7063 | 118.1379 | 109.9887 | Ca-Hdb, mg/L CaCO3 | 122.7988 | 178.722 | 80.3341 | 70.1292
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on AA10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on DN20: C. Rice: Consultant verified value; no explanation given.
Note on EB9: C. Rice: Consultant verified the reported recoveries for the 50% run; no explanations were given.
Print All Fields

## NF70. 2nd Quarter
FIELD-SET 1: Membrane A, Run 2 (FILE: Margate2.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [21 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.91418 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | NF70 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-05-03 | 1999-05-06 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 15.7 | [10 empty] | Feed flow rate during sample collection (mL/min) | 12.4 | [7 empty] | Feed flow rate during sample collection (mL/min) | 22 | [7 empty] | Feed flow rate during sample collection (mL/min) | 37 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 17:40 | 16:35 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 531 | [10 empty] | Influent flow rate during sample collection (mL/min) | 531 | [7 empty] | Influent flow rate during sample collection (mL/min) | 531 | [7 empty] | Influent flow rate during sample collection (mL/min) | 531 | [6 empty] | SDS-THM4F, ug/L | 182.8 | 182.8 | 182.8 | 182.8 | SDS-THM4F, ug/L | 182.8 | 182.8 | 182.8 | 182.8 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 6.1 | 76.7 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 8.45 | 15.4 | 3 | 6 | SDS-THM4p, ug/L | 8.45 | 15.4 | 3 | 6 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.97 | 6.54 | 6.755 | 6.3657 | 1999-05-01 | 16:41 | 1 | 23.7 | 93.6 | 93 | 531 | 11 | 4.7 | 15.7 | 0.40183 | 0.70064 | 32.8217 | 25.1069 | 23.8765 | 98.7192 | 29.1836 | 97.2787 | 0.68815 | 92.6118 | 0.25781 | 1999-05-03 | 11:30 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 122.15 | 122.15 | 122.15 | 122.15 | SDS-HAA5F, ug/L | 122.15 | 122.15 | 122.15 | 122.15 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32671 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1999-05-02 | 8:30 | [19 empty] | 1999-05-03 | 12:13 | 0.7 | 24.2 | 96.7 | 96.4 | 531 | 11 | 4.7 |  | 15.7 | 0.40183 | 0.70064 | 32.8217 | 25.1069 | 23.5262 | 1425.2755 | 119.9982 | 1398.2359 | 12.9176 | 83.6324 | 0.2813 | 5.96 |  |  | 216.855 |  |  | 1198.5894 |  | 57.5419 | 1188.4207 | 81.7527 | 0.011 |  |  | 0.74255 |  | 95.2174 | 0.73498 | 98.5034 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0.6 | 1.8 | 0 | 0 | SDS-HAA5p, ug/L | 0.6 | 1.8 | 0 | 0 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative charge | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 145 | 145 | 145 | 0 | 1999-05-02 | 11:43 | 20 | 23.2 | 51.4 | 50.5 | 620 | 6.5 | 2.8 | 9.3 | 0.46918 | 0.69892 | 65.6667 | 14.8359 | 14.3189 | 98.1915 | 29.2406 | 97.4686 | 0.68589 | 50.2641 | 0.28487 | 1999-05-03 | 14:40 | 3.1 | 25.2 | 104.1 | 103.3 | 531 | 11 | 4.8 |  | 15.8 | 0.40183 | 0.6962 | 32.6076 | 25.1069 | 22.841 | 1409.3044 | 118.6535 | 1382.5677 | 12.7728 | 90.9272 | 0.2512 | 6.05 |  |  | 109.251 |  |  | 1430.8519 |  | 78.6097 | 1417.163 | 92.2909 | 0.01 |  |  | 0.73417 |  | 95.6522 | 0.72667 | 98.6239 | [8 empty] | Sampling date | MM/DD/YY | 1999-05-03 | 1999-05-03 | --- | --- | 1999-05-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-04 | 1999-05-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-05 | 1999-05-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-06 | 1999-05-06 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 790.5 | 790.5 | 790.5 | 790.5 | SDS-TOXF, ug Cl- /L | 790.5 | 790.5 | 790.5 | 790.5 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 534.5 | 487 | 510.75 | 9.3 | 1999-05-02 | 16:00 | 24.3 | 23.4 | 51.5 | 50.7 | 620 | 6.5 | 2.7 | 9.2 | 0.46918 | 0.70652 | 66.3913 | 14.8359 | 14.2345 | 99.2311 | 29.5502 | 98.5006 | 0.69316 | 50.4068 | 0.28239 | 1999-05-03 | 17:40 | 6.1 | 25.4 | 103.9 | 103.4 | 531 | 11 | 4.8 |  | 15.8 | 0.40183 | 0.6962 | 32.6076 | 25.1069 | 22.7063 | 1409.3044 | 118.6535 | 1382.5677 | 12.7728 | 90.8772 | 0.24986 | 6 | 7.02 | 7.2 | 115.29 | 489.21 | 1345.086 | 1417.0125 | -5.3474 | 77.4273 | 1403.5295 | 91.7857 | BRML | 0.296 | 1.065 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 17:40 | 17:40 | --- | --- | 17:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:47 | 17:47 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:18 | 17:18 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:35 | 16:35 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | 36.7 | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | 36.7 | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 321 | 300 | 310.5 | 6.7633 | 1999-05-02 | 18:23 | 26.7 | 23.4 | 53.1 | 52.9 | 299 | 6.6 | 2.7 | 9.3 | 0.22627 | 0.70968 | 31.1505 | 15.0641 | 14.4535 | 100.0172 | 29.5384 | 98.4614 | 0.69701 | 52.303 | 0.27634 | 1999-05-04 | 10:55 | 23.4 | 25 | 118.5 | 118 | 531 | 10.9 | 1.2 |  | 12.1 | 0.40183 | 0.90083 | 42.8843 | 24.8787 | 22.7675 | 2918.0682 | 245.7241 | 2863.2122 | 26.4492 | 91.8008 | 0.24801 | 6.23 |  |  | 144.354 |  |  | 3838.847 |  | 71.7369 | 3800.928 | 96.2021 | 0.012 |  |  | 2.2102 |  | 94.7826 | 2.1876 | 99.4515 | [8 empty] | Operation time | hh.hh | 6.1 | 6.1 | --- | --- | 6.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 30.3 | 30.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 53.4 | 53.4 | --- | --- | --- | --- | --- | Cumulative time | hr | 76.7 | 76.7 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.35 | 11.35 | 11.35 | 11.35 | SDS-CDF, mg/L | 11.35 | 11.35 | 11.35 | 11.35 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 25 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 302 | 282 | 292 | 6.8493 | [21 empty] | 1999-05-04 | 14:55 | 27.4 | 25.4 | 129.7 | 129.1 | 531 | 11.1 | 1.3 |  | 12.4 | 0.40183 | 0.89516 | 41.8226 | 25.3352 | 22.9127 | 2834.4807 | 238.6014 | 2780.2165 | 25.6875 | 103.7125 | 0.22093 | 6.37 |  |  | 153.683 |  |  | 3559.5528 |  | 69.9103 | 3523.9548 | 95.6389 | 0.016 |  |  | 2.0572 |  | 93.0435 | 2.0359 | 99.2141 | [8 empty] | pH | --- | 6.46 | 6.48 | 6.47 | 0.30912 | 7.67 | --- | --- | --- | --- | --- | pH | --- | 6.54 | 8.06 | --- | --- | --- | --- | --- | pH | --- | 5.98 | 7.07 | --- | --- | --- | --- | --- | pH | --- | 5.85 | 6.67 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.68 | 3.53 | 1.83 | 1.58 | SDS-CDp, mg/L | 2.68 | 3.53 | 1.83 | 1.58 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 25 | 14.3517 | 90.8732 | 531.2481 | 10.952 | 15.6457 | 4.6937 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.21 | 0.35 | 0.28 | 50 | [21 empty] | 1999-05-04 | 17:47 | 30.3 | 25.5 | 129 | 129 | 531 | 11.1 | 1.3 |  | 12.4 | 0.40183 | 0.89516 | 41.8226 | 25.3352 | 22.8451 | 2834.4807 | 238.6014 | 2780.2165 | 25.6875 | 103.3125 | 0.22113 | 6.36 | 7.02 | 8.07 | 158.102 | 545.1 | 2790.3 | 3521.8214 | -26.2166 | 69.0451 | 3486.6639 | 95.4655 | 0.016 | 0.32 | 2.484 | 2.0572 | 17.1807 | 93.0435 | 2.0359 | 99.2141 | [8 empty] | Temperature | oC | 25.2 | 25.2 | 25.2 | 0 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 24.7 | 24.7 | --- | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | Temperature | oC | 21.9 | 21.9 | --- | --- | --- | --- | --- | TOCF, mg/L | 9.285 | 9.285 | 9.285 | 9.285 | TOCF, mg/L | 9.285 | 9.285 | 9.285 | 9.285 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.357 | 2 | 0.9 | 25 | 39.785 | 116.3065 | 531.2481 | 10.952 | 12.1689 | 1.2169 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.6 | 0.62 | 0.61 | 3.2787 | [21 empty] | 1999-05-05 | 11:24 | 47.5 | 23.9 | 117.9 | 117.4 | 531 | 11.3 | 11.3 |  | 22.6 | 0.40183 | 0.5 | 22.4956 | 25.7916 | 24.3831 | 942.2141 | 79.2859 | 923.8505 | 8.5375 | 109.1125 | 0.22347 | 5.78 |  |  | 61 |  |  | 960.5 |  | 88.0568 | 950.929 | 93.5852 | 0.009 |  |  | 0.451 |  | 96.087 | 0.4463 | 97.9834 | [8 empty] | Alkalinity | mg/L as CaCO3 | 23.7 | 23.9 | 23.8 | 0.84034 | 787.5 | 427.8 | 45.6762 | 83.5862 | 423.6192 | 94.3817 | Alkalinity | mg/L as CaCO3 | 41 | 980.5 | 1081 | -10.2499 | 71.7241 | 1070.0712 | 96.1685 | Alkalinity | mg/L as CaCO3 | 19 | 289 | 271 | 6.2284 | 86.8966 | 268.3898 | 92.9207 | Alkalinity | mg/L as CaCO3 | 15.5 | 200.5 | 200.5 | 0 | 89.3103 | 198.5664 | 92.194 | TOCp, mg/L | 0.27 | 0.41 | BMRL | BMRL | TOCp, mg/L | 0.27 | 0.41 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 25 | 9.265 | 85.7865 | 531.2481 | 10.952 | 21.9039 | 10.952 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 9.67 | 8.9 | 9.285 | 8.2929 | [21 empty] | 1999-05-05 | 15:57 | 52.1 | 24.5 | 107.7 | 106.9 | 531 | 10.7 | 10.6 |  | 21.3 | 0.40183 | 0.50235 | 23.9296 | 24.4222 | 22.6825 | 945.8875 | 79.6792 | 928.4329 | 8.5748 | 98.7252 | 0.22975 | 5.73 |  |  | 129.808 |  |  | 895.2858 |  | 74.5848 | 887.5734 | 85.375 | BRML |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 115 | 115.5 | 115.25 | 0.43384 | 1345.5 | 1433.5833 | -6.5465 | 77.4351 | 1419.9407 | 91.8835 | Total dissolved solids | mg/L | 158 | 2790 | 3685.5 | -32.0968 | 69.0651 | 3648.4314 | 95.6694 | Total dissolved solids | mg/L | 62.5 | 1056 | 959 | 9.1856 | 87.7631 | 949.7142 | 93.4191 | Total dissolved solids | mg/L | 63 | 692 | 702.6429 | -1.538 | 87.6652 | 695.9573 | 90.9477 | UV254 F, cm-1 | 0.23 | 0.23 | 0.23 | 0.23 | UV254 F, cm-1 | 0.23 | 0.23 | 0.23 | 0.23 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 25 | 7.085 | 83.6065 | 531.2481 | 10.952 | 36.5066 | 25.5546 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.325 | 0.135 | 0.23 | 82.6087 | [21 empty] | 1999-05-05 | 17:18 | 53.4 | 24 | 111.4 | 110.7 | 531 | 10.9 | 11.1 |  | 22 | 0.40183 | 0.49545 | 23.1364 | 24.8787 | 23.4505 | 934.983 | 78.7329 | 917.4065 | 8.4746 | 102.5754 | 0.22862 | 5.65 | 6.69 | 6.84 | 62.464 | 527.16 | 1056.02 | 950.9588 | 9.9488 | 87.7701 | 941.8396 | 93.3679 | BRML | 0.312 | 0.639 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 46.7 | 46.8 | 46.75 | 0.2139 | 852 | 925.9167 | -8.6757 | 84.9436 | 916.8187 | 94.9008 | Total hardness | mg/L as CaCO3 | 82.2 | 1790 | 2365.2 | -32.1341 | 73.5266 | 2341.2092 | 96.489 | Total hardness | mg/L as CaCO3 | 27.7 | 608 | 593.3 | 2.4178 | 91.0789 | 587.4416 | 95.2846 | Total hardness | mg/L as CaCO3 | 27.4 | 423 | 431.8286 | -2.0871 | 91.1755 | 427.6015 | 93.5922 | UV254 p, cm-1 | #DIV/0! | 0.0135 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.0135 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 600 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.3609 | 1.5169 | 2.4389 | 75.6107 | [21 empty] | 1999-05-06 | 10:20 | 70.5 | 23.3 | 112 | 111.2 | 531 | 11 | 25.2 |  | 36.2 | 0.40183 | 0.30387 | 13.6685 | 25.1069 | 24.1604 | 707.6882 | 59.5824 | 694.2623 | 6.4139 | 105.1861 | 0.22969 | 5.69 |  |  | 35.28 |  |  | 718.2964 |  | 93.0925 | 711.2219 | 95.0395 | BRML |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 43.9 | 43.9 | 43.9 | 0 | 799 | 870.9 | -8.9987 | 84.9658 | 862.3419 | 94.9092 | Calcium hardness | mg/L as CaCO3 | 77.6 | 1680 | 2221.6 | -32.2381 | 73.4247 | 2199.0698 | 96.4712 | Calcium hardness | mg/L as CaCO3 | 27.7 | 571 | 556.3 | 2.5744 | 90.5137 | 550.8249 | 94.9712 | Calcium hardness | mg/L as CaCO3 | 27.4 | 397 | 405.4 | -2.1159 | 90.6164 | 401.4492 | 93.1747 | BromideF, ug/L | 178.5 | 178.5 | 178.5 | 178.5 | BromideF, ug/L | 178.5 | 178.5 | 178.5 | 178.5 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 180 | 177 | 178.5 | 1.6807 | [21 empty] | 1999-05-06 | 13:39 | 73.8 | 23.4 | 112 | 111.2 | 531 | 11 | 25.2 |  | 36.2 | 0.40183 | 0.30387 | 13.6685 | 25.1069 | 24.0891 | 707.6882 | 59.5824 | 694.2623 | 6.4139 | 105.1861 | 0.22901 | 5.65 |  |  | 33.48 |  |  | 719.0821 |  | 93.4449 | 711.9808 | 95.2976 | BRML |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0 | 0 | 0 | #DIV/0! | 0.28 | 0.93333 | -233.3333 | 100 | 0.92367 | 100 | Turbidity | ntu | 0.09 | 1.42 | 1.99 | -40.1408 | 67.8571 | 1.97 | 95.4316 | Turbidity | ntu | 0 | 0.31 | 0.56 | -80.6452 | 100 | 0.5542 | 100 | Turbidity | ntu | BMRL | 0.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromidep, ug/L | 45 | 83 | 28 | 25 | Bromidep, ug/L | 45 | 83 | 28 | 25 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 24.7 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.2 | 12.2 | 12.2 | 0 | [21 empty] | 1999-05-06 | 16:35 | 76.7 | 20.5 | 121.7 | 121.3 | 530 | 11.2 | 25.8 |  | 37 | 0.40107 | 0.3027 | 13.3243 | 25.5634 | 26.7223 | 706.6536 | 59.4721 | 692.9773 | 6.4034 | 115.0966 | 0.23217 | [27 empty] | Ammonia | mg NH3-N / L | 0.35 | 0.32 | 0.335 | 8.9552 | 1.08 | 1.2517 | -15.8951 | 45.082 | 1.2422 | 73.0313 | Ammonia | mg NH3-N / L | 0.53 | 1.33 | 1.33 | 1.6695e-14 | 13.1148 | 1.3216 | 59.8969 | Ammonia | mg NH3-N / L | 0.33 | 0.99 | 0.89 | 10.101 | 45.9016 | 0.8842 | 62.6781 | Ammonia | mg NH3-N / L | 0.24 | 0.72 | 0.76857 | -6.746 | 60.6557 | 0.76305 | 68.5471 | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145 | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.83 | 0.87 | 0.85 | 4.7059 | [21 empty] | 1999-05-07 | 18:24 | 95.1 | 23.2 | 123.4 | 122.9 | 530 | 10.4 | 26 | X | 36.4 | 0.40107 | 0.28571 | 13.5604 | 23.7374 | 22.9102 | 691.7306 | 58.2984 | 679.301 | 6.2722 | 116.8778 | 0.19602 | 5.88 |  |  | 121.68 |  |  | 666.378 |  | 76.1762 | 661.0338 | 81.5925 | 0.011 |  |  | 0.3176 |  | 95.2174 | 0.31459 | 96.5034 | [8 empty] | Total organic carbon | mg/L | 0.28 | 0.26 | 0.27 | 7.4074 | 28.6 | 30.32 | -6.014 | 97.0921 | 30.009 | 99.1003 | Total organic carbon | mg/L | 0.41 | 78.9 | 89.16 | -13.0038 | 95.5843 | 88.2274 | 99.5353 | Total organic carbon | mg/L | BMRL | 18.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 23.8 | 41 | 19 | 15.5 | Alkp, mg/L CaCO3 | 23.8 | 41 | 19 | 15.5
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.37 | 11.33 | 11.35 | 0.35242 | [21 empty] | 1999-05-08 | 8:54 | 109.7 | 23.2 | 122.3 | 121.4 | 530 | 11.3 | 25.4 |  | 36.7 | 0.40107 | 0.3079 | 13.4414 | 25.7916 | 24.8928 | 711.3444 | 59.8563 | 697.4542 | 6.4454 | 115.4046 | 0.2157 | 5.89 | 7.02 | 7.02 | 63 | 518.88 | 692.34 | 709.9459 | -2.543 | 87.6652 | 703.0492 | 91.039 | BRML | 0.312 | 0.446 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.831 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.0135 | 2.5345 | 2.1785 | 14.0462 | 94.1304 | 2.1557 | 99.3738 | UV254 | cm-1 | BMRL | 0.631 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.4085 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 310.5 | 310.5 | 310.5 | 310.5 | T-HdF, mg/L CaCO3 | 310.5 | 310.5 | 310.5 | 310.5
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | [70 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 2.9056 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.2927 | 3.2123 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.3564 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.1544 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 46.75 | 82.2 | 27.7 | 27.4 | T-Hdp, mg/L CaCO3 | 46.75 | 82.2 | 27.7 | 27.4
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.49 | 7.5 | 7.495 | 0.13342 | [70 empty] | Bromide | mg/L | 48 | 42 | 45 | 13.3333 | --- | 490 | --- | 74.7899 | 485.395 | 90.7292 | Bromide | mg/L | 83 | --- | 1038 | --- | 53.5014 | 1027.9644 | 91.9258 | Bromide | mg/L | 28 | --- | 329 | --- | 84.3137 | 325.8823 | 91.4079 | Bromide | mg/L | 25 | --- | 244.2857 | --- | 85.9944 | 241.9937 | 89.6692 | Ca-HdF, mg/L CaCO3 | 292 | 292 | 292 | 292 | Ca-HdF, mg/L CaCO3 | 292 | 292 | 292 | 292
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.33 | 24.08 | 24.205 | 1.0328 | [70 empty] | SDS-Cl2 dose | mg/L | 3.52 | 3.52 | 3.52 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.76 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 43.9 | 77.6 | 27.7 | 27.4 | Ca-Hdp, mg/L CaCO3 | 43.9 | 77.6 | 27.7 | 27.4
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.54 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 779 | 802 | 790.5 | 2.9096 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.86 | 0.82 | 0.84 | 4.7619 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.23 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.37 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.62 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 15 | [14 empty] | SDS-CHCl3 | mg/L | 125 | 129 | 127 | 3.1496 | [70 empty] | SDS-Cl2 demand | mg/L | 2.66 | 2.7 | 2.68 | 1.4925 | --- | 31.58 | --- | 76.3877 | 31.2809 | 91.4325 | SDS-Cl2 demand | mg/L | 3.53 | --- | 81.73 | --- | 68.8987 | 80.9082 | 95.637 | SDS-Cl2 demand | mg/L | 1.83 | --- | 20.87 | --- | 83.8767 | 20.6728 | 91.1478 | SDS-Cl2 demand | mg/L | 1.58 | --- | 15.5371 | --- | 86.0793 | 15.3913 | 89.7344 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | 10 | [14 empty] | SDS-BDCM | mg/L | 46.8 | 46.6 | 46.7 | 0.42827 | [70 empty] | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 63.5503 | 66.1888 | 61.624 | 62.6697 | Qp/QT (THM4), % | 84.1985 | 87.6941 | 81.6463 | 83.0317
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | 95% | [14 empty] | SDS-DBCM | mg/L | 9.1 | 9.1 | 9.1 | 0 | [70 empty] | SDS-Chlorination pH | --- | 7.45 | 7.48 | 7.465 | 0.40188 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.58 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.57 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.56 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 2000 ppm MgSO4 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.15 | 24.08 | 24.115 | 0.29028 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.73 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.62 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.05 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 44.9046 | 42.4918 | 46.8763 | 45.599 | SDS-HAA5b, ug/L | 19.8068 | 16.6101 | 22.4191 | 20.7268
|  | Variability of rejection of reference solute (%) | 3 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 180.9 | 184.7 | 182.8 | 2.0788 | [70 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | 36.7 | --- | 7574.7 | --- | 95.3574 | 7495.4871 | 99.5104 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 291.5691 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 129.4615 | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.4 | 6.6 | 6.5 | 3.0769 | [70 empty] | SDS-CHCl3 | mg/L | 2.3 | 1.9 | 2.1 | 19.0476 | --- | 418.4333 | --- | 98.3465 | 414.1249 | 99.4929 | SDS-CHCl3 | mg/L | 2.1 | --- | 1251.1 | --- | 98.3465 | 1237.9749 | 99.8304 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.5 | --- | 180.7857 | --- | 98.8189 | 178.9118 | 99.1616 | SDS-CDb, mg/L | 5.8402 | 6.174 | 5.4834 | 5.2272 | SDS-CDb, mg/L | 4.05 | 4.4923 | 3.5773 | 3.2378
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 45 | 40.2 | 42.6 | 11.2676 | [70 empty] | SDS-BDCM | mg/L | 3.3 | 2.9 | 3.1 | 12.9032 | --- | 148.4333 | --- | 93.3619 | 146.9294 | 97.8901 | SDS-BDCM | mg/L | 3.7 | --- | 433.7 | --- | 92.0771 | 429.1814 | 99.1379 | SDS-BDCM | mg/L | 1.2 | --- | 92.2 | --- | 97.4304 | 91.2574 | 98.685 | SDS-BDCM | mg/L | 2.1 | --- | 65.8143 | --- | 95.5032 | 65.1483 | 96.7766 | TOCb, mg/L | 3.5559 | 3.4107 | #VALUE! | #VALUE! | TOCb, mg/L | 1.6945 | 1.5021 | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | <250 psi | [14 empty] | SDS-TCAA* | mg/L | 77.6 | 63.3 | 70.45 | 20.2981 | [70 empty] | SDS-DBCM | mg/L | 3.4 | 3.1 | 3.25 | 9.2308 | --- | 22.75 | --- | 64.2857 | 22.5482 | 85.5864 | SDS-DBCM | mg/L | 6.6 | --- | 31.6 | --- | 27.4725 | 31.3373 | 78.9388 | SDS-DBCM | mg/L | 1.8 | --- | 16.4 | --- | 80.2198 | 16.2488 | 88.9222 | SDS-DBCM | mg/L | 2.4 | --- | 11.9714 | --- | 73.6264 | 11.8714 | 79.7833 | UV254 b, cm-1 | #DIV/0! | 0.086701 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.040142 | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [14 empty] | SDS-MBAA* | mg/L | 1.1 | 1 | 1.05 | 9.5238 | [70 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 93.6603 | 115.2897 | 85.7558 | 82.302 | Bromideb, ug/L | 66.0951 | 94.7521 | 55.6224 | 51.0464
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | 1.5 | 1.6 | 1.55 | 6.4516 | [70 empty] | SDS-THM4 | mg/L | 9 | 7.9 | 8.45 | 13.0178 | --- | 589.6167 | --- | 95.3775 | 583.6025 | 98.5521 | SDS-THM4 | mg/L | 15.4 | --- | 1689.4 | --- | 91.5755 | 1671.8088 | 99.0788 | SDS-THM4 | mg/L | 3 | --- | 362.6 | --- | 98.3589 | 358.8753 | 99.1641 | SDS-THM4 | mg/L | 6 | --- | 258.5714 | --- | 96.7177 | 255.9316 | 97.6556 | Alkb, mg/L CaCO3 | 67.977 | 76.1637 | 67.3537 | 63.8428 | Alkb, mg/L CaCO3 | 42.9515 | 53.7981 | 42.1257 | 37.474
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 11.4 | 11.3 | 11.35 | 0.88106 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 142.886 | 159.391 | 136.2273 | 133.0821 | T-Hdb, mg/L CaCO3 | 88.4266 | 110.2943 | 79.6043 | 75.4373
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | BMRL | 1.2 | 1.2 | #VALUE! | --- | 139.2 | --- | 97.1831 | 137.7719 | 99.129 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 134.3316 | 150.0913 | 129.1277 | 126.176 | Ca-Hdb, mg/L CaCO3 | 83.1036 | 103.9838 | 76.2089 | 72.2982
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hrs | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 131.6 | 112.7 | 122.15 | 15.4728 | [70 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.8 | --- | -0.7 | --- | -16.129 | -0.67373 | 367.1698 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 143 | 124 | 133.5 | 14.2322 | [70 empty] | SDS-BCAA* | mg/L | BMRL | 1.1 | 1.1 | #VALUE! | --- | 35.2667 | --- | 90.3084 | 34.9131 | 96.8493 | SDS-BCAA* | mg/L | 1.3 | --- | 101.8 | --- | 88.5463 | 100.7439 | 98.7096 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 56.0675 | 56.6265 | 55.7921 | 55.7921 | Qp/QT (HAA5), % | 78.2805 | 79.0611 | 77.896 | 77.896
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 85.0464 | 88.0072 | 82.4859 | 84.1596 | SDS-THM4b, ug/L | 46.3179 | 50.4518 | 42.7429 | 45.0798
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | #DIV/0! | 363.6494 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 194.5376 | #VALUE! | #VALUE!
[94 empty] | SDS-HAA5 | mg/L | 0 | 1.2 | 0.6 | 200 | --- | 405.7667 | --- | 99.5088 | 401.5738 | 99.8506 | SDS-HAA5 | mg/L | 1.8 | --- | 1205.3 | --- | 98.5264 | 1192.6531 | 99.8491 | SDS-HAA5 | mg/L | 0 | --- | 244.3 | --- | 100 | 241.7696 | 100 | SDS-HAA5 | mg/L | 0 | --- | 174.5 | --- | 100 | 172.6761 | 100 | SDS-CDb, mg/L | 6.489 | 6.9218 | 6.0386 | 5.8991 | SDS-CDb, mg/L | 4.5631 | 5.1674 | 3.9343 | 3.7396
[94 empty] | SDS-HAA6 | mg/L | 0 | 2.3 | 1.15 | 200 | --- | 442.3167 | --- | 99.1386 | 437.7513 | 99.7373 | SDS-HAA6 | mg/L | 3.1 | --- | 1307.1 | --- | 97.6779 | 1293.3969 | 99.7603 | SDS-HAA6 | mg/L | 0 | --- | 267 | --- | 100 | 264.2345 | 100 | SDS-HAA6 | mg/L | 0 | --- | 190.7143 | --- | 100 | 188.7209 | 100 | TOCb, mg/L | 4.2305 | 4.2594 | #VALUE! | #VALUE! | TOCb, mg/L | 2.228 | 2.2683 | #VALUE! | #VALUE!
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.1074 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.058833 | #VALUE! | #VALUE!
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 103.6499 | 124.4217 | 94.533 | 92.8592 | Bromideb, ug/L | 73.9955 | 102.9967 | 61.2665 | 58.9296
[133 empty] | Alkb, mg/L CaCO3 | 77.0462 | 86.1084 | 74.702 | 72.7493 | Alkb, mg/L CaCO3 | 50.124 | 62.7765 | 46.851 | 44.1246
[133 empty] | T-Hdb, mg/L CaCO3 | 162.6221 | 181.2217 | 152.7201 | 152.5527 | T-Hdb, mg/L CaCO3 | 104.0351 | 130.0036 | 90.21 | 89.9763
[133 empty] | Ca-Hdb, mg/L CaCO3 | 152.8966 | 170.5928 | 144.5416 | 144.3742 | Ca-Hdb, mg/L CaCO3 | 97.786 | 122.4931 | 86.1208 | 85.8871
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on AA10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on CD7: C. Rice: There is no record of an operational anomaly during the middle of 50% and 30% runs so the TDS data should be considered valid. TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Note on CY29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on DL29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on DV29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on EF29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Print All Fields

## NF200. 2nd Quarter
FIELD-SET 2: Membrane B, Run 2 (FILE: Margate2.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Film Tec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.47291 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-04-27 | 1999-04-27 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 12.9 | [10 empty] | Feed flow rate during sample collection (mL/min) | 10.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 37 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 1:15 | 1:15 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 344 | [10 empty] | Influent flow rate during sample collection (mL/min) | 344 | [7 empty] | Influent flow rate during sample collection (mL/min) | 344 | [7 empty] | Influent flow rate during sample collection (mL/min) | 344 | [6 empty] | SDS-THM4F, ug/L | 206.85 | 206.85 | 206.85 | 206.85 | SDS-THM4F, ug/L | 206.85 | 206.85 | 206.85 | 206.85 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 15.7 | 15.7 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 20.2 | 34.2 | 38.5 | 27.4 | SDS-THM4p, ug/L | 20.2 | 34.2 | 38.5 | 27.4 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.8 | 6.94 | 6.87 | 2.0378 | 1999-04-24 | 11:20 | 0 | 24.5 | 82 | 81 | 344 | 9 | 4 | 13 | 0.26032 | 0.69231 | 25.4615 | 20.542 | 19.0788 | 97.742 | 28.7813 | 95.9378 | 0.68059 | 80.8194 | 0.23607 | 1999-04-26 | 9:30 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 126.3 | 126.3 | 126.3 | 126.3 | SDS-HAA5F, ug/L | 126.3 | 126.3 | 126.3 | 126.3 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.2599 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1999-04-24 | 15:00 | 4.6 | 25.1 | 92 | 91 | 344 | 9 | 4 | 13 | 0.26032 | 0.69231 | 25.4615 | 20.542 | 18.7434 | 97.742 | 28.7813 | 95.9378 | 0.68059 | 90.8194 | 0.20638 | 1999-04-26 | 10:07 | 0.6 | 24.3 | 107.4 | 107.1 | 344 | 9.2 | 4.1 |  | 13.3 | 0.26032 | 0.69173 | 24.8647 | 20.9985 | 19.6184 | 768.4872 | 399.8644 | 758.6287 | 3.6369 | 103.6131 | 0.18934 | 6.59 |  |  | 291.486 |  |  | 1011.6778 |  | 43.2354 | 1002.0473 | 70.911 | 0.014 |  |  | 0.64007 |  | 93.2367 | 0.6317 | 97.7838 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.4 | 7.4 | 7.9 | 4.2 | SDS-HAA5p, ug/L | 2.4 | 7.4 | 7.9 | 4.2 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Highly Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 101.5 | 88.2 | 94.85 | 14.0221 | 1999-04-25 | 9:38 | 23.2 | 24.9 | 104 | 103 | 344 | 9.5 | 4.1 | 13.6 | 0.26032 | 0.69853 | 24.2941 | 21.6832 | 19.902 | 98.6301 | 29.0123 | 96.7075 | 0.68657 | 102.8134 | 0.19357 | 1999-04-26 | 13:55 | 4.4 | 24.6 | 107.8 | 107.2 | 344 | 9.2 | 4 |  | 13.2 | 0.26032 | 0.69697 | 25.0606 | 20.9985 | 19.4452 | 771.389 | 401.3743 | 761.4933 | 3.6507 | 103.8493 | 0.18724 | 6.54 |  |  | 297.258 |  |  | 1010.8566 |  | 42.1114 | 1001.3143 | 70.3132 | 0.014 |  |  | 0.6509 |  | 93.2367 | 0.64238 | 97.8206 | [8 empty] | Sampling date | MM/DD/YY | 1999-04-27 | 1999-04-27 | --- | --- | 1999-04-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-28 | 1999-04-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-29 | 1999-04-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-30 | 1999-04-30 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 618.25 | 618.25 | 618.25 | 618.25 | SDS-TOXF, ug Cl- /L | 618.25 | 618.25 | 618.25 | 618.25 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 388 | 639 | 513.5 | 48.8802 | 1999-04-25 | 11:30 | 25 | 25.1 | 102 | 101 | 344 | 8.9 | 4.1 | 13 | 0.26032 | 0.68462 | 25.4615 | 20.3138 | 18.5351 | 96.708 | 28.4829 | 94.9428 | 0.67343 | 100.8266 | 0.18383 | 1999-04-26 | 17:13 | 7.7 | 24.9 | 107 | 106 | 344 | 9 | 3.9 |  | 12.9 | 0.26032 | 0.69767 | 25.6667 | 20.542 | 18.8545 | 771.6603 | 401.6305 | 761.9793 | 3.6519 | 102.8481 | 0.18332 | 6.53 | 6.57 | 7.19 | 350.168 | 570.63 | 568.5 | 890.42 | -56.6262 | 31.8076 | 883.3528 | 60.3592 | 0.014 | 0.321 | 1 | 0.65238 | 34.7615 | 93.2367 | 0.64403 | 97.8262 | [8 empty] | Sampling time | hh:mm | 1:15 | 1:15 | --- | --- | 1:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 0:57 | 0:57 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 1:42 | 1:42 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 5:36 | 5:36 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 33.1 | 88.7 | 60.25 | 45.1 | SDS-TOXp, ug Cl- /L | 33.1 | 88.7 | 60.25 | 45.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 337 | 318 | 327.5 | 5.8015 | 1999-04-25 | 17:27 | 31 | 24.7 | 104.1 | 103.7 | 344 | 9.6 | 4.1 | 13.7 | 0.26032 | 0.70073 | 24.1095 | 21.9115 | 20.2307 | 98.9418 | 29.0978 | 96.9926 | 0.68869 | 103.2113 | 0.19601 | 1999-04-27 | 9:17 | 23.8 | 24.3 | 111.4 | 111 | 344 | 9.2 | 1 |  | 10.2 | 0.26032 | 0.90196 | 32.7255 | 20.9985 | 19.6184 | 905.0794 | 470.937 | 893.4687 | 4.2834 | 106.9166 | 0.18349 | 6.46 |  |  | 425.15 |  |  | 1326.32 |  | 17.2055 | 1314.2695 | 67.6512 | 0.016 |  |  | 1.9642 |  | 92.2705 | 1.9381 | 99.1745 | [8 empty] | Operation time | hh.hh | 15.7 | 15.7 | --- | --- | 15.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 39.5 | 39.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 63.5 | 63.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 91.4 | 91.4 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.515 | 11.515 | 11.515 | 11.515 | SDS-CDF, mg/L | 11.515 | 11.515 | 11.515 | 11.515 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 317 | 299 | 308 | 5.8442 | [21 empty] | 1999-04-27 | 13:01 | 27.5 | 24.9 | 108.5 | 108.3 | 344 | 9.1 | 1 |  | 10.1 | 0.26032 | 0.90099 | 33.0594 | 20.7703 | 19.064 | 904.2303 | 470.5626 | 892.7583 | 4.2793 | 104.1207 | 0.1831 | 6.54 |  |  | 432.3 |  |  | 1252.42 |  | 15.813 | 1241.5725 | 65.1813 | 0.018 |  |  | 1.9269 |  | 91.3043 | 1.9017 | 99.0535 | [8 empty] | pH | --- | 6.79 | 6.87 | 6.83 | 1.1713 | 7 | --- | --- | --- | --- | --- | pH | --- | 7.13 | 7.73 | --- | --- | --- | --- | --- | pH | --- | 6.7 | 6.9 | --- | --- | --- | --- | --- | pH | --- | 6.85 | 6.91 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.56 | 4.89 | 4.74 | 4.3 | SDS-CDp, mg/L | 4.56 | 4.89 | 4.74 | 4.3 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 21.1 | 14.3517 | 95.5367 | 344.1283 | 9.2435 | 13.2049 | 3.9615 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.22 | 1.5 | 0.86 | 148.8372 | [21 empty] | 1999-04-27 | 16:30 | 31 | 25.6 | 110.4 | 109.8 | 344 | 9.2 | 1 |  | 10.2 | 0.26032 | 0.90196 | 32.7255 | 20.9985 | 18.8788 | 905.0794 | 470.937 | 893.4687 | 4.2834 | 105.8166 | 0.17841 | 6.54 | 6.7 | 7.34 | 431.2 | 576.15 | 1130.07 | 1270.66 | -12.4408 | 16.0273 | 1259.4347 | 65.7624 | 0.02 | 0.308 | 2.497 | 1.9274 | 22.8114 | 90.3382 | 1.9019 | 98.9484 | [8 empty] | Temperature | oC | 24.6 | 24.6 | 24.6 | 0 | 24.6 | --- | --- | --- | --- | --- | Temperature | oC | 24.9 | 24.9 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23.8 | 23.8 | --- | --- | --- | --- | --- | TOCF, mg/L | 8.5 | 8.5 | 8.5 | 8.5 | TOCF, mg/L | 8.5 | 8.5 | 8.5 | 8.5 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 21.1 | 39.785 | 120.97 | 344.1283 | 9.2435 | 10.2705 | 1.0271 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.81 | 0.62 | 0.715 | 26.5734 | [21 empty] | 1999-04-28 | 9:25 | 47.9 | 24.1 | 113.1 | 112.5 | 344 | 9.3 | 9.1 |  | 18.4 | 0.26032 | 0.50543 | 17.6957 | 21.2268 | 19.9492 | 677.871 | 352.6639 | 669.0791 | 3.2081 | 109.5919 | 0.18203 | [27 empty] | Alkalinity | mg/L as CaCO3 | 75 | 78.6 | 76.8 | 4.6875 | 149.9 | 136.9667 | 8.628 | 19.03 | 136.177 | 43.6028 | Alkalinity | mg/L as CaCO3 | 93.1 | 177.5 | 110.6 | 37.6901 | 1.845 | 110.3665 | 15.6447 | Alkalinity | mg/L as CaCO3 | 41.2 | 79 | 148.5 | -87.9747 | 56.563 | 147.0808 | 71.9882 | Alkalinity | mg/L as CaCO3 | 53.2 | 106.7 | 112.7 | -5.6232 | 43.9114 | 111.74 | 52.3895 | TOCp, mg/L | 0.415 | 0.74 | 0.86 | 3.12 | TOCp, mg/L | 0.415 | 0.74 | 0.86 | 3.12 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 21.1 | 9.265 | 90.45 | 344.1283 | 9.2435 | 18.4869 | 9.2435 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 8.6 | 8.4 | 8.5 | 2.3529 | [21 empty] | 1999-04-28 | 10:49 | 48.6 | 23.5 | 108.6 | 108.2 | 344 | 9.2 | 9.3 |  | 18.5 | 0.26032 | 0.4973 | 17.5946 | 20.9985 | 20.0878 | 674.3626 | 350.8889 | 665.7116 | 3.1915 | 105.2085 | 0.19093 | 6.52 |  |  | 457.1 |  |  | 569.2935 |  | 10.9834 | 567.7933 | 19.4953 | 0.02 |  |  | 0.39199 |  | 90.3382 | 0.38701 | 94.8322 | [8 empty] | Total dissolved solids | mg/L | 212 | 488 | 350 | 78.8571 | 568 | 895 | -57.5704 | 31.8403 | 887.8469 | 60.5788 | Total dissolved solids | mg/L | 431.5 | 1130 | 1251.5 | -10.7522 | 15.9688 | 1240.5587 | 65.2173 | Total dissolved solids | mg/L | 469 | 700 | 558 | 20.2857 | 8.666 | 556.8228 | 15.7721 | Total dissolved solids | mg/L | 374 | 583 | 573.2857 | 1.6663 | 27.1665 | 570.0705 | 34.3941 | UV254 F, cm-1 | 0.207 | 0.207 | 0.207 | 0.207 | UV254 F, cm-1 | 0.207 | 0.207 | 0.207 | 0.207 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 21.1 | 7.085 | 88.27 | 344.1283 | 9.2435 | 30.8115 | 21.5681 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.122 | 0.292 | 0.207 | 82.1256 | [21 empty] | 1999-04-28 | 12:44 | 50.5 | 23.8 | 108.5 | 108.1 | 344 | 9.3 | 9.3 |  | 18.6 | 0.26032 | 0.5 | 17.4946 | 21.2268 | 20.1269 | 675.5458 | 351.4542 | 666.784 | 3.1971 | 105.1029 | 0.1915 | 6.51 |  |  | 451.223 |  |  | 575.777 |  | 12.1279 | 574.0933 | 21.4025 | 0.02 |  |  | 0.394 |  | 90.3382 | 0.38894 | 94.8579 | [8 empty] | Total hardness | mg/L as CaCO3 | 253 | 253 | 253 | 0 | 474 | 501.3333 | -5.7665 | 22.7481 | 498.074 | 49.2043 | Total hardness | mg/L as CaCO3 | 274 | 651 | 809 | -24.2704 | 16.3359 | 801.8615 | 65.8295 | Total hardness | mg/L as CaCO3 | 232 | 378 | 423 | -11.9048 | 29.1603 | 420.4737 | 44.8241 | Total hardness | mg/L as CaCO3 | 211 | 350 | 377.4286 | -7.8367 | 35.5725 | 374.7435 | 43.6948 | UV254 p, cm-1 | 0.01025 | 0.02 | 0.026 | 0.018 | UV254 p, cm-1 | 0.01025 | 0.02 | 0.026 | 0.018 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 1.4186 | 3.4762 | 2.4474 | 84.0724 | [21 empty] | 1999-04-28 | 17:49 | 55.6 | 23.4 | 108.4 | 108.1 | 344 | 9.1 | 9.1 |  | 18.2 | 0.26032 | 0.5 | 17.9011 | 20.7703 | 19.9283 | 675.4796 | 351.5204 | 666.9097 | 3.1967 | 105.0533 | 0.1897 | 6.33 | 6.34 | 6.56 | 468.854 | 611.34 | 700.398 | 558.146 | 20.3102 | 8.6944 | 556.965 | 15.8198 | 0.026 | 0.31 | 0.556 | 0.388 | 30.2158 | 87.4396 | 0.38321 | 93.2152 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 239 | 239 | 239 | 0 | 439 | 469 | -6.8337 | 22.4026 | 465.9812 | 48.7104 | Calcium hardness | mg/L as CaCO3 | 259 | 599 | 749 | -25.0417 | 15.9091 | 742.4619 | 65.1161 | Calcium hardness | mg/L as CaCO3 | 220 | 352 | 396 | -12.5 | 28.5714 | 393.6721 | 44.1159 | Calcium hardness | mg/L as CaCO3 | 201 | 327 | 353.8571 | -8.2132 | 34.7403 | 351.391 | 42.7988 | BromideF, ug/L | 194 | 194 | 194 | 194 | BromideF, ug/L | 194 | 194 | 194 | 194 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 211 | 177 | 194 | 17.5258 | [21 empty] | 1999-04-29 | 9:36 | 71.3 | 22.6 | 112.8 | 112.4 | 344 | 9.3 | 21.5 |  | 30.8 | 0.26032 | 0.30195 | 10.1688 | 21.2268 | 20.8536 | 600.4857 | 312.404 | 592.6975 | 2.8419 | 109.7581 | 0.19 | 6.3 |  |  | 387.672 |  |  | 567.9279 |  | 24.504 | 565.4913 | 31.4451 | 0.021 |  |  | 0.28746 |  | 89.8551 | 0.28385 | 92.6018 | [8 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.42 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.61 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0 | 0.29 | 1.72 | -493.1034 | 100 | 1.6972 | 100 | Turbidity | ntu | 0 | 0.2 | 1.2286 | -514.2857 | 100 | 1.2087 | 100 | Bromidep, ug/L | 170 | 174 | 175 | 155 | Bromidep, ug/L | 170 | 174 | 175 | 155 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.6 | 12.6 | 12.6 | 0 | [21 empty] | 1999-04-29 | 14:10 | 75.9 | 23.3 | 112.2 | 111.8 | 344 | 9.3 | 21.5 |  | 30.8 | 0.26032 | 0.30195 | 10.1688 | 21.2268 | 20.4266 | 600.4857 | 312.404 | 592.6975 | 2.8419 | 109.1581 | 0.18713 | 6.35 |  |  | 379.874 |  |  | 571.301 |  | 26.0226 | 568.7134 | 33.2047 | 0.019 |  |  | 0.28832 |  | 90.8213 | 0.28468 | 93.3258 | [8 empty] | Ammonia | mg NH3-N / L | 0.59 | 0.63 | 0.61 | 6.5574 | 0.93 | 0.96 | -3.2258 | 14.6853 | 0.95541 | 36.1528 | Ammonia | mg NH3-N / L | 0.7 | 0.9 | 0.85 | 5.5556 | 2.0979 | 0.848 | 17.4527 | Ammonia | mg NH3-N / L | 0.58 | 0.74 | 0.85 | -14.8649 | 18.8811 | 0.84643 | 31.4768 | Ammonia | mg NH3-N / L | 0.5 | 0.65 | 0.80714 | -24.1758 | 30.0699 | 0.80219 | 37.6704 | AlkF, mg/L CaCO3 | 94.85 | 94.85 | 94.85 | 94.85 | AlkF, mg/L CaCO3 | 94.85 | 94.85 | 94.85 | 94.85
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.6667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.04 | 1.13 | 1.085 | 8.2949 | [21 empty] | 1999-04-29 | 18:37 | 80.4 | 23.8 | 112.1 | 111.7 | 344 | 9.3 | 21.7 |  | 31 | 0.26032 | 0.3 | 10.0968 | 21.2268 | 20.1269 | 599.8302 | 312.0629 | 592.0504 | 2.8388 | 109.0612 | 0.18455 | 6.37 | 6.72 | 6.58 | 374.304 | 593.4 | 583.16 | 573.1554 | 1.7156 | 27.1073 | 570.4675 | 34.3864 | 0.018 | 0.315 | 0.43 | 0.288 | 33.0233 | 91.3043 | 0.28435 | 93.6698 | [8 empty] | Total organic carbon | mg/L | 0.43 | 0.4 | 0.415 | 7.2289 | 28.7 | 27.365 | 4.6516 | 95.1176 | 27.0113 | 98.4636 | Total organic carbon | mg/L | 0.74 | 78.4 | 78.34 | 0.076531 | 91.2941 | 77.3046 | 99.0427 | Total organic carbon | mg/L | 0.86 | 17 | 16.14 | 5.0588 | 89.8824 | 15.9379 | 94.6041 | Total organic carbon | mg/L | 3.12 | 12.1 | 10.8057 | 10.6966 | 63.2941 | 10.6817 | 70.7912 | Alkp, mg/L CaCO3 | 76.8 | 93.1 | 41.2 | 53.2 | Alkp, mg/L CaCO3 | 76.8 | 93.1 | 41.2 | 53.2
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.56 | 11.47 | 11.515 | 0.78159 | [21 empty] | 1999-04-30 | 16:35 | 94.4 | [6 empty] | X | [39 empty] | UV254 | cm-1 | 0.0105 | 0.01 | 0.01025 | 4.878 | 0.9515 | 0.66608 | 29.9965 | 95.0483 | 0.65748 | 98.441 | UV254 | cm-1 | 0.02 | 2.583 | 1.89 | 26.8293 | 90.3382 | 1.865 | 98.9276 | UV254 | cm-1 | 0.026 | 0.562 | 0.388 | 30.9609 | 87.4396 | 0.38321 | 93.2152 | UV254 | cm-1 | 0.018 | 0.427 | 0.288 | 32.5527 | 91.3043 | 0.28364 | 93.654 | T-HdF, mg/L CaCO3 | 327.5 | 327.5 | 327.5 | 327.5 | T-HdF, mg/L CaCO3 | 327.5 | 327.5 | 327.5 | 327.5
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | [21 empty] | 1999-04-30 | 17:25 | 95.1 | 20.1 | 83.4 | 83.1 | 344 | 9.2 | 21.7 |  | 30.9 | 0.26032 | 0.29773 | 10.1327 | 20.9985 | 22.2116 | 599.0541 | 311.7039 | 591.3692 | 2.8351 | 80.4149 | 0.27621 | 6.45 |  |  | 275.158 |  |  | 614.5482 |  | 46.4152 | 610.0099 | 54.8929 | 0.029 |  |  | 0.28247 |  | 85.9903 | 0.27908 | 89.6086 | [8 empty] | SUVA | L/(mg*m) | 2.4419 | 2.5 | 2.4709 | 2.3529 | 3.3153 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.7027 | 3.2946 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.0233 | 3.3059 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 0.57692 | 3.5289 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 253 | 274 | 232 | 211 | T-Hdp, mg/L CaCO3 | 253 | 274 | 232 | 211
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.42 | 7.45 | 7.435 | 0.4035 | [21 empty] | 1999-04-30 | 21:35 | 99.2 | 20.7 | 83.5 | 83.2 | 344 | 9.2 | 21.9 |  | 31.1 | 0.26032 | 0.29582 | 10.0611 | 20.9985 | 21.8211 | 598.413 | 311.3703 | 590.7362 | 2.832 | 80.518 | 0.27101 | 6.51 |  |  | 281.842 |  |  | 610.8175 |  | 45.1135 |  |  | 0.018 |  |  | 0.2864 |  | 91.3043 | 0.28281 | 93.6353 | [8 empty] | Bromide | mg/L | 168 | 172 | 170 | 2.3529 | --- | 250 | --- | 12.3711 | 248.95 | 31.7132 | Bromide | mg/L | 174 | --- | 374 | --- | 10.3093 | 371.3314 | 53.1416 | Bromide | mg/L | 175 | --- | 213 | --- | 9.7938 | 212.4974 | 17.646 | Bromide | mg/L | 155 | --- | 210.7143 | --- | 20.1031 | 209.8154 | 26.1255 | Ca-HdF, mg/L CaCO3 | 308 | 308 | 308 | 308 | Ca-HdF, mg/L CaCO3 | 308 | 308 | 308 | 308
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | - | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.03 | 24.13 | 24.08 | 0.41528 | [21 empty] | 1999-04-30 | 23:47 | 101.4 | 21.2 | 82.7 | 82.4 | 344 | 9.2 | 21.8 |  | 31 | 0.26032 | 0.29677 | 10.0968 | 20.9985 | 21.501 | 598.7323 | 311.5364 | 591.0515 | 2.8336 | 79.7164 | 0.26972 | 6.44 | 6.74 | 6.61 | 293.539 | 520.26 | 514.84 | 606.3276 | -17.7701 | 42.8356 | 602.1449 | 51.2511 | 0.016 | 0.314 | 0.408 | 0.28761 | 29.5085 | 92.2705 | 0.28397 | 94.3657 | [8 empty] | SDS-Cl2 dose | mg/L | 5.4 | 5.4 | 5.4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 6.6 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 239 | 259 | 220 | 201 | Ca-Hdp, mg/L CaCO3 | 239 | 259 | 220 | 201
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | - | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 568.5 | 668 | 618.25 | 16.0938 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.86 | 0.82 | 0.84 | 4.7619 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.71 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.56 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.7 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 19 | [14 empty] | SDS-CHCl3 | mg/L | 146 | 147 | 146.5 | 0.68259 | [70 empty] | SDS-Cl2 demand | mg/L | 4.54 | 4.58 | 4.56 | 0.87719 | --- | 27.7433 | --- | 60.3995 | 27.4391 | 83.3814 | SDS-Cl2 demand | mg/L | 4.89 | --- | 71.14 | --- | 57.5337 | 70.256 | 93.0397 | SDS-Cl2 demand | mg/L | 4.74 | --- | 18.29 | --- | 58.8363 | 18.1108 | 73.8277 | SDS-Cl2 demand | mg/L | 4.3 | --- | 14.6071 | --- | 62.6574 | 14.4409 | 70.2234 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | -10%, +25% | [14 empty] | SDS-BDCM | mg/L | 50.5 | 51.1 | 50.8 | 1.1811 | [70 empty] | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 72.2475 | 78.106 | 80.101 | 75.1463 | Qp/QT (THM4), % | 91.535 | 98.9574 | 101.485 | 95.2076
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | >99% of 2,000 ppm MgSO4 | [14 empty] | SDS-DBCM | mg/L | 9.6 | 9.5 | 9.55 | 1.0471 | [70 empty] | SDS-Chlorination pH | --- | 7.53 | 7.65 | 7.59 | 1.581 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.6 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | NA | 36
|  | (e.g., solute type and concentration) | <50% 500 ppm CaCl2 | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 22.02 | 24 | 23.01 | 8.605 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.98 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.23 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 36.7853 | 33.432 | 31.4604 | 34.5464 | SDS-HAA5b, ug/L | 12.8882 | 8.6396 | NA | 10.0515
|  | Variability of rejection of reference solute (%) | - | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 206.1 | 207.6 | 206.85 | 0.72516 | [70 empty] | SDS-TOX | mg Cl- /L | 34.65 | 31.55 | 33.1 | 9.3656 | --- | 1983.6 | --- | 94.6462 | 1957.9997 | 98.3095 | SDS-TOX | mg Cl- /L | 88.7 | --- | 5384.2 | --- | 85.6531 | 5313.542 | 98.3307 | SDS-TOX | mg Cl- /L | 60.25 | --- | 1176.25 | --- | 90.2548 | 1161.489 | 94.8127 | SDS-TOX | mg Cl- /L | 45.1 | --- | 863.8857 | --- | 92.7052 | 850.6757 | 94.6983 | SDS-TOXb, ug Cl- /L | 195.4936 | 204.6397 | 171.2865 | 187.5491 | SDS-TOXb, ug Cl- /L | 82.6332 | 94.2209 | NA | 72.5678
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 8.6 | 6 | 7.3 | 35.6164 | [70 empty] | SDS-CHCl3 | mg/L | 1.7 | 1.6 | 1.65 | 6.0606 | --- | 484.4833 | --- | 98.8737 | 478.1461 | 99.6549 | SDS-CHCl3 | mg/L | 4.1 | --- | 1428.1 | --- | 97.2014 | 1409.0995 | 99.709 | SDS-CHCl3 | mg/L | 3.8 | --- | 289.2 | --- | 97.4061 | 285.4251 | 98.6687 | SDS-CHCl3 | mg/L | 2.6 | --- | 208.1714 | --- | 98.2253 | 204.8548 | 98.7308 | SDS-CDb, mg/L | 6.4902 | 6.3405 | 6.0882 | 6.0932 | SDS-CDb, mg/L | 5.1487 | 4.9591 | NA | 4.6458
|  | Standard testing pH | 6.7-7.3 | [14 empty] | SDS-DCAA* | mg/L | 44.6 | 43 | 43.8 | 3.653 | [70 empty] | SDS-BDCM | mg/L | 4 | 3.9 | 3.95 | 2.5316 | --- | 160.1167 | --- | 92.2244 | 158.067 | 97.5011 | SDS-BDCM | mg/L | 9.2 | --- | 425.2 | --- | 81.8898 | 419.6493 | 97.8077 | SDS-BDCM | mg/L | 9.3 | --- | 92.3 | --- | 81.6929 | 91.2022 | 89.8029 | SDS-BDCM | mg/L | 6.4 | --- | 69.8286 | --- | 87.4016 | 68.8052 | 90.6984 | TOCb, mg/L | 2.6588 | 2.439 | 2.3803 | 4.4571 | TOCb, mg/L | 1.0994 | 0.8209 | NA | 3.3778
|  | Acceptable range of operating pressures | <105 psi | [14 empty] | SDS-TCAA* | mg/L | 73.1 | 71.8 | 72.45 | 1.7943 | [70 empty] | SDS-DBCM | mg/L | 8.4 | 8.9 | 8.65 | 5.7803 | --- | 11.65 | --- | 9.4241 | 11.6106 | 25.4993 | SDS-DBCM | mg/L | 14.6 | --- | -35.9 | --- | -52.8796 | -35.2262 | 141.4465 | SDS-DBCM | mg/L | 16.8 | --- | 2.3 | --- | -75.9162 | 2.4918 | -574.2147 | SDS-DBCM | mg/L | 12.2 | --- | 8.4143 | --- | -27.7487 | 8.4754 | -43.9466 | UV254 b, cm-1 | 0.064853 | 0.060942 | 0.062017 | 0.064974 | UV254 b, cm-1 | 0.026905 | 0.02195 | NA | 0.027058
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | 1.2 | 1.2 | 1.2 | 0 | [70 empty] | SDS-CHBr3 | mg/L | 5.5 | 6.4 | 5.95 | 15.1261 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 6.3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 8.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 6.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 176.6606 | 178.3788 | 178.7808 | 164.693 | Bromideb, ug/L | 172.0316 | 174.2085 | NA | 156.869
|  | Typical pressure drop across a single element (psi) | 3 | [14 empty] | SDS-DBAA* | mg/L | 1.7 | 1.4 | 1.55 | 19.3548 | [70 empty] | SDS-THM4 | mg/L | 19.6 | 20.8 | 20.2 | 5.9406 | --- | 642.3667 | --- | 90.2345 | 634.2007 | 96.8149 | SDS-THM4 | mg/L | 34.2 | --- | 1760.7 | --- | 83.4663 | 1737.6633 | 98.0318 | SDS-THM4 | mg/L | 38.5 | --- | 375.2 | --- | 81.3875 | 370.7466 | 89.6155 | SDS-THM4 | mg/L | 27.4 | --- | 283.7571 | --- | 86.7537 | 279.6211 | 90.201 | Alkb, mg/L CaCO3 | 81.8093 | 93.4831 | 51.8758 | 63.5516 | Alkb, mg/L CaCO3 | 78.3279 | 93.1182 | NA | 55.196
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 12.6 | 10.6 | 11.6 | 17.2414 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 273.6756 | 285.7133 | 251.0036 | 239.9546 | T-Hdb, mg/L CaCO3 | 259.3065 | 274.5578 | NA | 216.5832
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 2.2 | --- | 418.2 | --- | 94.9772 | 412.6493 | 99.4669 | SDS-DCAA* | mg/L | 2 | --- | 85.6 | --- | 95.4338 | 84.4942 | 97.633 | SDS-DCAA* | mg/L | 1.3 | --- | 62.0143 | --- | 97.032 | 61.0347 | 97.8701 | Ca-Hdb, mg/L CaCO3 | 258.1492 | 269.7281 | 237.5111 | 227.5935 | Ca-Hdb, mg/L CaCO3 | 244.8409 | 259.5109 | NA | 206.1279
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hr | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.7 | --- | 709.2 | --- | 97.6536 | 699.7598 | 99.7571 | SDS-TCAA* | mg/L | 1.5 | --- | 143.4 | --- | 97.9296 | 141.5231 | 98.9401 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 129.2 | 123.4 | 126.3 | 4.5922 | [70 empty] | SDS-DBAA* | mg/L | 2.3 | 2.5 | 2.4 | 8.3333 | --- | -0.43333 | --- | -54.8387 | -0.39615 | 705.8375 | SDS-DBAA* | mg/L | 3.5 | --- | -16 | --- | -125.8065 | -15.7398 | 122.2366 | SDS-DBAA* | mg/L | 4.4 | --- | -1.3 | --- | -183.871 | -1.2246 | 459.2988 | SDS-DBAA* | mg/L | 2.9 | --- | 0.97143 | --- | -87.0968 | 1.0025 | -189.2642 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 141.8 | 134 | 137.9 | 5.6563 | [70 empty] | SDS-BCAA* | mg/L | 1.5 | 1.5 | 1.5 | 0 | --- | 35.1667 | --- | 87.069 | 34.7248 | 95.6803 | SDS-BCAA* | mg/L | 3.1 | --- | 88.1 | --- | 73.2759 | 86.9658 | 96.4354 | SDS-BCAA* | mg/L | 3.4 | --- | 19.8 | --- | 70.6897 | 19.5831 | 82.6381 | SDS-BCAA* | mg/L | 2.3 | --- | 15.5857 | --- | 80.1724 | 15.3714 | 85.0371 | Qp/QT (HAA5), % | 58.3535 | 60.8074 | 61.0642 | 59.2138 | Qp/QT (HAA5), % | 80.1453 | 83.5156 | 83.8682 | 81.3268
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 97.9332 | 101.866 | 104.0484 | 100.5909 | SDS-THM4b, ug/L | 57.2588 | 62.6604 | 65.6578 | 60.9091
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 276.7944 | 296.2444 | 277.5118 | 278.8663 | SDS-TOXb, ug Cl- /L | 149.2799 | 175.9934 | 150.2652 | 152.1256
[94 empty] | SDS-HAA5 | mg/L | 2.3 | 2.5 | 2.4 | 8.3333 | --- | 415.4 | --- | 98.0998 | 409.9794 | 99.4146 | SDS-HAA5 | mg/L | 7.4 | --- | 1196.4 | --- | 94.1409 | 1180.5351 | 99.3732 | SDS-HAA5 | mg/L | 7.9 | --- | 244.7 | --- | 93.7451 | 241.5679 | 96.7297 | SDS-HAA5 | mg/L | 4.2 | --- | 178.6286 | --- | 96.6746 | 175.8144 | 97.6111 | SDS-CDb, mg/L | 7.4565 | 7.4865 | 7.3779 | 7.2427 | SDS-CDb, mg/L | 5.9409 | 5.9821 | 5.8329 | 5.6473
[94 empty] | SDS-HAA6 | mg/L | 3.8 | 4 | 3.9 | 5.1282 | --- | 450.5667 | --- | 97.1719 | 444.7042 | 99.123 | SDS-HAA6 | mg/L | 10.5 | --- | 1284.5 | --- | 92.3858 | 1267.501 | 99.1716 | SDS-HAA6 | mg/L | 11.3 | --- | 264.5 | --- | 91.8057 | 261.151 | 95.673 | SDS-HAA6 | mg/L | 6.5 | --- | 194.2143 | --- | 95.2864 | 191.1858 | 96.6002 | TOCb, mg/L | 3.7821 | 3.7813 | 3.8347 | 5.3143 | TOCb, mg/L | 2.0203 | 2.0192 | 2.0925 | 4.1246
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.092189 | 0.09329 | 0.096474 | 0.095086 | UV254 b, cm-1 | 0.049314 | 0.050826 | 0.055198 | 0.053292
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 179.9952 | 181.8385 | 182.3978 | 170.9066 | Bromideb, ug/L | 174.7651 | 177.2969 | 178.065 | 162.2826
[133 empty] | Alkb, mg/L CaCO3 | 84.3172 | 93.7859 | 62.0891 | 70.1875 | Alkb, mg/L CaCO3 | 80.3838 | 93.3885 | 49.8547 | 60.9774
[133 empty] | T-Hdb, mg/L CaCO3 | 284.0266 | 294.968 | 269.1837 | 258.516 | T-Hdb, mg/L CaCO3 | 267.7918 | 282.8192 | 247.4058 | 232.7543
[133 empty] | Ca-Hdb, mg/L CaCO3 | 267.7361 | 278.2044 | 254.2635 | 244.6413 | Ca-Hdb, mg/L CaCO3 | 252.6998 | 267.0774 | 234.1959 | 220.9803
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X12: C. Rice: Consultant verified the feed UV, TDS and turbidity analyses; no explanations were given for the substantial differences in the two values.
Note on X15: C. Rice: Consultant verified the feed UV, TDS and turbidity analyses; no explanations were given for the substantial differences in the two values.
Note on X18: C. Rice: Consultant verified the feed UV, TDS and turbidity analyses; no explanations were given for the substantial differences in the two values.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on AA10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on BF24: C. Rice: Consultant verified the drop in pressure at the end of the 90% run.
Note on BV24: C. Rice: Consultant verified the rise in MTCw; no explanation was provided.
Note on CD7: C. Rice: There is no record of an operational anomaly during the middle of 50% and 30% runs so the TDS data should be considered valid. TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Note on CD8: C. Rice: Consultant verified the data that resulted in high MB closure errors.
Note on CL8: C. Rice: Consultant verified the data that resulted in high MB closure errors.
Note on CY17: C. Rice: Consultant verified UV, TDS, THM and HAA data but did not explain the "zigzag" trend seen with increasing recovery.
Note on CY22: C. Rice: Consultant verified the TOC concentrations but provided no explanation of the decreasing concentrations with increasing recovery.
Note on CY23: C. Rice: Consultant verified UV, TDS, THM and HAA data but did not explain the "zigzag" trend seen with increasing recovery.
Note on CY29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on CY32: C. Rice: Consultant verified TOX values.
Note on CY37: C. Rice: Consultant verified UV, TDS, THM and HAA data but did not explain the "zigzag" trend seen with increasing recovery.
Note on CY47: C. Rice: Consultant verified UV, TDS, THM and HAA data but did not explain the "zigzag" trend seen with increasing recovery.
Note on DL22: C. Rice: Consultant verified the TOC concentrations but provided no explanation of the decreasing concentrations with increasing recovery.
Note on DL29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on DV22: C. Rice: Consultant verified the TOC concentrations but provided no explanation of the decreasing concentrations with increasing recovery.
Note on DV29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on EF22: C. Rice: Consultant verified the TOC concentrations but provided no explanation of the decreasing concentrations with increasing recovery.
Note on EF29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Print All Fields

## ESNA. 2nd Quarter
FIELD-SET 3: Membrane C, Run 2 (FILE: Margate2.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Hydranautics | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.71443 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.28 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | ESNA1 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-04-27 | 1999-04-30 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 16.9 | [10 empty] | Feed flow rate during sample collection (mL/min) | 13.1 | [7 empty] | Feed flow rate during sample collection (mL/min) | 23 | [7 empty] | Feed flow rate during sample collection (mL/min) | 38.7 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 180 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 1:15 | 6:20 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 411 | [10 empty] | Influent flow rate during sample collection (mL/min) | 411 | [7 empty] | Influent flow rate during sample collection (mL/min) | 411 | [7 empty] | Influent flow rate during sample collection (mL/min) | 411 | [6 empty] | SDS-THM4F, ug/L | 206.85 | 206.85 | 206.85 | 206.85 | SDS-THM4F, ug/L | 206.85 | 206.85 | 206.85 | 206.85 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 15.7 | 92 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 51.5 | 59.5 | 34 | 20.9 | SDS-THM4p, ug/L | 51.5 | 59.5 | 34 | 20.9 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.8 | 6.94 | 6.87 | 2.0378 | 1999-04-24 | 11:20 | 0 | 24 | 93 | 92 | 411 | 12 | 5 | 17 | 0.31102 | 0.70588 | 23.1765 | 27.3894 | 25.8171 | 99.6977 | 29.2926 | 97.6421 | 0.69377 | 91.8062 | 0.28121 | 1999-04-26 | 9:30 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 126.3 | 126.3 | 126.3 | 126.3 | SDS-HAA5F, ug/L | 126.3 | 126.3 | 126.3 | 126.3 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.32945 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1999-04-24 | 15:20 | 4 | 25.6 | 96.5 | 96 | 411 | 12 | 5 | 17 | 0.31102 | 0.70588 | 23.1765 | 27.3894 | 24.6245 | 99.6977 | 29.2926 | 97.6421 | 0.69377 | 95.5562 | 0.2577 | 1999-04-26 | 10:36 | 1.1 | 25 | 120.1 | 119.8 | 400 | 11.7 | 5.1 |  | 16.8 | 0.3027 | 0.69643 | 22.8095 | 26.7046 | 24.4385 | 1030.5825 | 288.1051 | 1008.8651 | 7.3162 | 112.6338 | 0.21697 | 6.48 |  |  | 289.742 |  |  | 1026.8272 |  | 43.5751 | 1016.0473 | 71.4834 | 0.066 |  |  | 0.83188 |  | 77.8894 | 0.82068 | 91.9579 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 13.85 | 22.2 | 8.9 | 5.7 | SDS-HAA5p, ug/L | 13.85 | 22.2 | 8.9 | 5.7 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 101.5 | 88.2 | 94.85 | 14.0221 | 1999-04-25 | 9:36 | 23.1 | 25.5 | 95 | 94 | 411 | 11.7 | 5.2 | 16.9 | 0.31102 | 0.69231 | 23.3195 | 26.7046 | 24.08 | 97.8071 | 28.7524 | 95.8413 | 0.68072 | 93.8193 | 0.25666 | 1999-04-26 | 14:15 | 4.7 | 25.5 | 133.4 | 133.1 | 360 | 11.8 | 5.1 |  | 16.9 | 0.27243 | 0.69822 | 20.3018 | 26.9329 | 24.2858 | 1034.3309 | 288.3951 | 1009.8808 | 7.3371 | 125.9129 | 0.19288 | 6.45 |  |  | 279.216 |  |  | 1055.5689 |  | 45.6249 | 1042.8453 | 73.2256 | 0.063 |  |  | 0.84338 |  | 78.8945 | 0.83059 | 92.4151 | [8 empty] | Sampling date | MM/DD/YY | 1999-04-27 | 1999-04-27 | --- | --- | 1999-04-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-28 | 1999-04-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-29 | 1999-04-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-30 | 1999-04-30 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 618.25 | 618.25 | 618.25 | 618.25 | SDS-TOXF, ug Cl- /L | 618.25 | 618.25 | 618.25 | 618.25 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 388 | 639 | 513.5 | 48.8802 | 1999-04-25 | 11:37 | 25.1 | 25.5 | 95 | 94 | 411 | 11.4 | 5.3 | 16.7 | 0.31102 | 0.68263 | 23.6108 | 26.0199 | 23.4625 | 96.4979 | 28.3826 | 94.6085 | 0.67171 | 93.8283 | 0.25006 | 1999-04-26 | 17:15 | 7.7 | 26.1 | 132 | 131 | 411 | 11.6 | 5.3 |  | 16.9 | 0.31102 | 0.68639 | 23.3195 | 26.4764 | 23.4545 | 1015.545 | 284.1174 | 994.9013 | 7.2111 | 124.2889 | 0.18871 | 6.26 | 6.57 | 7.17 | 331.292 | 570.63 | 799.528 | 912.2949 | -14.1042 | 35.4835 | 904.0958 | 63.3565 | 0.055 | 0.321 | 0.407 | 0.83144 | -104.2858 | 81.5745 | 0.82049 | 93.2967 | [8 empty] | Sampling time | hh:mm | 1:15 | 1:15 | --- | --- | 1:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 0:57 | 0:57 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 1:42 | 1:42 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 6:20 | 6:20 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 108.75 | 140 | 72.7 | 55.1 | SDS-TOXp, ug Cl- /L | 108.75 | 140 | 72.7 | 55.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 337 | 318 | 327.5 | 5.8015 | 1999-04-25 | 17:36 | 31.1 | 25.3 | 94.7 | 94.2 | 411 | 11.4 | 5.1 | 16.5 | 0.31102 | 0.69091 | 23.9091 | 26.0199 | 23.6017 | 97.598 | 28.7061 | 95.6872 | 0.67936 | 93.7706 | 0.2517 | 1999-04-27 | 9:50 | 24.3 | 26 | 148.8 | 148.4 | 411 | 11.8 | 1.4 |  | 13.2 | 0.31102 | 0.89394 | 30.1364 | 26.9329 | 23.9295 | 1442.1469 | 403.3216 | 1412.3217 | 10.2391 | 138.3609 | 0.17295 | 6.39 |  |  | 419.84 |  |  | 1302.92 |  | 18.2395 | 1290.2432 | 67.4604 | 0.072 |  |  | 2.2076 |  | 75.8794 | 2.1769 | 96.6926 | [8 empty] | Operation time | hh.hh | 15.7 | 15.7 | --- | --- | 15.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 39.5 | 39.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 63.5 | 63.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 92 | 92 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.515 | 11.515 | 11.515 | 11.515 | SDS-CDF, mg/L | 11.515 | 11.515 | 11.515 | 11.515 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 27 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 317 | 299 | 308 | 5.8442 | [21 empty] | 1999-04-27 | 13:02 | 27.5 | 26.8 | 148 | 147.8 | 411 | 11.6 | 1.5 |  | 13.1 | 0.31102 | 0.8855 | 30.374 | 26.4764 | 22.9742 | 1417.5777 | 396.5934 | 1388.7616 | 10.0658 | 137.8342 | 0.16668 | 6.4 |  |  | 450.56 |  |  | 1000.236 |  | 12.2571 | 992.479 | 54.6026 | 0.075 |  |  | 2.0269 |  | 74.8744 | 1.9994 | 96.2488 | [8 empty] | pH | --- | 6.83 | 6.79 | 6.81 | 0.58737 | 7.26 | --- | --- | --- | --- | --- | pH | --- | 7.08 | 8.01 | --- | --- | --- | --- | --- | pH | --- | 6.65 | 7.05 | --- | --- | --- | --- | --- | pH | --- | 6.76 | 6.99 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.665 | 4.81 | 3.77 | 3.6 | SDS-CDp, mg/L | 4.665 | 4.81 | 3.77 | 3.6 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 68 | 1 | 0.7 | 27 | 14.3517 | 96.3062 | 411.456 | 11.8281 | 16.8973 | 5.0692 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.22 | 1.5 | 0.86 | 148.8372 | [21 empty] | 1999-04-27 | 16:39 | 31.1 | 27.3 | 147.6 | 147.1 | 411 | 11.7 | 1.4 |  | 13.1 | 0.31102 | 0.89313 | 30.374 | 26.7046 | 22.8323 | 1439.6068 | 402.6838 | 1410.0885 | 10.2216 | 137.1284 | 0.1665 | 6.54 | 6.7 | 7.54 | 444.16 | 576.15 | 1546.405 | 1092.9843 | 29.321 | 13.5034 | 1083.7492 | 59.0163 | 0.069 | 0.308 | 1.966 | 2.2165 | -12.7398 | 76.8844 | 2.1859 | 96.8434 | [8 empty] | Temperature | oC | 26.1 | 26.1 | 26.1 | 0 | 26.1 | --- | --- | --- | --- | --- | Temperature | oC | 27.3 | 27.3 | --- | --- | --- | --- | --- | Temperature | oC | 25.3 | 25.3 | --- | --- | --- | --- | --- | Temperature | oC | 24.3 | 24.3 | --- | --- | --- | --- | --- | TOCF, mg/L | 8.5 | 8.5 | 8.5 | 8.5 | TOCF, mg/L | 8.5 | 8.5 | 8.5 | 8.5 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.36 | 2 | 0.9 | 27 | 39.785 | 121.7395 | 411.456 | 11.8281 | 13.1424 | 1.3142 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.81 | 0.62 | 0.715 | 26.5734 | [21 empty] | 1999-04-28 | 11:45 | 49.5 | 25.9 | 149.4 | 149.1 | 411 | 11.3 | 11.8 |  | 23.1 | 0.31102 | 0.48918 | 16.7922 | 25.7916 | 22.9834 | 792.7405 | 221.9037 | 777.046 | 5.6299 | 143.6201 | 0.16003 | 6.33 |  |  | 242.721 |  |  | 772.8053 |  | 52.732 | 765.5183 | 68.2932 | 0.035 |  |  | 0.55083 |  | 88.2747 | 0.54374 | 93.5631 | [8 empty] | Alkalinity | mg/L as CaCO3 | 58.2 | 58.8 | 58.5 | 1.0256 | 197 | 175.7581 | 10.7827 | 38.3237 | 174.0946 | 66.3976 | Alkalinity | mg/L as CaCO3 | 77.2 | 288 | 237.6545 | 17.4811 | 18.6083 | 235.3787 | 67.2018 | Alkalinity | mg/L as CaCO3 | 25.2 | 89.6 | 161.7686 | -80.5453 | 73.4317 | 159.8962 | 84.2398 | Alkalinity | mg/L as CaCO3 | 35.5 | 112 | 117.9306 | -5.2951 | 62.5725 | 116.8439 | 69.6176 | TOCp, mg/L | 1.725 | 2.18 | 0.95 | 0.64 | TOCp, mg/L | 1.725 | 2.18 | 0.95 | 0.64 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 27 | 9.265 | 91.2195 | 411.456 | 11.8281 | 23.6562 | 11.8281 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 8.6 | 8.4 | 8.5 | 2.3529 | [21 empty] | 1999-04-28 | 12:46 | 50.5 | 26 | 149.7 | 149.3 | 411 | 11.5 | 11.8 |  | 23.3 | 0.31102 | 0.49356 | 16.6395 | 26.2481 | 23.3211 | 796.6851 | 222.9275 | 780.631 | 5.6573 | 143.8427 | 0.16213 | 6.26 |  |  | 241.092 |  |  | 778.9824 |  | 53.0493 | 771.4571 | 68.7485 | 0.031 |  |  | 0.5592 |  | 89.6147 | 0.55181 | 94.3821 | [8 empty] | Total dissolved solids | mg/L | 314 | 349 | 331.5 | 10.5581 | 800 | 918.5968 | -14.8246 | 35.443 | 910.2681 | 63.5822 | Total dissolved solids | mg/L | 438 | 1546 | 1124.3636 | 27.2727 | 14.703 | 1114.6285 | 60.7044 | Total dissolved solids | mg/L | 297 | 804 | 721.5098 | 10.26 | 42.1616 | 715.6896 | 58.5016 | Total dissolved solids | mg/L | 209.5 | 649 | 631.7222 | 2.6622 | 59.2016 | 626.1563 | 66.5419 | UV254 F, cm-1 | 0.2985 | 0.2985 | 0.2985 | 0.2985 | UV254 F, cm-1 | 0.2985 | 0.2985 | 0.2985 | 0.2985 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 27 | 7.085 | 89.0395 | 411.456 | 11.8281 | 39.4271 | 27.599 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.305 | 0.292 | 0.2985 | 4.3551 | [21 empty] | 1999-04-28 | 17:55 | 55.6 | 25.3 | 151.5 | 151.2 | 411 | 11.2 | 11.8 |  | 23 | 0.31102 | 0.48696 | 16.8696 | 25.5634 | 23.1876 | 790.7582 | 221.3887 | 775.2425 | 5.6161 | 145.7339 | 0.15911 | 6.17 | 6.34 | 6.7 | 297.021 | 611.34 | 804.525 | 718.9716 | 10.634 | 42.1575 | 713.2224 | 58.3551 | 0.031 | 0.31 | 0.529 | 0.5524 | -4.4231 | 89.6147 | 0.54529 | 94.315 | [8 empty] | Total hardness | mg/L as CaCO3 | 208 | 210 | 209 | 0.95694 | 611 | 591.2581 | 3.2311 | 36.1832 | 585.8353 | 64.3244 | Total hardness | mg/L as CaCO3 | 254 | 858 | 922.1818 | -7.4804 | 22.4427 | 912.7045 | 72.1706 | Total hardness | mg/L as CaCO3 | 143 | 445 | 504.7647 | -13.4303 | 56.3359 | 499.8047 | 71.3888 | Total hardness | mg/L as CaCO3 | 115 | 377 | 410.1389 | -8.7902 | 64.8855 | 406.2482 | 71.6922 | UV254 p, cm-1 | 0.048 | 0.0615 | 0.028 | 0.021 | UV254 p, cm-1 | 0.048 | 0.0615 | 0.028 | 0.021 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 875 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.5465 | 3.4762 | 3.5114 | 2.0027 | [21 empty] | 1999-04-29 | 9:59 | 71.7 | 25 | 149.1 | 148.6 | 411 | 10.8 | 27.5 |  | 38.3 | 0.31102 | 0.28198 | 9.7311 | 24.6504 | 22.5586 | 644.2752 | 180.5077 | 632.0886 | 4.5767 | 144.2733 | 0.15636 | 5.96 |  |  | 124.696 |  |  | 666.1939 |  | 75.7165 | 659.0794 | 81.0803 | 0.023 |  |  | 0.4067 |  | 92.2948 | 0.40166 | 94.2737 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 195 | 197 | 196 | 1.0204 | 574 | 557.2903 | 2.9111 | 36.3636 | 552.165 | 64.5034 | Calcium hardness | mg/L as CaCO3 | 239 | 806 | 866.2727 | -7.478 | 22.4026 | 857.3757 | 72.1242 | Calcium hardness | mg/L as CaCO3 | 134 | 416 | 475.1765 | -14.2251 | 56.4935 | 470.4988 | 71.5196 | Calcium hardness | mg/L as CaCO3 | 107 | 354 | 386.1667 | -9.0866 | 65.2597 | 382.4866 | 72.0252 | BromideF, ug/L | 194 | 194 | 194 | 194 | BromideF, ug/L | 194 | 194 | 194 | 194 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 211 | 177 | 194 | 17.5258 | [21 empty] | 1999-04-29 | 14:18 | 76 | 25.5 | 148.7 | 148.4 | 411 | 10.9 | 27.6 |  | 38.5 | 0.31102 | 0.28312 | 9.6753 | 24.8787 | 22.4335 | 644.9464 | 180.6633 | 632.6333 | 4.5813 | 143.9687 | 0.15582 | 5.97 |  |  | 108.394 |  |  | 673.4875 |  | 78.8911 | 665.9942 | 83.7245 | 0.024 |  |  | 0.40691 |  | 91.9598 | 0.40183 | 94.0273 | [8 empty] | Turbidity | ntu | BMRL | BMRL | #DIV/0! | #VALUE! | 0.19 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu | BMRL | 0.32 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.27 | 1.6671 | -517.4292 | 97.6744 | 1.6445 | 98.7838 | Turbidity | ntu | 0 | 0.11 | 1.1944 | -985.8586 | 100 | 1.1787 | 100 | Bromidep, ug/L | 126.5 | 146 | 91 | 82 | Bromidep, ug/L | 126.5 | 146 | 91 | 82 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.6 | 12.6 | 12.6 | 0 | [21 empty] | 1999-04-29 | 18:56 | 80.6 | 26 | 149.8 | 149.2 | 411 | 11 | 27.7 |  | 38.7 | 0.31102 | 0.28424 | 9.6202 | 25.1069 | 22.3072 | 645.6123 | 180.8172 | 633.1725 | 4.5858 | 144.9142 | 0.15393 | 6.18 | 6.72 | 6.63 | 209.638 | 593.4 | 648.825 | 634.1672 | 2.2591 | 59.1747 | 628.4862 | 66.644 | 0.025 | 0.315 | 0.403 | 0.40711 | -1.0199 | 91.6248 | 0.402 | 93.781 | [8 empty] | Ammonia | mg NH3-N / L | 0.42 | 0.43 | 0.425 | 2.3529 | 0.92 | 1.3605 | -47.8787 | 40.5594 | 1.3472 | 68.4534 | Ammonia | mg NH3-N / L | 0.63 | 1.36 | 1.4027 | -3.1417 | 11.8881 | 1.3918 | 54.7338 | Ammonia | mg NH3-N / L | 0.46 | 0.89 | 0.96 | -7.8652 | 35.6643 | 0.95314 | 51.7387 | Ammonia | mg NH3-N / L | 0.33 | 0.7 | 0.86472 | -23.5317 | 53.8462 | 0.85767 | 61.5238 | AlkF, mg/L CaCO3 | 94.85 | 94.85 | 94.85 | 94.85 | AlkF, mg/L CaCO3 | 94.85 | 94.85 | 94.85 | 94.85
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 76.667 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.04 | 1.13 | 1.085 | 8.2949 | [21 empty] | 1999-04-30 | 17:45 | 95.4 | 22.5 | 148.5 | 148 | 411 | 11.9 | 27.4 | x | 39.3 | 0.31102 | 0.3028 | 9.458 | 27.1611 | 26.7626 | 656.7598 | 183.6412 | 643.0613 | 4.6627 | 143.5873 | 0.18639 | 6.47 |  |  | 120.692 |  |  | 684.0991 |  | 76.4962 | 675.9427 | 82.1446 | 0.044 |  |  | 0.40903 |  | 85.2596 | 0.40375 | 89.1021 | [8 empty] | Total organic carbon | mg/L | 1.74 | 1.71 | 1.725 | 1.7391 | 18.8 | 23.5798 | -25.4247 | 79.7059 | 23.2698 | 92.587 | Total organic carbon | mg/L | 2.18 | 59 | 59.6345 | -1.0755 | 74.3529 | 58.8196 | 96.2938 | Total organic carbon | mg/L | 0.95 | 16.3 | 15.7539 | 3.3502 | 88.8235 | 15.551 | 93.891 | Total organic carbon | mg/L | 0.64 | 11.8 | 11.5567 | 2.0621 | 92.4706 | 11.4128 | 94.3922 | Alkp, mg/L CaCO3 | 58.5 | 77.2 | 25.2 | 35.5 | Alkp, mg/L CaCO3 | 58.5 | 77.2 | 25.2 | 35.5
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.56 | 11.47 | 11.515 | 0.78159 | [21 empty] | 1999-04-30 | 21:20 | 99 | 23 | 147.1 | 146.7 | 411 | 12 | 27.9 |  | 39.9 | 0.31102 | 0.30075 | 9.3008 | 27.3894 | 26.5916 | 655.5361 | 183.266 | 641.7472 | 4.6538 | 142.2462 | 0.18694 | 6.19 |  |  | 94.094 |  |  | 693.8897 |  | 81.6759 | 685.1335 | 86.2663 | 0.032 |  |  | 0.41312 |  | 89.2797 | 0.40756 | 92.1484 | [8 empty] | UV254 | cm-1 | 0.048 | 0.048 | 0.048 | 0 | 0.459 | 0.85606 | -86.5064 | 83.9196 | 0.8446 | 94.3168 | UV254 | cm-1 | 0.0615 | 2.072 | 2.216 | -6.952 | 79.397 | 2.1855 | 97.186 | UV254 | cm-1 | 0.028 | 0.609 | 0.55839 | 8.31 | 90.6198 | 0.55112 | 94.9194 | UV254 | cm-1 | 0.021 | 0.43 | 0.40642 | 5.4845 | 92.9648 | 0.40134 | 94.7675 | T-HdF, mg/L CaCO3 | 327.5 | 327.5 | 327.5 | 327.5 | T-HdF, mg/L CaCO3 | 327.5 | 327.5 | 327.5 | 327.5
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | [21 empty] | 1999-04-30 | 23:50 | 101.5 | 23.3 | 147.9 | 147.4 | 411 | 12 | 26.8 |  | 38.8 | 0.31102 | 0.30928 | 9.5928 | 27.3894 | 26.3568 | 660.7174 | 184.7145 | 646.8195 | 4.6905 | 142.9595 | 0.18437 | 6.21 | 6.74 | 6.73 | 88.66 | 520.26 | 597.552 | 703.7269 | -17.7683 | 82.7342 | 694.7478 | 87.2385 | 0.03 | 0.314 | 0.447 | 0.41872 | 6.3258 | 89.9497 | 0.41305 | 92.7369 | [8 empty] | SUVA | L/(mg*m) | 2.7586 | 2.807 | 2.7828 | 1.7391 | 2.4415 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8211 | 3.5119 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.9474 | 3.7362 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.2812 | 3.6441 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 209 | 254 | 143 | 115 | T-Hdp, mg/L CaCO3 | 209 | 254 | 143 | 115
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.42 | 7.45 | 7.435 | 0.4035 | [70 empty] | Bromide | mg/L | 126 | 127 | 126.5 | 0.79051 | --- | 344.2419 | --- | 34.7938 | 341.153 | 62.9199 | Bromide | mg/L | 146 | --- | 582.3636 | --- | 24.7423 | 576.1744 | 74.6604 | Bromide | mg/L | 91 | --- | 292.9608 | --- | 53.0928 | 290.1918 | 68.6414 | Bromide | mg/L | 82 | --- | 237.5556 | --- | 57.732 | 235.5049 | 65.1812 | Ca-HdF, mg/L CaCO3 | 308 | 308 | 308 | 308 | Ca-HdF, mg/L CaCO3 | 308 | 308 | 308 | 308
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | Unknown | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.03 | 24.13 | 24.08 | 0.41528 | [70 empty] | SDS-Cl2 dose | mg/L | 5.4 | 5.4 | 5.4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 6.4 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.12 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 196 | 239 | 134 | 107 | Ca-Hdp, mg/L CaCO3 | 196 | 239 | 134 | 107
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | 5 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 568.5 | 668 | 618.25 | 16.0938 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.7 | 0.77 | 0.735 | 9.5238 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.59 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.53 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.52 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 20 | [14 empty] | SDS-CHCl3 | mg/L | 146 | 147 | 146.5 | 0.68259 | [70 empty] | SDS-Cl2 demand | mg/L | 4.7 | 4.63 | 4.665 | 1.5005 | --- | 26.7618 | --- | 59.4876 | 26.4483 | 82.3618 | SDS-Cl2 demand | mg/L | 4.81 | --- | 65.7645 | --- | 58.2284 | 64.9 | 92.5886 | SDS-Cl2 demand | mg/L | 3.77 | --- | 18.9563 | --- | 67.2601 | 18.7481 | 79.8913 | SDS-Cl2 demand | mg/L | 3.6 | --- | 14.5931 | --- | 68.7364 | 14.4481 | 75.0833 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 50.5 | 51.1 | 50.8 | 1.1811 | [70 empty] | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 86.804 | 91.5168 | 78.0156 | 72.5195 | Qp/QT (THM4), % | 109.9775 | 115.9484 | 98.8429 | 91.8795
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | min 70% avg 80% | [14 empty] | SDS-DBCM | mg/L | 9.6 | 9.5 | 9.55 | 1.0471 | [70 empty] | SDS-Chlorination pH | --- | 7.56 | 7.59 | 7.575 | 0.39604 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.43 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.52 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | 36 | 36
|  | (e.g., solute type and concentration) | 500 ppm NaCl | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 23.97 | 24 | 23.985 | 0.12508 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.1 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48.1 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.58 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 28.6889 | 31.031 | 34.7097 | 38.8415 | SDS-HAA5b, ug/L | NA | NA | 10.2584 | 15.4933
|  | Variability of rejection of reference solute (%) | 10 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 206.1 | 207.6 | 206.85 | 0.72516 | [70 empty] | SDS-TOX | mg Cl- /L | 107 | 110.5 | 108.75 | 3.2184 | --- | 1752.2984 | --- | 82.41 | 1728.9828 | 93.7102 | SDS-TOX | mg Cl- /L | 140 | --- | 4487.7273 | --- | 77.3554 | 4426.0604 | 96.8369 | SDS-TOX | mg Cl- /L | 72.7 | --- | 1142.4059 | --- | 88.241 | 1127.7397 | 93.5535 | SDS-TOX | mg Cl- /L | 55.1 | --- | 837.2528 | --- | 91.0877 | 826.9421 | 93.3369 | SDS-TOXb, ug Cl- /L | 175.9837 | 180.5709 | 192.6358 | 209.8565 | SDS-TOXb, ug Cl- /L | NA | NA | 79.0124 | 100.8304
|  | Standard testing recovery (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 8.6 | 6 | 7.3 | 35.6164 | [70 empty] | SDS-CHCl3 | mg/L | 13.4 | 13 | 13.2 | 3.0303 | --- | 443.2 | --- | 90.9898 | 437.1 | 96.9801 | SDS-CHCl3 | mg/L | 18.2 | --- | 1184.5636 | --- | 87.5768 | 1168.0203 | 98.4418 | SDS-CHCl3 | mg/L | 7.7 | --- | 279.8569 | --- | 94.744 | 276.1255 | 97.2114 | SDS-CHCl3 | mg/L | 4.2 | --- | 201.8389 | --- | 97.1331 | 199.2335 | 97.8919 | SDS-CDb, mg/L | 5.5689 | 5.3788 | 5.4727 | 5.7751 | SDS-CDb, mg/L | NA | NA | 3.8596 | 4.2427
|  | Standard testing pH | 6.5-7 | [14 empty] | SDS-DCAA* | mg/L | 44.6 | 43 | 43.8 | 3.653 | [70 empty] | SDS-BDCM | mg/L | 18.5 | 17.1 | 17.8 | 7.8652 | --- | 124.2516 | --- | 64.9606 | 122.7415 | 85.498 | SDS-BDCM | mg/L | 22.1 | --- | 283.0091 | --- | 56.4961 | 279.3084 | 92.0876 | SDS-BDCM | mg/L | 11.9 | --- | 88.1745 | --- | 76.5748 | 87.1288 | 86.3421 | SDS-BDCM | mg/L | 6.7 | --- | 67.95 | --- | 86.811 | 67.1426 | 90.0212 | TOCb, mg/L | 2.619 | 2.7161 | 2.6098 | 2.8 | TOCb, mg/L | NA | NA | 1.0374 | 1.2783
|  | Acceptable range of operating pressures | <400 psi | [14 empty] | SDS-TCAA* | mg/L | 73.1 | 71.8 | 72.45 | 1.7943 | [70 empty] | SDS-DBCM | mg/L | 17.5 | 16.1 | 16.8 | 8.3333 | --- | -6.5871 | --- | -75.9162 | -6.2553 | 368.5712 | SDS-DBCM | mg/L | 17.3 | --- | -53.1545 | --- | -81.1518 | -52.1552 | 133.1702 | SDS-DBCM | mg/L | 12 | --- | 7.1961 | --- | -25.6545 | 7.2619 | -65.245 | SDS-DBCM | mg/L | 8.4 | --- | 9.9972 | --- | 12.0419 | 9.9762 | 15.7993 | UV254 b, cm-1 | 0.081056 | 0.081605 | 0.087468 | 0.097258 | UV254 b, cm-1 | NA | NA | 0.03113 | 0.043534
|  | Acceptable range of operating pH values | 3-10 | [14 empty] | SDS-MBAA* | mg/L | 1.2 | 1.2 | 1.2 | 0 | [70 empty] | SDS-CHBr3 | mg/L | 3.8 | 3.6 | 3.7 | 5.4054 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.9 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 135.4073 | 150.0719 | 113.6439 | 112.7782 | Bromideb, ug/L | NA | NA | 92.1918 | 91.0949
|  | Typical pressure drop across a single element (psi) | 3-5 | [14 empty] | SDS-DBAA* | mg/L | 1.7 | 1.4 | 1.55 | 19.3548 | [70 empty] | SDS-THM4 | mg/L | 53.2 | 49.8 | 51.5 | 6.6019 | --- | 552.629 | --- | 75.1027 | 545.5199 | 90.5595 | SDS-THM4 | mg/L | 59.5 | --- | 1399.0455 | --- | 71.2352 | 1380.0457 | 95.6885 | SDS-THM4 | mg/L | 34 | --- | 372.9216 | --- | 83.563 | 368.2748 | 90.7678 | SDS-THM4 | mg/L | 20.9 | --- | 279.1639 | --- | 89.8961 | 275.7593 | 92.4209 | Alkb, mg/L CaCO3 | 63.2967 | 78.6973 | 40.5121 | 51.8097 | Alkb, mg/L CaCO3 | NA | NA | 26.0059 | 40.3195
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 12.6 | 10.6 | 11.6 | 17.2414 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | 2.2 | --- | 48.5636 | --- | 69.863 | 47.906 | 95.4077 | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 224.6373 | 260.2352 | 183.5612 | 173.3961 | T-Hdb, mg/L CaCO3 | NA | NA | 145.1348 | 132.256
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 5.7 | 5.3 | 5.5 | 7.2727 | --- | 129.0484 | --- | 87.4429 | 127.2957 | 95.6794 | SDS-DCAA* | mg/L | 7.3 | --- | 339.1182 | --- | 83.3333 | 334.4118 | 97.8171 | SDS-DCAA* | mg/L | 3.6 | --- | 82.4235 | --- | 91.7808 | 81.3428 | 95.5743 | SDS-DCAA* | mg/L | 1.9 | --- | 60.0944 | --- | 95.6621 | 59.3273 | 96.7974 | Ca-Hdb, mg/L CaCO3 | 210.7795 | 244.8534 | 172.2528 | 162.2358 | Ca-Hdb, mg/L CaCO3 | NA | NA | 136.0133 | 123.3221
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 4.2 | 4.3 | 4.25 | 2.3529 | --- | 224.25 | --- | 94.1339 | 221.1291 | 98.078 | SDS-TCAA* | mg/L | 8.3 | --- | 591.4818 | --- | 88.5438 | 583.2101 | 98.5768 | SDS-TCAA* | mg/L | 2.6 | --- | 139.5608 | --- | 96.4113 | 137.683 | 98.1116 | SDS-TCAA* | mg/L | 2 | --- | 99.8472 | --- | 97.2395 | 98.5574 | 97.9707
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | 1 | --- | 2.8182 | --- | 16.6667 | 2.7924 | 64.1884 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 129.2 | 123.4 | 126.3 | 4.5922 | [70 empty] | SDS-DBAA* | mg/L | 4.4 | 3.8 | 4.1 | 14.6341 | --- | -4.1258 | --- | -164.5161 | -4.0091 | 202.267 | SDS-DBAA* | mg/L | 3.4 | --- | -13.4182 | --- | -119.3548 | -13.1796 | 125.7974 | SDS-DBAA* | mg/L | 2.7 | --- | 0.4451 | --- | -74.1935 | 0.47601 | -467.2105 | SDS-DBAA* | mg/L | 1.8 | --- | 1.4528 | --- | -16.129 | 1.4574 | -23.5114 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 141.8 | 134 | 137.9 | 5.6563 | [70 empty] | SDS-BCAA* | mg/L | 6.6 | 5.6 | 6.1 | 16.3934 | --- | 23.8419 | --- | 47.4138 | 23.5902 | 74.1419 | SDS-BCAA* | mg/L | 6.8 | --- | 50.4364 | --- | 41.3793 | 49.8174 | 86.3502 | SDS-BCAA* | mg/L | 4.1 | --- | 18.8059 | --- | 64.6552 | 18.6043 | 77.962 | SDS-BCAA* | mg/L | 2.2 | --- | 15.2556 | --- | 81.0345 | 15.0835 | 85.4145 | Qp/QT (HAA5), % | 64.2952 | 69.4524 | 61.5843 | 59.9502 | Qp/QT (HAA5), % | 88.3059 | 95.389 | 84.5826 | 82.3383
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 106.9673 | 104.5118 | 100.4015 | 95.3725 | SDS-THM4b, ug/L | 69.6668 | 66.2942 | 60.6489 | 53.7419
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 290.6657 | 286.0937 | 282.2767 | 280.6402 | SDS-TOXb, ug Cl- /L | 168.3314 | 162.0519 | 156.8095 | 154.5618
[94 empty] | SDS-HAA5 | mg/L | 14.3 | 13.4 | 13.85 | 6.4982 | --- | 376.5919 | --- | 89.034 | 371.446 | 96.2713 | SDS-HAA5 | mg/L | 22.2 | --- | 968.5636 | --- | 82.4228 | 955.1407 | 97.6757 | SDS-HAA5 | mg/L | 8.9 | --- | 239.0961 | --- | 92.9533 | 235.94 | 96.2279 | SDS-HAA5 | mg/L | 5.7 | --- | 173.2 | --- | 95.4869 | 170.9919 | 96.6665 | SDS-CDb, mg/L | 7.1108 | 6.8582 | 6.7453 | 6.7699 | SDS-CDb, mg/L | 5.466 | 5.1192 | 4.9641 | 4.9979
[94 empty] | SDS-HAA6 | mg/L | 20.9 | 19 | 19.95 | 9.5238 | --- | 400.4339 | --- | 85.533 | 395.0363 | 94.9498 | SDS-HAA6 | mg/L | 29 | --- | 1019 | --- | 78.9703 | 1004.9581 | 97.1143 | SDS-HAA6 | mg/L | 13 | --- | 257.902 | --- | 90.5729 | 254.5442 | 94.8928 | SDS-HAA6 | mg/L | 7.9 | --- | 188.4556 | --- | 94.2712 | 186.0754 | 95.7544 | TOCb, mg/L | 4.144 | 4.1106 | 3.8504 | 3.7879 | TOCb, mg/L | 2.5173 | 2.4714 | 2.114 | 2.0282
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.13744 | 0.1339 | 0.13191 | 0.13214 | UV254 b, cm-1 | 0.077294 | 0.072428 | 0.069704 | 0.070011
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 150.6007 | 160.6628 | 130.5681 | 126.8557 | Bromideb, ug/L | 134.3935 | 148.2133 | 106.8799 | 101.7811
[133 empty] | Alkb, mg/L CaCO3 | 71.4787 | 82.5916 | 51.9565 | 59.2695 | Alkb, mg/L CaCO3 | 62.7508 | 78.0138 | 35.9382 | 45.9822
[133 empty] | T-Hdb, mg/L CaCO3 | 251.3101 | 276.4524 | 213.8769 | 200.1057 | T-Hdb, mg/L CaCO3 | 222.8575 | 257.389 | 171.4451 | 152.5311
[133 empty] | Ca-Hdb, mg/L CaCO3 | 235.9893 | 260.0778 | 200.8433 | 187.5 | Ca-Hdb, mg/L CaCO3 | 209.0974 | 242.1816 | 160.8262 | 142.5
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on X12: C. Rice: Consultant verified the feed UV, TDS and turbidity analyses; no explanations were given for the substantial differences in the two values.
Note on X15: C. Rice: Consultant verified the feed TDS and turbidity analyses; no explanations were given for the substantial differences in the two values.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on AA10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on CD7: C. Rice: There is no record of an operational anomaly during the 30% run so the TDS data should be considered valid. TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Note on CD8: C. Rice: Consultant verified the data that resulted in the high MB closure errors for TDS.
Note on CL8: C. Rice: Consultant verified the data that resulted in high MB closure errors.
Note on CY29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on CZ9: Consultant stated that there were no anomalies reported for the 70% run; there was no explanation for the lower concentrations of TOC, UV, TOX, TDS, alkalinity, total hardness, bromide, THM4 and individual species, and HAA6 and individual species during the 4th quarter at 70% recovery.
Note on DL29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on DV29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on EF29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Print All Fields

## TFC. 2nd Quarter
FIELD-SET 4: Membrane D, Run 2 (FILE: Margate1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Margate, DEES | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | 243 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.7 | [5 empty] | TDS concentration of setting solution (mg/L) | 50 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.85835 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.31 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060845 | Membrane trade name | TFC 8921S-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33333 |  |  | Calcium Hardness (mg/L as CaCO3) | 295 | Acidification | Hydrochloric acid to pH 6.5 | Bench | Sampling date | MM/DD/YY | 1999-05-04 | 1999-05-07 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.4 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.1 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.2 | [7 empty] | Feed flow rate during sample collection (mL/min) | 22.3 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 5.75%
Water Industry Data Base Number (optional) | N/A | Molecular weight cutoff (Daltons) | 200 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI |  | Antiscalant addition | King Lee PreTreat 0100, 3 ppm by volume | Bench | Sampling time | hh:mm | 2:19 | 5:19 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 299 | [10 empty] | Influent flow rate during sample collection (mL/min) | 299 | [7 empty] | Influent flow rate during sample collection (mL/min) | 299 | [7 empty] | Influent flow rate during sample collection (mL/min) | 299 | [6 empty] | SDS-THM4F, ug/L | 182.8 | 182.8 | 182.8 | 182.8 | SDS-THM4F, ug/L | 182.8 | 182.8 | 182.8 | 182.8 | Capital Recovery Period (years) | 25
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 545 |  |  | Dissolved iron (mg/L) |  | Cartridge filtration | 5 micron nominal | Bench | Operation time | hh.hh | 14.9 | 89.3 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 20.65 | 31.4 | 24.3 | 6.9 | SDS-THM4p, ug/L | 20.65 | 31.4 | 24.3 | 6.9 | Overhead & Profit Factor (% of construction costs) | 15%
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.7 |  |  | Total iron (mg/L) |  |  |  |  | pH | --- | 6.97 | 6.54 | 6.755 | 6.3657 | 1999-05-01 | 16:42 | 1 | 23.3 | 74.5 | 74.5 | 299 | 6.4 | 2.8 | 9.2 | 0.24367 | 0.69565 | 31.5 | 14.6077 | 14.057 | 98.0591 | 28.9741 | 96.5804 | 0.68346 | 73.8165 | 0.19043 | 1999-05-03 | 11:18 | 0 | [46 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 122.15 | 122.15 | 122.15 | 122.15 | SDS-HAA5F, ug/L | 122.15 | 122.15 | 122.15 | 122.15 | Special Sitework Factor (% of construction costs) | 5%
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.24251 |  |  | Dissolved aluminum (mg/L) |  |  |  |  | Temperature | oC | 21.5 | 21.5 | 21.5 | 0 | 1999-05-02 | 11:47 | 20.1 | 23.6 | 74.8 | 74.7 | 299 | 6.7 | 2.6 | 9.3 | 0.24367 | 0.72043 | 31.1505 | 15.2924 | 14.586 | 101.567 | 29.9889 | 99.9631 | 0.70776 | 74.0422 | 0.197 | 1999-05-03 | 12:42 | 1 | 24.3 | 86.5 | 86.2 | 299 | 6.5 | 2.7 |  | 9.2 | 0.24367 | 0.70652 | 31.5 | 14.8359 | 13.8608 | 1303.98 | 181.2545 | 1279.5729 | 11.1052 | 75.2448 | 0.18421 | 6.23 |  |  | 135.128 |  |  | 1415.0252 |  | 73.5432 | 1401.1133 | 90.3557 | 0.066 |  |  | 0.97067 |  | 80.0905 | 0.96083 | 93.131 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 6.25 | 8.7 | 6.7 | 0 | SDS-HAA5p, ug/L | 6.25 | 8.7 | 6.7 | 0 | Construction Contingencies (% of construction costs) | 15%
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  |  | Alkalinity | mg/L as CaCO3 | 145 | 145 | 145 | 0 | 1999-05-02 | 16:30 | 24.8 | 23.8 | 74.4 | 74.2 | 299 | 6.7 | 2.6 | 9.3 | 0.24367 | 0.72043 | 31.1505 | 15.2924 | 14.5 | 101.567 | 29.9889 | 99.9631 | 0.70776 | 73.5922 | 0.19703 | 1999-05-03 | 14:45 | 3.3 | 24.9 | 94 | 93.7 | 299 | 6.5 | 2.9 |  | 9.4 | 0.24367 | 0.69149 | 30.8085 | 14.8359 | 13.6171 | 1262.2696 | 175.4567 | 1238.6432 | 10.75 | 83.1 | 0.16386 | 6.44 |  |  | 139.192 |  |  | 1343.5524 |  | 72.7475 | 1330.4615 | 89.5381 | 0.063 |  |  | 0.93331 |  | 80.9955 | 0.92385 | 93.1807 | [8 empty] | Sampling date | MM/DD/YY | 1999-05-04 | 1999-05-04 | --- | --- | 1999-05-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-05 | 1999-05-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-06 | 1999-05-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-05-07 | 1999-05-07 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 790.5 | 790.5 | 790.5 | 790.5 | SDS-TOXF, ug Cl- /L | 790.5 | 790.5 | 790.5 | 790.5 | Engineering Fee Factor (% of construction costs) | 10%
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  |  | Total dissolved solids | mg/L | 534.5 | 487 | 510.75 | 9.3 | 1999-05-02 | 18:37 | 26.9 | 23.9 | 73.8 | 73.6 | 299 | 6.7 | 2.6 | 9.3 | 0.24367 | 0.72043 | 31.1505 | 15.2924 | 14.4572 | 101.567 | 29.9889 | 99.9631 | 0.70776 | 72.9922 | 0.19807 | 1999-05-03 | 17:45 | 6.4 | 25.1 | 95.3 | 95.1 | 299 | 6.6 | 2.8 |  | 9.4 | 0.24367 | 0.70213 | 30.8085 | 15.0641 | 13.7451 | 1291.5992 | 179.4807 | 1267.0507 | 10.9984 | 84.2016 | 0.16324 | 6.28 | 7.02 | 7.33 | 152.908 | 489.21 | 1340.964 | 1354.2347 | -0.98964 | 70.0621 | 1340.9759 | 88.5973 | 0.055 | 0.321 | 0.407 | 0.98325 | -141.5848 | 83.4087 | 0.97301 | 94.3474 | [8 empty] | Sampling time | hh:mm | 2:17 | 2:17 | --- | --- | 2:17 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 2:57 | 2:57 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 2:17 | 2:17 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 5:19 | 5:19 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 57.2 | 83.3 | 67.5 | BMRL | SDS-TOXp, ug Cl- /L | 57.2 | 83.3 | 67.5 | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5875
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  |  | Total hardness | mg/L as CaCO3 | 321 | 300 | 310.5 | 6.7633 | [21 empty] | 1999-05-04 | 10:49 | 23.4 | 24.7 | 103.8 | 103.5 | 299 | 6.5 | 0.7 |  | 7.2 | 0.24367 | 0.90278 | 40.5278 | 14.8359 | 13.6979 | 2293.3495 | 318.7777 | 2250.424 | 19.5311 | 84.1189 | 0.16284 | 6.47 |  |  | 152.716 |  |  | 3835.3514 |  | 70.0997 | 3795.3228 | 95.9762 | 0.075 |  |  | 2.7133 |  | 77.3756 | 2.6846 | 97.2063 | [8 empty] | Operation time | hh.hh | 14.9 | 14.9 | --- | --- | 14.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 39.5 | 39.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 62.2 | 62.2 | --- | --- | --- | --- | --- | Cumulative time | hr | 89.3 | 89.3 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.35 | 11.35 | 11.35 | 11.35 | SDS-CDF, mg/L | 11.35 | 11.35 | 11.35 | 11.35 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design flux, FW (gfd) | 15 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 26.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 302 | 282 | 292 | 6.8493 | [21 empty] | 1999-05-04 | 15:25 | 28 | 25 | 111.6 | 111.3 | 299 | 6.5 | 0.7 |  | 7.2 | 0.24367 | 0.90278 | 40.5278 | 14.8359 | 13.577 | 2293.3495 | 318.7777 | 2250.424 | 19.5311 | 91.9189 | 0.14771 | 6.63 |  |  | 188.803 |  |  | 3500.2579 |  | 63.0342 | 3464.2638 | 94.55 | 0.069 | 0.308 | 1.966 | 2.769 | -40.8444 | 79.1855 | 2.7397 | 97.4814 | [8 empty] | pH | --- | 6.92 | 6.82 | 6.87 | 1.4556 | 7.63 | --- | --- | --- | --- | --- | pH | --- | 6.98 | 8.15 | --- | --- | --- | --- | --- | pH | --- | 6.58 | 7.51 | --- | --- | --- | --- | --- | pH | --- | 6.11 | 6.77 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 3.23 | 4.75 | 3.83 | 1.61 | SDS-CDp, mg/L | 3.23 | 4.75 | 3.83 | 1.61 | Labor Rate + Fringe ($/work-hour) | 23.13
|  | Net driving pressure at the design flux, NDP (psi) | 56.5 | 1 | 0.7 | 15 | 14.3517 | 76.2041 | 299.4788 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  |  | Turbidity | ntu | 0.21 | 0.35 | 0.28 | 50 | [21 empty] | 1999-05-04 | 17:51 | 30.4 | 25.2 | 112.6 | 112.5 | 299 | 6.4 | 0.7 |  | 7.1 | 0.24367 | 0.90141 | 41.1127 | 14.6077 | 13.2893 | 2280.8971 | 317.1402 | 2238.8635 | 19.4274 | 93.1226 | 0.14271 | 6.59 | 7.02 | 8.38 | 213.907 | 545.1 | 2631.34 | 3224.7431 | -22.5514 | 58.119 | 3192.5201 | 93.2997 | 0.035 |  |  | 3.0424 |  | 89.4419 | 3.0102 | 98.8373 | [8 empty] | Temperature | oC | 24.9 | 24.9 | 24.9 | 0 | 24.9 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 22.6 | 22.6 | --- | --- | --- | --- | --- | TOCF, mg/L | 9.285 | 9.285 | 9.285 | 9.285 | TOCF, mg/L | 9.285 | 9.285 | 9.285 | 9.285 | Labor Overhead Factor (% of labor) | 6%
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.265 | 2 | 0.9 | 15 | 39.785 | 101.6375 | 299.4788 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) | 0.018 |  |  |  | Ammonia | mg NH3-N / L | 0.6 | 0.62 | 0.61 | 3.2787 | [21 empty] | 1999-05-05 | 12:04 | 48 | 23.8 | 111.3 | 111 | 299 | 6.7 | 6.5 |  | 13.2 | 0.24367 | 0.50758 | 21.6515 | 15.2924 | 14.5 | 907.2964 | 126.0408 | 889.79 | 7.725 | 103.425 | 0.1402 | 6.08 |  |  | 246.82 |  |  | 782.8009 |  | 51.675 | 776.7958 | 68.2259 | 0.031 | 0.31 | 0.529 | 0.64125 | -21.2186 | 90.6486 | 0.63441 | 95.1136 | [8 empty] | Alkalinity | mg/L as CaCO3 | 36.9 | 33.7 | 35.3 | 9.0652 | 740 | 400.9667 | 45.8153 | 75.6552 | 396.9431 | 91.107 | Alkalinity | mg/L as CaCO3 | 59.5 | 890 | 914.5 | -2.7528 | 58.9655 | 905.3638 | 93.4281 | Alkalinity | mg/L as CaCO3 | 44.5 | 458 | 249.602 | 45.5017 | 69.3103 | 247.2931 | 82.0052 | Alkalinity | mg/L as CaCO3 | 17.5 | 208 | 202.2826 | 2.7487 | 87.931 | 200.1465 | 91.2564 | TOCp, mg/L | 0.755 | 1.07 | 0.7 | 0.33 | TOCp, mg/L | 0.755 | 1.07 | 0.7 | 0.33 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 9.265 | 71.1175 | 299.4788 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  |  | Total organic carbon | mg/L | 9.67 | 8.9 | 9.285 | 8.2929 | [21 empty] | 1999-05-05 | 15:44 | 51.7 | 24.4 | 111 | 110.8 | 299 | 6.9 | 6.7 |  | 13.6 | 0.24367 | 0.50735 | 20.9853 | 15.7489 | 14.6703 | 907.0542 | 125.9329 | 889.0283 | 7.7211 | 103.1789 | 0.14218 | 6 |  |  | 226.352 |  |  | 803.6375 |  | 55.6824 | 796.9765 | 71.5987 | 0.023 |  |  | 0.64921 |  | 93.0618 | 0.64198 | 96.4174 | [8 empty] | Total dissolved solids | mg/L | 152 | 154 | 153 | 1.3072 | 1341.5 | 1345.5 | -0.29817 | 70.0441 | 1332.3785 | 88.5168 | Total dissolved solids | mg/L | 214 | 2630 | 3181.5 | -20.9696 | 58.1008 | 3149.7904 | 93.2059 | Total dissolved solids | mg/L | 201 | 1632 | 833.1429 | 48.9496 | 60.6461 | 826.0265 | 75.6666 | Total dissolved solids | mg/L | 88.5 | 750 | 700.4565 | 6.6058 | 82.6725 | 693.3822 | 87.2365 | UV254 F, cm-1 | 0.3315 | 0.3315 | 0.3315 | 0.3315 | UV254 F, cm-1 | 0.3315 | 0.3315 | 0.3315 | 0.3315 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 7.085 | 68.9375 | 299.4788 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) | 32.8 |  |  |  | UV254 | cm-1 | 0.325 | 0.338 | 0.3315 | 3.9216 | [21 empty] | 1999-05-05 | 17:39 | 53.6 | 24.2 | 105 | 104.8 | 299 | 6.7 | 6.5 |  | 13.2 | 0.24367 | 0.50758 | 21.6515 | 15.2924 | 14.3296 | 907.2964 | 126.0408 | 889.79 | 7.725 | 97.175 | 0.14746 | 6.01 | 6.69 | 7.01 | 201.068 | 527.16 | 1632.621 | 829.9607 | 49.1639 | 60.6328 | 822.9146 | 75.5664 | 0.024 |  |  | 0.64846 |  | 92.7602 | 0.64147 | 96.2586 | [8 empty] | Total hardness | mg/L as CaCO3 | 69.1 | 68.1 | 68.6 | 1.4577 | 797 | 874.9333 | -9.7783 | 77.9066 | 866.061 | 92.0791 | Total hardness | mg/L as CaCO3 | 123 | 1600 | 1998 | -24.875 | 60.3865 | 1977.9645 | 93.7815 | Total hardness | mg/L as CaCO3 | 84 | 974 | 546.2449 | 43.9174 | 72.9469 | 541.0412 | 84.4744 | Total hardness | mg/L as CaCO3 | 23.2 | 437 | 439.5768 | -0.58966 | 92.5282 | 434.7634 | 94.6638 | UV254 p, cm-1 | 0.02 | 0.033 | 0.022 | BMRL | UV254 p, cm-1 | 0.02 | 0.033 | 0.022 | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 846 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  |  | SUVA | L/(mg*m) | 3.3609 | 3.7978 | 3.5793 | 12.2046 | [21 empty] | 1999-05-06 | 10:56 | 70.9 | 23.7 | 106.5 | 106.2 | 299 | 6.7 | 15.6 |  | 22.3 | 0.24367 | 0.30045 | 12.4081 | 15.2924 | 14.5429 | 689.002 | 95.7155 | 675.7076 | 5.8664 | 100.4836 | 0.14473 | 5.89 |  |  | 62.04 |  |  | 703.4652 |  | 87.8532 | 696.2787 | 91.0898 | 0.044 |  |  | 0.45498 |  | 86.727 | 0.45037 | 90.2303 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 64.4 | 63.6 | 64 | 1.25 | 746 | 824 | -10.4558 | 78.0822 | 815.6375 | 92.1534 | Calcium hardness | mg/L as CaCO3 | 116 | 1500 | 1876 | -25.0667 | 60.274 | 1857.1933 | 93.754 | Calcium hardness | mg/L as CaCO3 | 78.9 | 913 | 513.798 | 43.7242 | 72.9795 | 508.9021 | 84.496 | Calcium hardness | mg/L as CaCO3 | 23.2 | 409 | 412.7652 | -0.92059 | 92.0548 | 408.2618 | 94.3174 | BromideF, ug/L | 178.5 | 178.5 | 178.5 | 178.5 | BromideF, ug/L | 178.5 | 178.5 | 178.5 | 178.5 | Current Process Water Rate ($/1000 gal) | 0.65
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 180 | 177 | 178.5 | 1.6807 | [21 empty] | 1999-05-06 | 14:00 | 74 | 23.6 | 104.7 | 104.5 | 299 | 6.8 | 15.1 |  | 21.9 | 0.24367 | 0.3105 | 12.653 | 15.5206 | 14.8037 | 697.1557 | 96.8197 | 683.5026 | 5.9351 | 98.6649 | 0.15004 | 5.96 |  |  | 63.732 |  |  | 712.0561 |  | 87.5219 | 704.6839 | 90.9559 | 0.032 |  |  | 0.46637 |  | 90.3469 | 0.46143 | 93.0651 | [8 empty] | Turbidity | ntu | 0 | 0 | 0 | #DIV/0! | 0.26 | 0.93333 | -258.9744 | 100 | 0.92306 | 100 | Turbidity | ntu | 0.03 | 0.92 | 2.53 | -175 | 89.2857 | 2.5033 | 98.8016 | Turbidity | ntu | 0 | 0.45 | 0.57143 | -26.9841 | 100 | 0.565 | 100 | Turbidity | ntu | 0 | 0.22 | 0.4058 | -84.4532 | 100 | 0.40111 | 100 | Bromidep, ug/L | 63.5 | 120 | 78 | 24 | Bromidep, ug/L | 63.5 | 120 | 78 | 24 | Modifications to Existing Plant (% of construction costs) | 10%
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 15 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 12.2 | 12.2 | 12.2 | 0 | [21 empty] | 1999-05-06 | 16:15 | 76.2 | 22.5 | 112.2 | 112 | 299 | 7 | 15.3 |  | 22.3 | 0.24367 | 0.3139 | 12.4081 | 15.9771 | 15.7427 | 699.9768 | 97.1542 | 685.8639 | 5.9577 | 106.1423 | 0.14832 | [11 empty] | 0.03 | 0.314 | 0.447 | 0.46944 | -5.0204 | 90.9502 | 0.4643 | 93.5386 | [8 empty] | Ammonia | mg NH3-N / L | 0.41 | 0.33 | 0.37 | 21.6216 | 1.01 | 1.17 | -15.8416 | 39.3443 | 1.1612 | 68.1363 | Ammonia | mg NH3-N / L | 0.55 | 0.9 | 1.15 | -27.7778 | 9.8361 | 1.1436 | 51.9058 | Ammonia | mg NH3-N / L | 0.48 | 1.25 | 0.74531 | 40.3755 | 21.3115 | 0.74232 | 35.3378 | Ammonia | mg NH3-N / L | 0.2 | 0.76 | 0.7942 | -4.5004 | 67.2131 | 0.78733 | 74.5978 | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145 | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 63.2 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.83 | 0.87 | 0.85 | 4.7059 | [21 empty] | 1999-05-07 | 18:23 | 94.9 | 22.6 | 92.4 | 92 | 299 | 6.8 | 14.8 | x | 21.6 | 0.24367 | 0.31481 | 12.8426 | 15.5206 | 15.2478 | 700.7075 | 97.313 | 686.9849 | 5.9653 | 86.2347 | 0.17682 | 6.61 |  |  | 141 |  |  | 680.6351 |  | 72.3935 | 674.4988 | 79.0956 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | 0.78 | 0.73 | 0.755 | 6.6225 | 27.2 | 29.1883 | -7.31 | 91.8686 | 28.8755 | 97.3853 | Total organic carbon | mg/L | 1.07 | 76.4 | 83.22 | -8.9267 | 88.476 | 82.3422 | 98.7005 | Total organic carbon | mg/L | 0.7 | 34.5 | 18.2204 | 47.1872 | 92.461 | 18.0232 | 96.1161 | Total organic carbon | mg/L | 0.33 | 13.6 | 13.3083 | 2.1451 | 96.4459 | 13.1582 | 97.4921 | Alkp, mg/L CaCO3 | 35.3 | 59.5 | 44.5 | 17.5 | Alkp, mg/L CaCO3 | 35.3 | 59.5 | 44.5 | 17.5
Plant Name | City of Margate, DEES | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0021667 | [9 empty] | pH | 7.2 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.37 | 11.33 | 11.35 | 0.35242 | [21 empty] | 1999-05-08 | 9:03 | 109.6 | 22 | 98.2 | 98 | 299 | 6.5 | 15.5 |  | 22 | 0.24367 | 0.29545 | 12.5909 | 14.8359 | 14.8359 | 685.006 | 95.2165 | 672.1845 | 5.8338 | 92.2662 | 0.16079 | 6.06 | 7.02 | 6.92 | 88.548 | 518.88 | 750.496 | 687.8025 | 8.3536 | 82.6631 | 681.2888 | 87.0029 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | 0.02 | 0.02 | 0.02 | 0 | 0.988 | 1.0583 | -7.1188 | 93.9668 | 1.0469 | 98.0896 | UV254 | cm-1 | 0.033 | 2.492 | 3.018 | -21.1075 | 90.0452 | 2.9861 | 98.8949 | UV254 | cm-1 | 0.022 | 1.116 | 0.65363 | 41.4308 | 93.3635 | 0.64652 | 96.5972 | UV254 | cm-1 | BMRL | 0.486 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 310.5 | 310.5 | 310.5 | 310.5 | T-HdF, mg/L CaCO3 | 310.5 | 310.5 | 310.5 | 310.5
Treatment Plant Category | Class A, Level 2 | [11 empty] | Chloride (mg/L) | 59.9 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | [70 empty] | SUVA | L/(mg*m) | 2.5641 | 2.7397 | 2.6519 | 6.6225 | 3.6324 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.0841 | 3.2618 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.1429 | 3.2348 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.5735 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 68.6 | 123 | 84 | 23.2 | T-Hdp, mg/L CaCO3 | 68.6 | 123 | 84 | 23.2
Process Train Name | Lime Softening | Additional Information | [10 empty] | Mg (mg/L) | 44 |  |  |  | SDS-Chlorination pH | --- | 7.49 | 7.5 | 7.495 | 0.13342 | [70 empty] | Bromide | mg/L | 63 | 64 | 63.5 | 1.5748 | --- | 446.8333 | --- | 64.4258 | 442.6154 | 85.6535 | Bromide | mg/L | 120 | --- | 705 | --- | 32.7731 | 698.7489 | 82.8264 | Bromide | mg/L | 78 | --- | 283.102 | --- | 56.3025 | 280.7931 | 72.2215 | Bromide | mg/L | 24 | --- | 247.913 | --- | 86.5546 | 245.3246 | 90.217 | Ca-HdF, mg/L CaCO3 | 292 | 292 | 292 | 292 | Ca-HdF, mg/L CaCO3 | 292 | 292 | 292 | 292
ICR Treatment Plant Identification Number | 1077 | Design cross-flow velocity (fps) | .7 ft/sec @ 15 gfd, 10% recovery | [9 empty] | Potassium (mg/L) | 25.1 |  |  |  | SDS-Incubation time | hours | 24.33 | 24.08 | 24.205 | 1.0328 | [70 empty] | SDS-Cl2 dose | mg/L | 4.2 | 4.2 | 4.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.12 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.6 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 64 | 116 | 78.9 | 23.2 | Ca-Hdp, mg/L CaCO3 | 64 | 116 | 78.9 | 23.2
PWSID Number of Plant (if assigned) | 4060845 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | [9 empty] | Strontium (mg/L) | 1.14 |  |  |  | SDS-TOX | mg Cl- /L | 779 | 802 | 790.5 | 2.9096 | [70 empty] | SDS-Free Cl2 residual | mg/L | 0.96 | 0.98 | 0.97 | 2.0619 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.37 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.17 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.99 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 20 | Maximum element recovery (%) | 17 | [14 empty] | SDS-CHCl3 | mg/L | 125 | 129 | 127 | 3.1496 | [70 empty] | SDS-Cl2 demand | mg/L | 3.24 | 3.22 | 3.23 | 0.6192 | --- | 30.2967 | --- | 71.5419 | 29.9988 | 89.2329 | SDS-Cl2 demand | mg/L | 4.75 | --- | 70.75 | --- | 58.1498 | 70.0447 | 93.2186 | SDS-Cl2 demand | mg/L | 3.83 | --- | 19.1769 | --- | 66.2555 | 19.0042 | 79.8465 | SDS-Cl2 demand | mg/L | 1.61 | --- | 15.7259 | --- | 85.815 | 15.5628 | 89.6548 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.2 | Variability of design flux (%) | 15 | [14 empty] | SDS-BDCM | mg/L | 46.8 | 46.6 | 46.7 | 0.42827 | [70 empty] | SDS-Chlorination temp. | oC | 22 | 22 | 22 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 68.3318 | 73.1836 | 69.9054 | 62.9903 | Qp/QT (THM4), % | 90.5335 | 96.9617 | 92.6183 | 83.4565
State Approved Plant Capacity (MGD) | 18 | Rejection of reference solute and conditions of test | 0.85 | [14 empty] | SDS-DBCM | mg/L | 9.1 | 9.1 | 9.1 | 0 | [70 empty] | SDS-Chlorination pH | --- | 7.51 | 7.54 | 7.525 | 0.39867 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.48 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.56 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.53 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 500 mg/L NaCl @ 80 psi | [9 empty] | Sodium (mg/L) | 32.8 |  |  |  | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [70 empty] | SDS-Incubation time | hours | 24.02 | 24.05 | 24.035 | 0.12482 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.05 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.22 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.73 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 42.9535 | 39.1232 | 41.4443 | 45.2073 | SDS-HAA5b, ug/L | 17.2217 | 12.147 | 15.2222 | 20.2079
|  | Variability of rejection of reference solute (%) | 5 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-THM4 | mg/L | 180.9 | 184.7 | 182.8 | 2.0788 | [70 empty] | SDS-TOX | mg Cl- /L | 57.4 | 57 | 57.2 | 0.6993 | --- | 2501.5333 | --- | 92.7641 | 2474.6375 | 97.6886 | SDS-TOX | mg Cl- /L | 83.3 | --- | 7155.3 | --- | 89.4624 | 7079.7313 | 98.8234 | SDS-TOX | mg Cl- /L | 67.5 | --- | 1543.0102 | --- | 91.4611 | 1526.3996 | 95.5778 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 289.423 | 272.9454 | 285.0842 | #VALUE! | SDS-TOXb, ug Cl- /L | 126.6182 | 104.7869 | 120.8697 | #VALUE!
|  | Standard testing recovery (%) | 10 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-MCAA* | mg/L | 6.4 | 6.6 | 6.5 | 3.0769 | [70 empty] | SDS-CHCl3 | mg/L | 5.2 | 5.3 | 5.25 | 1.9048 | --- | 411.0833 | --- | 95.8661 | 406.6178 | 98.7089 | SDS-CHCl3 | mg/L | 6.8 | --- | 1208.8 | --- | 94.6457 | 1195.9559 | 99.4314 | SDS-CHCl3 | mg/L | 5.6 | --- | 253.3551 | --- | 95.5906 | 250.566 | 97.7651 | SDS-CHCl3 | mg/L | 2 | --- | 183.1594 | --- | 98.4252 | 181.0652 | 98.8954 | SDS-CDb, mg/L | 5.8015 | 6.5199 | 6.0931 | 5.2147 | SDS-CDb, mg/L | 3.9987 | 4.9505 | 4.3851 | 3.2213
|  | Standard testing pH | 7.5 | [14 empty] | SDS-DCAA* | mg/L | 45 | 40.2 | 42.6 | 11.2676 | [70 empty] | SDS-BDCM | mg/L | 7.3 | 7.2 | 7.25 | 1.3793 | --- | 138.75 | --- | 84.4754 | 137.3031 | 94.7197 | SDS-BDCM | mg/L | 10.6 | --- | 371.6 | --- | 77.3019 | 367.7425 | 97.1175 | SDS-BDCM | mg/L | 8.5 | --- | 86.4592 | --- | 81.7987 | 85.5816 | 90.068 | SDS-BDCM | mg/L | 2.6 | --- | 66.513 | --- | 94.4325 | 65.7742 | 96.0471 | TOCb, mg/L | 3.4563 | 3.273 | 3.2836 | 3.6442 | TOCb, mg/L | 1.5625 | 1.3196 | 1.3337 | 1.8115
|  | Acceptable range of operating pressures | 0-350 | [14 empty] | SDS-TCAA* | mg/L | 77.6 | 63.3 | 70.45 | 20.2981 | [70 empty] | SDS-DBCM | mg/L | 7.1 | 7 | 7.05 | 1.4184 | --- | 13.8833 | --- | 22.5275 | 13.8081 | 48.9432 | SDS-DBCM | mg/L | 11.9 | --- | -16.1 | --- | -30.7692 | -15.8008 | 175.3126 | SDS-DBCM | mg/L | 8.8 | --- | 9.4122 | --- | 3.2967 | 9.4054 | 6.4363 | SDS-DBCM | mg/L | 2.3 | --- | 12.1551 | --- | 74.7253 | 12.0411 | 80.8988 | UV254 b, cm-1 | 0.11865 | 0.11305 | 0.11514 | #VALUE! | UV254 b, cm-1 | 0.049488 | 0.042069 | 0.044846 | #VALUE!
|  | Acceptable range of operating pH values | 4-11 | [14 empty] | SDS-MBAA* | mg/L | 1.1 | 1 | 1.05 | 9.5238 | [70 empty] | SDS-CHBr3 | mg/L | 1.1 | 1.1 | 1.1 | 0 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 99.9184 | 135.6876 | 108.2451 | 81.1799 | Bromideb, ug/L | 74.3865 | 121.7774 | 85.4186 | 49.5597
|  | Typical pressure drop across a single element (psi) | 5 | [14 empty] | SDS-DBAA* | mg/L | 1.5 | 1.6 | 1.55 | 6.4516 | [70 empty] | SDS-THM4 | mg/L | 20.7 | 20.6 | 20.65 | 0.48426 | --- | 561.15 | --- | 88.7035 | 555.2027 | 96.2806 | SDS-THM4 | mg/L | 31.4 | --- | 1545.4 | --- | 82.8228 | 1529.222 | 97.9467 | SDS-THM4 | mg/L | 24.3 | --- | 347.7694 | --- | 86.7068 | 344.1279 | 92.9387 | SDS-THM4 | mg/L | 6.9 | --- | 261.8275 | --- | 96.2254 | 258.8805 | 97.3347 | Alkb, mg/L CaCO3 | 70.04 | 82.428 | 74.7451 | 64.6873 | Alkb, mg/L CaCO3 | 45.6848 | 62.0978 | 51.9186 | 38.593
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 11.4 | 11.3 | 11.35 | 0.88106 | [70 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 145.2054 | 173.2807 | 152.1644 | 129.5288 | T-Hdb, mg/L CaCO3 | 91.4996 | 128.6968 | 100.7196 | 70.7294
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-DCAA* | mg/L | 2.6 | 2.5 | 2.55 | 3.9216 | --- | 136.05 | --- | 94.0141 | 134.5811 | 98.1052 | SDS-DCAA* | mg/L | 3 | --- | 399 | --- | 92.9577 | 394.7685 | 99.2401 | SDS-DCAA* | mg/L | 2.6 | --- | 84.2327 | --- | 93.8967 | 83.3137 | 96.8793 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 136.2035 | 163.1968 | 143.0317 | 122.682 | Ca-Hdb, mg/L CaCO3 | 85.5837 | 121.3474 | 94.6304 | 67.6689
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 mg/L extended | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-TCAA* | mg/L | 2.2 | 2.3 | 2.25 | 4.4444 | --- | 229.5833 | --- | 96.8062 | 227.0819 | 99.0092 | SDS-TCAA* | mg/L | 3.2 | --- | 675.7 | --- | 95.4578 | 668.5139 | 99.5213 | SDS-TCAA* | mg/L | 2.3 | --- | 141.3816 | --- | 96.7353 | 139.8159 | 98.355 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [70 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 131.6 | 112.7 | 122.15 | 15.4728 | [70 empty] | SDS-DBAA* | mg/L | 1.4 | 1.5 | 1.45 | 6.8966 | --- | 1.7833 | --- | 6.4516 | 1.7797 | 18.524 | SDS-DBAA* | mg/L | 2.5 | --- | -7 | --- | -61.2903 | -6.8985 | 136.2398 | SDS-DBAA* | mg/L | 1.8 | --- | 1.2898 | --- | -16.129 | 1.2955 | -38.9383 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 143 | 124 | 133.5 | 14.2322 | [70 empty] | SDS-BCAA* | mg/L | 2.4 | 2.4 | 2.4 | 0 | --- | 32.2333 | --- | 78.8546 | 31.9051 | 92.4777 | SDS-BCAA* | mg/L | 3.5 | --- | 82 | --- | 69.163 | 81.1612 | 95.6876 | SDS-BCAA* | mg/L | 2.7 | --- | 20.3531 | --- | 76.2115 | 20.1543 | 86.6034 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 58.8007 | 60.0705 | 59.0299 | 55.7921 | Qp/QT (HAA5), % | 82.0966 | 83.8695 | 82.4166 | 77.896
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [75 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 87.4547 | 91.8532 | 89.2376 | 84.6618 | SDS-THM4b, ug/L | 49.6803 | 55.8215 | 52.1696 | 45.7809
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [75 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [75 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 359.3145 | 365.6813 | 363.7139 | #VALUE! | SDS-TOXb, ug Cl- /L | 188.4854 | 197.3746 | 194.6278 | #VALUE!
[94 empty] | SDS-HAA5 | mg/L | 6.2 | 6.3 | 6.25 | 1.6 | --- | 392.5833 | --- | 94.8833 | 388.3324 | 98.3906 | SDS-HAA5 | mg/L | 8.7 | --- | 1143.2 | --- | 92.8776 | 1131.0772 | 99.2308 | SDS-HAA5 | mg/L | 6.7 | --- | 242.3122 | --- | 94.5149 | 239.6598 | 97.2044 | SDS-HAA5 | mg/L | 0 | --- | 177.029 | --- | 100 | 174.9825 | 100 | SDS-CDb, mg/L | 6.5754 | 7.3853 | 6.911 | 5.9159 | SDS-CDb, mg/L | 4.6838 | 5.8146 | 5.1523 | 3.7629
[94 empty] | SDS-HAA6 | mg/L | 8.6 | 8.7 | 8.65 | 1.1561 | --- | 424.8167 | --- | 93.5206 | 420.2374 | 97.9416 | SDS-HAA6 | mg/L | 12.2 | --- | 1225.2 | --- | 90.8614 | 1212.2383 | 98.9936 | SDS-HAA6 | mg/L | 9.4 | --- | 262.6653 | --- | 92.9588 | 259.8142 | 96.382 | SDS-HAA6 | mg/L | 0 | --- | 193.4783 | --- | 100 | 191.2416 | 100 | TOCb, mg/L | 4.2693 | 4.3502 | 4.2173 | 4.2888 | TOCb, mg/L | 2.2822 | 2.3951 | 2.2095 | 2.3094
[94 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.14834 | 0.15219 | 0.1488 | #VALUE! | UV254 b, cm-1 | 0.075769 | 0.081149 | 0.076421 | #VALUE!
[94 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 110.8792 | 143.3587 | 119.175 | 92.3013 | Bromideb, ug/L | 84.0889 | 129.4363 | 95.6713 | 58.1506
[133 empty] | Alkb, mg/L CaCO3 | 80.4956 | 93.6397 | 85.675 | 73.8651 | Alkb, mg/L CaCO3 | 54.94 | 73.2915 | 62.1713 | 45.6826
[133 empty] | T-Hdb, mg/L CaCO3 | 168.2611 | 197.8678 | 176.7973 | 150.2094 | T-Hdb, mg/L CaCO3 | 111.9082 | 153.2446 | 123.8263 | 86.7047
[133 empty] | Ca-Hdb, mg/L CaCO3 | 157.9344 | 186.2759 | 166.2073 | 142.0309 | Ca-Hdb, mg/L CaCO3 | 104.8197 | 144.3896 | 116.3702 | 82.6155
[133 empty] | Notes: |  |  |  |  | Notes:
[133 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[133 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[133 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[133 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[133 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[133 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[133 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[133 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[133 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[133 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[133 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on Z10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on AA10: Gregg Thompson: Feed temperature not neasured. Laboratory temperature normally varied between 21 to 22 deg C.
Note on CD7: C. Rice: There is no record of an operational anomaly during the middle of 50% and 30% runs so the TDS data should be considered valid. TSC_ADM: Originally consultant reported measured conductivity data in the columns for TDS operational data; however, in this version of the DCS a factor was used to convert the conductivity data to TDS.
Note on CD8: C. Rice: Consultant verified the data that resulted in high MB closure errors.
Note on CL8: C. Rice: Consultant verified the data that resulted in high MB closure errors.
Note on CY29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on DL29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on DV29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Note on EF29: C. Rice: Consultant verified that all SDS samples were contacted simultaneously using an incubator. The reported temperature is a measured value.
Print All Fields