## NF200. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Boca Raton | Membrane manufacturer | FilmTec Corporation | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 226 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.63 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500130 | Membrane trade name | FILMTEC | Temperature normalized MTCW (gfd/psi) | 0.274 | Calcium Hardness (mg/L as CaCO3) | 216 | Pressurized Dual Media Filtration | Silica/Garnet | Pilot-Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 41.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.9 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 26 | [6 empty] | System feed flow rate during sample collection (gpm) | 42.1 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.9 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 26 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.8 |  |  |  |  | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Membrane element model number | NF200-4040 |  |  | LSI | 0.06 | Scale Inhibitor Addition | Calgon EL-5600 4.0 mg/l | Pilot-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 41.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 42.1 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 42.1 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 |  |  |  |  | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 nominal | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.26 | pH Adjustment | sulfuric acid to pH 6.0 to 6.4 | Pilot-Scale | 1998-10-06 | 9:00 | 23801 | 25.6 | 85 | 55 | 20 | 0 | 33.6 | 6.2 |  | 39.8 | 39.8 | 0.84422 | 0 | 14.4 | 14.1469 | 6.1952 | 43.8048 | 0.32295 | 6.6 | 6.05 | 204 | 360 | 371 | 1197 | 1276.0323 | -6.6025 | 45.0135 | 823.5161 | 75.2282 | 85 | 68 | 18 | 24.6 | 16.2 | 40.8 | 40.8 | 0.493 | 0.60294 | 15.8143 | 15.5363 | 4.0815 | 54.4185 | 0.2855 | 6.1 |  | 177 | 409 | 730 | 761.2963 | -4.2872 | 52.2911 | 585.1481 | 69.7513 | 68 | 55 | 21 | 8.5 | 6.2 | 14.7 | 14.7 | 0.36153 | 0.57823 | 10.9286 | 10.7365 | 7.2981 | 33.2019 | 0.32337 |  | 6.46 | 297 | 730 | 1197 | 1323.629 | -10.5789 | 19.9461 | 1026.8145 | 71.0756 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.28 | Cartridge Filtration | 5 um exclusion size | Pilot-Scale | 1998-10-07 | 10:00 | 23826 | 25.4 | 89 | 57 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.739 | 5.8756 | 46.1244 | 0.31955 | 6.71 | 6.07 | 201 | 347 | 359 | 1194 | 1218.125 | -2.0205 | 44.0111 | 788.5625 | 74.5106 | 89 | 71 | 19 | 25.6 | 16.1 | 41.7 | 41.7 | 0.49992 | 0.61391 | 16.4571 | 16.2637 | 4.0747 | 56.9253 | 0.2857 | 6.08 |  | 173 | 400 | 726 | 760.9441 | -4.8132 | 51.8106 | 580.472 | 70.1967 | 71 | 57 | 22 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.1813 | 7.3575 | 34.6425 | 0.32276 |  | 6.43 | 290 | 726 | 1194 | 1325.5 | -11.0134 | 19.2201 | 1025.75 | 71.728 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 16.5 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 1998-10-08 | 11:30 | 23852 | 25.4 | 88 | 56 | 20 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 6.6613 | 45.3387 | 0.32509 | 6.5 | 6.38 | 205 | 373 | 380 | 1218 | 1362.2581 | -11.8438 | 46.0526 | 871.129 | 76.4673 | 88 | 70 | 19 | 25.6 | 15.7 | 41.3 | 41.3 | 0.493 | 0.61985 | 16.4571 | 16.2637 | 4.0844 | 55.9156 | 0.29086 | 6.43 |  | 178 | 403 | 732 | 769.879 | -5.1747 | 53.1579 | 586.4395 | 69.6473 | 70 | 56 | 22 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.0542 | 7.4871 | 33.5129 | 0.32985 |  | 6.8 | 292 | 732 | 1218 | 1349.4194 | -10.7898 | 23.1579 | 1040.7097 | 71.9422 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | hydrophylic | Number of elements per pressure vessel, Ne | 7 | Total aluminum (mg/L) | <0.10 |  |  |  | 1998-10-09 | 9:25 | 23874 | 25.5 | 89 | 57 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.6955 | 5.8756 | 46.1244 | 0.31861 | 6.58 | 6.19 | 210 | 356 | 368 | 1183 | 1227.125 | -3.7299 | 42.9348 | 797.5625 | 73.6698 | 89 | 70 | 19 | 25.6 | 16.2 | 41.8 | 41.8 | 0.50165 | 0.61244 | 16.4571 | 16.2157 | 4.0099 | 56.4901 | 0.28705 | 6.16 |  | 183 | 407 | 726 | 760.9753 | -4.8175 | 50.2717 | 583.9877 | 68.6637 | 70 | 57 | 22 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.1483 | 7.155 | 34.345 | 0.3246 |  | 6.36 | 302 | 726 | 1183 | 1309 | -10.6509 | 17.9348 | 1017.5 | 70.3194 | Sampling date | MM/DD/YY | 1998-10-21 | 1998-10-21 | 1998-10-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-21 | 1998-10-21 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-04 | 1998-11-04 | 1998-11-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-04 | 1998-11-04 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-18 | 1998-11-18 | 1998-11-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-18 | 1998-11-18 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-03 | 1998-12-03 | 1998-12-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-03 | 1998-12-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 13
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 4 | Fluoride (mg/L) | 0.25 |  |  |  | 1998-10-10 | 9:10 | 23898 | 25.4 | 89 | 57 | 21 | 0 | 34.9 | 6.4 |  | 41.3 | 41.3 | 0.84504 | 0 | 14.9571 | 14.7813 | 5.7016 | 46.2984 | 0.31926 | 6.83 | 6.23 | 212 | 361 | 365 | 1194 | 1199.3281 | -0.44624 | 41.9178 | 782.1641 | 72.8957 | 89 | 70 | 19 | 25.7 | 15.9 | 41.6 | 41.6 | 0.49732 | 0.61779 | 16.5214 | 16.3272 | 4.1226 | 56.3774 | 0.28961 | 6.16 |  | 183 | 411 | 732 | 779.5283 | -6.4929 | 49.863 | 595.2642 | 69.2573 | 70 | 57 | 23 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.1813 | 7.2394 | 33.2606 | 0.33617 |  | 6.48 | 303 | 732 | 1194 | 1321.875 | -10.7098 | 16.9863 | 1026.9375 | 70.4948 | Sampling time | hh:mm | 7:40 | 7:30 | 7:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:50 | 7:30 | --- | --- | --- | --- | Sampling time | hh:mm | 6:45 | 6:55 | 7:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:05 | 6:50 | --- | --- | --- | --- | Sampling time | hh:mm | 7:10 | 7:15 | 7:25 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:25 | 7:20 | --- | --- | --- | --- | Sampling time | hh:mm | 7:45 | 7:50 | 7:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:05 | 7:55 | --- | --- | --- | --- | Sampling time | hh:mm | 7:20 | 7:30 | 7:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:20 | 7:30 | 7:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:25 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5999
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 2 | Phosphate (mg/L) | 0.56 |  |  |  | 1998-10-11 | 8:00 | 23920 | 25.4 | 87 | 56 | 20 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 6.2045 | 45.2955 | 0.3254 | 6.67 | 6.08 | 210 | 357 | 373 | 1200 | 1287.9032 | -7.3253 | 43.6997 | 830.4516 | 74.7126 | 87 | 69 | 19 | 25.3 | 15.7 | 41 | 41 | 0.4904 | 0.61707 | 16.2643 | 16.0731 | 4.081 | 54.919 | 0.29267 | 6.19 |  | 182 | 408 | 730 | 772.1911 | -5.7796 | 51.2064 | 590.0955 | 69.1575 | 69 | 56 | 22 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.0542 | 7.2999 | 33.2001 | 0.33296 |  | 6.46 | 301 | 730 | 1200 | 1331.9839 | -10.9987 | 19.3029 | 1030.9919 | 70.8048 | Operation time | hh.hh | 24160 | 24160 | 24160 | --- | --- | --- | --- | --- | Operation time | hh.hh | 24160 | 24160 | --- | --- | --- | --- | Operation time | hh.hh | 24496 | 24496 | 24496 | --- | --- | --- | --- | --- | Operation time | hh.hh | 24496 | 24496 | --- | --- | --- | --- | Operation time | hh.hh | 24832 | 24832 | 24832 | --- | --- | --- | --- | --- | Operation time | hh.hh | 24832 | 24832 | --- | --- | --- | --- | Operation time | hh.hh | 25192 | 25192 | 25192 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25192 | 25192 | --- | --- | --- | --- | Operation time | hh.hh | 25503 | 25503 | 25503 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25503 | 25503 | --- | --- | --- | --- | Operation time | hh.hh | 25503 | 25503 | 25503 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25503 | 25503 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.91667 | Sulfate (mg/L) | 14.9 |  |  |  | 1998-10-12 | 8:05 | 23944 | 25.4 | 88 | 56 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.1782 | 44.8218 | 0.32695 | 6.7 | 6.06 | 209 | 356 | 372 | 1215 | 1281.6452 | -5.4852 | 43.8172 | 826.8226 | 74.7225 | 88 | 70 | 19 | 25.4 | 16.5 | 41.9 | 41.9 | 0.50511 | 0.60621 | 16.3286 | 16.1366 | 4.0349 | 55.9651 | 0.28833 | 6.19 |  | 181 | 409 | 732 | 759.9818 | -3.8227 | 51.3441 | 584.4909 | 69.0329 | 70 | 57 | 22 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.0542 | 7.351 | 34.149 | 0.32371 |  | 6.44 | 300 | 732 | 1215 | 1338.1935 | -10.1394 | 19.3548 | 1035.0968 | 71.0172 | pH | --- | 6.53 | 6.58 | 6.84 | --- | --- | --- | --- | --- | pH | --- | 6.45 | 6.51 | --- | --- | --- | --- | pH | --- | 5.84 | 6.04 | 6.38 | --- | --- | --- | --- | --- | pH | --- | NA | 6.04 | --- | --- | --- | --- | pH | --- | 6.33 | 6.5 | 6.78 | --- | --- | --- | --- | --- | pH | --- | 6.27 | 6.54 | --- | --- | --- | --- | pH | --- | 6.37 | 6.4 | 6.55 | --- | --- | --- | --- | --- | pH | --- | 6.28 | 6.28 | --- | --- | --- | --- | pH | --- | 6.38 | 6.37 | 6.62 | --- | --- | --- | --- | --- | pH | --- | 6.34 | 6.33 | --- | --- | --- | --- | pH | --- | 6.32 | 6.32 | 6.63 | --- | --- | --- | --- | --- | pH | --- | 6.33 | 6.33 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 17
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 6.4167 | Calcium (mg/L) | 95 |  |  |  | 1998-10-13 | 8:30 | 23969 | 25.4 | 89 | 55 | 20 | 0 | 34.6 | 6.8 |  | 41.4 | 41.4 | 0.83575 | 0 | 14.8286 | 14.6543 | 5.5643 | 46.4357 | 0.31558 | 6.49 | 6.19 | 205 | 350 | 362 | 1163 | 1160.8529 | 0.18461 | 43.3702 | 761.4265 | 73.0768 | 89 | 70 | 19 | 25.5 | 19.5 | 45 | 45 | 0.55787 | 0.56667 | 16.3929 | 16.2002 | 3.8038 | 56.6962 | 0.28574 | 6.16 |  | 179 | 409 | 724 | 709.7692 | 1.9656 | 50.5525 | 559.3846 | 68.0006 | 70 | 55 | 22 | 8.6 | 6.8 | 15.4 | 15.4 | 0.38402 | 0.55844 | 11.0571 | 10.9272 | 7.0354 | 33.4646 | 0.32653 |  | 6.46 | 293 | 724 | 1163 | 1269.0882 | -9.1219 | 19.0608 | 996.5441 | 70.5984 | Temperature | oC | 25.8 | 25.8 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.8 | 25.8 | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | Temperature | oC | 25.8 | 25.6 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.6 | 25.6 | --- | --- | --- | --- | Temperature | oC | 25 | 25 | 24.8 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | Temperature | oC | 25 | 25 | 24.8 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 25.6667 | Barium (mg/L) | 0.021 |  |  |  | 1998-10-14 | 8:30 | 23993 | 25.4 | 88 | 56 | 20 | 0 | 34.9 | 6.2 |  | 41.1 | 41.1 | 0.84915 | 0 | 14.9571 | 14.7813 | 6.0651 | 45.9349 | 0.32179 | 6.73 | 6.13 | 209 | 334 | 368 | 1080 | 1263.0161 | -16.9459 | 43.2065 | 815.5081 | 74.3718 | 88 | 70 | 19 | 25.4 | 15.8 | 41.2 | 41.2 | 0.493 | 0.6165 | 16.3286 | 16.1366 | 4.1127 | 55.8873 | 0.28874 | 6.2 |  | 182 | 410 | 731 | 776.5316 | -6.2287 | 50.5435 | 593.2658 | 69.3224 | 70 | 56 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 7.3516 | 33.6484 | 0.3323 |  | 6.45 | 301 | 731 | 1080 | 1341.3226 | -24.1965 | 18.2065 | 1036.1613 | 70.9505 | Alkalinity | mg/L as CaCO3 | 86 | 134 | 360 | 406 | -12.7778 | 35.8209 | 270 | 68.1481 | Alkalinity | mg/L as CaCO3 | 70 | 140 | 252.875 | 47.7612 | 196.4375 | 64.3653 | Alkalinity | mg/L as CaCO3 | 78 | 120 | 318 | 340.5 | -7.0755 | 35 | 230.25 | 66.1238 | Alkalinity | mg/L as CaCO3 | 68 | 124 | 215.5723 | 43.3333 | 169.7862 | 59.9496 | Alkalinity | mg/L as CaCO3 | 76 | 116 | 280 | 326 | -16.4286 | 34.4828 | 221 | 65.6109 | Alkalinity | mg/L as CaCO3 | 62 | 110 | 186.7407 | 46.5517 | 148.3704 | 58.2127 | Alkalinity | mg/L as CaCO3 | 70 | 98 | 260 | 256.6667 | 1.2821 | 28.5714 | 177.3333 | 60.5263 | Alkalinity | mg/L as CaCO3 | 54 | 110 | 203.9355 | 44.898 | 156.9677 | 65.598 | Alkalinity | mg/L as CaCO3 | 80 | 140 | 300 | 480 | -60 | 42.8571 | 310 | 74.1935 | Alkalinity | mg/L as CaCO3 | 66 | 120 | 208.7389 | 52.8571 | 164.3694 | 59.8465 | Alkalinity | mg/L as CaCO3 | 80 | 130 | 315 | 413.3333 | -31.2169 | 38.4615 | 271.6667 | 70.5521 | Alkalinity | mg/L as CaCO3 | 64 | 120 | 212.0255 | 50.7692 | 166.0127 | 61.4487 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 27.8 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.8333 | Strontium (mg/L) | 0.53 |  |  |  | 1998-10-15 | 9:00 | 24017 | 25.3 | 88 | 56 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 6.3948 | 44.6052 | 0.33141 | 6.75 | 6.1 | 208 | 364 | 376 | 1217 | 1318.9677 | -8.3786 | 44.6809 | 847.4839 | 75.4568 | 88 | 70 | 19 | 25.4 | 15.6 | 41 | 41 | 0.48954 | 0.61951 | 16.3286 | 16.1844 | 4.1543 | 55.8457 | 0.28981 | 6.19 |  | 180 | 409 | 732 | 781.859 | -6.8113 | 52.1277 | 595.4295 | 69.7697 | 70 | 56 | 22 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.087 | 7.351 | 33.649 | 0.32949 |  | 6.46 | 300 | 732 | 1217 | 1338.1935 | -9.9584 | 20.2128 | 1035.0968 | 71.0172 | Total dissolved solids | mg/L | 163 | 362 | 1060 | 1489.6667 | -40.5346 | 54.9724 | 925.8333 | 82.3942 | Total dissolved solids | mg/L | 148 | 362 | 707.075 | 59.116 | 534.5375 | 72.3125 | Total dissolved solids | mg/L | 161 | 371 | 1120 | 1473.5 | -31.5625 | 56.6038 | 922.25 | 82.5427 | Total dissolved solids | mg/L | 146 | 372 | 741.5597 | 60.6469 | 556.7799 | 73.7778 | Total dissolved solids | mg/L | 158 | 366 | 1090 | 1458 | -33.7615 | 56.8306 | 912 | 82.6754 | Total dissolved solids | mg/L | 144 | 367 | 723.5247 | 60.6557 | 545.2623 | 73.5907 | Total dissolved solids | mg/L | 152 | 365 | 1120 | 1572 | -40.3571 | 58.3562 | 968.5 | 84.3056 | Total dissolved solids | mg/L | 137 | 365 | 747.4516 | 62.4658 | 556.2258 | 75.3697 | Total dissolved solids | mg/L | 153 | 370 | 1130 | 1599.6667 | -41.5634 | 58.6486 | 984.8333 | 84.4644 | Total dissolved solids | mg/L | 140 | 370 | 747.9618 | 62.1622 | 558.9809 | 74.9544 | Total dissolved solids | mg/L | 154 | 374 | 1130 | 1620.6667 | -43.4218 | 58.8235 | 997.3333 | 84.5588 | Total dissolved solids | mg/L | 140 | 371 | 750.6051 | 62.5668 | 560.8025 | 75.0358 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 38.5 | Reactive silica (mg/L as SiO2) | 9.4 |  |  |  | 1998-10-16 | 9:13 | 24041 | 25.4 | 88 | 56 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 6.1565 | 45.8435 | 0.32058 | 6.7 | 6.1 | 205 | 357 | 369 | 1178 | 1272.3016 | -8.0052 | 44.4444 | 820.6508 | 75.0198 | 88 | 70 | 19 | 25.3 | 16 | 41.3 | 41.3 | 0.49559 | 0.61259 | 16.2643 | 16.0731 | 4.1005 | 55.8995 | 0.28754 | 6.16 |  | 178 | 407 | 726 | 769.1063 | -5.9375 | 51.7615 | 588.0531 | 69.7306 | 70 | 56 | 22 | 8.6 | 6.3 | 14.9 | 14.9 | 0.36672 | 0.57718 | 11.0571 | 10.9272 | 7.2686 | 33.7314 | 0.32395 |  | 6.45 | 294 | 726 | 1178 | 1315.7143 | -11.6905 | 20.3252 | 1020.8571 | 71.2007 | Total hardness | mg/L as CaCO3 | 110 | 244 | 980 | 1003.3333 | -2.381 | 54.918 | 623.6667 | 82.3624 | Total hardness | mg/L as CaCO3 | 84 | 260 | 543.8 | 65.5738 | 401.9 | 79.0993 | Total hardness | mg/L as CaCO3 | 94 | 250 | 1140 | 1069 | 6.2281 | 62.4 | 659.5 | 85.7468 | Total hardness | mg/L as CaCO3 | 78 | 246 | 520.717 | 68.8 | 383.3585 | 79.6535 | Total hardness | mg/L as CaCO3 | 94 | 236 | 1020 | 981.5 | 3.7745 | 60.1695 | 608.75 | 84.5585 | Total hardness | mg/L as CaCO3 | 78 | 262 | 556.1728 | 66.9492 | 409.0864 | 80.9331 | Total hardness | mg/L as CaCO3 | 106 | 265 | 1110 | 1166 | -5.045 | 60 | 715.5 | 85.1852 | Total hardness | mg/L as CaCO3 | 72 | 260 | 575.3548 | 72.8302 | 417.6774 | 82.7618 | Total hardness | mg/L as CaCO3 | 100 | 265 | 1070 | 1200 | -12.1495 | 62.2642 | 732.5 | 86.3481 | Total hardness | mg/L as CaCO3 | 82 | 280 | 605.3758 | 69.0566 | 442.6879 | 81.4768 | Total hardness | mg/L as CaCO3 | 100 | 260 | 1070 | 1166.6667 | -9.0343 | 61.5385 | 713.3333 | 85.9813 | Total hardness | mg/L as CaCO3 | 84 | 270 | 575.6561 | 67.6923 | 422.828 | 80.1338 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.274 | Feed flow rate to system, QF-sys (gpm) | 45.2941 | Turbidity (ntu) | 1.14 |  |  |  | 1998-10-17 | 10:30 | 24067 | 25.4 | 89 | 57 | 21 | 0 | 34.9 | 6.2 |  | 41.1 | 41.1 | 0.84915 | 0 | 14.9571 | 14.7813 | 5.9125 | 46.0875 | 0.32072 | 6.74 | 6.19 | 208 | 360 | 363 | 1225 | 1235.5 | -0.85714 | 42.6997 | 799.25 | 73.9756 | 89 | 71 | 19 | 25.6 | 16.2 | 41.8 | 41.8 | 0.50165 | 0.61244 | 16.4571 | 16.2637 | 4.1173 | 56.8827 | 0.28592 | 6.18 |  | 180 | 410 | 736 | 773.4568 | -5.0892 | 50.4132 | 591.7284 | 69.5806 | 71 | 57 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 7.4542 | 33.5458 | 0.33331 |  | 6.47 | 300 | 736 | 1225 | 1354.8387 | -10.5991 | 17.3554 | 1045.4194 | 71.3034 | Calcium hardness | mg/L as CaCO3 | 102 | 238 | 940 | 1008.6667 | -7.305 | 57.1429 | 623.3333 | 83.6364 | Calcium hardness | mg/L as CaCO3 | 81 | 240 | 496.3875 | 65.9664 | 368.1938 | 78.0007 | Calcium hardness | mg/L as CaCO3 | 94 | 230 | 1100 | 944 | 14.1818 | 59.1304 | 587 | 83.9864 | Calcium hardness | mg/L as CaCO3 | 74 | 228 | 479.8239 | 67.8261 | 353.9119 | 79.0908 | Calcium hardness | mg/L as CaCO3 | 86 | 228 | 920 | 973.5 | -5.8152 | 62.2807 | 600.75 | 85.6846 | Calcium hardness | mg/L as CaCO3 | 70 | 232 | 491 | 69.2982 | 361.5 | 80.6362 | Calcium hardness | mg/L as CaCO3 | 82 | 250 | 1030 | 1202 | -16.699 | 67.2 | 726 | 88.7052 | Calcium hardness | mg/L as CaCO3 | 66 | 240 | 531.871 | 73.6 | 385.9355 | 82.8987 | Calcium hardness | mg/L as CaCO3 | 92 | 240 | 990 | 1078.6667 | -8.9562 | 61.6667 | 659.3333 | 86.0465 | Calcium hardness | mg/L as CaCO3 | 76 | 250 | 535.9363 | 68.3333 | 392.9682 | 80.66 | Calcium hardness | mg/L as CaCO3 | 93 | 250 | 1000 | 1139.6667 | -13.9667 | 62.8 | 694.8333 | 86.6155 | Calcium hardness | mg/L as CaCO3 | 76 | 250 | 535.9363 | 69.6 | 392.9682 | 80.66 | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 6.7941 | SDI | >7.0 |  |  |  | 1998-10-18 | 9:30 | 24090 | 25.4 | 90 | 57 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.254 | 46.246 | 0.31688 | 6.72 | 6.09 | 208 | 362 | 373 | 1225 | 1293.8065 | -5.6169 | 44.2359 | 833.4032 | 75.0421 | 90 | 71 | 19 | 25.7 | 16.4 | 42.1 | 42.1 | 0.50597 | 0.61045 | 16.5214 | 16.3272 | 4.1021 | 57.3979 | 0.28446 | 6.21 |  | 180 | 410 | 736 | 770.4268 | -4.6776 | 51.7426 | 590.2134 | 69.5026 | 71 | 57 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 7.4542 | 33.5458 | 0.33331 |  | 6.46 | 300 | 736 | 1225 | 1354.8387 | -10.5991 | 19.571 | 1045.4194 | 71.3034 | Turbidity | ntu | 0.05 | 1.52 | 1.46 | 9.85 | -574.6575 | 96.7105 | 5.685 | 99.1205 | Turbidity | ntu | 0.04 | 1.32 | 3.384 | 97.3684 | 2.352 | 98.2993 | Turbidity | ntu | 0.06 | 1.72 | 2.34 | 10.435 | -345.9402 | 96.5116 | 6.0775 | 99.0128 | Turbidity | ntu | 0.07 | 1.93 | 4.9715 | 95.9302 | 3.4508 | 97.9715 | Turbidity | ntu | 0.042 | 0.653 | 1.64 | 3.8607 | -135.4116 | 93.5681 | 2.2569 | 98.139 | Turbidity | ntu | 0.061 | 0.224 | 0.4846 | 90.6585 | 0.3543 | 82.7829 | Turbidity | ntu | 0.05 | 0.17 | 0.9 | 0.85 | 5.5556 | 70.5882 | 0.51 | 90.1961 | Turbidity | ntu | 0.04 | 0.14 | 0.30774 | 76.4706 | 0.22387 | 82.1326 | Turbidity | ntu | 0.042 | 1.1 | 2.54 | 7.0953 | -179.3438 | 96.1818 | 4.0977 | 98.975 | Turbidity | ntu | 0.05 | 1.14 | 2.9312 | 95.4545 | 2.0356 | 97.5437 | Turbidity | ntu | 0.04 | 1.7 | 2.47 | 11.1067 | -349.6626 | 97.6471 | 6.4033 | 99.3753 | Turbidity | ntu | 0.05 | 1.63 | 4.2264 | 97.0588 | 2.9282 | 98.2925 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 18 |  |  | MFI |  |  |  |  | 1998-10-19 | 11:10 | 24115 | 25.3 | 91 | 57 | 22 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.6977 | 6.0731 | 45.9269 | 0.32002 | 6.74 | 6.1 | 205 | 345 | 369 | 1197 | 1255.625 | -4.8977 | 44.4444 | 812.3125 | 74.7634 | 91 | 72 | 20 | 25.7 | 16.2 | 41.9 | 41.9 | 0.50251 | 0.61337 | 16.5214 | 16.3756 | 4.1065 | 57.3935 | 0.28532 | 6.1 |  | 178 | 407 | 730 | 770.2901 | -5.5192 | 51.7615 | 588.6451 | 69.7611 | 72 | 57 | 25 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.2144 | 7.29 | 32.21 | 0.34817 |  | 6.45 | 298 | 730 | 1197 | 1324 | -10.6099 | 19.2412 | 1027 | 70.9834 | Ammonia | mg NH3-N / L | 0.62 | 0.73 | 1.62 | 1.3533 | 16.4609 | 15.0685 | 1.0417 | 40.48 | Total organic carbon | mg/L | BMRL | 12.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.53 | 0.73 | 1.41 | 1.78 | -26.2411 | 27.3973 | 1.255 | 57.7689 | Total organic carbon | mg/L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.47 | 0.58 | 1.34 | 1.1575 | 13.6194 | 18.9655 | 0.86875 | 45.8993 | Total organic carbon | mg/L | BMRL | 16.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.52 | 0.68 | 1.62 | 1.5867 | 2.0576 | 23.5294 | 1.1333 | 54.1176 | Total organic carbon | mg/L | BMRL | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.54 | 0.62 | 1.51 | 1.0733 | 28.9183 | 12.9032 | 0.84667 | 36.2205 | Total organic carbon | mg/L | BMRL | 12.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.52 | 0.67 | 1.54 | 1.52 | 1.2987 | 22.3881 | 1.095 | 52.5114 | Total organic carbon | mg/L | BMRL | 13.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-10-20 | 7:50 | 24136 | 25.3 | 91 | 57 | 21 | 0 | 34.6 | 6.3 |  | 40.9 | 40.9 | 0.84597 | 0 | 14.8286 | 14.6977 | 5.9937 | 47.0063 | 0.31267 | 6.63 | 6.09 | 208 | 346 | 368 | 1194 | 1246.7302 | -4.4163 | 43.4783 | 807.3651 | 74.2372 | 91 | 71 | 19 | 25.6 | 16.3 | 41.9 | 41.9 | 0.50338 | 0.61098 | 16.4571 | 16.3119 | 4.0169 | 57.9831 | 0.28132 | 6.12 |  | 180 | 405 | 721 | 758.3742 | -5.1837 | 51.087 | 581.6871 | 69.0555 | 71 | 57 | 22 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3418 | 7.1325 | 34.8675 | 0.32528 |  | 6.46 | 303 | 721 | 1194 | 1311.5079 | -9.8415 | 17.663 | 1016.254 | 70.1846 | Total organic carbon | mg/L | BMRL | 12.5 | 81.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.438 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 13.2 | 85.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.462 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 16.5 | 91.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.451 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.59 | 13.4 | 83.4 | 85.99 | -3.1055 | 95.597 | 49.695 | 98.8128 | UV254 | cm-1 | BMRL | 0.448 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 13.5 | 78.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.468 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.56 | 12.7 | 78.2 | 81.4933 | -4.2114 | 95.5906 | 47.0967 | 98.811 | UV254 | cm-1 | BMRL | 0.449 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Glades Road Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 14 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 23.2941 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-10-21 | 9:20 | 24161 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 5.8937 | 47.1063 | 0.31199 | 6.74 | 6.15 | 210 | 344 | 367 | 1192 | 1231.746 | -3.3344 | 42.7793 | 799.373 | 73.7294 | 91 | 71 | 20 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.3908 | 4.046 | 56.954 | 0.28779 | 6.13 |  | 181 | 405 | 721 | 766.2 | -6.2691 | 50.6812 | 585.6 | 69.0915 | 71 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 7.0654 | 33.9346 | 0.3295 |  | 6.51 | 305 | 721 | 1192 | 1302.0794 | -9.2348 | 16.8937 | 1011.5397 | 69.8479 | UV254 | cm-1 | BMRL | 0.42 | 2.475 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.504 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.186 | 2.83 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.448 | 2.571 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.784 | --- | --- | --- | --- | UV254 | cm-1 | 0.009 | 0.446 | 2.805 | 2.9223 | -4.183 | 97.9821 | 1.6842 | 99.4656 | SUVA | L/(mg*m) | NR | 3.4462 | --- | --- | --- | --- | UV254 | cm-1 | 0.009 | 0.446 | 2.588 | 2.9223 | -12.9186 | 97.9821 | 1.6842 | 99.4656 | SUVA | L/(mg*m) | NR | 3.6279 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.449 | 2.766 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 3.4275 | --- | --- | --- | ---
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0023 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 8.6275 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-10-22 | 9:33 | 24186 | 25.4 | 90 | 57 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.739 | 5.9814 | 46.5186 | 0.31684 | 6.63 | 6.09 | 212 | 352 | 371 | 1189 | 1249.2857 | -5.0703 | 42.8571 | 810.1429 | 73.8318 | 90 | 71 | 19 | 25.7 | 16 | 41.7 | 41.7 | 0.49905 | 0.61631 | 16.5214 | 16.3272 | 4.039 | 57.461 | 0.28414 | 6.14 |  | 183 | 407 | 725 | 766.8 | -5.7655 | 50.6739 | 586.9 | 68.8192 | 71 | 57 | 22 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3084 | 7.1325 | 34.8675 | 0.32432 |  | 6.49 | 307 | 725 | 1189 | 1315.5079 | -10.6399 | 17.2507 | 1020.254 | 69.9095 | SUVA | L/(mg*m) | NR | 3.36 | 3.0518 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 1.4091 | 3.3022 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.7152 | 2.7976 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.5254 | 3.3284 | 3.3633 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.3037 | 3.2926 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5354 | 3.5371 | --- | --- | --- | --- | ---
Process Train Name | SOFT | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1998-10-23 | 9:45 | 24210 | 25.4 | 93 | 58 | 21 | 0 | 35.3 | 6.6 |  | 41.9 | 41.9 | 0.84248 | 0 | 15.1286 | 14.9508 | 5.4379 | 49.0621 | 0.30473 | 6.69 | 6.16 | 204 | 343 | 352 | 1178 | 1143.5758 | 2.9223 | 42.0455 | 747.7879 | 72.7195 | 93 | 73 | 20 | 26.2 | 16.7 | 42.9 | 42.9 | 0.51549 | 0.61072 | 16.8429 | 16.6449 | 4.0328 | 58.9672 | 0.28227 | 6.11 |  | 177 | 403 | 722 | 757.5629 | -4.9256 | 49.7159 | 580.2814 | 69.4976 | 73 | 58 | 23 | 9 | 6.6 | 15.6 | 15.6 | 0.38402 | 0.57692 | 11.5714 | 11.4354 | 7.1477 | 35.3523 | 0.32347 |  | 6.48 | 297 | 722 | 1178 | 1301.5455 | -10.4877 | 15.625 | 1011.7727 | 70.6456 | Bromide | mg/L | 188 | 202 | --- | 281.3333 | --- | 6.9307 | 241.6667 | 22.2069 | [8 empty] | Bromide | mg/L | 188 | 178 | --- | 125.5 | --- | -5.618 | 151.75 | -23.888 | [8 empty] | Bromide | mg/L | 188 | 188 | --- | 188 | --- | 0 | 188 | 0 | [8 empty] | Bromide | mg/L | 191 | 186 | --- | 157.6667 | --- | -2.6882 | 171.8333 | -11.1542 | [8 empty] | Bromide | mg/L | 174 | 182 | --- | 227.3333 | --- | 4.3956 | 204.6667 | 14.9837 | [8 empty] | Bromide | mg/L | 191 | 181 | --- | 124.3333 | --- | -5.5249 | 152.6667 | -25.1092
ICR Treatment Plant Identification Number | 306 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-10-24 | 9:10 | 24234 | 25.3 | 91 | 57 | 21 | 0 | 34.8 | 6.6 |  | 41.4 | 41.4 | 0.84058 | 0 | 14.9143 | 14.7826 | 5.4182 | 47.5818 | 0.31068 | 6.78 | 6.2 | 205 | 341 | 354 | 1175 | 1139.6364 | 3.0097 | 42.0904 | 746.8182 | 72.5502 | 91 | 72 | 20 | 25.8 | 16.8 | 42.6 | 42.6 | 0.51376 | 0.60563 | 16.5857 | 16.4393 | 4.013 | 57.487 | 0.28597 | 6.12 |  | 177 | 404 | 721 | 752.6071 | -4.3838 | 50 | 578.3036 | 69.3932 | 72 | 57 | 22 | 8.9 | 6.6 | 15.5 | 15.5 | 0.38229 | 0.57419 | 11.4429 | 11.3418 | 7.0988 | 35.4012 | 0.32038 |  | 6.51 | 297 | 721 | 1175 | 1292.7576 | -10.0219 | 16.1017 | 1006.8788 | 70.5029 | SDS-Cl2 dose | mg/L | 5 | 22 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 6 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 22 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4500130 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -7.2941 | [5 empty] | 1998-10-25 | 10:50 | 24260 | 25.3 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 5.706 | 47.294 | 0.31167 | 6.76 | 6.19 | 209 | 350 | 361 | 1208 | 1198.2063 | 0.81073 | 42.1053 | 779.6032 | 73.1915 | 91 | 72 | 19 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.4393 | 4.1363 | 58.3637 | 0.28167 | 6.13 |  | 180 | 409 | 733 | 778.2625 | -6.175 | 50.1385 | 593.6313 | 69.6781 | 72 | 57 | 22 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3418 | 7.3373 | 35.1627 | 0.32255 |  | 6.48 | 303 | 733 | 1208 | 1340.4603 | -10.9653 | 16.0665 | 1036.7302 | 70.7735 | SDS-Free Cl2 residual | mg/L | 0.3 | 1.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 0.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.6 | 0.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.5 | 0.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.4 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.4 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -0.62745 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-10-26 | 9:00 | 24282 | 25.3 | 91 | 58 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 5.9688 | 47.5312 | 0.31012 | 6.81 | 5.88 | 210 | 355 | 369 | 1190 | 1244.7619 | -4.6018 | 43.0894 | 806.881 | 73.9739 | 91 | 72 | 20 | 25.8 | 16.4 | 42.2 | 42.2 | 0.50684 | 0.61137 | 16.5857 | 16.4393 | 4.0913 | 57.4087 | 0.28636 | 6.15 |  | 178 | 407 | 722 | 767.2561 | -6.2682 | 51.7615 | 587.128 | 69.6829 | 72 | 58 | 22 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3418 | 7.2008 | 35.7992 | 0.31682 |  | 6.28 | 300 | 722 | 1190 | 1318.1587 | -10.7696 | 18.6992 | 1020.0794 | 70.5905 | SDS-Cl2 demand | mg/L | 4.7 | 20.8 | --- | 112.0333 | --- | 77.4038 | 66.4167 | 92.9235 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 5 | 20.5 | --- | 101.875 | --- | 75.6098 | 61.1875 | 91.8284 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.82 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.9 | 19.4 | --- | 95.525 | --- | 74.7423 | 57.4625 | 91.4727 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.75 |  |  |  |  | SDS-Cl2 demand | mg/L | 5 | 21.3 | --- | 113.6667 | --- | 76.5258 | 67.4833 | 92.5908 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.6 | 20.2 | --- | 108.6 | --- | 77.2277 | 64.4 | 92.8571 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.82 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.6 | 20.2 | --- | 108.6 | --- | 77.2277 | 64.4 | 92.8571 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.82
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | not specified | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-10-27 | 9:15 | 24306 | 25.2 | 91 | 58 | 22 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7838 | 6.4944 | 46.0056 | 0.32135 | 6.75 | 6.01 | 201 | 356 | 374 | 1246 | 1326.873 | -6.4906 | 46.2567 | 850.4365 | 76.3651 | 91 | 72 | 20 | 25.8 | 16.1 | 41.9 | 41.9 | 0.50165 | 0.61575 | 16.5857 | 16.488 | 4.2689 | 57.2311 | 0.28809 | 6.08 |  | 174 | 411 | 746 | 790.7888 | -6.0039 | 53.4759 | 600.8944 | 71.0432 | 72 | 58 | 22 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2476 | 7.7787 | 35.2213 | 0.31934 |  | 6.4 | 288 | 746 | 1246 | 1385.746 | -11.2156 | 22.9947 | 1065.873 | 72.9799 | SDS-Chlorination temp. | oC | 21.2 | 21.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16 |  |  |  |  | SDS-Chlorination temp. | oC | 21.5 | 21.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.9 |  |  |  |  | SDS-Chlorination temp. | oC | 21.5 | 21.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.2 |  |  |  |  | SDS-Chlorination temp. | oC | 23 | 22.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.5 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.5 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.7
State Approved Plant Capacity (MGD) | 70 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.2:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-10-28 | 7:30 | 24329 | 25.3 | 91 | 58 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.7826 | 6.621 | 46.879 | 0.31534 | 6.76 | 6.03 | 201 | 354 | 377 | 1242 | 1349.1905 | -8.6305 | 46.6844 | 863.0952 | 76.7117 | 91 | 72 | 20 | 25.8 | 16.2 | 42 | 42 | 0.50338 | 0.61429 | 16.5857 | 16.4393 | 4.2752 | 57.2248 | 0.28728 | 6.09 |  | 173 | 411 | 747 | 790.037 | -5.7613 | 54.1114 | 600.5185 | 71.1916 | 72 | 58 | 25 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 7.8127 | 32.1873 | 0.34841 |  | 6.42 | 287 | 747 | 1242 | 1389.5397 | -11.8792 | 23.8727 | 1068.2698 | 73.1341 | SDS-Chlorination pH | --- | 8.4 | 8.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.2 | 8.2 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.4 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 19 | [7 empty] | 1998-10-29 | 8:30 | 24354 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.5 |  | 41.2 | 41.2 | 0.84223 | 0 | 14.8714 | 14.6966 | 6.5312 | 46.4688 | 0.31627 | 6.75 | 6.06 | 203 | 358 | 381 | 1214 | 1331.2462 | -9.6578 | 46.7192 | 856.1231 | 76.2885 | 91 | 72 | 20 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.3908 | 4.2447 | 57.2553 | 0.28628 | 6.07 |  | 176 | 411 | 740 | 789.9375 | -6.7483 | 53.8058 | 600.4688 | 70.6896 | 72 | 57 | 23 | 8.8 | 6.5 | 15.3 | 15.3 | 0.3771 | 0.57516 | 11.3143 | 11.1813 | 7.5294 | 33.9706 | 0.32915 |  | 6.43 | 291 | 740 | 1214 | 1347.8769 | -11.0278 | 23.622 | 1043.9385 | 72.1248 | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 40 | 40 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 40 | 40 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 20 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-10-30 | 10:10 | 24379 | 25.3 | 91 | 58 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6977 | 5.3065 | 48.1935 | 0.30497 | 6.7 | 6.2 | 214 | 352 | 354 | 1197 | 1135.2903 | 5.1554 | 39.548 | 744.6452 | 71.2615 | 91 | 72 | 19 | 25.7 | 16.5 | 42.2 | 42.2 | 0.5077 | 0.609 | 16.5214 | 16.3756 | 3.9845 | 58.5155 | 0.27985 | 6.15 |  | 184 | 408 | 730 | 756.897 | -3.6845 | 48.0226 | 582.4485 | 68.4092 | 72 | 58 | 23 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3418 | 7.163 | 34.837 | 0.32557 |  | 6.53 | 313 | 730 | 1197 | 1328.5968 | -10.9939 | 11.5819 | 1029.2984 | 69.5909 | SDS-TOX | mg Cl- /L | BMRL | 1600 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1490 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1420 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1540 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1810 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1475 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95% 2000 ppm MgSO4 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 26.7059 | [5 empty] | 1998-10-31 | 9:40 | 24403 | 25.5 | 91 | 58 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6533 | 5.4433 | 48.0567 | 0.30492 | 6.73 | 6.18 | 210 | 347 | 355 | 1214 | 1153.6508 | 4.9711 | 40.8451 | 754.3254 | 72.1606 | 91 | 72 | 20 | 25.7 | 16.5 | 42.2 | 42.2 | 0.5077 | 0.609 | 16.5214 | 16.279 | 4.0556 | 57.4444 | 0.28339 | 6.1 |  | 181 | 409 | 736 | 764.1273 | -3.8216 | 49.0141 | 586.5636 | 69.1423 | 72 | 58 | 23 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.275 | 7.3544 | 34.6456 | 0.32544 |  | 6.5 | 305 | 736 | 1214 | 1344.873 | -10.7803 | 14.0845 | 1040.4365 | 70.6854 | SDS-CHCl3 | mg/L | 1.5 | 350 | --- | 2324.8333 | --- | 99.5714 | 1337.4167 | 99.8878 | Sampling date | MM/DD/YY | 1998-10-21 | 1998-10-21 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 392 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-04 | 1998-11-04 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 380 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-18 | 1998-11-18 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 414 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-12-03 | 1998-12-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 415 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 386 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | 40-50% 500ppm CaCl2 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 16.3725 | [5 empty] | 1998-11-01 | 11:25 | 24428 | 25.5 | 91 | 57 | 21 | 0 | 34.7 | 6.5 |  | 41.2 | 41.2 | 0.84223 | 0 | 14.8714 | 14.6533 | 6.0909 | 46.9091 | 0.31238 | 6.64 | 6.04 | 202 | 334 | 368 | 1194 | 1254.1846 | -5.0406 | 45.1087 | 811.0923 | 75.0953 | 91 | 71 | 20 | 25.8 | 16.7 | 42.5 | 42.5 | 0.51203 | 0.60706 | 16.5857 | 16.3424 | 4.0944 | 56.9056 | 0.28718 | 6.06 |  | 175 | 406 | 730 | 762.8743 | -4.5033 | 52.4457 | 584.4371 | 70.0567 | 71 | 57 | 22 | 8.8 | 6.5 | 15.3 | 15.3 | 0.3771 | 0.57516 | 11.3143 | 11.1483 | 7.3785 | 34.6215 | 0.322 |  | 6.44 | 290 | 730 | 1194 | 1325.6923 | -11.0295 | 21.1957 | 1027.8462 | 71.7857 | SDS-BDCM | mg/L | BMRL | 63.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:50 | 7:25 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 70.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:10 | 6:40 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 68.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:30 | 7:05 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 66.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 7:40 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 63.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:10 | 7:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 57.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:10 | 7:00 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | N/A | [7 empty] | 1998-11-02 | 9:30 | 24451 | 25.4 | 91 | 58 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 5.7811 | 47.7189 | 0.30798 | 6.82 | 6.17 | 203 | 341 | 357 | 1083 | 1205.2222 | -11.2855 | 43.1373 | 781.1111 | 74.0114 | 91 | 72 | 20 | 25.8 | 16.3 | 42.1 | 42.1 | 0.50511 | 0.61283 | 16.5857 | 16.3908 | 4.1919 | 57.3081 | 0.28601 | 6.03 |  | 176 | 410 | 742 | 780.3804 | -5.1726 | 50.7003 | 595.1902 | 70.4296 | 72 | 58 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 7.6429 | 34.3571 | 0.32544 |  | 6.48 | 292 | 742 | 1083 | 1370.5714 | -26.5532 | 18.2073 | 1056.2857 | 72.356 | SDS-DBCM | mg/L | 1.2 | 7.8 | --- | 45.2 | --- | 84.6154 | 26.5 | 95.4717 | Operation time | hh.hh | 24160 | 24160 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.6 | 9.1 | --- | 48.475 | --- | 82.4176 | 28.7875 | 94.442 | Operation time | hh.hh | 24496 | 24496 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.3 | 8.2 | --- | 44.425 | --- | 84.1463 | 26.3125 | 95.0594 | Operation time | hh.hh | 24832 | 24832 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.4 | 8.3 | --- | 47.4 | --- | 83.1325 | 27.85 | 94.9731 | Operation time | hh.hh | 25192 | 25192 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.2 | 7.6 | --- | 43.8667 | --- | 84.2105 | 25.7333 | 95.3368 | Operation time | hh.hh | 25503 | 25503 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.2 | 7.4 | --- | 42.5333 | --- | 83.7838 | 24.9667 | 95.1936 | Operation time | hh.hh | 25503 | 25503 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-11-03 | 9:45 | 24475 | 25.2 | 91 | 57 | 21 | 0 | 34.8 | 6.5 |  | 41.3 | 41.3 | 0.84262 | 0 | 14.9143 | 14.8264 | 5.6257 | 47.3743 | 0.31296 | 6.7 | 6.08 | 201 | 352 | 354 | 1230 | 1173.1385 | 4.6229 | 43.2203 | 763.5692 | 73.6763 | 91 | 72 | 20 | 25.9 | 16 | 41.9 | 41.9 | 0.50078 | 0.61814 | 16.65 | 16.5519 | 4.2882 | 57.2118 | 0.28931 | 6.01 |  | 174 | 411 | 744 | 794.6437 | -6.807 | 50.8475 | 602.8219 | 71.1358 | 72 | 57 | 22 | 8.9 | 6.5 | 15.4 | 15.4 | 0.37883 | 0.57792 | 11.4429 | 11.3754 | 7.6818 | 34.8182 | 0.32671 |  | 6.39 | 288 | 744 | 1230 | 1368.3692 | -11.2495 | 18.6441 | 1056.1846 | 72.732 | SDS-CHBr3 | mg/L | 3.6 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.67 | 6.65 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | NA | NA | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.8 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.66 | 6.6 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.63 | 6.43 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.65 | 6.51 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.52 | 6.52 | --- | --- | --- | ---
|  | Standard testing pH | 8 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-11-04 | 9:10 | 24499 | 25.3 | 92 | 57 | 21 | 0 | 34.9 | 6.5 |  | 41.4 | 41.4 | 0.843 | 0 | 14.9571 | 14.8251 | 5.8954 | 47.6046 | 0.31142 | 6.68 | 6.02 | 197 | 358 | 357 | 1214 | 1216.0769 | -0.17108 | 44.8179 | 786.5385 | 74.9535 | 92 | 72 | 20 | 26 | 15.8 | 41.8 | 41.8 | 0.49819 | 0.62201 | 16.7143 | 16.5667 | 4.2653 | 57.7347 | 0.28695 | 6.04 |  | 173 | 407 | 736 | 792.0633 | -7.6173 | 51.5406 | 599.5316 | 71.1441 | 72 | 57 | 23 | 8.8 | 6.5 | 15.3 | 15.3 | 0.3771 | 0.57516 | 11.3143 | 11.2144 | 7.5462 | 33.9538 | 0.33028 |  | 6.38 | 286 | 736 | 1214 | 1345.2308 | -10.8098 | 19.888 | 1040.6154 | 72.5163 | SDS-THM4 | mg/L | 6.3 | 421.6 | --- | 2774.9667 | --- | 98.5057 | 1598.2833 | 99.6058 | Temperature | oC | 26 | 25.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 2.7 | 471.7 | --- | 2933.95 | --- | 99.4276 | 1702.825 | 99.8414 | Temperature | oC | 26 | 25.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.1 | 456.8 | --- | 2833.475 | --- | 99.1025 | 1645.1375 | 99.7508 | Temperature | oC | 25.5 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.3 | 488.5 | --- | 3232.3 | --- | 99.1198 | 1860.4 | 99.7689 | Temperature | oC | 25.6 | 25.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.5 | 486.3 | --- | 3222.1667 | --- | 99.2803 | 1854.2333 | 99.8112 | Temperature | oC | 25 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.4 | 450.8 | --- | 2986.0667 | --- | 99.2458 | 1718.4333 | 99.8021 | Temperature | oC | 25 | 25 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 16.3725 | [5 empty] | 1998-11-05 | 9:00 | 24522 | 25.3 | 92 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 5.8937 | 47.6063 | 0.30963 | 6.7 | 6.07 | 197 | 357 | 354 | 1248 | 1218.746 | 2.3441 | 44.3503 | 786.373 | 74.9483 | 92 | 71 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 4.3173 | 57.1827 | 0.28749 | 6 |  | 171 | 408 | 746 | 797.465 | -6.8988 | 51.6949 | 602.7325 | 71.6292 | 71 | 57 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 7.7961 | 33.2039 | 0.33774 |  | 6.35 | 290 | 746 | 1248 | 1393.2258 | -11.6367 | 18.0791 | 1069.6129 | 72.8874 | SDS-MCAA* | mg/L | BMRL | 17.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 145 | 230 | 333.8889 | -8.209 | 281.9444 | 48.5714 | SDS-MCAA* | mg/L | 1.83 | 7.39 | --- | 36.58 | --- | 75.2368 | 21.985 | 91.6761 | Alkalinity | mg/L as CaCO3 | 132 | 204 | 293.6949 | -10 | 248.8475 | 46.9555 | SDS-MCAA* | mg/L | 1.91 | 9.58 | --- | 49.8475 | --- | 80.0626 | 29.7138 | 93.572 | Alkalinity | mg/L as CaCO3 | 126 | 190 | 265.1678 | -8.6207 | 227.5839 | 44.6358 | SDS-MCAA* | mg/L | 0.6 | 15.8 | --- | 101.9333 | --- | 96.2025 | 58.8667 | 98.9807 | Alkalinity | mg/L as CaCO3 | 110 | 180 | 271.9403 | -12.2449 | 225.9701 | 51.321 | SDS-MCAA* | mg/L | 1.53 | 13.3 | --- | 79.9967 | --- | 88.4962 | 46.6483 | 96.7201 | Alkalinity | mg/L as CaCO3 | 128 | 210 | 318.2695 | 8.5714 | 264.1347 | 51.5399 | SDS-MCAA* | mg/L | 1.52 | 15.2 | --- | 92.72 | --- | 90 | 53.96 | 97.1831 | Alkalinity | mg/L as CaCO3 | 130 | 210 | 312.5581 | 0 | 261.2791 | 50.2448
|  | Acceptable range of operating pH values | 2 to11 | Design system recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-11-06 | 9:15 | 24546 | 25.2 | 91 | 58 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 5.8875 | 47.6125 | 0.3105 | NR | 6.01 | 199 | 358 | 354 | 1264 | 1221.5 | 3.3623 | 43.7853 | 787.75 | 74.7382 | 91 | 72 | 19 | 25.7 | 15.9 | 41.6 | 41.6 | 0.49732 | 0.61779 | 16.5214 | 16.424 | 4.3035 | 58.1965 | 0.28222 | 6.01 |  | 172 | 410 | 751 | 794.6918 | -5.8178 | 51.4124 | 602.3459 | 71.445 | 72 | 58 | 23 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3754 | 8.039 | 33.961 | 0.33496 |  | NR | 283 | 751 | 1264 | 1422.8065 | -12.5638 | 20.0565 | 1086.9032 | 73.9627 | SDS-DCAA* | mg/L | BMRL | 108 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 188 | 638 | 1188 | 48.0663 | 913 | 79.4085 | SDS-DCAA* | mg/L | BMRL | 98.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 186 | 659 | 1248.2458 | 49.8652 | 953.6229 | 80.4954 | SDS-DCAA* | mg/L | 0.54 | 108 | --- | 672.165 | --- | 99.5 | 390.0825 | 99.8616 | Total dissolved solids | mg/L | 184 | 660 | 1219.0604 | 49.7268 | 939.5302 | 80.4157 | SDS-DCAA* | mg/L | BMRL | 116 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 178 | 655 | 1281.5075 | 51.2329 | 968.2537 | 81.6164 | SDS-DCAA* | mg/L | 0.52 | 104 | --- | 690.3867 | --- | 99.5 | 397.1933 | 99.8691 | Total dissolved solids | mg/L | 177 | 663 | 1304.6946 | 52.1622 | 983.8473 | 82.0094 | SDS-DCAA* | mg/L | 0.5 | 105 | --- | 697.1667 | --- | 99.5238 | 401.0833 | 99.8753 | Total dissolved solids | mg/L | 177 | 665 | 1290.6047 | 52.6738 | 977.8023 | 81.8982
|  | Typical pressure drop across a single element (psi) | 3 to 5 psi | System influent flow rate, QI-sys (gpm) | 45.3041 | [5 empty] | 1998-11-07 | 9:40 | 24571 | 25.3 | 92 | 58 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.7826 | 6.7714 | 47.2286 | 0.313 | NR | 5.95 | 194 | 359 | 374 | 1267 | 1368.2857 | -7.9941 | 48.1283 | 871.1429 | 77.7304 | 92 | 72 | 19 | 25.9 | 15.8 | 41.7 | 41.7 | 0.49732 | 0.6211 | 16.65 | 16.503 | 4.4217 | 58.5783 | 0.28173 | 5.95 |  | 170 | 413 | 754 | 811.3354 | -7.6042 | 54.5455 | 612.1677 | 72.2298 | 72 | 58 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 7.9316 | 34.0684 | 0.32917 |  | NR | 278 | 745 | 1267 | 1397.3175 | -10.2855 | 25.6684 | 1071.1587 | 74.0468 | SDS-TCAA* | mg/L | BMRL | 121 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 163 | 510 | 934.1111 | 33.1967 | 722.0556 | 77.4256 | SDS-TCAA* | mg/L | BMRL | 126 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 150 | 520 | 980.9322 | 40 | 750.4661 | 80.0124 | SDS-TCAA* | mg/L | BMRL | 120 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 148 | 540 | 1000.4027 | 37.2881 | 770.2013 | 80.7842 | SDS-TCAA* | mg/L | BMRL | 162 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 132 | 530 | 1052.7463 | 50.1887 | 791.3731 | 83.3201 | SDS-TCAA* | mg/L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 144 | 570 | 1132.4731 | 45.6604 | 851.2365 | 83.0834 | SDS-TCAA* | mg/L | BMRL | 131 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 148 | 580 | 1133.814 | 43.0769 | 856.907 | 82.7286
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.00022078 | [5 empty] | 1998-11-08 | 8:22 | 24593 | 25.2 | 91 | 57 | 21 | 0 | 34.6 | 6.5 |  | 41.1 | 41.1 | 0.84185 | 0 | 14.8286 | 14.7412 | 6.188 | 46.812 | 0.3149 | 7.51 | 6.59 | 209 | 368 | 378 | 1197 | 1277.6 | -6.7335 | 44.709 | 827.8 | 74.7524 | 91 | 72 | 19 | 25.7 | 16.4 | 42.1 | 42.1 | 0.50597 | 0.61045 | 16.5214 | 16.424 | 4.0843 | 58.4157 | 0.28116 | 6.16 |  | 181 | 410 | 733 | 768.8598 | -4.8922 | 52.1164 | 589.4299 | 69.2924 | 72 | 57 | 23 | 8.8 | 6.5 | 15.3 | 15.3 | 0.3771 | 0.57516 | 11.3143 | 11.2476 | 7.1772 | 34.3228 | 0.3277 |  | 6.96 | 305 | 733 | 1197 | 1312.4462 | -9.6446 | 19.3122 | 1022.7231 | 70.1777 | SDS-MBAA* | mg/L | BMRL | 1.36 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 150 | 490 | 905.5556 | 36.9748 | 697.7778 | 78.5032 | SDS-MBAA* | mg/L | BMRL | 1.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 132 | 490 | 935.9831 | 42.6087 | 712.9915 | 81.4865 | SDS-MBAA* | mg/L | BMRL | 0.87 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 132 | 490 | 910.4698 | 42.1053 | 700.2349 | 81.1492 | SDS-MBAA* | mg/L | BMRL | 0.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 122 | 490 | 973.3433 | 51.2 | 731.6716 | 83.3259 | SDS-MBAA* | mg/L | BMRL | 0.84 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 140 | 500 | 975.3293 | 41.6667 | 737.6647 | 81.0212 | SDS-MBAA* | mg/L | BMRL | 0.86 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 144 | 500 | 956.3837 | 42.4 | 728.1919 | 80.225
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-11-09 | 8:53 | 24618 | 25.3 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 7.0199 | 45.9801 | 0.32058 | 7.2 | 6.43 | 208 | 391 | 395 | 1208 | 1424.9841 | -17.9623 | 47.3418 | 909.9921 | 77.1427 | 91 | 72 | 19 | 25.7 | 15.9 | 41.6 | 41.6 | 0.49732 | 0.61779 | 16.5214 | 16.3756 | 4.1226 | 58.3774 | 0.28051 | 6.1 |  | 180 | 408 | 733 | 776.5283 | -5.9384 | 54.4304 | 592.2642 | 69.6082 | 72 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 7.3202 | 34.1798 | 0.3281 |  | 6.79 | 302 | 733 | 1208 | 1335.0317 | -10.5159 | 23.5443 | 1034.0159 | 70.7935 | SDS-DBAA* | mg/L | 0.53 | 1.24 | --- | 5.2633 | --- | 57.2581 | 3.2517 | 83.7007 | Turbidity | ntu | 0.05 | 2.13 | 4.6722 | 96.7105 | 3.4011 | 98.5299 | SDS-DBAA* | mg/L | 0.53 | 1.22 | --- | 4.8425 | --- | 56.5574 | 3.0312 | 82.5155 | Turbidity | ntu | 0.04 | 2.42 | 5.3849 | 97.6744 | 3.9025 | 98.975 | SDS-DBAA* | mg/L | 0.61 | 1.32 | --- | 5.0475 | --- | 53.7879 | 3.1837 | 80.8402 | Turbidity | ntu | 0.045 | 2.05 | 4.4049 | 93.1087 | 3.2274 | 98.6057 | SDS-DBAA* | mg/L | 0.5 | 1.3 | --- | 5.8333 | --- | 61.5385 | 3.5667 | 85.9813 | Turbidity | ntu | 0.06 | 1.31 | 2.9518 | 64.7059 | 2.1309 | 97.1843 | SDS-DBAA* | mg/L | BMRL | 1.12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 2.13 | 4.8631 | 94.5455 | 3.4966 | 98.284 | SDS-DBAA* | mg/L | BMRL | 1.22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.05 | 1.89 | 4.2488 | 97.0588 | 3.0694 | 98.371
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | maximum system recycle flow rates. | [6 empty] | 1998-11-10 | 8:57 | 24642 | 25.3 | 92 | 57 | 22 | 0 | 34.8 | 6.7 |  | 41.5 | 41.5 | 0.83855 | 0 | 14.9143 | 14.7826 | 7.3019 | 45.1981 | 0.32706 | 7.13 | 6.47 | 205 | 424 | 408 | 1190 | 1462.3881 | -22.8898 | 49.7549 | 935.194 | 78.0794 | 92 | 72 | 20 | 25.9 | 16.3 | 42.2 | 42.2 | 0.50597 | 0.61374 | 16.65 | 16.503 | 4.1632 | 57.8368 | 0.28534 | 6.09 |  | 177 | 409 | 733 | 777.638 | -6.0898 | 56.6176 | 593.319 | 70.1678 | 72 | 57 | 24 | 8.9 | 6.7 | 15.6 | 15.6 | 0.38575 | 0.57051 | 11.4429 | 11.3418 | 7.2392 | 33.2608 | 0.341 |  | 6.75 | 298 | 733 | 1190 | 1310.8358 | -10.1543 | 26.9608 | 1021.9179 | 70.8391 | SDS-BCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.59 | 31.3 | 68.8344 | 95.28 | 50.0672 | 98.8216 | SDS-BCAA* | mg/L | BMRL | 11.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.58 | 33.5 | 74.5105 | 95.6061 | 54.0053 | 98.926 | SDS-BCAA* | mg/L | BMRL | 12.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.57 | 35.9 | 77.395 | 96.5455 | 56.6475 | 98.9938 | SDS-BCAA* | mg/L | BMRL | 13.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.71 | 34 | 77.7242 | 94.7015 | 55.8621 | 98.729 | SDS-BCAA* | mg/L | BMRL | 11.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.66 | 33.1 | 75.9325 | 95.1111 | 54.5162 | 98.7894 | SDS-BCAA* | mg/L | BMRL | 12.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.59 | 33.4 | 75.4617 | 95.3543 | 54.4308 | 98.9161
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-11-11 | 7:20 | 24664 | 25.2 | 91 | 57 | 21 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.7412 | 6.0731 | 46.9269 | 0.31413 | 6.9 | 6.29 | 205 | 363 | 369 | 1219 | 1255.625 | -3.0045 | 44.4444 | 812.3125 | 74.7634 | 91 | 72 | 19 | 25.8 | 17.2 | 43 | 43 | 0.52068 | 0.6 | 16.5857 | 16.488 | 4.0775 | 58.4225 | 0.28222 | 6.11 |  | 177 | 410 | 737 | 759.5 | -3.0529 | 52.0325 | 584.75 | 69.7307 | 72 | 57 | 23 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.2476 | 7.4081 | 34.0919 | 0.32992 |  | 6.51 | 298 | 737 | 1219 | 1340.625 | -9.9774 | 19.2412 | 1038.8125 | 71.3134 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.145 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.149 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.156 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.155 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-11-12 | 11:05 | 24692 | 25.1 | 91 | 57 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.8275 | 5.8115 | 48.1885 | 0.3077 | 6.97 | 6.26 | 203 | 356 | 356 | 1214 | 1212.3065 | 0.1395 | 42.9775 | 784.1532 | 74.1122 | 91 | 71 | 19 | 25.9 | 16.1 | 42 | 42 | 0.50251 | 0.61667 | 16.65 | 16.6009 | 4.1139 | 57.8861 | 0.28678 | 6.1 |  | 175 | 403 | 727 | 769.7826 | -5.8848 | 50.8427 | 586.3913 | 70.1564 | 71 | 57 | 22 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.1527 | 7.368 | 34.632 | 0.32203 |  | 6.51 | 294 | 727 | 1214 | 1334.5968 | -9.9338 | 17.4157 | 1030.7984 | 71.4784 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6581 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6716 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.2006 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4894 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NA | 3.6826 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 45.3041 | [5 empty] | 1998-11-13 | 6:50 | 24712 | 25.2 | 91 | 57 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.8264 | 5.9438 | 47.0562 | 0.31508 | 6.95 | 6.25 | 204 | 359 | 362 | 1222 | 1234.7619 | -1.0443 | 43.6464 | 798.381 | 74.4483 | 91 | 72 | 20 | 25.9 | 15.8 | 41.7 | 41.7 | 0.49732 | 0.6211 | 16.65 | 16.5519 | 4.2033 | 57.2967 | 0.28888 | 6.11 |  | 177 | 408 | 736 | 786.6646 | -6.8838 | 51.105 | 597.3323 | 70.3683 | 72 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2476 | 7.473 | 34.027 | 0.33055 |  | 6.49 | 296 | 736 | 1222 | 1350.6032 | -10.524 | 18.232 | 1043.3016 | 71.6285 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 25.6667 | [5 empty] | 1998-11-14 | 10:02 | 24739 | 25.3 | 91 | 57 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 6.0015 | 46.9985 | 0.31363 | 7 | 6.24 | 205 | 362 | 363 | 1243 | 1247.2903 | -0.34516 | 43.5262 | 805.1452 | 74.5388 | 91 | 72 | 19 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.4393 | 4.2323 | 58.2677 | 0.28213 | 6.09 |  | 177 | 410 | 743 | 790.4684 | -6.3887 | 51.2397 | 600.2342 | 70.5115 | 72 | 57 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 7.6423 | 33.8577 | 0.33122 |  | 6.51 | 296 | 743 | 1243 | 1377.4516 | -10.8167 | 18.4573 | 1060.2258 | 72.0814 | SDS-HAA5 | mg/L | 0.53 | 249 | --- | 1656.9967 | --- | 99.7871 | 952.9983 | 99.9444 | [8 empty] | SDS-HAA5 | mg/L | 2.36 | 234.91 | --- | 1455.7975 | --- | 98.9954 | 845.3537 | 99.7208 | [8 empty] | SDS-HAA5 | mg/L | 3.06 | 239.77 | --- | 1482.4975 | --- | 98.7238 | 861.1337 | 99.6447 | [8 empty] | SDS-HAA5 | mg/L | 1.1 | 296 | --- | 1967.1 | --- | 99.6284 | 1131.55 | 99.9028 | [8 empty] | SDS-HAA5 | mg/L | 2.05 | 248.26 | --- | 1643.45 | --- | 99.1743 | 945.855 | 99.7833 | [8 empty] | SDS-HAA5 | mg/L | 2.02 | 253.28 | --- | 1677.0867 | --- | 99.2025 | 965.1833 | 99.7907
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 19.6375 | [5 empty] | 1998-11-15 | 8:10 | 24761 | 25.4 | 91 | 57 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.739 | 6.4705 | 46.5295 | 0.31677 | 7.23 | 6.28 | 201 | 360 | 373 | 1234 | 1323.0952 | -7.22 | 46.1126 | 848.0476 | 76.2985 | 91 | 72 | 19 | 25.9 | 16.1 | 42 | 42 | 0.50251 | 0.61667 | 16.65 | 16.4543 | 4.2402 | 58.2598 | 0.28243 | 6.14 |  | 174 | 409 | 740 | 787.0435 | -6.3572 | 53.3512 | 598.0217 | 70.9041 | 72 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 7.6598 | 33.8402 | 0.33042 |  | 6.62 | 289 | 740 | 1234 | 1369.9683 | -11.0185 | 22.5201 | 1054.9841 | 72.6062 | SDS-HAA6 | mg/L | 0.53 | 262 | --- | 1743.6633 | --- | 99.7977 | 1002.8317 | 99.9471 | [8 empty] | SDS-HAA6 | mg/L | 2.36 | 246.21 | --- | 1526.4225 | --- | 99.0415 | 886.3162 | 99.7337 | [8 empty] | SDS-HAA6 | mg/L | 3.06 | 252.37 | --- | 1561.2475 | --- | 98.7875 | 906.8088 | 99.6626 | [8 empty] | SDS-HAA6 | mg/L | 1.1 | 309.3 | --- | 2055.7667 | --- | 99.6444 | 1182.5333 | 99.907 | [8 empty] | SDS-HAA6 | mg/L | 2.05 | 259.76 | --- | 1720.1167 | --- | 99.2108 | 989.9383 | 99.7929 | [8 empty] | SDS-HAA6 | mg/L | 2.02 | 265.88 | --- | 1761.0867 | --- | 99.2403 | 1013.4833 | 99.8007
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 19.6375 | [5 empty] | 1998-11-16 | 9:00 | 24786 | 25.3 | 91 | 57 | 21 | 0 | 34.7 | 6.1 |  | 40.8 | 40.8 | 0.85049 | 0 | 14.8714 | 14.7401 | 6.6506 | 46.3494 | 0.31802 | 6.95 | 6.22 | 200 | 352 | 373 | 1257 | 1357.1148 | -7.9646 | 46.3807 | 865.0574 | 76.8801 | 91 | 72 | 19 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 4.2809 | 58.2191 | 0.28237 | 6.1 |  | 174 | 409 | 747 | 795.1783 | -6.4496 | 53.3512 | 602.0892 | 71.1006 | 72 | 57 | 23 | 8.8 | 6.1 | 14.9 | 14.9 | 0.36326 | 0.5906 | 11.3143 | 11.2144 | 7.8664 | 33.6336 | 0.33343 |  | 6.48 | 290 | 747 | 1257 | 1406.2787 | -11.8758 | 22.252 | 1076.6393 | 73.0643 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.8333 | [5 empty] | 1998-11-17 | 9:26 | 24810 | 25.4 | 92 | 57 | 21 | 0 | 34.7 | 6.5 |  | 41.2 | 41.2 | 0.84223 | 0 | 14.8714 | 14.6966 | 6.0542 | 47.4458 | 0.30976 | 6.95 | 6.21 | 199 | 364 | 364 | 1222 | 1244.8462 | -1.8696 | 45.3297 | 804.4231 | 75.2618 | 92 | 72 | 20 | 25.9 | 16.9 | 42.8 | 42.8 | 0.51635 | 0.60514 | 16.65 | 16.4543 | 4.1861 | 57.8139 | 0.28461 | 6.07 |  | 173 | 410 | 741 | 773.213 | -4.3472 | 52.4725 | 591.6065 | 70.7576 | 72 | 56 | 23 | 8.7 | 6.5 | 15.2 | 15.2 | 0.37537 | 0.57237 | 11.1857 | 11.0542 | 7.595 | 33.405 | 0.33092 |  | 6.45 | 286 | 741 | 1222 | 1350 | -10.4746 | 21.4286 | 1045.5 | 72.6447 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 6.8041 | [5 empty] | 1998-11-18 | 12:15 | 24837 | 25.4 | 92 | 56 | 22 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.6966 | 5.9746 | 46.0254 | 0.31932 | 6.94 | 6.2 | 199 | 357 | 360 | 1233 | 1232.9219 | 0.0063362 | 44.7222 | 796.4609 | 75.0145 | 92 | 72 | 20 | 25.9 | 16.2 | 42.1 | 42.1 | 0.50424 | 0.6152 | 16.65 | 16.4543 | 4.2645 | 57.7355 | 0.28499 | 6.06 |  | 173 | 410 | 743 | 788.9074 | -6.1787 | 51.9444 | 599.4537 | 71.1404 | 72 | 56 | 24 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.1813 | 7.7119 | 32.2881 | 0.3463 |  | 6.42 | 286 | 743 | 1233 | 1371.375 | -11.2226 | 20.5556 | 1057.1875 | 72.9471
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-11-19 | 11:20 | 24860 | 25.4 | 92 | 56 | 22 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.739 | 6.32 | 45.68 | 0.32266 | 6.95 | 6.23 | 199 | 360 | 367 | 1243 | 1295 | -4.1834 | 45.7766 | 831 | 76.0529 | 92 | 72 | 19 | 25.9 | 15.9 | 41.8 | 41.8 | 0.49905 | 0.61962 | 16.65 | 16.4543 | 4.2821 | 58.7179 | 0.28023 | 6.07 |  | 173 | 409 | 747 | 793.4277 | -6.2152 | 52.861 | 601.2138 | 71.2249 | 72 | 56 | 24 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 7.8297 | 32.1703 | 0.34757 |  | 6.43 | 286 | 747 | 1243 | 1390.9365 | -11.9016 | 22.0708 | 1068.9683 | 73.2452 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 6.7941 | [5 empty] | 1998-11-20 | 6:00 | 24879 | 25.3 | 92 | 56 | 21 | 0 | 34.9 | 6.4 |  | 41.3 | 41.3 | 0.84504 | 0 | 14.9571 | 14.8251 | 6.6333 | 46.3667 | 0.31974 | 7 | 6.19 | 197 | 356 | 375 | 1242 | 1345.6562 | -8.3459 | 47.4667 | 860.3281 | 77.1018 | 92 | 72 | 19 | 26.1 | 16.1 | 42.2 | 42.2 | 0.50424 | 0.61848 | 16.7786 | 16.6304 | 4.2729 | 58.7271 | 0.28318 | 6.05 |  | 171 | 407 | 743 | 789.5839 | -6.2697 | 54.4 | 598.2919 | 71.4186 | 72 | 56 | 22 | 8.7 | 6.4 | 15.1 | 15.1 | 0.37191 | 0.57616 | 11.1857 | 11.087 | 7.7938 | 34.2062 | 0.32412 |  | 6.43 | 283 | 747 | 1242 | 1377.75 | -10.93 | 24.5333 | 1062.375 | 73.3616 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 38.5 | [5 empty] | 1998-11-21 | 10:00 | 24907 | 25.4 | 91 | 56 | 21 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.6543 | 6.2213 | 46.2788 | 0.31665 | 6.99 | 6.23 | 195 | 357 | 363 | 1236 | 1271.25 | -2.8519 | 46.281 | 817.125 | 76.1358 | 91 | 72 | 20 | 25.7 | 16.4 | 42.1 | 42.1 | 0.50597 | 0.61045 | 16.5214 | 16.3272 | 4.2091 | 57.2909 | 0.28499 | 6.05 |  | 171 | 407 | 743 | 776.8293 | -4.5531 | 52.8926 | 591.9146 | 71.1107 | 72 | 56 | 23 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.1813 | 7.8131 | 33.1869 | 0.33692 |  | 6.43 | 280 | 743 | 1236 | 1379.625 | -11.6201 | 22.865 | 1061.3125 | 73.6176 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 45.2941 | [5 empty] | 1998-11-22 | 8:35 | 24930 | 25.4 | 92 | 56 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 6.6613 | 46.3387 | 0.31807 | 6.98 | 6.22 | 197 | 358 | 372 | 1247 | 1354.2581 | -8.6013 | 47.043 | 863.129 | 77.1761 | 92 | 72 | 20 | 25.9 | 15.7 | 41.6 | 41.6 | 0.49559 | 0.6226 | 16.65 | 16.4543 | 4.3431 | 57.6569 | 0.28538 | 6.11 |  | 171 | 409 | 744 | 801.6242 | -7.7452 | 54.0323 | 605.3121 | 71.7501 | 72 | 57 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 7.8645 | 33.6355 | 0.33243 |  | 6.47 | 284 | 744 | 1247 | 1396.9032 | -12.0211 | 23.6559 | 1070.4516 | 73.4691 | Qp/QT (THM4), % | 84.1801 | 92.8485 |  | Qp/QT (HAA5), % | 78.4803 | 89.3468 | [11 empty] | Qp/QT (THM4), % | 85.2239 | 92.8998 |  | Qp/QT (HAA5), % | 77.794 | 89.4044 | [11 empty] | Qp/QT (THM4), % | 85.0011 | 92.9534 |  | Qp/QT (HAA5), % | 78.48 | 89.8864 | [11 empty] | Qp/QT (THM4), % | 86.0182 | 93.4531 |  | Qp/QT (HAA5), % | 82.0617 | 91.2174 | [11 empty] | Qp/QT (THM4), % | 85.8119 | 93.2684 |  | Qp/QT (HAA5), % | 78.9001 | 89.8664 | [11 empty] | Qp/QT (THM4), % | 84.667 | 92.7135 |  | Qp/QT (HAA5), % | 79.3123 | 90.0581
[11 empty] | 1998-11-23 | 10:30 | 24956 | 25.4 | 91 | 57 | 21 | 0 | 34.6 | 6.3 |  | 40.9 | 40.9 | 0.84597 | 0 | 14.8286 | 14.6543 | 7.4921 | 45.5079 | 0.32202 | 6.98 | 5.98 | 175 | 356 | 375 | 1332 | 1473.4127 | -10.6166 | 53.3333 | 924.2063 | 81.0648 | 91 | 72 | 20 | 25.8 | 15.9 | 41.7 | 41.7 | 0.49819 | 0.61871 | 16.5857 | 16.3908 | 4.6732 | 56.8268 | 0.28843 | 5.85 |  | 156 | 414 | 775 | 832.6415 | -7.4376 | 58.4 | 623.3208 | 74.9728 | 72 | 57 | 22 | 8.7 | 6.3 | 15 | 15 | 0.36845 | 0.58 | 11.1857 | 11.0542 | 9.0271 | 33.4729 | 0.33024 |  | 6.44 | 241 | 775 | 1332 | 1512.4286 | -13.5457 | 35.7333 | 1143.7143 | 78.9283 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 95.6713 | 50.5427 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 106.846 | 52.3932 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 101.5211 | 49.8845 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 91.1572 | 46.8255 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 105.3702 | 52.4251 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 95.9569 | 47.88
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-11-24 | 9:45 | 24979 | 25.4 | 92 | 57 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.739 | 6.32 | 47.18 | 0.3124 | 6.98 | 6.21 | 201 | 361 | 369 | 1257 | 1297 | -3.1822 | 45.5285 | 833 | 75.8703 | 92 | 72 | 20 | 25.9 | 15.8 | 41.7 | 41.7 | 0.49732 | 0.6211 | 16.65 | 16.4543 | 4.3489 | 57.6511 | 0.28541 | 6.13 |  | 175 | 414 | 755 | 805.7785 | -6.7256 | 52.5745 | 609.8892 | 71.3063 | 72 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 7.8976 | 33.6024 | 0.33275 |  | 6.46 | 290 | 755 | 1257 | 1404.5238 | -11.7362 | 21.4092 | 1079.7619 | 73.1422 | SDS-HAA5b, mg/L | 39.8377 | 18.2992 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 36.7219 | 18.8715 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 38.5639 | 19.74 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 42.3324 | 20.4068 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 36.9824 | 18.6238 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 40.5458 | 20.3282 |  | SDS-HAA5b, mg/L | 54 | 27
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 3.7 | [5 empty] | 1998-11-25 | 10:45 | 25004 | 25.3 | 91 | 55 | 21 | 0 | 34.8 | 6.1 |  | 40.9 | 40.9 | 0.85086 | 0 | 14.9143 | 14.7826 | 7.2426 | 44.7574 | 0.33028 | 6.9 | 6.06 | 189 | 365 | 377 | 1147 | 1449.5246 | -26.3753 | 49.8674 | 913.2623 | 79.305 | 91 | 72 | 19 | 26 | 15.4 | 41.4 | 41.4 | 0.49127 | 0.62802 | 16.7143 | 16.5667 | 4.5551 | 57.9449 | 0.2859 | 6.04 |  | 166 | 413 | 764 | 830.013 | -8.6404 | 55.9682 | 621.5065 | 73.2907 | 72 | 55 | 23 | 8.7 | 6.1 | 14.8 | 14.8 | 0.36153 | 0.58784 | 11.1857 | 11.087 | 8.497 | 32.003 | 0.34644 |  | 6.34 | 268 | 764 | 1147 | 1471.4098 | -28.2833 | 28.9125 | 1117.7049 | 76.0223 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9.5 | [5 empty] | 1998-11-26 | 6:25 | 25023 | 25.4 | 91 | 56 | 21 | 0 | 34.8 | 6.5 |  | 41.3 | 41.3 | 0.84262 | 0 | 14.9143 | 14.739 | 6.8758 | 45.6242 | 0.32305 | 6.97 | 6.03 | 186 | 357 | 373 | 1283 | 1374.1692 | -7.1059 | 50.134 | 873.5846 | 78.7084 | 91 | 72 | 19 | 25.9 | 16.3 | 42.2 | 42.2 | 0.50597 | 0.61374 | 16.65 | 16.4543 | 4.4862 | 58.0138 | 0.28363 | 6.05 |  | 164 | 414 | 761 | 811.2393 | -6.6017 | 56.0322 | 612.6196 | 73.2297 | 72 | 56 | 23 | 8.8 | 6.5 | 15.3 | 15.3 | 0.3771 | 0.57516 | 11.3143 | 11.1813 | 8.4014 | 32.5986 | 0.343 |  | 6.28 | 260 | 761 | 1283 | 1439.2769 | -12.1806 | 30.2949 | 1100.1385 | 76.3666 | SDS-CDb, mg/L | 7.247 | 5.8514 |  | SDS-CDb, mg/L | 8.1647 | 6.4152 | [11 empty] | SDS-CDb, mg/L | 7.2903 | 6.1005 |  | SDS-CDb, mg/L | 8.4419 | 6.6423 | [11 empty] | SDS-CDb, mg/L | 7.0748 | 5.9218 |  | SDS-CDb, mg/L | 8.0204 | 6.3665 | [11 empty] | SDS-CDb, mg/L | 7.279 | 6.0671 |  | SDS-CDb, mg/L | 7.9239 | 6.4316 | [11 empty] | SDS-CDb, mg/L | 6.8133 | 5.6501 |  | SDS-CDb, mg/L | 7.8916 | 6.1808 | [11 empty] | SDS-CDb, mg/L | 6.992 | 5.7367 |  | SDS-CDb, mg/L | 7.8273 | 6.1509
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1998-11-27 | 8:50 | 25050 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 7.0199 | 45.9801 | 0.31963 | 7.09 | 6.1 | 188 | 362 | 375 | 1319 | 1404.9841 | -6.5189 | 49.8667 | 889.9921 | 78.8762 | 91 | 72 | 19 | 25.9 | 15.8 | 41.7 | 41.7 | 0.49732 | 0.6211 | 16.65 | 16.4543 | 4.5672 | 57.9328 | 0.28402 | 5.99 |  | 167 | 418 | 775 | 829.4494 | -7.0257 | 55.4667 | 623.7247 | 73.2254 | 72 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 8.6619 | 32.8381 | 0.3405 |  | 6.39 | 265 | 775 | 1319 | 1487.381 | -12.7658 | 29.3333 | 1131.1905 | 76.5734 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 2.3811 | 1.4287 |  | TOCb, mg/L | 2.8879 | 1.7151 | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 2.4214 | 1.4446 |  | TOCb, mg/L | 3.0715 | 1.7669
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-11-28 | 8:30 | 25074 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 7.3202 | 45.6798 | 0.32173 | 6.92 | 6.11 | 182 | 361 | 377 | 1306 | 1451.0476 | -11.1062 | 51.7241 | 914.0238 | 80.088 | 91 | 71 | 19 | 25.8 | 16.2 | 42 | 42 | 0.50338 | 0.61429 | 16.5857 | 16.3908 | 4.5267 | 57.4733 | 0.28519 | 5.99 |  | 160 | 412 | 764 | 813.3333 | -6.4572 | 57.5597 | 612.6667 | 73.8847 | 71 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 8.6619 | 32.3381 | 0.34576 |  | 6.25 | 254 | 764 | 1306 | 1476.381 | -13.046 | 32.626 | 1120.1905 | 77.3253 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | 0.070101 | 0.03761 |  | UV254 b, cm-1 | 0.08739 | 0.04738 | [11 empty] | UV254 b, cm-1 | 0.071002 | 0.038417 |  | UV254 b, cm-1 | 0.10121 | 0.053284 | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
|  |  |  | Design permeate pressure, Pp (psi) | 10 | [5 empty] | 1998-11-29 | 8:05 | 25097 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 7.6206 | 45.3794 | 0.32386 | 6.92 | 6 | 182 | 369 | 385 | 1326 | 1503.1111 | -13.3568 | 52.7273 | 944.0556 | 80.7215 | 91 | 72 | 19 | 25.9 | 16 | 41.9 | 41.9 | 0.50078 | 0.61814 | 16.65 | 16.4543 | 4.5958 | 57.9042 | 0.28416 | 6.02 |  | 160 | 414 | 772 | 825.1625 | -6.8863 | 58.4416 | 619.5812 | 74.1761 | 72 | 57 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 8.8148 | 32.6852 | 0.34209 |  | 6.23 | 253 | 772 | 1326 | 1496.9524 | -12.8923 | 34.2857 | 1134.4762 | 77.699 | Bromideb, mg/L | 190.2148 | 189.0012 |  | Bromideb, mg/L | 191.0128 | 189.4914 | [11 empty] | Bromideb, mg/L | 186.5224 | 187.29 |  | Bromideb, mg/L | 185.7794 | 186.9404 | [11 empty] | Bromideb, mg/L | 188 | 188 |  | Bromideb, mg/L | 188 | 188 | [11 empty] | Bromideb, mg/L | 190.3009 | 190.6727 |  | Bromideb, mg/L | 190.1031 | 190.5609 | [11 empty] | Bromideb, mg/L | 175.135 | 174.5385 |  | Bromideb, mg/L | 175.688 | 174.8107 | [11 empty] | Bromideb, mg/L | 189.4667 | 190.2713 |  | Bromideb, mg/L | 188.9312 | 190.0058
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 26 | [5 empty] | 1998-11-30 | 10:35 | 25124 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 7.2549 | 45.7451 | 0.32127 | 6.95 | 6.2 | 180 | 361 | 371 | 1319 | 1439.9839 | -9.1724 | 51.4825 | 905.4919 | 80.1213 | 91 | 72 | 19 | 25.9 | 15.6 | 41.5 | 41.5 | 0.49386 | 0.6241 | 16.65 | 16.4543 | 4.6302 | 57.8698 | 0.28433 | 6.21 |  | 160 | 413 | 769 | 833.0449 | -8.3283 | 56.8733 | 623.0224 | 74.3187 | 72 | 57 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.839 | 32.661 | 0.34234 |  | 6.47 | 252 | 769 | 1319 | 1502.8065 | -13.9353 | 32.0755 | 1135.9032 | 77.815 | Alkb, mg/L CaCO3 | 93.5935 | 89.4327 |  | Alkb, mg/L CaCO3 | 96.3295 | 91.1135 | [11 empty] | Alkb, mg/L CaCO3 | 84.206 | 80.9821 |  | Alkb, mg/L CaCO3 | 87.3265 | 82.4501 | [11 empty] | Alkb, mg/L CaCO3 | 81.9996 | 78.8186 |  | Alkb, mg/L CaCO3 | 84.608 | 80.0455 | [11 empty] | Alkb, mg/L CaCO3 | 73.9149 | 71.8331 |  | Alkb, mg/L CaCO3 | 75.0227 | 72.4591 | [11 empty] | Alkb, mg/L CaCO3 | 88.5128 | 84.0389 |  | Alkb, mg/L CaCO3 | 92.6599 | 86.0802 | [11 empty] | Alkb, mg/L CaCO3 | 87.6665 | 83.6433 |  | Alkb, mg/L CaCO3 | 90.3439 | 84.9709
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 60.219 | [5 empty] | 1998-12-01 | 10:10 | 25147 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 6.9448 | 46.0552 | 0.31911 | 6.92 | 6.14 | 194 | 352 | 379 | 1261 | 1397.9683 | -10.8619 | 48.8127 | 888.4841 | 78.1651 | 91 | 72 | 20 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3908 | 4.3958 | 57.1042 | 0.28703 | 6.15 |  | 169 | 411 | 751 | 806.1646 | -7.3455 | 55.409 | 608.5823 | 72.2305 | 72 | 57 | 22 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 8.0505 | 34.4495 | 0.32457 |  | 6.4 | 277 | 751 | 1261 | 1413.0952 | -12.0615 | 26.9129 | 1082.0476 | 74.4004 | T-Hdb, mg/L CaCO3 | 131.1987 | 119.583 |  | T-Hdb, mg/L CaCO3 | 138.8364 | 124.2753 | [11 empty] | T-Hdb, mg/L CaCO3 | 117.0507 | 105.0763 |  | T-Hdb, mg/L CaCO3 | 128.6413 | 110.5291 | [11 empty] | T-Hdb, mg/L CaCO3 | 115.2984 | 104.0062 |  | T-Hdb, mg/L CaCO3 | 124.5584 | 108.3614 | [11 empty] | T-Hdb, mg/L CaCO3 | 128.2311 | 116.4095 |  | T-Hdb, mg/L CaCO3 | 134.5219 | 119.9644 | [11 empty] | T-Hdb, mg/L CaCO3 | 123.4103 | 111.1071 |  | T-Hdb, mg/L CaCO3 | 134.8148 | 116.7205 | [11 empty] | T-Hdb, mg/L CaCO3 | 124.5329 | 111.6585 |  | T-Hdb, mg/L CaCO3 | 133.1004 | 115.907
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 35.9667 | [5 empty] | 1998-12-02 | 9:30 | 25170 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 7.065 | 45.935 | 0.31994 | 6.9 | 6.1 | 190 | 354 | 376 | 1273 | 1417 | -11.3119 | 49.4681 | 896.5 | 78.8065 | 91 | 72 | 19 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3908 | 4.4322 | 58.0678 | 0.28227 | 6.12 |  | 167 | 411 | 755 | 809.4304 | -7.2093 | 55.5851 | 610.2152 | 72.6326 | 72 | 57 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.2748 | 34.2252 | 0.3267 |  | 6.43 | 271 | 755 | 1273 | 1441.9677 | -13.2732 | 27.9255 | 1098.4839 | 75.3296 | Ca-Hdb, mg/L CaCO3 | 123.515 | 111.726 |  | Ca-Hdb, mg/L CaCO3 | 131.2668 | 116.4883 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 114.0955 | 103.6563 |  | Ca-Hdb, mg/L CaCO3 | 124.2001 | 108.41 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 107.2984 | 96.0062 |  | Ca-Hdb, mg/L CaCO3 | 116.5584 | 100.3614 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 105.4895 | 92.9988 |  | Ca-Hdb, mg/L CaCO3 | 112.1363 | 96.7548 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 112.9983 | 101.9627 |  | Ca-Hdb, mg/L CaCO3 | 123.2278 | 106.9978 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 117.0729 | 104.4399 |  | Ca-Hdb, mg/L CaCO3 | 125.4797 | 108.6088
|  |  |  | Required influent pressure to the system, PI (psi) | 106.1856 | [5 empty] | 1998-12-03 | 9:25 | 25194 | 25.3 | 91 | 57 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.7826 | 6.9595 | 46.0405 | 0.32108 | 6.93 | 6.06 | 186 | 356 | 371 | 1257 | 1392.9048 | -10.8118 | 49.8652 | 881.9524 | 78.9104 | 91 | 72 | 19 | 26 | 15.5 | 41.5 | 41.5 | 0.493 | 0.62651 | 16.7143 | 16.5667 | 4.4681 | 58.0319 | 0.28548 | 6.12 |  | 162 | 405 | 743 | 812.6129 | -9.3692 | 56.3342 | 608.8065 | 73.3906 | 72 | 57 | 22 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 8.1354 | 34.3646 | 0.32634 |  | 6.36 | 264 | 743 | 1257 | 1412.0794 | -12.3373 | 28.841 | 1077.5397 | 75.4997 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-12-04 | 8:40 | 25218 | 25.4 | 91 | 57 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.7847 | 46.2153 | 0.31709 | 6.87 | 5.96 | 183 | 350 | 362 | 1279 | 1360.9355 | -6.4062 | 49.4475 | 861.4677 | 78.7572 | 91 | 72 | 19 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.3908 | 4.4448 | 58.0552 | 0.28233 | 6.06 |  | 161 | 405 | 747 | 805.9682 | -7.894 | 55.5249 | 605.4841 | 73.4097 | 72 | 57 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.3603 | 34.1397 | 0.32752 |  | 6.3 | 258 | 747 | 1279 | 1441.0645 | -12.6712 | 28.7293 | 1094.0323 | 76.4175 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-12-05 | 6:05 | 25239 | 25.3 | 92 | 57 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 6.6055 | 46.8945 | 0.31433 | 6.88 | 5.98 | 181 | 342 | 359 | 1259 | 1324.0938 | -5.1703 | 49.5822 | 841.5469 | 78.492 | 92 | 72 | 20 | 25.9 | 15.8 | 41.7 | 41.7 | 0.49732 | 0.6211 | 16.65 | 16.503 | 4.4581 | 57.5419 | 0.2868 | 6.05 |  | 160 | 405 | 747 | 806.6139 | -7.9804 | 55.4318 | 605.807 | 73.5889 | 72 | 57 | 22 | 8.7 | 6.4 | 15.1 | 15.1 | 0.37191 | 0.57616 | 11.1857 | 11.087 | 8.2641 | 34.2359 | 0.32384 |  | 6.27 | 255 | 747 | 1258 | 1415.8125 | -12.5447 | 28.9694 | 1081.4062 | 76.4196 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1998-12-06 | 10:50 | 25268 | 25.4 | 92 | 57 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.739 | 6.1695 | 47.3305 | 0.31141 | 6.94 | 6.22 | 203 | 352 | 367 | 1201 | 1272.9048 | -5.9871 | 44.6866 | 819.9524 | 75.2425 | 92 | 72 | 19 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3908 | 4.1052 | 58.8948 | 0.27831 | 6.32 |  | 175 | 401 | 726 | 770.038 | -6.0658 | 52.3161 | 585.519 | 70.112 | 72 | 57 | 22 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3084 | 7.3714 | 35.1286 | 0.32191 |  | 6.48 | 294 | 726 | 1201 | 1336.2857 | -11.2644 | 19.891 | 1031.1429 | 71.4879 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1998-12-08 | 9:45 | 25314 | 25.4 | 91 | 57 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 6.7991 | 46.2009 | 0.3181 | 6.93 | 6.08 | 190 | 353 | 369 | 1255 | 1370.8226 | -9.2289 | 48.5095 | 869.9113 | 78.1587 | 91 | 72 | 20 | 25.9 | 15.7 | 41.6 | 41.6 | 0.49559 | 0.6226 | 16.65 | 16.4543 | 4.3796 | 57.1204 | 0.28806 | 6.2 |  | 165 | 405 | 745 | 800.9236 | -7.5065 | 55.2846 | 602.9618 | 72.6351 | 72 | 57 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.0868 | 34.4132 | 0.32491 |  | 6.39 | 272 | 745 | 1255 | 1416.3548 | -12.857 | 26.2873 | 1080.6774 | 74.8306 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1998-12-09 | 10:10 | 25339 | 25.4 | 92 | 59 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 6.5319 | 47.9681 | 0.30638 | 6.91 | 6.03 | 189 | 350 | 363 | 1232 | 1321.381 | -7.2549 | 47.9339 | 842.1905 | 77.5585 | 92 | 73 | 19 | 25.8 | 16.3 | 42.1 | 42.1 | 0.50511 | 0.61283 | 16.5857 | 16.3908 | 4.2277 | 59.2723 | 0.27653 | 6.19 |  | 164 | 400 | 729 | 773.546 | -6.1106 | 54.8209 | 586.773 | 72.0505 | 73 | 59 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 7.8297 | 35.1703 | 0.31792 |  | 6.34 | 268 | 729 | 1232 | 1372.9365 | -11.4397 | 26.1708 | 1050.9683 | 74.4997 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1998-12-10 | 10:08 | 25361 | 25.4 | 93 | 59 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.739 | 6.0616 | 48.9384 | 0.30117 | 6.81 | 5.99 | 188 | 327 | 351 | 1210 | 1237.3125 | -2.2572 | 46.4387 | 794.1562 | 76.3271 | 93 | 73 | 19 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.3908 | 4.2447 | 59.7553 | 0.2743 | 6.18 |  | 163 | 398 | 723 | 776.9375 | -7.4602 | 53.5613 | 587.4688 | 72.2538 | 73 | 58 | 22 | 8.9 | 6.4 | 15.3 | 15.3 | 0.37537 | 0.5817 | 11.4429 | 11.3084 | 7.7306 | 35.7694 | 0.31615 |  | 6.35 | 267 | 723 | 1210 | 1357.125 | -12.1591 | 23.9316 | 1040.0625 | 74.3285 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1998-12-11 | 9:25 | 25386 | 25.4 | 94 | 59 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.739 | 6.0616 | 49.4384 | 0.29813 | 6.87 | 6.07 | 194 | 343 | 357 | 1242 | 1243.3125 | -0.10568 | 45.6583 | 800.1562 | 75.7547 | 94 | 74 | 20 | 25.8 | 16.1 | 41.9 | 41.9 | 0.50165 | 0.61575 | 16.5857 | 16.3908 | 4.323 | 59.677 | 0.27466 | 6.2 |  | 169 | 409 | 743 | 793.5963 | -6.8097 | 52.6611 | 601.2981 | 71.8941 | 74 | 59 | 23 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.1813 | 7.8637 | 35.6362 | 0.31376 |  | 6.36 | 277 | 743 | 1242 | 1383.75 | -11.413 | 22.409 | 1063.375 | 73.9509 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1998-12-12 | 9:20 | 25410 | 25.3 | 94 | 59 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.7826 | 6.5078 | 48.9922 | 0.30173 | 6.87 | 6.1 | 194 | 362 | 369 | 1251 | 1320.5625 | -5.5606 | 47.4255 | 844.7812 | 77.0355 | 94 | 74 | 20 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.4393 | 4.3711 | 59.6289 | 0.27569 | 6.21 |  | 169 | 411 | 747 | 801.225 | -7.259 | 54.2005 | 606.1125 | 72.1174 | 74 | 59 | 23 | 8.9 | 6.4 | 15.3 | 15.3 | 0.37537 | 0.5817 | 11.4429 | 11.3418 | 7.951 | 35.549 | 0.31905 |  | 6.35 | 278 | 747 | 1251 | 1399.2031 | -11.8468 | 24.6612 | 1073.1016 | 74.0938 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1998-12-13 | 10:05 | 25437 | 25.4 | 93 | 59 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 6.7231 | 49.2769 | 0.29825 | 6.89 | 6.18 | 194 | 360 | 371 | 1265 | 1361.629 | -7.6387 | 47.7089 | 866.3145 | 77.6063 | 93 | 73 | 19 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3908 | 4.3958 | 59.6042 | 0.27499 | 6.24 |  | 169 | 411 | 751 | 806.1646 | -7.3455 | 54.4474 | 608.5823 | 72.2305 | 73 | 59 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.121 | 35.879 | 0.31164 |  | 6.35 | 276 | 751 | 1265 | 1425.1935 | -12.6635 | 25.6065 | 1088.0968 | 74.6346 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1998-12-14 | 10:40 | 25459 | 25.4 | 94 | 60 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 7.2323 | 48.7677 | 0.30223 | 6.8 | 5.99 | 189 | 362 | 379 | 1283 | 1445.4516 | -12.6619 | 50.1319 | 912.2258 | 79.2814 | 94 | 74 | 19 | 25.9 | 15.6 | 41.5 | 41.5 | 0.49386 | 0.6241 | 16.65 | 16.4543 | 4.4838 | 60.5162 | 0.2719 | 6.25 |  | 166 | 411 | 751 | 817.7628 | -8.8899 | 56.2005 | 614.3814 | 72.981 | 74 | 60 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.2406 | 36.7594 | 0.30418 |  | 6.3 | 269 | 751 | 1283 | 1435.129 | -11.8573 | 29.0237 | 1093.0645 | 75.3903 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1998-12-15 | 10:10 | 25483 | 25.3 | 94 | 60 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.7826 | 7.2605 | 48.7395 | 0.3033 | 6.8 | 5.97 | 188 | 368 | 381 | 1289 | 1447.0952 | -12.265 | 50.6562 | 914.0476 | 79.4321 | 94 | 75 | 19 | 25.9 | 15.6 | 41.5 | 41.5 | 0.49386 | 0.6241 | 16.65 | 16.503 | 4.5387 | 60.9613 | 0.27071 | 6.26 |  | 164 | 412 | 758 | 823.7436 | -8.6733 | 56.9554 | 617.8718 | 73.4573 | 75 | 60 | 22 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 8.3562 | 37.1438 | 0.30192 |  | 6.26 | 266 | 758 | 1289 | 1445.2381 | -12.1209 | 30.1837 | 1101.619 | 75.8537
[11 empty] | 1998-12-16 | 9:30 | 25506 | 25.2 | 94 | 60 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 6.8371 | 49.1629 | 0.30071 | 6.77 | 6.05 | 195 | 368 | 375 | 1265 | 1382.4194 | -9.2822 | 48 | 878.7097 | 77.8084 | 94 | 75 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.488 | 4.3538 | 60.1462 | 0.27413 | 6.1 |  | 170 | 409 | 747 | 801.7516 | -7.3295 | 54.6667 | 605.3758 | 71.9183 | 75 | 60 | 23 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2476 | 7.95 | 36.55 | 0.30773 |  | 6.31 | 282 | 747 | 1265 | 1407 | -11.2253 | 24.8 | 1077 | 73.8162
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on E23: S Allgeier (10/4/99): Reviewer replaced value of 29.2 ft with 14 ft -- a value more typical for this membrane.
Note on AR6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on BP6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on CU17: C. Rice: Consultant stated that the TDS values for the biweekly sampling are lower than the operational TDS values because the operational TDS values were recorded by an in-line conductivity probe; the biweekly TDS measurements were taken with a laboratory TDS meter.
Note on DR23: C. Rice: Consultant stated that although the low feed UV254 value for week 4 is inconsistent with Stage 1 influent values, the contract lab QC report confirms the reading.

## NF200. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Week 12 | [9 empty] | Field 2-7: System And Stage Water Quality For Week 12 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Boca Raton | Membrane manufacturer | FilmTec Corporation | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 226 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500130 | Membrane trade name | FILMTEC | Temperature normalized MTCW (gfd/psi) | 0.274 | Calcium Hardness (mg/L as CaCO3) | 216 | Dual Media Filtration | Silica/Garnet | Pilot-Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 42 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.4 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.7 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.4 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.6 | [6 empty] | System feed flow rate during sample collection (gpm) | 42.2 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.6 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.4 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.4 |  |  |  |  | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Membrane element model number | NF200-4040 |  |  | LSI | 0.06 | Scale Inhibitor Addition | Calgon EL-5600 4.0 mg/l | Pilot-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 42 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 42 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.7 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 42.2 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 42.2 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 |  |  |  |  | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 nominal | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.26 | pH Adjustment | sulfuric acid to pH 6.0-6.4 | Pilot-Scale | 1998-12-17 | 9:00 | 25530 | 25.3 | 95 | 59 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 6.7168 | 49.2832 | 0.29909 | 6.9 | 6.1 | 196 | 360 | 377 | 1246 | 1358.3594 | -9.0176 | 48.0106 | 867.6797 | 77.411 | 95 | 74 | 20 | 25.8 | 15.9 | 41.7 | 41.7 | 0.49819 | 0.61871 | 16.5857 | 16.4393 | 4.3291 | 60.1709 | 0.27321 | 6.08 |  | 171 | 410 | 747 | 797.8113 | -6.8021 | 54.6419 | 603.9057 | 71.6843 | 74 | 59 | 22 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.2144 | 7.8469 | 36.6531 | 0.30596 |  | 6.39 | 282 | 747 | 1246 | 1386.375 | -11.2661 | 25.1989 | 1066.6875 | 73.563 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.28 | Cartridge Filtration | 5 um exclusion size | Pilot-Scale | 1998-12-18 | 9:35 | 25554 | 25.2 | 95 | 60 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7838 | 6.5319 | 49.9681 | 0.29586 | 6.83 | 6.06 | 193 | 360 | 367 | 1275 | 1325.381 | -3.9514 | 47.4114 | 846.1905 | 77.1919 | 95 | 75 | 19 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.488 | 4.414 | 61.586 | 0.26772 | 6.01 |  | 168 | 411 | 751 | 807.7975 | -7.5629 | 54.2234 | 609.3987 | 72.4318 | 75 | 60 | 23 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2476 | 8.0505 | 36.4495 | 0.30858 |  | 6.33 | 277 | 751 | 1275 | 1413.0952 | -10.831 | 24.5232 | 1082.0476 | 74.4004 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 16.5 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 1998-12-19 | 9:12 | 25580 | 25.3 | 101 | 66 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 7.3084 | 55.1916 | 0.26784 | 6.78 | 5.83 | 173 | 356 | 365 | 1350 | 1442.6774 | -6.865 | 52.6027 | 903.8387 | 80.8594 | 101 | 81 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2481 | 4.6769 | 67.3231 | 0.24135 | 5.72 |  | 154 | 415 | 761 | 828.3851 | -8.8548 | 57.8082 | 621.6925 | 75.2289 | 81 | 66 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8516 | 9.205 | 41.295 | 0.287 |  | 6.16 | 235 | 761 | 1350 | 1550 | -14.8148 | 35.6164 | 1155.5 | 79.6625 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | hydrophylic | Number of elements per pressure vessel, Ne | 7 | Total aluminum (mg/L) | <0.10 |  |  |  | 1998-12-20 | 8:05 | 25600 | 25.3 | 102 | 66 | 21 | 0 | 34.6 | 6.5 |  | 41.1 | 41.1 | 0.84185 | 0 | 14.8286 | 14.6977 | 7.6526 | 55.3474 | 0.26555 | 6.8 | 5.77 | 167 | 358 | 376 | 1325 | 1488.5231 | -12.3414 | 55.5851 | 932.2615 | 82.0866 | 102 | 82 | 19 | 25.4 | 16.7 | 42.1 | 42.1 | 0.50857 | 0.60333 | 16.3286 | 16.1844 | 4.6477 | 68.3523 | 0.23678 | 5.72 |  | 150 | 414 | 758 | 815.5329 | -7.5901 | 60.1064 | 614.7665 | 75.6005 | 82 | 66 | 23 | 9.1 | 6.5 | 15.6 | 15.6 | 0.38229 | 0.58333 | 11.7 | 11.5967 | 9.061 | 41.939 | 0.27651 |  | 6.04 | 225 | 758 | 1325 | 1504.2 | -13.5245 | 40.1596 | 1131.1 | 80.1079 | Sampling date | MM/DD/YY | 1998-12-28 | 1998-12-28 | 1998-12-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-28 | 1998-12-28 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-01-13 | 1998-01-13 | 1998-01-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-13 | 1999-01-13 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-27 | 1999-01-27 | 1999-01-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-27 | 1999-01-27 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-10 | 1999-02-10 | 1999-02-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-10 | 1999-02-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 13
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 4 | Fluoride (mg/L) | 0.25 |  |  |  | 1998-12-21 | 9:50 | 25626 | 25.4 | 102 | 67 | 21 | 0 | 34.7 | 6.1 |  | 40.8 | 40.8 | 0.85049 | 0 | 14.8714 | 14.6966 | 7.9192 | 55.5808 | 0.26442 | 6.75 | 5.82 | 171 | 364 | 377 | 1357 | 1548.8361 | -14.1368 | 54.6419 | 962.918 | 82.2415 | 102 | 82 | 19 | 25.4 | 16.2 | 41.6 | 41.6 | 0.49992 | 0.61058 | 16.3286 | 16.1366 | 4.674 | 68.326 | 0.23617 | 5.76 |  | 152 | 414 | 762 | 824.7901 | -8.2402 | 59.6817 | 619.3951 | 75.4599 | 82 | 67 | 23 | 9.1 | 6.1 | 15.2 | 15.2 | 0.36845 | 0.59868 | 11.7 | 11.5625 | 9.2533 | 42.2467 | 0.27369 |  | 6.11 | 232 | 762 | 1357 | 1552.6557 | -14.4183 | 38.4615 | 1157.3279 | 79.9538 | Sampling time | hh:mm | 7:20 | 7:25 | 7:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:50 | 7:55 | 8:10 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:10 | 7:55 | --- | --- | --- | --- | Sampling time | hh:mm | 7:20 | 7:25 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:20 | 7:25 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:05 | 7:15 | 7:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:15 | --- | --- | --- | --- | Sampling time | hh:mm | 7:05 | 7:15 | 7:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:15 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5999
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 2 | Phosphate (mg/L) | 0.56 |  |  |  | 1998-12-22 | 7:58 | 25648 | 25.4 | 104 | 68 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 6.9131 | 58.0869 | 0.25301 | 6.83 | 6.06 | 193 | 363 | 375 | 1272 | 1393.6129 | -9.5608 | 48.5333 | 884.3065 | 78.175 | 104 | 83 | 19 | 25.4 | 16.6 | 42 | 42 | 0.50684 | 0.60476 | 16.3286 | 16.1366 | 4.2891 | 70.2109 | 0.22983 | 6.05 |  | 167 | 410 | 737 | 781.8193 | -6.0813 | 55.4667 | 595.9096 | 71.9756 | 83 | 68 | 24 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.6895 | 8.1 | 43.4 | 0.26934 |  | 6.37 | 272 | 737 | 1272 | 1427 | -12.1855 | 27.4667 | 1082 | 74.8614 | Operation time | hh.hh | 25792 | 25792 | 25792 | --- | --- | --- | --- | --- | Operation time | hh.hh | 25792 | 25792 | --- | --- | --- | --- | Operation time | hh.hh | 26176 | 26176 | 26176 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26176 | 26176 | --- | --- | --- | --- | Operation time | hh.hh | 26508 | 26508 | 26508 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26508 | 26508 | --- | --- | --- | --- | Operation time | hh.hh | 26816 | 26816 | 26816 | --- | --- | --- | --- | --- | Operation time | hh.hh | 26816 | 26816 | --- | --- | --- | --- | Operation time | hh.hh | 27147 | 27147 | 27147 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27147 | 27147 | --- | --- | --- | --- | Operation time | hh.hh | 27147 | 27147 | 27147 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27147 | 27147 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.91667 | Sulfate (mg/L) | 14.9 |  |  |  | 1998-12-23 | 8:55 | 25673 | 25.4 | 103 | 67 | 21 | 0 | 34.7 | 6.5 |  | 41.2 | 41.2 | 0.84223 | 0 | 14.8714 | 14.6966 | 6.8615 | 57.1385 | 0.25721 | 6.73 | 5.95 | 192 | 366 | 379 | 1265 | 1377.2923 | -8.8769 | 49.3404 | 878.1462 | 78.1358 | 103 | 83 | 19 | 25.5 | 16.6 | 42.1 | 42.1 | 0.5077 | 0.6057 | 16.3929 | 16.2002 | 4.3848 | 69.6152 | 0.23271 | 5.97 |  | 167 | 415 | 744 | 795.9639 | -6.9844 | 55.9367 | 605.4819 | 72.4187 | 83 | 67 | 23 | 9.1 | 6.5 | 15.6 | 15.6 | 0.38229 | 0.58333 | 11.7 | 11.5625 | 8.092 | 43.908 | 0.26333 |  | 6.34 | 268 | 744 | 1265 | 1410.4 | -11.4941 | 29.2876 | 1077.2 | 75.1207 | pH | --- | 6.33 | 6.38 | 6.6 | --- | --- | --- | --- | --- | pH | --- | 6.31 | 6.31 | --- | --- | --- | --- | pH | --- | 6.64 | 6.69 | 7.06 | --- | --- | --- | --- | --- | pH | --- | 6.65 | 6.74 | --- | --- | --- | --- | pH | --- | 6.31 | 6.44 | 6.83 | --- | --- | --- | --- | --- | pH | --- | 6.41 | 6.49 | --- | --- | --- | --- | pH | --- | 6.78 | 6.64 | 6.85 | --- | --- | --- | --- | --- | pH | --- | 6.78 | 6.61 | --- | --- | --- | --- | pH | --- | 6.62 | 6.65 | 6.93 | --- | --- | --- | --- | --- | pH | --- | 6.74 | 6.66 | --- | --- | --- | --- | pH | --- | 6.61 | 6.63 | 6.96 | --- | --- | --- | --- | --- | pH | --- | 6.64 | 6.66 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 17
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 6.4167 | Calcium (mg/L) | 95 |  |  |  | 1998-12-24 | 7:10 | 25695 | 25.2 | 103 | 67 | 21 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.7412 | 6.9248 | 57.0752 | 0.25828 | 6.7 | 5.9 | 192 | 364 | 379 | 1273 | 1389.9688 | -9.1884 | 49.3404 | 884.4844 | 78.2924 | 103 | 83 | 19 | 25.5 | 16.5 | 42 | 42 | 0.50597 | 0.60714 | 16.3929 | 16.2962 | 4.3964 | 69.6036 | 0.23413 | 5.98 |  | 167 | 415 | 743 | 798.2727 | -7.4391 | 55.9367 | 606.6364 | 72.4712 | 83 | 67 | 23 | 9.1 | 6.4 | 15.5 | 15.5 | 0.37883 | 0.5871 | 11.7 | 11.631 | 8.127 | 43.873 | 0.26511 |  | 6.31 | 268 | 743 | 1273 | 1418.3906 | -11.4211 | 29.2876 | 1080.6953 | 75.2012 | Temperature | oC | 25.7 | 25.5 | 25.7 | --- | --- | --- | --- | --- | Temperature | oC | 25.3 | 25.5 | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | 25.8 | --- | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.5 | --- | --- | --- | --- | Temperature | oC | 25.7 | 25.5 | 25.8 | --- | --- | --- | --- | --- | Temperature | oC | 25.6 | 25.5 | --- | --- | --- | --- | Temperature | oC | 25.7 | 25.4 | 25.6 | --- | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | --- | Temperature | oC | 25 | 24.3 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 25.2 | 24.3 | --- | --- | --- | --- | Temperature | oC | 25 | 24.3 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 25.2 | 24.3 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 25.6667 | Barium (mg/L) | 0.021 |  |  |  | 1998-12-25 | 8:00 | 25721 | 25.2 | 103 | 67 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7838 | 6.9448 | 57.0552 | 0.25911 | 6.68 | 5.81 | 190 | 360 | 375 | 1275 | 1393.9683 | -9.3308 | 49.3333 | 884.4841 | 78.5186 | 103 | 83 | 19 | 25.4 | 16.6 | 42 | 42 | 0.50684 | 0.60476 | 16.3286 | 16.2323 | 4.3244 | 69.6756 | 0.23297 | 5.94 |  | 166 | 411 | 740 | 785.8795 | -6.1999 | 55.7333 | 598.4398 | 72.2612 | 83 | 67 | 23 | 9.2 | 6.3 | 15.5 | 15.5 | 0.3771 | 0.59355 | 11.8286 | 11.7589 | 8.2356 | 43.7644 | 0.26869 |  | 6.26 | 264 | 740 | 1275 | 1435.1111 | -12.5577 | 29.6 | 1087.5556 | 75.7254 | Alkalinity | mg/L as CaCO3 | 78 | 120 | 290 | 358 | -23.4483 | 35 | 239 | 67.364 | Alkalinity | mg/L as CaCO3 | 64 | 120 | 205.6867 | 46.6667 | 162.8434 | 60.6984 | Alkalinity | mg/L as CaCO3 | 92 | 142 | 374 | 404.5 | -8.1551 | 35.2113 | 273.25 | 66.3312 | Alkalinity | mg/L as CaCO3 | 74 | 142 | 247.9632 | 47.8873 | 194.9816 | 62.0477 | Alkalinity | mg/L as CaCO3 | 84 | 120 | 304 | 309 | -1.6447 | 30 | 214.5 | 60.8392 | Alkalinity | mg/L as CaCO3 | 66 | 118 | 201.2 | 45 | 159.6 | 58.6466 | Alkalinity | mg/L as CaCO3 | 132 | 150 | 310 | 244.5 | 21.129 | 12 | 197.25 | 33.0798 | Alkalinity | mg/L as CaCO3 | 110 | 165 | 249.8193 | 26.6667 | 207.4096 | 46.9649 | Alkalinity | mg/L as CaCO3 | 127 | 171 | 365 | 402 | -10.137 | 25.731 | 286.5 | 55.6719 | Alkalinity | mg/L as CaCO3 | 100 | 170 | 280.4348 | 41.5205 | 225.2174 | 55.5985 | Alkalinity | mg/L as CaCO3 | 124 | 170 | 372 | 411.5 | -10.6183 | 27.0588 | 290.75 | 57.3517 | Alkalinity | mg/L as CaCO3 | 103 | 170 | 275.7019 | 39.4118 | 222.8509 | 53.7808 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 27.8 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.8333 | Strontium (mg/L) | 0.53 |  |  |  | 1998-12-26 | 7:00 | 25743 | 25.2 | 104 | 68 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 7.027 | 57.973 | 0.25501 | 6.87 | 5.99 | 188 | 359 | 373 | 1276 | 1408.4032 | -10.3764 | 49.5979 | 890.7016 | 78.893 | 104 | 84 | 19 | 25.5 | 16 | 41.5 | 41.5 | 0.49732 | 0.61446 | 16.3929 | 16.2962 | 4.4023 | 70.5977 | 0.23083 | 5.98 |  | 164 | 409 | 739 | 799.4688 | -8.1825 | 56.0322 | 604.2344 | 72.8582 | 84 | 68 | 23 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 8.309 | 44.691 | 0.26311 |  | 6.43 | 262 | 739 | 1276 | 1446.8065 | -13.3861 | 29.7587 | 1092.9032 | 76.0272 | Total dissolved solids | mg/L | 177 | 376 | 1120 | 1503.6667 | -34.256 | 52.9255 | 939.8333 | 81.1669 | Total dissolved solids | mg/L | 152 | 375 | 716.2169 | 59.5745 | 545.6084 | 72.1412 | Total dissolved solids | mg/L | 193 | 361 | 1050 | 1243 | -18.381 | 46.5374 | 802 | 75.9352 | Total dissolved solids | mg/L | 165 | 361 | 666.4233 | 54.2936 | 513.7117 | 67.8808 | Total dissolved solids | mg/L | 185 | 374 | 1120 | 1366.25 | -21.9866 | 50.5348 | 870.125 | 78.7387 | Total dissolved solids | mg/L | 158 | 374 | 719.6 | 57.754 | 546.8 | 71.1046 | Total dissolved solids | mg/L | 240 | 368 | 872 | 1040 | -19.2661 | 34.7826 | 704 | 65.9091 | Total dissolved solids | mg/L | 216 | 363 | 589.6988 | 41.3043 | 476.3494 | 54.6551 | Total dissolved solids | mg/L | 229 | 365 | 923 | 1079 | -16.9014 | 37.2603 | 722 | 68.2825 | Total dissolved solids | mg/L | 208 | 367 | 617.8447 | 43.0137 | 492.4224 | 57.7598 | Total dissolved solids | mg/L | 229 | 363 | 925 | 1066.5 | -15.2973 | 36.9146 | 714.75 | 67.9608 | Total dissolved solids | mg/L | 204 | 365 | 619 | 43.8017 | 492 | 58.5366 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 38.5 | Reactive silica (mg/L as SiO2) | 9.4 |  |  |  | 1998-12-27 | 7:55 | 25768 | 25.3 | 104 | 68 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.7826 | 7.14 | 57.86 | 0.25549 | 6.76 | 6 | 188 | 371 | 380 | 1279 | 1424 | -11.337 | 50.5263 | 902 | 79.1574 | 104 | 84 | 19 | 25.5 | 16.2 | 41.7 | 41.7 | 0.50078 | 0.61151 | 16.3929 | 16.2481 | 4.4497 | 70.5503 | 0.23031 | 6 |  | 164 | 413 | 743 | 804.9444 | -8.3371 | 56.8421 | 608.9722 | 73.0694 | 84 | 68 | 23 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.7241 | 8.2672 | 44.7328 | 0.26209 |  | 6.29 | 262 | 743 | 1279 | 1434.4375 | -12.153 | 31.0526 | 1088.7188 | 75.935 | Total hardness | mg/L as CaCO3 | 94 | 280 | 1070 | 1334 | -24.6729 | 66.4286 | 807 | 88.3519 | Total hardness | mg/L as CaCO3 | 78 | 270 | 563.7831 | 72.1429 | 416.8916 | 81.2901 | Total hardness | mg/L as CaCO3 | 112 | 282 | 980 | 1174.5 | -19.8469 | 60.2837 | 728.25 | 84.6207 | Total hardness | mg/L as CaCO3 | 88 | 246 | 492.2086 | 68.7943 | 369.1043 | 76.1585 | Total hardness | mg/L as CaCO3 | 100 | 260 | 1080 | 1100 | -1.8519 | 61.5385 | 680 | 85.2941 | Total hardness | mg/L as CaCO3 | 86 | 256 | 528 | 66.9231 | 392 | 78.0612 | Total hardness | mg/L as CaCO3 | 154 | 265 | 800 | 847.75 | -5.9687 | 41.8868 | 556.375 | 72.3208 | Total hardness | mg/L as CaCO3 | 124 | 250 | 444.3133 | 53.2075 | 347.1566 | 64.2813 | Total hardness | mg/L as CaCO3 | 142 | 262 | 840 | 892 | -6.1905 | 45.8015 | 577 | 75.3899 | Total hardness | mg/L as CaCO3 | 116 | 263 | 494.913 | 55.7252 | 378.9565 | 69.3896 | Total hardness | mg/L as CaCO3 | 140 | 265 | 850 | 921.25 | -8.3824 | 47.1698 | 593.125 | 76.3962 | Total hardness | mg/L as CaCO3 | 118 | 260 | 484.0248 | 55.4717 | 372.0124 | 68.2806 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.274 | Feed flow rate to system, QF-sys (gpm) | 45.2941 | Turbidity (ntu) | 1.14 |  |  |  | 1998-12-28 | 9:00 | 25793 | 25.3 | 104 | 68 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 7.1325 | 57.8675 | 0.25472 | 6.8 | 5.97 | 189 | 363 | 379 | 1297 | 1425.5079 | -9.9081 | 50.1319 | 902.254 | 79.0525 | 104 | 84 | 19 | 25.4 | 16.6 | 42 | 42 | 0.50684 | 0.60476 | 16.3286 | 16.1844 | 4.4127 | 70.5873 | 0.22928 | 5.98 |  | 165 | 415 | 751 | 797.5301 | -6.1958 | 56.4644 | 606.2651 | 72.7842 | 84 | 68 | 23 | 9.2 | 6.3 | 15.5 | 15.5 | 0.3771 | 0.59355 | 11.8286 | 11.7241 | 8.4086 | 44.5914 | 0.26292 |  | 6.26 | 265 | 751 | 1297 | 1460.7143 | -12.6225 | 30.0792 | 1105.8571 | 76.0367 | Calcium hardness | mg/L as CaCO3 | 90 | 240 | 1000 | 1090 | -9 | 62.5 | 665 | 86.4662 | Calcium hardness | mg/L as CaCO3 | 76 | 250 | 516.241 | 68.3333 | 383.1205 | 80.1629 | Calcium hardness | mg/L as CaCO3 | 98 | 230 | 860 | 923 | -7.3256 | 57.3913 | 576.5 | 83.0009 | Calcium hardness | mg/L as CaCO3 | 84 | 230 | 457.5092 | 63.4783 | 343.7546 | 75.564 | Calcium hardness | mg/L as CaCO3 | 94 | 234 | 880 | 969 | -10.1136 | 59.8291 | 601.5 | 84.3724 | Calcium hardness | mg/L as CaCO3 | 80 | 236 | 485.6 | 65.812 | 360.8 | 77.8271 | Calcium hardness | mg/L as CaCO3 | 136 | 240 | 760 | 786 | -3.4211 | 43.3333 | 513 | 73.4893 | Calcium hardness | mg/L as CaCO3 | 116 | 240 | 431.2289 | 51.6667 | 335.6145 | 65.4365 | Calcium hardness | mg/L as CaCO3 | 130 | 240 | 788 | 817.5 | -3.7437 | 45.8333 | 528.75 | 75.4137 | Calcium hardness | mg/L as CaCO3 | 113 | 244 | 450.6708 | 52.9167 | 347.3354 | 67.4666 | Calcium hardness | mg/L as CaCO3 | 130 | 238 | 786 | 805 | -2.4173 | 45.3782 | 521.5 | 75.0719 | Calcium hardness | mg/L as CaCO3 | 112 | 242 | 447.0932 | 52.9412 | 344.5466 | 67.4935 | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 6.7941 | SDI | >7.0 |  |  |  | 1998-12-29 | 9:33 | 25818 | 25.2 | 104 | 68 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7838 | 7.2363 | 57.7637 | 0.25594 | 6.778 | 5.8 | 186 | 365 | 381 | 1293 | 1438.2656 | -11.2348 | 51.1811 | 909.6328 | 79.5522 | 104 | 84 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2962 | 4.5157 | 70.4843 | 0.2312 | 5.97 |  | 163 | 415 | 751 | 814.1304 | -8.4062 | 57.2178 | 614.5652 | 73.4772 | 84 | 68 | 23 | 9.1 | 6.4 | 15.5 | 15.5 | 0.37883 | 0.5871 | 11.7 | 11.631 | 8.4349 | 44.5651 | 0.26099 |  | 6.28 | 258 | 751 | 1293 | 1451.9844 | -12.2958 | 32.2835 | 1101.4922 | 76.5772 | Turbidity | ntu | 0.04 | 0.15 | 0.59 | 0.77333 | -31.0734 | 73.3333 | 0.46167 | 91.3357 | Turbidity | ntu | 0.079 | 0.218 | 0.43069 | 47.3333 | 0.32434 | 75.6431 | Turbidity | ntu | 0.064 | 0.227 | 1.05 | 1.0828 | -3.119 | 71.8062 | 0.65487 | 90.2271 | Turbidity | ntu | 0.072 | 0.158 | 0.29201 | 68.2819 | 0.22501 | 68.0009 | Turbidity | ntu | 0.044 | 0.338 | 2.11 | 1.8815 | 10.8294 | 86.9822 | 1.1098 | 96.0351 | Turbidity | ntu | 0.063 | 0.883 | 2.195 | 81.3609 | 1.539 | 95.9064 | Turbidity | ntu | 0.05 | 0.22 | 0.79 | 1.1125 | -40.8228 | 77.2727 | 0.66625 | 92.4953 | Turbidity | ntu | 0.06 | 0.28 | 0.61928 | 72.7273 | 0.44964 | 86.6559 | Turbidity | ntu | 0.042 | 0.257 | 0.906 | 1.3858 | -52.9525 | 83.6576 | 0.82137 | 94.8866 | Turbidity | ntu | 0.086 | 0.291 | 0.61442 | 66.537 | 0.45271 | 81.0032 | Turbidity | ntu | 0.051 | 0.312 | 0.876 | 1.6823 | -92.0377 | 83.6538 | 0.99713 | 94.8853 | Turbidity | ntu | 0.051 | 0.253 | 0.57168 | 83.6538 | 0.41234 | 87.6316 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 18 |  |  | MFI |  |  |  |  | 1998-12-30 | 9:20 | 25842 | 25.2 | 106 | 70 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 3.9503 | 63.0497 | 0.23448 | 6.81 | 6.75 | 264 | 366 | 368 | 1022 | 950.0645 | 7.0387 | 28.2609 | 659.0323 | 59.9413 | 106 | 86 | 19 | 25.4 | 16.1 | 41.5 | 41.5 | 0.49819 | 0.61205 | 16.3286 | 16.2323 | 3.2378 | 73.7622 | 0.22006 | 6.92 |  | 220 | 401 | 666 | 686.5528 | -3.086 | 40.2174 | 543.7764 | 59.5422 | 86 | 70 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8867 | 4.8125 | 50.1875 | 0.23685 |  | 6.46 | 391 | 666 | 1022 | 1078.5 | -5.5284 | -6.25 | 872.25 | 55.1734 | Ammonia | mg NH3-N / L | 0.5 | 0.65 | 1.58 | 1.5 | 5.0633 | 23.0769 | 1.075 | 53.4884 | Total organic carbon | mg/L | 0.54 | 13.6 | 33.5834 | 96.0584 | 23.5917 | 97.7111 | Ammonia | mg NH3-N / L | 0.53 | 0.68 | 1.37 | 1.4675 | -7.1168 | 22.0588 | 1.0737 | 50.6403 | Total organic carbon | mg/L | 0.56 | 13.7 | 34.1758 | 96 | 23.9379 | 97.6606 | Ammonia | mg NH3-N / L | 0.5 | 0.64 | 1.44 | 1.375 | 4.5139 | 21.875 | 1.0075 | 50.3722 | Total organic carbon | mg/L | 0.6 | 14.7 | 37.26 | 96.0265 | 25.98 | 97.6905 | Ammonia | mg NH3-N / L | 0.5 | 0.58 | 1.08 | 1 | 7.4074 | 13.7931 | 0.79 | 36.7089 | Total organic carbon | mg/L | 0.65 | 15 | 37.1301 | 95.6954 | 26.0651 | 97.5062 | Ammonia | mg NH3-N / L | 0.48 | 0.61 | 1.17 | 1.2925 | -10.4701 | 21.3115 | 0.95125 | 49.5401 | Total organic carbon | mg/L | 0.51 | 13.4 | 33.7358 | 96.4085 | 23.5679 | 97.836 | Ammonia | mg NH3-N / L | 0.48 | 0.37 | 0.99 | -0.2075 | 120.9596 | -29.7297 | 0.08125 | -490.7692 | Total organic carbon | mg/L | 0.53 | 13.1 | 32.9309 | 95.9231 | 23.0155 | 97.6972
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-12-31 | 7:15 | 25864 | 25.2 | 106 | 69 | 22 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 6.8371 | 58.6629 | 0.25201 | 6.7 | 6.1 | 205 | 379 | 385 | 1225 | 1392.4194 | -13.6669 | 46.7532 | 888.7097 | 76.9328 | 106 | 85 | 19 | 25.4 | 16.5 | 41.9 | 41.9 | 0.50511 | 0.60621 | 16.3286 | 16.2323 | 4.088 | 72.412 | 0.22417 | 6.14 |  | 177 | 408 | 725 | 763.6 | -5.3241 | 54.026 | 585.8 | 69.7849 | 85 | 69 | 24 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 7.5077 | 45.4923 | 0.25848 |  | 6.45 | 294 | 725 | 1225 | 1364.5484 | -11.3917 | 23.6364 | 1044.7742 | 71.8599 | Total organic carbon | mg/L | 0.59 | 13.7 | 76 | 87.99 | -15.7763 | 95.6934 | 50.845 | 98.8396 | UV254 | cm-1 | BMRL | 0.388 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.98 | 14 | 79.5 | 82.355 | -3.5912 | 93 | 48.1775 | 97.9659 | UV254 | cm-1 | BMRL | 0.426 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.54 | 15.1 | 81.3 | 91.54 | -12.5953 | 96.4238 | 53.32 | 98.9872 | UV254 | cm-1 | BMRL | 0.447 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.64 | 15.1 | 79.7 | 91.015 | -14.197 | 95.7616 | 53.0575 | 98.7938 | UV254 | cm-1 | BMRL | 0.423 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.59 | 14.2 | 76.7 | 85.6525 | -11.6721 | 95.8451 | 49.9263 | 98.8183 | UV254 | cm-1 | BMRL | 0.439 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.8 | 13 | 79.8 | 77.05 | 3.4461 | 93.8462 | 45.025 | 98.2232 | UV254 | cm-1 | BMRL | 0.437 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Glades Road Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 14 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 23.2941 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1999-01-01 | 6:35 | 25889 | 25.3 | 106 | 69 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.7826 | 5.8756 | 60.6244 | 0.24384 | 6.69 | 6.12 | 204 | 364 | 362 | 1204 | 1221.125 | -1.4223 | 43.6464 | 791.5625 | 74.2282 | 106 | 85 | 19 | 25.5 | 16.4 | 41.9 | 41.9 | 0.50424 | 0.60859 | 16.3929 | 16.2481 | 4.0881 | 72.4119 | 0.22438 | 6.04 |  | 176 | 406 | 719 | 763.622 | -6.2061 | 51.3812 | 584.811 | 69.9048 | 85 | 69 | 24 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.7241 | 7.3563 | 45.6437 | 0.25686 |  | 6.47 | 291 | 719 | 1204 | 1334.25 | -10.8181 | 19.6133 | 1026.625 | 71.6547 | UV254 | cm-1 | BMRL | 0.44 | 2.22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.8529 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.401 | 2.529 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.11 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.435 | 2.634 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.0408 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.437 | 2.578 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.82 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.42 | 2.416 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.2761 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.422 | 2.555 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3359 | --- | --- | --- | ---
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0023 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 8.6275 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1999-01-02 | 9:10 | 25915 | 25.3 | 106 | 69 | 22 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 6.0142 | 59.4858 | 0.24851 | 6.7 | 6.12 | 206 | 355 | 364 | 1225 | 1250.8387 | -2.1093 | 43.4066 | 807.4194 | 74.4866 | 106 | 85 | 19 | 25.5 | 16.2 | 41.7 | 41.7 | 0.50078 | 0.61151 | 16.3929 | 16.2481 | 4.1459 | 72.3541 | 0.22456 | 6.03 |  | 178 | 410 | 726 | 775.1852 | -6.7748 | 51.0989 | 592.5926 | 69.9625 | 85 | 69 | 24 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7241 | 7.4903 | 45.5097 | 0.25762 |  | 6.54 | 296 | 726 | 1225 | 1364.0645 | -11.3522 | 18.6813 | 1045.0323 | 71.6755 | SUVA | L/(mg*m) | NR | 3.2117 | 2.9211 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.8643 | 3.1811 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.8808 | 3.2399 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.894 | 3.2346 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.9577 | 3.1499 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.2462 | 3.2018 | --- | --- | --- | --- | ---
Process Train Name | SOFT | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1999-01-03 | 8:10 | 25936 | 25.3 | 106 | 69 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 6.4193 | 60.0807 | 0.24534 | 6.75 | 5.97 | 205 | 362 | 374 | 1223 | 1319.8548 | -7.9194 | 45.1872 | 846.9274 | 75.7949 | 106 | 85 | 19 | 25.4 | 16.7 | 42.1 | 42.1 | 0.50857 | 0.60333 | 16.3286 | 16.1844 | 4.0667 | 72.4333 | 0.22344 | 6.11 |  | 177 | 408 | 722 | 759.3413 | -5.1719 | 52.6738 | 583.6707 | 69.6747 | 85 | 69 | 23 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7241 | 7.4555 | 46.5445 | 0.25189 |  | 6.46 | 294 | 722 | 1223 | 1357.0968 | -10.9646 | 21.3904 | 1039.5484 | 71.7185 | Bromide | mg/L | 175 | 172 | --- | 155 | --- | -1.7442 | 163.5 | -7.0336 | [8 empty] | Bromide | mg/L | 149 | 172 | --- | 292.75 | --- | 13.3721 | 232.375 | 35.8795 | [8 empty] | Bromide | mg/L | 173 | 174 | --- | 179.25 | --- | 0.57471 | 176.625 | 2.0524 | [8 empty] | Bromide | mg/L | 187 | 170 | --- | 80.75 | --- | -10 | 125.375 | -49.1525 | [8 empty] | Bromide | mg/L | 174 | 165 | --- | 117.75 | --- | -5.4545 | 141.375 | -23.0769 | [8 empty] | Bromide | mg/L | 174 | 166 | --- | 124 | --- | -4.8193 | 145 | -20
ICR Treatment Plant Identification Number | 306 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1999-01-04 | 7:45 | 25960 | 25.1 | 106 | 70 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.8275 | 6.4193 | 60.5807 | 0.24476 | 6.8 | 5.96 | 203 | 366 | 374 | 1247 | 1315.8571 | -5.5218 | 45.7219 | 844.9286 | 75.9743 | 106 | 86 | 19 | 25.6 | 16.3 | 41.9 | 41.9 | 0.50338 | 0.61098 | 16.4571 | 16.4086 | 4.2133 | 72.7867 | 0.22543 | 5.97 |  | 175 | 411 | 733 | 781.6503 | -6.6371 | 53.2086 | 596.3252 | 70.6536 | 86 | 70 | 24 | 9.1 | 6.3 | 15.4 | 15.4 | 0.37537 | 0.59091 | 11.7 | 11.6655 | 7.6467 | 46.3533 | 0.25166 |  | 6.41 | 289 | 733 | 1247 | 1374.3333 | -10.2112 | 22.7273 | 1053.6667 | 72.572 | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4500130 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -7.2941 | [5 empty] | 1999-01-05 | 9:00 | 25985 | 25.1 | 107 | 70 | 22 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.8703 | 6.4705 | 60.0295 | 0.24772 | 6.64 | 6.01 | 199 | 359 | 371 | 1275 | 1321.0952 | -3.6153 | 46.3612 | 846.0476 | 76.4789 | 107 | 86 | 19 | 25.6 | 16 | 41.6 | 41.6 | 0.49819 | 0.61538 | 16.4571 | 16.4086 | 4.356 | 73.144 | 0.22433 | 5.93 |  | 173 | 415 | 743 | 802.2 | -7.9677 | 53.3693 | 608.6 | 71.5741 | 86 | 70 | 24 | 9.1 | 6.3 | 15.4 | 15.4 | 0.37537 | 0.59091 | 11.7 | 11.6655 | 7.9394 | 46.0606 | 0.25326 |  | 6.4 | 282 | 743 | 1275 | 1408.8889 | -10.5011 | 23.9892 | 1075.9444 | 73.7905 | SDS-Free Cl2 residual | mg/L | 0.9 | 0.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.8 | 1.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.58 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.8 | 0.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 1.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -0.62745 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1999-01-06 | 9:40 | 26010 | 25.2 | 106 | 69 | 22 | 0 | 34.6 | 6.5 |  | 41.1 | 41.1 | 0.84185 | 0 | 14.8286 | 14.7412 | 4.8332 | 60.6668 | 0.24299 | 6.68 | 6.28 | 229 | 355 | 361 | 1121 | 1063.6462 | 5.1163 | 36.5651 | 712.3231 | 67.8517 | 106 | 85 | 19 | 25.3 | 16.5 | 41.8 | 41.8 | 0.50424 | 0.60526 | 16.2643 | 16.1684 | 3.6923 | 72.8077 | 0.22207 | 6.23 |  | 195 | 404 | 694 | 724.4667 | -4.39 | 45.9834 | 564.2333 | 65.4398 | 85 | 69 | 24 | 9.3 | 6.5 | 15.8 | 15.8 | 0.38575 | 0.58861 | 11.9571 | 11.8867 | 6.1925 | 46.8075 | 0.25395 |  | 6.66 | 333 | 694 | 1121 | 1210.5077 | -7.9846 | 7.7562 | 952.2538 | 65.0303 | SDS-Cl2 demand | mg/L | 4.6 | 19.6 | --- | 104.6 | --- | 76.5306 | 62.1 | 92.5926 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 9.2 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.7 | 18.4 | --- | 95.575 | --- | 79.8913 | 56.9875 | 93.5073 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 9.3 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.5 | 19.2 | --- | 96.375 | --- | 76.5625 | 57.7875 | 92.2128 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 9.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.7 | 19.4 | --- | 96.575 | --- | 75.7732 | 57.9875 | 91.8948 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 9.1 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.5 | 19 | --- | 95.125 | --- | 76.3158 | 57.0625 | 92.1139 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 9.2 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.5 | 18.8 | --- | 93.875 | --- | 76.0638 | 56.3375 | 92.0124 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 9.2
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | not specified | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1999-01-07 | 11:06 | 26035 | 25.2 | 106 | 69 | 22 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.8264 | 4.9103 | 60.5897 | 0.2447 | 6.62 | 6.21 | 228 | 360 | 357 | 1161 | 1081.0645 | 6.8851 | 36.1345 | 719.0323 | 68.2907 | 106 | 85 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2962 | 3.8168 | 72.6832 | 0.22421 | 6.13 |  | 194 | 407 | 704 | 744.3602 | -5.733 | 45.6583 | 575.6801 | 66.3007 | 85 | 69 | 26 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 6.5148 | 44.4852 | 0.26433 |  | 6.63 | 330 | 704 | 1161 | 1258.9677 | -8.4382 | 7.563 | 981.4839 | 66.3774 | SDS-Chlorination temp. | oC | 21.9 | 21.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.6 |  |  |  |  | SDS-Chlorination temp. | oC | 21.7 | 21.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.3 |  |  |  |  | SDS-Chlorination temp. | oC | 21.8 | 22.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16 |  |  |  |  | SDS-Chlorination temp. | oC | 22.4 | 22.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.6 |  |  |  |  | SDS-Chlorination temp. | oC | 21.4 | 21.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.1 |  |  |  |  | SDS-Chlorination temp. | oC | 21.4 | 21.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.1
State Approved Plant Capacity (MGD) | 70 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.2:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1999-01-08 | 9:35 | 26058 | 25.2 | 106 | 69 | 22 | 0 | 34.7 | 6.5 |  | 41.2 | 41.2 | 0.84223 | 0 | 14.8714 | 14.7838 | 4.9902 | 60.5098 | 0.24432 | 6.75 | 6.29 | 222 | 360 | 358 | 1122 | 1084.0308 | 3.3841 | 37.9888 | 721.0154 | 69.2101 | 106 | 85 | 19 | 25.4 | 16.5 | 41.9 | 41.9 | 0.50511 | 0.60621 | 16.3286 | 16.2323 | 3.7341 | 72.7659 | 0.22308 | 6.13 |  | 190 | 401 | 691 | 725.8121 | -5.0379 | 46.9274 | 563.4061 | 66.2765 | 85 | 69 | 25 | 9.2 | 6.5 | 15.7 | 15.7 | 0.38402 | 0.58599 | 11.8286 | 11.7589 | 6.2672 | 45.7328 | 0.25712 |  | 6.66 | 324 | 691 | 1122 | 1210.4462 | -7.8829 | 9.4972 | 950.7231 | 65.9207 | SDS-Chlorination pH | --- | 8.2 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.5 | 8.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.24 | 8.27 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.36 | 8.66 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.49 | 8.53 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 19 | [7 empty] | 1999-01-09 | 9:00 | 26083 | 25.3 | 106 | 69 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 5.0245 | 61.4755 | 0.24046 | 6.65 | 6.24 | 220 | 354 | 352 | 1146 | 1092.9032 | 4.6332 | 37.5 | 722.4516 | 69.5481 | 106 | 85 | 19 | 25.4 | 16.2 | 41.6 | 41.6 | 0.49992 | 0.61058 | 16.3286 | 16.1844 | 3.7641 | 72.7359 | 0.22251 | 6.09 |  | 188 | 399 | 694 | 729.8272 | -5.1624 | 46.5909 | 564.4136 | 66.6911 | 85 | 69 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8516 | 6.5625 | 47.4375 | 0.24984 |  | 6.62 | 319 | 694 | 1146 | 1256.5 | -9.6422 | 9.375 | 975.25 | 67.2904 | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 20 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1999-01-10 | 11:30 | 26107 | 25.4 | 106 | 70 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 5.6716 | 61.3284 | 0.24033 | 6.65 | 6.12 | 217 | 356 | 366 | 1158 | 1202.3226 | -3.8275 | 40.7104 | 784.1613 | 72.3271 | 106 | 85 | 19 | 25.4 | 16.4 | 41.8 | 41.8 | 0.50338 | 0.60766 | 16.3286 | 16.1366 | 3.7972 | 72.7028 | 0.22195 | 6.15 |  | 186 | 400 | 698 | 731.439 | -4.7907 | 49.1803 | 565.7195 | 67.1215 | 85 | 69 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8166 | 6.7025 | 47.2975 | 0.24984 |  | 6.56 | 315 | 698 | 1158 | 1272.5 | -9.8877 | 13.9344 | 985.25 | 68.0284 | SDS-TOX | mg Cl- /L | BMRL | 1460 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1445 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1475 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1440 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1360 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1465 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95% 2000 ppm MgSO4 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 26.7059 | [5 empty] | 1999-01-11 | 7:45 | 26128 | 25.3 | 106 | 70 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 5.9761 | 61.0239 | 0.24224 | 6.67 | 6.22 | 216 | 356 | 373 | 1189 | 1254.2258 | -5.4858 | 42.0912 | 813.6129 | 73.4517 | 106 | 86 | 19 | 25.4 | 15.8 | 41.2 | 41.2 | 0.493 | 0.6165 | 16.3286 | 16.1844 | 3.9684 | 73.0316 | 0.22161 | 6.15 |  | 184 | 404 | 707 | 757.6709 | -7.167 | 50.6702 | 580.8354 | 68.3215 | 86 | 70 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8516 | 6.965 | 48.035 | 0.24673 |  | 6.57 | 309 | 707 | 1189 | 1304 | -9.672 | 17.1582 | 1005.5 | 69.269 | SDS-CHCl3 | mg/L | BMRL | 406 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-12-28 | 1998-12-28 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 404 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-13 | 1999-01-13 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 417 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-27 | 1999-01-27 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 471 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-02-10 | 1999-02-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 431 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 427 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | 40-50% 500 ppm CaCl2 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 16.3725 | [5 empty] | 1999-01-12 | 11:45 | 26156 | 25.3 | 106 | 70 | 21 | 0 | 34.9 | 6.2 |  | 41.1 | 41.1 | 0.84915 | 0 | 14.9571 | 14.8251 | 5.264 | 61.736 | 0.24014 | 6.74 | 6.19 | 215 | 352 | 353 | 1159 | 1129.8065 | 2.5189 | 39.0935 | 741.4032 | 71.0009 | 106 | 85 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2481 | 3.8526 | 72.6474 | 0.22366 | 6.05 |  | 184 | 399 | 698 | 739.528 | -5.9496 | 47.8754 | 569.264 | 67.6776 | 85 | 70 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8516 | 6.7725 | 47.7275 | 0.24832 |  | 6.58 | 311 | 698 | 1159 | 1278.5 | -10.3106 | 11.898 | 988.25 | 68.5302 | SDS-BDCM | mg/L | BMRL | 69.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:30 | 7:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 69.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:05 | 7:45 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 83.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:35 | 7:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 82.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:40 | 7:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 67.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:25 | 6:55 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 65 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:25 | 6:55 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | N/A | [7 empty] | 1999-01-13 | 1:00 | 26181 | 25.3 | 106 | 70 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 5.329 | 61.671 | 0.2397 | 6.69 | 6.2 | 218 | 354 | 358 | 1165 | 1143.8065 | 1.8192 | 39.1061 | 750.9032 | 70.9683 | 106 | 85 | 19 | 25.4 | 16.3 | 41.7 | 41.7 | 0.50165 | 0.60911 | 16.3286 | 16.1844 | 3.8252 | 72.6748 | 0.2227 | 6.08 |  | 186 | 401 | 701 | 736.0307 | -4.9972 | 48.0447 | 568.5153 | 67.2832 | 85 | 70 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8516 | 6.7725 | 47.7275 | 0.24832 |  | 6.6 | 314 | 701 | 1165 | 1281.5 | -10 | 12.2905 | 991.25 | 68.3228 | SDS-DBCM | mg/L | 1.2 | 8.9 | --- | 52.5333 | --- | 86.5169 | 30.7167 | 96.0933 | Operation time | hh.hh | 25792 | 25792 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 7.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 26176 | 26276 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 9.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 26508 | 26508 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.6 | 9.9 | --- | 53.475 | --- | 83.8384 | 31.6875 | 94.9507 | Operation time | hh.hh | 26816 | 26816 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.14 | 9.04 | --- | 50.515 | --- | 87.3894 | 29.7775 | 96.1716 | Operation time | hh.hh | 27147 | 27147 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.26 | 8.66 | --- | 47.51 | --- | 85.4503 | 28.085 | 95.5136 | Operation time | hh.hh | 27147 | 27147 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1999-01-14 | 11:08 | 26203 | 25.3 | 107 | 69 | 21 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.6977 | 5.4436 | 61.5564 | 0.23877 | 6.61 | 6.13 | 220 | 363 | 367 | 1176 | 1161.7188 | 1.2144 | 40.0545 | 764.3594 | 71.2177 | 107 | 85 | 19 | 25.4 | 16.3 | 41.7 | 41.7 | 0.50165 | 0.60911 | 16.3286 | 16.1844 | 3.9319 | 73.0681 | 0.2215 | 6.07 |  | 188 | 409 | 712 | 753.3804 | -5.8118 | 48.7738 | 581.1902 | 67.6526 | 85 | 69 | 23 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.7241 | 6.8063 | 47.1938 | 0.24843 |  | 6.55 | 316 | 712 | 1176 | 1281.25 | -8.9498 | 13.8965 | 996.625 | 68.293 | SDS-CHBr3 | mg/L | 1.6 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.64 | 6.49 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.9 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.89 | 6.94 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.6 | 6.66 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 3.3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.86 | 6.74 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.8 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.89 | 6.79 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2.05 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.87 | 6.78 | --- | --- | --- | ---
|  | Standard testing pH | 8 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1999-01-15 | 9:55 | 26226 | 25.4 | 107 | 70 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 5.4432 | 62.0568 | 0.23751 | 6.58 | 6.17 | 217 | 358 | 360 | 1184 | 1162.6452 | 1.8036 | 39.7222 | 761.3226 | 71.497 | 107 | 85 | 19 | 25.4 | 16 | 41.4 | 41.4 | 0.49646 | 0.61353 | 16.3286 | 16.1366 | 3.9283 | 73.0717 | 0.22083 | 6.09 |  | 186 | 405 | 709 | 752.6625 | -6.1583 | 48.3333 | 578.8312 | 67.8663 | 85 | 70 | 23 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8166 | 6.9475 | 47.5525 | 0.2485 |  | 6.53 | 312 | 709 | 1184 | 1304.5 | -10.1774 | 13.3333 | 1006.75 | 69.0092 | SDS-THM4 | mg/L | 2.8 | 484.6 | --- | 3214.8 | --- | 99.4222 | 1849.7 | 99.8486 | Temperature | oC | 25.7 | 25.7 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.9 | 480.9 | --- | 2995.65 | --- | 99.6049 | 1738.275 | 99.8907 | Temperature | oC | 25.7 | 25.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.2 | 510.3 | --- | 3183.075 | --- | 99.7648 | 1846.6875 | 99.935 | Temperature | oC | 25.6 | 25.7 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.9 | 563.4 | --- | 3495.525 | --- | 99.1303 | 2029.4625 | 99.7586 | Temperature | oC | 25.7 | 25.7 | --- | --- | --- | --- | SDS-THM4 | mg/L | 2.94 | 507.64 | --- | 3157.315 | --- | 99.4208 | 1832.4775 | 99.8396 | Temperature | oC | 25.2 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.31 | 500.66 | --- | 3111.7475 | --- | 99.3389 | 1806.2037 | 99.8167 | Temperature | oC | 25.2 | 25 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 16.3725 | [5 empty] | 1999-01-16 | 5:35 | 26245 | 25.2 | 107 | 70 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.7412 | 5.3444 | 62.1556 | 0.23717 | 6.68 | 6.2 | 213 | 354 | 354 | 1178 | 1140.871 | 3.1519 | 39.8305 | 747.4355 | 71.5026 | 107 | 86 | 19 | 25.3 | 16.6 | 41.9 | 41.9 | 0.50597 | 0.60382 | 16.2643 | 16.1684 | 3.8589 | 73.6411 | 0.21956 | 6.12 |  | 182 | 401 | 704 | 734.7771 | -4.3717 | 48.5876 | 567.8886 | 67.9515 | 86 | 70 | 24 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 6.9155 | 47.0845 | 0.24974 |  | 6.52 | 307 | 704 | 1178 | 1293.0968 | -9.7705 | 13.2768 | 998.5484 | 69.2554 | SDS-MCAA* | mg/L | 1.66 | 8.28 | --- | 45.7933 | --- | 79.9517 | 27.0367 | 93.8602 | Alkalinity | mg/L as CaCO3 | 120 | 200 | 299.4595 | 0 | 249.7297 | 51.9481 | SDS-MCAA* | mg/L | 1.56 | 9.04 | --- | 48.31 | --- | 82.7434 | 28.675 | 94.5597 | Alkalinity | mg/L as CaCO3 | 152 | 244 | 366.2286 | -7.0423 | 305.1143 | 50.1826 | SDS-MCAA* | mg/L | 1.65 | 6.96 | --- | 34.8375 | --- | 76.2931 | 20.8987 | 92.1048 | Alkalinity | mg/L as CaCO3 | 128 | 200 | 297.9115 | -6.6667 | 248.9558 | 48.5852 | SDS-MCAA* | mg/L | BMRL | 7.22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 192 | 240 | 298.24 | -28 | 269.12 | 28.6564 | SDS-MCAA* | mg/L | BMRL | 8.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 190 | 270 | 376.6667 | -11.1111 | 323.3333 | 41.2371 | SDS-MCAA* | mg/L | BMRL | 7.78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 187 | 268 | 376 | -10 | 322 | 41.9255
|  | Acceptable range of operating pH values | 2 to 11 | Design system recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1999-01-17 | 12:10 | 26275 | 25.3 | 106 | 70 | 21 | 0 | 34.8 | 6.1 |  | 40.9 | 40.9 | 0.85086 | 0 | 14.9143 | 14.7826 | 6.7033 | 60.2967 | 0.24516 | 6.59 | 5.82 | 190 | 356 | 364 | 1269 | 1356.6557 | -6.9075 | 47.8022 | 860.3279 | 77.9154 | 106 | 85 | 19 | 25.4 | 16.4 | 41.8 | 41.8 | 0.50338 | 0.60766 | 16.3286 | 16.1844 | 4.2408 | 72.2592 | 0.22398 | 5.88 |  | 166 | 405 | 731 | 775.1585 | -6.0408 | 54.3956 | 590.0793 | 71.8682 | 85 | 70 | 23 | 9.3 | 6.1 | 15.4 | 15.4 | 0.37191 | 0.6039 | 11.9571 | 11.8516 | 8.177 | 46.323 | 0.25585 |  | 6.41 | 267 | 731 | 1269 | 1438.4098 | -13.3499 | 26.6484 | 1084.7049 | 75.385 | SDS-DCAA* | mg/L | BMRL | 111 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 249 | 664 | 1179.9459 | 33.7766 | 921.973 | 72.9927 | SDS-DCAA* | mg/L | BMRL | 110 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 280 | 628 | 1090.3429 | 22.4377 | 859.1714 | 67.4105 | SDS-DCAA* | mg/L | BMRL | 97.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 266 | 660 | 1195.7935 | 28.877 | 927.8968 | 71.333 | SDS-DCAA* | mg/L | BMRL | 115 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 320 | 575 | 884.4 | 13.0435 | 729.7 | 56.1464 | SDS-DCAA* | mg/L | 0.6 | 116 | --- | 721.85 | --- | 99.4828 | 418.925 | 99.8568 | Total dissolved solids | mg/L | 319 | 587 | 944.3333 | 12.6027 | 765.6667 | 58.337 | SDS-DCAA* | mg/L | 0.58 | 119 | --- | 740.705 | --- | 99.5126 | 429.8525 | 99.8651 | Total dissolved solids | mg/L | 314 | 585 | 946.3333 | 13.4986 | 765.6667 | 58.99
|  | Typical pressure drop across a single element (psi) | 3 to 5 psi | System influent flow rate, QI-sys (gpm) | 45.3041 | [5 empty] | 1999-01-18 | 7:15 | 26294 | 25.3 | 107 | 70 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 7.179 | 60.321 | 0.24436 | 6.73 | 5.88 | 185 | 360 | 374 | 1286 | 1431.7903 | -11.3367 | 50.5348 | 902.8952 | 79.5104 | 107 | 85 | 19 | 25.4 | 16 | 41.4 | 41.4 | 0.49646 | 0.61353 | 16.3286 | 16.1844 | 4.3947 | 72.6053 | 0.22291 | 5.83 |  | 162 | 407 | 740 | 795.9375 | -7.5591 | 56.6845 | 601.4688 | 73.0659 | 85 | 70 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7241 | 8.3961 | 47.1039 | 0.2489 |  | 6.22 | 258 | 740 | 1286 | 1455.2258 | -13.1591 | 31.016 | 1097.6129 | 76.4944 | SDS-TCAA* | mg/L | BMRL | 137 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 142 | 540 | 1034.8108 | 49.2857 | 787.4054 | 81.9661 | SDS-TCAA* | mg/L | BMRL | 138 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 168 | 520 | 987.6571 | 40.4255 | 753.8286 | 77.7138 | SDS-TCAA* | mg/L | 0.51 | 139 | --- | 866.0725 | --- | 99.6331 | 502.5362 | 99.8985 | Total hardness | mg/L as CaCO3 | 142 | 510 | 1010.4366 | 45.3846 | 760.2183 | 81.3212 | SDS-TCAA* | mg/L | BMRL | 120 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 202 | 450 | 750.9067 | 23.7736 | 600.4533 | 66.3588 | SDS-TCAA* | mg/L | BMRL | 126 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 198 | 468 | 828 | 24.4275 | 648 | 69.4444 | SDS-TCAA* | mg/L | 0.51 | 145 | --- | 903.5725 | --- | 99.6483 | 524.2862 | 99.9027 | Total hardness | mg/L as CaCO3 | 200 | 470 | 830 | 24.5283 | 650 | 69.2308
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.00022078 | [5 empty] | 1999-01-19 | 9:40 | 26320 | 25.4 | 107 | 69 | 21 | 0 | 34.8 | 6.3 |  | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.739 | 6.7714 | 60.2286 | 0.24472 | 6.67 | 5.9 | 186 | 356 | 366 | 1287 | 1360.2857 | -5.6943 | 49.1803 | 863.1429 | 78.4508 | 107 | 85 | 19 | 25.6 | 16.3 | 41.9 | 41.9 | 0.50338 | 0.61098 | 16.4571 | 16.2637 | 4.4453 | 72.5547 | 0.22416 | 5.77 |  | 160 | 409 | 740 | 800.0675 | -8.1172 | 56.2842 | 604.5337 | 73.5333 | 85 | 69 | 22 | 9.1 | 6.3 | 15.4 | 15.4 | 0.37537 | 0.59091 | 11.7 | 11.5625 | 8.4044 | 46.5956 | 0.24815 |  | 6.24 | 252 | 740 | 1287 | 1444.8889 | -12.268 | 31.1475 | 1092.4444 | 76.9325 | SDS-MBAA* | mg/L | BMRL | 0.87 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 134 | 500 | 955.027 | 44.1667 | 727.5135 | 81.5811 | SDS-MBAA* | mg/L | BMRL | 0.78 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 138 | 480 | 934.3714 | 40 | 707.1857 | 80.486 | SDS-MBAA* | mg/L | BMRL | 0.86 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 134 | 470 | 926.9204 | 42.735 | 698.4602 | 80.8149 | SDS-MBAA* | mg/L | BMRL | 0.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 194 | 420 | 694.2133 | 19.1667 | 557.1067 | 65.1772 | SDS-MBAA* | mg/L | BMRL | 0.81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 190 | 442 | 778 | 20.8333 | 610 | 68.8525 | SDS-MBAA* | mg/L | BMRL | 0.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 194 | 442 | 772.6667 | 18.4874 | 607.3333 | 68.0571
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1999-01-20 | 10:15 | 26345 | 25.4 | 107 | 69 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.6966 | 6.7168 | 60.2832 | 0.24379 | 6.64 | 5.83 | 182 | 356 | 363 | 1283 | 1344.3594 | -4.7825 | 49.8623 | 853.6797 | 78.6805 | 107 | 85 | 19 | 25.4 | 16.3 | 41.7 | 41.7 | 0.50165 | 0.60911 | 16.3286 | 16.1366 | 4.4301 | 72.5699 | 0.22236 | 5.76 |  | 160 | 409 | 741 | 797.0123 | -7.559 | 55.9229 | 603.0061 | 73.4663 | 85 | 69 | 22 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.6895 | 8.4047 | 46.5953 | 0.25087 |  | 6.19 | 252 | 741 | 1283 | 1443.9375 | -12.5438 | 30.5785 | 1092.4688 | 76.933 | SDS-DBAA* | mg/L | 0.5 | 1.71 | --- | 8.5667 | --- | 70.7602 | 5.1383 | 90.2692 | Turbidity | ntu | 0.058 | 0.835 | 1.801 | 61.3333 | 1.318 | 95.5994 | SDS-DBAA* | mg/L | BMRL | 1.41 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.062 | 0.311 | 0.64181 | 72.6872 | 0.47641 | 86.9859 | SDS-DBAA* | mg/L | BMRL | 1.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.044 | 2.08 | 4.8487 | 86.9822 | 3.4644 | 98.7299 | SDS-DBAA* | mg/L | 0.69 | 1.69 | --- | 6.94 | --- | 59.1716 | 4.315 | 84.0093 | Turbidity | ntu | 0.06 | 1.32 | 2.8488 | 72.7273 | 2.0844 | 97.1215 | SDS-DBAA* | mg/L | 0.64 | 1.7 | --- | 7.265 | --- | 62.3529 | 4.4825 | 85.7223 | Turbidity | ntu | 0.8 | 0.37 | -0.20333 | -211.284 | 0.083333 | -860 | SDS-DBAA* | mg/L | 0.58 | 1.68 | --- | 7.455 | --- | 65.4762 | 4.5675 | 87.3016 | Turbidity | ntu | 0.101 | 0.373 | 0.73567 | 67.6282 | 0.55433 | 81.7799
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | maximum system recycle flow rates. | [6 empty] | 1999-01-21 | 11:45 | 26370 | 25.3 | 108 | 70 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6977 | 5.9129 | 62.0871 | 0.23673 | 6.63 | 6.02 | 215 | 369 | 371 | 1240 | 1241.5806 | -0.12747 | 42.0485 | 806.2903 | 73.3347 | 108 | 86 | 19 | 25.4 | 16.2 | 41.6 | 41.6 | 0.49992 | 0.61058 | 16.3286 | 16.1844 | 4.1566 | 73.8434 | 0.21917 | 6.05 |  | 185 | 418 | 736 | 783.321 | -6.4295 | 50.1348 | 600.6605 | 69.2006 | 86 | 70 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7241 | 7.4555 | 48.5445 | 0.24151 |  | 6.47 | 308 | 736 | 1240 | 1371.0968 | -10.5723 | 16.9811 | 1053.5484 | 70.7655 | SDS-BCAA* | mg/L | BMRL | 17.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.68 | 32.2 | 71.387 | 95.0365 | 51.7935 | 98.6871 | SDS-BCAA* | mg/L | BMRL | 14.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.93 | 32.3 | 73.9773 | 93.3571 | 53.1386 | 98.2499 | SDS-BCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.86 | 34.1 | 79.3025 | 94.3046 | 56.7012 | 98.4833 | SDS-BCAA* | mg/L | BMRL | 17.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.75 | 33.7 | 73.6793 | 95.0331 | 53.6897 | 98.6031 | SDS-BCAA* | mg/L | BMRL | 17.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.64 | 31.4 | 72.4133 | 95.493 | 51.9067 | 98.767 | SDS-BCAA* | mg/L | BMRL | 17.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.71 | 31 | 71.3867 | 94.5385 | 51.1933 | 98.6131
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1999-01-22 | 9:40 | 26391 | 25.4 | 108 | 70 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 6.1154 | 61.8846 | 0.23748 | 6.84 | 6.07 | 203 | 357 | 364 | 1225 | 1265.0806 | -3.2719 | 44.2308 | 814.5403 | 75.078 | 108 | 86 | 19 | 25.4 | 16 | 41.4 | 41.4 | 0.49646 | 0.61353 | 16.3286 | 16.1366 | 4.1256 | 73.8744 | 0.21843 | 6.01 | 6.27 | 176 | 406 | 722 | 771.125 | -6.804 | 51.6484 | 588.5625 | 70.0966 | 86 | 70 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.6895 | 7.5252 | 48.4748 | 0.24115 | 6.27 | 6.43 | 290 | 722 | 1225 | 1363.0323 | -11.2679 | 20.3297 | 1042.5161 | 72.1827 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.995 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.041 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.139 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.049 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.053 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.996 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1999-01-23 | 8:00 | 26414 | 25.4 | 108 | 70 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 6.0015 | 61.9985 | 0.23705 | 6.65 | 6 | 201 | 358 | 359 | 1225 | 1243.2903 | -1.4931 | 44.0111 | 801.1452 | 74.9109 | 108 | 86 | 19 | 25.4 | 16.3 | 41.7 | 41.7 | 0.50165 | 0.60911 | 16.3286 | 16.1366 | 4.1276 | 73.8724 | 0.21844 | 6 | 6.28 | 174 | 406 | 722 | 767.5215 | -6.3049 | 51.532 | 586.7607 | 70.3457 | 86 | 70 | 23 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.6895 | 7.5948 | 47.4052 | 0.24659 | 6.28 | 6.43 | 286 | 722 | 1225 | 1368.9677 | -11.7525 | 20.3343 | 1045.4839 | 72.6442 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.0901 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.22 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3402 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.1128 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3535 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.2129 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 45.3041 | [5 empty] | 1999-01-24 | 8:30 | 26438 | 25.3 | 108 | 69 | 21 | 0 | 34.6 | 6.5 |  | 41.1 | 41.1 | 0.84185 | 0 | 14.8286 | 14.6977 | 6.2246 | 61.2754 | 0.23986 | 6.69 | 5.99 | 203 | 362 | 373 | 1215 | 1277.9231 | -5.1789 | 45.5764 | 825.4615 | 75.4077 | 108 | 86 | 19 | 25.4 | 16.7 | 42.1 | 42.1 | 0.50857 | 0.60333 | 16.3286 | 16.1844 | 4.1195 | 73.8805 | 0.21906 | 6.06 | 5.86 | 177 | 411 | 726 | 766.9042 | -5.6342 | 52.5469 | 588.9521 | 69.9466 | 86 | 69 | 22 | 9.1 | 6.5 | 15.6 | 15.6 | 0.38229 | 0.58333 | 11.7 | 11.5967 | 7.582 | 47.918 | 0.24201 | 5.86 | 6.4 | 290 | 736 | 1215 | 1360.4 | -11.9671 | 22.252 | 1048.2 | 72.3335 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 25.6667 | [5 empty] | 1999-01-25 | 8:43 | 26461 | 25.2 | 109 | 71 | 21 | 0 | 34.6 | 6.1 |  | 40.7 | 40.7 | 0.85012 | 0 | 14.8286 | 14.7412 | 5.9459 | 63.0541 | 0.23379 | 6.73 | 5.94 | 205 | 364 | 360 | 1262 | 1239.1803 | 1.8082 | 43.0556 | 799.5902 | 74.3619 | 109 | 87 | 19 | 25.4 | 15.9 | 41.3 | 41.3 | 0.49473 | 0.61501 | 16.3286 | 16.2323 | 4.2091 | 74.7909 | 0.21704 | 6.07 | 6.16 | 178 | 412 | 738 | 785.8113 | -6.4785 | 50.5556 | 598.9057 | 70.2791 | 87 | 71 | 23 | 9.2 | 6.1 | 15.3 | 15.3 | 0.37018 | 0.60131 | 11.8286 | 11.7589 | 7.8233 | 48.1767 | 0.24408 | 6.16 | 6.34 | 292 | 738 | 1262 | 1410.6557 | -11.7794 | 18.8889 | 1074.3279 | 72.8202 | SDS-HAA5 | mg/L | 2.16 | 258.86 | --- | 1713.4933 | --- | 99.1656 | 986.1767 | 99.781 | [8 empty] | SDS-HAA5 | mg/L | 1.56 | 259.23 | --- | 1611.9975 | --- | 99.3982 | 935.6137 | 99.8333 | [8 empty] | SDS-HAA5 | mg/L | 2.16 | 245.99 | --- | 1526.0975 | --- | 99.1219 | 886.0438 | 99.7562 | [8 empty] | SDS-HAA5 | mg/L | 0.69 | 244.71 | --- | 1525.815 | --- | 99.718 | 885.2625 | 99.9221 | [8 empty] | SDS-HAA5 | mg/L | 1.24 | 252.59 | --- | 1572.1775 | --- | 99.5091 | 912.3837 | 99.8641 | [8 empty] | SDS-HAA5 | mg/L | 1.67 | 274.26 | --- | 1705.3575 | --- | 99.3911 | 989.8088 | 99.8313
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 19.6375 | [5 empty] | 1999-01-26 | 9:50 | 26487 | 25.3 | 109 | 70 | 21 | 0 | 34.8 | 6.3 | X | 41.1 | 41.1 | 0.84672 | 0 | 14.9143 | 14.7826 | 6.019 | 62.481 | 0.23659 | 6.56 | 5.92 | 203 | 362 | 363 | 1247 | 1246.8095 | 0.015275 | 44.0771 | 804.9048 | 74.7796 | 109 | 87 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2481 | 4.2289 | 74.7711 | 0.21731 | 6.01 | 6.24 | 176 | 412 | 732 | 785.7888 | -7.3482 | 51.5152 | 598.8944 | 70.6125 | 87 | 70 | 23 | 9.2 | 6.3 | 15.5 | 15.5 | 0.3771 | 0.59355 | 11.8286 | 11.7241 | 7.6819 | 47.8181 | 0.24518 | 6.24 | 6.34 | 288 | 732 | 1247 | 1380.381 | -10.6961 | 20.6612 | 1056.1905 | 72.7322 | SDS-HAA6 | mg/L | 2.16 | 276.16 | --- | 1828.8267 | --- | 99.2178 | 1052.4933 | 99.7948 | [8 empty] | SDS-HAA6 | mg/L | 1.56 | 274.03 | --- | 1704.4975 | --- | 99.4307 | 989.2637 | 99.8423 | [8 empty] | SDS-HAA6 | mg/L | 2.16 | 261.99 | --- | 1626.0975 | --- | 99.1755 | 944.0438 | 99.7712 | [8 empty] | SDS-HAA6 | mg/L | 0.69 | 262.11 | --- | 1634.565 | --- | 99.7368 | 948.3375 | 99.9272 | [8 empty] | SDS-HAA6 | mg/L | 1.24 | 270.09 | --- | 1681.5525 | --- | 99.5409 | 975.8212 | 99.8729 | [8 empty] | SDS-HAA6 | mg/L | 1.67 | 291.86 | --- | 1815.3575 | --- | 99.4278 | 1053.6088 | 99.8415
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 19.6375 | [5 empty] | 1999-01-28 | 1:48 | 26513 | 25.2 | 87 | 52 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 |  |  |  | NR | 5.97 | 275 | NR | NR | 994 | [5 empty] | 87 | 66 | 20 | 26.2 | 15.2 | 41.4 | 41.4 | 0.48954 | 0.63285 | 16.8429 | 16.7436 | 2.7369 | 53.7631 | 0.31143 | 6 | NR | 265 | 412 | 634 | 665.3816 | -4.9498 | #VALUE! | 538.6908 | 50.8067 | 66 | 52 | 21 | 8.4 | 6.2 | 14.6 | 14.6 | 0.3598 | 0.57534 | 10.8 | 10.7363 | 5.3342 | 32.6658 | 0.32867 | NR | NR | 316 | 634 | 994 | 1064.8387 | -7.1266 | #VALUE! | 849.4194 | 62.7981 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.8333 | [5 empty] | 1999-01-29 | 9:35 | 26534 | 25.3 | 90 | 54 | 21 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.7826 | 4.3881 | 46.6119 | 0.31714 | 6.67 | 6.01 | 255 | 356 | 373 | 1033 | 1014.625 | 1.7788 | 31.6354 | 693.8125 | 63.2466 | 90 | 69 | 20 | 26.3 | 15.4 | 41.7 | 41.7 | 0.49386 | 0.6307 | 16.9071 | 16.7579 | 3.0775 | 56.4225 | 0.29701 | 5.94 | 6.16 | 243 | 409 | 658 | 692.4935 | -5.2422 | 34.8525 | 550.7468 | 55.8781 | 69 | 54 | 22 | 8.4 | 6.4 | 14.8 | 14.8 | 0.36672 | 0.56757 | 10.8 | 10.7047 | 5.8963 | 33.6037 | 0.31856 | 6.16 | 6.13 | 302 | 658 | 1033 | 1125.25 | -8.9303 | 19.0349 | 891.625 | 66.1293 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 6.8041 | [5 empty] | 1999-01-30 | 9:20 | 26558 | 25.2 | 91 | 55 | 20 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7838 | 3.2656 | 49.7344 | 0.29725 | 6.74 | 6.17 | 276 | 362 | 364 | 963 | 841.125 | 12.6558 | 24.1758 | 602.5625 | 54.1956 | 91 | 69 | 20 | 26 | 15.8 | 41.8 | 41.8 | 0.49819 | 0.62201 | 16.7143 | 16.6158 | 2.7159 | 57.2841 | 0.29006 | 6.06 | 6.49 | 260 | 409 | 630 | 654.1899 | -3.8397 | 28.5714 | 531.5949 | 51.0906 | 69 | 55 | 21 | 8.6 | 6.4 | 15 | 15 | 0.37018 | 0.57333 | 11.0571 | 10.992 | 4.932 | 36.068 | 0.30476 | 6.49 | 6.37 | 335 | 630 | 963 | 1026.4062 | -6.5842 | 7.967 | 828.2031 | 59.551
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1999-01-31 | 10:00 | 26581 | 25.4 | 91 | 55 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 2.7348 | 50.2652 | 0.29238 | 6.71 | 5.92 | 297 | 363 | 369 | 872 | 771.9677 | 11.4716 | 19.5122 | 570.4839 | 47.9389 | 91 | 70 | 19 | 25.9 | 15.9 | 41.8 | 41.8 | 0.49905 | 0.61962 | 16.65 | 16.4543 | 2.2499 | 59.2501 | 0.27771 | 6.32 | 6.3 | 278 | 402 | 591 | 603.9874 | -2.1975 | 24.6612 | 502.9937 | 44.7309 | 70 | 55 | 22 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 3.8126 | 36.6874 | 0.30477 | 6.3 | 6.37 | 368 | 591 | 872 | 907.5161 | -4.073 | 0.271 | 749.2581 | 50.8847 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 6.7941 | [5 empty] | 1999-02-01 | 8:05 | 26603 | 25.3 | 92 | 55 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 2.853 | 49.647 | 0.2969 | 6.4 | 6.1 | 290 | 359 | 366 | 891 | 784.6032 | 11.9413 | 20.765 | 575.3016 | 49.5917 | 92 | 70 | 20 | 25.9 | 15.8 | 41.7 | 41.7 | 0.49732 | 0.6211 | 16.65 | 16.503 | 2.4019 | 58.5981 | 0.28163 | 6.28 | 6.25 | 270 | 402 | 598 | 618.3797 | -3.408 | 26.2295 | 510.1899 | 47.0785 | 70 | 55 | 22 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 4.0932 | 36.4068 | 0.30803 | 6.25 | 6.49 | 357 | 598 | 891 | 934.6349 | -4.8973 | 2.459 | 766.3175 | 53.4136 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 38.5 | [5 empty] | 1999-02-02 | 8:20 | 26627 | 25.3 | 92 | 55 | 20 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.7826 | 2.975 | 50.525 | 0.29258 | 6.41 | 6.24 | 287 | 362 | 367 | 890 | 802 | 9.8876 | 21.7984 | 584.5 | 50.8982 | 92 | 70 | 20 | 25.9 | 16.2 | 42.1 | 42.1 | 0.50424 | 0.6152 | 16.65 | 16.503 | 2.4472 | 58.5528 | 0.28185 | 6.28 | 6.27 | 267 | 403 | 598 | 620.4321 | -3.7512 | 27.248 | 511.716 | 47.8226 | 70 | 55 | 21 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.2144 | 4.1006 | 37.3994 | 0.29986 | 6.27 | 6.52 | 355 | 598 | 890 | 932.125 | -4.7331 | 3.2698 | 765.0625 | 53.5986 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 45.2941 | [5 empty] | 1999-02-03 | 9:50 | 26652 | 25.4 | 93 | 56 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 3.0767 | 51.4233 | 0.2858 | 6.58 | 6.31 | 285 | 360 | 366 | 915 | 819.3387 | 10.4548 | 22.1311 | 592.6694 | 51.9125 | 93 | 71 | 19 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3908 | 2.5067 | 60.4933 | 0.27095 | 6.25 | 6.32 | 264 | 402 | 605 | 627.3418 | -3.6929 | 27.8689 | 514.6709 | 48.7051 | 71 | 56 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 4.3115 | 38.1885 | 0.29612 | 6.32 | 6.58 | 354 | 605 | 915 | 965.3065 | -5.498 | 3.2787 | 785.1532 | 54.9133 | Qp/QT (THM4), % | 85.6372 | 93.1092 |  | Qp/QT (HAA5), % | 79.8052 | 90.3233 | [11 empty] | Qp/QT (THM4), % | 85.3653 | 92.881 |  | Qp/QT (HAA5), % | 79.6484 | 90.1269 | [11 empty] | Qp/QT (THM4), % | 86.0931 | 93.1644 |  | Qp/QT (HAA5), % | 78.7393 | 89.8126 | [11 empty] | Qp/QT (THM4), % | 87.9857 | 94.4315 |  | Qp/QT (HAA5), % | 78.1534 | 89.2181 | [11 empty] | Qp/QT (THM4), % | 86.3166 | 93.4496 |  | Qp/QT (HAA5), % | 79.0093 | 89.7513 | [11 empty] | Qp/QT (THM4), % | 86.1888 | 93.4272 |  | Qp/QT (HAA5), % | 80.8027 | 90.7077
[11 empty] | 1999-02-04 | 9:50 | 26676 | 25.4 | 94 | 56 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.6966 | 3.2284 | 51.7716 | 0.28387 | 6.52 | 6.2 | 282 | 360 | 368 | 925 | 841.6825 | 9.0073 | 23.3696 | 604.8413 | 53.3762 | 94 | 71 | 19 | 25.7 | 16 | 41.7 | 41.7 | 0.49905 | 0.61631 | 16.5214 | 16.3272 | 2.5424 | 60.9576 | 0.26785 | 6.24 | 6.28 | 262 | 403 | 613 | 629.4813 | -2.6886 | 28.8043 | 516.2406 | 49.2485 | 71 | 56 | 21 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3084 | 4.4536 | 38.0464 | 0.29723 | 6.28 | 6.53 | 352 | 613 | 925 | 981.7143 | -6.1313 | 4.3478 | 797.3571 | 55.8542 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 100.0984 | 49.4222 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 99.3842 | 49.1921 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 109.4383 | 53.0642 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 126.9131 | 65.1169 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 108.8798 | 54.665 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 98.7879 | 49.5255
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1999-02-05 | 10:15 | 26700 | 25.3 | 94 | 57 | 20 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 2.931 | 52.569 | 0.2812 | 6.57 | 6.23 | 280 | 356 | 357 | 933 | 789.1935 | 15.4133 | 21.5686 | 573.0968 | 51.1426 | 94 | 72 | 19 | 25.8 | 16.6 | 42.4 | 42.4 | 0.5103 | 0.60849 | 16.5857 | 16.4393 | 2.5235 | 61.4765 | 0.26741 | 6.21 | 6.45 | 259 | 401 | 609 | 621.6988 | -2.0852 | 27.451 | 511.3494 | 49.3497 | 72 | 57 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3418 | 4.449 | 39.051 | 0.29044 | 6.45 | 6.5 | 350 | 609 | 933 | 980.7903 | -5.1222 | 1.9608 | 794.8952 | 55.969 | SDS-HAA5b, mg/L | 39.0293 | 19.8488 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 39.2691 | 19.9035 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 36.0692 | 18.8272 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 30.0074 | 14.2782 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 35.6332 | 17.7045 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 39.3179 | 19.5869 |  | SDS-HAA5b, mg/L | 54 | 27
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 3.7 | [5 empty] | 1999-02-06 | 9:15 | 26724 | 25.3 | 95 | 57 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 3.0059 | 51.9941 | 0.2835 | 6.45 | 6.14 | 277 | 359 | 358 | 934 | 797.1719 | 14.6497 | 22.6257 | 577.5859 | 52.0418 | 95 | 73 | 20 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.4393 | 2.6371 | 61.3629 | 0.2679 | 6.19 | 6.42 | 256 | 402 | 617 | 637.425 | -3.3104 | 28.4916 | 519.7125 | 50.742 | 73 | 57 | 22 | 8.8 | 6.4 | 15.2 | 15.2 | 0.37364 | 0.57895 | 11.3143 | 11.2144 | 4.59 | 38.41 | 0.29197 | 6.42 | 6.46 | 345 | 617 | 934 | 991 | -6.1028 | 3.6313 | 804 | 57.0896 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9.5 | [5 empty] | 1999-02-07 | 11:15 | 26749 | 25.3 | 95 | 58 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 3.4912 | 53.0088 | 0.27807 | 6.58 | 6.09 | 275 | 362 | 368 | 959 | 880.2381 | 8.2129 | 25.2717 | 624.119 | 55.9379 | 95 | 73 | 19 | 25.7 | 15.9 | 41.6 | 41.6 | 0.49732 | 0.61779 | 16.5214 | 16.3756 | 2.7303 | 62.2697 | 0.26298 | 6.2 | 6.25 | 254 | 405 | 624 | 649.0692 | -4.0175 | 30.9783 | 527.0346 | 51.8058 | 73 | 58 | 21 | 9 | 6.3 | 15.3 | 15.3 | 0.37364 | 0.58824 | 11.5714 | 11.4693 | 4.6971 | 39.8029 | 0.28815 | 6.25 | 6.48 | 350 | 624 | 959 | 1015.4286 | -5.8841 | 4.8913 | 819.7143 | 57.3022 | SDS-CDb, mg/L | 6.7544 | 5.6336 |  | SDS-CDb, mg/L | 7.6292 | 6.0515 | [11 empty] | SDS-CDb, mg/L | 5.8513 | 4.7465 |  | SDS-CDb, mg/L | 6.6917 | 5.1513 | [11 empty] | SDS-CDb, mg/L | 6.5443 | 5.5048 |  | SDS-CDb, mg/L | 7.6253 | 5.9976 | [11 empty] | SDS-CDb, mg/L | 6.4661 | 5.5186 |  | SDS-CDb, mg/L | 7.9114 | 6.2849 | [11 empty] | SDS-CDb, mg/L | 6.4841 | 5.4498 |  | SDS-CDb, mg/L | 7.5436 | 5.9861 | [11 empty] | SDS-CDb, mg/L | 6.475 | 5.4399 |  | SDS-CDb, mg/L | 7.2452 | 5.8288
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1999-02-08 | 10:20 | 26771 | 25.3 | 96 | 59 | 20 | 0 | 34.8 | 6.4 |  | 41.2 | 41.2 | 0.84466 | 0 | 14.9143 | 14.7826 | 3.57 | 53.93 | 0.27411 | 6.44 | 5.93 | 273 | 356 | 369 | 965 | 891 | 7.6684 | 26.0163 | 630 | 56.6667 | 96 | 74 | 19 | 25.7 | 16 | 41.7 | 41.7 | 0.49905 | 0.61631 | 16.5214 | 16.3756 | 2.8129 | 63.1871 | 0.25916 | 6.23 | 6.16 | 249 | 405 | 630 | 655.575 | -4.0595 | 32.5203 | 530.2875 | 53.0443 | 74 | 59 | 22 | 9 | 6.4 | 15.4 | 15.4 | 0.3771 | 0.58442 | 11.5714 | 11.4693 | 4.7177 | 39.7823 | 0.2883 | 6.16 | 6.45 | 353 | 630 | 965 | 1019.5312 | -5.6509 | 4.336 | 824.7656 | 57.2 | TOCb, mg/L | 2.473 | 1.4934 |  | TOCb, mg/L | 3.2375 | 1.8586 | [11 empty] | TOCb, mg/L | 2.8854 | 1.9069 |  | TOCb, mg/L | 3.6298 | 2.2655 | [11 empty] | TOCb, mg/L | 2.5648 | 1.5353 |  | TOCb, mg/L | 3.6356 | 2.0233 | [11 empty] | TOCb, mg/L | 2.3773 | 1.4452 |  | TOCb, mg/L | 3.799 | 2.1991 | [11 empty] | TOCb, mg/L | 2.4523 | 1.4815 |  | TOCb, mg/L | 3.4468 | 1.9848 | [11 empty] | TOCb, mg/L | 2.485 | 1.6019 |  | TOCb, mg/L | 3.1421 | 1.9337
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1999-02-09 | 11:20 | 26796 | 25.3 | 97 | 60 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 3.7224 | 53.7776 | 0.27409 | 6.53 | 6.06 | 271 | 361 | 369 | 987 | 917.4839 | 7.0432 | 26.5583 | 643.2419 | 57.8697 | 97 | 75 | 19 | 25.6 | 16.4 | 42 | 42 | 0.50511 | 0.60952 | 16.4571 | 16.3119 | 2.8666 | 64.1334 | 0.25434 | 6.21 | 6.24 | 244 | 405 | 638 | 656.3171 | -2.871 | 33.8753 | 530.6585 | 54.0194 | 75 | 60 | 22 | 9.1 | 6.2 | 15.3 | 15.3 | 0.37191 | 0.59477 | 11.7 | 11.5967 | 4.9242 | 40.5758 | 0.2858 | 6.24 | 6.47 | 354 | 638 | 987 | 1054.8387 | -6.8732 | 4.065 | 846.4194 | 58.1768 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
|  |  |  | Design permeate pressure, Pp (psi) | 10 | [5 empty] | 1999-02-10 | 1:20 | 26822 | 25.3 | 98 | 59 | 20 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 3.7109 | 54.7891 | 0.26903 | 6.64 | 5.86 | 266 | 359 | 366 | 968 | 908.1875 | 6.179 | 27.3224 | 637.0938 | 58.2479 | 98 | 75 | 19 | 25.6 | 16.6 | 42.2 | 42.2 | 0.50857 | 0.60664 | 16.4571 | 16.3119 | 2.9046 | 64.5954 | 0.25252 | 5.86 | 6.22 | 239 | 403 | 630 | 655.9157 | -4.1136 | 34.6995 | 529.4578 | 54.8595 | 75 | 59 | 21 | 9.1 | 6.4 | 15.5 | 15.5 | 0.37883 | 0.5871 | 11.7 | 11.5967 | 4.7564 | 41.2436 | 0.28118 | 6.22 | 6.47 | 352 | 630 | 968 | 1025.2812 | -5.9175 | 3.8251 | 827.6406 | 57.4695 | Bromideb, mg/L | 174.5691 | 174.7933 |  | Bromideb, mg/L | 174.3942 | 174.7097 | [11 empty] | Bromideb, mg/L | 152.366 | 150.6374 |  | Bromideb, mg/L | 153.6809 | 151.2708 | [11 empty] | Bromideb, mg/L | 173.1391 | 173.0684 |  | Bromideb, mg/L | 173.2126 | 173.1019 | [11 empty] | Bromideb, mg/L | 184.9576 | 186.0534 |  | Bromideb, mg/L | 183.2861 | 185.1671 | [11 empty] | Bromideb, mg/L | 172.7685 | 173.4105 |  | Bromideb, mg/L | 172.1108 | 173.0776 | [11 empty] | Bromideb, mg/L | 172.8951 | 173.4742 |  | Bromideb, mg/L | 172.4642 | 173.2566
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 26 | [5 empty] | 1999-02-11 | 8:20 | 26841 | 25.3 | 99 | 60 | 20 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 3.8594 | 55.6406 | 0.26492 | 6.45 | 5.91 | 262 | 351 | 366 | 988 | 929.875 | 5.8831 | 28.4153 | 647.9375 | 59.564 | 99 | 76 | 19 | 25.5 | 16.2 | 41.7 | 41.7 | 0.50078 | 0.61151 | 16.3929 | 16.2481 | 2.9844 | 65.5156 | 0.248 | 5.86 | 6.05 | 235 | 402 | 641 | 664.8704 | -3.7239 | 35.7923 | 533.4352 | 55.9459 | 76 | 60 | 22 | 9.1 | 6.4 | 15.5 | 15.5 | 0.37883 | 0.5871 | 11.7 | 11.5967 | 5.013 | 40.987 | 0.28294 | 6.05 | 6.37 | 348 | 641 | 988 | 1057.6094 | -7.0455 | 4.918 | 849.3047 | 59.0253 | Alkb, mg/L CaCO3 | 84.0324 | 80.8941 |  | Alkb, mg/L CaCO3 | 86.4818 | 82.0642 | [11 empty] | Alkb, mg/L CaCO3 | 99.3173 | 95.5595 |  | Alkb, mg/L CaCO3 | 102.1758 | 96.9365 | [11 empty] | Alkb, mg/L CaCO3 | 89.0065 | 86.4608 |  | Alkb, mg/L CaCO3 | 91.6539 | 87.6675 | [11 empty] | Alkb, mg/L CaCO3 | 134.1626 | 133.0023 |  | Alkb, mg/L CaCO3 | 135.9324 | 133.9407 | [11 empty] | Alkb, mg/L CaCO3 | 133.0207 | 129.8822 |  | Alkb, mg/L CaCO3 | 136.2359 | 131.5094 | [11 empty] | Alkb, mg/L CaCO3 | 130.3532 | 127.0235 |  | Alkb, mg/L CaCO3 | 132.8308 | 128.2745
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 60.219 | [5 empty] | 1999-02-12 | 10:15 | 26867 | 25.3 | 99 | 61 | 20 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 3.6161 | 56.3839 | 0.26218 | 6.69 | 6.25 | 267 | 361 | 362 | 1001 | 895.2258 | 10.5669 | 26.2431 | 628.6129 | 57.5255 | 99 | 77 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2481 | 3.0104 | 65.9896 | 0.24622 | 5.9 | 6.44 | 238 | 406 | 645 | 672.087 | -4.1995 | 34.2541 | 539.0435 | 55.8477 | 77 | 61 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7241 | 5.0168 | 41.9832 | 0.27926 | 6.44 | 6.49 | 357 | 645 | 1001 | 1072.3548 | -7.1284 | 1.3812 | 858.6774 | 58.4244 | T-Hdb, mg/L CaCO3 | 120.7148 | 106.8169 |  | T-Hdb, mg/L CaCO3 | 131.5623 | 111.9986 | [11 empty] | T-Hdb, mg/L CaCO3 | 136.8789 | 124.1023 |  | T-Hdb, mg/L CaCO3 | 146.5977 | 128.7843 | [11 empty] | T-Hdb, mg/L CaCO3 | 122.251 | 110.9369 |  | T-Hdb, mg/L CaCO3 | 134.0171 | 116.2999 | [11 empty] | T-Hdb, mg/L CaCO3 | 167.3359 | 160.181 |  | T-Hdb, mg/L CaCO3 | 178.2497 | 165.9679 | [11 empty] | T-Hdb, mg/L CaCO3 | 158.4201 | 149.8605 |  | T-Hdb, mg/L CaCO3 | 167.1888 | 154.2984 | [11 empty] | T-Hdb, mg/L CaCO3 | 157.264 | 148.216 |  | T-Hdb, mg/L CaCO3 | 163.9967 | 151.6154
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 35.9667 | [5 empty] | 1999-02-13 | 9:30 | 26890 | 25.3 | 99 | 61 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 2.9248 | 56.0752 | 0.26286 | 6.51 | 6.22 | 280 | 350 | 357 | 954 | 787.9516 | 17.4055 | 21.5686 | 572.4758 | 51.0896 | 99 | 77 | 19 | 25.5 | 15.8 | 41.3 | 41.3 | 0.49386 | 0.61743 | 16.3929 | 16.2481 | 2.855 | 66.145 | 0.24564 | 6.07 | 6.58 | 247 | 405 | 630 | 660 | -4.7619 | 30.8123 | 532.5 | 53.615 | 77 | 61 | 22 | 9.1 | 6.2 | 15.3 | 15.3 | 0.37191 | 0.59477 | 11.7 | 11.5967 | 4.352 | 42.648 | 0.27192 | 6.58 | 6.64 | 379 | 630 | 954 | 998.4032 | -4.6544 | -6.1625 | 814.2016 | 53.4513 | Ca-Hdb, mg/L CaCO3 | 111.5442 | 100.3362 |  | Ca-Hdb, mg/L CaCO3 | 120.2922 | 104.515 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 117.3177 | 107.3971 |  | Ca-Hdb, mg/L CaCO3 | 124.8641 | 111.0325 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 113.4697 | 103.5698 |  | Ca-Hdb, mg/L CaCO3 | 123.765 | 108.2624 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 148.4949 | 141.7912 |  | Ca-Hdb, mg/L CaCO3 | 158.7204 | 147.2132 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 145.0517 | 137.2055 |  | Ca-Hdb, mg/L CaCO3 | 153.0897 | 141.2735 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 144.9161 | 137.0987 |  | Ca-Hdb, mg/L CaCO3 | 150.7331 | 140.0357
|  |  |  | Required influent pressure to the system, PI (psi) | 106.1856 | [5 empty] | 1999-02-14 | 12:15 | 26916 | 25.4 | 100 | 62 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 3.7303 | 56.2697 | 0.26193 | 6.59 | 6.16 | 273 | 364 | 371 | 987 | 921.0645 | 6.6804 | 26.4151 | 646.0323 | 57.742 | 100 | 78 | 19 | 25.5 | 16.5 | 42 | 42 | 0.50597 | 0.60714 | 16.3929 | 16.2002 | 2.925 | 67.075 | 0.24152 | 6.01 | 6.14 | 241 | 406 | 640 | 661 | -3.2812 | 35.0404 | 533.5 | 54.8266 | 78 | 62 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.6895 | 4.7381 | 43.2619 | 0.2702 | 6.14 | 6.52 | 368 | 640 | 987 | 1043.6129 | -5.7359 | 0.80863 | 841.8065 | 56.2845 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1999-02-15 | 7:30 | 26935 | 24.2 | 100 | 62 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 15.2273 | 4.0078 | 55.9922 | 0.27195 | 6.38 | 5.96 | 269 | 364 | 377 | 996 | 962.5625 | 3.3572 | 28.6472 | 669.7812 | 59.8376 | 100 | 78 | 19 | 25.4 | 16.7 | 42.1 | 42.1 | 0.50857 | 0.60333 | 16.3286 | 16.7193 | 2.9928 | 67.0072 | 0.24951 | 6.18 | 6.05 | 239 | 409 | 647 | 667.5629 | -3.1782 | 36.6048 | 538.2814 | 55.5994 | 78 | 62 | 22 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 12.1116 | 4.8469 | 43.1531 | 0.28067 | 6.05 | 6.46 | 365 | 647 | 996 | 1052.375 | -5.6601 | 3.183 | 849.6875 | 57.043 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1999-02-16 | 6:10 | 26957 | 25.2 | 100 | 63 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 3.4565 | 57.0435 | 0.25917 | 6.43 | 6.11 | 271 | 364 | 362 | 993 | 871.3065 | 12.2551 | 25.1381 | 616.6532 | 56.0531 | 100 | 79 | 19 | 25.4 | 16.2 | 41.6 | 41.6 | 0.49992 | 0.61058 | 16.3286 | 16.2323 | 2.9792 | 67.5208 | 0.2404 | 5.94 | 6.44 | 239 | 406 | 644 | 667.8395 | -3.7018 | 33.9779 | 536.9198 | 55.4868 | 79 | 63 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 4.7555 | 44.2445 | 0.26577 | 6.44 | 6.51 | 371 | 644 | 993 | 1049.0968 | -5.6492 | -2.4862 | 846.5484 | 56.175 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1999-02-17 | 8:15 | 26983 | 25.2 | 100 | 63 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 3.2666 | 57.2334 | 0.25831 | 6.83 | 6.41 | 283 | 361 | 369 | 938 | 850.3226 | 9.3473 | 23.3062 | 609.6613 | 53.5808 | 100 | 78 | 19 | 25.4 | 16.1 | 41.5 | 41.5 | 0.49819 | 0.61205 | 16.3286 | 16.2323 | 2.7727 | 67.2273 | 0.24145 | 6.04 | 6.67 | 248 | 403 | 626 | 647.5342 | -3.44 | 32.7913 | 525.2671 | 52.7859 | 78 | 63 | 22 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 4.1458 | 44.3542 | 0.26511 | 6.67 | 6.72 | 388 | 626 | 926 | 979.1613 | -5.741 | -5.1491 | 802.5806 | 51.6559 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1999-02-18 | 8:00 | 27006 | 25.2 | 100 | 63 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7838 | 3.4161 | 57.0839 | 0.25898 | 6.77 | 6.42 | 277 | 362 | 368 | 954 | 869.2222 | 8.8866 | 24.7283 | 618.6111 | 55.2223 | 100 | 78 | 19 | 25.4 | 16.2 | 41.6 | 41.6 | 0.49992 | 0.61058 | 16.3286 | 16.2323 | 2.9435 | 67.0565 | 0.24207 | 6.04 | 6.63 | 243 | 408 | 630 | 666.7037 | -5.826 | 33.9674 | 537.3519 | 54.7782 | 78 | 63 | 22 | 9.2 | 6.3 | 15.5 | 15.5 | 0.3771 | 0.59355 | 11.8286 | 11.7589 | 4.2908 | 44.2092 | 0.26598 | 6.63 | 6.73 | 382 | 630 | 954 | 992.1587 | -3.9999 | -3.8043 | 811.0794 | 52.9023 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1999-02-19 | 9:30 | 27032 | 25.3 | 101 | 63 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 3.0801 | 57.9199 | 0.25449 | 6.39 | 6.19 | 274 | 358 | 357 | 951 | 807.0156 | 15.1403 | 23.2493 | 582.0078 | 52.9216 | 101 | 79 | 19 | 25.5 | 16.5 | 42 | 42 | 0.50597 | 0.60714 | 16.3929 | 16.2481 | 2.8718 | 68.1282 | 0.23849 | 6.02 | 6.58 | 239 | 401 | 630 | 651.3636 | -3.3911 | 33.0532 | 526.1818 | 54.5784 | 79 | 63 | 22 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.7241 | 4.3656 | 44.6344 | 0.26267 | 6.58 | 6.62 | 376 | 630 | 951 | 995.125 | -4.6399 | -5.3221 | 812.5625 | 53.7266 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1999-02-20 | 8:10 | 27054 | 25.2 | 101 | 63 | 21 | 0 | 34.5 | 6.5 |  | 41 | 41 | 0.84146 | 0 | 14.7857 | 14.6986 | 3.2154 | 57.7846 | 0.25437 | 6.66 | 6.24 | 268 | 359 | 356 | 968 | 823.0769 | 14.9714 | 24.7191 | 589.5385 | 54.5407 | 101 | 80 | 19 | 25.5 | 16.7 | 42.2 | 42.2 | 0.50943 | 0.60427 | 16.3929 | 16.2962 | 2.945 | 68.555 | 0.23771 | 6.02 | 6.53 | 235 | 402 | 636 | 657 | -3.3019 | 33.9888 | 529.5 | 55.6185 | 80 | 63 | 22 | 9.1 | 6.5 | 15.6 | 15.6 | 0.38229 | 0.58333 | 11.7 | 11.631 | 4.556 | 44.944 | 0.25879 | 6.53 | 6.61 | 368 | 636 | 968 | 1011.2 | -4.4628 | -3.3708 | 823.6 | 55.3181 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1999-02-21 | 8:00 | 27078 | 25.2 | 102 | 64 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.8264 | 4.2632 | 57.7368 | 0.25679 | 6.5 | 6.12 | 265 | 368 | 377 | 1008 | 1005.6452 | 0.23361 | 29.7082 | 691.3226 | 61.6677 | 102 | 80 | 19 | 25.5 | 16.4 | 41.9 | 41.9 | 0.50424 | 0.60859 | 16.3929 | 16.2962 | 3.0572 | 68.9428 | 0.23637 | 6.12 | 6.1 | 232 | 404 | 647 | 671.439 | -3.7773 | 38.4615 | 537.7195 | 56.8548 | 80 | 64 | 23 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 4.9297 | 44.0703 | 0.26682 | 6.1 | 6.54 | 364 | 647 | 1008 | 1066.9355 | -5.8468 | 3.4483 | 856.9677 | 57.5247 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1999-02-22 | 9:00 | 27102 | 25.2 | 103 | 65 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 4.2922 | 58.7078 | 0.25182 | 6.6 | 6.17 | 260 | 365 | 373 | 1043 | 1005.4355 | 3.6016 | 30.2949 | 689.2177 | 62.2761 | 103 | 81 | 19 | 25.4 | 16 | 41.4 | 41.4 | 0.49646 | 0.61353 | 16.3286 | 16.2323 | 3.2108 | 69.7892 | 0.23259 | 6.07 | 6.13 | 228 | 407 | 659 | 691.1625 | -4.8805 | 38.874 | 549.0812 | 58.4761 | 81 | 65 | 23 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 5.2781 | 44.7219 | 0.26293 | 6.13 | 6.56 | 356 | 659 | 1043 | 1108.6129 | -6.2908 | 4.5576 | 883.8065 | 59.7197 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1999-02-23 | 9:45 | 27127 | 25.2 | 103 | 65 | 21 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.7412 | 4.2586 | 58.7414 | 0.25095 | 6.69 | 6.09 | 260 | 360 | 375 | 1030 | 996.7188 | 3.2312 | 30.6667 | 685.8594 | 62.0914 | 103 | 82 | 19 | 25.3 | 16 | 41.3 | 41.3 | 0.49559 | 0.61259 | 16.2643 | 16.1684 | 3.2052 | 70.2948 | 0.23001 | 6.15 | 6.21 | 228 | 407 | 659 | 690.0438 | -4.7107 | 39.2 | 548.5219 | 58.4337 | 82 | 65 | 23 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.7589 | 5.2078 | 45.2922 | 0.25962 | 6.21 | 6.6 | 356 | 659 | 1030 | 1094.5625 | -6.2682 | 5.0667 | 876.7812 | 59.3969 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1999-02-24 | 7:55 | 27148 | 25.2 | 103 | 66 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.7412 | 5.1548 | 58.3452 | 0.25265 | 6.3 | 5.96 | 239 | 364 | 375 | 1121 | 1133.9677 | -1.1568 | 36.2667 | 754.4839 | 68.3227 | 103 | 81 | 19 | 25.4 | 16.1 | 41.5 | 41.5 | 0.49819 | 0.61205 | 16.3286 | 16.2323 | 3.5061 | 69.4939 | 0.23358 | 6.22 | 5.83 | 214 | 410 | 684 | 719.2174 | -5.1487 | 42.9333 | 564.6087 | 62.0976 | 81 | 66 | 23 | 9.2 | 6.2 | 15.4 | 15.4 | 0.37364 | 0.5974 | 11.8286 | 11.7589 | 6.3058 | 44.1942 | 0.26607 | 5.83 | 6.34 | 322 | 684 | 1121 | 1221.1613 | -8.935 | 14.1333 | 952.5806 | 66.1971 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1999-02-25 | 8:55 | 27173 | 25.1 | 104 | 66 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.8275 | 4.8051 | 59.1949 | 0.25049 | 6.79 | 6.2 | 243 | 373 | 371 | 1056 | 1076.0159 | -1.8954 | 34.5013 | 723.5079 | 66.4136 | 104 | 82 | 19 | 25.4 | 16.1 | 41.5 | 41.5 | 0.49819 | 0.61205 | 16.3286 | 16.2804 | 3.4166 | 70.5834 | 0.23065 | 5.92 | 6.38 | 216 | 407 | 668 | 708.3292 | -6.0373 | 41.779 | 557.6646 | 61.267 | 82 | 66 | 22 | 9.2 | 6.3 | 15.5 | 15.5 | 0.3771 | 0.59355 | 11.8286 | 11.7937 | 5.8652 | 46.1348 | 0.25563 | 6.38 | 6.53 | 329 | 668 | 1081 | 1163.0476 | -7.59 | 11.3208 | 915.5238 | 64.0643
[11 empty] | 1999-02-26 | 9:30 | 27198 | 25.2 | 104 | 66 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7838 | 3.4 | 60.6 | 0.24396 | 6.56 | 6.13 | 373 | 364 | 364 | 1065 | 315.2031 | 70.4035 | -2.4725 | 339.6016 | -9.8346 | 104 | 82 | 19 | 25.4 | 16.6 | 42 | 42 | 0.50684 | 0.60476 | 16.3286 | 16.2323 | 3.3 | 70.7 | 0.22959 | 5.93 | 6.4 | 223 | 409 | 669 | 693.6024 | -3.6775 | 38.7363 | 551.3012 | 59.5502 | 82 | 66 | 22 | 9.2 | 6.4 | 15.6 | 15.6 | 0.38056 | 0.58974 | 11.8286 | 11.7589 | 5.6 | 46.4 | 0.25342 | 6.4 | 6.58 | 341 | 669 | 1065 | 1140.5 | -7.0892 | 6.3187 | 904.75 | 62.31
[11 empty] | 1999-02-27 | 8:00 | 27221 | 25.3 | 105 | 66 | 21 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 3.4 | 61.1 | 0.24125 | 6.58 | 6.06 | 362 | 363 | 363 | 1078 | 368.5079 | 65.8156 | 0.27548 | 365.754 | 1.0264 | 105 | 82 | 19 | 25.4 | 16.3 | 41.7 | 41.7 | 0.50165 | 0.60911 | 16.3286 | 16.1844 | 3.4 | 71.1 | 0.22763 | 5.95 | 6.36 | 220 | 409 | 673 | 703.5153 | -4.5342 | 39.3939 | 556.2577 | 60.45 | 82 | 66 | 22 | 9.2 | 6.3 | 15.5 | 15.5 | 0.3771 | 0.59355 | 11.8286 | 11.7241 | 5.8 | 46.2 | 0.25377 | 6.36 | 6.45 | 335 | 673 | 1078 | 1166.5873 | -8.2177 | 7.7135 | 919.7937 | 63.5788
[11 empty] | 1999-02-28 | 11:00 | 27247 | 25.3 | 105 | 65 | 21 | 0 | 34.6 | 6.5 |  | 41.1 | 41.1 | 0.84185 | 0 | 14.8286 | 14.6977 | 3.4 | 60.6 | 0.24254 | 6.59 | 6.08 | 365 | 365 | 373 | 1065 | 415.5846 | 60.978 | 2.1448 | 394.2923 | 7.4291 | 105 | 82 | 19 | 25.4 | 16.6 | 42 | 42 | 0.50684 | 0.60476 | 16.3286 | 16.1844 | 3.3 | 71.2 | 0.22731 | 5.98 | 6.01 | 220 | 409 | 668 | 698.1928 | -4.5199 | 41.0188 | 553.5964 | 60.2599 | 82 | 65 | 22 | 9.1 | 6.5 | 15.6 | 15.6 | 0.38229 | 0.58333 | 11.7 | 11.5967 | 5.7 | 45.8 | 0.2532 | 6.01 | 6.49 | 334 | 668 | 1065 | 1135.6 | -6.6291 | 10.4558 | 901.8 | 62.963
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on E23: S Allgeier (10/4/99): Reviewer replaced value of 29.2 ft with 14 ft -- a value more typical for this membrane.
Note on AR6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on BP6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.

## NF200. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Boca Raton | Membrane manufacturer | FilmTec Corporation | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 226 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.63 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500130 | Membrane trade name | FILMTEC | Temperature normalized MTCW (gfd/psi) | 0.274 | Calcium Hardness (mg/L as CaCO3) | 216 | Dual Media Filtration | Silica/Garnet | Pilot-Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 26 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 25.7 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Membrane element model number | NF200-4040 |  |  | LSI | 0.06 | Scale Inhibitor Addition | Calgon EL-5600 4.0 mg/l | Pilot-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 41.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 41.5 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 nominal | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.26 | pH Adjustment | sulfuric acid to pH 6.0 - 6.4 | Pilot-Scale | 1999-03-01 | 8:30 | 27269 | 25.3 | 105 | 66 | 21 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 5.0098 | 59.4902 | 0.24777 | 6.63 | 6.06 | 245 | 372 | 380 | 1082 | 1111.9531 | -2.7683 | 35.5263 | 745.9766 | 67.1571 | 105 | 83 | 19 | 25.5 | 16.6 | 42.1 | 42.1 | 0.5077 | 0.6057 | 16.3929 | 16.2481 | 3.377 | 71.623 | 0.22686 | 6.11 | 5.99 | 219 | 410 | 673 | 703.4036 | -4.5176 | 42.3684 | 556.7018 | 60.6612 | 83 | 66 | 22 | 9.1 | 6.4 | 15.5 | 15.5 | 0.37883 | 0.5871 | 11.7 | 11.5967 | 5.8343 | 46.6657 | 0.24851 | 5.99 | 6.43 | 332 | 673 | 1082 | 1157.8594 | -7.011 | 12.6316 | 915.4297 | 63.7329 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.28 | Cartridge Filtration | 5 um exclusion | Pilot-Scale | 1999-03-02 | 9:00 | 27293 | 25.2 | 105 | 67 | 21 | 0 | 34.7 | 6.1 |  | 40.8 | 40.8 | 0.85049 | 0 | 14.8714 | 14.7838 | 4.4978 | 60.5022 | 0.24435 | 6.58 | 6.04 | 245 | 367 | 362 | 1115 | 1027.5574 | 7.8424 | 32.3204 | 694.7787 | 64.737 | 105 | 83 | 19 | 25.4 | 16 | 41.4 | 41.4 | 0.49646 | 0.61353 | 16.3286 | 16.2323 | 3.444 | 71.556 | 0.22685 | 6.05 | 6.31 | 218 | 410 | 679 | 714.8 | -5.2725 | 39.779 | 562.4 | 61.2376 | 83 | 67 | 22 | 9.2 | 6.1 | 15.3 | 15.3 | 0.37018 | 0.60131 | 11.8286 | 11.7589 | 6.1218 | 46.8782 | 0.25084 | 6.31 | 6.42 | 330 | 679 | 1115 | 1205.3607 | -8.1041 | 8.8398 | 942.1803 | 64.9749 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 16.5 | Dissolved aluminum (mg/L) | BDL |  |  |  | 1999-03-03 | 9:30 | 27317 | 25.3 | 105 | 67 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 4.4155 | 60.5845 | 0.244 | 6.76 | 6.18 | 245 | 363 | 361 | 1100 | 1012.0968 | 7.9912 | 32.133 | 686.5484 | 64.3142 | 105 | 83 | 19 | 25.5 | 16.3 | 41.8 | 41.8 | 0.50251 | 0.61005 | 16.3929 | 16.2481 | 3.4397 | 71.5603 | 0.22706 | 6.04 | 6.4 | 218 | 411 | 676 | 712.9325 | -5.4634 | 39.6122 | 561.9663 | 61.2076 | 83 | 67 | 22 | 9.3 | 6.2 | 15.5 | 15.5 | 0.37537 | 0.6 | 11.9571 | 11.8516 | 6.055 | 46.945 | 0.25246 | 6.4 | 6.49 | 330 | 676 | 1100 | 1195 | -8.6364 | 8.5873 | 935.5 | 64.7247 | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 (dup) | CF-sys-30 (dup) | CC-sys-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 (dup) | CI-s1-30 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | hydrophylic | Number of elements per pressure vessel, Ne | 7 | Total aluminum (mg/L) | BDL |  |  |  | 1999-03-04 | 11:30 | 27342 | 25.2 | 105 | 68 | 21 | 0 | 34.7 | 6 | X | 40.7 | 40.7 | 0.85258 | 0 | 14.8714 | 14.7838 | 4.9035 | 60.5965 | 0.24397 | 6.56 | 6.06 | 244 | 366 | 370 | 1136 | 1098.7 | 3.2835 | 34.0541 | 734.35 | 66.7733 | 105 | 84 | 19 | 25.4 | 15.9 | 41.3 | 41.3 | 0.49473 | 0.61501 | 16.3286 | 16.2323 | 3.5795 | 71.9205 | 0.2257 | 6.06 | 6.32 | 216 | 415 | 687 | 732.8994 | -6.6811 | 41.6216 | 573.9497 | 62.366 | 84 | 68 | 23 | 9.2 | 6 | 15.2 | 15.2 | 0.36672 | 0.60526 | 11.8286 | 11.7589 | 6.254 | 46.746 | 0.25155 | 6.32 | 6.4 | 333 | 687 | 1136 | 1229.8 | -8.257 | 10 | 958.4 | 65.2546 | Sampling date | MM/DD/YY | 1999-03-10 | 1999-03-10 | 1999-03-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-10 | 1999-03-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-24 | 1999-03-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-24 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-07 | 1999-04-07 | 1999-04-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-07 | 1999-04-07 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 13
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 4 | Fluoride (mg/L) | 0.25 |  |  |  | 1999-03-06 | 10:00 | 27363 | 25.2 | 94 | 58 | 20 | 0 | 34.8 | 6.5 |  | 41.3 | 41.3 | 0.84262 | 0 | 14.9143 | 14.8264 | 3.7872 | 52.2128 | 0.28396 | 6.61 | 6.04 | 261 | 364 | 364 | 1025 | 915.4462 | 10.6882 | 28.2967 | 639.7231 | 59.2011 | 94 | 73 | 20 | 26.3 | 15.4 | 41.7 | 41.7 | 0.49386 | 0.6307 | 16.9071 | 16.8075 | 3.1145 | 60.3855 | 0.27834 | 6.05 | 6.3 | 243 | 411 | 662 | 697.9091 | -5.4243 | 33.2418 | 554.4545 | 56.1731 | 73 | 58 | 21 | 8.4 | 6.5 | 14.9 | 14.9 | 0.37018 | 0.56376 | 10.8 | 10.7363 | 5.5146 | 38.9854 | 0.27539 | 6.3 | 6.34 | 327 | 662 | 1025 | 1094.9231 | -6.8218 | 10.1648 | 878.4615 | 62.7758 | Sampling time | hh:mm | 7:15 | 7:20 | 7:25 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:25 | 7:20 | --- | --- | --- | --- | Sampling time | hh:mm | 6:25 | 6:30 | 6:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 6:35 | 6:30 | --- | --- | --- | --- | Sampling time | hh:mm | 6:45 | 6:50 | 7:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:00 | 6:50 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5999
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 2 | Phosphate (mg/L) | 0.56 |  |  |  | 1999-03-07 | 10:40 | 27386 | 25.3 | 94 | 59 | 20 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 4.3418 | 52.1582 | 0.2826 | 6.6 | 6.02 | 257 | 364 | 374 | 1051 | 1008.3594 | 4.0571 | 31.2834 | 691.1797 | 62.8172 | 94 | 73 | 20 | 26.1 | 15.4 | 41.5 | 41.5 | 0.49213 | 0.62892 | 16.7786 | 16.6304 | 3.1775 | 60.3225 | 0.27569 | 6.06 | 6.08 | 239 | 411 | 665 | 702.5065 | -5.6401 | 36.0963 | 556.7532 | 57.0725 | 73 | 59 | 21 | 8.5 | 6.4 | 14.9 | 14.9 | 0.36845 | 0.57047 | 10.9286 | 10.8321 | 5.6745 | 39.3255 | 0.27545 | 6.08 | 6.31 | 324 | 665 | 1051 | 1117.8906 | -6.3645 | 13.369 | 891.4453 | 63.6545 | Operation time | hh.hh | 27454 | 27454 | 27454 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27454 | 27454 | --- | --- | --- | --- | Operation time | hh.hh | 27786 | 27786 | 27786 | --- | --- | --- | --- | --- | Operation time | hh.hh | 27786 | 27786 | --- | --- | --- | --- | Operation time | hh.hh | 28118 | 28118 | 28118 | --- | --- | --- | --- | --- | Operation time | hh.hh | 28118 | 28118 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 132
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.91667 | Sulfate (mg/L) | 14.9 |  |  |  | 1999-03-08 | 8:36 | 27408 | 25.2 | 95 | 58 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.7412 | 4.7379 | 50.7621 | 0.2904 | 6.7 | 6.1 | 254 | 369 | 379 | 1076 | 1076.5806 | -0.053963 | 32.9815 | 727.7903 | 65.0998 | 95 | 75 | 20 | 26 | 15.5 | 41.5 | 41.5 | 0.493 | 0.62651 | 16.7143 | 16.6158 | 3.2361 | 61.7639 | 0.26902 | 6.07 | 6.1 | 236 | 412 | 673 | 707.2258 | -5.0856 | 37.7309 | 559.6129 | 57.828 | 75 | 58 | 22 | 8.6 | 6.2 | 14.8 | 14.8 | 0.36326 | 0.58108 | 11.0571 | 10.992 | 5.9782 | 38.5218 | 0.28534 | 6.1 | 6.4 | 320 | 673 | 1076 | 1162.6452 | -8.0525 | 15.5673 | 917.8226 | 65.1349 | pH | --- | 6.49 | 6.52 | 6.76 | --- | --- | --- | --- | --- | pH | --- | 6.51 | 6.53 | --- | --- | --- | --- | pH | --- | 6.27 | 6.33 | 6.68 | --- | --- | --- | --- | --- | pH | --- | 6.38 | 6.38 | --- | --- | --- | --- | pH | --- | 6.38 | 6.31 | 6.59 | --- | --- | --- | --- | --- | pH | --- | 6.23 | 6.36 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 17
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 6.4167 | Calcium (mg/L) | 95 |  |  |  | 1999-03-09 | 10:00 | 27433 | 25.3 | 96 | 60 | 20 | 0 | 34.7 | 6.4 |  | 41.1 | 41.1 | 0.84428 | 0 | 14.8714 | 14.7401 | 4.1191 | 53.8809 | 0.27357 | 6.64 | 6.09 | 254 | 367 | 365 | 1065 | 966.8281 | 9.218 | 30.411 | 665.9141 | 61.8569 | 96 | 75 | 20 | 26.3 | 15.7 | 42 | 42 | 0.49905 | 0.62619 | 16.9071 | 16.7579 | 3.2525 | 62.2475 | 0.26921 | 6.04 | 6.29 | 235 | 412 | 673 | 708.5032 | -5.2754 | 35.6164 | 560.2516 | 58.0546 | 75 | 58 | 22 | 8.6 | 6.4 | 15 | 15 | 0.37018 | 0.57333 | 11.0571 | 10.9595 | 5.885 | 38.615 | 0.28382 | 6.29 | 6.34 | 321 | 673 | 1065 | 1146 | -7.6056 | 12.0548 | 909.5 | 64.7059 | Temperature | oC | 25.5 | 25.3 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.3 | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.3 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.3 | --- | --- | --- | --- | Temperature | oC | 25.7 | 25.7 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.8 | 25.7 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 25.6667 | Barium (mg/L) | 0.021 |  |  |  | 1999-03-10 | 10:00 | 27457 | 25.2 | 96 | 60 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7838 | 3.9883 | 54.0117 | 0.27371 | 6.84 | 6.22 | 253 | 359 | 358 | 1075 | 945.6613 | 12.0315 | 29.3296 | 651.8306 | 61.1862 | 96 | 75 | 20 | 25.9 | 15.5 | 41.4 | 41.4 | 0.49213 | 0.6256 | 16.65 | 16.5519 | 3.2855 | 62.2145 | 0.26605 | 6.03 | 6.27 | 233 | 412 | 677 | 711.1032 | -5.0374 | 34.9162 | 561.5516 | 58.5078 | 76 | 60 | 21 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.1198 | 6.0748 | 40.9252 | 0.27171 | 6.27 | 6.4 | 320 | 677 | 1075 | 1177.9516 | -9.5769 | 10.6145 | 927.4758 | 65.4978 | Alkalinity | mg/L as CaCO3 | 110 | 132 | 226 | 247.5 | -9.5133 | 16.6667 | 189.75 | 42.029 | Alkalinity | mg/L as CaCO3 | 88 | 126 | 189.7419 | 33.3333 | 157.871 | 44.2583 | Alkalinity | mg/L as CaCO3 | 88 | 112 | 222 | 238 | -7.2072 | 21.4286 | 175 | 49.7143 | Alkalinity | mg/L as CaCO3 | 78 | 114 | 173.1592 | 30.3571 | 143.5796 | 45.6747 | Alkalinity | mg/L as CaCO3 | 88 | 110 | 240 | 225.5 | 6.0417 | 20 | 167.75 | 47.541 | Alkalinity | mg/L as CaCO3 | 54 | 110 | 201.0886 | 50.9091 | 155.5443 | 65.2832 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 27.8 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.8333 | Strontium (mg/L) | 0.53 |  |  |  | 1999-03-11 | 9:48 | 27481 | 25.3 | 97 | 61 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 4.2795 | 54.7205 | 0.26937 | 6.64 | 5.99 | 248 | 360 | 362 | 1080 | 989.9048 | 8.3422 | 31.4917 | 675.9524 | 63.311 | 97 | 76 | 20 | 25.9 | 16.1 | 42 | 42 | 0.50251 | 0.61667 | 16.65 | 16.503 | 3.302 | 63.198 | 0.26113 | 6.03 | 6.2 | 229 | 412 | 677 | 706.3913 | -4.3414 | 36.7403 | 559.1957 | 59.0483 | 76 | 61 | 21 | 8.7 | 6.3 | 15 | 15 | 0.36845 | 0.58 | 11.1857 | 11.087 | 6.1364 | 41.3636 | 0.26804 | 6.2 | 6.27 | 314 | 677 | 1080 | 1178.2857 | -9.1005 | 13.2597 | 927.6429 | 66.1508 | Total dissolved solids | mg/L | 224 | 367 | 944 | 1117.75 | -18.4057 | 38.9646 | 742.375 | 69.8266 | Total dissolved solids | mg/L | 201 | 368 | 648.129 | 45.2316 | 508.0645 | 60.4381 | Total dissolved solids | mg/L | 202 | 363 | 1017 | 1208.25 | -18.8053 | 44.3526 | 785.625 | 74.288 | Total dissolved solids | mg/L | 189 | 366 | 656.8662 | 47.9339 | 511.4331 | 63.045 | Total dissolved solids | mg/L | 193 | 370 | 1050 | 1299.25 | -23.7381 | 47.8378 | 834.625 | 76.8758 | Total dissolved solids | mg/L | 180 | 369 | 676.4241 | 51.3514 | 522.712 | 65.5642 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 38.5 | Reactive silica (mg/L as SiO2) | 9.4 |  |  |  | 1999-03-12 | 9:45 | 27504 | 25.4 | 98 | 61 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 4.3394 | 54.1606 | 0.27213 | 6.48 | 6.01 | 250 | 362 | 364 | 1083 | 1003.871 | 7.3065 | 31.3187 | 683.9355 | 63.4468 | 98 | 76 | 20 | 25.9 | 15.7 | 41.6 | 41.6 | 0.49559 | 0.6226 | 16.65 | 16.4543 | 3.2665 | 63.7335 | 0.25817 | 6.05 | 6.24 | 231 | 410 | 671 | 705.293 | -5.1107 | 36.5385 | 557.6465 | 58.5759 | 76 | 61 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 6.0352 | 41.4648 | 0.26966 | 6.24 | 6.32 | 318 | 671 | 1083 | 1172.0323 | -8.2209 | 12.6374 | 921.5161 | 65.4917 | Total hardness | mg/L as CaCO3 | 124 | 262 | 1070 | 986.5 | 7.8037 | 52.6718 | 624.25 | 80.1362 | Total hardness | mg/L as CaCO3 | 102 | 254 | 508.9677 | 61.0687 | 381.4839 | 73.2623 | Total hardness | mg/L as CaCO3 | 110 | 256 | 960 | 1022.5 | -6.5104 | 57.0312 | 639.25 | 82.7923 | Total hardness | mg/L as CaCO3 | 94 | 240 | 479.9236 | 63.2812 | 359.9618 | 73.8861 | Total hardness | mg/L as CaCO3 | 112 | 270 | 1005 | 1099.5 | -9.403 | 58.5185 | 684.75 | 83.6437 | Total hardness | mg/L as CaCO3 | 101 | 298 | 618.4367 | 62.5926 | 458.2184 | 77.9581 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.274 | Feed flow rate to system, QF-sys (gpm) | 45.2941 | Turbidity (ntu) | 1.14 |  |  |  | 1999-03-13 | 8:00 | 27527 | 25.3 | 98 | 61 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 4.5581 | 54.9419 | 0.26829 | 6.52 | 5.9 | 242 | 359 | 362 | 1100 | 1033.6129 | 6.0352 | 33.1492 | 697.8065 | 65.3199 | 98 | 76 | 20 | 25.9 | 16.5 | 42.4 | 42.4 | 0.50943 | 0.61085 | 16.65 | 16.503 | 3.302 | 63.698 | 0.25908 | 6.01 | 6.24 | 224 | 409 | 677 | 699.3939 | -3.3078 | 38.1215 | 554.197 | 59.5812 | 76 | 61 | 21 | 8.7 | 6.2 | 14.9 | 14.9 | 0.36499 | 0.58389 | 11.1857 | 11.087 | 6.313 | 41.187 | 0.26919 | 6.24 | 6.3 | 306 | 677 | 1100 | 1197.5968 | -8.8724 | 15.4696 | 937.2984 | 67.353 | Calcium hardness | mg/L as CaCO3 | 116 | 222 | 740 | 778.5 | -5.2027 | 47.7477 | 500.25 | 76.8116 | Calcium hardness | mg/L as CaCO3 | 94 | 218 | 426 | 57.6577 | 322 | 70.8075 | Calcium hardness | mg/L as CaCO3 | 96 | 218 | 910 | 858.5 | 5.6593 | 55.9633 | 538.25 | 82.1644 | Calcium hardness | mg/L as CaCO3 | 92 | 220 | 430.3439 | 57.7982 | 325.172 | 71.7073 | Calcium hardness | mg/L as CaCO3 | 105 | 242 | 946 | 961.25 | -1.6121 | 56.6116 | 601.625 | 82.5473 | Calcium hardness | mg/L as CaCO3 | 92 | 240 | 480.7342 | 61.9835 | 360.3671 | 74.4705 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 6.7941 | SDI | >5.0 |  |  |  | 1999-03-14 | 1:35 | 27556 | 25.3 | 98 | 62 | 20 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 4.9865 | 55.0135 | 0.26871 | 6.67 | 6.01 | 240 | 358 | 371 | 1100 | 1106.2903 | -0.57185 | 35.31 | 738.6452 | 67.5081 | 98 | 77 | 21 | 25.9 | 15.7 | 41.6 | 41.6 | 0.49559 | 0.6226 | 16.65 | 16.503 | 3.4125 | 63.0875 | 0.26159 | 6.05 | 5.97 | 222 | 409 | 677 | 717.4904 | -5.9809 | 40.1617 | 563.2452 | 60.5856 | 77 | 62 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 6.36 | 42.14 | 0.26612 | 5.97 | 6.31 | 305 | 677 | 1100 | 1205 | -9.5455 | 17.7898 | 941 | 67.5877 | Turbidity | ntu | 0.127 | 0.443 | 0.859 | 2.102 | -144.7031 | 71.3318 | 1.2725 | 90.0196 | Turbidity | ntu | 0.122 | 0.429 | 0.94397 | 72.4605 | 0.68648 | 82.2283 | Turbidity | ntu | 0.052 | 0.229 | 0.875 | 1.1583 | -32.3714 | 77.2926 | 0.69363 | 92.5032 | Turbidity | ntu | 0.063 | 0.356 | 0.83749 | 72.4891 | 0.59675 | 89.4427 | Turbidity | ntu | 0.058 | 0.263 | 0.636 | 1.3393 | -110.5739 | 77.9468 | 0.80112 | 92.7602 | Turbidity | ntu | 0.05 | 0.312 | 0.73816 | 80.9886 | 0.52508 | 90.4777 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 18 |  |  | MFI |  |  |  |  | 1999-03-15 | 9:50 | 27576 | 25.3 | 99 | 62 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 5.1054 | 55.3946 | 0.26609 | 6.64 | 5.98 | 240 | 366 | 376 | 1104 | 1125.0794 | -1.9094 | 36.1702 | 750.5397 | 68.023 | 99 | 77 | 20 | 25.9 | 16.3 | 42.2 | 42.2 | 0.50597 | 0.61374 | 16.65 | 16.503 | 3.3916 | 64.6084 | 0.25543 | 6.07 | 5.95 | 222 | 411 | 679 | 711.3129 | -4.7589 | 40.9574 | 561.1564 | 60.4388 | 77 | 62 | 21 | 8.7 | 6.3 | 15 | 15 | 0.36845 | 0.58 | 11.1857 | 11.087 | 6.3224 | 42.1776 | 0.26286 | 5.95 | 6.28 | 305 | 679 | 1104 | 1195.4762 | -8.2859 | 18.883 | 937.2381 | 67.4576 | Ammonia | mg NH3-N / L | 0.41 | 0.5 | 1.14 | 0.9725 | 14.693 | 18 | 0.73625 | 44.3124 | Total organic carbon | mg/L | 0.62 | 14.7 | 38.3181 | 95.974 | 26.509 | 97.6612 | Ammonia | mg NH3-N / L | 0.34 | 0.3 | 0.84 | 0.09 | 89.2857 | -13.3333 | 0.195 | -74.359 | Total organic carbon | mg/L | BMRL | 12.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.62 | 0.65 | 1.66 | 0.8075 | 51.3554 | 4.6154 | 0.72875 | 14.9228 | Total organic carbon | mg/L | 0.54 | 12.7 | 32.4792 | 96.1972 | 22.5896 | 97.6095 | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1999-03-16 | 9:25 | 27599 | 25.3 | 100 | 63 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 4.6819 | 55.8181 | 0.26484 | 6.63 | 5.97 | 240 | 360 | 363 | 1123 | 1053.3871 | 6.1988 | 33.8843 | 708.1935 | 66.111 | 100 | 78 | 20 | 25.9 | 15.7 | 41.6 | 41.6 | 0.49559 | 0.6226 | 16.65 | 16.503 | 3.4672 | 65.5328 | 0.25183 | 6.03 | 6.21 | 222 | 412 | 687 | 725.4395 | -5.5953 | 38.843 | 568.7197 | 60.965 | 78 | 63 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 6.531 | 42.969 | 0.26099 | 6.21 | 6.25 | 305 | 687 | 1123 | 1229.1935 | -9.4562 | 15.978 | 958.0968 | 68.1661 | Total organic carbon | mg/L | 0.63 | 15.4 | 79.6 | 92.9425 | -16.7619 | 95.9091 | 54.1713 | 98.837 | UV254 | cm-1 | BMRL | 0.428 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.8 | 77.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.423 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.52 | 14.2 | 84.3 | 86.02 | -2.0403 | 96.338 | 50.11 | 98.9623 | UV254 | cm-1 | BMRL | 0.455 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Glades Raod Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 14 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 23.2941 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1999-03-17 | 10:05 | 27624 | 25.3 | 99 | 64 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 4.748 | 55.752 | 0.26439 | 6.58 | 6.07 | 235 | 360 | 360 | 1136 | 1059.5968 | 6.7256 | 34.7222 | 709.7984 | 66.892 | 99 | 79 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 3.5522 | 65.4478 | 0.25118 | 6.02 | 6.21 | 216 | 411 | 690 | 731.4459 | -6.0066 | 40 | 571.2229 | 62.1864 | 79 | 64 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 6.6335 | 43.8665 | 0.25565 | 6.21 | 6.29 | 302 | 690 | 1136 | 1240.7097 | -9.2174 | 16.1111 | 965.3548 | 68.7162 | UV254 | cm-1 | BMRL | 0.453 | 2.483 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.9116 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.428 | 2.51 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.384 | --- | --- | --- | --- | UV254 | cm-1 | 0.01 | 0.465 | 2.616 | 2.8537 | -9.0883 | 97.8495 | 1.6594 | 99.3974 | SUVA | L/(mg*m) | NR | 3.5827 | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0023 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 8.6275 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1999-03-18 | 12:09 | 27650 | 25.3 | 100 | 64 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 4.786 | 57.214 | 0.25763 | 6.58 | 5.91 | 237 | 362 | 363 | 1142 | 1068.1935 | 6.4629 | 34.7107 | 715.5968 | 66.8808 | 100 | 79 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 3.5704 | 65.9296 | 0.24935 | 6.03 | 6.16 | 218 | 414 | 694 | 736.0892 | -6.0647 | 39.9449 | 575.0446 | 62.0899 | 79 | 64 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3418 | 6.6648 | 43.8352 | 0.25874 | 6.16 | 6.27 | 306 | 694 | 1142 | 1250.9677 | -9.5418 | 15.7025 | 972.4839 | 68.5342 | SUVA | L/(mg*m) | NR | 2.9416 | 3.1193 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.3438 | 3.2429 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.9231 | 3.2746 | 3.1032 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | SOFT | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1999-03-19 | 9:47 | 27671 | 25.3 | 100 | 62 | 20 | 0 | 34 | 6.4 |  | 40.4 | 40.4 | 0.84158 | 0 | 14.5714 | 14.4428 | 4.2778 | 56.7222 | 0.25462 | 6.65 | 6.69 | 232 | 353 | 349 | 1111 | 970.5625 | 12.6406 | 33.5244 | 659.7812 | 64.8368 | 100 | 77 | 19 | 25.4 | 16.6 | 42 | 42 | 0.50684 | 0.60476 | 16.3286 | 16.1844 | 3.4419 | 66.0581 | 0.245 | 6.02 | 6.91 | 212 | 407 | 683 | 705.3735 | -3.2758 | 39.255 | 556.1867 | 61.8833 | 77 | 62 | 21 | 8.6 | 6.4 | 15 | 15 | 0.37018 | 0.57333 | 11.0571 | 10.9595 | 6.4367 | 42.0633 | 0.26055 | 6.91 | 7.01 | 298 | 683 | 1111 | 1200.3438 | -8.0417 | 14.6132 | 941.6719 | 68.3542 | Bromide | mg/L | 183 | 166 | --- | 76.75 | --- | -10.241 | 121.375 | -50.7724 | [8 empty] | Bromide | mg/L | 245 | 170 | --- | -223.75 | --- | -44.1176 | -26.875 | 1011.6279 | [8 empty] | Bromide | mg/L | 189 | 166 | --- | 45.25 | --- | -13.8554 | 105.625 | -78.9349 | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 306 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1999-03-20 | 9:58 | 27695 | 25.3 | 100 | 64 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 4.8619 | 57.1381 | 0.25797 | 6.64 | 5.94 | 233 | 359 | 361 | 1132 | 1077.3871 | 4.8245 | 35.4571 | 719.1935 | 67.6026 | 100 | 79 | 20 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.4393 | 3.5421 | 65.9579 | 0.24924 | 6.04 | 6.22 | 213 | 408 | 686 | 726.4177 | -5.8918 | 40.9972 | 567.2089 | 62.4477 | 79 | 64 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 6.5823 | 43.9177 | 0.25535 | 6.22 | 6.28 | 301 | 686 | 1132 | 1232.4516 | -8.8738 | 16.6205 | 959.2258 | 68.6205 | SDS-Cl2 dose | mg/L | 5.5 | 20 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.5 | 22 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4.5 | 22 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4500130 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -7.2941 | [5 empty] | 1999-03-21 | 10:20 | 27719 | 25.3 | 100 | 65 | 20 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6977 | 5.3823 | 57.1177 | 0.25732 | 6.6 | 5.9 | 228 | 358 | 370 | 1140 | 1162.4516 | -1.9694 | 38.3784 | 766.2258 | 70.2438 | 100 | 80 | 20 | 25.7 | 15.8 | 41.5 | 41.5 | 0.49559 | 0.61928 | 16.5214 | 16.3756 | 3.5903 | 66.4097 | 0.24658 | 6.06 | 5.85 | 209 | 407 | 686 | 729.0633 | -6.2774 | 43.5135 | 568.0316 | 63.2063 | 80 | 65 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 6.7361 | 44.7639 | 0.25052 | 5.85 | 6.25 | 292 | 686 | 1140 | 1245.2258 | -9.2303 | 21.0811 | 965.6129 | 69.7601 | SDS-Free Cl2 residual | mg/L | 0.8 | 0.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.8 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.5 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -0.62745 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1999-03-22 | 8:10 | 27741 | 25.2 | 101 | 65 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7838 | 5.706 | 57.294 | 0.25803 | 6.67 | 6.03 | 229 | 354 | 381 | 1140 | 1218.2063 | -6.8602 | 39.895 | 799.6032 | 71.3608 | 101 | 80 | 19 | 25.8 | 15.6 | 41.4 | 41.4 | 0.493 | 0.62319 | 16.5857 | 16.488 | 3.6538 | 67.8462 | 0.24302 | 6.11 | 5.92 | 210 | 410 | 694 | 740.7692 | -6.7391 | 44.8819 | 575.3846 | 63.5027 | 80 | 65 | 21 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3754 | 6.7913 | 44.7087 | 0.25443 | 5.92 | 6.29 | 296 | 694 | 1140 | 1256.254 | -10.1977 | 22.3097 | 975.127 | 69.645 | SDS-Cl2 demand | mg/L | 4.7 | 19.6 | --- | 97.825 | --- | 76.0204 | 58.7125 | 91.9949 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.7 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.7 | 21.2 | --- | 107.825 | --- | 77.8302 | 64.5125 | 92.7146 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.84 |  |  |  |  | SDS-Cl2 demand | mg/L | 4 | 21.2 | --- | 111.5 | --- | 81.1321 | 66.35 | 93.9714 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.87 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | not specified | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1999-03-23 | 10:10 | 27766 | 25.3 | 101 | 65 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 5.2038 | 57.7962 | 0.25504 | 6.53 | 5.9 | 227 | 358 | 364 | 1166 | 1130.7581 | 3.0225 | 37.6374 | 747.379 | 69.6272 | 101 | 80 | 20 | 25.7 | 15.7 | 41.4 | 41.4 | 0.49386 | 0.62077 | 16.5214 | 16.3756 | 3.7097 | 66.7903 | 0.24518 | 6.03 | 6.15 | 207 | 411 | 697 | 744.9363 | -6.8775 | 43.1319 | 577.9682 | 64.1849 | 80 | 65 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3418 | 6.9397 | 44.5603 | 0.25453 | 6.15 | 6.23 | 293 | 697 | 1166 | 1276.9355 | -9.5142 | 19.5055 | 986.9677 | 70.3131 | SDS-Chlorination temp. | oC | 22.3 | 22.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.5 |  |  |  |  | SDS-Chlorination temp. | oC | 23.9 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.7 |  |  |  |  | SDS-Chlorination temp. | oC | 24.3 | 24.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.8 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 70 | Required influent flow to permeate flow rate ratio, QI:Qp | 1.2:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1999-03-24 | 1:17 | 27793 | 25.3 | 101 | 65 | 20 | 0 | 34.7 | 6.3 |  | 41 | 41 | 0.84634 | 0 | 14.8714 | 14.7401 | 5.0679 | 57.9321 | 0.25444 | 6.59 | 5.86 | 229 | 354 | 364 | 1138 | 1107.5714 | 2.6739 | 37.0879 | 735.7857 | 68.8768 | 101 | 80 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 3.6433 | 66.8567 | 0.24589 | 6.07 | 6.17 | 209 | 409 | 692 | 737.6624 | -6.5986 | 42.5824 | 573.3312 | 63.5464 | 80 | 65 | 21 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.2144 | 6.7087 | 44.7913 | 0.25037 | 6.17 | 6.27 | 297 | 692 | 1138 | 1243.746 | -9.2923 | 18.4066 | 967.873 | 69.3142 | SDS-Chlorination pH | --- | 8.26 | 8.32 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.28 | 8.23 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.37 | 8.36 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 19 | [7 empty] | 1999-03-25 | 10:10 | 27814 | 25.3 | 102 | 65 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 3.9587 | 58.5413 | 0.25252 | 6.77 | 6.17 | 248 | 356 | 352 | 1047 | 935.7419 | 10.6264 | 29.5455 | 643.871 | 61.483 | 102 | 81 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 3.2243 | 68.2757 | 0.24078 | 6.27 | 6.43 | 224 | 401 | 655 | 691.8662 | -5.6284 | 36.3636 | 546.4331 | 59.0069 | 81 | 65 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3418 | 5.617 | 46.383 | 0.24453 | 6.43 | 6.52 | 328 | 655 | 1047 | 1124.4032 | -7.3929 | 6.8182 | 889.7016 | 63.1337 | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 40 | 40 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 20 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1999-03-26 | 2:15 | 27842 | 25.4 | 102 | 65 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 4.1023 | 59.3977 | 0.24743 | 6.67 | 6.14 | 252 | 357 | 360 | 1047 | 964.4516 | 7.8843 | 30 | 662.2258 | 61.9465 | 102 | 80 | 20 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.3908 | 3.2425 | 67.7575 | 0.2419 | 6.32 | 6.4 | 226 | 404 | 658 | 696.5096 | -5.8525 | 37.2222 | 550.2548 | 58.9281 | 80 | 65 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 5.5827 | 45.9173 | 0.24628 | 6.4 | 6.49 | 333 | 658 | 1047 | 1124.5323 | -7.4052 | 7.5 | 891.2661 | 62.6374 | SDS-TOX | mg Cl- /L | BMRL | 1585 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1555 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1535 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95% 2000 ppm MgSO4 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 26.7059 | [5 empty] | 1999-03-27 | 7:30 | 27859 | 25.3 | 102 | 66 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 4.0643 | 59.9357 | 0.24593 | 6.56 | 6.11 | 243 | 352 | 350 | 1057 | 948.8548 | 10.2313 | 30.5714 | 649.4274 | 62.5824 | 102 | 81 | 20 | 25.7 | 15.8 | 41.5 | 41.5 | 0.49559 | 0.61928 | 16.5214 | 16.3756 | 3.2458 | 68.2542 | 0.23992 | 6.3 | 6.36 | 220 | 399 | 658 | 690.1582 | -4.8873 | 37.1429 | 544.5791 | 59.6018 | 81 | 66 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3418 | 5.806 | 46.694 | 0.2429 | 6.36 | 6.42 | 320 | 658 | 1057 | 1143.1935 | -8.1545 | 8.5714 | 900.5968 | 64.468 | SDS-CHCl3 | mg/L | BMRL | 464 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-03-10 | 1999-03-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 385 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-03-24 | 1999-03-24 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 428 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-04-07 | 1999-04-07 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | 40-50% 500 ppm CaCl2 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 16.3725 | [5 empty] | 1999-03-28 | 11:00 | 27886 | 25.4 | 102 | 66 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 4.4821 | 59.5179 | 0.24693 | 6.6 | 6.08 | 250 | 351 | 368 | 1056 | 1028.4194 | 2.6118 | 32.0652 | 698.2097 | 64.1941 | 102 | 81 | 20 | 25.7 | 15.8 | 41.5 | 41.5 | 0.49559 | 0.61928 | 16.5214 | 16.3272 | 3.2458 | 68.2542 | 0.23921 | 6.46 | 6.03 | 225 | 404 | 662 | 695.1582 | -5.0088 | 38.8587 | 549.5791 | 59.0596 | 81 | 66 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 5.7029 | 46.7971 | 0.24165 | 6.03 | 6.35 | 330 | 662 | 1056 | 1138.5806 | -7.8201 | 10.3261 | 900.2903 | 63.3452 | SDS-BDCM | mg/L | BMRL | 71.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:30 | 7:10 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 56.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 6:45 | 6:20 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 77.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:05 | 6:40 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | N/A | [7 empty] | 1999-03-29 | 9:40 | 27908 | 25.4 | 103 | 66 | 21 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.739 | 4.6058 | 58.8942 | 0.25026 | 6.59 | 6.15 | 248 | 359 | 369 | 1054 | 1048.1613 | 0.55396 | 32.7913 | 708.5806 | 65.0005 | 103 | 81 | 20 | 25.7 | 15.8 | 41.5 | 41.5 | 0.49559 | 0.61928 | 16.5214 | 16.3272 | 3.3002 | 68.6998 | 0.23766 | 6.25 | 5.98 | 224 | 406 | 658 | 702.038 | -6.6927 | 39.2954 | 554.019 | 59.5682 | 81 | 66 | 21 | 9 | 6.2 | 15.2 | 15.2 | 0.37018 | 0.59211 | 11.5714 | 11.4354 | 5.6952 | 46.8048 | 0.24432 | 5.98 | 6.48 | 328 | 658 | 1054 | 1137.0323 | -7.8778 | 11.1111 | 897.5161 | 63.4547 | SDS-DBCM | mg/L | 1.6 | 7.68 | --- | 39.6 | --- | 79.1667 | 23.64 | 93.2318 | Operation time | hh.hh | 27454 | 27454 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 7.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 27786 | 27786 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.3 | 9 | --- | 49.425 | --- | 85.5556 | 29.2125 | 95.5499 | Operation time | hh.hh | 28118 | 28118 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1999-03-30 | 8:30 | 27931 | 25.3 | 103 | 66 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.7401 | 4.9759 | 59.5241 | 0.24763 | 6.59 | 5.91 | 231 | 357 | 362 | 1129 | 1095.1774 | 2.9958 | 36.1878 | 728.5887 | 68.2949 | 103 | 81 | 19 | 25.6 | 16 | 41.6 | 41.6 | 0.49819 | 0.61538 | 16.4571 | 16.3119 | 3.528 | 69.472 | 0.2348 | 6.19 | 6.31 | 211 | 407 | 686 | 720.6 | -5.0437 | 41.7127 | 563.8 | 62.5754 | 81 | 66 | 21 | 9 | 6.2 | 15.2 | 15.2 | 0.37018 | 0.59211 | 11.5714 | 11.4693 | 6.6098 | 45.8902 | 0.24993 | 6.31 | 6.39 | 303 | 686 | 1129 | 1241.9677 | -10.006 | 16.2983 | 963.9839 | 68.5679 | SDS-CHBr3 | mg/L | 3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.82 | 6.7 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.6 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.64 | 6.61 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 3.8 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.63 | 6.44 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 8 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1999-03-31 | 8:40 | 27955 | 25.3 | 103 | 66 | 20 | 0 | 34.8 | 6.2 |  | 41 | 41 | 0.84878 | 0 | 14.9143 | 14.7826 | 6.0903 | 58.4097 | 0.25309 | 6.59 | 5.78 | 207 | 359 | 367 | 1222 | 1265.0645 | -3.5241 | 43.5967 | 816.0323 | 74.6334 | 103 | 81 | 19 | 25.8 | 15.7 | 41.5 | 41.5 | 0.49473 | 0.62169 | 16.5857 | 16.4393 | 4.0259 | 68.9741 | 0.23834 | 5.99 | 6.06 | 191 | 412 | 719 | 775.172 | -7.8125 | 47.9564 | 593.586 | 67.8227 | 81 | 66 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.2144 | 7.8132 | 44.6868 | 0.25096 | 6.06 | 6.11 | 262 | 719 | 1222 | 1367.6452 | -11.9186 | 28.6104 | 1043.3226 | 74.8879 | SDS-THM4 | mg/L | 4.6 | 543.08 | --- | 3370.1 | --- | 99.153 | 1956.59 | 99.7649 | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.6 | 449 | --- | 2797.85 | --- | 99.6437 | 1623.425 | 99.9014 | Temperature | oC | 25.5 | 25.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.1 | 514.3 | --- | 3187.6 | --- | 99.0084 | 1850.95 | 99.7245 | Temperature | oC | 25.8 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 16.3725 | [5 empty] | 1999-04-01 | 9:25 | 27979 | 25.4 | 103 | 65 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.6331 | 56.3669 | 0.25998 | 6.58 | 5.89 | 202 | 356 | 377 | 1112 | 1353.6129 | -21.7278 | 46.4191 | 865.3065 | 76.6557 | 103 | 83 | 20 | 26.4 | 17.1 | 43.5 | 43.5 | 0.52414 | 0.6069 | 16.9714 | 16.7719 | 3.9691 | 69.0309 | 0.24296 | 5.98 | 5.76 | 187 | 411 | 704 | 756.8246 | -7.5035 | 50.3979 | 583.9123 | 67.9746 | 83 | 65 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 7.6955 | 45.3045 | 0.24961 | 5.76 | 6.1 | 256 | 704 | 1112 | 1347.0968 | -21.1418 | 32.0955 | 1025.5484 | 75.0377 | SDS-MCAA* | mg/L | BMRL | 6.68 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 154 | 192 | 240.6176 | -16.6667 | 216.3088 | 28.8055 | SDS-MCAA* | mg/L | 1 | 7.54 | --- | 41.875 | --- | 86.7374 | 24.7075 | 95.9526 | Alkalinity | mg/L as CaCO3 | 126 | 172 | 231.277 | -12.5 | 201.6385 | 37.5119 | SDS-MCAA* | mg/L | BMRL | 12.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 129 | 178 | 240.7172 | -17.2727 | 209.3586 | 38.3832 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 2 to 11 | Design system recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1999-04-02 | 8:05 | 28002 | 25.4 | 103 | 66 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.3677 | 57.1323 | 0.2565 | 6.56 | 5.73 | 201 | 359 | 369 | 1248 | 1306.5484 | -4.6914 | 45.5285 | 837.7742 | 76.0079 | 103 | 82 | 20 | 25.7 | 16.1 | 41.8 | 41.8 | 0.50078 | 0.61483 | 16.5214 | 16.3272 | 4.0818 | 68.4182 | 0.23864 | 5.94 | 5.99 | 186 | 413 | 727 | 775.354 | -6.6512 | 49.5935 | 594.177 | 68.6962 | 82 | 66 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.0868 | 44.9132 | 0.24895 | 5.99 | 6.04 | 254 | 727 | 1248 | 1398.3548 | -12.0477 | 31.1653 | 1062.6774 | 76.0981 | SDS-DCAA* | mg/L | BMRL | 99.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 285 | 583 | 964.2647 | 22.3433 | 773.6324 | 63.1608 | SDS-DCAA* | mg/L | 0.5 | 110 | --- | 684.875 | --- | 99.5455 | 397.4375 | 99.8742 | Total dissolved solids | mg/L | 264 | 618 | 1074.1749 | 27.2727 | 846.0875 | 68.7976 | SDS-DCAA* | mg/L | BMRL | 118 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 259 | 617 | 1075.2193 | 30 | 846.1097 | 69.3893 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 3 to 5 psi | System influent flow rate, QI-sys (gpm) | 45.3041 | [5 empty] | 1999-04-03 | 8:05 | 28027 | 25.4 | 104 | 67 | 20 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.5194 | 58.9806 | 0.24846 | 6.59 | 5.7 | 197 | 357 | 369 | 1253 | 1328.871 | -6.0551 | 46.6125 | 848.9355 | 76.7945 | 104 | 82 | 20 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3908 | 4.1597 | 68.8403 | 0.2381 | 5.92 | 5.96 | 182 | 411 | 726 | 784.9367 | -8.118 | 50.6775 | 597.9684 | 69.5636 | 82 | 67 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 8.1552 | 45.3448 | 0.24658 | 5.96 | 6 | 249 | 726 | 1253 | 1403.0323 | -11.9738 | 32.5203 | 1064.5161 | 76.6091 | SDS-TCAA* | mg/L | BMRL | 145 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 168 | 480 | 879.1765 | 35.8779 | 679.5882 | 75.2791 | SDS-TCAA* | mg/L | BMRL | 180 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 146 | 490 | 933.2886 | 42.9688 | 711.6443 | 79.4841 | SDS-TCAA* | mg/L | 0.99 | 128 | --- | 794.8025 | --- | 99.2266 | 461.4013 | 99.7854 | Total hardness | mg/L as CaCO3 | 152 | 487 | 915.7807 | 43.7037 | 701.3903 | 78.3288 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.00022078 | [5 empty] | 1999-04-04 | 3:10 | 28055 | 25.4 | 104 | 67 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 6.7611 | 58.7389 | 0.2502 | 6.6 | 5.8 | 198 | 354 | 376 | 1265 | 1372.2258 | -8.4763 | 47.3404 | 874.1129 | 77.3485 | 104 | 82 | 19 | 25.8 | 16 | 41.8 | 41.8 | 0.49992 | 0.61722 | 16.5857 | 16.3908 | 4.1724 | 69.8276 | 0.23473 | 5.96 | 5.72 | 182 | 413 | 733 | 785.4875 | -7.1606 | 51.5957 | 599.2437 | 69.6284 | 82 | 67 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 8.2967 | 45.2033 | 0.25017 | 5.72 | 6.04 | 250 | 733 | 1265 | 1426.3387 | -12.754 | 33.5106 | 1079.6694 | 76.8448 | SDS-MBAA* | mg/L | BMRL | 0.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 138 | 440 | 826.3824 | 37.8378 | 633.1912 | 78.2056 | SDS-MBAA* | mg/L | BMRL | 0.83 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 124 | 410 | 778.5481 | 43.1193 | 594.2741 | 79.1342 | SDS-MBAA* | mg/L | BMRL | 0.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 141 | 462 | 872.8615 | 41.7355 | 667.4307 | 78.8742 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1999-04-05 | 11:35 | 28075 | 25.4 | 104 | 67 | 20 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 6.9742 | 58.5258 | 0.25039 | 6.6 | 5.74 | 193 | 356 | 377 | 1275 | 1403.8387 | -10.105 | 48.8064 | 890.4194 | 78.3248 | 104 | 82 | 20 | 25.7 | 15.7 | 41.4 | 41.4 | 0.49386 | 0.62077 | 16.5214 | 16.3272 | 4.2734 | 68.7266 | 0.23757 | 5.78 | 5.56 | 179 | 414 | 732 | 798.6815 | -9.1095 | 52.5199 | 606.3408 | 70.4786 | 82 | 67 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 8.3998 | 45.1002 | 0.25074 | 5.56 | 5.96 | 243 | 732 | 1275 | 1433.9516 | -12.4668 | 35.5438 | 1082.9758 | 77.5618 | SDS-DBAA* | mg/L | 0.83 | 1.48 | --- | 4.8925 | --- | 43.9189 | 3.1862 | 73.9506 | Turbidity | ntu | 0.262 | 0.414 | 0.60847 | 40.8578 | 0.51124 | 48.7516 | SDS-DBAA* | mg/L | 0.8 | 14.6 | --- | 87.05 | --- | 94.5205 | 50.825 | 98.426 | Turbidity | ntu | 0.078 | 0.483 | 1.0049 | 65.9389 | 0.74395 | 89.5154 | SDS-DBAA* | mg/L | BMRL | 1.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.138 | 0.461 | 0.87442 | 47.5285 | 0.66771 | 79.3324 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | maximum system recycle flow rates. | [6 empty] | 1999-04-06 | 7:40 | 28095 | 25.4 | 105 | 67 | 20 | 0 | 34.6 | 6.3 |  | 40.9 | 40.9 | 0.84597 | 0 | 14.8286 | 14.6543 | 6.8927 | 59.1073 | 0.24793 | 6.52 | 5.7 | 193 | 356 | 377 | 1264 | 1387.5397 | -9.7737 | 48.8064 | 882.2698 | 78.1246 | 105 | 83 | 20 | 25.8 | 15.9 | 41.7 | 41.7 | 0.49819 | 0.61871 | 16.5857 | 16.3908 | 4.2385 | 69.7615 | 0.23495 | 5.8 | 5.62 | 180 | 414 | 733 | 793.6981 | -8.2808 | 52.2546 | 603.8491 | 70.1912 | 83 | 67 | 21 | 8.8 | 6.3 | 15.1 | 15.1 | 0.37018 | 0.58278 | 11.3143 | 11.1813 | 8.3052 | 45.6948 | 0.2447 | 5.62 | 5.98 | 244 | 733 | 1264 | 1416.0476 | -12.0291 | 35.2785 | 1074.5238 | 77.2923 | SDS-BCAA* | mg/L | BMRL | 15.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.9 | 33 | 74.0691 | 94.1558 | 53.5346 | 98.3188 | SDS-BCAA* | mg/L | BMRL | 15.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.57 | 32 | 72.5016 | 95.5469 | 52.2508 | 98.9091 | SDS-BCAA* | mg/L | BMRL | 17.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.67 | 33.9 | 76.4325 | 95.2817 | 55.1662 | 98.7855 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1999-04-07 | 9:30 | 28121 | 25.4 | 105 | 68 | 20 | 0 | 34.5 | 6.2 |  | 40.7 | 40.7 | 0.84767 | 0 | 14.7857 | 14.6119 | 5.8625 | 60.6375 | 0.24097 | 6.59 | 5.92 | 218 | 358 | 373 | 1179 | 1235.5 | -4.7922 | 41.555 | 804.25 | 72.894 | 105 | 83 | 20 | 25.7 | 15.8 | 41.5 | 41.5 | 0.49559 | 0.61928 | 16.5214 | 16.3272 | 3.826 | 70.174 | 0.23267 | 6.02 | 5.85 | 198 | 409 | 701 | 752.2089 | -7.3051 | 46.9169 | 580.6044 | 65.8976 | 83 | 68 | 21 | 8.8 | 6.2 | 15 | 15 | 0.36672 | 0.58667 | 11.3143 | 11.1813 | 7.0952 | 47.4048 | 0.23587 | 5.85 | 6.26 | 286 | 701 | 1179 | 1290.0323 | -9.4175 | 23.3244 | 995.5161 | 71.2712 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.049 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.105 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.112 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1999-04-08 | 1:25 | 28148 | 25.5 | 105 | 68 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6533 | 5.9255 | 60.5745 | 0.2419 | 6.6 | 5.95 | 218 | 358 | 374 | 1186 | 1247.0968 | -5.1515 | 41.7112 | 810.5484 | 73.1046 | 105 | 83 | 20 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3424 | 3.8691 | 70.1309 | 0.23303 | 6.01 | 5.7 | 198 | 411 | 704 | 758.8101 | -7.7855 | 47.0588 | 584.9051 | 66.1484 | 83 | 68 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.275 | 7.2145 | 47.2855 | 0.23844 | 5.7 | 6.23 | 284 | 704 | 1186 | 1306.9032 | -10.1942 | 24.0642 | 1005.4516 | 71.754 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.1788 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4531 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.2802 | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 45.3041 | [5 empty] | 1999-04-09 | 9:15 | 28168 | 25.5 | 105 | 68 | 20 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6533 | 5.6216 | 60.8784 | 0.2407 | 6.52 | 5.81 | 216 | 360 | 364 | 1183 | 1192.3226 | -0.78805 | 40.6593 | 778.1613 | 72.2423 | 105 | 84 | 20 | 25.8 | 15.8 | 41.6 | 41.6 | 0.49646 | 0.62019 | 16.5857 | 16.3424 | 3.8509 | 70.6491 | 0.23132 | 5.97 | 6.07 | 196 | 408 | 704 | 754.1772 | -7.1274 | 46.1538 | 581.0886 | 66.2702 | 84 | 68 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.275 | 7.2489 | 47.7511 | 0.23612 | 6.07 | 6.15 | 282 | 704 | 1183 | 1309.7742 | -10.7163 | 22.5275 | 1006.8871 | 71.9929 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 25.6667 | [5 empty] | 1999-04-10 | 8:00 | 28191 | 25.4 | 106 | 67 | 20 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.6543 | 5.3695 | 61.1305 | 0.23972 | 6.57 | 5.8 | 215 | 358 | 360 | 1169 | 1143.9062 | 2.1466 | 40.2778 | 751.9531 | 71.4078 | 106 | 84 | 21 | 25.7 | 16 | 41.7 | 41.7 | 0.49905 | 0.61631 | 16.5214 | 16.3272 | 3.8587 | 70.1413 | 0.23278 | 5.98 | 6.14 | 196 | 410 | 704 | 753.7375 | -7.065 | 45.5556 | 581.8687 | 66.3154 | 84 | 67 | 21 | 8.9 | 6.4 | 15.3 | 15.3 | 0.37537 | 0.5817 | 11.4429 | 11.3084 | 7.1712 | 47.3288 | 0.23893 | 6.14 | 6.17 | 281 | 704 | 1169 | 1292.2344 | -10.5419 | 21.9444 | 998.1172 | 71.847 | SDS-HAA5 | mg/L | 0.83 | 253.56 | --- | 1580.3925 | --- | 99.6727 | 916.9763 | 99.9095 | [8 empty] | SDS-HAA5 | mg/L | 2.3 | 312.97 | --- | 1943.9875 | --- | 99.2651 | 1128.4787 | 99.7962 | [8 empty] | SDS-HAA5 | mg/L | 0.99 | 260.6 | --- | 1623.5525 | --- | 99.6201 | 942.0762 | 99.8949 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 19.6375 | [5 empty] | 1999-04-11 | 11:00 | 28217 | 25.4 | 106 | 68 | 20 | 0 | 34.6 | 6.4 |  | 41 | 41 | 0.8439 | 0 | 14.8286 | 14.6543 | 4.4437 | 62.5562 | 0.23426 | 6.54 | 5.96 | 242 | 343 | 362 | 1061 | 1010.75 | 4.7361 | 33.1492 | 686.375 | 64.7423 | 106 | 84 | 20 | 25.7 | 16 | 41.7 | 41.7 | 0.49905 | 0.61631 | 16.5214 | 16.3272 | 3.3899 | 71.6101 | 0.228 | 6.26 | 5.96 | 216 | 404 | 665 | 705.975 | -6.1617 | 40.3315 | 554.9875 | 61.0802 | 84 | 68 | 21 | 8.9 | 6.4 | 15.3 | 15.3 | 0.37537 | 0.5817 | 11.4429 | 11.3084 | 5.781 | 49.219 | 0.22976 | 5.82 | 6.15 | 324 | 665 | 1061 | 1139.2031 | -7.3707 | 10.4972 | 902.1016 | 64.0839 | SDS-HAA6 | mg/L | 0.83 | 268.96 | --- | 1676.6425 | --- | 99.6914 | 972.8012 | 99.9147 | [8 empty] | SDS-HAA6 | mg/L | 2.3 | 328.67 | --- | 2042.1125 | --- | 99.3002 | 1185.3912 | 99.806 | [8 empty] | SDS-HAA6 | mg/L | 0.99 | 277.8 | --- | 1731.0525 | --- | 99.6436 | 1004.4262 | 99.9014 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 19.6375 | [5 empty] | 1999-04-12 | 9:07 | 28239 | 25.5 | 107 | 68 | 20 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.611 | 4.8895 | 62.6105 | 0.23336 | 6.56 | 6.03 | 239 | 354 | 368 | 1087 | 1087.9032 | -0.083093 | 35.0543 | 727.9516 | 67.1681 | 107 | 84 | 20 | 25.6 | 16 | 41.6 | 41.6 | 0.49819 | 0.61538 | 16.4571 | 16.2157 | 3.42 | 72.08 | 0.22497 | 6.26 | 5.92 | 215 | 405 | 673 | 709 | -5.3492 | 41.5761 | 557 | 61.4004 | 84 | 68 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.275 | 6.0293 | 48.9707 | 0.23024 | 5.92 | 6.42 | 322 | 673 | 1087 | 1176.8548 | -8.2663 | 12.5 | 924.9274 | 65.1865 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.8333 | [5 empty] | 1999-04-13 | 10:10 | 28264 | 25.4 | 107 | 68 | 21 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 4.9274 | 61.5726 | 0.238 | 6.59 | 6 | 239 | 358 | 369 | 1087 | 1094.4839 | -0.68849 | 35.2304 | 731.7419 | 67.3382 | 107 | 85 | 20 | 25.6 | 16 | 41.6 | 41.6 | 0.49819 | 0.61538 | 16.4571 | 16.2637 | 3.438 | 72.562 | 0.22414 | 6.02 | 5.93 | 214 | 405 | 673 | 710.6 | -5.5869 | 42.0054 | 557.8 | 61.635 | 85 | 68 | 21 | 8.9 | 6.2 | 15.1 | 15.1 | 0.36845 | 0.5894 | 11.4429 | 11.3084 | 6.0636 | 49.4364 | 0.22875 | 5.93 | 6.4 | 320 | 673 | 1087 | 1179.7258 | -8.5304 | 13.2791 | 926.3629 | 65.4563 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 6.8041 | [5 empty] | 1999-04-14 | 11:00 | 28288 | 25.4 | 107 | 67 | 21 | 0 | 34.5 | 6.5 |  | 41 | 41 | 0.84146 | 0 | 14.7857 | 14.6119 | 4.7865 | 61.2135 | 0.2387 | 6.64 | 6.05 | 239 | 353 | 370 | 1075 | 1065.3077 | 0.90161 | 35.4054 | 717.6538 | 66.697 | 107 | 84 | 20 | 25.6 | 16.2 | 41.8 | 41.8 | 0.50165 | 0.61244 | 16.4571 | 16.2637 | 3.4549 | 72.0451 | 0.22574 | 6.02 | 6.05 | 214 | 407 | 672 | 711.9877 | -5.9505 | 42.1622 | 559.4938 | 61.7511 | 84 | 67 | 21 | 8.9 | 6.5 | 15.4 | 15.4 | 0.37883 | 0.57792 | 11.4429 | 11.3084 | 5.9635 | 48.5365 | 0.23299 | 6.05 | 6.42 | 318 | 672 | 1075 | 1156.7077 | -7.6007 | 14.0541 | 914.3538 | 65.2213
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1999-04-15 | 9:45 | 28311 | 25.4 | 106 | 68 | 20 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 14.8286 | 14.6543 | 5.0032 | 61.9968 | 0.23637 | 6.56 | 5.98 | 234 | 351 | 366 | 1100 | 1102.6452 | -0.24047 | 36.0656 | 734.3226 | 68.1339 | 106 | 84 | 19 | 25.6 | 16.2 | 41.8 | 41.8 | 0.50165 | 0.61244 | 16.4571 | 16.2637 | 3.4728 | 72.5272 | 0.22424 | 6.01 | 5.86 | 210 | 404 | 672 | 710.5679 | -5.7393 | 42.623 | 557.284 | 62.3172 | 84 | 68 | 21 | 9 | 6.2 | 15.2 | 15.2 | 0.37018 | 0.59211 | 11.5714 | 11.4354 | 6.2302 | 48.7698 | 0.23448 | 5.86 | 6.33 | 311 | 672 | 1100 | 1196.0323 | -8.7302 | 15.0273 | 934.0161 | 66.7029 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 6.7941 | [5 empty] | 1999-04-16 | 9:30 | 28335 | 25.4 | 106 | 68 | 20 | 0 | 34.5 | 6 |  | 40.5 | 40.5 | 0.85185 | 0 | 14.7857 | 14.6119 | 4.805 | 62.195 | 0.23494 | 6.54 | 6.03 | 237 | 358 | 361 | 1111 | 1074 | 3.3303 | 34.349 | 717.5 | 66.9686 | 106 | 84 | 20 | 25.6 | 15.7 | 41.3 | 41.3 | 0.493 | 0.61985 | 16.4571 | 16.2637 | 3.4672 | 71.5328 | 0.22736 | 6 | 6.3 | 212 | 403 | 677 | 714.4395 | -5.5302 | 41.2742 | 558.7197 | 62.0561 | 84 | 68 | 21 | 9 | 6 | 15 | 15 | 0.36326 | 0.6 | 11.5714 | 11.4354 | 6.3175 | 48.6825 | 0.2349 | 6.3 | 6.4 | 316 | 677 | 1111 | 1218.5 | -9.676 | 12.4654 | 947.75 | 66.6579 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 38.5 | [5 empty] | 1999-04-17 | 8:09 | 28357 | 25.3 | 107 | 67 | 20 | 0 | 34.5 | 6.5 |  | 41 | 41 | 0.84146 | 0 | 14.7857 | 14.6552 | 4.4577 | 62.5423 | 0.23432 | 6.55 | 5.99 | 236 | 357 | 358 | 1080 | 1005.5385 | 6.8946 | 34.0782 | 681.7692 | 65.3842 | 107 | 84 | 19 | 25.6 | 16.6 | 42.2 | 42.2 | 0.50857 | 0.60664 | 16.4571 | 16.3119 | 3.4359 | 73.0641 | 0.22325 | 6 | 6.26 | 211 | 405 | 673 | 704.1807 | -4.6331 | 41.0615 | 554.5904 | 61.9539 | 84 | 67 | 21 | 9 | 6.5 | 15.5 | 15.5 | 0.38056 | 0.58065 | 11.5714 | 11.4693 | 6.0923 | 48.4077 | 0.23693 | 6.26 | 6.37 | 313 | 673 | 1080 | 1171.4615 | -8.4687 | 12.5698 | 922.2308 | 66.0606 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 45.2941 | [5 empty] | 1999-04-18 | 10:30 | 28383 | 25.3 | 108 | 69 | 21 | 0 | 34.5 | 6.3 |  | 40.8 | 40.8 | 0.84559 | 0 | 14.7857 | 14.6552 | 5.3829 | 62.1171 | 0.23593 | 6.47 | 5.92 | 231 | 356 | 375 | 1119 | 1163.5714 | -3.9831 | 38.4 | 769.2857 | 69.9721 | 108 | 85 | 19 | 25.6 | 16 | 41.6 | 41.6 | 0.49819 | 0.61538 | 16.4571 | 16.3119 | 3.582 | 73.918 | 0.22067 | 5.98 | 5.83 | 208 | 407 | 684 | 725.4 | -6.0526 | 44.5333 | 566.2 | 63.2639 | 85 | 69 | 22 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3418 | 6.4329 | 48.5671 | 0.23353 | 5.83 | 6.28 | 307 | 684 | 1119 | 1216.5873 | -8.7209 | 18.1333 | 950.2937 | 67.6942 | Qp/QT (THM4), % | 87.4833 | 94.1688 |  | Qp/QT (HAA5), % | 78.9617 | 89.6451 | [11 empty] | Qp/QT (THM4), % | 84.2646 | 92.3111 |  | Qp/QT (HAA5), % | 83.3585 | 92.0494 | [11 empty] | Qp/QT (THM4), % | 86.8617 | 93.9317 |  | Qp/QT (HAA5), % | 79.5809 | 89.9811 | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[11 empty] | 1999-04-19 | 10:00 | 28406 | 25.4 | 108 | 69 | 20 | 0 | 34.5 | 6.3 |  | 40.8 | 40.8 | 0.84559 | 0 | 14.7857 | 14.6119 | 5.3455 | 63.1545 | 0.23137 | 6.63 | 5.96 | 229 | 358 | 372 | 1121 | 1155.0952 | -3.0415 | 38.4409 | 763.5476 | 70.0084 | 108 | 85 | 19 | 25.6 | 16 | 41.6 | 41.6 | 0.49819 | 0.61538 | 16.4571 | 16.2637 | 3.6 | 73.9 | 0.22008 | 5.96 | 5.85 | 207 | 407 | 684 | 727 | -6.2865 | 44.3548 | 567 | 63.4921 | 85 | 69 | 21 | 8.9 | 6.3 | 15.2 | 15.2 | 0.37191 | 0.58553 | 11.4429 | 11.3084 | 6.4671 | 49.5329 | 0.2283 | 5.85 | 6.34 | 305 | 684 | 1121 | 1219.4127 | -8.779 | 18.0108 | 951.7063 | 67.9523 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 117.8868 | 60.3592 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 76.0539 | 37.1708 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 109.074 | 56.1161 | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1999-04-20 | 10:30 | 28430 | 25.3 | 109 | 69 | 20 | 0 | 34.5 | 6.2 |  | 40.7 | 40.7 | 0.84767 | 0 | 14.7857 | 14.6552 | 4.2361 | 64.7639 | 0.22629 | 6.57 | 6.14 | 258 | 362 | 370 | 1038 | 993.2258 | 4.3135 | 30.2703 | 681.6129 | 62.1486 | 109 | 86 | 19 | 25.5 | 16.1 | 41.6 | 41.6 | 0.49905 | 0.61298 | 16.3929 | 16.2481 | 3.1538 | 75.3462 | 0.21565 | 6.19 | 6.02 | 229 | 405 | 656 | 683.7578 | -4.2314 | 38.1081 | 544.3789 | 57.9337 | 86 | 69 | 22 | 9 | 6.2 | 15.2 | 15.2 | 0.37018 | 0.59211 | 11.5714 | 11.4693 | 5.3155 | 50.1845 | 0.22854 | 6.02 | 6.48 | 348 | 656 | 1038 | 1103.0968 | -6.2714 | 5.9459 | 879.5484 | 60.4342 | SDS-HAA5b, mg/L | 32.4635 | 15.5673 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 51.185 | 26.187 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 35.0982 | 16.744 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 3.7 | [5 empty] | 1999-04-21 | 9:50 | 28453 | 25.4 | 108 | 69 | 21 | 0 | 34.7 | 6.2 |  | 40.9 | 40.9 | 0.84841 | 0 | 14.8714 | 14.6966 | 4.2922 | 63.2078 | 0.23251 | 6.59 | 6.12 | 254 | 360 | 367 | 1041 | 999.4355 | 3.9927 | 30.7902 | 683.2177 | 62.823 | 108 | 86 | 20 | 25.7 | 15.9 | 41.6 | 41.6 | 0.49732 | 0.61779 | 16.5214 | 16.3272 | 3.2186 | 73.7814 | 0.22129 | 6.17 | 6.04 | 225 | 403 | 655 | 690.7107 | -5.452 | 38.6921 | 546.8553 | 58.8557 | 86 | 69 | 22 | 9 | 6.2 | 15.2 | 15.2 | 0.37018 | 0.59211 | 11.5714 | 11.4354 | 5.419 | 50.081 | 0.22834 | 6.04 | 6.52 | 341 | 655 | 1041 | 1110.8065 | -6.7057 | 7.0845 | 882.9032 | 61.3774 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 9.5 | [5 empty] | 1999-04-22 | 10:30 | 28477 | 25.4 | 108 | 69 | 20 | 0 | 34.5 | 6.1 | X | 40.6 | 40.6 | 0.84975 | 0 | 14.7857 | 14.6119 | 4.3255 | 64.1745 | 0.22769 | 6.53 | 6.04 | 256 | 361 | 369 | 1047 | 1008.0984 | 3.7155 | 30.6233 | 688.5492 | 62.8204 | 108 | 85 | 20 | 25.5 | 15.9 | 41.4 | 41.4 | 0.49559 | 0.61594 | 16.3929 | 16.2002 | 3.2074 | 73.2926 | 0.22103 | 6.21 | 6.01 | 227 | 405 | 658 | 690.4717 | -4.9349 | 38.4824 | 547.7358 | 58.5567 | 85 | 69 | 21 | 9 | 6.1 | 15.1 | 15.1 | 0.36672 | 0.59603 | 11.5714 | 11.4354 | 5.439 | 50.561 | 0.22617 | 6.01 | 6.51 | 345 | 658 | 1047 | 1119.8033 | -6.9535 | 6.5041 | 888.9016 | 61.1881 | SDS-CDb, mg/L | 6.565 | 5.5689 |  | SDS-CDb, mg/L | 7.8347 | 6.2429 | [11 empty] | SDS-CDb, mg/L | 7.2963 | 5.9687 |  | SDS-CDb, mg/L | 7.4458 | 6.0118 | [11 empty] | SDS-CDb, mg/L | 6.2598 | 5.0438 |  | SDS-CDb, mg/L | 7.5121 | 5.7232 | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 5 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | TOCb, mg/L | 2.4787 | 1.4913 |  | TOCb, mg/L | 3.7374 | 2.1594 | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 2.3173 | 1.3501 |  | TOCb, mg/L | 3.3133 | 1.8906 | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | 0.069779 | 0.037611 |  | UV254 b, cm-1 | 0.10291 | 0.055586 | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 10 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Bromideb, mg/L | 180.8722 | 182.0087 |  | Bromideb, mg/L | 179.4235 | 181.2397 | [11 empty] | Bromideb, mg/L | 233.1985 | 239.2333 |  | Bromideb, mg/L | 232.5189 | 239.0371 | [11 empty] | Bromideb, mg/L | 185.9782 | 187.6043 |  | Bromideb, mg/L | 184.3036 | 186.6957 | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 26 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Alkb, mg/L CaCO3 | 112.7537 | 111.2829 |  | Alkb, mg/L CaCO3 | 114.6284 | 112.2781 | [11 empty] | Alkb, mg/L CaCO3 | 91.7765 | 89.8453 |  | Alkb, mg/L CaCO3 | 91.9939 | 89.9081 | [11 empty] | Alkb, mg/L CaCO3 | 90.8904 | 89.335 |  | Alkb, mg/L CaCO3 | 92.4922 | 90.2042 | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 60.219 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | T-Hdb, mg/L CaCO3 | 141.2731 | 132.0471 |  | T-Hdb, mg/L CaCO3 | 153.0328 | 138.2898 | [11 empty] | T-Hdb, mg/L CaCO3 | 132.9736 | 121.2257 |  | T-Hdb, mg/L CaCO3 | 134.2965 | 121.6078 | [11 empty] | T-Hdb, mg/L CaCO3 | 132.7584 | 121.588 |  | T-Hdb, mg/L CaCO3 | 144.2622 | 127.8298 | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 35.9667 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Ca-Hdb, mg/L CaCO3 | 129.2677 | 122.1811 |  | Ca-Hdb, mg/L CaCO3 | 138.3006 | 126.9762 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 115.1971 | 105.3804 |  | Ca-Hdb, mg/L CaCO3 | 116.3026 | 105.6997 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 122.9994 | 113.3136 |  | Ca-Hdb, mg/L CaCO3 | 132.9742 | 118.7259 | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 106.1856 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on E23: S Allgeier (10/4/99): Reviewer replaced value of 29.2 ft with 14 ft -- a value more typical for this membrane.
Note on AR6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on BP6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on DQ25: C. Rice: Consultant verified value; no explanation given.

## ESNA. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Boca Raton | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 216 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.58 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.61 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.6 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500130 | Membrane trade name | ESNA | Temperature normalized MTCW (gfd/psi) | 0.32 | Calcium Hardness (mg/L as CaCO3) | 260 | Dual Media Filtration | Silica/Garnet | Pilot-Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 39.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 23.1 | [6 empty] | System feed flow rate during sample collection (gpm) | 39.1 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 24.1 | [6 empty] | System feed flow rate during sample collection (gpm) | 38.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 23.6 | [6 empty] | System feed flow rate during sample collection (gpm) | 39.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 23.7 | [6 empty] | System feed flow rate during sample collection (gpm) | 38.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 20.5 | [6 empty] | System feed flow rate during sample collection (gpm) | 38.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 20.5 |  |  |  |  | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Membrane element model number | 4040-UHA-ESNA |  |  | LSI | 0.09 | Scale Inhibitor Addition | Calgon EL-5600 4.0 mg/l | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 39.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 39.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 39.1 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 39.1 | [6 empty] | System influent flow rate during sample collection (gpm) | 38.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 38.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 39.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 39.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 38.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 38.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 38.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 38.5 |  |  |  |  | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 100 - 180 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 1 | pH Adjustment | sulfuric acid to pH 6.0-6.4 | Pilot Scale | 1998-03-17 | 1:15 | 19400 | 25.2 | 150 | 109 | 19.6 | 0 | 33.5 | 6.3 |  | 39.8 | 39.8 | 0.84171 | 0 | 13.5126 | 13.433 | 13.1714 | 96.7286 | 0.13887 | 6.84 | 6.25 | 41 | 269 | 401 | 1740 | 2315.2857 | -33.0624 | 89.7756 | 1358.1429 | 96.9812 | 150 | 127 | 18 | 24 | 18.1 | 42.1 | 42.1 | 0.50805 | 0.57007 | 14.521 | 14.4354 | 6.1198 | 114.3802 | 0.12621 | 6.24 |  | 33 | 401 | 870 | 888.9558 | -2.1788 | 91.7706 | 644.9779 | 94.8835 | 127 | 109 | 21 | 9.4 | 6.3 | 15.7 | 15.7 | 0.37133 | 0.59873 | 11.3748 | 11.3077 | 13.9508 | 83.0492 | 0.13616 |  | 6.68 | 71 | 870 | 1740 | 2062.1587 | -18.5149 | 82.2943 | 1466.0794 | 95.1572 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamid | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 1 | Cartridge Filtration | 5 um exclusion size | Pilot Scale | 1998-03-18 | 10:30 | 19421 | 25.2 | 153 | 113 | 19.5 | 0 | 34 | 6.1 |  | 40.1 | 40.1 | 0.84788 | 0 | 13.7143 | 13.6334 | 13.4434 | 100.0566 | 0.13626 | 6.86 | 6.21 | 39 | 394 | 394 | 1754 | 2372.6885 | -35.273 | 90.1015 | 1383.3443 | 97.1807 | 153 | 130 | 18 | 24.7 | 16.6 | 41.3 | 41.3 | 0.48864 | 0.59806 | 14.9445 | 14.8564 | 6.3306 | 117.1694 | 0.12679 | 6.18 |  | 31 | 394 | 879 | 934.1265 | -6.2715 | 92.132 | 664.0633 | 95.3318 | 130 | 113 | 21 | 9.3 | 6.1 | 15.4 | 15.4 | 0.3629 | 0.6039 | 11.2538 | 11.1874 | 14.2922 | 86.2078 | 0.12977 |  | 6.69 | 68 | 879 | 1754 | 2115.4426 | -20.6068 | 82.7411 | 1497.2213 | 95.4583 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 0.01 |  |  |  | 1998-03-19 | 8:30 | 19443 | 24 | 153 | 113 | 19.3 | 0 | 33.6 | 6.1 |  | 39.7 | 39.7 | 0.84635 | 0 | 13.5529 | 13.9595 | 14.0028 | 99.6972 | 0.14002 | 6.87 | 6.22 | 40 | 398 | 413 | 1826 | 2467.5574 | -35.1346 | 90.3148 | 1440.2787 | 97.2228 | 153 | 130 | 18 | 24.4 | 16 | 40.4 | 40.4 | 0.47598 | 0.60396 | 14.763 | 15.2059 | 6.6975 | 116.8025 | 0.13018 | 6.1 |  | 33 | 413 | 902 | 992.5 | -10.0333 | 92.0097 | 702.75 | 95.3042 | 130 | 113 | 21 | 9.1 | 6.1 | 15.2 | 15.2 | 0.35952 | 0.59868 | 11.0118 | 11.3421 | 14.5608 | 85.9392 | 0.13198 |  | 6.68 | 68 | 902 | 1826 | 2146.1639 | -17.5336 | 83.5351 | 1524.082 | 95.5383 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | hydrophylic | Number of elements per pressure vessel, Ne | 7 | Total aluminum (mg/L) | 1 |  |  |  | 1998-03-20 | 8:06 | 19465 | 24 | 154 | 115 | 19.3 | 0 | 34.3 | 5.9 |  | 40.2 | 40.2 | 0.85323 | 0 | 13.8353 | 14.2504 | 14.5723 | 100.6277 | 0.14161 | 6.88 | 6.13 | 41 | 397 | 414 | 1856 | 2582.4576 | -39.141 | 90.0966 | 1498.2288 | 97.2634 | 154 | 131 | 18 | 25 | 15.4 | 40.4 | 40.4 | 0.47092 | 0.61881 | 15.1261 | 15.5798 | 6.8844 | 117.6156 | 0.13246 | 6.16 |  | 34 | 414 | 906 | 1030.8831 | -13.784 | 91.7874 | 722.4416 | 95.2937 | 131 | 115 | 21 | 9.2 | 5.9 | 15.1 | 15.1 | 0.35446 | 0.60927 | 11.1328 | 11.4668 | 14.8958 | 87.1042 | 0.13164 |  | 6.77 | 69 | 906 | 1856 | 2211.1525 | -19.1354 | 83.3333 | 1558.5763 | 95.5729 | Sampling date | MM/DD/YY | 1998-04-01 | 1998-04-01 | 1998-04-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-01 | 1998-04-01 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-15 | 1998-04-15 | 1998-04-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-15 | 1998-04-15 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-29 | 1998-04-29 | 1998-04-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-29 | 1998-04-29 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-13 | 1998-05-13 | 1998-05-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-13 | 1998-05-13 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 13
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 4 | Fluoride (mg/L) | 0.231 |  |  |  | 1998-03-21 | 7:50 | 19489 | 23 | 154 | 115 | 19.1 | 0 | 32.3 | 6.1 |  | 38.4 | 38.4 | 0.84115 | 0 | 13.0286 | 13.822 | 13.6418 | 101.7582 | 0.13583 | 6.87 | 6.21 | 31 | 384 | 405 | 1823 | 2385.3607 | -30.8481 | 92.3457 | 1395.1803 | 97.7781 | 154 | 132 | 18 | 22.8 | 17.5 | 40.3 | 40.3 | 0.4878 | 0.56576 | 13.795 | 14.6351 | 6.1763 | 118.8237 | 0.12317 | 6.16 |  | 31 | 405 | 894 | 892.2686 | 0.19367 | 92.3457 | 648.6343 | 95.2207 | 132 | 115 | 21 | 9.5 | 6.1 | 15.6 | 15.6 | 0.36627 | 0.60897 | 11.4958 | 12.1959 | 14.7275 | 87.7725 | 0.13895 |  | 6.78 | 66 | 894 | 1823 | 2183.5082 | -19.7755 | 83.7037 | 1538.7541 | 95.7108 | Sampling time | hh:mm | 8:45 | 8:45 | 8:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:45 | 8:45 | --- | --- | --- | --- | Sampling time | hh:mm | 8:10 | 8:20 | 8:25 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:35 | 8:20 | --- | --- | --- | --- | Sampling time | hh:mm | 8:55 | 9:00 | 9:05 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:10 | 9:00 | --- | --- | --- | --- | Sampling time | hh:mm | 7:25 | 7:35 | 7:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:50 | 7:35 | --- | --- | --- | --- | Sampling time | hh:mm | 9:35 | 9:50 | 9:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:05 | 9:40 | --- | --- | --- | --- | Sampling time | hh:mm | 9:35 | 9:50 | 9:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:05 | 9:40 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881(May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 2 | Phosphate (mg/L) | < 0.1 |  |  |  | 1998-03-22 | 9:00 | 19514 | 22 | 153 | 114 | 18.9 | 0 | 34.4 | 6.2 |  | 40.6 | 40.6 | 0.84729 | 0 | 13.8756 | 15.1623 | 13.7003 | 100.8997 | 0.15027 | 6.87 | 6.18 | 41 | 403 | 404 | 1786 | 2418.0645 | -35.39 | 89.8515 | 1411.0323 | 97.0943 | 153 | 131 | 18 | 24 | 17.2 | 41.2 | 41.2 | 0.49286 | 0.58252 | 14.521 | 15.8675 | 6.3323 | 117.6677 | 0.13485 | 6.11 |  | 31 | 404 | 889 | 924.4651 | -3.9893 | 92.3267 | 664.2326 | 95.333 | 131 | 114 | 20 | 9 | 6.2 | 15.2 | 15.2 | 0.36121 | 0.59211 | 10.8908 | 11.9006 | 14.2034 | 88.2966 | 0.13478 |  | 6.72 | 66 | 889 | 1786 | 2083.6774 | -16.6673 | 83.6634 | 1486.3387 | 95.5596 | Operation time | hh.hh | 19890 | 19890 | 19890 | --- | --- | --- | --- | --- | Operation time | hh.hh | 19890 | 19890 | --- | --- | --- | --- | Operation time | hh.hh | 20058 | 20058 | 20058 | --- | --- | --- | --- | --- | Operation time | hh.hh | 20058 | 20058 | --- | --- | --- | --- | Operation time | hh.hh | 20394 | 20394 | 20394 | --- | --- | --- | --- | --- | Operation time | hh.hh | 20394 | 20394 | --- | --- | --- | --- | Operation time | hh.hh | 20729 | 20729 | 20729 | --- | --- | --- | --- | --- | Operation time | hh.hh | 20729 | 20729 | --- | --- | --- | --- | Operation time | hh.hh | 21091 | 21091 | 21091 | --- | --- | --- | --- | --- | Operation time | hh.hh | 21091 | 21091 | --- | --- | --- | --- | Operation time | hh.hh | 21091 | 21091 | 21091 | --- | --- | --- | --- | --- | Operation time | hh.hh | 21091 | 21091 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 130
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.88542 | Sulfate (mg/L) | 17.1 |  |  |  | 1998-03-23 | 8:50 | 19538 | 22 | 155 | 116 | 19 | 0 | 32.2 | 6.1 |  | 38.3 | 38.3 | 0.84073 | 0 | 12.9882 | 14.1926 | 13.3564 | 103.1436 | 0.1376 | 6.87 | 6.13 | 38 | 402 | 405 | 1812 | 2342.2787 | -29.2648 | 90.6173 | 1373.6393 | 97.2336 | 155 | 132 | 18 | 23.8 | 16.4 | 40.2 | 40.2 | 0.47767 | 0.59204 | 14.4 | 15.7353 | 6.471 | 119.029 | 0.1322 | 6.09 |  | 30 | 405 | 892 | 949.2073 | -6.4134 | 92.5926 | 677.1037 | 95.5694 | 132 | 115 | 21 | 8.9 | 6.1 | 15 | 15 | 0.35614 | 0.59333 | 10.7697 | 11.7684 | 14.2857 | 88.2143 | 0.13341 |  | 6.75 | 66 | 892 | 1812 | 2097.1475 | -15.7366 | 83.7037 | 1494.5738 | 95.584 | pH | --- | 5.48 | 6.45 | 7.03 | --- | --- | --- | --- | --- | pH | --- | 5.37 | 6.71 | --- | --- | --- | --- | pH | --- | 5.51 | 6.57 | 7.2 | --- | --- | --- | --- | --- | pH | --- | 5.5 | 6.33 | --- | --- | --- | --- | pH | --- | 5.33 | 6.48 | 7.08 | --- | --- | --- | --- | --- | pH | --- | 5.46 | 6.43 | --- | --- | --- | --- | pH | --- | 5.61 | 6.76 | 7.19 | --- | --- | --- | --- | --- | pH | --- | 5.69 | 6.99 | --- | --- | --- | --- | pH | --- | 5.51 | 6.63 | 7.12 | --- | --- | --- | --- | --- | pH | --- | 5.42 | 6.54 | --- | --- | --- | --- | pH | --- | 5.53 | 6.6 | 7.16 | --- | --- | --- | --- | --- | pH | --- | 5.47 | 6.58 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 17
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 6.1979 | Calcium (mg/L) | 97.9 |  |  |  | 1998-03-24 | 2:30 | 19553 | 25 | 155 | 116 | 19 | 0 | 34.3 | 6.3 |  | 40.6 | 40.6 | 0.84483 | 0 | 13.8353 | 13.8353 | 13.6233 | 102.8767 | 0.13448 | 6.83 | 6.13 | 41 | 398 | 407 | 1690 | 2399.6667 | -41.9921 | 89.9263 | 1403.3333 | 97.0784 | 155 | 126 | 19 | 23.4 | 16.8 | 40.2 | 40.2 | 0.48105 | 0.58209 | 14.158 | 14.158 | 6.3616 | 115.1384 | 0.12296 | 6.12 |  | 32 | 407 | 898 | 929.3214 | -3.4879 | 92.1376 | 668.1607 | 95.2107 | 126 | 109 | 21 | 9.7 | 6.3 | 16 | 16 | 0.3764 | 0.60625 | 11.7378 | 11.7378 | 14.6012 | 81.8988 | 0.14332 |  | 6.65 | 72 | 897 | 1690 | 2167.2381 | -28.2389 | 82.3096 | 1532.119 | 95.3006 | Temperature | oC | 26 | 25.5 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 25.5 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.5 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 25.5 | --- | --- | --- | --- | Temperature | oC | 26 | 25.5 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 25.5 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 24.7917 | Barium (mg/L) | 0.5 |  |  |  | 1998-03-25 | 8:50 | 19563 | 24 | 152 | 112 | 20 | 0 | 34.2 | 6.1 |  | 40.3 | 40.3 | 0.84864 | 0 | 13.795 | 14.2088 | 14.1102 | 97.8898 | 0.14515 | 6.79 | 6.12 | 43 | 406 | 414 | 1800 | 2494.0328 | -38.5574 | 89.6135 | 1454.0164 | 97.0427 | 152 | 128 | 18 | 24.8 | 16.5 | 41.3 | 41.3 | 0.4878 | 0.60048 | 15.005 | 15.4552 | 6.5682 | 115.4318 | 0.13389 | 6.06 |  | 32 | 407 | 891 | 970.6364 | -8.9379 | 92.2705 | 688.8182 | 95.3544 | 128 | 111 | 21 | 9.4 | 6.1 | 15.5 | 15.5 | 0.36458 | 0.60645 | 11.3748 | 11.716 | 14.4826 | 84.0174 | 0.13945 |  | 6.74 | 73 | 891 | 1800 | 2151.5246 | -19.5291 | 82.3671 | 1521.2623 | 95.2014 | Alkalinity | mg/L as CaCO3 | 17 | 122 | 760 | 673.25 | 11.4145 | 86.0656 | 397.625 | 95.7246 | Alkalinity | mg/L as CaCO3 | 8 | 120 | 274.9222 | 93.4426 | 197.4611 | 95.9486 | Alkalinity | mg/L as CaCO3 | 14 | 126 | 670 | 760.6667 | -13.5323 | 88.8889 | 443.3333 | 96.8421 | Alkalinity | mg/L as CaCO3 | 14 | 92 | 217.32 | 88.8889 | 154.66 | 90.9479 | Alkalinity | mg/L as CaCO3 | 14 | 145 | 810 | 832.75 | -2.8086 | 90.3448 | 488.875 | 97.1363 | Alkalinity | mg/L as CaCO3 | 13 | 140 | 339.8133 | 91.0345 | 239.9067 | 94.5812 | Alkalinity | mg/L as CaCO3 | 14 | 106 | 628 | 589 | 6.2102 | 86.7925 | 347.5 | 95.9712 | Alkalinity | mg/L as CaCO3 | 10 | 114 | 270.9936 | 90.566 | 192.4968 | 94.8051 | Alkalinity | mg/L as CaCO3 | 14 | 122 | 604 | 649.2941 | -7.499 | 88.5246 | 385.6471 | 96.3697 | Alkalinity | mg/L as CaCO3 | 12 | 114 | 230.1667 | 90.1639 | 172.0833 | 93.0266 | Alkalinity | mg/L as CaCO3 | 14 | 112 | 598 | 590.4706 | 1.2591 | 87.5 | 351.2353 | 96.0141 | Alkalinity | mg/L as CaCO3 | 14 | 112 | 223.6111 | 87.5 | 167.8056 | 91.657 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.3958 | Strontium (mg/L) | 0.2 |  |  |  | 1998-03-26 | 8:40 | 19587 | 25 | 152 | 113 | 19.2 | 0 | 34.9 | 6.1 |  | 41 | 41 | 0.85122 | 0 | 14.0773 | 14.0773 | 13.8211 | 99.4789 | 0.14151 | 6.83 | 6.41 | 37 | 400 | 395 | 1860 | 2443.2295 | -31.3564 | 90.6329 | 1419.1148 | 97.3927 | 152 | 129 | 18 | 25.1 | 15.8 | 40.9 | 40.9 | 0.47852 | 0.61369 | 15.1866 | 15.1866 | 6.5851 | 115.9149 | 0.13101 | 6.46 |  | 28 | 395 | 892 | 978.019 | -9.6434 | 92.9114 | 686.5095 | 95.9214 | 129 | 113 | 20 | 8.7 | 6.1 | 14.8 | 14.8 | 0.35277 | 0.58784 | 10.5277 | 10.5277 | 14.1675 | 86.8325 | 0.12124 |  | 7.09 | 65 | 892 | 1860 | 2071.4918 | -11.3705 | 83.5443 | 1481.7459 | 95.6133 | Total dissolved solids | mg/L | 22 | 393 | 1824 | 2340.75 | -28.3306 | 94.402 | 1366.875 | 98.3905 | Total dissolved solids | mg/L | 19 | 394 | 912.7126 | 95.1654 | 653.3563 | 97.0919 | Total dissolved solids | mg/L | 40 | 414 | 1860 | 2533.3333 | -36.2007 | 90.3382 | 1473.6667 | 97.2857 | Total dissolved solids | mg/L | 29.9 | 420 | 1046.7607 | 92.7778 | 733.3803 | 95.923 | Total dissolved solids | mg/L | 38 | 409 | 1837 | 2356.75 | -28.2934 | 90.709 | 1382.875 | 97.2521 | Total dissolved solids | mg/L | 27.6 | 410 | 1011.6427 | 93.2518 | 710.8213 | 96.1172 | Total dissolved solids | mg/L | 37 | 412 | 1880 | 2380.75 | -26.6356 | 91.0194 | 1396.375 | 97.3503 | Total dissolved solids | mg/L | 26 | 416 | 1004.7261 | 93.6893 | 710.3631 | 96.3399 | Total dissolved solids | mg/L | 37.3 | 427 | 1930 | 2329.6529 | -20.7074 | 91.2646 | 1378.3265 | 97.2938 | Total dissolved solids | mg/L | 28.1 | 428 | 883.4417 | 93.4192 | 655.7208 | 95.7146 | Total dissolved solids | mg/L | 36.9 | 428 | 1934 | 2337.4882 | -20.8629 | 91.3785 | 1382.7441 | 97.3314 | Total dissolved solids | mg/L | 28 | 423 | 872.8611 | 93.4579 | 647.9306 | 95.6785 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 71 | Permeate flow rate from system, Qp-sys (gpm) | 37.1875 | Reactive silica (mg/L as SiO2) | 78 |  |  |  | 1998-03-27 | 9:15 | 19611 | 25 | 152 | 112 | 19 | 0 | 34.4 | 6.2 |  | 40.6 | 40.6 | 0.84729 | 0 | 13.8756 | 13.8756 | 13.5871 | 99.4129 | 0.13958 | 6.82 | 6.33 | 36 | 383 | 396 | 1806 | 2393.4194 | -32.526 | 90.9091 | 1394.7097 | 97.4188 | 152 | 129 | 18 | 25.3 | 16.6 | 41.9 | 41.9 | 0.49371 | 0.60382 | 15.3076 | 15.3076 | 6.4843 | 116.0157 | 0.13194 | 6.34 |  | 28 | 396 | 889 | 956.8675 | -7.6341 | 92.9293 | 676.4337 | 95.8606 | 129 | 112 | 20 | 9 | 6.2 | 15.2 | 15.2 | 0.36121 | 0.59211 | 10.8908 | 10.8908 | 14.2206 | 86.2794 | 0.12623 |  | 6.78 | 65 | 889 | 1806 | 2085.129 | -15.4556 | 83.5859 | 1487.0645 | 95.629 | Total hardness | mg/L as CaCO3 | 12 | 270 | 1440 | 1624.5 | -12.8125 | 95.5556 | 947.25 | 98.7332 | Total hardness | mg/L as CaCO3 | 12 | 320 | 746.0359 | 95.5556 | 533.018 | 97.7487 | Total hardness | mg/L as CaCO3 | 14 | 248 | 1460 | 1574 | -7.8082 | 94.3548 | 911 | 98.4632 | Total hardness | mg/L as CaCO3 | 10 | 275 | 700.7667 | 95.9677 | 487.8833 | 97.9503 | Total hardness | mg/L as CaCO3 | 13 | 240 | 1400 | 1431.75 | -2.2679 | 94.5833 | 835.875 | 98.4447 | Total hardness | mg/L as CaCO3 | 10 | 260 | 653.3333 | 95.8333 | 456.6667 | 97.8102 | Total hardness | mg/L as CaCO3 | 12 | 252 | 1520 | 1512 | 0.52632 | 95.2381 | 882 | 98.6395 | Total hardness | mg/L as CaCO3 | 10 | 250 | 612.293 | 96.0317 | 431.1465 | 97.6806 | Total hardness | mg/L as CaCO3 | 16 | 260 | 1160 | 1451.2941 | -25.1116 | 93.8462 | 855.6471 | 98.1301 | Total hardness | mg/L as CaCO3 | 14 | 250 | 518.7778 | 94.6154 | 384.3889 | 96.3579 | Total hardness | mg/L as CaCO3 | 16 | 248 | 1380 | 1380.7059 | -0.051151 | 93.5484 | 814.3529 | 98.0352 | Total hardness | mg/L as CaCO3 | 14 | 256 | 531.6111 | 94.3548 | 393.8056 | 96.4449 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | Feed flow rate to system, QF-sys (gpm) | 43.75 | Turbidity (ntu) | 0.95 |  |  |  | 1998-03-28 | 8:55 | 19635 | 25 | 153 | 114 | 18.9 | 0 | 34.4 | 6.1 |  | 40.5 | 40.5 | 0.84938 | 0 | 13.8756 | 13.8756 | 13.789 | 100.811 | 0.13764 | 6.75 | 6.1 | 38 | 390 | 399 | 1794 | 2434.8033 | -35.7192 | 90.4762 | 1416.9016 | 97.3181 | 153 | 130 | 18 | 25.8 | 14.6 | 40.4 | 40.4 | 0.46417 | 0.63861 | 15.6101 | 15.6101 | 6.9315 | 116.5685 | 0.13391 | 6.07 |  | 30 | 398 | 885 | 1048.3014 | -18.4521 | 92.4812 | 723.1507 | 95.8515 | 130 | 114 | 20 | 8.8 | 6.1 | 14.9 | 14.9 | 0.35446 | 0.5906 | 10.6487 | 10.6487 | 14.1148 | 87.8852 | 0.12117 |  | 6.82 | 65 | 885 | 1794 | 2067.9508 | -15.2704 | 83.7093 | 1476.4754 | 95.5976 | Calcium hardness | mg/L as CaCO3 | 10 | 230 | 1400 | 1385 | 1.0714 | 95.6522 | 807.5 | 98.7616 | Calcium hardness | mg/L as CaCO3 | 10 | 270 | 629.6407 | 95.6522 | 449.8204 | 97.7769 | Calcium hardness | mg/L as CaCO3 | 12 | 234 | 1400 | 1492 | -6.5714 | 94.8718 | 863 | 98.6095 | Calcium hardness | mg/L as CaCO3 | 8 | 260 | 664.88 | 96.5812 | 462.44 | 98.27 | Calcium hardness | mg/L as CaCO3 | 12 | 230 | 1330 | 1374.5 | -3.3459 | 94.7826 | 802.25 | 98.5042 | Calcium hardness | mg/L as CaCO3 | 8 | 240 | 605.0133 | 96.5217 | 422.5067 | 98.1065 | Calcium hardness | mg/L as CaCO3 | 8 | 220 | 1240 | 1333 | -7.5 | 96.3636 | 776.5 | 98.9697 | Calcium hardness | mg/L as CaCO3 | 6 | 224 | 553.0828 | 97.2727 | 388.5414 | 98.4558 | Calcium hardness | mg/L as CaCO3 | 10 | 234 | 1140 | 1327.6471 | -16.4603 | 95.7265 | 780.8235 | 98.7193 | Calcium hardness | mg/L as CaCO3 | 4 | 220 | 466 | 98.2906 | 343 | 98.8338 | Calcium hardness | mg/L as CaCO3 | 10 | 240 | 1260 | 1362.9412 | -8.1699 | 95.8333 | 801.4706 | 98.7523 | Calcium hardness | mg/L as CaCO3 | 8 | 212 | 444.3333 | 96.6667 | 328.1667 | 97.5622 | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 6.5625 | SDI | 4 |  |  |  | 1998-03-29 | 8:25 | 19658 | 25 | 154 | 114 | 19 | 0 | 33 | 6.1 |  | 39.1 | 39.1 | 0.84399 | 0 | 13.3109 | 13.3109 | 13.56 | 101.44 | 0.13122 | 6.76 | 6.08 | 38 | 393 | 404 | 1776 | 2384 | -34.2342 | 90.5941 | 1394 | 97.274 | 154 | 131 | 18 | 24.1 | 16.2 | 40.3 | 40.3 | 0.47683 | 0.59801 | 14.5815 | 14.5815 | 6.4173 | 118.0827 | 0.12349 | 6 |  | 30 | 398 | 882 | 945.4568 | -7.1946 | 92.5743 | 671.7284 | 95.5339 | 131 | 115 | 20 | 8.6 | 6.1 | 14.7 | 14.7 | 0.35108 | 0.58503 | 10.4067 | 10.4067 | 13.9292 | 89.0708 | 0.11684 |  | 6.8 | 65 | 882 | 1776 | 2033.8361 | -14.5178 | 83.9109 | 1457.918 | 95.5416 | Turbidity | ntu | 0.06 | 0.5 | 1 | 2.81 | -181 | 88 | 1.655 | 96.3746 | Turbidity | ntu | 0.2 | 0.6 | 1.1533 | 60 | 0.87665 | 77.1858 | Turbidity | ntu | 0.048 | 0.5 | 1.1 | 3.0613 | -178.303 | 90.4 | 1.7807 | 97.3044 | Turbidity | ntu | 0.045 | 0.28 | 0.65757 | 91 | 0.46878 | 90.4007 | Turbidity | ntu | 0.043 | 0.6 | 1 | 3.5242 | -252.425 | 92.8333 | 2.0621 | 97.9148 | Turbidity | ntu | 0.05 | 0.4 | 0.95067 | 91.6667 | 0.67533 | 92.5962 | Turbidity | ntu | 0.043 | 0.209 | 1.78 | 1.0805 | 39.2978 | 79.4258 | 0.64475 | 93.3307 | Turbidity | ntu | 0.053 | 0.221 | 0.47461 | 74.6411 | 0.3478 | 84.7615 | Turbidity | ntu | 0.04 | 0.973 | 1.03 | 5.5282 | -436.7219 | 95.889 | 3.2506 | 98.7695 | Turbidity | ntu | 0.046 | 0.262 | 0.508 | 95.2724 | 0.385 | 88.0519 | Turbidity | ntu | 0.037 | 0.209 | 0.955 | 1.0488 | -9.8183 | 82.2967 | 0.62888 | 94.1165 | Turbidity | ntu | 0.049 | 0.267 | 0.51528 | 76.555 | 0.39114 | 87.4725 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI |  |  |  |  | 1998-03-30 | 9:45 | 19684 | 26 | 154 | 115 | 18.8 | 0 | 34.5 | 6 |  | 40.5 | 40.5 | 0.85185 | 0 | 13.916 | 13.5106 | 14.1825 | 101.5175 | 0.13309 | 6.75 | 6.05 | 38 | 385 | 404 | 1802 | 2508.5 | -39.2064 | 90.5941 | 1456.25 | 97.3906 | 154 | 131 | 18 | 25.7 | 14.3 | 40 | 40 | 0.45826 | 0.6425 | 15.5496 | 15.0967 | 7.0058 | 117.4942 | 0.12849 | 6.1 |  | 31 | 400 | 889 | 1063.1678 | -19.5914 | 92.3267 | 731.5839 | 95.7626 | 131 | 115 | 20 | 9.2 | 6 | 15.2 | 15.2 | 0.35783 | 0.60526 | 11.1328 | 10.8085 | 14.5573 | 88.4427 | 0.12221 |  | 6.74 | 65 | 889 | 1802 | 2152.4667 | -19.4488 | 83.9109 | 1520.7333 | 95.7257 | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.21 | 0.77 | 3.9 | 3.9433 | -1.1111 | 72.7273 | 2.3567 | 91.0891 | Total organic carbon | mg/L | BMRL | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.21 | 0.61 | 2.24 | 2.71 | -20.9821 | 65.5738 | 1.66 | 87.3494 | Total organic carbon | mg/L | BMRL | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.17 | 0.52 | 2.23 | 2.3575 | -5.7175 | 67.3077 | 1.4387 | 88.1842 | Total organic carbon | mg/L | BMRL | 12.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.15 | 0.49 | 2.01 | 2.15 | -6.9652 | 69.3878 | 1.32 | 88.6364 | Total organic carbon | mg/L | BMRL | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.15 | 0.48 | 1.96 | 2.0912 | -6.6927 | 68.75 | 1.2856 | 88.3322 | Total organic carbon | mg/L | BMRL | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-03-31 | 8:22 | 19706 | 26 | 153 | 115 | 18.7 | 0 | 34.7 | 6 |  | 40.7 | 40.7 | 0.85258 | 0 | 13.9966 | 13.589 | 14.1267 | 101.1732 | 0.13431 | 6.78 | 6.03 | 38 | 370 | 401 | 1819 | 2500.35 | -37.4574 | 90.5237 | 1450.675 | 97.3805 | 153 | 131 | 17 | 26 | 13.8 | 39.8 | 39.8 | 0.45235 | 0.65327 | 15.7311 | 15.2729 | 7.1855 | 117.8145 | 0.12964 | 6.06 |  | 31 | 401 | 892 | 1098.1014 | -23.1055 | 92.2693 | 749.5507 | 95.8642 | 131 | 115 | 20 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 10.2211 | 14.2658 | 88.7343 | 0.11519 |  | 6.71 | 65 | 892 | 1819 | 2091.15 | -14.9615 | 83.7905 | 1491.575 | 95.6422 | Total organic carbon | mg/L | BMRL | 12.9 | 75.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.503 | 1.1794 | 96.8254 | 0.8412 | 98.3357 | Total organic carbon | mg/L | BMRL | 12.7 | 74.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.435 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.6 | 73.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.41 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 11.7 | 74.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.443 | 1.0966 | 97.8723 | 0.76982 | 98.701 | Total organic carbon | mg/L | BMRL | 12 | 79.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.462 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.3 | 80.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.458 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Glades Road Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 15 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 22.5 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-04-01 | 8:10 | 19730 | 25.2 | 154 | 114 | 18.7 | 0 | 31.8 | 6 |  | 37.8 | 37.8 | 0.84127 | 0 | 12.8269 | 12.7513 | 12.994 | 102.306 | 0.12464 | 6.77 | 6.01 | 38 | 378 | 394 | 1802 | 2280.8 | -26.5705 | 90.3553 | 1337.4 | 97.1587 | 154 | 131 | 18 | 23.1 | 16.7 | 39.8 | 39.8 | 0.47683 | 0.5804 | 13.9765 | 13.8941 | 6.259 | 118.241 | 0.11751 |  |  | 31 | 401 | 889 | 912.7964 | -2.6768 | 92.132 | 656.8982 | 95.2809 | 131 | 114 | 20 | 8.6 | 6 | 14.6 | 14.6 | 0.3477 | 0.58904 | 10.4067 | 10.3454 | 14.1282 | 88.3718 | 0.11707 |  | 6.69 | 66 | 889 | 1802 | 2068.6333 | -14.7965 | 83.2487 | 1478.8167 | 95.537 | UV254 | cm-1 | BMRL | 0.441 | 2.665 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8992 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.464 | 2.561 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3462 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.418 | 2.61 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.1538 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.47 | 2.65 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4341 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.428 | 2.644 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5538 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.433 | 2.584 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8167 | --- | --- | --- | ---
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0022 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 8.3333 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-04-02 | 9:30 | 19755 | 25.3 | 154 | 116 | 18.7 | 0 | 33.1 | 6 |  | 39.1 | 39.1 | 0.84655 | 0 | 13.3513 | 13.2334 | 13.2669 | 103.0331 | 0.12844 | 6.8 | 6.3 | 35 | 384 | 388 | 1805 | 2335.3833 | -29.3841 | 90.9794 | 1361.6917 | 97.4297 | 154 | 132 | 18 | 25 | 14.6 | 39.6 | 39.6 | 0.45742 | 0.63131 | 15.1261 | 14.9925 | 6.8307 | 118.1693 | 0.12687 |  |  | 28 | 396 | 885 | 1026.137 | -15.9477 | 92.7835 | 711.0685 | 96.0623 | 132 | 116 | 20 | 8.8 | 6 | 14.8 | 14.8 | 0.35108 | 0.59459 | 10.6487 | 10.5547 | 14.2307 | 89.7693 | 0.11758 |  | 6.98 | 64 | 885 | 1805 | 2089.1333 | -15.7415 | 83.5052 | 1487.0667 | 95.6962 | SUVA | L/(mg*m) | NR | 3.4186 | 3.5205 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.6535 | 3.4284 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.3175 | 3.5414 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.0171 | 3.5762 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5667 | 3.33 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5203 | 3.226 | --- | --- | --- | --- | ---
Process Train Name | SOFT | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1998-04-03 | 8:29 | 19778 | 25.3 | 154 | 115 | 18.6 | 0 | 33.2 | 6 |  | 39.2 | 39.2 | 0.84694 | 0 | 13.3916 | 13.2734 | 13.673 | 102.227 | 0.12984 | 6.77 | 6.24 | 36 | 389 | 399 | 1784 | 2407.6 | -34.9552 | 90.9774 | 1403.3 | 97.4346 | 154 | 132 | 18 | 24.5 | 15.3 | 39.8 | 39.8 | 0.46501 | 0.61558 | 14.8235 | 14.6927 | 6.6264 | 118.3736 | 0.12412 |  |  | 28 | 396 | 886 | 985.281 | -11.2055 | 92.9825 | 690.6405 | 95.9458 | 132 | 115 | 20 | 8.6 | 6.1 | 14.7 | 14.7 | 0.35108 | 0.58503 | 10.4067 | 10.3148 | 13.9974 | 89.5026 | 0.11525 |  | 6.9 | 65 | 886 | 1784 | 2043.4754 | -14.5446 | 83.7093 | 1464.7377 | 95.5623 | Bromide | mg/L | 27 | 185 | --- | 1014.5 | --- | 85.4054 | 599.75 | 95.4981 | [8 empty] | Bromide | mg/L | 47 | 190 | --- | 1000.3333 | --- | 75.2632 | 595.1667 | 92.1031 | [8 empty] | Bromide | mg/L | 27.8 | 177 | --- | 960.3 | --- | 84.2938 | 568.65 | 95.1112 | [8 empty] | Bromide | mg/L | 27.7 | 182 | --- | 992.075 | --- | 84.7802 | 587.0375 | 95.2814 | [8 empty] | Bromide | mg/L | 25.7 | 178 | --- | 921.5824 | --- | 85.5618 | 549.7912 | 95.3255 | [8 empty] | Bromide | mg/L | 28 | 183 | --- | 939.7647 | --- | 84.6995 | 561.3824 | 95.0123
ICR Treatment Plant Identification Number | 306 | Purchase price for an equivalent 8" x 40 " element ($) | $895 / quantity discount | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-04-04 | 9:10 | 19803 | 25.3 | 155 | 116 | 18.3 | 0 | 31.2 | 6 |  | 37.2 | 37.2 | 0.83871 | 0 | 12.5849 | 12.4738 | 13.032 | 104.168 | 0.11975 | 6.81 | 6.27 | 33 | 393 | 395 | 1819 | 2277.4 | -25.2007 | 91.6456 | 1336.2 | 97.5303 | 155 | 132 | 17 | 22.5 | 17.2 | 39.7 | 39.7 | 0.4802 | 0.56675 | 13.6134 | 13.4933 | 5.9547 | 120.5453 | 0.11194 |  |  | 33 | 393 | 892 | 863.9302 | 3.1468 | 91.6456 | 628.4651 | 94.7491 | 132 | 116 | 19 | 8.6 | 6 | 14.6 | 14.6 | 0.3477 | 0.58904 | 10.4067 | 10.3148 | 14.1968 | 90.8032 | 0.1136 |  | 6.91 | 65 | 892 | 1819 | 2077.3667 | -14.2038 | 83.5443 | 1484.6833 | 95.622 | SDS-Cl2 dose | mg/L | 5 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 23 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4500130 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -10.5 | [5 empty] | 1998-04-05 | 10:15 | 19820 | 25.3 | 154 | 115 | 18.7 | 0 | 32.6 | 6 |  | 38.6 | 38.6 | 0.84456 | 0 | 13.1496 | 13.0335 | 13.7145 | 102.0855 | 0.12767 | 6.79 | 6.23 | 39 | 403 | 408 | 1816 | 2412.9 | -32.8689 | 90.4412 | 1410.45 | 97.2349 | 154 | 131 | 18 | 24.1 | 16.1 | 40.2 | 40.2 | 0.47514 | 0.5995 | 14.5815 | 14.4528 | 6.4168 | 118.0832 | 0.12239 |  |  | 30 | 397 | 893 | 946.3602 | -5.9754 | 92.6471 | 671.6801 | 95.5336 | 131 | 115 | 20 | 8.4 | 6 | 14.4 | 14.4 | 0.34433 | 0.58333 | 10.1647 | 10.075 | 14.025 | 88.975 | 0.11323 |  | 6.86 | 68 | 893 | 1816 | 2048 | -12.7753 | 83.3333 | 1470.5 | 95.3757 | SDS-Free Cl2 residual | mg/L | BMRL | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.2 | 0.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.4 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.3 | 0.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.5 | 1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.5 | 0.95 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -2.3333 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-04-06 | 10:04 | 19844 | 25.3 | 156 | 117 | 18.9 | 0 | 33.7 | 6 |  | 39.7 | 39.7 | 0.84887 | 0 | 13.5933 | 13.4733 | 14.1289 | 103.4711 | 0.13021 | 6.8 | 6.25 | 37 | 398 | 408 | 1816 | 2491.7833 | -37.2127 | 90.9314 | 1449.8917 | 97.4481 | 156 | 133 | 18 | 24.7 | 15.6 | 40.3 | 40.3 | 0.47176 | 0.6129 | 14.9445 | 14.8126 | 6.45 | 120.05 | 0.12339 | 6.23 |  | 37 | 397 | 896 | 967 | -7.9241 | 90.9314 | 682 | 94.5748 | 133 | 117 | 20 | 8.9 | 5.9 | 14.8 | 14.8 | 0.34939 | 0.60135 | 10.7697 | 10.6747 | 14.5602 | 90.4398 | 0.11803 |  | 6.87 | 66 | 896 | 1816 | 2148.0339 | -18.2838 | 83.8235 | 1522.0169 | 95.6636 | SDS-Cl2 demand | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.8 | 20.5 | --- | 120.8 | --- | 86.3415 | 70.65 | 96.0368 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.33 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.6 | 20.2 | --- | 112.6 | --- | 87.1287 | 66.4 | 96.0843 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.52 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.7 | 22.4 | --- | 125.825 | --- | 87.9464 | 74.1125 | 96.3569 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.9 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.5 | 20 | --- | 105.4412 | --- | 87.5 | 62.7206 | 96.0141 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.5 | 20.05 | --- | 105.7353 | --- | 87.5312 | 62.8926 | 96.025 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.6
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | not specified | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-04-07 | 8:15 | 19866 | 25.2 | 157 | 117 | 18.7 | 0 | 34.3 | 6 |  | 40.3 | 40.3 | 0.85112 | 0 | 13.8353 | 13.7537 | 14.4688 | 103.8312 | 0.13246 | 6.71 | 6.08 | 36 | 395 | 411 | 1812 | 2554.75 | -40.9906 | 91.2409 | 1482.875 | 97.5723 | 157 | 134 | 18 | 25.4 | 14.4 | 39.8 | 39.8 | 0.45742 | 0.63819 | 15.3681 | 15.2775 | 7.0008 | 120.4992 | 0.12678 | 5.97 |  | 29 | 401 | 896 | 1057.1667 | -17.9874 | 92.944 | 729.0833 | 96.0224 | 134 | 117 | 20 | 8.8 | 6 | 14.8 | 14.8 | 0.35108 | 0.59459 | 10.6487 | 10.586 | 14.3867 | 91.1133 | 0.11618 |  | 6.71 | 66 | 896 | 1812 | 2113.3333 | -16.6299 | 83.9416 | 1504.6667 | 95.6136 | SDS-Chlorination temp. | oC | 23 | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 16.7 |  |  |  |  | SDS-Chlorination temp. | oC | 22.5 | 22.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15 |  |  |  |  | SDS-Chlorination temp. | oC | 23 | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15 |  |  |  |  | SDS-Chlorination temp. | oC | 23 | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.7 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 18 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 18
State Approved Plant Capacity (MGD) | 70 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-04-08 | 7:50 | 19889 | 25.2 | 157 | 117 | 19.5 | 0 | 30.9 | 6 |  | 36.9 | 36.9 | 0.8374 | 0 | 12.4639 | 12.3904 | 13.4062 | 104.0938 | 0.11903 | 6.77 | 6.2 | 37 | 399 | 412 | 1819 | 2343.25 | -28.8208 | 91.0194 | 1377.625 | 97.3142 | 157 | 134 | 18 | 22.1 | 17.6 | 39.7 | 39.7 | 0.48358 | 0.55668 | 13.3714 | 13.2926 | 6.0556 | 121.4444 | 0.10945 | 6.19 |  | 30 | 402 | 900 | 869.1136 | 3.4318 | 92.7184 | 635.5568 | 95.2797 | 134 | 117 | 20 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 10.4657 | 14.3865 | 91.1135 | 0.11486 |  | 6.81 | 66 | 900 | 1819 | 2109.3 | -15.9593 | 83.9806 | 1504.65 | 95.6136 | SDS-Chlorination pH | --- | 8.4 | 8.4 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.4 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.4 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.37 | 8.36 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.37 | 8.31 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 21 | [7 empty] | 1998-04-09 | 10:30 | 19916 | 25.2 | 157 | 117 | 19.5 | 0 | 34 | 6 |  | 40 | 40 | 0.85 | 0 | 13.7143 | 13.6334 | 14.3367 | 103.1633 | 0.13215 | 6.75 | 6.18 | 37 | 397 | 411 | 1816 | 2530.3333 | -39.3355 | 90.9976 | 1470.6667 | 97.4841 | 157 | 134 | 18 | 25.5 | 14.2 | 39.7 | 39.7 | 0.45489 | 0.64232 | 15.4286 | 15.3376 | 7.0791 | 120.4209 | 0.12737 | 6.12 |  | 30 | 403 | 903 | 1072.8239 | -18.8066 | 92.7007 | 737.912 | 95.9345 | 134 | 117 | 21 | 8.4 | 6 | 14.4 | 14.4 | 0.34433 | 0.58333 | 10.1647 | 10.1048 | 14.229 | 90.271 | 0.11194 |  | 6.81 | 66 | 903 | 1816 | 2074.8 | -14.2511 | 83.9416 | 1488.9 | 95.5672 | SDS-Incubation time | hours | 42 | 42 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41.5 | 41.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 40 | 40 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 29 | 29.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 29 | 29.5 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | not specified | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-04-10 | 9:45 | 19939 | 25.2 | 156 | 117 | 18.7 | 0 | 30.9 | 6 |  | 36.9 | 36.9 | 0.8374 | 0 | 12.4639 | 12.3904 | 13.5135 | 104.2865 | 0.11881 | 6.79 | 6.22 | 38 | 390 | 416 | 1858 | 2362.7 | -27.1636 | 90.8654 | 1389.35 | 97.2649 | 156 | 134 | 17 | 22.2 | 18.4 | 40.6 | 40.6 | 0.49793 | 0.5468 | 13.4319 | 13.3528 | 6.0924 | 121.9076 | 0.10953 | 6.09 |  | 31 | 411 | 917 | 869.4783 | 5.1823 | 92.5481 | 640.2391 | 95.1581 | 134 | 119 | 20 | 8.6 | 5.8 | 14.4 | 14.4 | 0.34095 | 0.59722 | 10.4067 | 10.3454 | 14.9236 | 91.5764 | 0.11297 |  | 6.79 | 60 | 917 | 1858 | 2187.7241 | -17.7462 | 85.5769 | 1552.3621 | 96.1349 | SDS-TOX | mg Cl- /L | BMRL | 118 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1525 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1445 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1692 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1655 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1550 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 percent | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 20.25 | [5 empty] | 1998-04-11 | 9:20 | 19963 | 25.2 | 157 | 119 | 18.8 | 0 | 31.1 | 6 |  | 37.1 | 37.1 | 0.83827 | 0 | 12.5445 | 12.4706 | 13.2173 | 105.9827 | 0.11767 | 6.85 | 6.21 | 38 | 394 | 406 | 1855 | 2313.4667 | -24.7152 | 90.6404 | 1359.7333 | 97.2053 | 157 | 135 | 18 | 22.8 | 16.5 | 39.3 | 39.3 | 0.47092 | 0.58015 | 13.795 | 13.7136 | 6.2733 | 121.7267 | 0.11266 | 6.06 |  | 30 | 401 | 906 | 913.6545 | -0.84487 | 92.6108 | 657.3273 | 95.4361 | 135 | 118 | 20 | 8.3 | 5.9 | 14.2 | 14.2 | 0.33927 | 0.58451 | 10.0437 | 9.9845 | 14.2914 | 92.2086 | 0.10828 |  | 6.77 | 67 | 906 | 1855 | 2086.2881 | -12.4684 | 83.4975 | 1496.1441 | 95.5218 | SDS-CHCl3 | mg/L | BMRL | 3.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-01 | 1998-04-01 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 432 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-15 | 1998-04-15 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 462 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-29 | 1998-04-29 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1 | 465 | --- | 2901 | --- | 99.7849 | 1683 | 99.9406 | Sampling date | MM/DD/YY | 1998-05-13 | 1998-05-13 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 382 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 409 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | 500 mg/l NaCl | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 13.0417 | [5 empty] | 1998-04-12 | 10:30 | 19988 | 25.2 | 156 | 118 | 18.5 | 0 | 32.5 | 6 |  | 38.5 | 38.5 | 0.84416 | 0 | 13.1092 | 13.032 | 14.3142 | 104.1858 | 0.12508 | 6.77 | 6.11 | 38 | 421 | 424 | 1841 | 2514.8333 | -36.6015 | 91.0377 | 1469.4167 | 97.4139 | 156 | 134 | 18 | 23.7 | 15.4 | 39.1 | 39.1 | 0.45995 | 0.60614 | 14.3395 | 14.255 | 6.6356 | 120.3644 | 0.11843 | 6.06 |  | 30 | 405 | 910 | 982.1104 | -7.9242 | 92.9245 | 693.5552 | 95.6745 | 134 | 118 | 20 | 8.7 | 5.9 | 14.6 | 14.6 | 0.34602 | 0.59589 | 10.5277 | 10.4657 | 14.6453 | 91.3547 | 0.11456 |  | 6.82 | 67 | 910 | 1841 | 2153.0678 | -16.951 | 84.1981 | 1531.5339 | 95.6253 | SDS-BDCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:45 | 8:45 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.8 | 60.8 | --- | 395.1333 | --- | 97.0395 | 227.9667 | 99.2104 | Sampling time | hh:mm | 8:25 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.3 | 83 | --- | 511.925 | --- | 98.4337 | 297.4625 | 99.563 | Sampling time | hh:mm | 9:15 | 8:50 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.4 | 69.9 | --- | 429.525 | --- | 97.9971 | 249.7125 | 99.4394 | Sampling time | hh:mm | 7:50 | 7:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 54.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:10 | 10:20 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 59.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:10 | 10:20 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | not specified | [7 empty] | 1998-04-13 | 9:15 | 20011 | 25.3 | 157 | 118 | 18.7 | 0 | 34.4 | 6 |  | 40.4 | 40.4 | 0.85149 | 0 | 13.8756 | 13.7531 | 14.3067 | 104.4933 | 0.13162 | 6.77 | 6.07 | 37 | 396 | 407 | 1822 | 2528.3333 | -38.7669 | 90.9091 | 1467.6667 | 97.479 | 157 | 135 | 18 | 25.5 | 13.8 | 39.3 | 39.3 | 0.44813 | 0.64885 | 15.4286 | 15.2924 | 7.1377 | 120.8623 | 0.12653 | 6.03 |  | 30 | 401 | 900 | 1086.5435 | -20.7271 | 92.629 | 743.7717 | 95.9665 | 135 | 118 | 20 | 8.8 | 5.9 | 14.7 | 14.7 | 0.3477 | 0.59864 | 10.6487 | 10.5547 | 14.5597 | 91.9403 | 0.1148 |  | 6.76 | 66 | 900 | 1822 | 2143.9322 | -17.6692 | 83.7838 | 1521.9661 | 95.6635 | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 19890 | 19890 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.8 | 8.3 | --- | 45.1333 | --- | 78.3133 | 26.7167 | 93.2626 | Operation time | hh.hh | 20058 | 20058 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.6 | 9.7 | --- | 52.225 | --- | 83.5052 | 30.9625 | 94.8325 | Operation time | hh.hh | 20394 | 20394 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.6 | 13.6 | --- | 76.6 | --- | 88.2353 | 45.1 | 96.4523 | Operation time | hh.hh | 20729 | 20729 | --- | --- | --- | --- | SDS-DBCM | mg/L | 0.6 | 7.3 | --- | 40.0118 | --- | 91.7808 | 23.6559 | 97.4636 | Operation time | hh.hh | 21091 | 21091 | --- | --- | --- | --- | SDS-DBCM | mg/L | 0.5 | 7.6 | --- | 42.2647 | --- | 93.4211 | 24.9324 | 97.9946 | Operation time | hh.hh | 21091 | 21091 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-04-14 | 8:30 | 20034 | 25.3 | 157 | 118 | 18.6 | 0 | 31.4 | 6 |  | 37.4 | 37.4 | 0.83957 | 0 | 12.6655 | 12.5537 | 13.2732 | 105.6268 | 0.11885 | 6.76 | 6.06 | 38 | 395 | 405 | 1822 | 2325.6333 | -27.6418 | 90.6173 | 1365.3167 | 97.2168 | 157 | 134 | 18 | 22.9 | 16.3 | 39.2 | 39.2 | 0.46839 | 0.58418 | 13.8555 | 13.7331 | 6.214 | 121.286 | 0.11323 | 6.03 |  | 30 | 395 | 903 | 907.7914 | -0.53061 | 92.5926 | 651.3957 | 95.3945 | 134 | 118 | 20 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.1949 | 14.3992 | 91.6008 | 0.1113 |  | 6.75 | 66 | 903 | 1822 | 2108.8475 | -15.7435 | 83.7037 | 1505.9237 | 95.6173 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.92 | 7.24 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.5 | 1.4 | --- | 0.83333 | --- | -7.1429 | 1.1167 | -34.3284 | pH | --- | 5.81 | 7.22 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.8 | 1.3 | --- | -1.325 | --- | -38.4615 | -0.0125 | 14500 | pH | --- | 5.88 | 6.72 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.1 | 7.05 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.8 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.79 | 6.79 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.7 | 0.5 | --- | -0.47647 | --- | -40 | 0.011765 | -5850 | pH | --- | 5.84 | 6.87 | --- | --- | --- | ---
|  | Standard testing pH | 6.5-7.0 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-04-15 | 8:45 | 20058 | 25.2 | 156 | 117 | 18.4 | 0 | 32.5 | 6 |  | 38.5 | 38.5 | 0.84416 | 0 | 13.1092 | 13.032 | 13.8321 | 104.2679 | 0.12499 | 6.72 | 6.11 | 37 | 398 | 410 | 1794 | 2430.4167 | -35.4747 | 90.9756 | 1420.2083 | 97.3947 | 156 | 134 | 17 | 24.1 | 15 | 39.1 | 39.1 | 0.45657 | 0.61637 | 14.5815 | 14.4956 | 6.6723 | 121.3277 | 0.11947 | 6.11 |  | 31 | 401 | 896 | 995.4667 | -11.1012 | 92.439 | 698.2333 | 95.5602 | 134 | 117 | 20 | 8.3 | 5.9 | 14.2 | 14.2 | 0.33927 | 0.58451 | 10.0437 | 9.9845 | 14.1552 | 91.3448 | 0.10931 |  | 6.73 | 65 | 896 | 1794 | 2065.0339 | -15.1078 | 84.1463 | 1480.5169 | 95.6096 | SDS-THM4 | mg/L | 0 | 3.6 | --- | 22.5 | --- | 100 | 13.05 | 100 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.1 | 502.5 | --- | 3321.1 | --- | 98.9851 | 1911.8 | 99.7332 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.7 | 556 | --- | 3450.325 | --- | 99.1547 | 2003.1625 | 99.7654 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 6 | 548.5 | --- | 3396.625 | --- | 98.9061 | 1972.5625 | 99.6958 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.4 | 444.1 | --- | 2605.5176 | --- | 99.6848 | 1524.8088 | 99.9082 | Temperature | oC | 26 | 26.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.2 | 476.5 | --- | 2797.0824 | --- | 99.7482 | 1636.7912 | 99.9267 | Temperature | oC | 26 | 26.2 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 13.0417 | [5 empty] | 1998-04-16 | 10:30 | 20084 | 25.2 | 157 | 118 | 18.5 | 0 | 32.5 | 6 |  | 38.5 | 38.5 | 0.84416 | 0 | 13.1092 | 13.032 | 13.9804 | 105.0196 | 0.12409 | 6.82 | 6.12 | 38 | 404 | 415 | 1856 | 2457.0833 | -32.386 | 90.8434 | 1436.0417 | 97.3538 | 157 | 135 | 17 | 24.4 | 14.5 | 38.9 | 38.9 | 0.45067 | 0.62725 | 14.763 | 14.676 | 6.9604 | 122.0396 | 0.12026 | 6.13 |  | 31 | 409 | 917 | 1045.0828 | -13.9676 | 92.5301 | 727.0414 | 95.7361 | 135 | 118 | 20 | 8 | 5.8 | 13.8 | 13.8 | 0.33083 | 0.57971 | 9.6807 | 9.6236 | 14.3621 | 92.1379 | 0.10445 |  | 6.76 | 67 | 917 | 1848 | 2089.4138 | -13.0635 | 83.8554 | 1503.2069 | 95.5429 | SDS-MCAA* | mg/L | 1.8 | 19.6 | --- | 113.05 | --- | 90.8163 | 66.325 | 97.2861 | Alkalinity | mg/L as CaCO3 | 21 | 294 | 583.8519 | 82.7869 | 438.9259 | 95.2156 | SDS-MCAA* | mg/L | 12.3 | 14.2 | --- | 24.9667 | --- | 13.3803 | 19.5833 | 37.1915 | Alkalinity | mg/L as CaCO3 | 24 | 286 | 613.2054 | 80.9524 | 449.6027 | 94.662 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 470 | 1056.4074 | 83.4483 | 763.2037 | 96.8554 | SDS-MCAA* | mg/L | 0.8 | 12.8 | --- | 75.8 | --- | 93.75 | 44.3 | 98.1941 | Alkalinity | mg/L as CaCO3 | 20 | 244 | 537.1765 | 81.1321 | 390.5882 | 94.8795 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 276 | 513.8723 | 86.8852 | 394.9362 | 95.9487 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 264 | 485.4043 | 80.3571 | 374.7021 | 94.1287
|  | Acceptable range of operating pH values | 3 to 10 | Design system recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-04-17 | 10:00 | 20108 | 25.2 | 159 | 120 | 18.5 | 0 | 32.6 | 6 |  | 38.6 | 38.6 | 0.84456 | 0 | 13.1496 | 13.0721 | 13.7145 | 107.2855 | 0.12184 | 6.78 | 6.03 | 39 | 391 | 408 | 1862 | 2412.9 | -29.5865 | 90.4412 | 1410.45 | 97.2349 | 159 | 136 | 17 | 24 | 15.3 | 39.3 | 39.3 | 0.46079 | 0.61069 | 14.521 | 14.4354 | 6.7982 | 123.7018 | 0.1167 | 6.09 |  | 31 | 412 | 923 | 1009.6471 | -9.3875 | 92.402 | 710.8235 | 95.6389 | 136 | 120 | 20 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.2251 | 14.4164 | 93.5836 | 0.10926 |  | 6.78 | 68 | 906 | 1830 | 2113.2881 | -15.4802 | 83.3333 | 1509.6441 | 95.4956 | SDS-DCAA* | mg/L | BMRL | 2.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 50 | 897 | 1796.284 | 87.2774 | 1346.642 | 96.2871 | SDS-DCAA* | mg/L | BMRL | 84.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 69.1 | 920 | 1982.6682 | 83.3092 | 1451.3341 | 95.2389 | SDS-DCAA* | mg/L | BMRL | 142 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 64.2 | 900 | 1998.9222 | 84.3032 | 1449.4611 | 95.5708 | SDS-DCAA* | mg/L | BMRL | 135 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 63 | 897 | 1988.5588 | 84.7087 | 1442.7794 | 95.6334 | SDS-DCAA* | mg/L | BMRL | 122 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 62.5 | 947 | 1756.2234 | 85.363 | 1351.6117 | 95.3759 | SDS-DCAA* | mg/L | BMRL | 134 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 62.6 | 952 | 1765.7064 | 85.3738 | 1358.8532 | 95.3932
|  | Typical pressure drop across a single element (psi) | 4 | System influent flow rate, QI-sys (gpm) | 43.76 | [5 empty] | 1998-04-18 | 10:25 | 20132 | 25.2 | 158 | 119 | 18.7 | 0 | 30.9 | 6 |  | 36.9 | 36.9 | 0.8374 | 0 | 12.4639 | 12.3904 | 13.299 | 106.501 | 0.11634 | 6.74 | 6.04 | 37 | 397 | 409 | 1830 | 2324.8 | -27.0383 | 90.9535 | 1366.9 | 97.2931 | 158 | 136 | 18 | 22.3 | 17.1 | 39.4 | 39.4 | 0.47683 | 0.56599 | 13.4924 | 13.4129 | 6.2117 | 122.7883 | 0.10924 | 6.12 |  | 30 | 406 | 906 | 896.3392 | 1.0663 | 92.665 | 651.1696 | 95.3929 | 136 | 119 | 20 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.2251 | 14.7777 | 92.7223 | 0.11028 |  | 6.73 | 64 | 923 | 1862 | 2160.5424 | -16.0334 | 84.3521 | 1541.7712 | 95.8489 | SDS-TCAA* | mg/L | BMRL | 0.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 720 | 1458.963 | 91.1111 | 1089.4815 | 97.7971 | SDS-TCAA* | mg/L | BMRL | 81.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 650 | 1431.7961 | 90.3226 | 1040.8981 | 97.6943 | SDS-TCAA* | mg/L | BMRL | 137 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 680 | 1542.5185 | 90 | 1111.2593 | 97.8403 | SDS-TCAA* | mg/L | BMRL | 115 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 687 | 1554.75 | 90.4762 | 1120.875 | 97.8588 | SDS-TCAA* | mg/L | BMRL | 112 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 22 | 580 | 1090.5106 | 91.5385 | 835.2553 | 97.3661 | SDS-TCAA* | mg/L | BMRL | 146 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 600 | 1126.9787 | 90.3226 | 863.4894 | 97.2206
|  | Maximum permissible SDI | 4 | Recycle ratio, r | 0.00022857 | [5 empty] | 1998-04-19 | 8:45 | 20154 | 25.2 | 158 | 119 | 18.8 | 0 | 30.1 | 6 |  | 36.1 | 36.1 | 0.8338 | 0 | 12.1412 | 12.0696 | 13.3667 | 106.3333 | 0.11351 | 6.74 | 6.08 | 37 | 403 | 418 | 1848 | 2329.35 | -26.0471 | 91.1483 | 1373.675 | 97.3065 | 158 | 136 | 18 | 21.9 | 17.8 | 39.7 | 39.7 | 0.48527 | 0.55164 | 13.2504 | 13.1723 | 6.1215 | 122.8785 | 0.1072 | 6.12 |  | 30 | 409 | 917 | 875.2978 | 4.5477 | 92.823 | 642.1489 | 95.3282 | 136 | 119 | 20 | 8.2 | 5.9 | 14.1 | 14.1 | 0.33758 | 0.58156 | 9.9227 | 9.8642 | 14.4407 | 93.0593 | 0.106 |  | 6.73 | 65 | 917 | 1856 | 2101.1356 | -13.2077 | 84.4498 | 1509.0678 | 95.6927 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 22 | 610 | 1234.2963 | 90.4348 | 922.1481 | 97.6143 | SDS-MBAA* | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 635 | 1403.0585 | 91.453 | 1019.0292 | 98.0373 | SDS-MBAA* | mg/L | BMRL | 44.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 620 | 1408.8889 | 91.3043 | 1014.4444 | 98.0285 | SDS-MBAA* | mg/L | 5.19 | 17.1 | --- | 79.6275 | --- | 69.6491 | 48.3638 | 89.2688 | Calcium hardness | mg/L as CaCO3 | 18 | 344 | 770.6765 | 91.8182 | 557.3382 | 96.7704 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 520 | 977.4468 | 91.453 | 748.7234 | 97.3288 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 420 | 789.617 | 93.3333 | 604.8085 | 97.3545
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-04-20 | 10:00 | 20180 | 25.2 | 159 | 119 | 18.5 | 0 | 31.9 | 6 |  | 37.9 | 37.9 | 0.84169 | 0 | 12.8672 | 12.7914 | 13.7553 | 106.7447 | 0.11983 | 6.69 | 6.05 | 37 | 398 | 413 | 1825 | 2412.0667 | -32.168 | 91.0412 | 1412.5333 | 97.3806 | 159 | 136 | 17 | 23.1 | 16.2 | 39.3 | 39.3 | 0.46839 | 0.58779 | 13.9765 | 13.8941 | 6.4579 | 124.0421 | 0.11201 | 6.11 |  | 30 | 407 | 910 | 944.5741 | -3.7993 | 92.7361 | 675.787 | 95.5607 | 136 | 119 | 20 | 8.8 | 5.9 | 14.7 | 14.7 | 0.3477 | 0.59864 | 10.6487 | 10.586 | 14.7517 | 92.7483 | 0.11414 |  | 6.72 | 65 | 910 | 1825 | 2170.339 | -18.9227 | 84.2615 | 1540.1695 | 95.7797 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.12 | 0.29 | 0.47049 | 76 | 0.38025 | 68.4416 | SDS-DBAA* | mg/L | BMRL | 1.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.069 | 0.3 | 0.58849 | 86.2 | 0.44425 | 84.468 | SDS-DBAA* | mg/L | 0.79 | 1.52 | --- | 5.3525 | --- | 48.0263 | 3.4362 | 77.0098 | Turbidity | ntu | 0.046 | 0.88 | 1.9766 | 92.3333 | 1.4283 | 96.7793 | SDS-DBAA* | mg/L | 0.84 | 3.48 | --- | 17.34 | --- | 75.8621 | 10.41 | 91.9308 | Turbidity | ntu | 0.052 | 0.392 | 0.837 | 75.1196 | 0.6145 | 91.5378 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.047 | 0.753 | 1.3989 | 95.1696 | 1.076 | 95.6318 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.044 | 0.761 | 1.417 | 78.9474 | 1.089 | 95.9596
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | maximum system recycle flow rates. | [6 empty] | 1998-04-21 | 8:45 | 20202 | 25.3 | 158 | 119 | 18.5 | 0 | 31.6 | 6 |  | 37.6 | 37.6 | 0.84043 | 0 | 12.7462 | 12.6337 | 13.952 | 106.048 | 0.11913 | 6.67 | 6.02 | 37 | 412 | 421 | 1845 | 2443.4 | -32.4336 | 91.2114 | 1432.2 | 97.4166 | 158 | 136 | 17 | 22.9 | 16.3 | 39.2 | 39.2 | 0.46839 | 0.58418 | 13.8555 | 13.7331 | 6.4353 | 123.5647 | 0.11114 | 6.11 |  | 30 | 408 | 914 | 939.0552 | -2.7413 | 92.8741 | 673.5276 | 95.5458 | 136 | 119 | 20 | 8.6 | 5.9 | 14.5 | 14.5 | 0.34433 | 0.5931 | 10.4067 | 10.3148 | 14.6776 | 92.8224 | 0.11112 |  | 6.72 | 65 | 914 | 1845 | 2151.5254 | -16.6138 | 84.5606 | 1532.7627 | 95.7593 | SDS-BCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 0.6 | 23.8 | --- | 155.2667 | --- | 97.479 | 89.5333 | 99.3299 | Total organic carbon | mg/L | BMRL | 33.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.52 | 31 | --- | 185.77 | --- | 95.0968 | 108.385 | 98.5976 | Total organic carbon | mg/L | BMRL | 31.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.53 | 26.8 | --- | 159.4675 | --- | 94.291 | 93.1338 | 98.3572 | Total organic carbon | mg/L | BMRL | 31.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 15 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.71 | 32.8 | 62.1589 | 94.0833 | 47.4795 | 98.5046 | SDS-BCAA* | mg/L | BMRL | 15.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 32.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-04-22 | 9:25 | 20227 | 25.2 | 158 | 119 | 18.3 | 0 | 33.9 | 6 |  | 39.9 | 39.9 | 0.84962 | 0 | 13.6739 | 13.5934 | 14.688 | 105.512 | 0.12883 | 6.77 | 6.25 | 36 | 406 | 420 | 1802 | 2589.6 | -43.707 | 91.4286 | 1504.8 | 97.6077 | 158 | 136 | 17 | 25.3 | 13.7 | 39 | 39 | 0.44476 | 0.64872 | 15.3076 | 15.2173 | 7.5011 | 122.4989 | 0.12422 | 6.02 |  | 28 | 418 | 914 | 1138.219 | -24.5316 | 93.3333 | 778.1095 | 96.4015 | 136 | 119 | 19 | 8.5 | 6.1 | 14.6 | 14.6 | 0.34939 | 0.58219 | 10.2857 | 10.2251 | 14.4391 | 94.0609 | 0.10871 |  | 6.9 | 63 | 914 | 1802 | 2099.8197 | -16.5272 | 85 | 1506.9098 | 95.8193 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 1.363 | 2.8006 | 97.9592 | 2.0818 | 99.5677 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.127 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.016 | 0.923 | 2.1155 | 96.1722 | 1.5193 | 98.9469 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.095 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.148 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-04-23 | 8:23 | 20250 | 25.2 | 159 | 120 | 18.6 | 0 | 33.6 | 6 |  | 39.6 | 39.6 | 0.84848 | 0 | 13.5529 | 13.4731 | 14.25 | 106.65 | 0.12633 | 6.6 | 6.15 | 36 | 400 | 411 | 1845 | 2511 | -36.0976 | 91.2409 | 1461 | 97.5359 | 159 | 137 | 17 | 25.3 | 13.8 | 39.1 | 39.1 | 0.44645 | 0.64706 | 15.3076 | 15.2173 | 7.2258 | 123.7742 | 0.12294 | 5.96 |  | 29 | 406 | 917 | 1097.1667 | -19.6474 | 92.944 | 751.5833 | 96.1415 | 137 | 120 | 20 | 8.2 | 5.9 | 14.1 | 14.1 | 0.33758 | 0.58156 | 9.9227 | 9.8642 | 14.4576 | 94.0424 | 0.10489 |  | 6.87 | 64 | 917 | 1845 | 2102.5254 | -13.958 | 84.4282 | 1509.7627 | 95.7609 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.1303 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3844 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.8934 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5238 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3384 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5323 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 43.76 | [5 empty] | 1998-04-24 | 8:18 | 20274 | 25.2 | 159 | 120 | 18.5 | 0 | 31.9 | 6 |  | 37.9 | 37.9 | 0.84169 | 0 | 12.8672 | 12.7914 | 13.5358 | 107.4642 | 0.11903 | 6.72 | 6.16 | 36 | 404 | 406 | 1844 | 2373.1667 | -28.6967 | 91.133 | 1389.5833 | 97.4093 | 159 | 137 | 17 | 23.5 | 15.5 | 39 | 39 | 0.45995 | 0.60256 | 14.2185 | 14.1347 | 6.6279 | 124.3721 | 0.11365 | 6.17 |  | 29 | 406 | 920 | 977.5806 | -6.2588 | 92.8571 | 691.7903 | 95.808 | 137 | 120 | 20 | 8.4 | 5.9 | 14.3 | 14.3 | 0.34095 | 0.58741 | 10.1647 | 10.1048 | 14.6364 | 93.8636 | 0.10765 |  | 6.84 | 65 | 920 | 1844 | 2137.2881 | -15.905 | 83.9901 | 1528.6441 | 95.7479 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 24.7917 | [5 empty] | 1998-04-25 | 1:00 | 20302 | 25.2 | 159 | 121 | 18.5 | 0 | 32 | 6 |  | 38 | 38 | 0.84211 | 0 | 12.9076 | 12.8315 | 14.1533 | 107.3467 | 0.11953 | 6.8 | 6.19 | 39 | 418 | 425 | 1800 | 2483.6667 | -37.9815 | 90.8235 | 1454.3333 | 97.3184 | 159 | 137 | 17 | 23.3 | 15.4 | 38.7 | 38.7 | 0.45657 | 0.60207 | 14.0975 | 14.0144 | 6.9908 | 124.0092 | 0.11301 | 6.19 |  | 27 | 425 | 945 | 1027.1688 | -8.6951 | 93.6471 | 726.0844 | 96.2814 | 137 | 121 | 20 | 8.6 | 5.7 | 14.3 | 14.3 | 0.33758 | 0.6014 | 10.4067 | 10.3454 | 15.4386 | 93.5614 | 0.11057 |  | 6.86 | 65 | 945 | 1800 | 2272.7193 | -26.2622 | 84.7059 | 1608.8596 | 95.9599 | SDS-HAA5 | mg/L | 1.8 | 22.7 | --- | 132.425 | --- | 92.0705 | 77.5625 | 97.6793 | [8 empty] | SDS-HAA5 | mg/L | 12.3 | 188.2 | --- | 1184.9667 | --- | 93.4644 | 686.5833 | 98.2085 | [8 empty] | SDS-HAA5 | mg/L | 0.79 | 325.42 | --- | 2029.7275 | --- | 99.7572 | 1177.5738 | 99.9329 | [8 empty] | SDS-HAA5 | mg/L | 6.83 | 283.38 | --- | 1735.2675 | --- | 97.5898 | 1009.3238 | 99.3233 | [8 empty] | SDS-HAA5 | mg/L | 0 | 234 | --- | 1376.4706 | --- | 100 | 805.2353 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 280 | --- | 1647.0588 | --- | 100 | 963.5294 | 100
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 18.9683 | [5 empty] | 1998-04-26 | 9:10 | 20323 | 25.2 | 159 | 121 | 18.6 | 0 | 31.3 | 6 |  | 37.3 | 37.3 | 0.83914 | 0 | 12.6252 | 12.5508 | 13.7838 | 107.6162 | 0.11663 | 6.67 | 6.13 | 37 | 412 | 419 | 1892 | 2411.7667 | -27.4718 | 91.1695 | 1415.3833 | 97.3859 | 159 | 138 | 17 | 22.8 | 15.9 | 38.7 | 38.7 | 0.46079 | 0.58915 | 13.795 | 13.7136 | 6.5074 | 124.9926 | 0.10972 | 6.16 |  | 30 | 409 | 931 | 952.4717 | -2.3063 | 92.8401 | 680.7358 | 95.593 | 138 | 121 | 20 | 8.5 | 5.6 | 14.1 | 14.1 | 0.33251 | 0.60284 | 10.2857 | 10.2251 | 15.2147 | 94.2853 | 0.10845 |  | 6.8 | 66 | 931 | 1892 | 2243.9464 | -18.6018 | 84.2482 | 1587.4732 | 95.8424 | SDS-HAA6 | mg/L | 1.8 | 22.7 | --- | 132.425 | --- | 92.0705 | 77.5625 | 97.6793 | [8 empty] | SDS-HAA6 | mg/L | 12.9 | 212 | --- | 1340.2333 | --- | 93.9151 | 776.1167 | 98.3379 | [8 empty] | SDS-HAA6 | mg/L | 2.31 | 356.42 | --- | 2215.4975 | --- | 99.3519 | 1285.9588 | 99.8204 | [8 empty] | SDS-HAA6 | mg/L | 8.36 | 310.18 | --- | 1894.735 | --- | 97.3048 | 1102.4575 | 99.2417 | [8 empty] | SDS-HAA6 | mg/L | 0 | 249 | --- | 1464.7059 | --- | 100 | 856.8529 | 100 | [8 empty] | SDS-HAA6 | mg/L | 0 | 295.7 | --- | 1739.4118 | --- | 100 | 1017.5559 | 100
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 18.9683 | [5 empty] | 1998-04-27 | 9:40 | 20347 | 25.3 | 158 | 119 | 18.2 | 0 | 31.9 | 6 |  | 37.9 | 37.9 | 0.84169 | 0 | 12.8672 | 12.7536 | 13.9017 | 106.3983 | 0.11987 | 6.68 | 6.14 | 36 | 397 | 416 | 1823 | 2436.3333 | -33.6442 | 91.3462 | 1426.1667 | 97.4758 | 158 | 136 | 17 | 23.6 | 15.1 | 38.7 | 38.7 | 0.45404 | 0.60982 | 14.279 | 14.1529 | 6.7339 | 123.2661 | 0.11482 | 6.13 |  | 29 | 407 | 913 | 997.7815 | -9.286 | 93.0288 | 702.3907 | 95.8712 | 136 | 119 | 19 | 8.3 | 5.9 | 14.2 | 14.2 | 0.33927 | 0.58451 | 10.0437 | 9.955 | 14.4447 | 94.0553 | 0.10584 |  | 6.79 | 65 | 913 | 1823 | 2105.9492 | -15.5211 | 84.375 | 1509.4746 | 95.6939 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.3958 | [5 empty] | 1998-04-28 | 9:35 | 20371 | 25.2 | 158 | 119 | 18.2 | 0 | 30.4 | 6 |  | 36.4 | 36.4 | 0.83516 | 0 | 12.2622 | 12.1899 | 13.356 | 106.944 | 0.11398 | 6.67 | 6.11 | 36 | 397 | 414 | 1848 | 2329.2 | -26.039 | 91.3043 | 1371.6 | 97.3753 | 158 | 136 | 17 | 21.9 | 16.7 | 38.6 | 38.6 | 0.4667 | 0.56736 | 13.2504 | 13.1723 | 6.2751 | 123.7249 | 0.10646 | 6.11 |  | 29 | 408 | 925 | 905.012 | 2.1609 | 92.9952 | 656.506 | 95.5827 | 136 | 119 | 19 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 10.1048 | 14.8276 | 93.6724 | 0.10787 |  | 6.79 | 65 | 925 | 1848 | 2170.5172 | -17.4522 | 84.2995 | 1547.7586 | 95.8004 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 6.5725 | [5 empty] | 1998-04-29 | 8:55 | 20394 | 25.2 | 158 | 119 | 18.1 | 0 | 32.2 | 6 |  | 38.2 | 38.2 | 0.84293 | 0 | 12.9882 | 12.9117 | 13.702 | 106.698 | 0.12101 | 6.73 | 6.07 | 36 | 402 | 408 | 1823 | 2404.4 | -31.8925 | 91.1765 | 1406.2 | 97.4399 | 158 | 136 | 17 | 23.6 | 15 | 38.6 | 38.6 | 0.45235 | 0.6114 | 14.279 | 14.1948 | 6.7357 | 123.2643 | 0.11516 | 6.1 |  | 30 | 407 | 913 | 1000.1467 | -9.5451 | 92.6471 | 703.5733 | 95.7361 | 136 | 119 | 19 | 8.5 | 5.8 | 14.3 | 14.3 | 0.33927 | 0.59441 | 10.2857 | 10.2251 | 14.6938 | 93.8062 | 0.109 |  | 6.8 | 65 | 913 | 1823 | 2155.7586 | -18.2534 | 84.0686 | 1534.3793 | 95.7638
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-04-30 | 12:15 | 20422 | 25.3 | 158 | 118 | 17.8 | 0 | 33.7 | 5.8 |  | 39.5 | 39.5 | 0.85316 | 0 | 13.5933 | 13.4733 | 15.1521 | 105.0479 | 0.12826 | 6.66 | 6.1 | 36 | 405 | 424 | 1788 | 2678.4138 | -49.7994 | 91.5094 | 1551.2069 | 97.6792 | 158 | 135 | 17 | 25 | 13.7 | 38.7 | 38.7 | 0.44223 | 0.64599 | 15.1261 | 14.9925 | 7.248 | 122.252 | 0.12264 | 6.08 |  | 30 | 409 | 912 | 1100.6058 | -20.6805 | 92.9245 | 754.8029 | 96.0255 | 135 | 118 | 19 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 10.4348 | 14.6107 | 92.8893 | 0.11234 |  | 6.79 | 65 | 912 | 1788 | 2140.15 | -19.6952 | 84.6698 | 1526.075 | 95.7407 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 6.5625 | [5 empty] | 1998-05-01 | 9:00 | 20443 | 25.2 | 158 | 120 | 17.2 | 0 | 32.5 | 5.8 |  | 38.3 | 38.3 | 0.84856 | 0 | 13.1092 | 13.032 | 14.4085 | 107.3915 | 0.12135 | 6.75 | 6.16 | 37 | 402 | 416 | 1855 | 2539.7069 | -36.9114 | 91.1058 | 1477.8534 | 97.4964 | 158 | 137 | 16 | 24.8 | 13.8 | 38.6 | 38.6 | 0.44223 | 0.64249 | 15.005 | 14.9166 | 7.2335 | 124.2665 | 0.12004 | 6.08 |  | 30 | 411 | 928 | 1095.6957 | -18.0707 | 92.7885 | 753.3478 | 96.0178 | 137 | 120 | 18 | 8.3 | 5.8 | 14.1 | 14.1 | 0.33589 | 0.58865 | 10.0437 | 9.9845 | 14.7878 | 95.7122 | 0.10432 |  | 6.79 | 66 | 928 | 1855 | 2161.5517 | -16.5257 | 84.1346 | 1544.7759 | 95.7275 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 37.1875 | [5 empty] | 1998-05-02 | 8:48 | 20466 | 25.2 | 159 | 120 | 17.9 | 0 | 32.8 | 5.8 |  | 38.6 | 38.6 | 0.84974 | 0 | 13.2303 | 13.1523 | 13.8941 | 107.7059 | 0.12211 | 6.73 | 6.11 | 37 | 400 | 400 | 1826 | 2452.8276 | -34.3279 | 90.75 | 1426.4138 | 97.4061 | 159 | 137 | 17 | 24.5 | 14 | 38.5 | 38.5 | 0.44307 | 0.63636 | 14.8235 | 14.7362 | 7.0687 | 123.9313 | 0.11891 | 6.09 |  | 30 | 407 | 917 | 1066.75 | -16.3304 | 92.5 | 736.875 | 95.9288 | 137 | 120 | 19 | 8.2 | 5.8 | 14 | 14 | 0.3342 | 0.58571 | 9.9227 | 9.8642 | 14.5428 | 94.9572 | 0.10388 |  | 6.79 | 65 | 917 | 1826 | 2121.5517 | -16.1857 | 83.75 | 1519.2759 | 95.7216 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 43.75 | [5 empty] | 1998-05-03 | 8:38 | 20490 | 25.3 | 159 | 120 | 18.2 | 0 | 31.3 | 5.8 |  | 37.1 | 37.1 | 0.84367 | 0 | 12.6252 | 12.5137 | 13.8316 | 107.4684 | 0.11644 | 6.66 | 6.05 | 36 | 397 | 410 | 1802 | 2428.3103 | -34.7564 | 91.2195 | 1419.1552 | 97.4633 | 159 | 137 | 17 | 23.4 | 15 | 38.4 | 38.4 | 0.45067 | 0.60938 | 14.158 | 14.033 | 6.6394 | 124.3606 | 0.11284 | 6.08 |  | 30 | 403 | 906 | 984.88 | -8.7064 | 92.6829 | 693.94 | 95.6769 | 137 | 120 | 19 | 7.9 | 5.8 | 13.7 | 13.7 | 0.32914 | 0.57664 | 9.5597 | 9.4753 | 14.1375 | 95.3625 | 0.099361 |  | 6.76 | 65 | 906 | 1802 | 2051.5 | -13.8457 | 84.1463 | 1478.75 | 95.6044 | Qp/QT (THM4), % | -1900 | -900 |  | Qp/QT (HAA5), % | -149.7608 | -20.5742 | [11 empty] | Qp/QT (THM4), % | 86.5501 | 93.7877 |  | Qp/QT (HAA5), % | 76.2933 | 91.643 | [11 empty] | Qp/QT (THM4), % | 87.7925 | 94.3225 |  | Qp/QT (HAA5), % | 83.609 | 91.9262 | [11 empty] | Qp/QT (THM4), % | 87.8341 | 94.47 |  | Qp/QT (HAA5), % | 82.9434 | 92.7066 | [11 empty] | Qp/QT (THM4), % | 84.0524 | 92.1843 |  | Qp/QT (HAA5), % | 76.9231 | 88.4615 | [11 empty] | Qp/QT (THM4), % | 85.1041 | 92.6783 |  | Qp/QT (HAA5), % | 80.7143 | 90.3571
[11 empty] | 1998-05-04 | 9:50 | 20515 | 25.3 | 159 | 120 | 18 | 0 | 30.5 | 5.8 |  | 36.3 | 36.3 | 0.84022 | 0 | 12.3025 | 12.1939 | 13.6099 | 107.8901 | 0.11302 | 6.76 | 6.12 | 37 | 396 | 412 | 1826 | 2383.9828 | -30.5577 | 91.0194 | 1397.9914 | 97.3533 | 159 | 137 | 17 | 22.2 | 16.2 | 38.4 | 38.4 | 0.46079 | 0.57812 | 13.4319 | 13.3133 | 6.37 | 124.63 | 0.10682 | 6.07 |  | 30 | 408 | 921 | 926 | -0.54289 | 92.7184 | 667 | 95.5022 | 137 | 120 | 19 | 8.3 | 5.8 | 14.1 | 14.1 | 0.33589 | 0.58865 | 10.0437 | 9.955 | 14.6848 | 94.8152 | 0.10499 |  | 6.8 | 65 | 921 | 1826 | 2145.9655 | -17.5228 | 84.2233 | 1533.4828 | 95.7613 | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 123.0169 | 46.6678 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 95.0634 | 49.2109 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 98.532 | 45.5669 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 103.5615 | 52.4808 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 92.865 | 47.0325
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-05-05 | 9:13 | 20539 | 25.3 | 159 | 121 | 17.8 | 0 | 31.9 | 5.6 |  | 37.5 | 37.5 | 0.85067 | 0 | 12.8672 | 12.7536 | 14.2769 | 107.9231 | 0.11817 | 6.68 | 6.12 | 37 | 374 | 408 | 1891 | 2521.375 | -33.3355 | 90.9314 | 1464.6875 | 97.4739 | 159 | 137 | 17 | 23.5 | 14.5 | 38 | 38 | 0.44307 | 0.61842 | 14.2185 | 14.093 | 6.9155 | 124.0845 | 0.11358 | 6.06 |  | 30 | 412 | 935 | 1031.1034 | -10.2784 | 92.6471 | 721.5517 | 95.8423 | 137 | 121 | 19 | 8.3 | 5.6 | 13.9 | 13.9 | 0.32914 | 0.59712 | 10.0437 | 9.955 | 15.1125 | 94.8875 | 0.10491 |  | 6.73 | 67 | 935 | 1891 | 2221.5 | -17.4775 | 83.5784 | 1578.25 | 95.7548 | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA | [11 empty] | SDS-HAA5b, mg/L | 35.9584 | 23.2274 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 40.4192 | 19.2208 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 40.4748 | 22.1231 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 37.3174 | 18.2887 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 41.7084 | 20.5007 |  | SDS-HAA5b, mg/L | 54 | 27
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 6.8 | [5 empty] | 1998-05-06 | 8:32 | 20562 | 25.3 | 157 | 120 | 17.6 | 0 | 32.1 | 5.6 |  | 37.7 | 37.7 | 0.85146 | 0 | 12.9479 | 12.8336 | 13.8792 | 107.0208 | 0.11992 | 6.69 | 6.13 | 38 | 395 | 397 | 1858 | 2454.8393 | -32.1227 | 90.4282 | 1425.9196 | 97.3351 | 157 | 136 | 17 | 24.1 | 13.7 | 37.8 | 37.8 | 0.43463 | 0.63757 | 14.5815 | 14.4528 | 7.2175 | 122.2825 | 0.11819 | 6.04 |  | 30 | 414 | 935 | 1089.5036 | -16.5245 | 92.4433 | 751.7518 | 96.0093 | 136 | 120 | 19 | 7.9 | 5.6 | 13.5 | 13.5 | 0.32239 | 0.58519 | 9.5597 | 9.4753 | 14.8025 | 94.1975 | 0.10059 |  | 6.74 | 67 | 935 | 1858 | 2159.5 | -16.2271 | 83.1234 | 1547.25 | 95.6697 | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 26.1 | [5 empty] | 1998-05-07 | 8:17 | 20586 | 25.3 | 158 | 120 | 17.5 | 0 | 29.2 | 5.7 |  | 34.9 | 34.9 | 0.83668 | 0 | 11.7782 | 11.6742 | 13.4977 | 108.0023 | 0.10809 | 6.69 | 6.07 | 37 | 404 | 416 | 1826 | 2357.5439 | -29.1097 | 91.1058 | 1386.7719 | 97.3319 | 158 | 136 | 17 | 21.2 | 16.6 | 37.8 | 37.8 | 0.4591 | 0.56085 | 12.8269 | 12.7136 | 6.2101 | 123.7899 | 0.1027 | 6.04 |  | 30 | 409 | 921 | 893.0241 | 3.0376 | 92.7885 | 651.012 | 95.3918 | 136 | 120 | 19 | 8 | 5.7 | 13.7 | 13.7 | 0.32745 | 0.58394 | 9.6807 | 9.5952 | 14.55 | 94.45 | 0.10159 |  | 6.71 | 66 | 921 | 1826 | 2121 | -16.1555 | 84.1346 | 1521 | 95.6607 | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA | [11 empty] | SDS-CDb, mg/L | 5.1806 | 3.8996 |  | SDS-CDb, mg/L | 6.9961 | 4.2792 | [11 empty] | SDS-CDb, mg/L | 4.7485 | 3.5992 |  | SDS-CDb, mg/L | 5.4848 | 4.021 | [11 empty] | SDS-CDb, mg/L | 5.0967 | 3.7894 |  | SDS-CDb, mg/L | 6.0601 | 4.1368 | [11 empty] | SDS-CDb, mg/L | 5.2908 | 3.8677 |  | SDS-CDb, mg/L | 6.5385 | 4.5192 | [11 empty] | SDS-CDb, mg/L | 5.1142 | 3.785 |  | SDS-CDb, mg/L | 5.8846 | 4.1923
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1998-05-08 | 8:15 | 20610 | 25.3 | 158 | 121 | 17.6 | 0 | 31.1 | 5.5 |  | 36.6 | 36.6 | 0.84973 | 0 | 12.5445 | 12.4338 | 13.9313 | 107.9687 | 0.11516 | 6.72 | 6.07 | 38 | 381 | 402 | 1873 | 2460.2545 | -31.3537 | 90.5473 | 1431.1273 | 97.3448 | 158 | 137 | 17 | 22.8 | 14.9 | 37.7 | 37.7 | 0.44391 | 0.60477 | 13.795 | 13.6732 | 6.6191 | 123.8809 | 0.11037 | 6.06 |  | 30 | 405 | 925 | 978.8255 | -5.819 | 92.5373 | 691.9128 | 95.6642 | 137 | 121 | 19 | 8.2 | 5.5 | 13.7 | 13.7 | 0.32407 | 0.59854 | 9.9227 | 9.8351 | 14.9935 | 95.0065 | 0.10352 |  | 6.71 | 66 | 925 | 1873 | 2205.6909 | -17.7625 | 83.5821 | 1565.3455 | 95.7837 | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-05-09 | 8:18 | 20634 | 25.2 | 160 | 121 | 19.3 | 0 | 33 | 5.9 |  | 38.9 | 38.9 | 0.84833 | 0 | 13.3109 | 13.2325 | 14.2753 | 106.9247 | 0.12375 | 6.72 | 6.07 | 36 | 385 | 412 | 1860 | 2515.0508 | -35.2178 | 91.2621 | 1463.5254 | 97.5402 | 160 | 137 | 18 | 233.7 | 15.9 | 249.6 | 249.6 | 2.2407 | 0.9363 | 141.3983 | 140.5649 | 31.8099 | 98.6901 | 1.4243 | 6.07 |  | 30 | 411 | 906 | 6010.9811 | -563.4637 | 92.7184 | 3210.9906 | 99.0657 | 137 | 121 | 21 | 9.3 | 5.9 | 15.2 | 15.2 | 0.35614 | 0.61184 | 11.2538 | 11.1874 | 15.1097 | 92.8903 | 0.12044 |  | 6.66 | 61 | 906 | 1860 | 2237.9492 | -20.3198 | 85.1942 | 1571.9746 | 96.1195 | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
|  |  |  | Design permeate pressure, Pp (psi) | 10 | [5 empty] | 1998-05-10 | 8:45 | 20658 | 25.3 | 161 | 120 | 19.2 | 0 | 33.5 | 5.9 |  | 39.4 | 39.4 | 0.85025 | 0 | 13.5126 | 13.3933 | 14.6265 | 106.6735 | 0.12555 | 6.76 | 6.06 | 36 | 402 | 417 | 1855 | 2580.3051 | -39.1 | 91.3669 | 1498.6525 | 97.5978 | 161 | 137 | 18 | 24.4 | 14.8 | 39.2 | 39.2 | 0.45573 | 0.62245 | 14.763 | 14.6327 | 6.9507 | 124.0493 | 0.11796 | 6.07 |  | 30 | 411 | 906 | 1039.1351 | -14.6948 | 92.8058 | 725.0676 | 95.8625 | 137 | 120 | 21 | 9 | 5.9 | 14.9 | 14.9 | 0.35108 | 0.60403 | 10.8908 | 10.7946 | 14.8773 | 92.6227 | 0.11654 |  | 6.72 | 62 | 906 | 1855 | 2193.4576 | -18.2457 | 85.1319 | 1549.7288 | 95.9993 | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA | [11 empty] | Bromideb, mg/L | 66.2334 | 55.8836 |  | Bromideb, mg/L | 80.9005 | 58.9505 | [11 empty] | Bromideb, mg/L | 46.0136 | 36.2708 |  | Bromideb, mg/L | 52.2553 | 39.8461 | [11 empty] | Bromideb, mg/L | 46.472 | 36.2327 |  | Bromideb, mg/L | 54.0183 | 38.9538 | [11 empty] | Bromideb, mg/L | 49.9882 | 37.6033 |  | Bromideb, mg/L | 60.8462 | 43.2731 | [11 empty] | Bromideb, mg/L | 51.0886 | 39.3486 |  | Bromideb, mg/L | 57.8929 | 42.9464
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 26 | [5 empty] | 1998-05-11 | 9:40 | 20683 | 25.2 | 161 | 121 | 19.1 | 0 | 33.5 | 6 |  | 39.5 | 39.5 | 0.8481 | 0 | 13.5126 | 13.433 | 14.4842 | 107.4158 | 0.12506 | 6.77 | 6.05 | 36 | 403 | 418 | 1827 | 2550.8333 | -39.6187 | 91.3876 | 1484.4167 | 97.5748 | 161 | 137 | 18 | 24.7 | 15.1 | 39.8 | 39.8 | 0.46332 | 0.6206 | 14.9445 | 14.8564 | 6.8171 | 124.1829 | 0.11963 | 6.02 |  | 36 | 411 | 900 | 1024.4106 | -13.8234 | 91.3876 | 717.7053 | 94.984 | 137 | 121 | 21 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 10.4657 | 14.49 | 93.51 | 0.11192 |  | 6.7 | 60 | 900 | 1827 | 2118 | -15.9278 | 85.6459 | 1509 | 96.0239 | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA | [11 empty] | Alkb, mg/L CaCO3 | 29.0639 | 20.9578 |  | Alkb, mg/L CaCO3 | 40.5514 | 23.3599 | [11 empty] | Alkb, mg/L CaCO3 | 29.9918 | 21.4375 |  | Alkb, mg/L CaCO3 | 35.4722 | 24.5767 | [11 empty] | Alkb, mg/L CaCO3 | 25.1926 | 19.0876 |  | Alkb, mg/L CaCO3 | 29.6921 | 20.71 | [11 empty] | Alkb, mg/L CaCO3 | 31.2234 | 22.4409 |  | Alkb, mg/L CaCO3 | 38.9231 | 26.4615 | [11 empty] | Alkb, mg/L CaCO3 | 28.5979 | 21.1753 |  | Alkb, mg/L CaCO3 | 32.9 | 23.45
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 46.875 | [5 empty] | 1998-05-12 | 8:50 | 20706 | 25.3 | 162 | 123 | 18.6 | 0 | 32.5 | 6 |  | 38.5 | 38.5 | 0.84416 | 0 | 13.1092 | 12.9935 | 14.0917 | 109.8083 | 0.11833 | 6.73 | 6.05 | 36 | 401 | 416 | 1834 | 2474.3333 | -34.9146 | 91.3462 | 1445.1667 | 97.5089 | 162 | 139 | 17 | 24.1 | 15.4 | 39.5 | 39.5 | 0.46332 | 0.61013 | 14.5815 | 14.4528 | 6.7912 | 126.7088 | 0.11406 | 6.02 |  | 30 | 411 | 910 | 1007.2403 | -10.6857 | 92.7885 | 709.1201 | 95.7694 | 139 | 123 | 20 | 8.3 | 6 | 14.3 | 14.3 | 0.34264 | 0.58042 | 10.0437 | 9.955 | 14.3792 | 96.6208 | 0.10303 |  | 6.62 | 60 | 910 | 1834 | 2085.8333 | -13.7314 | 85.5769 | 1497.9167 | 95.9944 | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA | [11 empty] | T-Hdb, mg/L CaCO3 | 45.4729 | 28.5368 |  | T-Hdb, mg/L CaCO3 | 69.4736 | 33.5554 | [11 empty] | T-Hdb, mg/L CaCO3 | 40.711 | 25.8879 |  | T-Hdb, mg/L CaCO3 | 50.2075 | 31.3275 | [11 empty] | T-Hdb, mg/L CaCO3 | 41.1982 | 25.2719 |  | T-Hdb, mg/L CaCO3 | 52.9358 | 29.5042 | [11 empty] | T-Hdb, mg/L CaCO3 | 54.9121 | 35.0703 |  | T-Hdb, mg/L CaCO3 | 72.3077 | 44.1538 | [11 empty] | T-Hdb, mg/L CaCO3 | 50.5584 | 32.9863 |  | T-Hdb, mg/L CaCO3 | 60.7429 | 38.3714
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 43.5667 | [5 empty] | 1998-05-13 | 8:55 | 20730 | 25.3 | 161 | 122 | 18.5 | 0 | 32.6 | 6 |  | 38.6 | 38.6 | 0.84456 | 0 | 13.1496 | 13.0335 | 13.7145 | 109.2855 | 0.11926 | 6.69 | 6.03 | 36 | 389 | 405 | 1812 | 2409.9 | -32.9967 | 91.1111 | 1407.45 | 97.4422 | 161 | 139 | 17 | 23.7 | 15.7 | 39.4 | 39.4 | 0.46501 | 0.60152 | 14.3395 | 14.2129 | 6.6682 | 126.3318 | 0.1125 | 6.01 |  | 30 | 410 | 904 | 983.6306 | -8.8087 | 92.5926 | 696.8153 | 95.6947 | 139 | 122 | 20 | 8.9 | 6 | 14.9 | 14.9 | 0.35277 | 0.59732 | 10.7697 | 10.6747 | 14.6997 | 95.8003 | 0.11143 |  | 6.64 | 60 | 904 | 1812 | 2155.9333 | -18.9809 | 85.1852 | 1529.9667 | 96.0783 | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA | [11 empty] | Ca-Hdb, mg/L CaCO3 | 41.8589 | 25.7913 |  | Ca-Hdb, mg/L CaCO3 | 64.6288 | 30.5526 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 38.6124 | 24.3769 |  | Ca-Hdb, mg/L CaCO3 | 47.7323 | 29.6009 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 33.7917 | 19.7235 |  | Ca-Hdb, mg/L CaCO3 | 44.16 | 23.4621 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 45.7226 | 27.5071 |  | Ca-Hdb, mg/L CaCO3 | 61.6923 | 35.8462 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 44.2605 | 26.8399 |  | Ca-Hdb, mg/L CaCO3 | 54.3571 | 32.1786
|  |  |  | Required influent pressure to the system, PI (psi) | 100.4417 | [5 empty] | 1998-05-14 | 9:25 | 20755 | 25.3 | 162 | 122 | 18.7 | 0 | 33.9 | 6 |  | 39.9 | 39.9 | 0.84962 | 0 | 13.6739 | 13.5532 | 13.9995 | 109.3005 | 0.124 | 6.71 | 6.15 | 34 | 394 | 400 | 1798 | 2467.9 | -37.2581 | 91.5 | 1433.95 | 97.6289 | 162 | 139 | 17 | 25.4 | 14 | 39.4 | 39.4 | 0.45067 | 0.64467 | 15.3681 | 15.2324 | 7.1518 | 126.3482 | 0.12056 | 6.09 |  | 28 | 403 | 896 | 1083.3571 | -20.9104 | 93 | 743.1786 | 96.2324 | 139 | 122 | 20 | 8.4 | 6 | 14.4 | 14.4 | 0.34433 | 0.58333 | 10.1647 | 10.075 | 14.229 | 96.271 | 0.10465 |  | 6.79 | 59 | 896 | 1798 | 2067.8 | -15.0056 | 85.25 | 1481.9 | 96.0186 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-05-15 | 9:15 | 20778 | 25.3 | 162 | 123 | 18.8 | 0 | 30.7 | 6 |  | 36.7 | 36.7 | 0.83651 | 0 | 12.3832 | 12.2739 | 12.9879 | 110.7121 | 0.11086 | 6.76 | 6.13 | 34 | 386 | 399 | 1792 | 2266.5833 | -26.4834 | 91.4787 | 1332.7917 | 97.449 | 162 | 139 | 18 | 22.1 | 17.3 | 39.4 | 39.4 | 0.47852 | 0.56091 | 13.3714 | 13.2534 | 6.1452 | 126.3548 | 0.10489 | 6.06 |  | 28 | 403 | 896 | 882.0462 | 1.5573 | 92.9825 | 642.5231 | 95.6422 | 139 | 123 | 20 | 8.5 | 6 | 14.5 | 14.5 | 0.34602 | 0.58621 | 10.2857 | 10.1949 | 14.2988 | 96.7013 | 0.10543 |  | 6.76 | 59 | 896 | 1792 | 2081.75 | -16.1691 | 85.213 | 1488.875 | 96.0373 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-05-16 | 8:15 | 20801 | 25.2 | 161 | 122 | 18.2 | 0 | 33 | 6 |  | 39 | 39 | 0.84615 | 0 | 13.3109 | 13.2325 | 14.3625 | 108.9375 | 0.12147 | 6.95 | 6.26 | 35 | 408 | 418 | 1810 | 2524.5 | -39.4751 | 91.6268 | 1471.25 | 97.6211 | 161 | 138 | 17 | 24.2 | 15.9 | 40.1 | 40.1 | 0.47261 | 0.60349 | 14.642 | 14.5557 | 6.639 | 125.861 | 0.11565 | 6.01 |  | 29 | 406 | 900 | 979.7987 | -8.8665 | 93.0622 | 692.8994 | 95.8147 | 138 | 122 | 19 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 10.4657 | 14.49 | 96.51 | 0.10844 |  | 6.77 | 60 | 900 | 1810 | 2118 | -17.0166 | 85.6459 | 1509 | 96.0239 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1998-05-17 | 9:05 | 20826 | 25.3 | 161 | 122 | 18.4 | 0 | 30.8 | 5.9 |  | 36.7 | 36.7 | 0.83924 | 0 | 12.4235 | 12.3138 | 13.6103 | 109.4897 | 0.11247 | 6.81 | 6.16 | 35 | 397 | 412 | 1799 | 2380.0678 | -32.2995 | 91.5049 | 1396.0339 | 97.4929 | 161 | 139 | 17 | 22.2 | 16.9 | 39.1 | 39.1 | 0.47261 | 0.56777 | 13.4319 | 13.3133 | 6.2462 | 126.7538 | 0.10503 | 6.06 |  | 28 | 405 | 896 | 900.2308 | -0.47218 | 93.2039 | 652.6154 | 95.7096 | 139 | 122 | 20 | 8.6 | 5.9 | 14.5 | 14.5 | 0.34433 | 0.5931 | 10.4067 | 10.3148 | 14.4529 | 96.0471 | 0.10739 |  | 6.72 | 60 | 896 | 1799 | 2114.5763 | -17.5418 | 85.4369 | 1505.2881 | 96.0141 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1998-05-18 | 9:10 | 20850 | 25.4 | 162 | 124 | 18.5 | 0 | 32.8 | 5.9 |  | 38.7 | 38.7 | 0.84755 | 0 | 13.2303 | 13.0747 | 14.0981 | 110.4019 | 0.11843 | 6.85 | 6.13 | 34 | 397 | 407 | 1820 | 2480.6271 | -36.2982 | 91.6462 | 1443.8136 | 97.6451 | 162 | 140 | 17 | 23.5 | 15.9 | 39.4 | 39.4 | 0.4667 | 0.59645 | 14.2185 | 14.0514 | 6.5386 | 127.4614 | 0.11024 | 6.04 |  | 28 | 404 | 900 | 959.7233 | -6.6359 | 93.1204 | 681.8616 | 95.8936 | 140 | 124 | 20 | 9.3 | 5.9 | 15.2 | 15.2 | 0.35614 | 0.61184 | 11.2538 | 11.1215 | 15.0382 | 96.9618 | 0.1147 |  | 6.73 | 59 | 900 | 1820 | 2225.6441 | -22.2881 | 85.5037 | 1562.822 | 96.2248 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1998-05-19 | 8:43 | 20874 | 25.3 | 162 | 123 | 18.4 | 0 | 33.7 | 5.9 |  | 39.6 | 39.6 | 0.85101 | 0 | 13.5933 | 13.4733 | 14.7297 | 109.3703 | 0.12319 | 6.86 | 6.18 | 35 | 405 | 417 | 1837 | 2598.9322 | -41.477 | 91.6067 | 1507.9661 | 97.679 | 162 | 140 | 17 | 25 | 14.2 | 39.2 | 39.2 | 0.45067 | 0.63776 | 15.1261 | 14.9925 | 7.1451 | 126.8549 | 0.11819 | 6.04 |  | 29 | 409 | 910 | 1078.0141 | -18.4631 | 93.0456 | 743.507 | 96.0996 | 140 | 123 | 20 | 8.6 | 5.9 | 14.5 | 14.5 | 0.34433 | 0.5931 | 10.4067 | 10.3148 | 14.6949 | 96.8051 | 0.10655 |  | 6.68 | 60 | 910 | 1837 | 2148.9831 | -16.9833 | 85.6115 | 1529.4915 | 96.0771 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1998-05-20 | 8:30 | 20898 | 25.3 | 162 | 123 | 18.4 | 0 | 31 | 5.9 |  | 36.9 | 36.9 | 0.84011 | 0 | 12.5042 | 12.3938 | 13.7831 | 110.3169 | 0.11235 | 6.85 | 6.2 | 35 | 396 | 415 | 1820 | 2411.6102 | -32.5061 | 91.5663 | 1413.3051 | 97.5235 | 162 | 140 | 17 | 22.4 | 16.7 | 39.1 | 39.1 | 0.47092 | 0.57289 | 13.5529 | 13.4333 | 6.3485 | 127.6515 | 0.10523 | 6.02 |  | 29 | 409 | 906 | 918.7006 | -1.4018 | 93.012 | 663.8503 | 95.6315 | 140 | 123 | 20 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.1949 | 14.5541 | 96.9459 | 0.10516 |  | 6.7 | 60 | 906 | 1820 | 2124.8136 | -16.748 | 85.5422 | 1515.4068 | 96.0407 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1998-05-21 | 9:54 | 20923 | 25.3 | 162 | 123 | 18.5 | 0 | 31.9 | 5.9 |  | 37.8 | 37.8 | 0.84392 | 0 | 12.8672 | 12.7536 | 13.8877 | 110.1123 | 0.11582 | 6.88 | 6.2 | 35 | 396 | 410 | 1820 | 2437.5424 | -33.9309 | 91.4634 | 1423.7712 | 97.5417 | 162 | 140 | 17 | 23.4 | 15.6 | 39 | 39 | 0.46079 | 0.6 | 14.158 | 14.033 | 6.58 | 127.42 | 0.11013 | 6.11 |  | 29 | 405 | 903 | 969 | -7.309 | 92.9268 | 687 | 95.7787 | 140 | 123 | 20 | 8.4 | 5.9 | 14.3 | 14.3 | 0.34095 | 0.58741 | 10.1647 | 10.075 | 14.431 | 97.069 | 0.10379 |  | 6.7 | 60 | 903 | 1820 | 2103.2034 | -15.5606 | 85.3659 | 1503.1017 | 96.0083 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1998-05-22 | 9:26 | 20947 | 25.4 | 162 | 123 | 18.3 | 0 | 33.4 | 5.7 |  | 39.1 | 39.1 | 0.85422 | 0 | 13.4723 | 13.3139 | 14.4618 | 109.7382 | 0.12132 | 6.88 | 6.02 | 35 | 398 | 403 | 1841 | 2559.3509 | -39.0196 | 91.3151 | 1481.1754 | 97.637 | 162 | 139 | 17 | 24.8 | 14 | 38.8 | 38.8 | 0.4456 | 0.63918 | 15.005 | 14.8287 | 7.0903 | 126.4097 | 0.11731 | 6.1 |  | 29 | 405 | 904 | 1071.0571 | -18.4798 | 92.804 | 738.0286 | 96.0706 | 139 | 123 | 19 | 8.5 | 5.7 | 14.2 | 14.2 | 0.33589 | 0.59859 | 10.2857 | 10.1648 | 14.7155 | 97.2845 | 0.10449 |  | 6.52 | 61 | 904 | 1841 | 2161.1053 | -17.3876 | 84.8635 | 1532.5526 | 96.0197 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1998-05-23 | 8:10 | 20969 | 25.3 | 162 | 123 | 18.3 | 0 | 33.6 | 5.8 |  | 39.4 | 39.4 | 0.85279 | 0 | 13.5529 | 13.4333 | 14.9238 | 109.2762 | 0.12293 | 6.83 | 5.95 | 37 | 399 | 420 | 1827 | 2638.7586 | -44.4312 | 91.1905 | 1529.3793 | 97.5807 | 162 | 140 | 17 | 25.4 | 13.4 | 38.8 | 38.8 | 0.44054 | 0.65464 | 15.3681 | 15.2324 | 7.4404 | 126.5596 | 0.12036 | 5.94 |  | 31 | 413 | 910 | 1137.0896 | -24.9549 | 92.619 | 775.0448 | 96.0002 | 140 | 123 | 19 | 8.1 | 5.8 | 13.9 | 13.9 | 0.33251 | 0.58273 | 9.8017 | 9.7151 | 14.4014 | 98.0986 | 0.099034 |  | 6.52 | 62 | 910 | 1827 | 2094.2759 | -14.6292 | 85.2381 | 1502.1379 | 95.8725 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1998-05-24 | 7:35 | 20993 | 25.3 | 161 | 122 | 18.1 | 0 | 31.2 | 5.9 |  | 37.1 | 37.1 | 0.84097 | 0 | 12.5849 | 12.4738 | 14.0661 | 109.3339 | 0.11409 | 6.82 | 5.91 | 37 | 401 | 423 | 1788 | 2464.2203 | -37.8199 | 91.253 | 1443.6102 | 97.437 | 161 | 139 | 17 | 22.5 | 17 | 39.5 | 39.5 | 0.47683 | 0.56962 | 13.6134 | 13.4933 | 6.3479 | 126.6521 | 0.10654 | 5.89 |  | 31 | 413 | 906 | 918.5882 | -1.3894 | 92.6714 | 665.7941 | 95.3439 | 139 | 122 | 19 | 8.7 | 5.9 | 14.6 | 14.6 | 0.34602 | 0.59589 | 10.5277 | 10.4348 | 14.6801 | 96.8199 | 0.10778 |  | 6.45 | 61 | 906 | 1788 | 2152.0169 | -20.3589 | 85.5792 | 1529.0085 | 96.0105 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1998-05-25 | 8:10 | 21017 | 25.4 | 162 | 122 | 18.3 | 0 | 32.9 | 6 |  | 38.9 | 38.9 | 0.84576 | 0 | 13.2706 | 13.1146 | 14.2558 | 109.4442 | 0.11983 | 6.85 | 5.94 | 37 | 397 | 418 | 1770 | 2507.15 | -41.6469 | 91.1483 | 1462.575 | 97.4702 | 162 | 139 | 17 | 24.5 | 14.4 | 38.9 | 38.9 | 0.44982 | 0.62982 | 14.8235 | 14.6493 | 7.0697 | 126.4303 | 0.11587 | 5.89 |  | 31 | 413 | 902 | 1062.9306 | -17.8415 | 92.5837 | 737.9653 | 95.7993 | 139 | 122 | 19 | 8.3 | 6 | 14.3 | 14.3 | 0.34264 | 0.58042 | 10.0437 | 9.9256 | 14.2269 | 97.2731 | 0.10204 |  | 6.48 | 61 | 902 | 1770 | 2065.3833 | -16.6883 | 85.4067 | 1483.6917 | 95.8886
[11 empty] | 1998-05-26 | 8:35 | 21042 | 25.4 | 163 | 123 | 18.4 | 0 | 33.7 | 5.9 |  | 39.6 | 39.6 | 0.85101 | 0 | 13.5933 | 13.4335 | 14.9996 | 109.6004 | 0.12257 | 6.9 | 6 | 37 | 407 | 426 | 1812 | 2647.9153 | -46.1322 | 91.3146 | 1536.9576 | 97.5926 | 163 | 140 | 17 | 25 | 13.9 | 38.9 | 38.9 | 0.4456 | 0.64267 | 15.1261 | 14.9483 | 7.2363 | 127.2637 | 0.11746 | 6.08 |  | 29 | 410 | 903 | 1095.2518 | -21.2903 | 93.1925 | 752.6259 | 96.1468 | 140 | 123 | 20 | 8.6 | 5.9 | 14.5 | 14.5 | 0.34433 | 0.5931 | 10.4067 | 10.2844 | 14.6603 | 96.8397 | 0.1062 |  | 6.49 | 62 | 910 | 1812 | 2146.0678 | -18.4364 | 85.446 | 1528.0339 | 95.9425
[11 empty] | 1998-05-27 | 8:56 | 21066 | 25.3 | 162 | 122 | 18 | 0 | 30.5 | 6 |  | 36.5 | 36.5 | 0.83562 | 0 | 12.3025 | 12.1939 | 12.9625 | 111.0375 | 0.10982 | 6.86 | 6.1 | 35 | 385 | 401 | 1773 | 2261.5 | -27.5522 | 91.2718 | 1331.25 | 97.3709 | 162 | 139 | 17 | 21.9 | 16.9 | 38.8 | 38.8 | 0.47008 | 0.56443 | 13.2504 | 13.1334 | 6.3116 | 127.1884 | 0.10326 | 5.87 |  | 31 | 414 | 910 | 910.3136 | -0.034463 | 92.2693 | 662.1568 | 95.3183 | 139 | 122 | 19 | 8.5 | 6 | 14.5 | 14.5 | 0.34602 | 0.58621 | 10.2857 | 10.1949 | 14.4012 | 97.0987 | 0.105 |  | 6.63 | 60 | 903 | 1773 | 2097.25 | -18.2882 | 85.0374 | 1500.125 | 96.0003
[11 empty] | 1998-05-28 | 8:30 | 21090 | 25.3 | 163 | 124 | 17.9 | 0 | 29.7 | 5.8 |  | 35.5 | 35.5 | 0.83662 | 0 | 11.9798 | 11.8741 | 13.2801 | 112.3199 | 0.10572 | 6.89 | 6.17 | 36 | 405 | 409 | 1846 | 2319.0172 | -25.6239 | 91.198 | 1364.0086 | 97.3607 | 163 | 141 | 17 | 20.5 | 18 | 38.5 | 38.5 | 0.47683 | 0.53247 | 12.4034 | 12.2939 | 6.011 | 128.989 | 0.095309 | 6.09 |  | 30 | 413 | 921 | 849.1944 | 7.7965 | 92.665 | 631.0972 | 95.2464 | 141 | 124 | 19 | 8.7 | 5.8 | 14.5 | 14.5 | 0.34264 | 0.6 | 10.5277 | 10.4348 | 15.05 | 98.45 | 0.10599 |  | 6.69 | 61 | 921 | 1846 | 2211 | -19.7725 | 85.0856 | 1566 | 96.1047
[11 empty] | 1998-05-29 | 8:46 | 21114 | 25.3 | 164 | 125 | 18.2 | 0 | 30 | 5.8 |  | 35.8 | 35.8 | 0.83799 | 0 | 12.1008 | 11.994 | 14.0221 | 112.2779 | 0.10682 | 6.84 | 6.13 | 35 | 380 | 426 | 1846 | 2448.4138 | -32.6335 | 91.784 | 1437.2069 | 97.5647 | 164 | 142 | 17 | 21.4 | 17.4 | 38.8 | 38.8 | 0.4743 | 0.55155 | 12.9479 | 12.8336 | 6.1206 | 129.8794 | 0.098812 | 6.1 |  | 29 | 408 | 911 | 874.1264 | 4.0476 | 93.1925 | 641.0632 | 95.4763 | 142 | 125 | 19 | 8.5 | 5.8 | 14.3 | 14.3 | 0.33927 | 0.59441 | 10.2857 | 10.1949 | 14.7284 | 99.7716 | 0.10218 |  | 6.63 | 61 | 911 | 1846 | 2156.6897 | -16.8304 | 85.6808 | 1533.8448 | 96.0231
[11 empty] | 1998-05-30 | 8:25 | 21138 | 25.4 | 163 | 124 | 18 | 0 | 31.7 | 5.8 |  | 37.5 | 37.5 | 0.84533 | 0 | 12.7866 | 12.6363 | 13.8859 | 111.6141 | 0.11321 | 6.84 | 6.1 | 36 | 397 | 408 | 1827 | 2441.1724 | -33.6164 | 91.1765 | 1424.5862 | 97.473 | 163 | 141 | 17 | 23.5 | 14.9 | 38.4 | 38.4 | 0.44982 | 0.61198 | 14.2185 | 14.0514 | 6.8145 | 128.1855 | 0.10962 | 6.08 |  | 30 | 411 | 915 | 1011.906 | -10.5908 | 92.6471 | 711.453 | 95.7833 | 141 | 125 | 19 | 8.1 | 5.8 | 13.9 | 13.9 | 0.33251 | 0.58273 | 9.8017 | 9.6865 | 14.5033 | 99.4967 | 0.097355 |  | 6.6 | 61 | 915 | 1827 | 2107.6552 | -15.3615 | 85.049 | 1511.3276 | 95.9638
[11 empty] | 1998-05-31 | 8:55 | 21162 | 25.3 | 162 | 122 | 17.6 | 0 | 31.1 | 6 |  | 37.1 | 37.1 | 0.83827 | 0 | 12.5445 | 12.4338 | 16.5217 | 107.8783 | 0.11526 | 6.84 | 6.07 | 35 | 448 | 495 | 1763 | 2879.3333 | -63.3201 | 92.9293 | 1687.1667 | 97.9255 | 162 | 140 | 16 | 23.2 | 15.7 | 38.9 | 38.9 | 0.46079 | 0.5964 | 14.037 | 13.9131 | 6.5903 | 128.4097 | 0.10835 | 6.09 |  | 30 | 409 | 900 | 969.051 | -7.6723 | 93.9394 | 689.0255 | 95.646 | 140 | 122 | 19 | 7.8 | 6 | 13.8 | 13.8 | 0.3342 | 0.56522 | 9.4387 | 9.3553 | 13.86 | 98.14 | 0.095326 |  | 6.63 | 60 | 900 | 1763 | 1992 | -12.9892 | 87.8788 | 1446 | 95.8506
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on E23: S Allgeier (10/2/99): Reviewer changed width from 30 feet to 15 feet -- a value more typical for this membrane.
Note on BL7: C. Rice: Stage 1 concentrate pH was not measured.
Note on CJ7: C. Rice: Stage 2 influent pH was not measured.
Note on CW27: S Allgeier (8/21/99): Since a free residual was not measured at the end of incubation, this is not a valid SDS test, and the DBP data should not be used.
Note on CX27: S Allgeier (8/21/99): Since a free residual was not measured at the end of incubation, this is not a valid SDS test, and the DBP data should not be used.
Note on DB17: C. Rice: High MB closure errors for TDS are due to a TDS meter calibration error.
Note on DQ38: C. Rice: Consultant verified value; no explanation given.
Note on DR48: C. Rice: Consultant verified value. Dilution factor x10 was used; error could not be determined.
Note on DU17: C. Rice: High MB closure errors for TDS are due to a TDS meter calibration error.
Note on EO17: C. Rice: High MB closure errors for TDS are due to a TDS meter calibration error.
Note on FI17: C. Rice: High MB closure errors for TDS are due to a TDS meter calibration error.
Note on GC17: C. Rice: High MB closure errors for TDS are due to a TDS meter calibration error.
Note on GW17: C. Rice: High MB closure errors for TDS are due to a TDS meter calibration error.

## ESNA. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Week 12 | [9 empty] | Field 2-7: System And Stage Water Quality For Week 12 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Boca Raton | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 216 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.56 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.56 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.58 | [6 empty] | System recovery during sample collection (decimal) | 85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.62 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500130 | Membrane trade name | ESNA | Temperature normalized MTCW (gfd/psi) | 0.32 | Calcium Hardness (mg/L as CaCO3) | 260 | Dual Media Filtration | Silica/Garnet | Pilot-Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 40 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 22.3 | [6 empty] | System feed flow rate during sample collection (gpm) | 38.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 21.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 37.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 21.7 | [6 empty] | System feed flow rate during sample collection (gpm) | 38 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 23.6 | [6 empty] | System feed flow rate during sample collection (gpm) | 37 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 21.1 | [6 empty] | System feed flow rate during sample collection (gpm) | 37 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 21.1 |  |  |  |  | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Membrane element model number | 4040-UHA-ESNA |  |  | LSI | 0.09 | Scale Inhibitor Addition | Calgon EL-5600 4.0 mg/l | Pilot-Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 40 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 40 | [6 empty] | System influent flow rate during sample collection (gpm) | 38.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 38.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 37.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 37.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 38 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 38 | [6 empty] | System influent flow rate during sample collection (gpm) | 37 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 37 | [6 empty] | System influent flow rate during sample collection (gpm) | 37 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 37 |  |  |  |  | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 100-180 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 1 | pH Adjustment | sulfuric acid to pH 6.0 - 6.4 | Pilot-Scale | 1998-06-01 | 10:40 | 21188 | 25.3 | 162 | 123 | 17.8 | 0 | 31.2 | 5.8 |  | 37 | 37 | 0.84324 | 0 | 12.5849 | 12.4738 | 14.2052 | 110.4948 | 0.11289 | 7.02 | 6.16 | 36 | 404 | 421 | 1781 | 2492.0345 | -39.9233 | 91.4489 | 1456.5172 | 97.5284 | 162 | 140 | 17 | 22.6 | 16.1 | 38.7 | 38.7 | 0.46248 | 0.58398 | 13.6739 | 13.5532 | 6.4841 | 127.5159 | 0.10629 | 6.09 |  | 30 | 411 | 913 | 945.8199 | -3.5947 | 92.8741 | 678.4099 | 95.5779 | 140 | 123 | 19 | 8.5 | 5.8 | 14.3 | 14.3 | 0.33927 | 0.59441 | 10.2857 | 10.1949 | 14.7631 | 97.7369 | 0.10431 |  | 6.7 | 61 | 913 | 1781 | 2161.6207 | -21.3712 | 85.5107 | 1537.3103 | 96.032 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamid | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 1 | Cartridge Filtration | 5 um exclusion size | Pilot-Scale | 1998-06-02 | 8:50 | 21210 | 25.3 | 163 | 124 | 17.9 | 0 | 30.7 | 5.8 | X | 36.5 | 36.5 | 0.8411 | 0 | 12.3832 | 12.2739 | 20.4936 | 105.1064 | 0.11678 | 8.06 | 7.66 | 36 | 497 | 598 | 1823 | 3572.7241 | -95.9805 | 93.9799 | 2085.3621 | 98.2737 | 163 | 141 | 17 | 22.7 | 16.1 | 38.8 | 38.8 | 0.46332 | 0.58505 | 13.7345 | 13.6132 | 6.53 | 128.47 | 0.10596 | 6.09 |  | 30 | 413 | 917 | 953.0062 | -3.9265 | 94.9833 | 683.0031 | 95.6076 | 141 | 124 | 19 | 8 | 5.8 | 13.8 | 13.8 | 0.33083 | 0.57971 | 9.6807 | 9.5952 | 14.4634 | 99.0366 | 0.096886 |  | 7.84 | 61 | 917 | 1823 | 2097.6897 | -15.068 | 89.7993 | 1507.3448 | 95.9531 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 0.01 |  |  |  | 1998-06-04 | 9:40 | 21236 | 25.3 | 154 | 114 | 19.7 | 0 | 34 | 6.3 |  | 40.3 | 40.3 | 0.84367 | 0 | 13.7143 | 13.5932 | 13.5732 | 100.7268 | 0.13495 | 6.93 | 6.08 | 46 | 392 | 413 | 1762 | 2393.6349 | -35.8476 | 88.862 | 1403.3175 | 96.7221 | 154 | 131 | 18 | 24.8 | 16.7 | 41.5 | 41.5 | 0.49117 | 0.59759 | 15.005 | 14.8726 | 6.5519 | 117.9481 | 0.12609 | 6.08 |  | 37 | 413 | 892 | 971.3713 | -8.8981 | 91.0412 | 692.1856 | 94.6546 | 131 | 114 | 21 | 9.1 | 6.3 | 15.4 | 15.4 | 0.36627 | 0.59091 | 11.0118 | 10.9145 | 14.0361 | 87.4639 | 0.12479 |  | 6.66 | 77 | 892 | 1762 | 2069.2222 | -17.436 | 81.3559 | 1480.6111 | 94.7994 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | hydrophylic | Number of elements per pressure vessel, Ne | 7 | Total aluminum (mg/L) | 1 |  |  |  | 1998-06-05 | 9:30 | 21260 | 25.4 | 157 | 116 | 20 | 0 | 35 | 6.1 |  | 41.1 | 41.1 | 0.85158 | 0 | 14.1176 | 13.9517 | 14.0052 | 102.4948 | 0.13612 | 7.03 | 6.21 | 44 | 382 | 406 | 1805 | 2483.0492 | -37.5651 | 89.1626 | 1444.5246 | 96.954 | 157 | 133 | 19 | 25.7 | 15.2 | 40.9 | 40.9 | 0.47345 | 0.62836 | 15.5496 | 15.3668 | 6.9387 | 119.0613 | 0.12907 | 6.07 |  | 36 | 412 | 896 | 1047.7368 | -16.9349 | 91.133 | 729.8684 | 95.0676 | 133 | 116 | 21 | 9.2 | 6.1 | 15.3 | 15.3 | 0.36121 | 0.60131 | 11.1328 | 11.0019 | 14.4187 | 89.0813 | 0.1235 |  | 6.87 | 74 | 896 | 1805 | 2135.7377 | -18.3234 | 81.7734 | 1515.8689 | 95.1183 | Sampling date | MM/DD/YY | 1998-06-10 | 1998-06-10 | 1998-06-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-10 | 1998-06-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-08 | 1998-07-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-08 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | 1998-08-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | 1998-08-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 13
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 4 | Fluoride (mg/L) | 0.231 |  |  |  | 1998-06-06 | 8:45 | 21284 | 25.3 | 157 | 117 | 19.7 | 0 | 34.6 | 6.1 |  | 40.7 | 40.7 | 0.85012 | 0 | 13.9563 | 13.8331 | 13.7715 | 103.5285 | 0.13362 | 6.93 | 6.13 | 43 | 371 | 402 | 1824 | 2438.2951 | -33.6785 | 89.3035 | 1420.1475 | 96.9721 | 157 | 134 | 18 | 25.2 | 15.5 | 40.7 | 40.7 | 0.4743 | 0.61916 | 15.2471 | 15.1125 | 6.889 | 120.611 | 0.1253 | 6.1 |  | 36 | 416 | 908 | 1033.8065 | -13.8553 | 91.0448 | 724.9032 | 95.0338 | 134 | 117 | 21 | 9.4 | 6.1 | 15.5 | 15.5 | 0.36458 | 0.60645 | 11.3748 | 11.2744 | 14.8013 | 89.6987 | 0.12569 |  | 6.62 | 72 | 908 | 1824 | 2196.2623 | -20.4091 | 82.0896 | 1552.1311 | 95.3612 | Sampling time | hh:mm | 7:20 | 7:25 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:30 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:25 | 7:10 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:10 | --- | --- | --- | --- | Sampling time | hh:mm | 8:20 | 8:30 | 8:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:35 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 7:50 | 8:00 | 8:05 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:10 | 7:55 | --- | --- | --- | --- | Sampling time | hh:mm | 9:25 | 9:30 | 9:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:45 | 9:30 | --- | --- | --- | --- | Sampling time | hh:mm | 9:25 | 9:30 | 9:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:45 | 9:30 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881(May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 2 | Phosphate (mg/L) | <0.1 |  |  |  | 1998-06-07 | 8:20 | 21307 | 25.3 | 156 | 117 | 19.6 | 0 | 34.6 | 6.2 |  | 40.8 | 40.8 | 0.84804 | 0 | 13.9563 | 13.8331 | 13.9484 | 102.9516 | 0.13436 | 6.85 | 6.07 | 42 | 392 | 410 | 1799 | 2463.6774 | -36.947 | 89.7561 | 1436.8387 | 97.0769 | 156 | 134 | 18 | 25.8 | 15.1 | 40.9 | 40.9 | 0.47261 | 0.63081 | 15.6101 | 15.4723 | 7.0649 | 119.9351 | 0.12901 | 6.13 |  | 35 | 416 | 903 | 1066.9801 | -18.1595 | 91.4634 | 741.4901 | 95.2798 | 134 | 117 | 21 | 8.8 | 6.2 | 15 | 15 | 0.35783 | 0.58667 | 10.6487 | 10.5547 | 14.2245 | 90.2755 | 0.11692 |  | 6.64 | 71 | 903 | 1799 | 2083.9032 | -15.8368 | 82.6829 | 1493.4516 | 95.2459 | Operation time | hh.hh | 21378 | 21378 | 21378 | --- | --- | --- | --- | --- | Operation time | hh.hh | 21378 | 21378 | --- | --- | --- | --- | Operation time | hh.hh | 21714 | 21714 | 21714 | --- | --- | --- | --- | --- | Operation time | hh.hh | 21714 | 21714 | --- | --- | --- | --- | Operation time | hh.hh | 22051 | 22051 | 22051 | --- | --- | --- | --- | --- | Operation time | hh.hh | 22051 | 22051 | --- | --- | --- | --- | Operation time | hh.hh | 22386 | 22386 | 22386 | --- | --- | --- | --- | --- | Operation time | hh.hh | 22386 | 22386 | --- | --- | --- | --- | Operation time | hh.hh | 22723 | 22723 | 22723 | --- | --- | --- | --- | --- | Operation time | hh.hh | 22723 | 22723 | --- | --- | --- | --- | Operation time | hh.hh | 22723 | 22723 | 22723 | --- | --- | --- | --- | --- | Operation time | hh.hh | 22723 | 22723 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.88542 | Sulfate (mg/L) | 17.1 |  |  |  | 1998-06-08 | 9:40 | 21332 | 25.3 | 156 | 116 | 19.2 | 0 | 32.3 | 6.3 |  | 38.6 | 38.6 | 0.83679 | 0 | 13.0286 | 12.9135 | 12.9355 | 103.8645 | 0.12433 | 6.98 | 6.15 | 42 | 383 | 405 | 1767 | 2266.0952 | -28.2453 | 89.6296 | 1335.5476 | 96.8552 | 156 | 133 | 18 | 23.3 | 17.3 | 40.6 | 40.6 | 0.48864 | 0.57389 | 14.0975 | 13.973 | 6.359 | 120.141 | 0.11631 | 6.13 |  | 35 | 415 | 900 | 926.7919 | -2.9769 | 91.358 | 670.896 | 94.7831 | 133 | 116 | 20 | 9 | 6.3 | 15.3 | 15.3 | 0.36458 | 0.58824 | 10.8908 | 10.7946 | 14.2286 | 90.2714 | 0.11958 |  | 6.68 | 70 | 900 | 1767 | 2085.7143 | -18.037 | 82.716 | 1492.8571 | 95.311 | pH | --- | 5.39 | 6.14 | 6.62 | --- | --- | --- | --- | --- | pH | --- | 5.45 | 6.08 | --- | --- | --- | --- | pH | --- | 5.52 | 6.24 | 6.86 | --- | --- | --- | --- | --- | pH | --- | 5.28 | 6.23 | --- | --- | --- | --- | pH | --- | 5.39 | 6.19 | 6.86 | --- | --- | --- | --- | --- | pH | --- | 5.36 | 6.4 | --- | --- | --- | --- | pH | --- | 5.6 | 6.39 | 6.79 | --- | --- | --- | --- | --- | pH | --- | 5.46 | 6.18 | --- | --- | --- | --- | pH | --- | 5.27 | 6.02 | 6.57 | --- | --- | --- | --- | --- | pH | --- | 5.28 | 6.01 | --- | --- | --- | --- | pH | --- | 5.33 | 6.02 | 6.56 | --- | --- | --- | --- | --- | pH | --- | 5.34 | 6.02 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 17
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 6.1979 | Calcium (mg/L) | 97.9 |  |  |  | 1998-06-09 | 9:45 | 21356 | 25.3 | 157 | 118 | 19.5 | 0 | 30.9 | 6 |  | 36.9 | 36.9 | 0.8374 | 0 | 12.4639 | 12.3538 | 13.728 | 104.272 | 0.11848 | 6.88 | 5.86 | 43 | 405 | 427 | 1816 | 2404.6 | -32.4119 | 89.9297 | 1415.8 | 96.9628 | 157 | 135 | 18 | 23.3 | 16.7 | 40 | 40 | 0.47852 | 0.5825 | 14.0975 | 13.973 | 6.5358 | 121.4642 | 0.11504 | 5.9 |  | 35 | 420 | 907 | 957.1557 | -5.5298 | 91.8033 | 688.5778 | 94.9171 | 135 | 118 | 21 | 8.8 | 6 | 14.8 | 14.8 | 0.35108 | 0.59459 | 10.6487 | 10.5547 | 14.4907 | 91.0093 | 0.11597 |  | 6.38 | 71 | 907 | 1816 | 2133.1333 | -17.4633 | 83.3724 | 1520.0667 | 95.3292 | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.3 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 27 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 27 | 26 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 24.7917 | Barium (mg/L) | 0.5 |  |  |  | 1998-06-10 | 9:05 | 21380 | 25.3 | 158 | 119 | 19.4 | 0 | 31.1 | 6 |  | 37.1 | 37.1 | 0.83827 | 0 | 12.5445 | 12.4338 | 13.7202 | 105.3798 | 0.11799 | 6.8 | 5.82 | 43 | 403 | 425 | 1831 | 2405.0333 | -31.3508 | 89.8824 | 1415.0167 | 96.9612 | 158 | 135 | 18 | 22.3 | 17.6 | 39.9 | 39.9 | 0.48527 | 0.5589 | 13.4924 | 13.3733 | 6.2891 | 122.2109 | 0.10943 | 5.9 |  | 35 | 420 | 910 | 907.8125 | 0.24038 | 91.7647 | 663.9062 | 94.7282 | 135 | 119 | 21 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 10.4348 | 14.4727 | 91.5272 | 0.11401 |  | 6.38 | 71 | 910 | 1831 | 2126.55 | -16.1415 | 83.2941 | 1518.275 | 95.3236 | Alkalinity | mg/L as CaCO3 | 16 | 80 | 370 | 416 | -12.4324 | 80 | 248 | 93.5484 | Alkalinity | mg/L as CaCO3 | 14 | 100 | 208.3503 | 82.5 | 154.1751 | 90.9194 | Alkalinity | mg/L as CaCO3 | 16 | 110 | 500 | 603.5 | -20.7 | 85.4545 | 356.75 | 95.5151 | Alkalinity | mg/L as CaCO3 | 14 | 100 | 210.2824 | 87.2727 | 155.1412 | 90.976 | Alkalinity | mg/L as CaCO3 | 14 | 86 | 424 | 464 | -9.434 | 83.7209 | 275 | 94.9091 | Alkalinity | mg/L as CaCO3 | 14 | 86 | 184.2642 | 83.7209 | 135.1321 | 89.6398 | Alkalinity | mg/L as CaCO3 | 16 | 82 | 394 | 15.2143 | 96.1385 | 80.4878 | 48.6071 | 67.083 | Alkalinity | mg/L as CaCO3 | 12 | 100 | 244.2222 | 85.3659 | 172.1111 | 93.0278 | Alkalinity | mg/L as CaCO3 | 15 | 70 | 335 | 381.6667 | -13.9303 | 78.5714 | 225.8333 | 93.3579 | Alkalinity | mg/L as CaCO3 | 14 | 80 | 167.5849 | 80 | 123.7925 | 88.6907 | Alkalinity | mg/L as CaCO3 | 14 | 75 | 330 | 420.6667 | -27.4747 | 81.3333 | 247.8333 | 94.351 | Alkalinity | mg/L as CaCO3 | 14 | 80 | 167.5849 | 81.3333 | 123.7925 | 88.6907 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.3958 | Strontium (mg/L) | 0.2 |  |  |  | 1998-06-11 | 10:20 | 21405 | 25.3 | 158 | 118 | 19.3 | 0 | 32.4 | 6.1 |  | 38.5 | 38.5 | 0.84156 | 0 | 13.0689 | 12.9535 | 13.8552 | 104.8448 | 0.12355 | 6.92 | 5.91 | 43 | 400 | 422 | 1784 | 2435.0492 | -36.4938 | 89.8104 | 1428.5246 | 96.9899 | 158 | 135 | 18 | 23.1 | 17.1 | 40.2 | 40.2 | 0.48358 | 0.57463 | 13.9765 | 13.8531 | 6.4504 | 122.0496 | 0.1135 | 5.81 |  | 36 | 421 | 903 | 941.0877 | -4.2179 | 91.4692 | 681.0439 | 94.714 | 135 | 118 | 21 | 9.2 | 6.1 | 15.3 | 15.3 | 0.36121 | 0.60131 | 11.1328 | 11.0345 | 14.6116 | 90.8884 | 0.12141 |  | 6.42 | 70 | 903 | 1784 | 2159.3279 | -21.0386 | 83.4123 | 1531.1639 | 95.4283 | Total dissolved solids | mg/L | 43.6 | 427 | 1835 | 2439.85 | -32.9619 | 89.7892 | 1433.425 | 96.9583 | Total dissolved solids | mg/L | 33.3 | 429 | 927.5373 | 92.2014 | 678.2686 | 95.0904 | Total dissolved solids | mg/L | 33 | 345 | 1700 | 1983 | -16.6471 | 90.4348 | 1164 | 97.1649 | Total dissolved solids | mg/L | 26 | 393 | 863.6235 | 92.4638 | 628.3118 | 95.8619 | Total dissolved solids | mg/L | 40.6 | 414 | 1600 | 2374.35 | -48.3969 | 90.1932 | 1394.175 | 97.0879 | Total dissolved solids | mg/L | 31 | 417 | 943.805 | 92.5121 | 680.4025 | 95.4439 | Total dissolved solids | mg/L | 37 | 418 | 1590 | 32.4643 | 97.9582 | 91.1483 | 225.2321 | 83.5725 | Total dissolved solids | mg/L | 29.2 | 420 | 1060.4778 | 93.0144 | 740.2389 | 96.0553 | Total dissolved solids | mg/L | 33 | 366 | 1465 | 2253 | -53.7884 | 90.9836 | 1309.5 | 97.48 | Total dissolved solids | mg/L | 25 | 368 | 823.1761 | 93.1694 | 595.5881 | 95.8025 | Total dissolved solids | mg/L | 33 | 368 | 1464 | 2266.3333 | -54.8042 | 91.0326 | 1317.1667 | 97.4946 | Total dissolved solids | mg/L | 26 | 369 | 824.1761 | 92.9348 | 596.5881 | 95.6419 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 71 | Permeate flow rate from system, Qp-sys (gpm) | 37.1875 | Reactive silica (mg/L as SiO2) | 78 |  |  |  | 1998-06-12 | 9:15 | 21428 | 25.3 | 157 | 118 | 18.9 | 0 | 32.9 | 6 |  | 38.9 | 38.9 | 0.84576 | 0 | 13.2706 | 13.1534 | 14.4054 | 104.1946 | 0.12624 | 6.93 | 5.91 | 43 | 401 | 428 | 1808 | 2539.0833 | -40.436 | 89.9533 | 1483.5417 | 97.1015 | 157 | 135 | 17 | 23.9 | 16.3 | 40.2 | 40.2 | 0.47683 | 0.59453 | 14.4605 | 14.3328 | 6.7072 | 122.2928 | 0.1172 | 5.89 |  | 35 | 422 | 913 | 989.4417 | -8.3726 | 91.8224 | 705.7209 | 95.0405 | 135 | 118 | 20 | 8.9 | 6 | 14.9 | 14.9 | 0.35277 | 0.59732 | 10.7697 | 10.6747 | 14.6822 | 91.8178 | 0.11626 |  | 6.42 | 70 | 913 | 1808 | 2163.45 | -19.6598 | 83.6449 | 1538.225 | 95.4493 | Total hardness | mg/L as CaCO3 | 18 | 260 | 1380 | 1530.5 | -10.9058 | 93.0769 | 895.25 | 97.9894 | Total hardness | mg/L as CaCO3 | 14 | 300 | 660.3277 | 94.6154 | 480.1638 | 97.0843 | Total hardness | mg/L as CaCO3 | 14 | 280 | 1415 | 1676.5 | -18.4806 | 95 | 978.25 | 98.5689 | Total hardness | mg/L as CaCO3 | 14 | 260 | 575.4588 | 95 | 417.7294 | 96.6485 | Total hardness | mg/L as CaCO3 | 18 | 256 | 1560 | 1505.5 | 3.4936 | 92.9688 | 880.75 | 97.9563 | Total hardness | mg/L as CaCO3 | 14 | 270 | 619.3836 | 94.5312 | 444.6918 | 96.8518 | Total hardness | mg/L as CaCO3 | 14 | 252 | 1420 | 11.1667 | 99.2136 | 94.4444 | 131.5833 | 89.3604 | Total hardness | mg/L as CaCO3 | 14 | 268 | 684.2778 | 94.4444 | 476.1389 | 97.0597 | Total hardness | mg/L as CaCO3 | 17 | 260 | 1370 | 1637 | -19.4891 | 93.4615 | 948.5 | 98.2077 | Total hardness | mg/L as CaCO3 | 11 | 250 | 567.1635 | 95.7692 | 408.5818 | 97.3078 | Total hardness | mg/L as CaCO3 | 16 | 255 | 1350 | 1609.3333 | -19.2099 | 93.7255 | 932.1667 | 98.2836 | Total hardness | mg/L as CaCO3 | 10 | 260 | 591.761 | 96.0784 | 425.8805 | 97.6519 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | Feed flow rate to system, QF-sys (gpm) | 43.75 | Turbidity (ntu) | 0.95 |  |  |  | 1998-06-13 | 9:09 | 21452 | 25.4 | 158 | 119 | 19.2 | 0 | 34.2 | 6.1 |  | 40.3 | 40.3 | 0.84864 | 0 | 13.795 | 13.6328 | 15.061 | 104.239 | 0.13078 | 6.81 | 5.83 | 42 | 399 | 438 | 1805 | 2658.1967 | -47.2685 | 90.411 | 1548.0984 | 97.287 | 158 | 136 | 18 | 25.5 | 14.4 | 39.9 | 39.9 | 0.45826 | 0.6391 | 15.4286 | 15.2472 | 7.2777 | 121.7223 | 0.12526 | 5.9 |  | 35 | 421 | 906 | 1104.5417 | -21.9141 | 92.0091 | 762.7708 | 95.4115 | 136 | 119 | 21 | 8.6 | 6.1 | 14.7 | 14.7 | 0.35108 | 0.58503 | 10.4067 | 10.2844 | 14.2702 | 92.2298 | 0.11151 |  | 6.31 | 69 | 906 | 1805 | 2086.0328 | -15.5697 | 84.2466 | 1496.0164 | 95.3878 | Calcium hardness | mg/L as CaCO3 | 16 | 244 | 1300 | 1441 | -10.8462 | 93.4426 | 842.5 | 98.1009 | Calcium hardness | mg/L as CaCO3 | 12 | 260 | 572.452 | 95.082 | 416.226 | 97.117 | Calcium hardness | mg/L as CaCO3 | 12 | 250 | 1360 | 1499.5 | -10.2574 | 95.2 | 874.75 | 98.6282 | Calcium hardness | mg/L as CaCO3 | 10 | 230 | 512.1176 | 96 | 371.0588 | 97.305 | Calcium hardness | mg/L as CaCO3 | 14 | 230 | 1360 | 1364 | -0.29412 | 93.913 | 797 | 98.2434 | Calcium hardness | mg/L as CaCO3 | 8 | 240 | 556.6289 | 96.5217 | 398.3145 | 97.9915 | Calcium hardness | mg/L as CaCO3 | 8 | 230 | 1180 | 5.3571 | 99.546 | 96.5217 | 117.6786 | 93.2018 | Calcium hardness | mg/L as CaCO3 | 8 | 234 | 604.3889 | 96.5217 | 419.1944 | 98.0916 | Calcium hardness | mg/L as CaCO3 | 14 | 230 | 1260 | 1454 | -15.3968 | 93.913 | 842 | 98.3373 | Calcium hardness | mg/L as CaCO3 | 10 | 240 | 545.2201 | 95.6522 | 392.6101 | 97.4529 | Calcium hardness | mg/L as CaCO3 | 12 | 230 | 1260 | 1465.3333 | -16.2963 | 94.7826 | 847.6667 | 98.5843 | Calcium hardness | mg/L as CaCO3 | 10 | 250 | 568.4906 | 95.6522 | 409.2453 | 97.5565 | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 6.5625 | SDI | 4 |  |  |  | 1998-06-14 | 9:30 | 21476 | 25.4 | 157 | 118 | 18.9 | 0 | 34.2 | 6.1 |  | 40.3 | 40.3 | 0.84864 | 0 | 13.795 | 13.6328 | 13.4636 | 105.1364 | 0.12967 | 6.91 | 5.92 | 42 | 351 | 396 | 1727 | 2380.7213 | -37.853 | 89.3939 | 1388.3607 | 96.9748 | 157 | 135 | 18 | 25.3 | 14.8 | 40.1 | 40.1 | 0.46332 | 0.63092 | 15.3076 | 15.1276 | 6.7141 | 121.2859 | 0.12473 | 5.92 |  | 34 | 396 | 876 | 1014.8243 | -15.8475 | 91.4141 | 705.4122 | 95.1801 | 135 | 118 | 20 | 8.8 | 6.1 | 14.9 | 14.9 | 0.35446 | 0.5906 | 10.6487 | 10.5236 | 13.9254 | 92.5746 | 0.11368 |  | 6.4 | 67 | 876 | 1727 | 2043.082 | -18.3024 | 83.0808 | 1459.541 | 95.4095 | Turbidity | ntu | 0.045 | 1.62 | 3.34 | 9.8887 | -196.0704 | 97.2222 | 5.7544 | 99.218 | Turbidity | ntu | 0.044 | 1.9 | 4.2384 | 97.284 | 3.0692 | 98.5664 | Turbidity | ntu | 0.034 | 0.153 | 1.63 | 0.77775 | 52.2853 | 77.7778 | 0.46537 | 92.6941 | Turbidity | ntu | 0.045 | 0.205 | 0.41018 | 70.5882 | 0.30759 | 85.3701 | Turbidity | ntu | 0.081 | 0.144 | 2.29 | 0.47475 | 79.2686 | 43.75 | 0.30938 | 73.8182 | Turbidity | ntu | 0.039 | 0.138 | 0.27311 | 72.9167 | 0.20556 | 81.0271 | Turbidity | ntu | 0.064 | 0.15 | 1.99 | 0.062976 | 96.8354 | 57.3333 | 0.10649 | 39.8994 | Turbidity | ntu | 0.053 | 0.146 | 0.29842 | 64.6667 | 0.22221 | 76.1485 | Turbidity | ntu | 0.06 | 0.11 | 0.706 | 0.39333 | 44.2871 | 45.4545 | 0.25167 | 76.1589 | Turbidity | ntu | 0.057 | 0.152 | 0.27807 | 48.1818 | 0.21503 | 73.4926 | Turbidity | ntu | 0.052 | 0.115 | 0.889 | 0.472 | 46.9066 | 54.7826 | 0.2935 | 82.2828 | Turbidity | ntu | 0.068 | 0.167 | 0.29838 | 40.8696 | 0.23269 | 70.7764 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI |  |  |  |  | 1998-06-15 | 10:50 | 21501 | 25.5 | 158 | 119 | 19 | 0 | 31.9 | 5.9 |  | 37.8 | 37.8 | 0.84392 | 0 | 12.8672 | 12.6785 | 16.7023 | 102.7977 | 0.12333 | 6.99 | 5.91 | 42 | 466 | 493 | 1755 | 2931.4576 | -67.0346 | 91.4807 | 1712.2288 | 97.5471 | 158 | 135 | 18 | 22.8 | 16.7 | 39.5 | 39.5 | 0.4743 | 0.57722 | 13.795 | 13.5926 | 6.3099 | 122.1901 | 0.11124 | 5.88 |  | 33 | 408 | 884 | 919.976 | -4.0697 | 93.3063 | 663.988 | 95.03 | 135 | 119 | 20 | 9 | 5.9 | 14.9 | 14.9 | 0.35108 | 0.60403 | 10.8908 | 10.731 | 14.4014 | 92.5986 | 0.11589 |  | 6.41 | 67 | 884 | 1755 | 2130.2712 | -21.383 | 86.4097 | 1507.1356 | 95.5545 | Ammonia | mg NH3-N / L | 0.16 | 0.5 | 2.23 | 2.285 | -2.4664 | 68 | 1.3925 | 88.5099 | Total organic carbon | mg/L | 0.64 | 12.6 | 27.6682 | 94.8387 | 20.1341 | 96.8213 | Ammonia | mg NH3-N / L | 0.17 | 0.51 | 2.31 | 2.295 | 0.64935 | 66.6667 | 1.4025 | 87.8788 | Total organic carbon | mg/L | BMRL | 12.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.17 | 0.56 | 2.32 | 2.6075 | -12.3922 | 69.6429 | 1.5837 | 89.266 | Total organic carbon | mg/L | 0.71 | 13.5 | 30.9555 | 94.7407 | 22.2278 | 96.8058 | Ammonia | mg NH3-N / L | 0.15 | 0.47 | 1.87 | 0.14619 | 92.1823 | 68.0851 | 0.3081 | 51.3138 | Total organic carbon | mg/L | 1.33 | 13.6 | 33.7092 | 90.6993 | 23.6546 | 94.3774 | Ammonia | mg NH3-N / L | 0.2 | 0.62 | 2.76 | 3 | -8.6957 | 67.7419 | 1.81 | 88.9503 | Total organic carbon | mg/L | 0.51 | 16.1 | 36.7886 | 96.383 | 26.4443 | 98.0714 | Ammonia | mg NH3-N / L | 0.22 | 0.68 | 2.69 | 3.2867 | -22.1809 | 67.6471 | 1.9833 | 88.9076 | Total organic carbon | mg/L | 0.91 | 12.8 | 28.5786 | 92.9457 | 20.6893 | 95.6016
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-06-16 | 9:20 | 21524 | 25.4 | 157 | 119 | 18.9 | 0 | 31.8 | 5.9 |  | 37.7 | 37.7 | 0.8435 | 0 | 12.8269 | 12.6761 | 15.0383 | 104.0617 | 0.12181 | 6.88 | 5.82 | 42 | 425 | 449 | 1794 | 2642.661 | -47.3055 | 90.6459 | 1545.8305 | 97.283 | 157 | 135 | 18 | 22.7 | 16.6 | 39.3 | 39.3 | 0.47176 | 0.57761 | 13.7345 | 13.573 | 6.4319 | 121.5681 | 0.11165 | 5.88 |  | 35 | 417 | 896 | 939.3735 | -4.8408 | 92.2049 | 678.1867 | 94.8392 | 135 | 119 | 20 | 9 | 5.9 | 14.9 | 14.9 | 0.35108 | 0.60403 | 10.8908 | 10.7627 | 14.5953 | 92.4047 | 0.11647 |  | 6.36 | 68 | 896 | 1794 | 2159.0508 | -20.3484 | 84.8552 | 1527.5254 | 95.5484 | Total organic carbon | mg/L | BMRL | 12.4 | 76.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.377 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.8 | 76.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.418 | 0.94248 | 97.9452 | 0.68024 | 98.6769 | Total organic carbon | mg/L | 0.52 | 13.5 | 79.1 | 81.645 | -3.2174 | 96.1481 | 47.5725 | 98.9069 | UV254 | cm-1 | 0.012 | 0.435 | 1.0123 | 97.0443 | 0.72365 | 98.3417 | Total organic carbon | mg/L | 1.22 | 14.3 | 74.3 | 1.0643 | 98.5676 | 91.4685 | 7.6821 | 84.119 | UV254 | cm-1 | BMRL | 0.415 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.51 | 14.1 | 79.7 | 91.11 | -14.3162 | 96.383 | 52.605 | 99.0305 | UV254 | cm-1 | BMRL | 0.458 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.9 | 80.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.466 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Glades Road Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 15 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 22.5 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-06-17 | 10:05 | 21549 | 25.4 | 157 | 119 | 18.8 | 0 | 30.7 | 6 |  | 36.7 | 36.7 | 0.83651 | 0 | 12.3832 | 12.2376 | 14.3401 | 104.8599 | 0.1167 | 6.81 | 5.74 | 42 | 427 | 445 | 1773 | 2507.0167 | -41.3997 | 90.5618 | 1476.0083 | 97.1545 | 157 | 135 | 18 | 21.8 | 17.6 | 39.4 | 39.4 | 0.48105 | 0.5533 | 13.1899 | 13.0349 | 6.1858 | 121.8142 | 0.10701 | 5.88 |  | 35 | 417 | 896 | 890.1591 | 0.65189 | 92.1348 | 653.5795 | 94.6449 | 135 | 119 | 20 | 8.8 | 6 | 14.8 | 14.8 | 0.35108 | 0.59459 | 10.6487 | 10.5236 | 14.3693 | 92.6307 | 0.11361 |  | 6.32 | 67 | 896 | 1773 | 2111.8667 | -19.1126 | 84.9438 | 1503.9333 | 95.545 | UV254 | cm-1 | BMRL | 0.395 | 2.274 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.9921 | --- | --- | --- | --- | UV254 | cm-1 | 0.009 | 0.438 | 2.628 | 2.6902 | -2.3687 | 97.9452 | 1.5641 | 99.4246 | SUVA | L/(mg*m) | NR | 3.2913 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.406 | 2.592 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.6901 | 3.2222 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.408 | 2.427 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.0515 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.463 | 2.599 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 2.8447 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.464 | 2.632 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6406 | --- | --- | --- | ---
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0022 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 8.3333 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-06-18 | 10:15 | 21573 | 25.3 | 157 | 118 | 18.7 | 0 | 33 | 6.1 |  | 39.1 | 39.1 | 0.84399 | 0 | 13.3109 | 13.1934 | 16.6351 | 102.1649 | 0.12914 | 6.92 | 6.14 | 39 | 464 | 488 | 1763 | 2917.0164 | -65.4575 | 92.0082 | 1702.5082 | 97.7093 | 157 | 135 | 17 | 24.1 | 15.5 | 39.6 | 39.6 | 0.46501 | 0.60859 | 14.5815 | 14.4528 | 6.8075 | 122.1925 | 0.11828 | 6.16 |  | 32 | 415 | 892 | 1010.5032 | -13.2851 | 93.4426 | 712.7516 | 95.5104 | 135 | 118 | 20 | 8.8 | 6.1 | 14.9 | 14.9 | 0.35446 | 0.5906 | 10.6487 | 10.5547 | 14.2352 | 92.2648 | 0.1144 |  | 6.68 | 65 | 892 | 1763 | 2085.0492 | -18.2671 | 86.6803 | 1488.5246 | 95.6333 | SUVA | L/(mg*m) | NR | 3.1855 | 2.9882 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.4219 | 3.4174 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.0074 | 3.2769 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 2.8531 | 3.2665 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.2837 | 3.261 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5969 | 3.2534 | --- | --- | --- | --- | ---
Process Train Name | SOFT | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1998-06-19 | 9:15 | 21596 | 25.4 | 158 | 120 | 19.3 | 0 | 33 | 5.8 |  | 38.8 | 38.8 | 0.85052 | 0 | 13.3109 | 13.1545 | 16.2636 | 103.4364 | 0.12717 | 6.91 | 6.03 | 40 | 447 | 463 | 1841 | 2869.7241 | -55.8786 | 91.3607 | 1666.3621 | 97.5996 | 158 | 136 | 17 | 24.3 | 14.7 | 39 | 39 | 0.4532 | 0.62308 | 14.7025 | 14.5297 | 6.9408 | 123.0592 | 0.11807 | 6.11 |  | 33 | 413 | 906 | 1041.1633 | -14.9187 | 92.8726 | 727.0816 | 95.4613 | 136 | 120 | 21 | 8.6 | 5.8 | 14.4 | 14.4 | 0.34095 | 0.59722 | 10.4067 | 10.2844 | 14.6102 | 92.3898 | 0.11132 |  | 6.54 | 67 | 906 | 1841 | 2150.0345 | -16.7862 | 85.5292 | 1528.0172 | 95.6152 | Bromide | mg/L | 31.6 | 172 | --- | 909.1 | --- | 81.6279 | 540.55 | 94.1541 | [8 empty] | Bromide | mg/L | 29.6 | 184 | --- | 994.6 | --- | 83.913 | 589.3 | 94.9771 | [8 empty] | Bromide | mg/L | 30.3 | 185 | --- | 997.175 | --- | 83.6216 | 591.0875 | 94.8739 | [8 empty] | Bromide | mg/L | 43.7 | 176 | --- | 42.125 | --- | 75.1705 | 109.0625 | 59.9312 | [8 empty] | Bromide | mg/L | 28.9 | 199 | --- | 1162.9 | --- | 85.4774 | 680.95 | 95.7559 | [8 empty] | Bromide | mg/L | 27.2 | 193 | --- | 1132.5333 | --- | 85.9067 | 662.7667 | 95.896
ICR Treatment Plant Identification Number | 306 | Purchase price for an equivalent 8" x 40 " element ($) | $895/quantity discount | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-06-20 | 8:52 | 21620 | 25.4 | 158 | 120 | 19.3 | 0 | 32.3 | 5.9 |  | 38.2 | 38.2 | 0.84555 | 0 | 13.0286 | 12.8754 | 15.5845 | 104.1155 | 0.12366 | 6.91 | 6.08 | 39 | 436 | 456 | 1809 | 2738.8983 | -51.404 | 91.4474 | 1597.4492 | 97.5586 | 158 | 136 | 17 | 23.7 | 15.5 | 39.2 | 39.2 | 0.46164 | 0.60459 | 14.3395 | 14.171 | 6.6699 | 123.3301 | 0.1149 | 6.11 |  | 33 | 411 | 900 | 988.9742 | -9.886 | 92.7632 | 699.9871 | 95.2856 | 136 | 120 | 21 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.1648 | 14.3476 | 92.6524 | 0.10971 |  | 6.58 | 66 | 900 | 1809 | 2101.5254 | -16.1706 | 85.5263 | 1500.7627 | 95.6022 | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4 | 23 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4 | 23 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4500130 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -10.5 | [5 empty] | 1998-06-21 | 8:10 | 21643 | 25.4 | 157 | 119 | 18.9 | 0 | 32.7 | 5.9 |  | 38.6 | 38.6 | 0.84715 | 0 | 13.1899 | 13.0349 | 15.7636 | 103.3364 | 0.12614 | 6.85 | 5.98 | 39 | 432 | 457 | 1792 | 2773.7119 | -54.783 | 91.4661 | 1615.3559 | 97.5857 | 157 | 135 | 17 | 24.2 | 15.4 | 39.6 | 39.6 | 0.46417 | 0.61111 | 14.642 | 14.4699 | 6.8214 | 122.1786 | 0.11843 | 6.13 |  | 33 | 415 | 903 | 1015.2857 | -12.4347 | 92.779 | 715.1429 | 95.3855 | 135 | 119 | 21 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.1648 | 14.382 | 91.618 | 0.11095 |  | 6.53 | 67 | 903 | 1792 | 2107.4068 | -17.6008 | 85.3392 | 1505.2034 | 95.5488 | SDS-Free Cl2 residual | mg/L | 0.4 | 0.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.4 | 0.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.4 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.6 | 1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.58 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -2.3333 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-06-22 | 9:40 | 21668 | 25.4 | 158 | 120 | 19.1 | 0 | 30.1 | 5.9 |  | 36 | 36 | 0.83611 | 0 | 12.1412 | 11.9985 | 14.8781 | 105.0219 | 0.11425 | 6.83 | 6.04 | 39 | 444 | 458 | 1809 | 2595.6102 | -43.4831 | 91.4847 | 1526.8051 | 97.4456 | 158 | 136 | 17 | 21.4 | 17.5 | 38.9 | 38.9 | 0.47598 | 0.55013 | 12.9479 | 12.7957 | 6.1557 | 123.8443 | 0.10332 | 6.13 |  | 33 | 415 | 903 | 882.1314 | 2.311 | 92.7948 | 648.5657 | 94.9118 | 136 | 120 | 21 | 8.7 | 5.9 | 14.6 | 14.6 | 0.34602 | 0.59589 | 10.5277 | 10.404 | 14.5237 | 92.4763 | 0.1125 |  | 6.58 | 67 | 903 | 1809 | 2135.7458 | -18.0622 | 85.3712 | 1519.3729 | 95.5903 | SDS-Cl2 demand | mg/L | 2.6 | 20.1 | --- | 111.975 | --- | 87.0647 | 66.0375 | 96.0628 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.7 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.6 | 20.5 | --- | 114.475 | --- | 87.3171 | 67.4875 | 96.1474 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.44 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.6 | 20.2 | --- | 112.6 | --- | 87.1287 | 66.4 | 96.0843 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.13 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.4 | 20 | --- | 2.1905 | --- | 88 | 11.0952 | 78.3691 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.33 |  |  |  |  | SDS-Cl2 demand | mg/L | 3 | 22.2 | --- | 131 | --- | 86.4865 | 76.6 | 96.0836 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.52 |  |  |  |  | SDS-Cl2 demand | mg/L | 3 | 22.2 | --- | 131 | --- | 86.4865 | 76.6 | 96.0836 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.52
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | not specified | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-06-23 | 8:45 | 21691 | 25.3 | 158 | 119 | 18.8 | 0 | 31.3 | 6 |  | 37.3 | 37.3 | 0.83914 | 0 | 12.6252 | 12.5137 | 14.3251 | 105.3749 | 0.11875 | 6.88 | 6.06 | 39 | 418 | 436 | 1792 | 2507.0167 | -39.9005 | 91.055 | 1471.5083 | 97.3497 | 158 | 136 | 17 | 22.9 | 16 | 38.9 | 38.9 | 0.46332 | 0.58869 | 13.8555 | 13.7331 | 6.5537 | 123.4463 | 0.11125 | 6.13 |  | 33 | 415 | 903 | 961.7375 | -6.5047 | 92.4312 | 688.3687 | 95.2061 | 136 | 119 | 20 | 8.3 | 6 | 14.3 | 14.3 | 0.34264 | 0.58042 | 10.0437 | 9.955 | 14.1593 | 93.3407 | 0.10665 |  | 6.59 | 66 | 903 | 1792 | 2060.85 | -15.0028 | 84.8624 | 1481.925 | 95.5463 | SDS-Chlorination temp. | oC | 21 | 21 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 17.7 |  |  |  |  | SDS-Chlorination temp. | oC | 21 | 21 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 17 |  |  |  |  | SDS-Chlorination temp. | oC | 21 | 21 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.9 |  |  |  |  | SDS-Chlorination temp. | oC | 22 | 22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 14.4 |  |  |  |  | SDS-Chlorination temp. | oC | 22.2 | 22.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.9 |  |  |  |  | SDS-Chlorination temp. | oC | 22.2 | 22.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.9
State Approved Plant Capacity (MGD) | 70 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-06-24 | 8:30 | 21715 | 25.4 | 158 | 120 | 19 | 0 | 30.3 | 5.8 |  | 36.1 | 36.1 | 0.83934 | 0 | 12.2218 | 12.0782 | 13.2924 | 106.7076 | 0.11319 | 6.75 | 5.93 | 40 | 399 | 408 | 1818 | 2330.4828 | -28.1894 | 90.1961 | 1369.2414 | 97.0787 | 158 | 136 | 17 | 21.8 | 17 | 38.8 | 38.8 | 0.47092 | 0.56186 | 13.1899 | 13.0349 | 6.2529 | 123.7471 | 0.10533 | 6.13 |  | 33 | 414 | 908 | 902.5765 | 0.59731 | 91.9118 | 658.2882 | 94.987 | 136 | 120 | 21 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 10.0452 | 14.5 | 92.5 | 0.1086 |  | 6.57 | 67 | 908 | 1818 | 2126 | -16.9417 | 83.5784 | 1517 | 95.5834 | SDS-Chlorination pH | --- | 8.4 | 8.4 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.26 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.2 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.3 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 21 | [7 empty] | 1998-06-25 | 11:30 | 21741 | 25.4 | 157 | 117 | 19 | 0 | 33.3 | 5.8 |  | 39.1 | 39.1 | 0.85166 | 0 | 13.4319 | 13.2741 | 14.3216 | 103.6784 | 0.12803 | 6.9 | 6.15 | 39 | 396 | 409 | 1774 | 2533.3103 | -42.8022 | 90.4645 | 1471.1552 | 97.349 | 157 | 136 | 17 | 24.5 | 14.2 | 38.7 | 38.7 | 0.44645 | 0.63307 | 14.8235 | 14.6493 | 7.0409 | 122.4591 | 0.11963 | 6.11 |  | 33 | 411 | 900 | 1063.1831 | -18.1315 | 91.9315 | 737.0915 | 95.5229 | 136 | 117 | 21 | 8.7 | 5.8 | 14.5 | 14.5 | 0.34264 | 0.6 | 10.5277 | 10.404 | 14.5775 | 90.9225 | 0.11443 |  | 6.81 | 67 | 900 | 1774 | 2149.5 | -21.1669 | 83.6186 | 1524.75 | 95.6058 | SDS-Incubation time | hours | 40 | 40 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | not specified | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-06-26 | 10:45 | 21765 | 25.4 | 156 | 118 | 18.3 | 0 | 30.1 | 5.9 |  | 36 | 36 | 0.83611 | 0 | 12.1412 | 11.9985 | 13.2092 | 105.4908 | 0.11374 | 7.12 | 6.08 | 40 | 389 | 412 | 1768 | 2309.8305 | -30.6465 | 90.2913 | 1360.9153 | 97.0608 | 156 | 135 | 17 | 21.6 | 16.9 | 38.5 | 38.5 | 0.46754 | 0.56104 | 13.0689 | 12.9153 | 6.1792 | 122.3208 | 0.10559 | 6.08 |  | 33 | 410 | 892 | 891.8462 | 0.017247 | 91.9903 | 650.9231 | 94.9303 | 135 | 118 | 20 | 8.4 | 5.9 | 14.3 | 14.3 | 0.34095 | 0.58741 | 10.1647 | 10.0452 | 14.14 | 92.36 | 0.10876 |  | 6.68 | 66 | 892 | 1768 | 2068 | -16.9683 | 83.9806 | 1480 | 95.5405 | SDS-TOX | mg Cl- /L | BMRL | 1440 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1565 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1355 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1530 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1715 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1735 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 percent | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 20.25 | [5 empty] | 1998-06-27 | 11:30 | 21790 | 25.5 | 157 | 119 | 18.5 | 0 | 32 | 5.7 |  | 37.7 | 37.7 | 0.84881 | 0 | 12.9076 | 12.7182 | 13.6291 | 105.8709 | 0.12013 | 7.17 | 6.19 | 40 | 341 | 398 | 1734 | 2407.8246 | -38.8595 | 89.9497 | 1402.9123 | 97.1488 | 157 | 135 | 17 | 23.5 | 14.9 | 38.4 | 38.4 | 0.44982 | 0.61198 | 14.2185 | 14.0099 | 6.7609 | 122.2391 | 0.11461 | 6.08 |  | 33 | 411 | 903 | 1007.1745 | -11.5365 | 91.7085 | 709.0872 | 95.3461 | 135 | 119 | 20 | 8.4 | 5.7 | 14.1 | 14.1 | 0.3342 | 0.59574 | 10.1647 | 10.0156 | 14.52 | 92.48 | 0.1083 |  | 6.9 | 67 | 903 | 1734 | 2135 | -23.1257 | 83.1658 | 1519 | 95.5892 | SDS-CHCl3 | mg/L | BMRL | 448 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-06-10 | 1998-06-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 436 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 470 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-08 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 448 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 465 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1 | 471 | --- | 3134.3333 | --- | 99.7877 | 1802.6667 | 99.9445 | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | 500 mg/l NaCl | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 13.0417 | [5 empty] | 1998-06-28 | 7:35 | 21810 | 25.4 | 157 | 119 | 18.3 | 0 | 31.4 | 5.8 |  | 37.2 | 37.2 | 0.84409 | 0 | 12.6655 | 12.5167 | 12.1586 | 107.5414 | 0.11639 | 6.71 | 5.92 | 40 | 364 | 368 | 1809 | 2143.7241 | -18.5033 | 89.1304 | 1255.8621 | 96.8149 | 157 | 135 | 17 | 22.5 | 15.9 | 38.4 | 38.4 | 0.45826 | 0.58594 | 13.6134 | 13.4534 | 6.4545 | 122.5455 | 0.10978 | 6.12 |  | 33 | 411 | 899 | 945.9057 | -5.2175 | 91.0326 | 678.4528 | 95.136 | 135 | 119 | 20 | 8.9 | 5.8 | 14.7 | 14.7 | 0.34602 | 0.60544 | 10.7697 | 10.6432 | 14.7034 | 92.2966 | 0.11531 |  | 6.48 | 67 | 899 | 1809 | 2175.6897 | -20.2703 | 81.7935 | 1537.3448 | 95.6418 | SDS-BDCM | mg/L | 0.6 | 67.4 | --- | 418.1 | --- | 99.1098 | 242.75 | 99.7528 | Sampling time | hh:mm | 7:35 | 7:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 57.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:40 | 7:20 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1 | 76.3 | --- | 471.625 | --- | 98.6894 | 273.9625 | 99.635 | Sampling time | hh:mm | 8:40 | 8:25 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.6 | 68.7 | --- | -0.21071 | --- | 99.1266 | 34.2446 | 98.2479 | Sampling time | hh:mm | 8:15 | 7:45 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1 | 75.8 | --- | 499.6667 | --- | 98.6807 | 287.7333 | 99.6525 | Sampling time | hh:mm | 9:55 | 9:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1 | 19.9 | --- | 127 | --- | 94.9749 | 73.45 | 98.6385 | Sampling time | hh:mm | 9:55 | 9:15 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | not specified | [7 empty] | 1998-06-29 | 9:50 | 21836 | 25.5 | 156 | 118 | 18.1 | 0 | 29.9 | 5.8 |  | 35.7 | 35.7 | 0.83754 | 0 | 12.0605 | 11.8836 | 12.4858 | 106.4142 | 0.11167 | 6.82 | 6.11 | 39 | 367 | 388 | 1794 | 2187.1552 | -21.915 | 89.9485 | 1287.5776 | 96.9711 | 156 | 135 | 17 | 21.5 | 16.9 | 38.4 | 38.4 | 0.4667 | 0.5599 | 13.0084 | 12.8176 | 6.1681 | 122.3319 | 0.10478 | 6.1 |  | 32 | 409 | 900 | 888.6154 | 1.265 | 91.7526 | 648.8077 | 95.0679 | 135 | 118 | 20 | 8.3 | 5.8 | 14.1 | 14.1 | 0.33589 | 0.58865 | 10.0437 | 9.8963 | 14.3074 | 92.1926 | 0.10734 |  | 6.73 | 66 | 900 | 1794 | 2093.4828 | -16.6936 | 82.9897 | 1496.7414 | 95.5904 | SDS-DBCM | mg/L | 1.2 | 8.7 | --- | 48.075 | --- | 86.2069 | 28.3875 | 95.7728 | Operation time | hh.hh | 21378 | 21378 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1 | 8.3 | --- | 46.625 | --- | 87.9518 | 27.4625 | 96.3587 | Operation time | hh.hh | 21714 | 21714 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.4 | 8.8 | --- | 47.65 | --- | 84.0909 | 28.225 | 95.0399 | Operation time | hh.hh | 22051 | 22051 | --- | --- | --- | --- | SDS-DBCM | mg/L | 0.7 | 9.6 | --- | 0.59405 | --- | 92.7083 | 5.097 | 86.2665 | Operation time | hh.hh | 22386 | 22386 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.1 | 9.6 | --- | 57.7667 | --- | 88.5417 | 33.6833 | 96.7343 | Operation time | hh.hh | 22723 | 22723 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.1 | 8.8 | --- | 52.4333 | --- | 87.5 | 30.6167 | 96.4072 | Operation time | hh.hh | 22723 | 22723 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-06-30 | 9:20 | 21860 | 25.5 | 156 | 118 | 18.2 | 0 | 33.1 | 5.8 |  | 38.9 | 38.9 | 0.8509 | 0 | 13.3513 | 13.1554 | 14.2963 | 104.5037 | 0.12588 | 6.71 | 5.94 | 40 | 391 | 411 | 1809 | 2528.2586 | -39.76 | 90.2676 | 1469.6293 | 97.2782 | 156 | 135 | 17 | 24.6 | 13.6 | 38.2 | 38.2 | 0.43716 | 0.64398 | 14.884 | 14.6657 | 7.2177 | 121.2823 | 0.12092 | 5.93 |  | 33 | 412 | 902 | 1097.5441 | -21.6789 | 91.9708 | 754.7721 | 95.6278 | 135 | 118 | 20 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 10.0156 | 14.3966 | 92.1034 | 0.10874 |  | 6.57 | 67 | 902 | 1809 | 2111.3103 | -16.7115 | 83.6983 | 1506.6552 | 95.5531 | SDS-CHBr3 | mg/L | 1.5 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.63 | 6.31 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.54 | 6.53 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.79 | 6.56 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.8 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.74 | 6.47 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.68 | 6.23 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.59 | 6.21 | --- | --- | --- | ---
|  | Standard testing pH | 6.5 - 7.0 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-07-01 | 9:38 | 21884 | 25.5 | 156 | 118 | 18.3 | 0 | 29.8 | 5.8 |  | 35.6 | 35.6 | 0.83708 | 0 | 12.0202 | 11.8438 | 13.1695 | 105.5305 | 0.11223 | 6.79 | 5.74 | 43 | 392 | 412 | 1800 | 2307.8966 | -28.2165 | 89.5631 | 1359.9483 | 96.8381 | 156 | 135 | 17 | 21 | 17.3 | 38.3 | 38.3 | 0.46923 | 0.5483 | 12.7059 | 12.5195 | 6.1546 | 122.3454 | 0.10233 | 5.61 |  | 36 | 419 | 907 | 883.9133 | 2.5454 | 91.2621 | 651.4566 | 94.4739 | 135 | 118 | 20 | 8.7 | 5.8 | 14.5 | 14.5 | 0.34264 | 0.6 | 10.5277 | 10.3733 | 14.665 | 91.835 | 0.11296 |  | 6.25 | 69 | 907 | 1800 | 2164 | -20.2222 | 83.2524 | 1535.5 | 95.5063 | SDS-THM4 | mg/L | 3.3 | 524.1 | --- | 3258.3 | --- | 99.3703 | 1891.2 | 99.8255 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 2.2 | 501.7 | --- | 3124.075 | --- | 99.5615 | 1812.8875 | 99.8786 | Temperature | oC | 26.1 | 26.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.6 | 555.1 | --- | 3450.475 | --- | 99.3515 | 2002.7875 | 99.8203 | Temperature | oC | 26.5 | 26.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 2.1 | 526.3 | --- | -4.1405 | --- | 99.601 | 261.0798 | 99.1956 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 2.1 | 550.4 | --- | 3657.4333 | --- | 99.6185 | 2103.9167 | 99.9002 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.1 | 499.7 | --- | 3313.7667 | --- | 99.3796 | 1906.7333 | 99.8374 | Temperature | oC | 26 | 26 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 13.0417 | [5 empty] | 1998-07-02 | 8:48 | 21907 | 25.4 | 157 | 119 | 18 | 0 | 30.2 | 5.7 |  | 35.9 | 35.9 | 0.84123 | 0 | 12.1815 | 12.0383 | 13.4653 | 106.5347 | 0.113 | 6.79 | 5.72 | 42 | 386 | 411 | 1792 | 2366.0526 | -32.0342 | 89.781 | 1388.5263 | 96.9752 | 157 | 136 | 17 | 21.4 | 16.7 | 38.1 | 38.1 | 0.46248 | 0.56168 | 12.9479 | 12.7957 | 6.1199 | 123.3801 | 0.10371 | 5.54 |  | 42 | 415 | 896 | 892.976 | 0.33749 | 89.781 | 653.988 | 93.5779 | 136 | 119 | 20 | 8.7 | 5.7 | 14.4 | 14.4 | 0.33927 | 0.60417 | 10.5277 | 10.404 | 14.5989 | 92.9011 | 0.11199 |  | 6.23 | 68 | 896 | 1792 | 2159.7895 | -20.524 | 83.455 | 1527.8947 | 95.5494 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 280 | 529.4 | 72.5 | 404.7 | 94.5639 | SDS-MCAA* | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 220 | 415.2243 | 80 | 317.6121 | 93.0733 | SDS-MCAA* | mg/L | 1.2 | 13.7 | --- | 79.325 | --- | 91.2409 | 46.5125 | 97.42 | Alkalinity | mg/L as CaCO3 | 22 | 194 | 373.9691 | 74.4186 | 283.9846 | 92.2531 | SDS-MCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 170 | 375.8484 | 75.6098 | 272.9242 | 92.672 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 155 | 308.5447 | 68.5714 | 231.7724 | 90.5079 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 150 | 300.0813 | 73.3333 | 225.0407 | 91.1127
|  | Acceptable range of operating pH values | 3 to 10 | Design system recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-07-03 | 9:00 | 21932 | 25.4 | 154 | 117 | 17.6 | 0 | 31.4 | 5.7 |  | 37.1 | 37.1 | 0.84636 | 0 | 12.6655 | 12.5167 | 13.7035 | 104.1965 | 0.12013 | 6.81 | 6.02 | 40 | 396 | 405 | 1799 | 2415.7018 | -34.2803 | 90.1235 | 1410.3509 | 97.1638 | 154 | 133 | 16 | 23.1 | 16.5 | 39.6 | 39.6 | 0.47345 | 0.58333 | 13.9765 | 13.8122 | 6.426 | 121.074 | 0.11408 | 5.86 |  | 33 | 411 | 896 | 940.2 | -4.933 | 91.8519 | 675.6 | 95.1155 | 133 | 117 | 19 | 8.3 | 5.7 | 14 | 14 | 0.33251 | 0.59286 | 10.0437 | 9.9256 | 14.3257 | 91.6743 | 0.10827 |  | 6.53 | 67 | 896 | 1799 | 2103.1404 | -16.9061 | 83.4568 | 1499.5702 | 95.5321 | SDS-DCAA* | mg/L | BMRL | 142 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 71 | 907 | 1715.1333 | 83.3724 | 1311.0667 | 94.5846 | SDS-DCAA* | mg/L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 54 | 816 | 1567.3178 | 84.3478 | 1191.6589 | 95.4685 | SDS-DCAA* | mg/L | BMRL | 124 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 66 | 904 | 1780.8263 | 84.058 | 1342.4131 | 95.0835 | SDS-DCAA* | mg/L | BMRL | 189 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 60.1 | 895 | 2040.7524 | 85.622 | 1467.8762 | 95.9056 | SDS-DCAA* | mg/L | BMRL | 154 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 51 | 781 | 1623.7642 | 86.0656 | 1202.3821 | 95.7584 | SDS-DCAA* | mg/L | BMRL | 152 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 52 | 782 | 1624.7642 | 85.8696 | 1203.3821 | 95.6788
|  | Typical pressure drop across a single element (psi) | 4 | System influent flow rate, QI-sys (gpm) | 43.76 | [5 empty] | 1998-07-04 | 8:57 | 21955 | 25.5 | 156 | 119 | 18.6 | 0 | 29.3 | 5.5 |  | 34.8 | 34.8 | 0.84195 | 0 | 11.8185 | 11.6451 | 13.7386 | 105.1614 | 0.11074 | 6.83 | 5.99 | 39 | 389 | 414 | 1848 | 2411.7273 | -30.5047 | 90.5797 | 1412.8636 | 97.2396 | 156 | 135 | 17 | 20.9 | 16.8 | 37.7 | 37.7 | 0.45995 | 0.55438 | 12.6454 | 12.4599 | 6.1312 | 122.3688 | 0.10182 | 5.88 |  | 33 | 411 | 907 | 881.25 | 2.839 | 92.029 | 646.125 | 94.8926 | 135 | 119 | 20 | 8.3 | 5.5 | 13.8 | 13.8 | 0.32576 | 0.60145 | 10.0437 | 9.8963 | 14.7382 | 92.2618 | 0.10726 |  | 6.58 | 67 | 907 | 1848 | 2174.6364 | -17.6751 | 83.8164 | 1540.8182 | 95.6517 | SDS-TCAA* | mg/L | BMRL | 129 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 650 | 1255.1333 | 90.7692 | 952.5667 | 97.4805 | SDS-TCAA* | mg/L | BMRL | 121 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 27 | 610 | 1184.8271 | 90.3571 | 897.4136 | 96.9914 | SDS-TCAA* | mg/L | BMRL | 114 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 22 | 700 | 1409.4131 | 91.4062 | 1054.7066 | 97.9141 | SDS-TCAA* | mg/L | BMRL | 191 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 25 | 640 | 1483.9786 | 90.0794 | 1061.9893 | 97.6459 | SDS-TCAA* | mg/L | 1.6 | 254 | --- | 1684.2667 | --- | 99.3701 | 969.1333 | 99.8349 | Total hardness | mg/L as CaCO3 | 21 | 590 | 1246.8943 | 91.9231 | 918.4472 | 97.7135 | SDS-TCAA* | mg/L | 1.26 | 215 | --- | 1426.1933 | --- | 99.414 | 820.5967 | 99.8465 | Total hardness | mg/L as CaCO3 | 22 | 600 | 1267.2846 | 91.3725 | 933.6423 | 97.6436
|  | Maximum permissible SDI | 4 | Recycle ratio, r | 0.00022857 | [5 empty] | 1998-07-05 | 9:05 | 21980 | 25.5 | 155 | 118 | 17.5 | 0 | 30.4 | 5.6 |  | 36 | 36 | 0.84444 | 0 | 12.2622 | 12.0823 | 13.8914 | 105.1086 | 0.11495 | 6.78 | 5.9 | 39 | 389 | 413 | 1810 | 2443.2857 | -34.9882 | 90.5569 | 1428.1429 | 97.2692 | 155 | 134 | 16 | 21.9 | 16.1 | 38 | 38 | 0.45657 | 0.57632 | 13.2504 | 13.056 | 6.2837 | 122.2163 | 0.10683 | 5.91 |  | 39 | 413 | 904 | 921.7329 | -1.9616 | 90.5569 | 667.3665 | 94.1561 | 134 | 118 | 19 | 8.4 | 5.6 | 14 | 14 | 0.33083 | 0.6 | 10.1647 | 10.0156 | 14.6475 | 92.3525 | 0.10845 |  | 6.51 | 67 | 904 | 1810 | 2159.5 | -19.3094 | 83.7772 | 1531.75 | 95.6259 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 22 | 610 | 1178.4 | 90.9836 | 894.2 | 97.5397 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 550 | 1072.5701 | 92 | 811.285 | 97.5348 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 530 | 1063.6293 | 91.3043 | 796.8147 | 97.49 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 17 | 540 | 1257.7249 | 92.6087 | 898.8624 | 98.1087 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 560 | 1185.7236 | 92.1739 | 872.8618 | 97.9378 | SDS-MBAA* | mg/L | 0.55 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 550 | 1164.1789 | 92.1739 | 857.0894 | 97.8999
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-07-06 | 8:44 | 22003 | 25.4 | 155 | 117 | 17.5 | 0 | 30.2 | 5.9 |  | 36.1 | 36.1 | 0.83657 | 0 | 12.1815 | 12.0383 | 12.5644 | 105.9356 | 0.11364 | 6.87 | 6 | 39 | 395 | 392 | 1764 | 2198.8814 | -24.6531 | 90.051 | 1295.4407 | 96.9894 | 155 | 134 | 17 | 21.7 | 16.1 | 37.8 | 37.8 | 0.45489 | 0.57407 | 13.1294 | 12.9751 | 6.3441 | 121.1559 | 0.10709 | 5.88 |  | 33 | 412 | 896 | 922.8261 | -2.994 | 91.5816 | 667.413 | 95.0555 | 134 | 117 | 19 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.1648 | 14.2788 | 92.2212 | 0.11022 |  | 6.6 | 66 | 896 | 1764 | 2091.7627 | -18.5807 | 83.1633 | 1493.8814 | 95.582 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.058 | 2.64 | 5.1359 | 96.4198 | 3.888 | 98.5082 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.034 | 1.03 | 2.012 | 77.7778 | 1.521 | 97.7647 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.067 | 0.694 | 1.3501 | 53.4722 | 1.022 | 93.4444 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.049 | 0.279 | 0.59463 | 67.3333 | 0.43682 | 88.7825 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.053 | 0.88 | 1.8347 | 51.8182 | 1.3574 | 96.0954 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.067 | 1.42 | 2.982 | 41.7391 | 2.201 | 96.9559
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | maximum system recycle flow rates. | [6 empty] | 1998-07-07 | 8:43 | 22027 | 25.5 | 155 | 118 | 17.5 | 0 | 30.1 | 5.6 |  | 35.7 | 35.7 | 0.84314 | 0 | 12.1412 | 11.9631 | 14.1231 | 104.8769 | 0.11407 | 6.82 | 5.91 | 40 | 409 | 423 | 1803 | 2481.625 | -37.6387 | 90.5437 | 1452.3125 | 97.2458 | 155 | 134 | 17 | 21.5 | 16.1 | 37.6 | 37.6 | 0.4532 | 0.57181 | 13.0084 | 12.8176 | 6.3039 | 121.1961 | 0.10576 | 5.87 |  | 33 | 411 | 900 | 915.7826 | -1.7536 | 92.1986 | 663.3913 | 95.0256 | 134 | 118 | 19 | 8.5 | 5.6 | 14.1 | 14.1 | 0.33251 | 0.60284 | 10.2857 | 10.1348 | 14.6519 | 92.3481 | 0.10975 |  | 6.52 | 67 | 900 | 1803 | 2164.375 | -20.043 | 84.1608 | 1532.1875 | 95.6272 | SDS-BCAA* | mg/L | BMRL | 19.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 31.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 18.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.9 | 32.5 | 65.5641 | 93.3333 | 49.032 | 98.1645 | SDS-BCAA* | mg/L | BMRL | 20.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.13 | 31.6 | 73.4147 | 92.0979 | 52.5073 | 97.8479 | SDS-BCAA* | mg/L | BMRL | 22.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.6 | 32.7 | 69.7585 | 95.7447 | 51.2293 | 98.8288 | SDS-BCAA* | mg/L | BMRL | 21.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.52 | 32.5 | 69.42 | 95.969 | 50.96 | 98.9796
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-07-08 | 9:00 | 22052 | 25.4 | 155 | 118 | 17.3 | 0 | 30 | 5.7 |  | 35.7 | 35.7 | 0.84034 | 0 | 12.1008 | 11.9586 | 13.7274 | 105.4726 | 0.11338 | 6.85 | 6.01 | 40 | 391 | 418 | 1803 | 2407.4737 | -33.526 | 90.4306 | 1412.7368 | 97.1686 | 155 | 134 | 16 | 21.7 | 15.8 | 37.5 | 37.5 | 0.44982 | 0.57867 | 13.1294 | 12.9751 | 6.3926 | 122.1074 | 0.10626 | 5.86 |  | 33 | 412 | 903 | 932.5253 | -3.2697 | 92.1053 | 672.2627 | 95.0912 | 134 | 118 | 18 | 8.1 | 5.7 | 13.8 | 13.8 | 0.32914 | 0.58696 | 9.8017 | 9.6865 | 14.3 | 93.7 | 0.10338 |  | 6.47 | 67 | 903 | 1803 | 2091 | -15.9734 | 83.9713 | 1497 | 95.5244 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.979 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.976 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.225 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.047 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.172 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.227 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-07-09 | 9:00 | 22076 | 25.5 | 154 | 116 | 17 | 0 | 31 | 5.8 |  | 36.8 | 36.8 | 0.84239 | 0 | 12.5042 | 12.3208 | 13.5512 | 104.4488 | 0.11796 | 6.78 | 5.8 | 40 | 389 | 409 | 1746 | 2381.2414 | -36.3827 | 90.22 | 1395.1207 | 97.1329 | 154 | 133 | 16 | 22.6 | 14.4 | 37 | 37 | 0.43379 | 0.61081 | 13.6739 | 13.4733 | 6.7641 | 120.7359 | 0.11159 | 5.77 |  | 34 | 413 | 893 | 1007.8194 | -12.8577 | 91.687 | 710.4097 | 95.214 | 133 | 116 | 18 | 8.2 | 5.8 | 14 | 14 | 0.3342 | 0.58571 | 9.9227 | 9.7771 | 14.116 | 92.384 | 0.10583 |  | 6.36 | 66 | 893 | 1746 | 2062.2069 | -18.1104 | 83.8631 | 1477.6034 | 95.5333 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.0981 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.2533 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7692 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3133 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5841 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7754 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 43.76 | [5 empty] | 1998-07-10 | 8:28 | 22099 | 25.4 | 153 | 117 | 17.2 | 0 | 28.9 | 5.5 |  | 34.4 | 34.4 | 0.84012 | 0 | 11.6571 | 11.5201 | 13.5297 | 104.2703 | 0.11048 | 6.86 | 5.94 | 39 | 388 | 412 | 1792 | 2371.9455 | -32.363 | 90.534 | 1391.9727 | 97.1982 | 153 | 133 | 16 | 20.6 | 16.2 | 36.8 | 36.8 | 0.44729 | 0.55978 | 12.4639 | 12.3174 | 6.1833 | 120.8167 | 0.10195 | 5.86 |  | 33 | 411 | 896 | 891.6667 | 0.48363 | 91.9903 | 651.3333 | 94.9335 | 133 | 117 | 18 | 8.2 | 5.5 | 13.7 | 13.7 | 0.32407 | 0.59854 | 9.9227 | 9.8061 | 14.4873 | 92.5127 | 0.106 |  | 6.53 | 66 | 896 | 1792 | 2133.4545 | -19.0544 | 83.9806 | 1514.7273 | 95.6428 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 24.7917 | [5 empty] | 1998-07-11 | 8:15 | 22123 | 25.5 | 153 | 116 | 16.9 | 0 | 31.1 | 5.6 |  | 36.7 | 36.7 | 0.84741 | 0 | 12.5445 | 12.3605 | 14.0874 | 103.5126 | 0.11941 | 6.82 | 5.92 | 39 | 386 | 412 | 1782 | 2483.4821 | -39.3649 | 90.534 | 1447.7411 | 97.3061 | 153 | 132 | 16 | 23 | 14 | 37 | 37 | 0.43041 | 0.62162 | 13.916 | 13.7118 | 6.885 | 119.615 | 0.11463 | 5.88 |  | 33 | 411 | 896 | 1032 | -15.1786 | 91.9903 | 721.5 | 95.4262 | 132 | 116 | 18 | 8 | 5.6 | 13.6 | 13.6 | 0.32407 | 0.58824 | 9.6807 | 9.5386 | 14.2286 | 91.7714 | 0.10394 |  | 6.54 | 66 | 896 | 1782 | 2081.7143 | -16.819 | 83.9806 | 1488.8571 | 95.5671 | SDS-HAA5 | mg/L | 0 | 271 | --- | 1693.75 | --- | 100 | 982.375 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 252.9 | --- | 1580.625 | --- | 100 | 916.7625 | 100 | [8 empty] | SDS-HAA5 | mg/L | 1.2 | 251.7 | --- | 1566.825 | --- | 99.5232 | 909.2625 | 99.868 | [8 empty] | SDS-HAA5 | mg/L | 0 | 393 | --- | -4.6786 | --- | 100 | 194.1607 | 100 | [8 empty] | SDS-HAA5 | mg/L | 1.6 | 408 | --- | 2710.9333 | --- | 99.6078 | 1559.4667 | 99.8974 | [8 empty] | SDS-HAA5 | mg/L | 1.81 | 367 | --- | 2436.41 | --- | 99.5068 | 1401.705 | 99.8709
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 18.9683 | [5 empty] | 1998-07-12 | 8:02 | 22148 | 25.5 | 153 | 117 | 17 | 0 | 32.2 | 5.6 |  | 37.8 | 37.8 | 0.85185 | 0 | 12.9882 | 12.7977 | 14.415 | 103.585 | 0.12355 | 6.84 | 5.93 | 40 | 389 | 412 | 1814 | 2551 | -40.6284 | 90.2913 | 1481.5 | 97.3 | 153 | 133 | 16 | 23.5 | 13.5 | 37 | 37 | 0.42619 | 0.63514 | 14.2185 | 14.0099 | 7.07 | 119.93 | 0.11682 | 5.85 |  | 33 | 411 | 903 | 1069 | -18.3832 | 91.9903 | 740 | 95.5405 | 133 | 117 | 18 | 8.1 | 5.6 | 13.7 | 13.7 | 0.32576 | 0.59124 | 9.8017 | 9.6579 | 14.4061 | 92.5939 | 0.1043 |  | 6.47 | 67 | 903 | 1814 | 2112.2143 | -16.4396 | 83.7379 | 1507.6071 | 95.5559 | SDS-HAA6 | mg/L | 0 | 290.9 | --- | 1818.125 | --- | 100 | 1054.5125 | 100 | [8 empty] | SDS-HAA6 | mg/L | 0 | 271.9 | --- | 1699.375 | --- | 100 | 985.6375 | 100 | [8 empty] | SDS-HAA6 | mg/L | 1.2 | 270.2 | --- | 1682.45 | --- | 99.5559 | 976.325 | 99.8771 | [8 empty] | SDS-HAA6 | mg/L | 0 | 413.9 | --- | -4.9274 | --- | 100 | 204.4863 | 100 | [8 empty] | SDS-HAA6 | mg/L | 1.6 | 430.4 | --- | 2860.2667 | --- | 99.6283 | 1645.3333 | 99.9028 | [8 empty] | SDS-HAA6 | mg/L | 1.81 | 388.2 | --- | 2577.7433 | --- | 99.5337 | 1482.9717 | 99.8779
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 18.9683 | [5 empty] | 1998-07-13 | 7:30 | 22170 | 25.4 | 154 | 117 | 17.1 | 0 | 31.3 | 5.6 |  | 36.9 | 36.9 | 0.84824 | 0 | 12.6252 | 12.4768 | 14.192 | 104.208 | 0.11973 | 6.85 | 5.92 | 40 | 388 | 414 | 1785 | 2504.3929 | -40.3021 | 90.3382 | 1459.1964 | 97.2588 | 154 | 133 | 16 | 22.8 | 14.1 | 36.9 | 36.9 | 0.43041 | 0.61789 | 13.795 | 13.6328 | 6.8181 | 120.6819 | 0.11296 | 5.84 |  | 33 | 410 | 897 | 1019.617 | -13.6697 | 92.029 | 714.8085 | 95.3834 | 133 | 117 | 18 | 8.4 | 5.6 | 14 | 14 | 0.33083 | 0.6 | 10.1647 | 10.0452 | 14.5425 | 92.4575 | 0.10865 |  | 6.46 | 66 | 897 | 1785 | 2143.5 | -20.084 | 84.058 | 1520.25 | 95.6586 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.3958 | [5 empty] | 1998-07-14 | 9:06 | 22196 | 25.4 | 161 | 122 | 18.5 | 0 | 33.5 | 5.9 |  | 39.4 | 39.4 | 0.85025 | 0 | 13.5126 | 13.3538 | 14.0891 | 108.9109 | 0.12261 | 6.81 | 5.8 | 39 | 393 | 406 | 1799 | 2489.8136 | -38.3999 | 90.3941 | 1447.9068 | 97.3065 | 161 | 138 | 17 | 24.9 | 14.2 | 39.1 | 39.1 | 0.44982 | 0.63683 | 15.0655 | 14.8885 | 7.0942 | 125.4058 | 0.11872 | 5.75 |  | 32 | 410 | 882 | 1072.831 | -21.6362 | 92.1182 | 741.4155 | 95.6839 | 138 | 122 | 20 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 10.1648 | 14.124 | 95.876 | 0.10602 |  | 6.31 | 61 | 882 | 1799 | 2064.7966 | -14.7747 | 84.9754 | 1473.3983 | 95.8599 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 6.5725 | [5 empty] | 1998-07-15 | 8:47 | 22219 | 25.4 | 162 | 124 | 18.1 | 0 | 31.4 | 6 |  | 37.4 | 37.4 | 0.83957 | 0 | 12.6655 | 12.5167 | 13.4178 | 111.4822 | 0.11228 | 6.78 | 5.83 | 37 | 394 | 408 | 1799 | 2349.5667 | -30.604 | 90.9314 | 1378.7833 | 97.3165 | 162 | 140 | 17 | 22.8 | 16.1 | 38.9 | 38.9 | 0.46417 | 0.58612 | 13.795 | 13.6328 | 6.5248 | 127.4752 | 0.10694 | 5.8 |  | 32 | 414 | 896 | 954.9689 | -6.5814 | 92.1569 | 684.4845 | 95.3249 | 140 | 124 | 19 | 8.5 | 6 | 14.5 | 14.5 | 0.34602 | 0.58621 | 10.2857 | 10.1648 | 14.2988 | 98.7013 | 0.10299 |  | 6.3 | 59 | 896 | 1799 | 2081.75 | -15.7171 | 85.5392 | 1488.875 | 96.0373
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-07-16 | 8:56 | 22243 | 25.3 | 162 | 124 | 18.1 | 0 | 31.6 | 5.8 |  | 37.4 | 37.4 | 0.84492 | 0 | 12.7462 | 12.6337 | 14.04 | 110.86 | 0.11396 | 6.78 | 5.84 | 38 | 401 | 415 | 1835 | 2469 | -34.5504 | 90.8434 | 1442 | 97.3648 | 162 | 140 | 16 | 22.8 | 16 | 38.8 | 38.8 | 0.46248 | 0.58763 | 13.795 | 13.6732 | 6.5931 | 128.4069 | 0.10648 | 5.81 |  | 32 | 417 | 906 | 965.625 | -6.5811 | 92.2892 | 691.3125 | 95.3711 | 140 | 124 | 20 | 8.7 | 5.8 | 14.5 | 14.5 | 0.34264 | 0.6 | 10.5277 | 10.4348 | 14.7875 | 97.2125 | 0.10734 |  | 6.33 | 61 | 906 | 1835 | 2173.5 | -18.4469 | 85.3012 | 1539.75 | 96.0383 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 6.5625 | [5 empty] | 1998-07-17 | 8:45 | 22267 | 25.3 | 162 | 124 | 17.3 | 0 | 31.6 | 5.8 |  | 37.4 | 37.4 | 0.84492 | 0 | 12.7462 | 12.6337 | 14.189 | 111.511 | 0.1133 | 6.75 | 5.79 | 38 | 387 | 419 | 1835 | 2494.7931 | -35.956 | 90.9308 | 1456.8966 | 97.3917 | 162 | 140 | 16 | 22.6 | 16.2 | 38.8 | 38.8 | 0.46417 | 0.58247 | 13.6739 | 13.5532 | 6.5525 | 128.4475 | 0.10552 | 5.84 |  | 32 | 418 | 907 | 956.4938 | -5.4569 | 92.3628 | 687.2469 | 95.3437 | 140 | 124 | 18 | 8.8 | 5.8 | 14.6 | 14.6 | 0.34433 | 0.60274 | 10.6487 | 10.5547 | 14.8779 | 99.1221 | 0.10648 |  | 6.38 | 61 | 907 | 1835 | 2190.5862 | -19.378 | 85.4415 | 1548.7931 | 96.0614 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 37.1875 | [5 empty] | 1998-07-18 | 8:10 | 22290 | 25.3 | 162 | 123 | 17.9 | 0 | 33.1 | 5.9 |  | 39 | 39 | 0.84872 | 0 | 13.3513 | 13.2334 | 14.4593 | 110.1407 | 0.12015 | 6.78 | 5.8 | 37 | 397 | 417 | 1788 | 2548.8644 | -42.5539 | 91.1271 | 1482.9322 | 97.5049 | 162 | 140 | 17 | 24.1 | 14.7 | 38.8 | 38.8 | 0.45151 | 0.62113 | 14.5815 | 14.4528 | 6.9696 | 127.0304 | 0.11377 | 5.83 |  | 32 | 415 | 896 | 1042.9116 | -16.3964 | 92.3261 | 728.9558 | 95.6102 | 140 | 123 | 19 | 9 | 5.9 | 14.9 | 14.9 | 0.35108 | 0.60403 | 10.8908 | 10.7946 | 14.7363 | 97.7637 | 0.11042 |  | 6.39 | 60 | 896 | 1788 | 2171.2542 | -21.4348 | 85.6115 | 1533.6271 | 96.0877 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 43.75 | [5 empty] | 1998-07-19 | 9:16 | 22316 | 25.5 | 162 | 124 | 18.1 | 0 | 33.2 | 5.8 |  | 39 | 39 | 0.85128 | 0 | 13.3916 | 13.1951 | 14.6372 | 110.2628 | 0.11967 | 6.79 | 5.91 | 37 | 376 | 416 | 1821 | 2585.4483 | -41.9796 | 91.1058 | 1500.7241 | 97.5345 | 162 | 140 | 17 | 24.7 | 14 | 38.7 | 38.7 | 0.44476 | 0.63824 | 14.9445 | 14.7253 | 7.2086 | 126.7914 | 0.11614 | 5.85 |  | 32 | 415 | 903 | 1090.7214 | -20.7886 | 92.3077 | 752.8607 | 95.7495 | 140 | 124 | 19 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 10.0156 | 14.5172 | 98.4828 | 0.1017 |  | 6.45 | 61 | 903 | 1821 | 2122.4483 | -16.554 | 85.3365 | 1512.7241 | 95.9675 | Qp/QT (THM4), % | 86.8088 | 93.7212 |  | Qp/QT (HAA5), % | 80.0738 | 90.0369 | [11 empty] | Qp/QT (THM4), % | 86.026 | 93.2332 |  | Qp/QT (HAA5), % | 78.6477 | 89.3238 | [11 empty] | Qp/QT (THM4), % | 87.5975 | 94.1251 |  | Qp/QT (HAA5), % | 78.9222 | 89.7006 | [11 empty] | Qp/QT (THM4), % | 86.6654 | 93.533 |  | Qp/QT (HAA5), % | 86.2595 | 93.1298 | [11 empty] | Qp/QT (THM4), % | 87.2515 | 93.8173 |  | Qp/QT (HAA5), % | 87.1063 | 93.75 | [11 empty] | Qp/QT (THM4), % | 86.1257 | 93.3749 |  | Qp/QT (HAA5), % | 85.7088 | 93.1022
[11 empty] | 1998-07-20 | 9:11 | 22340 | 25.4 | 163 | 126 | 18 | 0 | 33.2 | 5.6 |  | 38.8 | 38.8 | 0.85567 | 0 | 13.3916 | 13.2342 | 14.3507 | 112.1493 | 0.11801 | 6.77 | 5.83 | 37 | 375 | 399 | 1871 | 2545.1429 | -36.0312 | 90.7268 | 1472.0714 | 97.4865 | 163 | 142 | 17 | 24.6 | 13.8 | 38.4 | 38.4 | 0.44054 | 0.64062 | 14.884 | 14.7091 | 7.2059 | 128.2941 | 0.11465 | 5.82 |  | 32 | 413 | 909 | 1092.1739 | -20.1511 | 91.9799 | 752.587 | 95.748 | 142 | 126 | 19 | 8.5 | 5.6 | 14.1 | 14.1 | 0.33251 | 0.60284 | 10.2857 | 10.1648 | 14.9157 | 100.0843 | 0.10156 |  | 6.38 | 61 | 909 | 1871 | 2196.1429 | -17.378 | 84.7118 | 1552.5714 | 96.071 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 107.0756 | 55.1878 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 108.8548 | 55.5274 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 119.8443 | 60.4012 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 74.1275 | 38.1137 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 72.7962 | 36.3687 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 74.0701 | 37.3544
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-07-21 | 8:22 | 22363 | 25.4 | 163 | 125 | 18 | 0 | 30.2 | 5.7 |  | 35.9 | 35.9 | 0.84123 | 0 | 12.1815 | 12.0383 | 13.1004 | 112.8996 | 0.10663 | 6.76 | 5.84 | 36 | 382 | 395 | 1842 | 2297.0702 | -24.7052 | 90.8861 | 1346.0351 | 97.3255 | 163 | 141 | 17 | 21.6 | 16.9 | 38.5 | 38.5 | 0.46754 | 0.56104 | 13.0689 | 12.9153 | 6.2612 | 128.7388 | 0.10032 | 5.84 |  | 31 | 413 | 903 | 901.2367 | 0.19527 | 92.1519 | 657.1183 | 95.2824 | 141 | 125 | 19 | 8.5 | 5.7 | 14.2 | 14.2 | 0.33589 | 0.59859 | 10.2857 | 10.1648 | 14.7155 | 99.2845 | 0.10238 |  | 6.33 | 60 | 903 | 1842 | 2160.1053 | -17.2696 | 84.8101 | 1531.5526 | 96.0824 | SDS-HAA5b, mg/L | 35.7483 | 17.0156 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 35.3402 | 17.1132 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 32.2684 | 15.9166 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 52.405 | 25.4153 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 53.4099 | 26.7267 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 52.4777 | 26.004 |  | SDS-HAA5b, mg/L | 54 | 27
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 5.7 | [5 empty] | 1998-07-22 | 8:29 | 22387 | 25.3 | 163 | 125 | 17.8 | 0 | 32 | 5.6 |  | 37.6 | 37.6 | 0.85106 | 0 | 12.9076 | 12.7936 | 14.31 | 111.89 | 0.11434 | 6.79 | 5.84 | 37 | 395 | 408 | 1849 | 2528 | -36.7226 | 90.9314 | 1468 | 97.4796 | 163 | 141 | 17 | 23.6 | 14.4 | 38 | 38 | 0.44223 | 0.62105 | 14.279 | 14.1529 | 6.8593 | 128.1407 | 0.11045 | 5.84 |  | 37 | 414 | 911 | 1031.8611 | -13.2669 | 90.9314 | 722.9306 | 94.8819 | 141 | 125 | 19 | 8.3 | 5.6 | 13.9 | 13.9 | 0.32914 | 0.59712 | 10.0437 | 9.955 | 14.8165 | 99.1835 | 0.10037 |  | 6.38 | 60 | 911 | 1849 | 2172.3036 | -17.4853 | 85.2941 | 1541.6518 | 96.1081 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 20.2 | [5 empty] | 1998-07-23 | 8:51 | 22411 | 25.4 | 162 | 124 | 17.7 | 0 | 31.1 | 5.7 |  | 36.8 | 36.8 | 0.84511 | 0 | 12.5445 | 12.3971 | 13.5702 | 111.7298 | 0.11096 | 6.77 | 5.8 | 36 | 382 | 400 | 1788 | 2386.0351 | -33.4472 | 91 | 1393.0175 | 97.4157 | 162 | 140 | 17 | 22.2 | 16 | 38.2 | 38.2 | 0.45742 | 0.58115 | 13.4319 | 13.2741 | 6.2838 | 127.7162 | 0.10393 | 5.82 |  | 36 | 407 | 889 | 921.7625 | -3.6853 | 91 | 664.3813 | 94.5814 | 140 | 124 | 19 | 8.8 | 5.7 | 14.5 | 14.5 | 0.34095 | 0.6069 | 10.6487 | 10.5236 | 14.707 | 98.293 | 0.10706 |  | 6.33 | 59 | 889 | 1788 | 2170.4035 | -21.3872 | 85.25 | 1529.7018 | 96.143 | SDS-CDb, mg/L | 4.9085 | 3.6988 |  | SDS-CDb, mg/L | 6.0871 | 4.3435 | [11 empty] | SDS-CDb, mg/L | 5.1013 | 3.8113 |  | SDS-CDb, mg/L | 6.4221 | 4.511 | [11 empty] | SDS-CDb, mg/L | 4.7828 | 3.634 |  | SDS-CDb, mg/L | 6.3097 | 4.4127 | [11 empty] | SDS-CDb, mg/L | 4.7469 | 3.5382 |  | SDS-CDb, mg/L | 4.8183 | 3.6092 | [11 empty] | SDS-CDb, mg/L | 5.4477 | 4.1871 |  | SDS-CDb, mg/L | 5.4756 | 4.2 | [11 empty] | SDS-CDb, mg/L | 5.6639 | 4.272 |  | SDS-CDb, mg/L | 5.7439 | 4.3244
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1998-07-24 | 8:55 | 22435 | 25.4 | 162 | 124 | 17.5 | 0 | 30.6 | 5.8 |  | 36.4 | 36.4 | 0.84066 | 0 | 12.3429 | 12.1978 | 13.7878 | 111.7122 | 0.10919 | 6.99 | 5.95 | 36 | 391 | 415 | 1788 | 2414.5517 | -35.042 | 91.3253 | 1414.7759 | 97.4554 | 162 | 140 | 16 | 22 | 16.1 | 38.1 | 38.1 | 0.45742 | 0.57743 | 13.3109 | 13.1545 | 6.3289 | 128.6711 | 0.10223 | 5.81 |  | 31 | 407 | 885 | 920.7888 | -4.0439 | 92.5301 | 663.8944 | 95.3306 | 140 | 124 | 19 | 8.6 | 5.8 | 14.4 | 14.4 | 0.34095 | 0.59722 | 10.4067 | 10.2844 | 14.3838 | 98.6162 | 0.10429 |  | 6.48 | 59 | 885 | 1788 | 2109.7586 | -17.9954 | 85.7831 | 1497.3793 | 96.0598 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 2.1298 | 1.2826 |  | TOCb, mg/L | 3.2559 | 1.8569 | [11 empty] | TOCb, mg/L | 2.9642 | 2.0659 |  | TOCb, mg/L | 3.0173 | 2.1186 | [11 empty] | TOCb, mg/L | 2.2425 | 1.3502 |  | TOCb, mg/L | 2.2623 | 1.3594 | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-07-25 | 7:50 | 22458 | 25.5 | 163 | 124 | 17.7 | 0 | 32.5 | 5.8 |  | 38.3 | 38.3 | 0.84856 | 0 | 13.1092 | 12.9169 | 14.1044 | 111.6956 | 0.11564 | 6.75 | 5.77 | 37 | 381 | 408 | 1771 | 2486.8793 | -40.4223 | 90.9314 | 1447.4397 | 97.4438 | 163 | 140 | 17 | 23.5 | 14.8 | 38.3 | 38.3 | 0.44813 | 0.61358 | 14.2185 | 14.0099 | 6.7272 | 127.7728 | 0.10965 | 5.81 |  | 31 | 406 | 885 | 1001.4392 | -13.157 | 92.402 | 703.7196 | 95.5948 | 140 | 124 | 19 | 8.9 | 5.8 | 14.7 | 14.7 | 0.34602 | 0.60544 | 10.7697 | 10.6117 | 14.5974 | 98.4026 | 0.10784 |  | 6.34 | 59 | 885 | 1771 | 2152.4828 | -21.5405 | 85.5392 | 1518.7414 | 96.1152 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | 0.068948 | 0.038029 |  | UV254 b, cm-1 | 0.1006 | 0.054801 | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
|  |  |  | Design permeate pressure, Pp (psi) | 10 | [5 empty] | 1998-07-26 | 8:36 | 22484 | 25.5 | 163 | 124 | 17.8 | 0 | 32.9 | 5.8 |  | 38.7 | 38.7 | 0.85013 | 0 | 13.2706 | 13.0759 | 14.3474 | 111.3526 | 0.11743 | 6.88 | 5.94 | 36 | 386 | 410 | 1795 | 2531.4828 | -41.0297 | 91.2195 | 1470.7414 | 97.5523 | 163 | 140 | 17 | 24.4 | 13.8 | 38.2 | 38.2 | 0.43885 | 0.63874 | 14.763 | 14.5464 | 7.1217 | 127.3783 | 0.1142 | 5.8 |  | 31 | 409 | 892 | 1077.3478 | -20.7789 | 92.439 | 743.1739 | 95.8287 | 140 | 124 | 19 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 10.0156 | 14.3448 | 98.6552 | 0.10152 |  | 6.44 | 60 | 892 | 1795 | 2096.9655 | -16.8226 | 85.3659 | 1494.4828 | 95.9852 | Bromideb, mg/L | 50.1205 | 40.4154 |  | Bromideb, mg/L | 59.5764 | 45.5882 | [11 empty] | Bromideb, mg/L | 51.1758 | 40.0479 |  | Bromideb, mg/L | 62.568 | 46.084 | [11 empty] | Bromideb, mg/L | 49.4867 | 39.3884 |  | Bromideb, mg/L | 62.9074 | 46.2332 | [11 empty] | Bromideb, mg/L | 61.3417 | 52.2558 |  | Bromideb, mg/L | 61.8786 | 52.7893 | [11 empty] | Bromideb, mg/L | 50.5852 | 39.4169 |  | Bromideb, mg/L | 50.8322 | 39.5312 | [11 empty] | Bromideb, mg/L | 50.2037 | 38.1843 |  | Bromideb, mg/L | 50.8948 | 38.6365
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 26 | [5 empty] | 1998-07-27 | 8:48 | 22507 | 25.4 | 163 | 124 | 17.7 | 0 | 31.3 | 5.8 |  | 37.1 | 37.1 | 0.84367 | 0 | 12.6252 | 12.4768 | 13.4617 | 112.3383 | 0.11106 | 6.83 | 5.9 | 37 | 380 | 401 | 1788 | 2365.3448 | -32.29 | 90.7731 | 1383.1724 | 97.325 | 163 | 140 | 17 | 22.9 | 15.3 | 38.2 | 38.2 | 0.45151 | 0.59948 | 13.8555 | 13.6926 | 6.6088 | 127.8912 | 0.10706 | 5.82 |  | 32 | 410 | 892 | 975.7647 | -9.3907 | 92.02 | 692.8824 | 95.3816 | 140 | 124 | 19 | 8.3 | 5.8 | 14.1 | 14.1 | 0.33589 | 0.58865 | 10.0437 | 9.9256 | 14.2731 | 98.7269 | 0.10054 |  | 6.38 | 60 | 892 | 1788 | 2082.6207 | -16.4777 | 85.0374 | 1487.3103 | 95.9659 | Alkb, mg/L CaCO3 | 24.4424 | 20.0184 |  | Alkb, mg/L CaCO3 | 28.7528 | 22.3764 | [11 empty] | Alkb, mg/L CaCO3 | 29.1355 | 22.3608 |  | Alkb, mg/L CaCO3 | 36.0712 | 26.0356 | [11 empty] | Alkb, mg/L CaCO3 | 22.9298 | 18.2299 |  | Alkb, mg/L CaCO3 | 29.176 | 21.4156 | [11 empty] | Alkb, mg/L CaCO3 | 24.8008 | 20.2682 |  | Alkb, mg/L CaCO3 | 25.0687 | 20.5344 | [11 empty] | Alkb, mg/L CaCO3 | 22.0117 | 18.4005 |  | Alkb, mg/L CaCO3 | 22.0915 | 18.4375 | [11 empty] | Alkb, mg/L CaCO3 | 22.4634 | 18.0413 |  | Alkb, mg/L CaCO3 | 22.7176 | 18.2076
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 46.875 | [5 empty] | 1998-07-28 | 11:00 | 22533 | 25.4 | 163 | 125 | 17.6 | 0 | 31.4 | 5.7 |  | 37.1 | 37.1 | 0.84636 | 0 | 12.6655 | 12.5167 | 13.9663 | 112.4337 | 0.11132 | 6.94 | 6 | 37 | 398 | 409 | 1795 | 2458.2632 | -36.9506 | 90.9535 | 1433.6316 | 97.4191 | 163 | 141 | 17 | 22.8 | 15.1 | 37.9 | 37.9 | 0.44729 | 0.60158 | 13.795 | 13.6328 | 6.6689 | 128.3311 | 0.10623 | 5.82 |  | 31 | 411 | 899 | 984.7748 | -9.5411 | 92.4205 | 697.8874 | 95.558 | 141 | 125 | 19 | 8.6 | 5.7 | 14.3 | 14.3 | 0.33758 | 0.6014 | 10.4067 | 10.2844 | 14.7193 | 99.2807 | 0.10359 |  | 6.52 | 60 | 899 | 1795 | 2164.8596 | -20.605 | 85.3301 | 1531.9298 | 96.0834 | T-Hdb, mg/L CaCO3 | 49.9228 | 33.1947 |  | T-Hdb, mg/L CaCO3 | 66.2214 | 42.1107 | [11 empty] | T-Hdb, mg/L CaCO3 | 51.1708 | 31.9996 |  | T-Hdb, mg/L CaCO3 | 70.7972 | 42.3986 | [11 empty] | T-Hdb, mg/L CaCO3 | 47.518 | 31.9822 |  | T-Hdb, mg/L CaCO3 | 68.1653 | 42.5126 | [11 empty] | T-Hdb, mg/L CaCO3 | 45.7364 | 29.3915 |  | T-Hdb, mg/L CaCO3 | 46.7023 | 30.3511 | [11 empty] | T-Hdb, mg/L CaCO3 | 47.9788 | 32.0241 |  | T-Hdb, mg/L CaCO3 | 48.3317 | 32.1875 | [11 empty] | T-Hdb, mg/L CaCO3 | 49.1597 | 31.8339 |  | T-Hdb, mg/L CaCO3 | 50.1559 | 32.4857
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 40.8667 | [5 empty] | 1998-07-29 | 8:51 | 22555 | 25.4 | 164 | 125 | 17.5 | 0 | 32.9 | 5.7 |  | 38.6 | 38.6 | 0.85233 | 0 | 13.2706 | 13.1146 | 14.1838 | 112.8162 | 0.11625 | 6.84 | 5.89 | 37 | 389 | 402 | 1813 | 2508.7544 | -38.3759 | 90.796 | 1455.3772 | 97.4577 | 164 | 141 | 16 | 24.3 | 13.7 | 38 | 38 | 0.43632 | 0.63947 | 14.7025 | 14.5297 | 7.1701 | 129.3299 | 0.11235 | 5.94 |  | 32 | 412 | 899 | 1086.0146 | -20.8025 | 92.0398 | 749.0073 | 95.7277 | 141 | 125 | 19 | 8.6 | 5.7 | 14.3 | 14.3 | 0.33758 | 0.6014 | 10.4067 | 10.2844 | 14.7193 | 99.2807 | 0.10359 |  | 6.46 | 60 | 899 | 1813 | 2164.8596 | -19.4076 | 85.0746 | 1531.9298 | 96.0834 | Ca-Hdb, mg/L CaCO3 | 46.076 | 30.3157 |  | Ca-Hdb, mg/L CaCO3 | 61.4317 | 38.7159 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 45.2581 | 28.1049 |  | Ca-Hdb, mg/L CaCO3 | 62.8185 | 37.4093 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 40.7895 | 26.6898 |  | Ca-Hdb, mg/L CaCO3 | 59.5281 | 36.2467 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 37.6028 | 22.3567 |  | Ca-Hdb, mg/L CaCO3 | 38.5038 | 23.2519 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 41.5367 | 27.3547 |  | Ca-Hdb, mg/L CaCO3 | 41.8504 | 27.5 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 42.2461 | 26.4426 |  | Ca-Hdb, mg/L CaCO3 | 43.1548 | 27.0372
|  |  |  | Required influent pressure to the system, PI (psi) | 97.7417 | [5 empty] | 1998-07-30 | 8:05 | 22578 | 25.4 | 161 | 122 | 17.1 | 0 | 30.3 | 5.8 |  | 36.1 | 36.1 | 0.83934 | 0 | 12.2218 | 12.0782 | 13.2563 | 111.1437 | 0.10867 | 6.82 | 5.9 | 37 | 373 | 404 | 1753 | 2321.2586 | -32.4164 | 90.8416 | 1362.6293 | 97.2847 | 161 | 139 | 16 | 21.9 | 17.9 | 39.8 | 39.8 | 0.48696 | 0.55025 | 13.2504 | 13.0947 | 6.1085 | 127.8915 | 0.10239 | 5.91 |  | 31 | 410 | 889 | 873.6927 | 1.7219 | 92.3267 | 641.8464 | 95.1702 | 139 | 122 | 18 | 8.3 | 5.8 | 14.1 | 14.1 | 0.33589 | 0.58865 | 10.0437 | 9.9256 | 14.2216 | 98.2784 | 0.101 |  | 6.39 | 60 | 889 | 1753 | 2075.3276 | -18.3872 | 85.1485 | 1482.1638 | 95.9519 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-07-31 | 9:05 | 22604 | 25.5 | 163 | 124 | 17.3 | 0 | 33.7 | 5.7 |  | 39.4 | 39.4 | 0.85533 | 0 | 13.5933 | 13.3939 | 12.9366 | 113.2634 | 0.11825 | 6.91 | 6.03 | 37 | 347 | 364 | 1806 | 2297.3158 | -27.2046 | 89.8352 | 1330.6579 | 97.2194 | 163 | 140 | 16 | 25.1 | 12.7 | 37.8 | 37.8 | 0.42619 | 0.66402 | 15.1866 | 14.9638 | 7.575 | 127.925 | 0.11697 | 5.95 |  | 31 | 412 | 898 | 1165 | -29.7327 | 91.4835 | 788.5 | 96.0685 | 140 | 124 | 18 | 8.5 | 5.7 | 14.2 | 14.2 | 0.33589 | 0.59859 | 10.2857 | 10.1348 | 14.6282 | 99.3718 | 0.10199 |  | 6.54 | 60 | 898 | 1806 | 2147.6491 | -18.9174 | 83.5165 | 1522.8246 | 96.06 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-08-01 | 8:15 | 22626 | 27 | 163 | 124 | 17.5 | 0 | 33.3 | 6 |  | 39.3 | 39.3 | 0.84733 | 0 | 13.4319 | 12.6609 | 12.6463 | 113.3538 | 0.11169 | 6.75 | 5.84 | 37 | 350 | 372 | 1799 | 2231.25 | -24.0272 | 90.0538 | 1301.625 | 97.1574 | 163 | 140 | 17 | 25 | 12.6 | 37.6 | 37.6 | 0.42366 | 0.66489 | 15.1261 | 14.2578 | 7.6495 | 126.8505 | 0.1124 | 5.97 |  | 31 | 415 | 906 | 1176.9048 | -29.9012 | 91.6667 | 795.9524 | 96.1053 | 140 | 124 | 18 | 8.3 | 5.9 | 14.2 | 14.2 | 0.33927 | 0.58451 | 10.0437 | 9.4671 | 14.4107 | 99.5893 | 0.095062 |  | 6.39 | 60 | 906 | 1799 | 2096.1356 | -16.5167 | 83.871 | 1501.0678 | 96.0028 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1998-08-02 | 8:00 | 22651 | 27 | 163 | 123 | 17.2 | 0 | 30.8 | 6 |  | 36.8 | 36.8 | 0.83696 | 0 | 12.4235 | 11.7104 | 11.556 | 114.244 | 0.1025 | 6.77 | 5.84 | 37 | 345 | 361 | 1735 | 2024.2 | -16.6686 | 89.7507 | 1192.6 | 96.8975 | 163 | 140 | 16 | 21.5 | 16.3 | 37.8 | 37.8 | 0.45657 | 0.56878 | 13.0084 | 12.2617 | 6.2398 | 129.2602 | 0.09486 | 5.9 |  | 32 | 408 | 882 | 903.9509 | -2.4888 | 91.1357 | 655.9755 | 95.1218 | 140 | 123 | 18 | 8.5 | 5.9 | 14.4 | 14.4 | 0.34264 | 0.59028 | 10.2857 | 9.6953 | 14.1584 | 99.3416 | 0.097595 |  | 6.3 | 59 | 882 | 1735 | 2067.678 | -19.1745 | 83.6565 | 1474.839 | 95.9996 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1998-08-03 | 8:20 | 22675 | 27 | 163 | 124 | 17.3 | 0 | 33.1 | 6 |  | 39.1 | 39.1 | 0.84655 | 0 | 13.3513 | 12.5848 | 12.0267 | 114.1733 | 0.11023 | 6.78 | 5.74 | 37 | 340 | 357 | 1788 | 2122.3333 | -18.6987 | 89.6359 | 1239.6667 | 97.0153 | 163 | 140 | 16 | 24.6 | 12.8 | 37.4 | 37.4 | 0.42366 | 0.65775 | 14.884 | 14.0296 | 7.3731 | 128.1269 | 0.1095 | 5.92 |  | 31 | 407 | 889 | 1129.625 | -27.0669 | 91.3165 | 768.3125 | 95.9652 | 140 | 124 | 18 | 8.5 | 5.6 | 14.1 | 14.1 | 0.33251 | 0.60284 | 10.2857 | 9.6953 | 14.5815 | 99.4185 | 0.09752 |  | 6.28 | 60 | 889 | 1788 | 2147.3036 | -20.0953 | 83.1933 | 1518.1518 | 96.0478 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1998-08-04 | 8:50 | 22699 | 27 | 162 | 123 | 17.1 | 0 | 31.8 | 6 |  | 37.8 | 37.8 | 0.84127 | 0 | 12.8269 | 12.0906 | 11.7165 | 113.6835 | 0.10635 | 6.85 | 5.77 | 37 | 338 | 358 | 1710 | 2059.3 | -20.4269 | 89.6648 | 1208.65 | 96.9387 | 162 | 140 | 16 | 23.7 | 13.7 | 37.4 | 37.4 | 0.43125 | 0.63369 | 14.3395 | 13.5164 | 6.9004 | 128.0996 | 0.10551 | 5.87 |  | 32 | 402 | 871 | 1042.073 | -19.641 | 91.0615 | 722.0365 | 95.5681 | 140 | 123 | 18 | 8.1 | 5.8 | 13.9 | 13.9 | 0.33251 | 0.58273 | 9.8017 | 9.239 | 13.807 | 99.693 | 0.092675 |  | 6.33 | 58 | 871 | 1710 | 2006.3966 | -17.3331 | 83.7989 | 1438.6983 | 95.9686 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1998-08-05 | 10:15 | 22724 | 27 | 164 | 126 | 17.2 | 0 | 29.7 | 5 |  | 34.7 | 34.7 | 0.85591 | 0 | 11.9798 | 11.2921 | 13.0613 | 114.7387 | 0.098416 | 6.78 | 5.75 | 37 | 344 | 366 | 1848 | 2320.26 | -25.5552 | 89.8907 | 1343.13 | 97.2452 | 164 | 141 | 16 | 21.1 | 15.9 | 37 | 37 | 0.44645 | 0.57027 | 12.7664 | 12.0335 | 6.2881 | 130.2119 | 0.092415 | 5.89 |  | 32 | 410 | 902 | 911.6226 | -1.0668 | 91.2568 | 660.8113 | 95.1575 | 141 | 126 | 18 | 8.5 | 5.4 | 13.9 | 13.9 | 0.32576 | 0.61151 | 10.2857 | 9.6953 | 15.029 | 100.471 | 0.096498 |  | 6.32 | 61 | 902 | 1848 | 2225.7963 | -20.4435 | 83.3333 | 1563.8981 | 96.0995 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1998-08-06 | 10:05 | 22748 | 27 | 163 | 124 | 17.1 | 0 | 31.5 | 6 |  | 37.5 | 37.5 | 0.84 | 0 | 12.7059 | 11.9765 | 11.8537 | 114.5463 | 0.10456 | 6.91 | 5.86 | 37 | 339 | 364 | 1803 | 2080.75 | -15.4049 | 89.8352 | 1222.375 | 96.9731 | 163 | 141 | 16 | 22.9 | 14.3 | 37.2 | 37.2 | 0.43463 | 0.61559 | 13.8555 | 13.0601 | 6.8066 | 129.1934 | 0.10109 | 5.91 |  | 31 | 409 | 896 | 1014.3287 | -13.2063 | 91.4835 | 711.6643 | 95.644 | 141 | 124 | 18 | 8.5 | 5.6 | 14.1 | 14.1 | 0.33251 | 0.60284 | 10.2857 | 9.6953 | 14.6871 | 99.8129 | 0.097134 |  | 6.36 | 61 | 896 | 1803 | 2163.4107 | -19.9895 | 83.2418 | 1529.7054 | 96.0123 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1998-08-07 | 1010 | 22772 | 27 | 163 | 125 | 17 | 0 | 32.6 | 6 |  | 38.6 | 38.6 | 0.84456 | 0 | 13.1496 | 12.3947 | 12.2278 | 114.7722 | 0.10799 | 6.69 | 5.76 | 37 | 346 | 366 | 1809 | 2153.5667 | -19.0474 | 89.8907 | 1259.7833 | 97.063 | 163 | 141 | 16 | 23.8 | 13.5 | 37.3 | 37.3 | 0.42872 | 0.63807 | 14.4 | 13.5734 | 7.1873 | 128.8127 | 0.10537 | 5.91 |  | 31 | 413 | 899 | 1086.4519 | -20.8512 | 91.5301 | 749.7259 | 95.8652 | 141 | 125 | 18 | 8.7 | 5.6 | 14.3 | 14.3 | 0.33589 | 0.60839 | 10.5277 | 9.9234 | 14.8895 | 100.1105 | 0.099124 |  | 6.35 | 61 | 899 | 1809 | 2200.8929 | -21.6635 | 83.3333 | 1549.9464 | 96.0644 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1998-08-08 | 7:30 | 22793 | 27 | 164 | 125 | 17 | 0 | 29.8 | 6 |  | 35.8 | 35.8 | 0.8324 | 0 | 12.0202 | 11.3302 | 11.6692 | 115.8308 | 0.097816 | 6.81 | 5.82 | 37 | 348 | 372 | 1837 | 2035.8333 | -10.8238 | 90.0538 | 1203.9167 | 96.9267 | 164 | 141 | 16 | 20.7 | 16.4 | 37.1 | 37.1 | 0.45151 | 0.55795 | 12.5244 | 11.8054 | 6.2797 | 130.2203 | 0.090657 | 5.96 |  | 32 | 417 | 914 | 902.9451 | 1.2095 | 91.3978 | 659.9726 | 95.1513 | 141 | 125 | 18 | 8.4 | 5.7 | 14.1 | 14.1 | 0.3342 | 0.59574 | 10.1647 | 9.5812 | 14.8153 | 100.1847 | 0.095635 |  | 6.4 | 61 | 914 | 1837 | 2171.0526 | -18.1847 | 83.6022 | 1542.5263 | 96.0454 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1998-08-09 | 7:30 | 22818 | 27 | 164 | 124 | 17 | 0 | 30.1 | 6 |  | 36.1 | 36.1 | 0.8338 | 0 | 12.1412 | 11.4442 | 11.4372 | 115.5628 | 0.09903 | 6.74 | 5.87 | 37 | 351 | 363 | 1775 | 1998.4333 | -12.5878 | 89.8072 | 1180.7167 | 96.8663 | 164 | 141 | 16 | 21.8 | 15.3 | 37.1 | 37.1 | 0.44223 | 0.5876 | 13.1899 | 12.4328 | 6.5243 | 129.9757 | 0.095655 | 5.95 |  | 32 | 413 | 897 | 955.8627 | -6.5622 | 91.1846 | 684.4314 | 95.3246 | 141 | 124 | 18 | 8.2 | 5.6 | 13.8 | 13.8 | 0.32745 | 0.5942 | 9.9227 | 9.3531 | 14.498 | 100.002 | 0.093529 |  | 6.34 | 60 | 897 | 1775 | 2122.6071 | -19.5835 | 83.4711 | 1509.8036 | 96.026 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1998-08-10 | 8:50 | 22843 | 27 | 164 | 126 | 17 | 0 | 29.3 | 5 |  | 34.3 | 34.3 | 0.85423 | 0 | 11.8185 | 11.1401 | 13.0083 | 114.9917 | 0.096877 | 6.93 | 5.94 | 37 | 342 | 368 | 1845 | 2307.66 | -25.0764 | 89.9457 | 1337.83 | 97.2343 | 164 | 142 | 16 | 20.9 | 16.2 | 37.1 | 37.1 | 0.44982 | 0.56334 | 12.6454 | 11.9195 | 6.3006 | 130.6994 | 0.091198 | 5.96 |  | 31 | 414 | 910 | 908.1173 | 0.20689 | 91.5761 | 661.0586 | 95.3106 | 142 | 126 | 18 | 8.3 | 5.5 | 13.8 | 13.8 | 0.32576 | 0.60145 | 10.0437 | 9.4671 | 14.8961 | 101.1039 | 0.093638 |  | 6.49 | 61 | 910 | 1845 | 2191.2182 | -18.7652 | 83.4239 | 1550.6091 | 96.0661
[11 empty] | 1998-08-11 | 9:45 | 22868 | 27 | 164 | 125 | 17 | 0 | 31.4 | 6 |  | 37.4 | 37.4 | 0.83957 | 0 | 12.6655 | 11.9385 | 12.1882 | 115.3118 | 0.10353 | 6.98 | 5.97 | 37 | 352 | 374 | 1820 | 2137.6333 | -17.4524 | 90.107 | 1255.8167 | 97.0537 | 164 | 141 | 16 | 23.3 | 13.8 | 37.1 | 37.1 | 0.42957 | 0.62803 | 14.0975 | 13.2882 | 7.0633 | 129.4367 | 0.10266 | 5.97 |  | 31 | 414 | 906 | 1060.6594 | -17.0706 | 91.7112 | 737.3297 | 95.7956 | 141 | 125 | 18 | 8 | 5.6 | 13.6 | 13.6 | 0.32407 | 0.58824 | 9.6807 | 9.125 | 14.4857 | 100.5143 | 0.090783 |  | 6.53 | 61 | 906 | 1820 | 2113.1429 | -16.1068 | 83.6898 | 1509.5714 | 95.9591
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on E23: S Allgeier (10/2/99): Reviewer changed width from 30 feet to 15 feet -- a value more typical for this membrane.
Note on BL7: C. Rice: Stage 1 concentrate pH was not measured.
Note on CJ7: C. Rice: Stage 2 influent pH was not measured.
Note on FF40: C. Rice: Consultant stated that although the feed TCAA concentrations are high for weeks 18 and 20, the analyst could not find any errors with the data.
Note on FZ40: C. Rice: Consultant stated that although the feed TCAA concentrations are high for weeks 18 and 20, the analyst could not find any errors with the data.

## ESNA. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Boca Raton | Membrane manufacturer | Hydranautics | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 216 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  |  |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.64 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.55 | [6 empty] | System recovery during sample collection (decimal) | 0.84 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.58 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL4500130 | Membrane trade name | ESNA | Temperature normalized MTCW (gfd/psi) | 0.32 | Calcium Hardness (mg/L as CaCO3) | 260 | Dual Media Filtration | Silica/Garnet | Pilot Scale |  |  | time | Influent | PI | Pc | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 36.9 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 23.5 | [6 empty] | System feed flow rate during sample collection (gpm) | 38.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 21.1 | [6 empty] | System feed flow rate during sample collection (gpm) | 36.9 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 21.4 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 8
Water Industry Data Base Number (optional) | NA | Membrane element model number | 4040-UHA-ESNA |  |  | LSI | 0.09 | Scale Inhibitor Addition | Calgon EL-5600 4.0 mg/l | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 36.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 36.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 38.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 38.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 36.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 36.9 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 100-180 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 1 | pH Adjustment | Sulfuric Acid to pH 6.0-6.4 | Pilot Scale | 1998-08-12 | 8:15 | 22890 | 27 | 164 | 124 | 16.8 | 0 | 31.7 | 6 |  | 37.7 | 37.7 | 0.84085 | 0 | 12.7866 | 12.0526 | 12.0903 | 115.1097 | 0.1047 | 6.79 | 5.86 | 37 | 346 | 369 | 1758 | 2123.0667 | -20.766 | 89.9729 | 1246.0333 | 97.0306 | 164 | 141 | 16 | 23.3 | 14 | 37.3 | 37.3 | 0.43294 | 0.62466 | 14.0975 | 13.2882 | 7.0354 | 129.4646 | 0.10264 | 5.98 |  | 31 | 415 | 899 | 1054.0857 | -17.2509 | 91.5989 | 734.5429 | 95.7797 | 141 | 124 | 18 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 9.5812 | 14.4655 | 100.0345 | 0.095779 |  | 6.36 | 60 | 899 | 1758 | 2114.1034 | -20.2562 | 83.7398 | 1506.5517 | 96.0174 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamid | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 1 | Cartridge Filtration | 5um exclusion size | Pilot Scale | 1998-08-13 | 9:10 | 22915 | 27 | 164 | 125 | 16.8 | 0 | 30.1 | 6 |  | 36.1 | 36.1 | 0.8338 | 0 | 12.1412 | 11.4442 | 11.6477 | 116.0523 | 0.098613 | 6.8 | 5.85 | 37 | 350 | 369 | 1773 | 2034.5333 | -14.7509 | 89.9729 | 1201.7667 | 96.9212 | 164 | 142 | 16 | 21.9 | 15.2 | 37.1 | 37.1 | 0.44138 | 0.5903 | 13.2504 | 12.4898 | 6.5203 | 130.4797 | 0.095722 | 5.85 |  | 31 | 410 | 896 | 956.0592 | -6.703 | 91.5989 | 683.0296 | 95.4614 | 142 | 125 | 18 | 8.1 | 5.7 | 13.8 | 13.8 | 0.32914 | 0.58696 | 9.8017 | 9.239 | 14.3 | 101.2 | 0.091295 |  | 6.38 | 60 | 896 | 1773 | 2084 | -17.5409 | 83.7398 | 1490 | 95.9732 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 0.01 |  |  |  | 1998-08-14 | 8:13 | 22938 | 27 | 164 | 125 | 16.9 | 0 | 30.5 | 6 |  | 36.5 | 36.5 | 0.83562 | 0 | 12.3025 | 11.5963 | 11.7937 | 115.8063 | 0.10014 | 6.79 | 5.52 | 40 | 335 | 373 | 1804 | 2065.75 | -14.5094 | 89.2761 | 1219.375 | 96.7196 | 164 | 142 | 16 | 22.2 | 14.9 | 37.1 | 37.1 | 0.43885 | 0.59838 | 13.4319 | 12.6609 | 6.7007 | 130.2993 | 0.097168 | 5.42 |  | 34 | 418 | 906 | 990.1342 | -9.2863 | 90.8847 | 704.0671 | 95.1709 | 142 | 125 | 18 | 8.2 | 5.6 | 13.8 | 13.8 | 0.32745 | 0.5942 | 9.9227 | 9.3531 | 14.5846 | 100.9154 | 0.092682 |  | 5.9 | 64 | 906 | 1804 | 2138.9286 | -18.5659 | 82.8418 | 1522.4643 | 95.7963 | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 (dup) | CF-sys-30 (dup) | CC-sys-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 (dup) | CI-s1-30 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophylic | Number of elements per pressure vessel, Ne | 7 | Total aluminum (mg/L) | 1 |  |  |  | 1998-08-15 | 9:05 | 22963 | 27 | 164 | 124 | 16.7 | 0 | 32.3 | 6 |  | 38.3 | 38.3 | 0.84334 | 0 | 13.0286 | 12.2807 | 12.404 | 114.896 | 0.10689 | 6.78 | 5.39 | 40 | 347 | 376 | 1795 | 2184.8 | -21.7159 | 89.3617 | 1280.4 | 96.876 | 164 | 140 | 16 | 24 | 13.4 | 37.4 | 37.4 | 0.42872 | 0.64171 | 14.521 | 13.6874 | 7.3167 | 128.6833 | 0.10637 | 5.33 |  | 35 | 421 | 913 | 1112.3433 | -21.8339 | 90.6915 | 766.6716 | 95.4348 | 140 | 124 | 18 | 8.3 | 5.6 | 13.9 | 13.9 | 0.32914 | 0.59712 | 10.0437 | 9.4671 | 14.7643 | 99.2357 | 0.095401 |  | 5.78 | 65 | 913 | 1795 | 2169.8571 | -20.8834 | 82.7128 | 1541.4286 | 95.7831 | Sampling date | MM/DD/YY | 1998-08-19 | 1998-08-19 | 1998-08-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-19 | 1998-08-19 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-02 | 1998-09-02 | 1998-09-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-02 | 1998-09-02 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-16 | 1998-09-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-16 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 13
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 4 | Fluoride (mg/L) | 0.231 |  |  |  | 1998-08-16 | 7:50 | 22986 | 27 | 164 | 125 | 16.8 | 0 | 32.1 | 6 |  | 38.1 | 38.1 | 0.84252 | 0 | 12.9479 | 12.2046 | 12.4582 | 115.2417 | 0.1059 | 6.86 | 5.38 | 41 | 343 | 380 | 1788 | 2193.65 | -22.6874 | 89.2105 | 1286.825 | 96.8139 | 164 | 141 | 16 | 23.7 | 13.4 | 37.1 | 37.1 | 0.42619 | 0.63881 | 14.3395 | 13.5164 | 7.1604 | 129.3396 | 0.1045 | 5.25 |  | 41 | 421 | 906 | 1093.0896 | -20.6501 | 89.2105 | 757.0448 | 94.5842 | 141 | 125 | 18 | 8.3 | 5.6 | 13.9 | 13.9 | 0.32914 | 0.59712 | 10.0437 | 9.4671 | 14.6424 | 100.3576 | 0.094334 |  | 5.78 | 65 | 906 | 1788 | 2152.4821 | -20.3849 | 82.8947 | 1529.2411 | 95.7495 | Sampling time | hh:mm | 7:05 | 7:10 | 7:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:20 | 7:10 | --- | --- | --- | --- | Sampling time | hh:mm | 7:15 | 7:25 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:35 | 7:25 | --- | --- | --- | --- | Sampling time | hh:mm | 7:50 | 7:55 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:05 | 7:55 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881 (May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 2 | Phosphate (mg/L) | <0.1 |  |  |  | 1998-08-17 | 8:30 | 23011 | 27 | 164 | 124 | 16.8 | 0 | 32 | 6 |  | 38 | 38 | 0.84211 | 0 | 12.9076 | 12.1666 | 12.32 | 114.88 | 0.10591 | 6.79 | 5.36 | 41 | 347 | 377 | 1756 | 2169 | -23.5194 | 89.1247 | 1273 | 96.7793 | 164 | 140 | 16 | 23.5 | 13.5 | 37 | 37 | 0.42619 | 0.63514 | 14.2185 | 13.4023 | 7.2196 | 128.7804 | 0.10407 | 5.34 |  | 35 | 421 | 903 | 1092.9259 | -21.0328 | 90.7162 | 756.963 | 95.3763 | 140 | 124 | 18 | 8.4 | 5.8 | 14.2 | 14.2 | 0.33758 | 0.59155 | 10.1647 | 9.5812 | 14.4483 | 99.5517 | 0.096244 |  | 5.64 | 65 | 903 | 1756 | 2116.6552 | -20.5384 | 82.7586 | 1509.8276 | 95.6949 | Operation time | hh.hh | 23057 | 23057 | 23057 | --- | --- | --- | --- | --- | Operation time | hh.hh | 23057 | 23057 | --- | --- | --- | --- | Operation time | hh.hh | 23389 | 23389 | 23389 | --- | --- | --- | --- | --- | Operation time | hh.hh | 23389 | 23389 | --- | --- | --- | --- | Operation time | hh.hh | 23725 | 23725 | 23725 | --- | --- | --- | --- | --- | Operation time | hh.hh | 23725 | 23725 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.88542 | Sulfate (mg/L) | 17.1 |  |  |  | 1998-08-18 | 7:50 | 23034 | 27 | 164 | 125 | 16.8 | 0 | 31.7 | 6 |  | 37.7 | 37.7 | 0.84085 | 0 | 12.7866 | 12.0526 | 12.3817 | 115.3183 | 0.10452 | 6.85 | 5.35 | 41 | 345 | 381 | 1792 | 2177.3333 | -21.503 | 89.2388 | 1279.1667 | 96.7948 | 164 | 141 | 16 | 23.4 | 13.6 | 37 | 37 | 0.42704 | 0.63243 | 14.158 | 13.3453 | 7.1993 | 129.3007 | 0.10321 | 5.35 |  | 35 | 422 | 906 | 1087.8676 | -20.0737 | 90.8136 | 754.9338 | 95.3638 | 141 | 125 | 18 | 8.2 | 5.6 | 13.8 | 13.8 | 0.32745 | 0.5942 | 9.9227 | 9.3531 | 14.5673 | 100.4327 | 0.093128 |  | 5.69 | 65 | 906 | 1792 | 2137.4643 | -19.2781 | 82.9396 | 1521.7321 | 95.7286 | pH | --- | 5.54 | 5.74 | 6.14 | --- | --- | --- | --- | --- | pH | --- | 5.52 | 5.73 | --- | --- | --- | --- | pH | --- | 5.38 | 6.23 | 6.64 | --- | --- | --- | --- | --- | pH | --- | 5.47 | 6.19 | --- | --- | --- | --- | pH | --- | 5.21 | 5.68 | 5.96 | --- | --- | --- | --- | --- | pH | --- | 5.38 | 5.61 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 17
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 6.1979 | Calcium (mg/L) | 97.9 |  |  |  | 1998-08-19 | 7:35 | 23058 | 27 | 164 | 124 | 16.7 | 0 | 32 | 6 |  | 38 | 38 | 0.84211 | 0 | 12.9076 | 12.1666 | 12.3933 | 114.9067 | 0.10588 | 6.79 | 5.5 | 39 | 349 | 377 | 1770 | 2179.6667 | -23.145 | 89.6552 | 1278.3333 | 96.9492 | 164 | 141 | 16 | 23.5 | 13.4 | 36.9 | 36.9 | 0.4245 | 0.63686 | 14.2185 | 13.4023 | 7.2259 | 129.2741 | 0.10367 | 5.59 |  | 33 | 418 | 899 | 1093.1866 | -21.6003 | 91.2467 | 755.5933 | 95.6326 | 141 | 124 | 18 | 8.4 | 5.7 | 14.1 | 14.1 | 0.3342 | 0.59574 | 10.1647 | 9.5812 | 14.5547 | 99.9453 | 0.095865 |  | 5.97 | 61 | 899 | 1770 | 2133.9474 | -20.562 | 83.8196 | 1516.4737 | 95.9775 | Temperature | oC | 26 | 26.2 | 26.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26.2 | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26.4 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | --- | --- | --- | --- | Temperature | oC | 26 | 25.8 | 26.2 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 25.8 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 85 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 24.7917 | Barium (mg/L) | 0.5 |  |  |  | 1998-08-20 | 10:30 | 23085 | 27 | 164 | 124 | 16.6 | 0 | 30.9 | 6 |  | 36.9 | 36.9 | 0.8374 | 0 | 12.4639 | 11.7484 | 12.3695 | 115.0305 | 0.10213 | 6.86 | 5.59 | 39 | 356 | 385 | 1799 | 2166.9 | -20.4503 | 89.8701 | 1275.95 | 96.9435 | 164 | 140 | 16 | 22.7 | 14.2 | 36.9 | 36.9 | 0.43125 | 0.61518 | 13.7345 | 12.946 | 7.0352 | 128.9648 | 0.10038 | 5.64 |  | 33 | 424 | 917 | 1049.0493 | -14.4001 | 91.4286 | 736.5246 | 95.5195 | 140 | 124 | 17 | 8.1 | 5.7 | 13.8 | 13.8 | 0.32914 | 0.58696 | 9.8017 | 9.239 | 14.625 | 100.375 | 0.092045 |  | 6.06 | 62 | 917 | 1799 | 2132 | -18.5103 | 83.8961 | 1524.5 | 95.9331 | Alkalinity | mg/L as CaCO3 | 14 | 36 | 170 | 160.6667 | 5.4902 | 61.1111 | 98.3333 | 85.7627 | Alkalinity | mg/L as CaCO3 | 14 | 38 | 80.0896 | 61.1111 | 59.0448 | 76.2892 | Alkalinity | mg/L as CaCO3 | 14 | 62 | 298 | 296.3529 | 0.5527 | 77.4194 | 179.1765 | 92.1865 | Alkalinity | mg/L as CaCO3 | 12 | 60 | 118.2069 | 80.6452 | 89.1034 | 86.5325 | Alkalinity | mg/L as CaCO3 | 12 | 24 | 78 | 87 | -11.5385 | 50 | 55.5 | 78.3784 | Alkalinity | mg/L as CaCO3 | 12 | 22 | 35.8065 | 50 | 28.9032 | 58.4821 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 30 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.3958 | Strontium (mg/L) | 0.2 |  |  |  | 1998-08-21 | 8:35 | 23107 | 27 | 164 | 125 | 16.4 | 0 | 29.1 | 6 |  | 35.1 | 35.1 | 0.82906 | 0 | 11.7378 | 11.064 | 11.508 | 116.592 | 0.094895 | 6.7 | 5.48 | 39 | 358 | 375 | 1824 | 2004.6 | -9.9013 | 89.6 | 1189.8 | 96.7221 | 164 | 141 | 16 | 21.2 | 15.3 | 36.5 | 36.5 | 0.43716 | 0.58082 | 12.8269 | 12.0906 | 6.585 | 129.915 | 0.093065 | 5.61 |  | 34 | 423 | 921 | 962.0065 | -4.4524 | 90.9333 | 692.5033 | 95.0903 | 141 | 125 | 17 | 7.8 | 5.5 | 13.3 | 13.3 | 0.31732 | 0.58647 | 9.4387 | 8.8968 | 14.6811 | 101.3189 | 0.08781 |  | 5.92 | 62 | 921 | 1824 | 2139.2182 | -17.2817 | 83.4667 | 1530.1091 | 95.948 | Total dissolved solids | mg/L | 34 | 373 | 1495 | 2294 | -53.4448 | 90.8847 | 1333.5 | 97.4503 | Total dissolved solids | mg/L | 19 | 373 | 993.8209 | 94.9062 | 683.4104 | 97.2198 | Total dissolved solids | mg/L | 36 | 367 | 1481 | 1983.0588 | -33.9 | 90.1907 | 1175.0294 | 96.9362 | Total dissolved solids | mg/L | 28 | 364 | 771.4483 | 92.3706 | 567.7241 | 95.068 | Total dissolved solids | mg/L | 36.6 | 384 | 1510 | 2207.85 | -46.2152 | 90.4688 | 1295.925 | 97.1758 | Total dissolved solids | mg/L | 29 | 383 | 871.7484 | 92.4479 | 627.3742 | 95.3776 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 71 | Permeate flow rate from system, Qp-sys (gpm) | 37.1875 | Reactive silica (mg/L as SiO2) | 78 |  |  |  | 1998-08-22 | 8:20 | 23130 | 27 | 164 | 125 | 16.4 | 0 | 29 | 6 |  | 35 | 35 | 0.82857 | 0 | 11.6975 | 11.026 | 11.4117 | 116.6883 | 0.094491 | 6.74 | 5.47 | 39 | 353 | 373 | 1834 | 1987.3333 | -8.3606 | 89.5442 | 1180.1667 | 96.6954 | 164 | 141 | 16 | 20.8 | 15.5 | 36.3 | 36.3 | 0.43716 | 0.573 | 12.5849 | 11.8625 | 6.6003 | 129.8997 | 0.09132 | 5.62 |  | 33 | 428 | 931 | 958.0645 | -2.907 | 91.1528 | 693.0323 | 95.2383 | 141 | 125 | 17 | 8.1 | 5.5 | 13.6 | 13.6 | 0.32239 | 0.59559 | 9.8017 | 9.239 | 15.0716 | 100.9284 | 0.09154 |  | 5.96 | 63 | 931 | 1834 | 2209.3273 | -20.465 | 83.1099 | 1570.1636 | 95.9877 | Total hardness | mg/L as CaCO3 | 20 | 260 | 1420 | 1620 | -14.0845 | 92.3077 | 940 | 97.8723 | Total hardness | mg/L as CaCO3 | 14 | 270 | 718.9552 | 94.6154 | 494.4776 | 97.1687 | Total hardness | mg/L as CaCO3 | 18 | 244 | 1280 | 1347.4118 | -5.2665 | 92.623 | 795.7059 | 97.7379 | Total hardness | mg/L as CaCO3 | 16 | 258 | 551.4598 | 93.4426 | 404.7299 | 96.0467 | Total hardness | mg/L as CaCO3 | 18 | 250 | 1240 | 1468 | -18.3871 | 92.8 | 859 | 97.9045 | Total hardness | mg/L as CaCO3 | 14 | 252 | 580.5935 | 94.4 | 416.2968 | 96.637 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | Feed flow rate to system, QF-sys (gpm) | 43.75 | Turbidity (ntu) | 0.95 |  |  |  | 1998-08-23 | 8:05 | 23154 | 27 | 163 | 124 | 16.4 | 0 | 29.3 | 5 |  | 34.3 | 34.3 | 0.85423 | 0 | 11.8185 | 11.1401 | 13.4013 | 113.6987 | 0.097979 | 6.79 | 5.5 | 39 | 347 | 380 | 1805 | 2378.26 | -31.7596 | 89.7368 | 1379.13 | 97.1721 | 163 | 140 | 16 | 21.2 | 15.5 | 36.7 | 36.7 | 0.44054 | 0.57766 | 12.8269 | 12.0906 | 6.5166 | 128.9834 | 0.093737 | 5.58 |  | 33 | 420 | 913 | 949.3161 | -3.9777 | 91.3158 | 684.6581 | 95.1801 | 140 | 124 | 17 | 8 | 5.5 | 13.5 | 13.5 | 0.3207 | 0.59259 | 9.6807 | 9.125 | 14.6991 | 100.3009 | 0.090976 |  | 6.01 | 62 | 913 | 1805 | 2150.8182 | -19.1589 | 83.6842 | 1531.9091 | 95.9528 | Calcium hardness | mg/L as CaCO3 | 14 | 240 | 1310 | 1520.6667 | -16.0814 | 94.1667 | 880.3333 | 98.4097 | Calcium hardness | mg/L as CaCO3 | 10 | 260 | 698.4328 | 95.8333 | 479.2164 | 97.9133 | Calcium hardness | mg/L as CaCO3 | 12 | 224 | 980 | 1259.0588 | -28.4754 | 94.6429 | 741.5294 | 98.3817 | Calcium hardness | mg/L as CaCO3 | 10 | 234 | 505.6322 | 95.5357 | 369.8161 | 97.296 | Calcium hardness | mg/L as CaCO3 | 12 | 234 | 1180 | 1399.5 | -18.6017 | 94.8718 | 816.75 | 98.5308 | Calcium hardness | mg/L as CaCO3 | 12 | 230 | 530.9806 | 94.8718 | 380.4903 | 96.8462 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 6.5625 | SDI | 4 |  |  |  | 1998-08-24 | 8:24 | 23179 | 27 | 163 | 124 | 16.2 | 0 | 29.7 | 5 |  | 34.7 | 34.7 | 0.85591 | 0 | 11.9798 | 11.2921 | 13.7759 | 113.5241 | 0.099469 | 6.76 | 5.48 | 39 | 356 | 386 | 1827 | 2447.18 | -33.9453 | 89.8964 | 1416.59 | 97.2469 | 163 | 140 | 15 | 22 | 14.3 | 36.3 | 36.3 | 0.42704 | 0.60606 | 13.3109 | 12.5468 | 6.9 | 129.6 | 0.096812 | 5.6 |  | 33 | 423 | 921 | 1023 | -11.0749 | 91.4508 | 723 | 95.4357 | 140 | 124 | 17 | 7.6 | 5.4 | 13 | 13 | 0.31057 | 0.58462 | 9.1966 | 8.6687 | 14.6348 | 100.3652 | 0.086372 |  | 5.98 | 62 | 921 | 1827 | 2129.963 | -16.5825 | 83.9378 | 1525.4815 | 95.9357 | Turbidity | ntu | 0.056 | 0.104 | 0.36 | 0.376 | -4.4444 | 46.1538 | 0.24 | 76.6667 | Turbidity | ntu | 0.04 | 0.101 | 0.20798 | 61.5385 | 0.15449 | 74.1082 | Turbidity | ntu | 0.046 | 0.145 | 7.94 | 0.62835 | 92.0862 | 68.2759 | 0.38668 | 88.1037 | Turbidity | ntu | 0.054 | 0.139 | 0.24207 | 62.7586 | 0.19054 | 71.6591 | Turbidity | ntu | 0.06 | 0.75 | 0.35 | 4.3725 | -1149.2857 | 92 | 2.5612 | 97.6574 | Turbidity | ntu | 0.05 | 0.1 | 0.16903 | 93.3333 | 0.13452 | 62.8297 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI |  |  |  |  | 1998-08-25 | 8:05 | 23202 | 27 | 158 | 124 | 17.9 | 0 | 30.6 | 5 | X | 35.6 | 35.6 | 0.85955 | 0 | 12.3429 | 11.6343 | 13.9664 | 109.1336 | 0.10661 | 6.81 | 5.49 | 39 | 355 | 383 | 1816 | 2488.28 | -37.0198 | 89.8172 | 1435.64 | 97.2834 | 158 | 140 | 16 | 21.8 | 17.3 | 39.1 | 39.1 | 0.47598 | 0.55754 | 13.1899 | 12.4328 | 6.3083 | 126.6917 | 0.098134 | 5.6 |  | 33 | 420 | 917 | 907.6647 | 1.018 | 91.3838 | 663.8324 | 95.0289 | 140 | 124 | 17 | 8.1 | 6.1 | 14.2 | 14.2 | 0.34264 | 0.57042 | 9.8017 | 9.239 | 14.2266 | 100.7734 | 0.091681 |  | 6 | 62 | 917 | 1816 | 2052.3279 | -13.0136 | 83.812 | 1484.6639 | 95.824 | Ammonia | mg NH3-N / L | 0.14 | 0.5 | 2.24 | 2.54 | -13.3929 | 72 | 1.52 | 90.7895 | Total organic carbon | mg/L | 0.55 | 12.2 | 32.631 | 96.0993 | 22.4155 | 97.5463 | Ammonia | mg NH3-N / L | 0.14 | 0.51 | 2.26 | 2.3165 | -2.4987 | 72.549 | 1.4132 | 90.0937 | Total organic carbon | mg/L | BMRL | 11.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.13 | 0.47 | 2.24 | 2.255 | -0.66964 | 72.3404 | 1.3625 | 90.4587 | Total organic carbon | mg/L | BMRL | 12.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-08-26 | 9:15 | 23223 | 27 | 157 | 119 | 18.1 | 0 | 30.6 | 6 |  | 36.6 | 36.6 | 0.83607 | 0 | 12.3429 | 11.6343 | 12.1055 | 107.7945 | 0.10793 | 6.83 | 5.47 | 44 | 354 | 385 | 1817 | 2124.1 | -16.9015 | 88.5714 | 1254.55 | 96.4928 | 157 | 135 | 17 | 21.9 | 16.9 | 38.8 | 38.8 | 0.47008 | 0.56443 | 13.2504 | 12.4898 | 6.3775 | 122.6225 | 0.10186 | 5.56 |  | 37 | 424 | 902 | 925.497 | -2.605 | 90.3896 | 674.7485 | 94.5165 | 135 | 119 | 19 | 8.7 | 5.8 | 14.5 | 14.5 | 0.34264 | 0.6 | 10.5277 | 9.9234 | 14.5425 | 93.4575 | 0.10618 |  | 5.93 | 71 | 902 | 1817 | 2148.5 | -18.2444 | 81.5584 | 1525.25 | 95.345 | Total organic carbon | mg/L | BMRL | 14.1 | 66.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.441 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 11.3 | 75.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.43 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12 | 76.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.43 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Glades Road Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 15 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 22.5 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-08-27 | 9:15 | 23247 | 27 | 159 | 121 | 19.2 | 0 | 32.3 | 6 |  | 38.3 | 38.3 | 0.84334 | 0 | 13.0286 | 12.2807 | 12.6255 | 108.1745 | 0.11353 | 6.86 | 5.53 | 42 | 358 | 384 | 1817 | 2225.1 | -22.4601 | 89.0625 | 1304.55 | 96.7805 | 159 | 137 | 17 | 23.4 | 15.3 | 38.7 | 38.7 | 0.45573 | 0.60465 | 14.158 | 13.3453 | 6.8824 | 124.1176 | 0.10752 | 5.61 |  | 36 | 426 | 898 | 1022.4706 | -13.8609 | 90.625 | 724.2353 | 95.0292 | 137 | 121 | 21 | 8.8 | 5.8 | 14.6 | 14.6 | 0.34433 | 0.60274 | 10.6487 | 10.0375 | 14.6317 | 93.3683 | 0.1075 |  | 5.97 | 66 | 898 | 1817 | 2160.3448 | -18.8962 | 82.8125 | 1529.1724 | 95.6839 | UV254 | cm-1 | BMRL | 0.433 | 2.527 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6148 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.442 | 2.495 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7719 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.431 | 2.51 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5246 | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0022 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 8.3333 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-08-28 | 9:00 | 23270 | 27 | 154 | 116 | 18 | 0 | 30.3 | 6 |  | 36.3 | 36.3 | 0.83471 | 0 | 12.2218 | 11.5203 | 11.8087 | 105.1912 | 0.10952 | 6.75 | 5.76 | 42 | 356 | 377 | 1781 | 2068.75 | -16.1567 | 88.8594 | 1222.875 | 96.5655 | 154 | 132 | 16 | 21.4 | 20 | 41.4 | 41.4 | 0.51818 | 0.51691 | 12.9479 | 12.2046 | 5.9711 | 121.0289 | 0.10084 | 5.52 |  | 36 | 425 | 881 | 841.23 | 4.5142 | 90.4509 | 633.115 | 94.3138 | 132 | 116 | 20 | 8.8 | 6.2 | 15 | 15 | 0.35783 | 0.58667 | 10.6487 | 10.0375 | 13.9681 | 90.0319 | 0.11149 |  | 6.06 | 64 | 881 | 1781 | 2040.6129 | -14.5768 | 83.0239 | 1460.8065 | 95.6189 | SUVA | L/(mg*m) | NR | 3.0709 | 3.7886 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.9115 | 3.3134 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5917 | 3.2768 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | SOFT | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1998-08-29 | 9:50 | 23295 | 27 | 158 | 118 | 18.7 | 0 | 32.1 | 6 |  | 38.1 | 38.1 | 0.84252 | 0 | 12.9479 | 12.2046 | 11.9437 | 107.3563 | 0.11368 | 6.9 | 5.82 | 38 | 358 | 363 | 1688 | 2101.75 | -24.5113 | 89.5317 | 1232.375 | 96.9165 | 158 | 135 | 17 | 22.9 | 16 | 38.9 | 38.9 | 0.46332 | 0.58869 | 13.8555 | 13.0601 | 6.5708 | 122.9292 | 0.10624 | 5.96 |  | 33 | 416 | 871 | 964.1688 | -10.6968 | 90.9091 | 690.0844 | 95.218 | 135 | 118 | 21 | 9.1 | 6.4 | 15.5 | 15.5 | 0.36965 | 0.5871 | 11.0118 | 10.3796 | 13.8757 | 91.6243 | 0.11328 |  | 6.32 | 60 | 871 | 1688 | 2024.1406 | -19.9135 | 83.4711 | 1447.5703 | 95.8551 | Bromide | mg/L | 30 | 176 | --- | 1003.3333 | --- | 82.9545 | 589.6667 | 94.9124 | [8 empty] | Bromide | mg/L | 33 | 185 | --- | 927.1176 | --- | 82.1622 | 556.0588 | 94.0654 | [8 empty] | Bromide | mg/L | 37 | 179 | --- | 924.5 | --- | 79.3296 | 551.75 | 93.2941 | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 306 | Purchase price for an equivalent 8" x 40 " element ($) | $895 / quantity discount | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-08-30 | 8:20 | 23318 | 27 | 157 | 118 | 19.5 | 0 | 31.4 | 6 |  | 37.4 | 37.4 | 0.83957 | 0 | 12.6655 | 11.9385 | 12.2967 | 105.7033 | 0.11294 | 6.77 | 5.7 | 39 | 356 | 379 | 1714 | 2158.3333 | -25.9238 | 89.7098 | 1268.6667 | 96.9259 | 157 | 135 | 17 | 22.5 | 16.2 | 38.7 | 38.7 | 0.46332 | 0.5814 | 13.6134 | 12.832 | 6.5236 | 122.4764 | 0.10477 | 5.91 |  | 33 | 418 | 874 | 952.7222 | -9.0071 | 91.2929 | 685.3611 | 95.185 | 135 | 118 | 22 | 8.8 | 6.2 | 15 | 15 | 0.35783 | 0.58667 | 10.6487 | 10.0375 | 13.9168 | 90.5832 | 0.11081 |  | 6.2 | 60 | 874 | 1714 | 2029.3548 | -18.3988 | 84.1689 | 1451.6774 | 95.8669 | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 21 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4500130 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -10.5 | [5 empty] | 1998-08-31 | 11:10 | 23345 | 28 | 158 | 120 | 18.6 | 0 | 30.6 | 6 |  | 36.6 | 36.6 | 0.83607 | 0 | 12.3429 | 11.2955 | 11.9635 | 108.4365 | 0.10417 | 6.88 | 5.8 | 38 | 350 | 375 | 1765 | 2093.7 | -18.6232 | 89.8667 | 1234.35 | 96.9215 | 158 | 136 | 17 | 21.5 | 17.1 | 38.6 | 38.6 | 0.47008 | 0.55699 | 13.0084 | 11.9045 | 6.2215 | 123.7785 | 0.096176 | 5.91 |  | 32 | 414 | 877 | 894.2924 | -1.9718 | 91.4667 | 654.1462 | 95.1081 | 136 | 120 | 21 | 9 | 5.9 | 14.9 | 14.9 | 0.35108 | 0.60403 | 10.8908 | 9.9666 | 14.4014 | 92.5986 | 0.10763 |  | 6.31 | 60 | 877 | 1765 | 2123.2712 | -20.2987 | 84 | 1500.1356 | 96.0004 | SDS-Free Cl2 residual | mg/L | 0.6 | 0.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.63 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.4 | 0.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.7 | 0.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -2.3333 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-09-01 | 9:20 | 23367 | 27 | 158 | 117 | 18.7 | 0 | 29.4 | 6 |  | 35.4 | 35.4 | 0.83051 | 0 | 11.8588 | 11.1781 | 11.247 | 107.553 | 0.10393 | 6.81 | 5.75 | 38 | 354 | 364 | 1659 | 1961.4 | -18.2278 | 89.5604 | 1162.7 | 96.7317 | 158 | 135 | 16 | 20.7 | 18.7 | 39.4 | 39.4 | 0.49033 | 0.52538 | 12.5244 | 11.8054 | 5.9032 | 124.5968 | 0.094749 | 5.98 |  | 32 | 412 | 860 | 832.6417 | 3.1812 | 91.2088 | 622.3209 | 94.858 | 135 | 117 | 21 | 8.6 | 6.4 | 15 | 15 | 0.36121 | 0.57333 | 10.4067 | 9.8093 | 13.3917 | 91.6083 | 0.10708 |  | 6.27 | 59 | 860 | 1659 | 1936.3438 | -16.7175 | 83.7912 | 1398.1719 | 95.7802 | SDS-Cl2 demand | mg/L | 2.4 | 20.6 | --- | 123.7333 | --- | 88.3495 | 72.1667 | 96.6744 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.4 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.6 | 20.6 | --- | 108.4824 | --- | 87.3786 | 64.5412 | 95.9716 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.3 | 20.4 | --- | 115.425 | --- | 88.7255 | 67.9125 | 96.6133 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 8.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | not specified | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-09-02 | 9:30 | 23391 | 27 | 158 | 119 | 18.9 | 0 | 30 | 6 |  | 36 | 36 | 0.83333 | 0 | 12.1008 | 11.4062 | 11.9 | 107.7 | 0.10591 | 6.8 | 5.71 | 38 | 358 | 378 | 1738 | 2078 | -19.5627 | 89.9471 | 1228 | 96.9055 | 158 | 136 | 16 | 21.1 | 18.9 | 40 | 40 | 0.49708 | 0.5275 | 12.7664 | 12.0335 | 5.9679 | 125.0321 | 0.096244 | 5.96 |  | 33 | 416 | 878 | 843.582 | 3.92 | 91.2698 | 629.791 | 94.7602 | 136 | 119 | 21 | 8.8 | 6.1 | 14.9 | 14.9 | 0.35446 | 0.5906 | 10.6487 | 10.0375 | 14.0803 | 92.4197 | 0.10861 |  | 6.21 | 60 | 878 | 1738 | 2058.0656 | -18.4157 | 84.127 | 1468.0328 | 95.9129 | SDS-Chlorination temp. | oC | 22.2 | 22.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 13.4 |  |  |  |  | SDS-Chlorination temp. | oC | 21.9 | 21.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 17.4 |  |  |  |  | SDS-Chlorination temp. | oC | 21.7 | 21.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 15.5 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 70 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-09-03 | 9:00 | 23414 | 27 | 157 | 118 | 18.6 | 0 | 32.8 | 6 |  | 38.8 | 38.8 | 0.84536 | 0 | 13.2303 | 12.4708 | 12.656 | 106.244 | 0.11738 | 6.81 | 5.75 | 38 | 354 | 377 | 1687 | 2230.2 | -32.1992 | 89.9204 | 1303.6 | 97.085 | 157 | 135 | 16 | 23.6 | 18.6 | 42.2 | 42.2 | 0.51312 | 0.55924 | 14.279 | 13.4593 | 6.2108 | 123.7892 | 0.10873 | 5.94 |  | 33 | 413 | 864 | 895.1505 | -3.6054 | 91.2467 | 654.0753 | 94.9547 | 135 | 118 | 21 | 9.1 | 6.2 | 15.3 | 15.3 | 0.3629 | 0.59477 | 11.0118 | 10.3796 | 13.9403 | 91.5597 | 0.11336 |  | 6.21 | 60 | 864 | 1687 | 2044.0645 | -21.1657 | 84.0849 | 1454.0323 | 95.8735 | SDS-Chlorination pH | --- | 8.3 | 8.3 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.4 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.4 | 8.2 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 21 | [7 empty] | 1998-09-04 | 8:50 | 23438 | 27 | 157 | 118 | 18.4 | 0 | 30.8 | 6 |  | 36.8 | 36.8 | 0.83696 | 0 | 12.4235 | 11.7104 | 11.877 | 107.223 | 0.10922 | 6.77 | 5.7 | 38 | 360 | 371 | 1705 | 2080.4 | -22.0176 | 89.7574 | 1225.7 | 96.8997 | 157 | 135 | 16 | 22.3 | 18.4 | 40.7 | 40.7 | 0.49877 | 0.54791 | 13.4924 | 12.7179 | 6.1991 | 123.8009 | 0.10273 | 5.96 |  | 33 | 419 | 873 | 886.8152 | -1.5825 | 91.1051 | 652.9076 | 94.9457 | 135 | 118 | 21 | 8.5 | 6.3 | 14.8 | 14.8 | 0.35614 | 0.57432 | 10.2857 | 9.6953 | 13.6145 | 91.8855 | 0.10551 |  | 6.19 | 60 | 873 | 1705 | 1969.9048 | -15.5369 | 83.8275 | 1421.4524 | 95.779 | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 41 | 41 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 42 | 42 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | not specified | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-09-05 | 7:15 | 23461 | 27 | 158 | 120 | 18.8 | 0 | 29.5 | 6 |  | 35.5 | 35.5 | 0.83099 | 0 | 11.8992 | 11.2161 | 11.4817 | 108.7183 | 0.10317 | 6.96 | 5.83 | 38 | 360 | 370 | 1748 | 2002.3333 | -14.55 | 89.7297 | 1186.1667 | 96.7964 | 158 | 136 | 17 | 20.4 | 18.8 | 39.2 | 39.2 | 0.48949 | 0.52041 | 12.3429 | 11.6343 | 5.8926 | 124.1074 | 0.093744 | 5.95 |  | 33 | 415 | 879 | 829.5106 | 5.6302 | 91.0811 | 622.2553 | 94.6967 | 136 | 120 | 21 | 9 | 6 | 15 | 15 | 0.35446 | 0.6 | 10.8908 | 10.2656 | 14.3325 | 92.6675 | 0.11078 |  | 6.26 | 60 | 879 | 1748 | 2107.5 | -20.5664 | 83.7838 | 1493.25 | 95.9819 | SDS-TOX | mg Cl- /L | BMRL | 1565 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1525 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 1255 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 80 percent | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 20.25 | [5 empty] | 1998-09-06 | 11:45 | 23489 | 27 | 158 | 116 | 18.2 | 0 | 29.5 | 6 |  | 35.5 | 35.5 | 0.83099 | 0 | 11.8992 | 11.2161 | 11.7929 | 107.0071 | 0.10482 | 6.82 | 5.7 | 40 | 356 | 381 | 1740 | 2057.5833 | -18.2519 | 89.5013 | 1219.2917 | 96.7194 | 158 | 132 | 16 | 20.8 | 18.2 | 39 | 39 | 0.48274 | 0.53333 | 12.5849 | 11.8625 | 6.0814 | 122.9186 | 0.096507 | 5.91 |  | 34 | 421 | 881 | 863.2857 | 2.0107 | 91.0761 | 642.1429 | 94.7052 | 132 | 116 | 21 | 8.6 | 5.9 | 14.5 | 14.5 | 0.34433 | 0.5931 | 10.4067 | 9.8093 | 14.159 | 88.841 | 0.11041 |  | 6.31 | 62 | 881 | 1740 | 2074.7966 | -19.2412 | 83.727 | 1477.8983 | 95.8049 | SDS-CHCl3 | mg/L | BMRL | 496 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-08-19 | 1998-08-19 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 411 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-02 | 1998-09-02 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 399 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-16 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | 500 mg/l NaCl | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 13.0417 | [5 empty] | 1998-09-07 | 7:10 | 23508 | 27 | 157 | 120 | 19 | 0 | 32.4 | 6 |  | 38.4 | 38.4 | 0.84375 | 0 | 13.0689 | 12.3187 | 12.58 | 106.92 | 0.11521 | 6.91 | 5.8 | 38 | 357 | 378 | 1795 | 2214 | -23.3426 | 89.9471 | 1296 | 97.0679 | 157 | 136 | 16 | 23.5 | 19 | 42.5 | 42.5 | 0.51902 | 0.55294 | 14.2185 | 13.4023 | 6.2309 | 124.2691 | 0.10785 | 5.98 |  | 33 | 418 | 889 | 894.1842 | -0.58315 | 91.2698 | 656.0921 | 94.9702 | 136 | 120 | 22 | 8.8 | 5.8 | 14.6 | 14.6 | 0.34433 | 0.60274 | 10.6487 | 10.0375 | 14.5614 | 91.4386 | 0.10977 |  | 6.28 | 61 | 889 | 1795 | 2145.2759 | -19.514 | 83.8624 | 1517.1379 | 95.9793 | SDS-BDCM | mg/L | BMRL | 70.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:25 | 7:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 70.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 7:40 | 7:20 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.1 | 70.5 | --- | 434.85 | --- | 98.4397 | 252.675 | 99.5647 | Sampling time | hh:mm | 8:10 | 7:45 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | not specified | [7 empty] | 1998-09-08 | 8:58 | 23534 | 27 | 157 | 121 | 19.1 | 0 | 32.8 | 6 |  | 38.8 | 38.8 | 0.84536 | 0 | 13.2303 | 12.4708 | 12.3573 | 107.5427 | 0.11596 | 6.79 | 5.72 | 39 | 358 | 370 | 1852 | 2179.4667 | -17.6818 | 89.4595 | 1274.7333 | 96.9405 | 157 | 136 | 16 | 24.2 | 19.1 | 43.3 | 43.3 | 0.52662 | 0.55889 | 14.642 | 13.8015 | 6.2727 | 124.2273 | 0.1111 | 5.97 |  | 33 | 417 | 892 | 903.534 | -1.2931 | 91.0811 | 660.267 | 95.002 | 136 | 121 | 22 | 8.5 | 5.5 | 14 | 14 | 0.32914 | 0.60714 | 10.2857 | 9.6953 | 14.7136 | 91.7864 | 0.10563 |  | 6.25 | 62 | 892 | 1852 | 2174.7273 | -17.4259 | 83.2432 | 1533.3636 | 95.9566 | SDS-DBCM | mg/L | 1.2 | 9.5 | --- | 56.5333 | --- | 87.3684 | 33.0167 | 96.3655 | Operation time | hh.hh | 23057 | 23057 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.3 | 11.3 | --- | 60.1235 | --- | 88.4956 | 35.7118 | 96.3597 | Operation time | hh.hh | 23389 | 23389 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.6 | 9.1 | --- | 48.475 | --- | 82.4176 | 28.7875 | 94.442 | Operation time | hh.hh | 23725 | 23725 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-09-09 | 9:00 | 23558 | 27 | 156 | 118 | 18.1 | 0 | 32.9 | 6 |  | 38.9 | 38.9 | 0.84576 | 0 | 13.2706 | 12.5088 | 12.2353 | 106.6647 | 0.11727 | 6.75 | 5.69 | 39 | 360 | 366 | 1745 | 2159.05 | -23.7278 | 89.3443 | 1262.525 | 96.911 | 156 | 135 | 16 | 24.2 | 18.1 | 42.3 | 42.3 | 0.50974 | 0.5721 | 14.642 | 13.8015 | 6.4238 | 123.0762 | 0.11214 | 5.97 |  | 33 | 418 | 882 | 932.7514 | -5.7541 | 90.9836 | 675.3757 | 95.1138 | 135 | 118 | 20 | 8.6 | 6 | 14.6 | 14.6 | 0.3477 | 0.58904 | 10.4067 | 9.8093 | 14.0938 | 92.4062 | 0.10615 |  | 6.24 | 61 | 882 | 1745 | 2058.7667 | -17.9809 | 83.3333 | 1470.3833 | 95.8514 | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.61 | 6.06 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.72 | 6.25 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.53 | 5.66 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 6.5-7.0 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-09-10 | 8:45 | 23582 | 26 | 156 | 119 | 18.5 | 0 | 31.8 | 6 |  | 37.8 | 37.8 | 0.84127 | 0 | 12.8269 | 12.4533 | 11.753 | 107.247 | 0.11612 | 6.95 | 6.03 | 38 | 336 | 360 | 1752 | 2066.6 | -17.9566 | 89.4444 | 1213.3 | 96.868 | 156 | 135 | 16 | 22.8 | 18.5 | 41.3 | 41.3 | 0.50468 | 0.55206 | 13.795 | 13.3932 | 5.9962 | 123.5038 | 0.10844 | 5.92 |  | 32 | 403 | 860 | 860.2324 | -0.027027 | 91.1111 | 631.6162 | 94.9336 | 135 | 119 | 21 | 8.9 | 5.7 | 14.6 | 14.6 | 0.34264 | 0.60959 | 10.7697 | 10.4561 | 14.2634 | 91.7366 | 0.11398 |  | 6.29 | 59 | 860 | 1752 | 2110.6842 | -20.4728 | 83.6111 | 1485.3421 | 96.0279 | SDS-THM4 | mg/L | 2.4 | 575.6 | --- | 3823.7333 | --- | 99.583 | 2199.6667 | 99.8909 | Temperature | oC | 26.2 | 26.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.3 | 493.2 | --- | 2894.8294 | --- | 99.7364 | 1694.0147 | 99.9233 | Temperature | oC | 26 | 26.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.9 | 478.6 | --- | 2970.775 | --- | 99.1851 | 1724.6875 | 99.7739 | Temperature | oC | 26 | 26 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | <400 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 13.0417 | [5 empty] | 1998-09-11 | 9:11 | 23607 | 27 | 155 | 117 | 17.8 | 0 | 31 | 6 |  | 37 | 37 | 0.83784 | 0 | 12.5042 | 11.7864 | 12.0042 | 106.1958 | 0.11099 | 6.82 | 5.74 | 39 | 363 | 374 | 1741 | 2104.8333 | -20.898 | 89.5722 | 1239.4167 | 96.8534 | 155 | 134 | 16 | 22.2 | 17.8 | 40 | 40 | 0.4878 | 0.555 | 13.4319 | 12.6609 | 6.2671 | 122.2329 | 0.10358 | 5.95 |  | 34 | 420 | 882 | 901.4157 | -2.2013 | 90.9091 | 660.7079 | 94.854 | 134 | 117 | 20 | 8.7 | 6 | 14.7 | 14.7 | 0.34939 | 0.59184 | 10.5277 | 9.9234 | 14.1623 | 91.3377 | 0.10865 |  | 6.22 | 61 | 882 | 1741 | 2072.45 | -19.0379 | 83.6898 | 1477.225 | 95.8706 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 80 | 182.48 | 47.2222 | 131.24 | 85.5227 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 116 | 214.2326 | 67.7419 | 165.1163 | 87.8873 | SDS-MCAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 34 | 55.8571 | 33.3333 | 44.9286 | 64.3879 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 3 to 10 | Design system recycle flow rate, QR-sys (gpm) | 0.01 | [5 empty] | 1998-09-12 | 10:30 | 23632 | 27 | 156 | 120 | 18 | 0 | 32.3 | 6 |  | 38.3 | 38.3 | 0.84334 | 0 | 13.0286 | 12.2807 | 12.4409 | 107.5591 | 0.11418 | 6.8 | 5.77 | 42 | 356 | 379 | 1834 | 2193.1833 | -19.5847 | 88.9182 | 1286.0917 | 96.7343 | 156 | 135 | 16 | 23.7 | 18 | 41.7 | 41.7 | 0.50383 | 0.56835 | 14.3395 | 13.5164 | 6.4841 | 123.0159 | 0.10987 | 5.58 |  | 36 | 427 | 898 | 941.8167 | -4.8794 | 90.5013 | 684.4083 | 94.74 | 135 | 120 | 20 | 8.5 | 5.6 | 14.1 | 14.1 | 0.33251 | 0.60284 | 10.2857 | 9.6953 | 14.6519 | 92.8481 | 0.10442 |  | 6.27 | 65 | 898 | 1834 | 2162.375 | -17.9049 | 82.8496 | 1530.1875 | 95.7522 | SDS-DCAA* | mg/L | BMRL | 138 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 54 | 785 | 2013.08 | 85.5228 | 1399.04 | 96.1402 | SDS-DCAA* | mg/L | BMRL | 197 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 53 | 779 | 1521.8837 | 85.5586 | 1150.4419 | 95.3931 | SDS-DCAA* | mg/L | BMRL | 200 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 56 | 783 | 1665.7857 | 85.4167 | 1224.3929 | 95.4263 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 4 | System influent flow rate, QI-sys (gpm) | 43.76 | [5 empty] | 1998-09-13 | 8:05 | 23653 | 27 | 157 | 121 | 17.9 | 0 | 30 | 6 |  | 36 | 36 | 0.83333 | 0 | 12.1008 | 11.4062 | 12.04 | 109.06 | 0.10459 | 6.75 | 5.18 | 42 | 356 | 386 | 1855 | 2106 | -13.531 | 89.1192 | 1246 | 96.6292 | 157 | 137 | 16 | 21.3 | 17.9 | 39.2 | 39.2 | 0.48189 | 0.54337 | 12.8874 | 12.1476 | 6.2204 | 124.7796 | 0.097352 | 5.39 |  | 36 | 426 | 898 | 890.0782 | 0.88216 | 90.6736 | 658.0391 | 94.5292 | 137 | 121 | 20 | 8.6 | 5.5 | 14.1 | 14.1 | 0.33083 | 0.60993 | 10.4067 | 9.8093 | 14.8425 | 94.1575 | 0.10418 |  | 5.55 | 65 | 898 | 1855 | 2200.5091 | -18.6258 | 83.1606 | 1549.2545 | 95.8044 | SDS-TCAA* | mg/L | 1.28 | 153 | --- | 1012.7467 | --- | 99.1634 | 582.8733 | 99.7804 | Total hardness | mg/L as CaCO3 | 22 | 600 | 1571.04 | 91.5385 | 1085.52 | 97.9733 | SDS-TCAA* | mg/L | 2.4 | 182 | --- | 1058.8706 | --- | 98.6813 | 620.4353 | 99.6132 | Total hardness | mg/L as CaCO3 | 24 | 620 | 1229.8605 | 90.1639 | 924.9302 | 97.4052 | SDS-TCAA* | mg/L | 2.2 | 221 | --- | 1369.7 | --- | 99.0045 | 795.35 | 99.7234 | Total hardness | mg/L as CaCO3 | 22 | 620 | 1346.1429 | 91.2 | 983.0714 | 97.7621 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 4 | Recycle ratio, r | 0.00022857 | [5 empty] | 1998-09-14 | 8:45 | 23678 | 27 | 157 | 121 | 18.3 | 0 | 29.2 | 6 |  | 35.2 | 35.2 | 0.82955 | 0 | 11.7782 | 11.102 | 11.8107 | 108.8893 | 0.10196 | 6.77 | 5.22 | 42 | 356 | 386 | 1808 | 2060.1333 | -13.9454 | 89.1192 | 1223.0667 | 96.566 | 157 | 136 | 16 | 20.5 | 18.3 | 38.8 | 38.8 | 0.48189 | 0.52835 | 12.4034 | 11.6914 | 6.0844 | 124.4156 | 0.09397 | 5.36 |  | 36 | 426 | 892 | 862.8852 | 3.264 | 90.6736 | 644.4426 | 94.4138 | 136 | 121 | 21 | 8.6 | 5.6 | 14.2 | 14.2 | 0.3342 | 0.60563 | 10.4067 | 9.8093 | 14.6202 | 92.8798 | 0.10561 |  | 5.45 | 65 | 892 | 1808 | 2162.0357 | -19.5816 | 83.1606 | 1527.0179 | 95.7433 | SDS-MBAA* | mg/L | 0.76 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 560 | 1467.2 | 91.6667 | 1013.6 | 98.0268 | SDS-MBAA* | mg/L | 2 | 1.3 | --- | -2.1176 | --- | -53.8462 | -0.40882 | 589.2086 | Calcium hardness | mg/L as CaCO3 | 18 | 520 | 1033.6744 | 91.9643 | 776.8372 | 97.6829 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 20 | 520 | 1127.1429 | 91.453 | 823.5714 | 97.5716 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | 1 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-09-15 | 9:15 | 23703 | 27 | 157 | 121 | 18.1 | 0 | 29.8 | 6 |  | 35.8 | 35.8 | 0.8324 | 0 | 12.0202 | 11.3302 | 11.8782 | 109.0218 | 0.10393 | 6.77 | 5.18 | 41 | 358 | 382 | 1784 | 2075.6333 | -16.3472 | 89.267 | 1228.8167 | 96.6635 | 157 | 136 | 16 | 21.2 | 18.1 | 39.3 | 39.3 | 0.48442 | 0.53944 | 12.8269 | 12.0906 | 6.1681 | 124.3319 | 0.097244 | 5.38 |  | 35 | 424 | 889 | 879.6243 | 1.0546 | 90.8377 | 651.8122 | 94.6304 | 136 | 121 | 20 | 8.7 | 5.8 | 14.5 | 14.5 | 0.34264 | 0.6 | 10.5277 | 9.9234 | 14.4725 | 94.0275 | 0.10554 |  | 5.51 | 62 | 889 | 1784 | 2129.5 | -19.3666 | 83.7696 | 1509.25 | 95.892 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.068 | 0.258 | 0.5772 | 34.6154 | 0.4176 | 83.7165 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.056 | 0.535 | 1.0251 | 61.3793 | 0.78007 | 92.8212 | SDS-DBAA* | mg/L | 0.7 | 1.4 | --- | 5.075 | --- | 50 | 3.2375 | 78.3784 | Turbidity | ntu | 0.07 | 0.19 | 0.33571 | 90.6667 | 0.26286 | 73.3696 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | maximum system recycle flow rates. | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-BCAA* | mg/L | BMRL | 18.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.57 | 27.6 | 73.0104 | 95.9574 | 50.3052 | 98.8669 | SDS-BCAA* | mg/L | BMRL | 26.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 28.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 13.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.59 | 29.1 | 63.7193 | 95.0833 | 46.4096 | 98.7287 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [19 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.04 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.01 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.007 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7681 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5689 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4605 | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 43.76 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 24.7917 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA5 | mg/L | 2.04 | 291 | --- | 1928.44 | --- | 99.299 | 1109.72 | 99.8162 | [8 empty] | SDS-HAA5 | mg/L | 4.4 | 380.3 | --- | 2215.5765 | --- | 98.843 | 1297.9382 | 99.661 | [8 empty] | SDS-HAA5 | mg/L | 2.9 | 423.5 | --- | 2631.65 | --- | 99.3152 | 1527.575 | 99.8102 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 18.9683 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA6 | mg/L | 2.04 | 309.5 | --- | 2051.7733 | --- | 99.3409 | 1180.6367 | 99.8272 | [8 empty] | SDS-HAA6 | mg/L | 4.4 | 406.7 | --- | 2370.8706 | --- | 98.9181 | 1388.7853 | 99.6832 | [8 empty] | SDS-HAA6 | mg/L | 2.9 | 437.1 | --- | 2716.65 | --- | 99.3365 | 1576.875 | 99.8161 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 18.9683 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 12.3958 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 6.5725 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0.01 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 6.5625 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 37.1875 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 43.75 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4), % | 87.8576 | 94.1382 |  | Qp/QT (HAA5), % | 82.0183 | 91.3621 | [11 empty] | Qp/QT (THM4), % | 85.6272 | 92.9457 |  | Qp/QT (HAA5), % | 86.805 | 93.9878 | [11 empty] | Qp/QT (THM4), % | 85.6541 | 93.2378 |  | Qp/QT (HAA5), % | 87.8507 | 94.2701 | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 105.4713 | 51.9123 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 66.2062 | 30.8742 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 61.5728 | 31.0999 | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA5b, mg/L | 37.1266 | 18.9783 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 58.4275 | 30.917 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 63.2389 | 31.3417 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 6.8 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 26.1 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CDb, mg/L | 4.6099 | 3.4669 |  | SDS-CDb, mg/L | 5.6727 | 3.9721 | [11 empty] | SDS-CDb, mg/L | 5.1871 | 3.8698 |  | SDS-CDb, mg/L | 4.9751 | 3.6822 | [11 empty] | SDS-CDb, mg/L | 4.8966 | 3.524 |  | SDS-CDb, mg/L | 4.499 | 3.3371 | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 5 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 10 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Bromideb, mg/L | 47.7278 | 38.5583 |  | Bromideb, mg/L | 56.2533 | 42.6113 | [11 empty] | Bromideb, mg/L | 54.8467 | 43.7225 |  | Bromideb, mg/L | 53.0564 | 42.1386 | [11 empty] | Bromideb, mg/L | 57.3712 | 46.6023 |  | Bromideb, mg/L | 54.252 | 45.1365 | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 26 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Alkb, mg/L CaCO3 | 16.6713 | 15.2896 |  | Alkb, mg/L CaCO3 | 17.956 | 15.9003 | [11 empty] | Alkb, mg/L CaCO3 | 20.899 | 17.3861 |  | Alkb, mg/L CaCO3 | 20.3336 | 16.8859 | [11 empty] | Alkb, mg/L CaCO3 | 13.7215 | 12.8115 |  | Alkb, mg/L CaCO3 | 13.4579 | 12.6876 | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 46.875 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | T-Hdb, mg/L CaCO3 | 49.1417 | 34.0684 |  | T-Hdb, mg/L CaCO3 | 63.1561 | 40.7309 | [11 empty] | T-Hdb, mg/L CaCO3 | 50.4826 | 33.9427 |  | T-Hdb, mg/L CaCO3 | 47.8207 | 31.5877 | [11 empty] | T-Hdb, mg/L CaCO3 | 51.2825 | 33.6882 |  | T-Hdb, mg/L CaCO3 | 46.1864 | 31.2934 | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 43.5667 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Ca-Hdb, mg/L CaCO3 | 41.4417 | 27.2477 |  | Ca-Hdb, mg/L CaCO3 | 54.6387 | 33.5216 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 42.4704 | 26.9551 |  | Ca-Hdb, mg/L CaCO3 | 39.9734 | 24.7459 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 43.8479 | 27.012 |  | Ca-Hdb, mg/L CaCO3 | 38.9715 | 24.7204 | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 100.4417 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on E23: S Allgeier (10/2/99): Reviewer changed width from 30 feet to 15 feet -- a value more typical for this membrane.
Note on AR6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on BL7: C. Rice: Stage 1 concentrate pH was not measured.
Note on BP6: C. Rice: Consultant verified that the influent TDS concentrations for Stage 1 are higher than the influent TDS concentrations for the system because different instruments were used to measure TDS; there was also a probe calibration error.
Note on CJ7: C. Rice: Stage 2 influent pH was not measured.
Note on DA17: C. Rice: Consultant verified that the high MB closure errors for TDS are due to a conductivity probe calibration error.
Note on DU17: C. Rice: Consultant verified that the high MB closure errors for TDS are due to a conductivity probe calibration error.
Note on EO17: C. Rice: Consultant verified that the high MB closure errors for TDS are due to a conductivity probe calibration error.