## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Sampling Event 1 | [9 empty] | Field 1-7: System And Stage Water Quality For Sampling Event 1 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Sampling Event 2 | [9 empty] | Field 1-8: System And Stage Water Quality For Sampling Event 2 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Sampling Event 3 | [9 empty] | Field 1-9: System And Stage Water Quality For Sampling Event 3 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Sampling Event 4 | [9 empty] | Field 1-10: System And Stage Water Quality For Sampling Event 4 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Sampling Event 5 | [9 empty] | Field 1-11: System And Stage Water Quality For Sampling Event 5 (continued) | [7 empty] | Field 1-12: System and Stage Water Quality for Sampling Event 6 | [9 empty] | Field 1-12: System and Stage Water Quality Sampling Event 6(continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Pinellas County Utilities | Membrane manufacturer | DOW USA, (FilmTec) | Average yearly temperature of feed water, TavgoC (oC) | 24 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.61 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.4 | [6 empty] | System recovery during sample collection (decimal) | 0.62 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.4 | [6 empty] | System recovery during sample collection (decimal) | 0.57 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.43 | [6 empty] | System recovery during sample collection (decimal) | 0.57 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.39 | [6 empty] | System recovery during sample collection (decimal) | 0.61 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.41 | [6 empty] | System recovery during sample collection (decimal) | 0.63 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.4 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL6521405 | Membrane trade name | NF-70 | Temperature normalized MTCW (gfd/psi) | 0.33981 | Calcium Hardness (mg/L as CaCO3) | 190 | Cartridge filtration | 5 mm exclusion size | Pilot-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 11.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.54 | [6 empty] | System feed flow rate during sample collection (gpm) | 11.15 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.5 | [6 empty] | System feed flow rate during sample collection (gpm) | 10.1 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.33 | [6 empty] | System feed flow rate during sample collection (gpm) | 10.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.14 | [6 empty] | System feed flow rate during sample collection (gpm) | 10.9 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.47 | [6 empty] | System feed flow rate during sample collection (gpm) | 11.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.58 |  |  |  |  | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) |  | Membrane element model number | NF-70, 4040 |  |  | LSI | 0.02 | Sulfuric acid addition | approx. dose 110 mg/L to pH = 6.0 | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 11.3 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 11.15 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.15 | [6 empty] | System influent flow rate during sample collection (gpm) | 10.1 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 10.1 | [6 empty] | System influent flow rate during sample collection (gpm) | 10.5 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 10.5 | [6 empty] | System influent flow rate during sample collection (gpm) | 10.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 10.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 11.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.4 |  |  |  |  | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.08 | (or) Flocon 100, anti-scalent | 2 ppm | Pilot-scale | 1990-02-06 |  | 2.2 | 24 | 144 | 67 | 47.5 | 0 | 9.37 | 2.47 |  | 11.84 | 11.84 | 0.79139 | 0 | 18.74 | 18.74 | 4.9245 | 53.0755 | 0.35308 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 884.8988 | -58.0176 | 70.8333 | 562.4494 | 87.5544 | 144 | 108 | 55 | 7.1653 | 4.6747 | 11.84 | 11.84 | 0.30662 | 0.60518 | 21.4959 | 21.4959 | 3.2148 | 67.7852 | 0.31712 | 7.5 | 6.8 | 58 | 240 | 360 | 518.9659 | -44.1572 | 75.8333 | 379.4829 | 84.716 | 108 | 67 | 40 | 2.2047 | 2.47 | 4.6747 | 4.6747 | 0.26531 | 0.47162 | 13.2282 | 13.2282 | 3.7604 | 43.7396 | 0.30243 | 6.8 | 6.7 | 100 | 360 | 560 | 592.0743 | -5.7276 | 58.3333 | 476.0372 | 78.9932 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 250
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.6 | Total iron (mg/L) | 0.08 |  |  |  | 1990-02-07 |  | 7.9 | 24 | 145 | 69 | 47.5 | 0 | 9.33 | 2.36 |  | 11.69 | 11.69 | 0.79812 | 0 | 18.66 | 18.66 | 5.0604 | 54.4396 | 0.34277 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 912.0763 | -62.8708 | 70.8333 | 576.0381 | 87.848 | 145 | 109 | 55 | 7.1347 | 4.5553 | 11.69 | 11.69 | 0.30162 | 0.61033 | 21.4041 | 21.4041 | 3.2453 | 68.7547 | 0.31131 | 7.5 | 6.8 | 58 | 240 | 360 | 525.0566 | -45.849 | 75.8333 | 382.5283 | 84.8377 | 109 | 69 | 40 | 2.1953 | 2.36 | 4.5553 | 4.5553 | 0.25679 | 0.48192 | 13.1718 | 13.1718 | 3.8093 | 45.1907 | 0.29147 | 6.8 | 6.7 | 100 | 360 | 560 | 601.8544 | -7.474 | 58.3333 | 480.9272 | 79.2068 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1990-02-08 |  | 29.6 | 24 | 145 | 68 | 46.5 | 0 | 9.2 | 2.5 |  | 11.7 | 11.7 | 0.78632 | 0 | 18.4 | 18.4 | 4.828 | 55.172 | 0.3335 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 865.6 | -54.5714 | 70.8333 | 552.8 | 87.3372 | 145 | 109 | 54 | 7.0605 | 4.6395 | 11.7 | 11.7 | 0.30337 | 0.60346 | 21.1814 | 21.1814 | 3.2048 | 69.7952 | 0.30348 | 7.5 | 6.8 | 58 | 240 | 360 | 516.9684 | -43.6023 | 75.8333 | 378.4842 | 84.6757 | 109 | 68 | 39 | 2.1395 | 2.5 | 4.6395 | 4.6395 | 0.26512 | 0.46115 | 12.8372 | 12.8372 | 3.7126 | 45.7874 | 0.28037 | 6.8 | 6.7 | 100 | 360 | 560 | 582.5116 | -4.0199 | 58.3333 | 471.2558 | 78.7801 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | NA |  |  |  | 1990-02-09 |  | 51 | 24 | 145 | 68 | 47 | 0 | 9.3 | 2.5 |  | 11.8 | 11.8 | 0.78814 | 0 | 18.6 | 18.6 | 4.862 | 54.638 | 0.34042 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 872.4 | -55.7857 | 70.8333 | 556.2 | 87.4146 | 145 | 108 | 54 | 7.1372 | 4.6628 | 11.8 | 11.8 | 0.30566 | 0.60485 | 21.4116 | 21.4116 | 3.2129 | 69.2871 | 0.30903 | 7.5 | 6.8 | 58 | 240 | 360 | 518.5825 | -44.0507 | 75.8333 | 379.2913 | 84.7083 | 108 | 68 | 40 | 2.1628 | 2.5 | 4.6628 | 4.6628 | 0.26598 | 0.46384 | 12.9767 | 12.9767 | 3.7247 | 44.2753 | 0.29309 | 6.8 | 6.7 | 100 | 360 | 560 | 584.9302 | -4.4518 | 58.3333 | 472.4651 | 78.8344 | Sampling date | MM/DD/YY | 1990-03-20 | 1990-03-20 | 1990-03-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-03-20 | 1990-03-20 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-06-12 | 1990-06-12 | 1990-06-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-06-12 | 1990-06-12 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-07-12 | 1990-07-12 | 1990-07-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-07-12 | 1990-07-12 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-08-28 | 1990-08-28 | 1990-08-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-08-28 | 1990-08-28 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-10-02 | 1990-10-02 | 1990-10-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-10-02 | 1990-10-02 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-11-05 | 1990-11-05 | 1990-11-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-11-05 | 1990-11-05 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.2 |  |  |  | 1990-02-12 |  | 125.1 | 24 | 145 | 68 | 45 | 0 | 9.2 | 2.5 |  | 11.7 | 11.7 | 0.78632 | 0 | 18.4 | 18.4 | 4.828 | 56.672 | 0.32468 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 865.6 | -54.5714 | 70.8333 | 552.8 | 87.3372 | 145 | 108 | 52 | 7.1805 | 4.5195 | 11.7 | 11.7 | 0.30114 | 0.61372 | 21.5415 | 21.5415 | 3.2658 | 71.2342 | 0.3024 | 7.5 | 6.8 | 58 | 240 | 360 | 529.157 | -46.9881 | 75.8333 | 384.5785 | 84.9186 | 108 | 68 | 38 | 2.0195 | 2.5 | 4.5195 | 4.5195 | 0.26066 | 0.44684 | 12.1171 | 12.1171 | 3.6501 | 46.3499 | 0.26143 | 6.8 | 6.7 | 100 | 360 | 560 | 570.0293 | -1.7909 | 58.3333 | 465.0146 | 78.4953 | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.2 |  |  |  | 1990-02-13 |  | 147.9 | 24 | 145 | 69 | 44.5 | 0 | 9.3 | 2.4 |  | 11.7 | 11.7 | 0.79487 | 0 | 18.6 | 18.6 | 4.9938 | 57.5063 | 0.32344 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 898.75 | -60.4911 | 70.8333 | 569.375 | 87.7058 | 145 | 109 | 52 | 7.1964 | 4.5036 | 11.7 | 11.7 | 0.30085 | 0.61508 | 21.5893 | 21.5893 | 3.2741 | 71.7259 | 0.301 | 7.5 | 6.8 | 58 | 240 | 360 | 530.8247 | -47.4513 | 75.8333 | 385.4124 | 84.9512 | 109 | 69 | 37 | 2.1036 | 2.4 | 4.5036 | 4.5036 | 0.25635 | 0.46709 | 12.6214 | 12.6214 | 3.7394 | 48.2606 | 0.26153 | 6.8 | 6.7 | 100 | 360 | 560 | 587.8869 | -4.9798 | 58.3333 | 473.9435 | 78.9004 | Operation time | hh.hh | 713.9 | 713.9 | 713.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 713.9 | 713.9 | --- | --- | --- | --- | Operation time | hh.hh | 2641.7 | 2641.7 | 2641.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2641.7 | 2641.7 | --- | --- | --- | --- | Operation time | hh.hh | 3306.6 | 3306.6 | 3306.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3306.6 | 3306.6 | --- | --- | --- | --- | Operation time | hh.hh | 4120.4 | 4120.4 | 4120.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4120.4 | 4120.4 | --- | --- | --- | --- | Operation time | hh.hh | 4798.4 | 4798.4 | 4798.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4798.4 | 4798.4 | --- | --- | --- | --- | Operation time | hh.hh | 5598.6 | 5598.6 | 5598.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5598.6 | 5598.6 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.83333 | Sulfate (mg/L) | 1.5 |  |  |  | 1990-02-14 |  | 168.3 | 24 | 145 | 70 | 43.5 | 0 | 8.9 | 2.4 |  | 11.3 | 11.3 | 0.78761 | 0 | 17.8 | 17.8 | 4.8521 | 59.1479 | 0.30094 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 870.4167 | -55.4315 | 70.8333 | 555.2083 | 87.3921 | 145 | 110 | 50 | 6.8378 | 4.4622 | 11.3 | 11.3 | 0.29265 | 0.60512 | 20.5134 | 20.5134 | 3.2145 | 74.2855 | 0.27614 | 7.5 | 6.8 | 58 | 240 | 360 | 518.8942 | -44.1373 | 75.8333 | 379.4471 | 84.7146 | 110 | 70 | 37 | 2.0622 | 2.4 | 4.4622 | 4.4622 | 0.25482 | 0.46215 | 12.3732 | 12.3732 | 3.717 | 49.283 | 0.25106 | 6.8 | 6.7 | 100 | 360 | 560 | 583.4045 | -4.1794 | 58.3333 | 471.7022 | 78.8002 | pH | --- | 6.1 | 6.6 | 6.8 | --- | --- | --- | --- | --- | pH | --- | 6 | 6.6 | --- | --- | --- | --- | pH | --- | 6.8 | 7.5 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 7.5 | --- | --- | --- | --- | pH | --- | 6.8 | 7.4 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 7.4 | --- | --- | --- | --- | pH | --- | 6.9 | 7.4 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 7.4 | --- | --- | --- | --- | pH | --- | 5.7 | 6.2 | 5.8 | --- | --- | --- | --- | --- | pH | --- | 7.7 | 6.2 | --- | --- | --- | --- | pH | --- | 5.7 | 5.8 | 5.7 | --- | --- | --- | --- | --- | pH | --- | 5.7 | 5.8 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.5 | Calcium (mg/L) | 76 |  |  |  | 1990-02-15 |  | 191.4 | 24 | 145 | 70 | 43.5 | 0 | 9.3 | 2.5 |  | 11.8 | 11.8 | 0.78814 | 0 | 18.6 | 18.6 | 4.862 | 59.138 | 0.31452 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 872.4 | -55.7857 | 70.8333 | 556.2 | 87.4146 | 145 | 109 | 50 | 7.1451 | 4.6549 | 11.8 | 11.8 | 0.30551 | 0.60552 | 21.4354 | 21.4354 | 3.2168 | 73.7832 | 0.29052 | 7.5 | 6.8 | 58 | 240 | 360 | 519.3655 | -44.2682 | 75.8333 | 379.6827 | 84.7241 | 109 | 70 | 37 | 2.1549 | 2.5 | 4.6549 | 4.6549 | 0.26569 | 0.46293 | 12.9293 | 12.9293 | 3.7205 | 48.7795 | 0.26506 | 6.8 | 6.7 | 100 | 360 | 560 | 584.1073 | -4.3049 | 58.3333 | 472.0537 | 78.816 | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5 | Barium (mg/L) | NA |  |  |  | 1990-02-16 |  | 217.6 | 24 | 144 | 68 | 42.5 | 0 | 9.2 | 2.7 |  | 11.9 | 11.9 | 0.77311 | 0 | 18.4 | 18.4 | 4.5963 | 58.9037 | 0.31237 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 819.2593 | -46.2963 | 70.8333 | 529.6296 | 86.7832 | 144 | 108 | 50 | 7.094 | 4.806 | 11.9 | 11.9 | 0.31018 | 0.59613 | 21.2819 | 21.2819 | 3.1632 | 72.8368 | 0.29219 | 7.5 | 6.8 | 58 | 240 | 360 | 508.6428 | -41.2897 | 75.8333 | 374.3214 | 84.5053 | 108 | 68 | 35 | 2.106 | 2.7 | 4.806 | 4.806 | 0.27872 | 0.43821 | 12.6361 | 12.6361 | 3.614 | 49.386 | 0.25586 | 6.8 | 6.7 | 100 | 360 | 560 | 562.8023 | -0.50041 | 58.3333 | 461.4012 | 78.3269 | Alkalinity | mg/L as CaCO3 | 41 | 130 | 250 | 269.2051 | -7.6821 | 68.4615 | 199.6026 | 79.4592 | Alkalinity | mg/L as CaCO3 | 34 | 130 | 194.4734 | 73.8462 | 162.2367 | 79.043 | Alkalinity | mg/L as CaCO3 | 53 | 210 | 480 | 466.1579 | 2.8838 | 74.7619 | 338.0789 | 84.3232 | Alkalinity | mg/L as CaCO3 | 56 | 210 | 314.2105 | 73.3333 | 262.1053 | 78.6345 | Alkalinity | mg/L as CaCO3 | 59 | 220 | 440 | 433.4186 | 1.4958 | 73.1818 | 326.7093 | 81.9411 | Alkalinity | mg/L as CaCO3 | 48 | 220 | 349.0745 | 78.1818 | 284.5373 | 83.1305 | Alkalinity | mg/L as CaCO3 | 57 | 230 | 480 | 459.3256 | 4.3072 | 75.2174 | 344.6628 | 83.4621 | Alkalinity | mg/L as CaCO3 | 45 | 230 | 350.4245 | 80.4348 | 290.2123 | 84.4941 | Alkalinity | mg/L as CaCO3 | 50 | 160 | 200 | 332.0513 | -66.0256 | 68.75 | 246.0256 | 79.6769 | Alkalinity | mg/L as CaCO3 | 42 | 160 | 242.0311 | 73.75 | 201.0156 | 79.1061 | Alkalinity | mg/L as CaCO3 | 47 | 98 | 160 | 184.8378 | -15.5236 | 52.0408 | 141.4189 | 66.7654 | Alkalinity | mg/L as CaCO3 | 33 | 98 | 141.651 | 66.3265 | 119.8255 | 72.46 | Electric Rate ($/kW-h) | 0.075
Mailing Address |  | Design flux, FW (gfd) | 15 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.5 | Strontium (mg/L) | NA |  |  |  | 1990-02-19 |  | 288 | 24 | 144 | 70 | 43 | 0 | 9 | 2.5 |  | 11.5 | 11.5 | 0.78261 | 0 | 18 | 18 | 4.76 | 59.24 | 0.30385 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 852 | -52.1429 | 70.8333 | 546 | 87.1795 | 144 | 109 | 50 | 7.0244 | 4.4756 | 11.5 | 11.5 | 0.29662 | 0.61082 | 21.0732 | 21.0732 | 3.2482 | 73.2518 | 0.28768 | 7.5 | 6.8 | 58 | 240 | 360 | 525.6458 | -46.0127 | 75.8333 | 382.8229 | 84.8494 | 109 | 70 | 36 | 1.9756 | 2.5 | 4.4756 | 4.4756 | 0.25903 | 0.44142 | 11.8537 | 11.8537 | 3.6273 | 49.8727 | 0.23768 | 6.8 | 6.7 | 100 | 360 | 560 | 565.4634 | -0.97561 | 58.3333 | 462.7317 | 78.3892 | Total dissolved solids | mg/L | 78 | 320 | 670 | 698.5128 | -4.2556 | 75.625 | 509.2564 | 84.6836 | Total dissolved solids | mg/L | 60 | 320 | 494.6154 | 81.25 | 407.3077 | 85.2691 | Total dissolved solids | mg/L | 69 | 240 | 560 | 519 | 7.3214 | 71.25 | 379.5 | 81.8182 | Total dissolved solids | mg/L | 58 | 240 | 363.1579 | 75.8333 | 301.5789 | 80.7679 | Total dissolved solids | mg/L | 74 | 260 | 480 | 506.5581 | -5.5329 | 71.5385 | 383.2791 | 80.6929 | Total dissolved solids | mg/L | 58 | 260 | 411.5875 | 77.6923 | 335.7938 | 82.7275 | Total dissolved solids | mg/L | 74 | 250 | 490 | 483.3023 | 1.3669 | 70.4 | 366.6512 | 79.8173 | Total dissolved solids | mg/L | 52 | 250 | 378.8868 | 79.2 | 314.4434 | 83.4628 | Total dissolved solids | mg/L | 82 | 340 | 640 | 743.5385 | -16.1779 | 75.8824 | 541.7692 | 84.8644 | Total dissolved solids | mg/L | 96 | 340 | 509.6236 | 71.7647 | 424.8118 | 77.4018 | Total dissolved solids | mg/L | 82 | 350 | 720 | 806.3243 | -11.9895 | 76.5714 | 578.1622 | 85.8171 | Total dissolved solids | mg/L | 52 | 350 | 550.1232 | 85.1429 | 450.0616 | 88.446 | Fuel Oil Rate ($/gal) | 1.25
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 7.5 | Reactive silica (mg/L as SiO2) | 15 |  |  |  | 1990-02-20 |  | 313 | 24 | 145 | 70 | 42.5 | 0 | 8.9 | 2.7 |  | 11.6 | 11.6 | 0.76724 | 0 | 17.8 | 17.8 | 4.5019 | 60.4981 | 0.29422 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 800.3704 | -42.9233 | 70.8333 | 520.1852 | 86.5433 | 145 | 108 | 50 | 6.8627 | 4.7373 | 11.6 | 11.6 | 0.30333 | 0.59161 | 20.588 | 20.588 | 3.1383 | 73.3617 | 0.28064 | 7.5 | 6.8 | 58 | 240 | 360 | 503.6501 | -39.9028 | 75.8333 | 371.825 | 84.4013 | 108 | 70 | 35 | 2.0373 | 2.7 | 4.7373 | 4.7373 | 0.27617 | 0.43006 | 12.2241 | 12.2241 | 3.5809 | 50.4191 | 0.24245 | 6.8 | 6.7 | 100 | 360 | 560 | 556.1892 | 0.6805 | 58.3333 | 458.0946 | 78.1704 | Total hardness | mg/L as CaCO3 | 52 | 210 | 460 | 457.1282 | 0.6243 | 75.2381 | 333.5641 | 84.4108 | Total hardness | mg/L as CaCO3 | 41 | 210 | 323.5 | 80.4762 | 266.75 | 84.6298 | Total hardness | mg/L as CaCO3 | 52 | 200 | 470 | 441.4737 | 6.0694 | 74 | 320.7368 | 83.7873 | Total hardness | mg/L as CaCO3 | 38 | 200 | 309.6241 | 81 | 254.812 | 85.087 | Total hardness | mg/L as CaCO3 | 50 | 200 | 400 | 398.8372 | 0.2907 | 75 | 299.4186 | 83.301 | Total hardness | mg/L as CaCO3 | 38 | 200 | 321.5702 | 81 | 260.7851 | 85.4286 | Total hardness | mg/L as CaCO3 | 48 | 210 | 420 | 424.7442 | -1.1296 | 77.1429 | 317.3721 | 84.8758 | Total hardness | mg/L as CaCO3 | 41 | 210 | 320.0094 | 80.4762 | 265.0047 | 84.5286 | Total hardness | mg/L as CaCO3 | 41 | 210 | 440 | 474.3333 | -7.803 | 80.4762 | 342.1667 | 88.0175 | Total hardness | mg/L as CaCO3 | 73 | 210 | 305.2395 | 65.2381 | 257.6198 | 71.6637 | Total hardness | mg/L as CaCO3 | 58 | 230 | 470 | 522.8649 | -11.2478 | 74.7826 | 376.4324 | 84.5922 | Total hardness | mg/L as CaCO3 | 83 | 230 | 328.7185 | 63.913 | 279.3592 | 70.2892 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.35 | Feed flow rate to system, QF-sys (gpm) | 12.5 | Turbidity (ntu) | 0.2 |  |  |  | 1990-02-21 |  | 337 | 24 | 145 | 70 | 42.5 | 0 | 8.8 | 2.7 |  | 11.5 | 11.5 | 0.76522 | 0 | 17.6 | 17.6 | 4.4704 | 60.5296 | 0.29077 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 794.0741 | -41.7989 | 70.8333 | 517.037 | 86.4613 | 145 | 110 | 50 | 6.82 | 4.68 | 11.5 | 11.5 | 0.30041 | 0.59304 | 20.46 | 20.46 | 3.1461 | 74.3539 | 0.27517 | 7.5 | 6.8 | 58 | 240 | 360 | 505.2222 | -40.3395 | 75.8333 | 372.6111 | 84.4342 | 110 | 70 | 35 | 1.98 | 2.7 | 4.68 | 4.68 | 0.27405 | 0.42308 | 11.88 | 11.88 | 3.5533 | 51.4467 | 0.23092 | 6.8 | 6.7 | 100 | 360 | 560 | 550.6667 | 1.6667 | 58.3333 | 455.3333 | 78.0381 | Calcium hardness | mg/L as CaCO3 | 44 | 180 | 410 | 392.7179 | 4.2151 | 75.5556 | 286.359 | 84.6347 | Calcium hardness | mg/L as CaCO3 | 33 | 180 | 278.7249 | 81.6667 | 229.3624 | 85.6123 | Calcium hardness | mg/L as CaCO3 | 43 | 190 | 440 | 429.8421 | 2.3086 | 77.3684 | 309.9211 | 86.1255 | Calcium hardness | mg/L as CaCO3 | 34 | 190 | 295.5639 | 82.1053 | 242.782 | 85.9957 | Calcium hardness | mg/L as CaCO3 | 47 | 190 | 370 | 379.5581 | -2.5833 | 75.2632 | 284.7791 | 83.496 | Calcium hardness | mg/L as CaCO3 | 33 | 190 | 307.818 | 82.6316 | 248.909 | 86.7421 | Calcium hardness | mg/L as CaCO3 | 46 | 190 | 340 | 380.8837 | -12.0246 | 75.7895 | 285.4419 | 83.8846 | Calcium hardness | mg/L as CaCO3 | 33 | 190 | 292.1981 | 82.6316 | 241.0991 | 86.3127 | Calcium hardness | mg/L as CaCO3 | 41 | 220 | 410 | 499.9744 | -21.945 | 81.3636 | 359.9872 | 88.6107 | Calcium hardness | mg/L as CaCO3 | 67 | 220 | 326.3624 | 69.5455 | 273.1812 | 75.4742 | Calcium hardness | mg/L as CaCO3 | 52 | 240 | 420 | 560.1081 | -33.3591 | 78.3333 | 400.0541 | 87.0018 | Calcium hardness | mg/L as CaCO3 | 76 | 240 | 350.1349 | 68.3333 | 295.0674 | 74.2432 | Current Process Water Rate ($/1000 gal) | 1.31
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 5 | SDI | 2.0 & 2.3 |  |  |  | 1990-02-22 |  | 360.4 | 24 | 140 | 60 | 37.5 | 0 | 8.8 | 2.5 |  | 11.3 | 11.3 | 0.77876 | 0 | 17.6 | 17.6 | 4.692 | 57.808 | 0.30446 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 838.4 | -49.7143 | 70.8333 | 539.2 | 87.0178 | 140 | 102 | 40 | 6.8683 | 4.4317 | 11.3 | 11.3 | 0.29209 | 0.60781 | 20.6049 | 20.6049 | 3.2303 | 77.7697 | 0.26495 | 7.5 | 6.8 | 58 | 240 | 360 | 522.0649 | -45.018 | 75.8333 | 381.0325 | 84.7782 | 102 | 60 | 35 | 1.9317 | 2.5 | 4.4317 | 4.4317 | 0.2574 | 0.43588 | 11.5902 | 11.5902 | 3.6045 | 42.3955 | 0.27338 | 6.8 | 6.7 | 100 | 360 | 560 | 560.8976 | -0.16028 | 58.3333 | 460.4488 | 78.2821 | Turbidity | ntu | 0.3 | 0.26 | 0.37 | 0.19744 | 46.6389 | -15.3846 | 0.22872 | -31.1659 | Turbidity | ntu | 0.58 | 0.26 | 0.045089 | -123.0769 | 0.15254 | -280.2172 | Turbidity | ntu | 0.07 | 0.2 | 0.36 | 0.41211 | -14.4737 | 65 | 0.30605 | 77.1281 | Turbidity | ntu | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 0 | Turbidity | ntu | 0.17 | 0.22 | 0.34 | 0.28628 | 15.8003 | 22.7273 | 0.25314 | 32.8434 | Turbidity | ntu | 0.19 | 0.22 | 0.24251 | 13.6364 | 0.23126 | 17.8401 | Turbidity | ntu | 0.06 | 0.44 | 0.64 | 0.94372 | -47.4564 | 86.3636 | 0.69186 | 91.3277 | Turbidity | ntu | 0.13 | 0.44 | 0.64179 | 70.4545 | 0.5409 | 75.9658 | Turbidity | ntu | 0.06 | 0.29 | 0.44 | 0.64974 | -47.669 | 79.3103 | 0.46987 | 87.2306 | Turbidity | ntu | 0.16 | 0.29 | 0.38037 | 44.8276 | 0.33519 | 52.2654 | Turbidity | ntu | 0.26 | 0.18 | 0.18 | 0.043784 | 75.6757 | -44.4444 | 0.11189 | -132.3671 | Turbidity | ntu | 0.12 | 0.18 | 0.22029 | 33.3333 | 0.20015 | 40.044 | Modifications to Existing Plant (% of construction costs) | NA
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI |  |  |  |  | 1990-02-22 |  | 364.2 | 24 | 146 | 73 | 40 | 0 | 8.66 | 2.52 |  | 11.18 | 11.18 | 0.7746 | 0 | 17.32 | 17.32 | 4.621 | 64.879 | 0.26696 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 824.2063 | -47.1797 | 70.8333 | 532.1032 | 86.8447 | 146 | 112 | 46 | 6.6356 | 4.5444 | 11.18 | 11.18 | 0.29195 | 0.59352 | 19.9068 | 19.9068 | 3.1487 | 79.8513 | 0.2493 | 7.5 | 6.8 | 58 | 240 | 360 | 505.7495 | -40.486 | 75.8333 | 372.8748 | 84.4452 | 112 | 73 | 34 | 2.0244 | 2.52 | 4.5444 | 4.5444 | 0.26233 | 0.44547 | 12.1465 | 12.1465 | 3.6443 | 54.8557 | 0.22143 | 6.8 | 6.7 | 100 | 360 | 560 | 568.8683 | -1.5836 | 58.3333 | 464.4341 | 78.4684 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 3.1 | 4.9133 | 87.0968 | 4.0067 | 90.0166 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.9 | 6.3361 | 92.3077 | 5.118 | 94.1384 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 3.9 | 6.5265 | 89.7436 | 5.2133 | 92.3273 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 3.6 | 5.683 | 88.8889 | 4.6415 | 91.3821 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1990-02-26 |  | 365.2 | 24 | 157 | 91 | 23.5 | 0 | 6.62 | 2.77 | X | 9.39 | 9.39 | 0.70501 | 0 | 13.24 | 13.24 | 3.7314 | 96.7686 | 0.13682 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 646.2816 | -15.4074 | 70.8333 | 443.1408 | 84.2037 | 157 | 129 | 28 | 4.7443 | 4.6457 | 9.39 | 9.39 | 0.2606 | 0.50525 | 14.233 | 14.233 | 2.7493 | 112.2507 | 0.1268 | 7.5 | 6.8 | 58 | 240 | 360 | 425.8654 | -18.2959 | 75.8333 | 332.9327 | 82.5791 | 129 | 91 | 19 | 1.8757 | 2.77 | 4.6457 | 4.6457 | 0.27537 | 0.40375 | 11.254 | 11.254 | 3.4803 | 87.5197 | 0.12859 | 6.8 | 6.7 | 100 | 360 | 560 | 536.0554 | 4.2758 | 58.3333 | 448.0277 | 77.68 | Total organic carbon | mg/L | 0.5 | 3.1 | 8.3 | 7.1667 | 13.6546 | 83.871 | 5.1333 | 90.2597 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.9 | 11 | 9.7737 | 11.1483 | 92.3077 | 6.8368 | 95.612 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.9 | 8.9 | 8.6721 | 2.5608 | 92.3077 | 6.286 | 95.2275 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.6 | 9.6 | 7.9744 | 16.9331 | 91.6667 | 5.7872 | 94.8162 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 3.5 | 8 | 8.5051 | -6.3141 | 91.4286 | 6.0026 | 95.0021 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3 | 7.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Keller Plant 2 | Total width of all membrane envelopes in the element, w (ft) | 12 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 9.1667 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1990-02-26 |  | 366.2 | 24 | 150 | 79 | 41 | 0 | 7.8 | 1.8 |  | 9.6 | 9.6 | 0.8125 | 0 | 15.6 | 15.6 | 5.3833 | 68.1167 | 0.22902 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 976.6667 | -74.4048 | 70.8333 | 608.3333 | 88.4932 | 150 | 118 | 43 | 5.7943 | 3.8057 | 9.6 | 9.6 | 0.2489 | 0.60357 | 17.3829 | 17.3829 | 3.2055 | 87.7945 | 0.19799 | 7.5 | 6.8 | 58 | 240 | 360 | 517.0991 | -43.6386 | 75.8333 | 378.5495 | 84.6784 | 118 | 79 | 39 | 2.0057 | 1.8 | 3.8057 | 3.8057 | 0.20816 | 0.52703 | 12.0343 | 12.0343 | 4.0486 | 55.4514 | 0.21702 | 6.8 | 6.7 | 100 | 360 | 560 | 649.7143 | -16.0204 | 58.3333 | 504.8571 | 80.1924 | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | ---
Treatment Plant Category | (11) Other/GW | Feed spacer thickness, T (ft) | 0.0025 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.8333 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1990-02-26 |  | 367.2 | 24 | 145 | 70 | 45.5 | 0 | 8.8 | 1.8 |  | 10.6 | 10.6 | 0.83019 | 0 | 17.6 | 17.6 | 5.8556 | 56.1444 | 0.31348 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 1071.1111 | -91.2698 | 70.8333 | 655.5556 | 89.322 | 145 | 110 | 51 | 6.7158 | 3.8842 | 10.6 | 10.6 | 0.26892 | 0.63357 | 20.1474 | 20.1474 | 3.3934 | 73.1066 | 0.27559 | 7.5 | 6.8 | 58 | 240 | 360 | 554.6775 | -54.0771 | 75.8333 | 397.3388 | 85.4029 | 110 | 70 | 40 | 2.0842 | 1.8 | 3.8842 | 3.8842 | 0.21107 | 0.53659 | 12.5053 | 12.5053 | 4.1053 | 45.8947 | 0.27248 | 6.8 | 6.7 | 100 | 360 | 560 | 661.0526 | -18.0451 | 58.3333 | 510.5263 | 80.4124 | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | ---
Process Train Name | Cascade Aeration | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1990-02-28 |  | 368.4 | 24 | 140 | 67 | 52.5 | 0 | 9.3 | 2.7 | X | 12 | 12 | 0.775 | 0 | 18.6 | 18.6 | 4.6278 | 46.3722 | 0.4011 | 7.5 | 7.5 | 70 | 240 | 240 | 560 | 825.5556 | -47.4206 | 70.8333 | 532.7778 | 86.8613 | 140 | 105 | 60 | 7.2212 | 4.7788 | 12 | 12 | 0.31153 | 0.60176 | 21.6635 | 21.6635 | 3.1951 | 59.3049 | 0.36529 | 7.5 | 6.8 | 58 | 240 | 360 | 515.0162 | -43.0601 | 75.8333 | 377.5081 | 84.6361 | 105 | 67 | 45 | 2.0788 | 2.7 | 4.7788 | 4.7788 | 0.27771 | 0.43501 | 12.4729 | 12.4729 | 3.6009 | 37.3991 | 0.33351 | 6.8 | 6.7 | 100 | 360 | 560 | 560.183 | -0.03268 | 58.3333 | 460.0915 | 78.2652 | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 717 | Purchase price for an equivalent 8" x 40 " element ($) | 500 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1990-03-05 |  | 368.5 | 24 | 145 | 44 | 58.5 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 31.7784 | 0.42167 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 145 | 100 | 87 | 4.4667 | 6.7333 | 11.2 | 11.2 | 0.33296 | 0.39881 | 13.4 | 13.4 | 3.4624 | 32.0376 | 0.41826 | 6.6 | 6.7 | 60 | 320 | 450 | 492.4752 | -9.4389 | 81.25 | 406.2376 | 85.2303 | 100 | 44 | 30 | 2.2333 | 4.5 | 6.7333 | 6.7333 | 0.41713 | 0.33168 | 13.4 | 13.4 | 4.2437 | 37.7563 | 0.35491 | 6.7 | 6.8 | 110 | 450 | 670 | 618.7407 | 7.6506 | 65.625 | 534.3704 | 79.415 | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL6521405 |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -1.1667 | [5 empty] | 1990-03-06 |  | 391.5 | 24 | 145 | 45 | 57.5 | 0 | 6.7 | 4.4 |  | 11.1 | 11.1 | 0.6036 | 0 | 13.4 | 13.4 | 4.2625 | 33.2375 | 0.40316 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 688.5 | -2.7612 | 75.625 | 504.25 | 84.5315 | 145 | 100 | 85 | 4.6063 | 6.4938 | 11.1 | 11.1 | 0.32666 | 0.41498 | 13.8187 | 13.8187 | 3.5221 | 33.9779 | 0.4067 | 6.6 | 6.7 | 60 | 320 | 450 | 504.4273 | -12.095 | 81.25 | 412.2137 | 85.4444 | 100 | 45 | 30 | 2.0938 | 4.4 | 6.4938 | 6.4938 | 0.40452 | 0.32243 | 12.5625 | 12.5625 | 4.2089 | 38.2911 | 0.32808 | 6.7 | 6.8 | 110 | 450 | 670 | 611.7898 | 8.6881 | 65.625 | 530.8949 | 79.2803 | SDS-Free Cl2 residual | mg/L | 3.9 | 1.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.34 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.5 | 0.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.35 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 4.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.26 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 2.2 | 1.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.29 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.2 | 3.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.33 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.5 | 5.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.38
Historical Minimum Water Temperature (oC) | 22 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -1.8333 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1990-03-07 |  | 415.9 | 24 | 145 | 44 | 57.5 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 32.7784 | 0.40881 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 145 | 99 | 85 | 4.5354 | 6.6646 | 11.2 | 11.2 | 0.33169 | 0.40495 | 13.6062 | 13.6062 | 3.4847 | 33.5153 | 0.40597 | 6.6 | 6.7 | 60 | 320 | 450 | 496.9344 | -10.4299 | 81.25 | 408.4672 | 85.3109 | 99 | 44 | 30 | 2.1646 | 4.5 | 6.6646 | 6.6646 | 0.41458 | 0.32479 | 12.9877 | 12.9877 | 4.2177 | 37.2823 | 0.34836 | 6.7 | 6.8 | 110 | 450 | 670 | 613.5487 | 8.4256 | 65.625 | 531.7744 | 79.3145 | SDS-Cl2 demand | mg/L | 1.1 | 10.9 | --- | 26.2282 | --- | 89.9083 | 18.5641 | 94.0746 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.32 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.5 | 12.3 | --- | 26.6579 | --- | 71.5447 | 19.4789 | 82.0319 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.36 |  |  |  |  | SDS-Cl2 demand | mg/L | 4 | 7.7 | --- | 12.6047 | --- | 48.0519 | 10.1523 | 60.6002 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 1.47 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.8 | 10.7 | --- | 21.1721 | --- | 73.8318 | 15.936 | 82.4298 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 1.86 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.8 | 9 | --- | 20.2615 | --- | 80 | 14.6308 | 87.6972 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.13 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.5 | 7.3 | --- | 17.1757 | --- | 79.4521 | 12.2378 | 87.7429 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.62
Historical Average Water Temperature (oC) | 24 | Design cross-flow velocity (fps) | 0.257 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1990-03-08 |  | 435.4 | 24 | 146 | 48 | 58.5 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.29 | 34.21 | 0.39754 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 694 | -3.5821 | 75.625 | 507 | 84.6154 | 146 | 100 | 87 | 4.5333 | 6.6667 | 11.2 | 11.2 | 0.33173 | 0.40476 | 13.6 | 13.6 | 3.484 | 32.516 | 0.41826 | 6.6 | 6.7 | 60 | 320 | 450 | 496.8 | -10.4 | 81.25 | 408.4 | 85.3085 | 100 | 48 | 30 | 2.2667 | 4.4 | 6.6667 | 6.6667 | 0.41094 | 0.34 | 13.6 | 13.6 | 4.2758 | 39.7242 | 0.34236 | 6.7 | 6.8 | 110 | 450 | 670 | 625.1515 | 6.6938 | 65.625 | 537.5758 | 79.5378 | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.76 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.65 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 5.77 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.36 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.43 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.82
State Approved Plant Capacity (MGD) | 50 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1990-03-09 |  | 459.9 | 24 | 145 | 50 | 58 | 0 | 7.1 | 4.4 |  | 11.5 | 11.5 | 0.61739 | 0 | 14.2 | 14.2 | 4.3725 | 35.1275 | 0.40424 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 710.5 | -6.0448 | 75.625 | 515.25 | 84.8617 | 145 | 100 | 86 | 4.7333 | 6.7667 | 11.5 | 11.5 | 0.33915 | 0.41159 | 14.2 | 14.2 | 3.5094 | 32.9906 | 0.43043 | 6.6 | 6.7 | 60 | 320 | 450 | 501.8719 | -11.5271 | 81.25 | 410.936 | 85.3992 | 100 | 50 | 30 | 2.3667 | 4.4 | 6.7667 | 6.7667 | 0.41466 | 0.34975 | 14.2 | 14.2 | 4.3144 | 40.6856 | 0.34902 | 6.7 | 6.8 | 110 | 450 | 670 | 632.8788 | 5.5405 | 65.625 | 541.4394 | 79.6838 | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 1990-03-12 |  | 528.7 | 24 | 145 | 49 | 58 | 0 | 7.1 | 4.5 |  | 11.6 | 11.6 | 0.61207 | 0 | 14.2 | 14.2 | 4.3291 | 34.6709 | 0.40957 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 701.8222 | -4.7496 | 75.625 | 510.9111 | 84.7332 | 145 | 100 | 86 | 4.7333 | 6.8667 | 11.6 | 11.6 | 0.34287 | 0.40805 | 14.2 | 14.2 | 3.4961 | 33.0039 | 0.43025 | 6.6 | 6.7 | 60 | 320 | 450 | 499.2233 | -10.9385 | 81.25 | 409.6117 | 85.352 | 100 | 49 | 30 | 2.3667 | 4.5 | 6.8667 | 6.8667 | 0.42208 | 0.34466 | 14.2 | 14.2 | 4.2941 | 40.2059 | 0.35318 | 6.7 | 6.8 | 110 | 450 | 670 | 628.8148 | 6.147 | 65.625 | 539.4074 | 79.6073 | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) |  | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1990-03-13 |  | 553.7 | 24 | 145 | 50 | 57.5 | 0 | 7.2 | 4.6 |  | 11.8 | 11.8 | 0.61017 | 0 | 14.4 | 14.4 | 4.3139 | 35.6861 | 0.40352 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 698.7826 | -4.2959 | 75.625 | 509.3913 | 84.6876 | 145 | 100 | 85 | 4.8343 | 6.9657 | 11.8 | 11.8 | 0.34842 | 0.40969 | 14.5029 | 14.5029 | 3.5022 | 33.9978 | 0.42658 | 6.6 | 6.7 | 60 | 320 | 450 | 500.443 | -11.2096 | 81.25 | 410.2215 | 85.3738 | 100 | 50 | 30 | 2.3657 | 4.6 | 6.9657 | 6.9657 | 0.42948 | 0.33962 | 14.1943 | 14.1943 | 4.2743 | 40.7257 | 0.34853 | 6.7 | 6.8 | 110 | 450 | 670 | 624.8571 | 6.7377 | 65.625 | 537.4286 | 79.5322 | SDS-TOX | mg Cl- /L | 32 | 400 | --- | 975.5897 | --- | 92 | 687.7949 | 95.3475 | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 42 | 280 | --- | 668.3158 | --- | 85 | 474.1579 | 91.1422 | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 27 | 420 | --- | 940.9535 | --- | 93.5714 | 680.4767 | 96.0322 | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 140 | 510 | --- | 1000.4651 | --- | 72.549 | 755.2326 | 81.4627 | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 21 | 430 | --- | 1069.7179 | --- | 95.1163 | 749.859 | 97.1995 | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 33 | 460 | --- | 1187.0541 | --- | 92.8261 | 823.527 | 95.9928 | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95 % at 2000 ppm | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 19.5 | [5 empty] | 1990-03-14 |  | 576.7 | 24 | 145 | 50 | 57.5 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.29 | 35.71 | 0.38085 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 694 | -3.5821 | 75.625 | 507 | 84.6154 | 145 | 100 | 85 | 4.5333 | 6.6667 | 11.2 | 11.2 | 0.33173 | 0.40476 | 13.6 | 13.6 | 3.484 | 34.016 | 0.39981 | 6.6 | 6.7 | 60 | 320 | 450 | 496.8 | -10.4 | 81.25 | 408.4 | 85.3085 | 100 | 50 | 30 | 2.2667 | 4.4 | 6.6667 | 6.6667 | 0.41094 | 0.34 | 13.6 | 13.6 | 4.2758 | 40.7242 | 0.33395 | 6.7 | 6.8 | 110 | 450 | 670 | 625.1515 | 6.6938 | 65.625 | 537.5758 | 79.5378 | SDS-CHCl3 | mg/L | 5 | 96 | --- | 238.3333 | --- | 94.7917 | 167.1667 | 97.009 | Sampling date | MM/DD/YY | 1990-03-20 | 1990-03-20 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 31 | --- | 76.6842 | --- | 90.3226 | 53.8421 | 94.4282 | Sampling date | MM/DD/YY | 1990-06-12 | 1990-06-12 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 2 | 84 | --- | 192.6977 | --- | 97.619 | 138.3488 | 98.5544 | Sampling date | MM/DD/YY | 1990-07-12 | 1990-07-12 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 2 | 110 | --- | 253.1628 | --- | 98.1818 | 181.5814 | 98.8986 | Sampling date | MM/DD/YY | 1990-08-28 | 1990-08-28 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 8 | 120 | --- | 295.1795 | --- | 93.3333 | 207.5897 | 96.1462 | Sampling date | MM/DD/YY | 1990-10-02 | 1990-10-02 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 6 | 120 | --- | 314.1081 | --- | 95 | 217.0541 | 97.2357 | Sampling date | MM/DD/YY | 1990-11-05 | 1990-11-05 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | MgSO4 solution | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 8.5 | [5 empty] | 1990-03-15 |  | 597.7 | 24 | 145 | 50 | 57.5 | 0 | 6.8 | 4.3 |  | 11.1 | 11.1 | 0.61261 | 0 | 13.6 | 13.6 | 4.3335 | 35.6665 | 0.38131 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 702.6977 | -4.8802 | 75.625 | 511.3488 | 84.7462 | 145 | 100 | 85 | 4.4657 | 6.6343 | 11.1 | 11.1 | 0.32927 | 0.40231 | 13.397 | 13.397 | 3.4751 | 34.0249 | 0.39374 | 6.6 | 6.7 | 60 | 320 | 450 | 495.0101 | -10.0022 | 81.25 | 407.5051 | 85.2763 | 100 | 50 | 30 | 2.3343 | 4.3 | 6.6343 | 6.6343 | 0.40603 | 0.35186 | 14.006 | 14.006 | 4.3229 | 40.6771 | 0.34432 | 6.7 | 6.8 | 110 | 450 | 670 | 634.5748 | 5.2873 | 65.625 | 542.2874 | 79.7156 | SDS-BDCM | mg/L | 7 | 20 | --- | 40.3333 | --- | 65 | 30.1667 | 76.7956 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 3 | 12 | --- | 26.6842 | --- | 75 | 19.3421 | 84.4898 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | 19 | --- | 41.5349 | --- | 89.4737 | 30.2674 | 93.3922 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | 19 | --- | 41.5349 | --- | 89.4737 | 30.2674 | 93.3922 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 5 | 15 | --- | 30.641 | --- | 66.6667 | 22.8205 | 78.0899 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 4 | 14 | --- | 31.027 | --- | 71.4286 | 22.5135 | 82.2329 | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | [8 empty] | 1990-03-16 |  | 621.7 | 24 | 145 | 49 | 57.5 | 0 | 6.8 | 4.8 |  | 11.6 | 11.6 | 0.58621 | 0 | 13.6 | 13.6 | 4.1342 | 35.3658 | 0.38455 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 662.8333 | 1.0697 | 75.625 | 491.4167 | 84.1275 | 145 | 100 | 85 | 4.4686 | 7.1314 | 11.6 | 11.6 | 0.34778 | 0.38522 | 13.4057 | 13.4057 | 3.4146 | 34.0854 | 0.3933 | 6.6 | 6.7 | 60 | 320 | 450 | 482.9167 | -7.3148 | 81.25 | 401.4583 | 85.0545 | 100 | 49 | 30 | 2.3314 | 4.8 | 7.1314 | 7.1314 | 0.44306 | 0.32692 | 13.9886 | 13.9886 | 4.2257 | 40.2743 | 0.34733 | 6.7 | 6.8 | 110 | 450 | 670 | 615.1429 | 8.1876 | 65.625 | 532.5714 | 79.3455 | SDS-DBCM | mg/L | 5 | 3 | --- | -0.12821 | --- | -66.6667 | 1.4359 | -248.2143 | Operation time | hh.hh | 713.9 | 713.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2641.7 | 2641.7 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | 2 | --- | 2 | --- | 0 | 2 | 0 | Operation time | hh.hh | 3306.6 | 3306.6 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4120.4 | 4120.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4798.4 | 4798.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5598.6 | 5598.6 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1990-03-19 |  | 694 | 24 | 145 | 50 | 57.5 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 4.2075 | 35.7925 | 0.3632 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 677.5 | -1.1194 | 75.625 | 498.75 | 84.3609 | 145 | 100 | 85 | 4.3333 | 6.5667 | 10.9 | 10.9 | 0.3243 | 0.39755 | 13 | 13 | 3.4579 | 34.0421 | 0.38188 | 6.6 | 6.7 | 60 | 320 | 450 | 491.5736 | -9.2386 | 81.25 | 405.7868 | 85.2139 | 100 | 50 | 30 | 2.1667 | 4.4 | 6.5667 | 6.5667 | 0.40723 | 0.32995 | 13 | 13 | 4.2371 | 40.7629 | 0.31892 | 6.7 | 6.8 | 110 | 450 | 670 | 617.4242 | 7.8471 | 65.625 | 533.7121 | 79.3896 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.2 | 6.7 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.9 | 6.8 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.8 | 6.9 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.8 | 7 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.1 | 6.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6 | 6.1 | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1990-03-20 |  | 713.9 | 24 | 145 | 50 | 58 | 0 | 6.86 | 4.44 |  | 11.3 | 11.3 | 0.60708 | 0 | 13.72 | 13.72 | 4.2895 | 35.2105 | 0.38966 | 7.5 | 6.6 | 78 | 260 | 320 | 670 | 693.9009 | -3.5673 | 75.625 | 506.9505 | 84.6139 | 145 | 100 | 86 | 4.5382 | 6.7618 | 11.3 | 11.3 | 0.33535 | 0.40161 | 13.6145 | 13.6145 | 3.4725 | 33.0275 | 0.41222 | 6.6 | 6.7 | 60 | 320 | 450 | 494.4967 | -9.8882 | 81.25 | 407.2484 | 85.267 | 100 | 50 | 30 | 2.3218 | 4.44 | 6.7618 | 6.7618 | 0.41596 | 0.34337 | 13.9311 | 13.9311 | 4.289 | 40.711 | 0.34219 | 6.7 | 6.8 | 110 | 450 | 670 | 627.799 | 6.2987 | 65.625 | 538.8995 | 79.588 | SDS-THM4 | mg/L | 17 | 119 | --- | 278.5385 | --- | 85.7143 | 198.7692 | 91.4474 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 6 | 43 | --- | 103.3684 | --- | 86.0465 | 73.1842 | 91.8015 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 6 | 105 | --- | 236.2326 | --- | 94.2857 | 170.6163 | 96.4833 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 4 | 129 | --- | 294.6977 | --- | 96.8992 | 211.8488 | 98.1119 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 14 | 135 | --- | 324.2564 | --- | 89.6296 | 229.6282 | 93.9032 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 12 | 134 | --- | 341.7297 | --- | 91.0448 | 237.8649 | 94.9551 | Temperature | oC | NA | NA | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 - 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 8.5 | [5 empty] | 1990-03-21 |  | 737.1 | 24 | 146 | 50 | 57.5 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.2753 | 36.2247 | 0.38096 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 691.0667 | -3.1443 | 75.625 | 505.5333 | 84.5708 | 146 | 100 | 85 | 4.5313 | 6.8687 | 11.4 | 11.4 | 0.33919 | 0.39749 | 13.594 | 13.594 | 3.4576 | 34.5424 | 0.39355 | 5.9 | 5.6 | 60 | 320 | 450 | 491.5254 | -9.2279 | 81.25 | 405.7627 | 85.213 | 100 | 50 | 30 | 2.3687 | 4.5 | 6.8687 | 6.8687 | 0.42216 | 0.34485 | 14.2119 | 14.2119 | 4.2948 | 40.7052 | 0.34914 | 5.6 | 5.5 | 110 | 450 | 670 | 628.9652 | 6.1246 | 65.625 | 539.4826 | 79.6101 | SDS-MCAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 54 | 250 | 352.4144 | 58.4615 | 301.2072 | 82.0721 | SDS-MCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 72 | 310 | 440.9277 | 65.7143 | 375.4639 | 80.8237 | SDS-MCAA* | mg/L | 1 | 5 | --- | 10.3023 | --- | 80 | 7.6512 | 86.9301 | Alkalinity | mg/L as CaCO3 | 82 | 360 | 455.0372 | 62.7273 | 407.5186 | 79.8782 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 84 | 360 | 474.08 | 63.4783 | 417.04 | 79.858 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 60 | 180 | 239.4419 | 62.5 | 209.7209 | 71.3906 | SDS-MCAA* | mg/L | 2 | 9 | --- | 20.9189 | --- | 77.7778 | 14.9595 | 86.6305 | Alkalinity | mg/L as CaCO3 | 42 | 140 | 201.1333 | 57.1429 | 170.5667 | 75.3762
|  | Acceptable range of operating pH values | 3 - 9 | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1990-03-22 |  | 760.7 | 24 | 145 | 50 | 59.5 | 0 | 6.5 | 4.5 |  | 11 | 11 | 0.59091 | 0 | 13 | 13 | 4.1678 | 33.8322 | 0.38425 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 669.5556 | 0.066335 | 75.625 | 494.7778 | 84.2353 | 145 | 100 | 86 | 4.3333 | 6.6667 | 11 | 11 | 0.32801 | 0.39394 | 13 | 13 | 3.445 | 33.055 | 0.39328 | 5.9 | 5.6 | 60 | 320 | 450 | 489 | -8.6667 | 81.25 | 404.5 | 85.1669 | 100 | 50 | 33 | 2.1667 | 4.5 | 6.6667 | 6.6667 | 0.41466 | 0.325 | 13 | 13 | 4.2185 | 37.7815 | 0.34408 | 5.6 | 5.5 | 110 | 450 | 670 | 613.7037 | 8.4024 | 65.625 | 531.8519 | 79.3175 | SDS-DCAA* | mg/L | 1 | 7 | --- | 16.3846 | --- | 85.7143 | 11.6923 | 91.4474 | Total dissolved solids | mg/L | 110 | 450 | 627.6577 | 65.625 | 538.8288 | 79.5854 | SDS-DCAA* | mg/L | 6 | 26 | --- | 58.6316 | --- | 76.9231 | 42.3158 | 85.8209 | Total dissolved solids | mg/L | 100 | 360 | 503.0303 | 58.3333 | 431.5152 | 76.8258 | SDS-DCAA* | mg/L | BMRL | 5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 58 | 260 | 329.0558 | 77.6923 | 294.5279 | 80.3075 | SDS-DCAA* | mg/L | 1 | 43 | --- | 98.6744 | --- | 97.6744 | 70.8372 | 98.5883 | Total dissolved solids | mg/L | 98 | 370 | 482.4267 | 60.8 | 426.2133 | 77.0068 | SDS-DCAA* | mg/L | 3 | 39 | --- | 95.3077 | --- | 92.3077 | 67.1538 | 95.5326 | Total dissolved solids | mg/L | 110 | 440 | 603.4651 | 67.6471 | 521.7326 | 78.9164 | SDS-DCAA* | mg/L | 4 | 56 | --- | 144.5405 | --- | 92.8571 | 100.2703 | 96.0108 | Total dissolved solids | mg/L | 84 | 510 | 775.7429 | 76 | 642.8714 | 86.9336
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 12.5 | [5 empty] | 1990-03-23 |  | 786 | 24 | 145 | 50 | 59 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 34.1978 | 0.40938 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 145 | 100 | 86 | 4.6667 | 6.8333 | 11.5 | 11.5 | 0.34039 | 0.4058 | 14 | 14 | 3.4878 | 33.0122 | 0.42409 | 5.9 | 5.6 | 60 | 320 | 450 | 497.561 | -10.5691 | 81.25 | 408.7805 | 85.3222 | 100 | 50 | 32 | 2.3333 | 4.5 | 6.8333 | 6.8333 | 0.42085 | 0.34146 | 14 | 14 | 4.2815 | 38.7185 | 0.36158 | 5.6 | 5.5 | 110 | 450 | 670 | 626.2963 | 6.5229 | 65.625 | 538.1481 | 79.5595 | SDS-TCAA* | mg/L | 1 | 10 | --- | 24.0769 | --- | 90 | 17.0385 | 94.1309 | Total hardness | mg/L as CaCO3 | 73 | 310 | 433.8378 | 65.2381 | 371.9189 | 80.3721 | SDS-TCAA* | mg/L | 2 | 25 | --- | 62.5263 | --- | 92 | 43.7632 | 95.4299 | Total hardness | mg/L as CaCO3 | 64 | 310 | 445.3287 | 68 | 377.6643 | 83.0537 | SDS-TCAA* | mg/L | 1 | 19 | --- | 42.8605 | --- | 94.7368 | 30.9302 | 96.7669 | Total hardness | mg/L as CaCO3 | 71 | 300 | 378.286 | 64.5 | 339.143 | 79.0649 | SDS-TCAA* | mg/L | 1 | 39 | --- | 89.3721 | --- | 97.4359 | 64.186 | 98.442 | Total hardness | mg/L as CaCO3 | 70 | 310 | 409.2 | 66.6667 | 359.6 | 80.5339 | SDS-TCAA* | mg/L | 2 | 46 | --- | 114.8205 | --- | 95.6522 | 80.4103 | 97.5128 | Total hardness | mg/L as CaCO3 | 62 | 350 | 492.6605 | 70.4762 | 421.3302 | 85.2847 | SDS-TCAA* | mg/L | 2 | 37 | --- | 96.5946 | --- | 94.5946 | 66.7973 | 97.0059 | Total hardness | mg/L as CaCO3 | 84 | 340 | 499.6952 | 63.4783 | 419.8476 | 79.9927
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [5 empty] | 1990-03-26 |  | 853.7 | 24 | 145 | 50 | 55.5 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 4.345 | 37.655 | 0.3718 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 705 | -5.2239 | 75.625 | 512.5 | 84.7805 | 145 | 100 | 84 | 4.597 | 6.803 | 11.4 | 11.4 | 0.33797 | 0.40325 | 13.791 | 13.791 | 3.4785 | 35.0215 | 0.39379 | 5.9 | 5.6 | 60 | 320 | 450 | 495.6911 | -10.1536 | 81.25 | 407.8455 | 85.2885 | 100 | 50 | 27 | 2.403 | 4.4 | 6.803 | 6.803 | 0.41601 | 0.35323 | 14.4179 | 14.4179 | 4.3284 | 43.6716 | 0.33014 | 5.6 | 5.5 | 110 | 450 | 670 | 635.6852 | 5.1216 | 65.625 | 542.8426 | 79.7363 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 55 | 270 | 382.3423 | 69.4444 | 326.1712 | 83.1377 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 60 | 280 | 401.0256 | 68.4211 | 340.5128 | 82.3795 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 64 | 290 | 367.2605 | 66.3158 | 328.6302 | 80.5252 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 64 | 280 | 369.28 | 66.3158 | 324.64 | 80.2859 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 62 | 260 | 358.0791 | 71.8182 | 309.0395 | 79.9378 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 74 | 300 | 440.981 | 69.1667 | 370.4905 | 80.0265
|  | Maximum permissible turbidity (ntu) | not reported | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1990-03-27 |  | 876 | 24 | 145 | 50 | 58 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.2753 | 35.2247 | 0.39177 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 691.0667 | -3.1443 | 75.625 | 505.5333 | 84.5708 | 145 | 99 | 85 | 4.4647 | 6.9353 | 11.4 | 11.4 | 0.34043 | 0.39164 | 13.3941 | 13.3941 | 3.4369 | 33.5631 | 0.39907 | 5.9 | 5.6 | 60 | 320 | 450 | 487.3791 | -8.3065 | 81.25 | 403.6896 | 85.1371 | 99 | 50 | 31 | 2.4353 | 4.5 | 6.9353 | 6.9353 | 0.42463 | 0.35115 | 14.6118 | 14.6118 | 4.32 | 39.18 | 0.37294 | 5.6 | 5.5 | 110 | 450 | 670 | 634 | 5.3731 | 65.625 | 542 | 79.7048 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 1.5 | 0.24 | -0.41838 | -476.9231 | -0.089189 | 1781.8182 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.19 | 0.18 | 0.1745 | 5 | 0.17725 | -7.1936 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.12 | 0.29 | 0.34812 | 45.4545 | 0.31906 | 62.3893 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.08 | 0.58 | 0.78667 | 81.8182 | 0.68333 | 88.2927 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.12 | 0.86 | 1.2266 | 58.6207 | 1.0433 | 88.4978 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 1 | 0.38 | -0.0067619 | -455.5556 | 0.18662 | -435.851
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 free chlorine | maximum system recycle flow rates. | [6 empty] | 1990-03-28 |  | 901.3 | 24 | 146 | 50 | 58 | 0 | 7.1 | 4.4 |  | 11.5 | 11.5 | 0.61739 | 0 | 14.2 | 14.2 | 4.3725 | 35.6275 | 0.39857 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 710.5 | -6.0448 | 75.625 | 515.25 | 84.8617 | 146 | 100 | 86 | 4.6627 | 6.8373 | 11.5 | 11.5 | 0.34046 | 0.40545 | 13.9881 | 13.9881 | 3.4865 | 33.5135 | 0.41739 | 5.9 | 5.6 | 60 | 320 | 450 | 497.3063 | -10.5125 | 81.25 | 408.6531 | 85.3176 | 100 | 50 | 30 | 2.4373 | 4.4 | 6.8373 | 6.8373 | 0.41728 | 0.35647 | 14.6239 | 14.6239 | 4.3417 | 40.6583 | 0.35968 | 5.6 | 5.5 | 110 | 450 | 670 | 638.3379 | 4.7257 | 65.625 | 544.1689 | 79.7857 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.6 | 5.4 | 7.9081 | 80.6452 | 6.6541 | 90.9829 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 6.2 | 9.3907 | 89.7436 | 7.7953 | 94.8687 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 6.5 | 8.5853 | 89.7436 | 7.5427 | 94.6968 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.5 | 5.2 | 7.5281 | 85.7143 | 6.3641 | 92.1434 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 4.8 | 7.5448 | 86.6667 | 6.1724 | 93.5195
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1990-03-29 |  | 924.5 | 24 | 145 | 50 | 56.5 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.2484 | 36.7516 | 0.37005 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 685.6889 | -2.3416 | 75.625 | 502.8444 | 84.4882 | 145 | 100 | 85 | 4.4657 | 6.8343 | 11.3 | 11.3 | 0.3367 | 0.39519 | 13.397 | 13.397 | 3.4494 | 34.0506 | 0.39344 | 5.9 | 5.6 | 60 | 320 | 450 | 489.8886 | -8.8641 | 81.25 | 404.9443 | 85.1831 | 100 | 50 | 28 | 2.3343 | 4.5 | 6.8343 | 6.8343 | 0.42088 | 0.34156 | 14.006 | 14.006 | 4.2819 | 42.7181 | 0.32787 | 5.6 | 5.5 | 110 | 450 | 670 | 626.3715 | 6.5117 | 65.625 | 538.1857 | 79.561 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1990-03-30 |  | 947.7 | 24 | 144 | 48 | 56 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 4.345 | 35.655 | 0.39265 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 705 | -5.2239 | 75.625 | 512.5 | 84.7805 | 144 | 98 | 84 | 4.5294 | 6.8706 | 11.4 | 11.4 | 0.33923 | 0.39732 | 13.5882 | 13.5882 | 3.457 | 33.543 | 0.4051 | 5.9 | 5.6 | 60 | 320 | 450 | 491.4041 | -9.2009 | 81.25 | 405.7021 | 85.2108 | 98 | 48 | 28 | 2.4706 | 4.4 | 6.8706 | 6.8706 | 0.41852 | 0.35959 | 14.8235 | 14.8235 | 4.3545 | 40.6455 | 0.3647 | 5.6 | 5.5 | 110 | 450 | 670 | 640.9091 | 4.3419 | 65.625 | 545.4545 | 79.8333 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 12.5 | [5 empty] | 1990-04-02 |  | 1015.4 | 24 | 145 | 49 | 55 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 4.345 | 37.655 | 0.3718 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 705 | -5.2239 | 75.625 | 512.5 | 84.7805 | 145 | 100 | 85 | 4.6 | 6.8 | 11.4 | 11.4 | 0.33791 | 0.40351 | 13.8 | 13.8 | 3.4794 | 34.0206 | 0.40564 | 5.9 | 5.6 | 60 | 320 | 450 | 495.8824 | -10.1961 | 81.25 | 407.9412 | 85.292 | 100 | 49 | 25 | 2.4 | 4.4 | 6.8 | 6.8 | 0.4159 | 0.35294 | 14.4 | 14.4 | 4.3273 | 45.1727 | 0.31878 | 5.6 | 5.5 | 110 | 450 | 670 | 635.4545 | 5.156 | 65.625 | 542.7273 | 79.732 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5 | [5 empty] | 1990-04-03 |  | 1035.4 | 24 | 145 | 50 | 57.5 | 0 | 6.84 | 4.37 |  | 11.21 | 11.21 | 0.61017 | 0 | 13.68 | 13.68 | 4.3139 | 35.6861 | 0.38334 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 698.7826 | -4.2959 | 75.625 | 509.3913 | 84.6876 | 145 | 99 | 85 | 4.5249 | 6.6851 | 11.21 | 11.21 | 0.33225 | 0.40365 | 13.5748 | 13.5748 | 3.4799 | 33.5201 | 0.40497 | 5.9 | 5.6 | 60 | 320 | 450 | 495.986 | -10.2191 | 81.25 | 407.993 | 85.2939 | 99 | 50 | 30 | 2.3151 | 4.37 | 6.6851 | 6.6851 | 0.41051 | 0.34631 | 13.8905 | 13.8905 | 4.3006 | 40.1994 | 0.34554 | 5.6 | 5.5 | 110 | 450 | 670 | 630.1204 | 5.9522 | 65.625 | 540.0602 | 79.6319 | SDS-HAA5 | mg/L | 2 | 18 | --- | 43.0256 | --- | 88.8889 | 30.5128 | 93.4454 | [8 empty] | SDS-HAA5 | mg/L | 8 | 64 | --- | 155.3684 | --- | 87.5 | 109.6842 | 92.7063 | [8 empty] | SDS-HAA5 | mg/L | 2 | 29 | --- | 64.7907 | --- | 93.1034 | 46.8953 | 95.7352 | [8 empty] | SDS-HAA5 | mg/L | 2 | 82 | --- | 188.0465 | --- | 97.561 | 135.0233 | 98.5188 | [8 empty] | SDS-HAA5 | mg/L | 5 | 85 | --- | 210.1282 | --- | 94.1176 | 147.5641 | 96.6116 | [8 empty] | SDS-HAA5 | mg/L | 8 | 102 | --- | 262.0541 | --- | 92.1569 | 182.027 | 95.605
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 7.5 | [5 empty] | 1990-04-04 |  | 1059.7 | 24 | 145 | 50 | 56.5 | 0 | 6.9 | 4.6 |  | 11.5 | 11.5 | 0.6 | 0 | 13.8 | 13.8 | 4.235 | 36.765 | 0.37536 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 683 | -1.9403 | 75.625 | 501.5 | 84.4467 | 145 | 100 | 85 | 4.4284 | 7.0716 | 11.5 | 11.5 | 0.34481 | 0.38507 | 13.2851 | 13.2851 | 3.4141 | 34.0859 | 0.38975 | 5.9 | 5.6 | 60 | 320 | 450 | 482.8155 | -7.2923 | 81.25 | 401.4078 | 85.0526 | 100 | 50 | 28 | 2.4716 | 4.6 | 7.0716 | 7.0716 | 0.43341 | 0.34951 | 14.8299 | 14.8299 | 4.3134 | 42.6866 | 0.34741 | 5.6 | 5.5 | 110 | 450 | 670 | 632.6866 | 5.5692 | 65.625 | 541.3433 | 79.6802 | SDS-HAA6 | mg/L | 2 | 18 | --- | 43.0256 | --- | 88.8889 | 30.5128 | 93.4454 | [8 empty] | SDS-HAA6 | mg/L | 8 | 64 | --- | 155.3684 | --- | 87.5 | 109.6842 | 92.7063 | [8 empty] | SDS-HAA6 | mg/L | 2 | 29 | --- | 64.7907 | --- | 93.1034 | 46.8953 | 95.7352 | [8 empty] | SDS-HAA6 | mg/L | 2 | 82 | --- | 188.0465 | --- | 97.561 | 135.0233 | 98.5188 | [8 empty] | SDS-HAA6 | mg/L | 5 | 85 | --- | 210.1282 | --- | 94.1176 | 147.5641 | 96.6116 | [8 empty] | SDS-HAA6 | mg/L | 8 | 102 | --- | 262.0541 | --- | 92.1569 | 182.027 | 95.605
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 7.5 | [5 empty] | 1990-04-05 |  | 1085.1 | 24 | 145 | 50 | 56.5 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 36.6978 | 0.38149 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 145 | 99 | 84 | 4.597 | 6.903 | 11.5 | 11.5 | 0.34168 | 0.39974 | 13.791 | 13.791 | 3.4657 | 34.5343 | 0.39934 | 5.9 | 5.6 | 60 | 320 | 450 | 493.1459 | -9.588 | 81.25 | 406.573 | 85.2425 | 99 | 50 | 29 | 2.403 | 4.5 | 6.903 | 6.903 | 0.42343 | 0.34811 | 14.4179 | 14.4179 | 4.3078 | 41.1922 | 0.35002 | 5.6 | 5.5 | 110 | 450 | 670 | 631.5589 | 5.7375 | 65.625 | 540.7794 | 79.659 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.5 | [5 empty] | 1990-04-06 |  | 1106.5 | 24 | 144 | 50 | 57 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 35.6978 | 0.39218 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 144 | 99 | 84 | 4.7015 | 6.7985 | 11.5 | 11.5 | 0.33974 | 0.40883 | 14.1045 | 14.1045 | 3.499 | 34.001 | 0.41483 | 5.9 | 5.6 | 60 | 320 | 450 | 499.8024 | -11.0672 | 81.25 | 409.9012 | 85.3623 | 99 | 50 | 30 | 2.2985 | 4.5 | 6.7985 | 6.7985 | 0.41955 | 0.33809 | 13.791 | 13.791 | 4.2683 | 40.2317 | 0.34279 | 5.6 | 5.5 | 110 | 450 | 670 | 623.665 | 6.9157 | 65.625 | 536.8325 | 79.5094 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 5 | [5 empty] | 1990-04-09 |  | 1177 | 24 | 145 | 50 | 56.5 | 0 | 7.1 | 4.5 |  | 11.6 | 11.6 | 0.61207 | 0 | 14.2 | 14.2 | 4.3291 | 36.6709 | 0.38723 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 701.8222 | -4.7496 | 75.625 | 510.9111 | 84.7332 | 145 | 99 | 85 | 4.6258 | 6.9742 | 11.6 | 11.6 | 0.34486 | 0.39877 | 13.8773 | 13.8773 | 3.4622 | 33.5378 | 0.41378 | 5.9 | 5.6 | 60 | 320 | 450 | 492.4484 | -9.433 | 81.25 | 406.2242 | 85.2298 | 99 | 50 | 28 | 2.4742 | 4.5 | 6.9742 | 6.9742 | 0.42608 | 0.35477 | 14.8455 | 14.8455 | 4.3347 | 42.1653 | 0.35208 | 5.6 | 5.5 | 110 | 450 | 670 | 636.9428 | 4.9339 | 65.625 | 543.4714 | 79.7597
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1990-04-10 |  | 1200.4 | 24 | 144 | 50 | 56 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 36.6978 | 0.38149 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 144 | 98 | 84 | 4.5606 | 6.9394 | 11.5 | 11.5 | 0.34236 | 0.39657 | 13.6818 | 13.6818 | 3.4544 | 33.5456 | 0.40786 | 5.9 | 5.6 | 60 | 320 | 450 | 490.8734 | -9.083 | 81.25 | 405.4367 | 85.2011 | 98 | 50 | 28 | 2.4394 | 4.5 | 6.9394 | 6.9394 | 0.42478 | 0.35153 | 14.6364 | 14.6364 | 4.3215 | 41.6785 | 0.35117 | 5.6 | 5.5 | 110 | 450 | 670 | 634.3098 | 5.3269 | 65.625 | 542.1549 | 79.7106 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 5 | [5 empty] | 1990-04-11 |  | 1223.1 | 24 | 144 | 50 | 56.5 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.2753 | 36.2247 | 0.38096 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 691.0667 | -3.1443 | 75.625 | 505.5333 | 84.5708 | 144 | 99 | 85 | 4.5281 | 6.8719 | 11.4 | 11.4 | 0.33925 | 0.3972 | 13.5844 | 13.5844 | 3.4566 | 33.0434 | 0.41111 | 5.9 | 5.6 | 60 | 320 | 450 | 491.3233 | -9.183 | 81.25 | 405.6617 | 85.2093 | 99 | 50 | 28 | 2.3719 | 4.5 | 6.8719 | 6.8719 | 0.42228 | 0.34516 | 14.2312 | 14.2312 | 4.296 | 42.204 | 0.3372 | 5.6 | 5.5 | 110 | 450 | 670 | 629.2083 | 6.0883 | 65.625 | 539.6042 | 79.6147 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 7.5 | [5 empty] | 1990-04-12 |  | 1248.5 | 24 | 144 | 48 | 56 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.29 | 35.71 | 0.38085 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 694 | -3.5821 | 75.625 | 507 | 84.6154 | 144 | 97 | 83 | 4.4625 | 6.7375 | 11.2 | 11.2 | 0.33304 | 0.39844 | 13.3875 | 13.3875 | 3.461 | 34.039 | 0.3933 | 5.9 | 5.6 | 60 | 320 | 450 | 492.2078 | -9.3795 | 81.25 | 406.1039 | 85.2255 | 97 | 48 | 29 | 2.3375 | 4.4 | 6.7375 | 6.7375 | 0.41357 | 0.34694 | 14.025 | 14.025 | 4.3031 | 39.1969 | 0.35781 | 5.6 | 5.5 | 110 | 450 | 670 | 630.625 | 5.8769 | 65.625 | 540.3125 | 79.6414 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 12.5 | [5 empty] | 1990-04-16 |  | 1340.3 | 24 | 144 | 50 | 56.5 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 36.1978 | 0.38676 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 144 | 99 | 83 | 4.597 | 6.903 | 11.5 | 11.5 | 0.34168 | 0.39974 | 13.791 | 13.791 | 3.4657 | 35.0343 | 0.39364 | 5.9 | 5.6 | 60 | 320 | 450 | 493.1459 | -9.588 | 81.25 | 406.573 | 85.2425 | 99 | 50 | 30 | 2.403 | 4.5 | 6.903 | 6.903 | 0.42343 | 0.34811 | 14.4179 | 14.4179 | 4.3078 | 40.1922 | 0.35872 | 5.6 | 5.5 | 110 | 450 | 670 | 631.5589 | 5.7375 | 65.625 | 540.7794 | 79.659 | Qp/QT (THM4), % | 46.0784 | 81.3725 |  | Qp/QT (HAA5), % | -225 | -56.25 | [11 empty] | Qp/QT (THM4), % | -78.3784 | 18.9189 |  | Qp/QT (HAA5), % | 17.8571 | 66.0714 | [11 empty] | Qp/QT (THM4), % | 33.3333 | 69.697 |  | Qp/QT (HAA5), % | -92.5926 | 7.4074 | [11 empty] | Qp/QT (THM4), % | 45.6 | 74.4 |  | Qp/QT (HAA5), % | 35 | 68.75 | [11 empty] | Qp/QT (THM4), % | 52.0661 | 81.8182 |  | Qp/QT (HAA5), % | 38.75 | 72.5 | [11 empty] | Qp/QT (THM4), % | 50.8197 | 80.3279 |  | Qp/QT (HAA5), % | 51.0638 | 79.7872
[11 empty] | 1990-04-17 |  | 1359.7 | 24 | 144 | 49 | 56.5 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 35.6978 | 0.39218 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 144 | 99 | 83 | 4.597 | 6.903 | 11.5 | 11.5 | 0.34168 | 0.39974 | 13.791 | 13.791 | 3.4657 | 35.0343 | 0.39364 | 5.9 | 5.6 | 60 | 320 | 450 | 493.1459 | -9.588 | 81.25 | 406.573 | 85.2425 | 99 | 49 | 30 | 2.403 | 4.5 | 6.903 | 6.903 | 0.42343 | 0.34811 | 14.4179 | 14.4179 | 4.3078 | 39.6922 | 0.36324 | 5.6 | 5.5 | 110 | 450 | 670 | 631.5589 | 5.7375 | 65.625 | 540.7794 | 79.659 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | NA | [11 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 36.3929 | 18.5536 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 97.6667 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 85.25 | 43.0625 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 88.1125 | 47.275 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 71.7021 | 36.6596
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1990-04-18 |  | 1385.7 | 24 | 144 | 50 | 55 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.29 | 37.71 | 0.36065 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 694 | -3.5821 | 75.625 | 507 | 84.6154 | 144 | 99 | 82 | 4.4303 | 6.7697 | 11.2 | 11.2 | 0.33364 | 0.39556 | 13.2909 | 13.2909 | 3.4508 | 36.0492 | 0.36869 | 5.9 | 5.6 | 60 | 320 | 450 | 490.1522 | -8.9227 | 81.25 | 405.0761 | 85.188 | 99 | 50 | 28 | 2.3697 | 4.4 | 6.7697 | 6.7697 | 0.41477 | 0.35004 | 14.2182 | 14.2182 | 4.3156 | 42.1844 | 0.33705 | 5.6 | 5.5 | 110 | 450 | 670 | 633.1129 | 5.5055 | 65.625 | 541.5565 | 79.6882 | SDS-HAA5b, mg/L | 10.6275 | 4.9804 |  | SDS-HAA5b, mg/L | NA | NA | [11 empty] | SDS-HAA5b, mg/L | NA | 53.4054 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 20 | 10.1818 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | 45.52 | 22.48 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 43.3471 | 19.5455 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 54.2295 | 26.4918 |  | SDS-HAA5b, mg/L | 54 | 27
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.3 | [5 empty] | 1990-04-20 |  | 1428.8 | 24 | 144 | 50 | 57.5 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.2753 | 35.2247 | 0.39177 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 691.0667 | -3.1443 | 75.625 | 505.5333 | 84.5708 | 144 | 99 | 84 | 4.5281 | 6.8719 | 11.4 | 11.4 | 0.33925 | 0.3972 | 13.5844 | 13.5844 | 3.4566 | 34.0434 | 0.39903 | 5.9 | 5.6 | 60 | 320 | 450 | 491.3233 | -9.183 | 81.25 | 405.6617 | 85.2093 | 99 | 50 | 31 | 2.3719 | 4.5 | 6.8719 | 6.8719 | 0.42228 | 0.34516 | 14.2312 | 14.2312 | 4.296 | 39.204 | 0.36301 | 5.6 | 5.5 | 110 | 450 | 670 | 629.2083 | 6.0883 | 65.625 | 539.6042 | 79.6147 | SDS-TOXb, mg Cl- /L | 230.4314 | 100.549 |  | SDS-TOXb, mg Cl- /L | NA | NA | [11 empty] | SDS-TOXb, mg Cl- /L | NA | 234.973 |  | SDS-TOXb, mg Cl- /L | 237.5 | 122.75 | [11 empty] | SDS-TOXb, mg Cl- /L | 289 | 146.0909 |  | SDS-TOXb, mg Cl- /L | NA | 390.8889 | [11 empty] | SDS-TOXb, mg Cl- /L | 341.28 | 234.72 |  | SDS-TOXb, mg Cl- /L | 380.5 | 255.625 | [11 empty] | SDS-TOXb, mg Cl- /L | 217.0496 | 95.3636 |  | SDS-TOXb, mg Cl- /L | 271.5125 | 133.475 | [11 empty] | SDS-TOXb, mg Cl- /L | 243 | 117 |  | SDS-TOXb, mg Cl- /L | 241.9574 | 119.3085
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 7 | [5 empty] | 1990-04-23 |  | 1501.6 | 24 | 144 | 48 | 56 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.2484 | 35.7516 | 0.3804 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 685.6889 | -2.3416 | 75.625 | 502.8444 | 84.4882 | 144 | 98 | 82 | 4.4625 | 6.8375 | 11.3 | 11.3 | 0.33675 | 0.39491 | 13.3875 | 13.3875 | 3.4484 | 35.5516 | 0.37657 | 5.9 | 5.6 | 60 | 320 | 450 | 489.6892 | -8.8198 | 81.25 | 404.8446 | 85.1795 | 98 | 48 | 30 | 2.3375 | 4.5 | 6.8375 | 6.8375 | 0.421 | 0.34186 | 14.025 | 14.025 | 4.2831 | 38.7169 | 0.36224 | 5.6 | 5.5 | 110 | 450 | 670 | 626.6111 | 6.476 | 65.625 | 538.3056 | 79.5655 | SDS-CDb, mg/L | 6.3843 | 2.9255 |  | SDS-CDb, mg/L | NA | NA | [11 empty] | SDS-CDb, mg/L | NA | 10.6351 |  | SDS-CDb, mg/L | 10.7286 | 6.4857 | [11 empty] | SDS-CDb, mg/L | 6.4667 | 5.1212 |  | SDS-CDb, mg/L | NA | 7.4259 | [11 empty] | SDS-CDb, mg/L | 7.0976 | 4.8224 |  | SDS-CDb, mg/L | 7.935 | 5.2687 | [11 empty] | SDS-CDb, mg/L | 5.2512 | 3.1091 |  | SDS-CDb, mg/L | 6.21 | 3.78 | [11 empty] | SDS-CDb, mg/L | 4.3525 | 2.641 |  | SDS-CDb, mg/L | 4.3383 | 2.6723
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 15 | [5 empty] | 1990-04-24 |  | 1523.4 | 24 | 144 | 49 | 56 | 0 | 6.8 | 4.6 |  | 11.4 | 11.4 | 0.59649 | 0 | 13.6 | 13.6 | 4.2087 | 36.2913 | 0.37475 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 677.7391 | -1.1551 | 75.625 | 498.8696 | 84.3647 | 144 | 98 | 83 | 4.4657 | 6.9343 | 11.4 | 11.4 | 0.34041 | 0.39173 | 13.397 | 13.397 | 3.4372 | 34.5628 | 0.38761 | 5.9 | 5.6 | 60 | 320 | 450 | 487.4387 | -8.3197 | 81.25 | 403.7193 | 85.1382 | 98 | 49 | 29 | 2.3343 | 4.6 | 6.9343 | 6.9343 | 0.42831 | 0.33663 | 14.006 | 14.006 | 4.2627 | 40.2373 | 0.34808 | 5.6 | 5.5 | 110 | 450 | 670 | 622.5373 | 7.084 | 65.625 | 536.2687 | 79.4879 | TOCb, mg/L | 1.902 | 0.98431 |  | TOCb, mg/L | NA | NA | [11 empty] | TOCb, mg/L | NA | 3.2189 |  | TOCb, mg/L | 3.2571 | 1.5214 | [11 empty] | TOCb, mg/L | 2.7 | 1.3909 |  | TOCb, mg/L | NA | 3.6333 | [11 empty] | TOCb, mg/L | 2.0952 | 1.1448 |  | TOCb, mg/L | 2.445 | 1.3313 | [11 empty] | TOCb, mg/L | 1.8339 | 0.88182 |  | TOCb, mg/L | 2.26 | 1.18 | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1990-04-25 |  | 1546.6 | 24 | 144 | 49 | 55.5 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.2484 | 36.7516 | 0.37005 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 685.6889 | -2.3416 | 75.625 | 502.8444 | 84.4882 | 144 | 98 | 83 | 4.4657 | 6.8343 | 11.3 | 11.3 | 0.3367 | 0.39519 | 13.397 | 13.397 | 3.4494 | 34.5506 | 0.38775 | 5.9 | 5.6 | 60 | 320 | 450 | 489.8886 | -8.8641 | 81.25 | 404.9443 | 85.1831 | 98 | 49 | 28 | 2.3343 | 4.5 | 6.8343 | 6.8343 | 0.42088 | 0.34156 | 14.006 | 14.006 | 4.2819 | 41.2181 | 0.3398 | 5.6 | 5.5 | 110 | 450 | 670 | 626.3715 | 6.5117 | 65.625 | 538.1857 | 79.561 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA | [11 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
|  |  |  | Design permeate pressure, Pp (psi) | 60 | [5 empty] | 1990-04-26 |  | 1569.8 | 24 | 144 | 48 | 55 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.29 | 36.71 | 0.37047 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 694 | -3.5821 | 75.625 | 507 | 84.6154 | 144 | 98 | 82 | 4.4657 | 6.7343 | 11.2 | 11.2 | 0.33298 | 0.39872 | 13.397 | 13.397 | 3.4621 | 35.5379 | 0.37698 | 5.9 | 5.6 | 60 | 320 | 450 | 492.4113 | -9.4247 | 81.25 | 406.2057 | 85.2292 | 98 | 48 | 28 | 2.3343 | 4.4 | 6.7343 | 6.7343 | 0.41346 | 0.34663 | 14.006 | 14.006 | 4.3019 | 40.6981 | 0.34414 | 5.6 | 5.5 | 110 | 450 | 670 | 630.3799 | 5.9134 | 65.625 | 540.19 | 79.6368 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA | [11 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 24 | [5 empty] | 1990-04-27 |  | 1595 | 24 | 144 | 48 | 55 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.2484 | 36.7516 | 0.37005 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 685.6889 | -2.3416 | 75.625 | 502.8444 | 84.4882 | 144 | 98 | 82 | 4.4303 | 6.8697 | 11.3 | 11.3 | 0.33735 | 0.39206 | 13.2909 | 13.2909 | 3.4384 | 35.5616 | 0.37374 | 5.9 | 5.6 | 60 | 320 | 450 | 487.6753 | -8.3723 | 81.25 | 403.8377 | 85.1425 | 98 | 48 | 28 | 2.3697 | 4.5 | 6.8697 | 6.8697 | 0.4222 | 0.34495 | 14.2182 | 14.2182 | 4.2952 | 40.7048 | 0.3493 | 5.6 | 5.5 | 110 | 450 | 670 | 629.0438 | 6.1129 | 65.625 | 539.5219 | 79.6116 | Alkb, mg/L CaCO3 | 88.9902 | 57.5784 |  | Alkb, mg/L CaCO3 | NA | NA | [11 empty] | Alkb, mg/L CaCO3 | NA | 180.2973 |  | Alkb, mg/L CaCO3 | 181.9643 | 106.2679 | [11 empty] | Alkb, mg/L CaCO3 | 166.3333 | 107.7879 |  | Alkb, mg/L CaCO3 | NA | 208.0741 | [11 empty] | Alkb, mg/L CaCO3 | 151.112 | 101.288 |  | Alkb, mg/L CaCO3 | 169.45 | 111.0625 | [11 empty] | Alkb, mg/L CaCO3 | 102.7273 | 70 |  | Alkb, mg/L CaCO3 | 117.375 | 80.25 | [11 empty] | Alkb, mg/L CaCO3 | 72.082 | 57.0328 |  | Alkb, mg/L CaCO3 | 71.9574 | 57.3085
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 44.1429 | [5 empty] | 1990-04-30 |  | 1663.5 | 24 | 143 | 48 | 55 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 36.2784 | 0.36937 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 143 | 98 | 82 | 4.4 | 6.8 | 11.2 | 11.2 | 0.3342 | 0.39286 | 13.2 | 13.2 | 3.4412 | 35.0588 | 0.37651 | 5.9 | 5.6 | 60 | 320 | 450 | 488.2353 | -8.4967 | 81.25 | 404.1176 | 85.1528 | 98 | 48 | 28 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 4.2689 | 40.7311 | 0.33881 | 5.6 | 5.5 | 110 | 450 | 670 | 623.7778 | 6.8988 | 65.625 | 536.8889 | 79.5116 | T-Hdb, mg/L CaCO3 | 137.1961 | 81.4314 |  | T-Hdb, mg/L CaCO3 | NA | NA | [11 empty] | T-Hdb, mg/L CaCO3 | NA | 172 |  | T-Hdb, mg/L CaCO3 | 173.5714 | 102.2143 | [11 empty] | T-Hdb, mg/L CaCO3 | 150 | 95.4545 |  | T-Hdb, mg/L CaCO3 | NA | 188.8889 | [11 empty] | T-Hdb, mg/L CaCO3 | 136.128 | 89.472 |  | T-Hdb, mg/L CaCO3 | 153.3 | 98.625 | [11 empty] | T-Hdb, mg/L CaCO3 | 122.0083 | 71.7273 |  | T-Hdb, mg/L CaCO3 | 144.5125 | 87.475 | [11 empty] | T-Hdb, mg/L CaCO3 | 142.5902 | 91.8361 |  | T-Hdb, mg/L CaCO3 | 142.1702 | 92.766
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 33.2 | [5 empty] | 1990-05-01 |  | 1686.4 | 24 | 143 | 48 | 55.5 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.2484 | 35.7516 | 0.3804 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 685.6889 | -2.3416 | 75.625 | 502.8444 | 84.4882 | 143 | 98 | 83 | 4.4657 | 6.8343 | 11.3 | 11.3 | 0.3367 | 0.39519 | 13.397 | 13.397 | 3.4494 | 34.0506 | 0.39344 | 5.9 | 5.6 | 60 | 320 | 450 | 489.8886 | -8.8641 | 81.25 | 404.9443 | 85.1831 | 98 | 48 | 28 | 2.3343 | 4.5 | 6.8343 | 6.8343 | 0.42088 | 0.34156 | 14.006 | 14.006 | 4.2819 | 40.7181 | 0.34397 | 5.6 | 5.5 | 110 | 450 | 670 | 626.3715 | 6.5117 | 65.625 | 538.1857 | 79.561 | Ca-Hdb, mg/L CaCO3 | 117.3333 | 69.3333 |  | Ca-Hdb, mg/L CaCO3 | NA | NA | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | 162.1892 |  | Ca-Hdb, mg/L CaCO3 | 163.75 | 92.875 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 142.3333 | 90.3333 |  | Ca-Hdb, mg/L CaCO3 | NA | 179.4074 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 124.336 | 82.864 |  | Ca-Hdb, mg/L CaCO3 | 139.6 | 91 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 126.8017 | 73.5455 |  | Ca-Hdb, mg/L CaCO3 | 150.6375 | 90.225 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 144.459 | 88.9836 |  | Ca-Hdb, mg/L CaCO3 | 144 | 90
|  |  |  | Required influent pressure to the system, PI (psi) | 137.3429 | [5 empty] | 1990-05-02 |  | 1706.6 | 24 | 144 | 48 | 55.5 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.3022 | 36.1978 | 0.38676 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 696.4444 | -3.9469 | 75.625 | 508.2222 | 84.6524 | 144 | 98 | 82 | 4.6667 | 6.8333 | 11.5 | 11.5 | 0.34039 | 0.4058 | 14 | 14 | 3.4878 | 35.5122 | 0.39423 | 5.9 | 5.6 | 60 | 320 | 450 | 497.561 | -10.5691 | 81.25 | 408.7805 | 85.3222 | 98 | 48 | 29 | 2.3333 | 4.5 | 6.8333 | 6.8333 | 0.42085 | 0.34146 | 14 | 14 | 4.2815 | 39.7185 | 0.35248 | 5.6 | 5.5 | 110 | 450 | 670 | 626.2963 | 6.5229 | 65.625 | 538.1481 | 79.5595 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1990-05-03 |  | 1734.9 | 24 | 144 | 48 | 55.5 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.2753 | 36.2247 | 0.38096 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 691.0667 | -3.1443 | 75.625 | 505.5333 | 84.5708 | 144 | 98 | 82 | 4.5313 | 6.8687 | 11.4 | 11.4 | 0.33919 | 0.39749 | 13.594 | 13.594 | 3.4576 | 35.5424 | 0.38247 | 5.9 | 5.6 | 60 | 320 | 450 | 491.5254 | -9.2279 | 81.25 | 405.7627 | 85.213 | 98 | 48 | 29 | 2.3687 | 4.5 | 6.8687 | 6.8687 | 0.42216 | 0.34485 | 14.2119 | 14.2119 | 4.2948 | 39.7052 | 0.35794 | 5.6 | 5.5 | 110 | 450 | 670 | 628.9652 | 6.1246 | 65.625 | 539.4826 | 79.6101 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1990-05-04 |  | 1758 | 24 | 142 | 49 | 55 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 36.2784 | 0.36937 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 142 | 98 | 82 | 4.4 | 6.8 | 11.2 | 11.2 | 0.3342 | 0.39286 | 13.2 | 13.2 | 3.4412 | 34.5588 | 0.38196 | 5.9 | 5.6 | 60 | 320 | 450 | 488.2353 | -8.4967 | 81.25 | 404.1176 | 85.1528 | 98 | 49 | 28 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 4.2689 | 41.2311 | 0.3347 | 5.6 | 5.5 | 110 | 450 | 670 | 623.7778 | 6.8988 | 65.625 | 536.8889 | 79.5116 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1990-05-07 |  | 1826.9 | 24 | 143 | 48 | 55 | 0 | 6.6 | 4.8 |  | 11.4 | 11.4 | 0.57895 | 0 | 13.2 | 13.2 | 4.0838 | 36.4162 | 0.36248 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 652.75 | 2.5746 | 75.625 | 486.375 | 83.963 | 143 | 97 | 82 | 4.3343 | 7.0657 | 11.4 | 11.4 | 0.34285 | 0.3802 | 13.003 | 13.003 | 3.3975 | 34.6025 | 0.37578 | 5.9 | 5.6 | 60 | 320 | 450 | 479.493 | -6.554 | 81.25 | 399.7465 | 84.9905 | 97 | 48 | 28 | 2.2657 | 4.8 | 7.0657 | 7.0657 | 0.44061 | 0.32066 | 13.594 | 13.594 | 4.2024 | 40.2976 | 0.33734 | 5.6 | 5.5 | 110 | 450 | 670 | 610.4851 | 8.8828 | 65.625 | 530.2425 | 79.2548 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1990-05-08 |  | 1845.4 | 24 | 142 | 49 | 55.5 | 0 | 6.9 | 4.4 |  | 11.3 | 11.3 | 0.61062 | 0 | 13.8 | 13.8 | 4.3175 | 35.6825 | 0.38674 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 699.5 | -4.403 | 75.625 | 509.75 | 84.6984 | 142 | 96 | 81 | 4.5629 | 6.7371 | 11.3 | 11.3 | 0.33489 | 0.4038 | 13.6887 | 13.6887 | 3.4805 | 34.5195 | 0.39655 | 5.9 | 5.6 | 60 | 320 | 450 | 496.0929 | -10.2429 | 81.25 | 408.0464 | 85.2958 | 96 | 49 | 30 | 2.3371 | 4.4 | 6.7371 | 6.7371 | 0.41356 | 0.3469 | 14.0226 | 14.0226 | 4.303 | 38.197 | 0.36711 | 5.6 | 5.5 | 110 | 450 | 670 | 630.5938 | 5.8815 | 65.625 | 540.2969 | 79.6408 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1990-05-09 |  | 1872.1 | 24 | 142 | 47 | 55 | 0 | 6.7 | 4.4 |  | 11.1 | 11.1 | 0.6036 | 0 | 13.4 | 13.4 | 4.2625 | 35.2375 | 0.38028 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 688.5 | -2.7612 | 75.625 | 504.25 | 84.5315 | 142 | 97 | 82 | 4.3652 | 6.7348 | 11.1 | 11.1 | 0.33114 | 0.39326 | 13.0955 | 13.0955 | 3.4426 | 34.0574 | 0.38451 | 5.9 | 5.6 | 60 | 320 | 450 | 488.5174 | -8.5594 | 81.25 | 404.2587 | 85.158 | 97 | 47 | 28 | 2.3348 | 4.4 | 6.7348 | 6.7348 | 0.41348 | 0.34668 | 14.0091 | 14.0091 | 4.3021 | 39.6979 | 0.35289 | 5.6 | 5.5 | 110 | 450 | 670 | 630.4201 | 5.9074 | 65.625 | 540.2101 | 79.6376 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1990-05-10 |  | 1893.1 | 24 | 142 | 48 | 55 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 35.7784 | 0.37453 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 142 | 98 | 82 | 4.4 | 6.8 | 11.2 | 11.2 | 0.3342 | 0.39286 | 13.2 | 13.2 | 3.4412 | 34.5588 | 0.38196 | 5.9 | 5.6 | 60 | 320 | 450 | 488.2353 | -8.4967 | 81.25 | 404.1176 | 85.1528 | 98 | 48 | 28 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 4.2689 | 40.7311 | 0.33881 | 5.6 | 5.5 | 110 | 450 | 670 | 623.7778 | 6.8988 | 65.625 | 536.8889 | 79.5116 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1990-05-11 |  | 1919.2 | 24 | 143 | 48 | 54.5 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 4.235 | 36.765 | 0.35904 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 683 | -1.9403 | 75.625 | 501.5 | 84.4467 | 143 | 97 | 82 | 4.3343 | 6.6657 | 11 | 11 | 0.32799 | 0.39403 | 13.003 | 13.003 | 3.4453 | 34.5547 | 0.3763 | 5.9 | 5.6 | 60 | 320 | 450 | 489.064 | -8.6809 | 81.25 | 404.532 | 85.168 | 97 | 48 | 27 | 2.2657 | 4.4 | 6.6657 | 6.6657 | 0.41091 | 0.3399 | 13.594 | 13.594 | 4.2754 | 41.2246 | 0.32976 | 5.6 | 5.5 | 110 | 450 | 670 | 625.0746 | 6.7053 | 65.625 | 537.5373 | 79.5363 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1990-05-14 |  | 1986.7 | 24 | 142 | 47 | 55 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 35.2784 | 0.37984 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 142 | 97 | 82 | 4.4 | 6.8 | 11.2 | 11.2 | 0.3342 | 0.39286 | 13.2 | 13.2 | 3.4412 | 34.0588 | 0.38756 | 5.9 | 5.6 | 60 | 320 | 450 | 488.2353 | -8.4967 | 81.25 | 404.1176 | 85.1528 | 97 | 47 | 28 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 4.2689 | 39.7311 | 0.34733 | 5.6 | 5.5 | 110 | 450 | 670 | 623.7778 | 6.8988 | 65.625 | 536.8889 | 79.5116 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1990-05-15 |  | 2010.9 | 24 | 143 | 47 | 54.5 | 0 | 6.7 | 4.5 |  | 11.2 | 11.2 | 0.59821 | 0 | 13.4 | 13.4 | 4.2216 | 36.2784 | 0.36937 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 680.3111 | -1.539 | 75.625 | 500.1556 | 84.4049 | 143 | 97 | 81 | 4.3652 | 6.8348 | 11.2 | 11.2 | 0.33485 | 0.38975 | 13.0955 | 13.0955 | 3.4303 | 35.5697 | 0.36816 | 5.9 | 5.6 | 60 | 320 | 450 | 486.0519 | -8.0115 | 81.25 | 403.0259 | 85.1126 | 97 | 47 | 28 | 2.3348 | 4.5 | 6.8348 | 6.8348 | 0.4209 | 0.34161 | 14.0091 | 14.0091 | 4.2821 | 39.7179 | 0.35271 | 5.6 | 5.5 | 110 | 450 | 670 | 626.4108 | 6.5059 | 65.625 | 538.2054 | 79.5617 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1990-05-16 |  | 2034.7 | 24 | 143 | 47 | 54 | 0 | 6.7 | 4.4 |  | 11.1 | 11.1 | 0.6036 | 0 | 13.4 | 13.4 | 4.2625 | 36.7375 | 0.36475 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 688.5 | -2.7612 | 75.625 | 504.25 | 84.5315 | 143 | 97 | 81 | 4.3652 | 6.7348 | 11.1 | 11.1 | 0.33114 | 0.39326 | 13.0955 | 13.0955 | 3.4426 | 35.5574 | 0.36829 | 5.9 | 5.6 | 60 | 320 | 450 | 488.5174 | -8.5594 | 81.25 | 404.2587 | 85.158 | 97 | 47 | 27 | 2.3348 | 4.4 | 6.7348 | 6.7348 | 0.41348 | 0.34668 | 14.0091 | 14.0091 | 4.3021 | 40.6979 | 0.34422 | 5.6 | 5.5 | 110 | 450 | 670 | 630.4201 | 5.9074 | 65.625 | 540.2101 | 79.6376 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1990-05-17 |  | 2058 | 24 | 142 | 47 | 55 | 0 | 6.7 | 4.4 |  | 11.1 | 11.1 | 0.6036 | 0 | 13.4 | 13.4 | 4.2625 | 35.2375 | 0.38028 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 688.5 | -2.7612 | 75.625 | 504.25 | 84.5315 | 142 | 97 | 82 | 4.3969 | 6.7031 | 11.1 | 11.1 | 0.33055 | 0.39611 | 13.1906 | 13.1906 | 3.4527 | 34.0473 | 0.38742 | 5.9 | 5.6 | 60 | 320 | 450 | 490.5455 | -9.0101 | 81.25 | 405.2727 | 85.1952 | 97 | 47 | 28 | 2.3031 | 4.4 | 6.7031 | 6.7031 | 0.4123 | 0.34359 | 13.8187 | 13.8187 | 4.2898 | 39.7102 | 0.34799 | 5.6 | 5.5 | 110 | 450 | 670 | 627.9688 | 6.2733 | 65.625 | 538.9844 | 79.5912
[11 empty] | 1990-05-18 |  | 2080.2 | 24 | 142 | 47 | 54.5 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 4.235 | 35.765 | 0.36908 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 683 | -1.9403 | 75.625 | 501.5 | 84.4467 | 142 | 97 | 82 | 4.3312 | 6.6688 | 11 | 11 | 0.32805 | 0.39375 | 12.9938 | 12.9938 | 3.4443 | 34.0557 | 0.38154 | 5.9 | 5.6 | 60 | 320 | 450 | 488.866 | -8.6369 | 81.25 | 404.433 | 85.1644 | 97 | 47 | 27 | 2.2687 | 4.4 | 6.6688 | 6.6688 | 0.41102 | 0.34021 | 13.6125 | 13.6125 | 4.2766 | 40.7234 | 0.33427 | 5.6 | 5.5 | 110 | 450 | 670 | 625.3125 | 6.6698 | 65.625 | 537.6562 | 79.5408
[11 empty] | 1990-05-21 |  | 2147.7 | 24 | 142 | 47 | 54.5 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 4.2075 | 35.7925 | 0.3632 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 677.5 | -1.1194 | 75.625 | 498.75 | 84.3609 | 142 | 96 | 81 | 4.2 | 6.7 | 10.9 | 10.9 | 0.32677 | 0.38532 | 12.6 | 12.6 | 3.4149 | 34.5851 | 0.36432 | 5.9 | 5.6 | 60 | 320 | 450 | 482.9851 | -7.33 | 81.25 | 401.4925 | 85.0558 | 96 | 47 | 28 | 2.3 | 4.4 | 6.7 | 6.7 | 0.41218 | 0.34328 | 13.8 | 13.8 | 4.2886 | 39.2114 | 0.35194 | 5.6 | 5.5 | 110 | 450 | 670 | 627.7273 | 6.3094 | 65.625 | 538.8636 | 79.5867
[11 empty] | 1990-05-23 |  | 2194.6 | 24 | 141 | 47 | 54.5 | 0 | 6.6 | 4.5 |  | 11.1 | 11.1 | 0.59459 | 0 | 13.2 | 13.2 | 4.1947 | 35.3053 | 0.37388 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 674.9333 | -0.73632 | 75.625 | 497.4667 | 84.3206 | 141 | 96 | 81 | 4.3 | 6.8 | 11.1 | 11.1 | 0.33234 | 0.38739 | 12.9 | 12.9 | 3.4221 | 34.0779 | 0.37854 | 5.9 | 5.6 | 60 | 320 | 450 | 484.4118 | -7.6471 | 81.25 | 402.2059 | 85.0823 | 96 | 47 | 28 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 4.2689 | 39.2311 | 0.35176 | 5.6 | 5.5 | 110 | 450 | 670 | 623.7778 | 6.8988 | 65.625 | 536.8889 | 79.5116
[11 empty] | 1990-05-24 |  | 2220.3 | 24 | 141 | 47 | 54.5 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 4.235 | 35.265 | 0.37431 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 683 | -1.9403 | 75.625 | 501.5 | 84.4467 | 141 | 96 | 81 | 4.3312 | 6.6688 | 11 | 11 | 0.32805 | 0.39375 | 12.9938 | 12.9938 | 3.4443 | 34.0557 | 0.38154 | 5.9 | 5.6 | 60 | 320 | 450 | 488.866 | -8.6369 | 81.25 | 404.433 | 85.1644 | 96 | 47 | 28 | 2.2687 | 4.4 | 6.6688 | 6.6688 | 0.41102 | 0.34021 | 13.6125 | 13.6125 | 4.2766 | 39.2234 | 0.34705 | 5.6 | 5.5 | 110 | 450 | 670 | 625.3125 | 6.6698 | 65.625 | 537.6562 | 79.5408
[11 empty] | 1990-05-25 |  | 2242.2 | 24 | 145 | 48 | 55.5 | 0 | 6.6 | 4.5 |  | 11.1 | 11.1 | 0.59459 | 0 | 13.2 | 13.2 | 4.1947 | 36.8053 | 0.35864 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 674.9333 | -0.73632 | 75.625 | 497.4667 | 84.3206 | 145 | 98 | 83 | 4.3343 | 6.7657 | 11.1 | 11.1 | 0.33171 | 0.39048 | 13.003 | 13.003 | 3.4328 | 35.0672 | 0.3708 | 5.9 | 5.6 | 60 | 320 | 450 | 486.5652 | -8.1256 | 81.25 | 403.2826 | 85.1221 | 98 | 48 | 28 | 2.2657 | 4.5 | 6.7657 | 6.7657 | 0.41833 | 0.33488 | 13.594 | 13.594 | 4.2559 | 40.7441 | 0.33364 | 5.6 | 5.5 | 110 | 450 | 670 | 621.1841 | 7.286 | 65.625 | 535.592 | 79.462
[11 empty] | 1990-05-29 |  | 2335.6 | 24 | 146 | 49 | 56.5 | 0 | 6.7 | 4.6 |  | 11.3 | 11.3 | 0.59292 | 0 | 13.4 | 13.4 | 4.1824 | 36.8176 | 0.36396 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 672.4783 | -0.36989 | 75.625 | 496.2391 | 84.2818 | 146 | 99 | 83 | 4.4338 | 6.8662 | 11.3 | 11.3 | 0.33729 | 0.39237 | 13.3015 | 13.3015 | 3.4395 | 36.0605 | 0.36887 | 5.9 | 5.6 | 60 | 320 | 450 | 487.8946 | -8.421 | 81.25 | 403.9473 | 85.1466 | 99 | 49 | 30 | 2.2662 | 4.6 | 6.8662 | 6.8662 | 0.42578 | 0.33005 | 13.5971 | 13.5971 | 4.2375 | 39.7625 | 0.34196 | 5.6 | 5.5 | 110 | 450 | 670 | 617.5 | 7.8358 | 65.625 | 533.75 | 79.3911
[11 empty] | 1990-05-30 |  | 2335.8 | 24 | 146 | 50 | 58 | 0 | 7.03 | 4.43 |  | 11.46 | 11.46 | 0.61344 | 0 | 14.06 | 14.06 | 4.3402 | 35.6598 | 0.39428 | 7.2 | 5.9 | 78 | 260 | 320 | 670 | 704.0316 | -5.0793 | 75.625 | 512.0158 | 84.7661 | 146 | 100 | 85 | 4.6867 | 6.7733 | 11.46 | 11.46 | 0.33853 | 0.40896 | 14.06 | 14.06 | 3.4995 | 34.5005 | 0.40753 | 5.9 | 5.6 | 60 | 320 | 450 | 499.9016 | -11.0892 | 81.25 | 409.9508 | 85.3641 | 100 | 50 | 31 | 2.3433 | 4.43 | 6.7733 | 6.7733 | 0.41602 | 0.34596 | 14.06 | 14.06 | 4.2992 | 39.7008 | 0.35415 | 5.6 | 5.5 | 110 | 450 | 670 | 629.8495 | 5.9926 | 65.625 | 539.9248 | 79.6268
[11 empty] | 1990-05-31 |  | 2362.8 | 24 | 145 | 49 | 56.5 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 3.021 | 37.479 | 0.36821 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 502.2 | 10.3214 | 71.25 | 371.1 | 81.4066 | 145 | 99 | 84 | 4.4955 | 6.9045 | 11.4 | 11.4 | 0.33986 | 0.39434 | 13.4864 | 13.4864 | 2.4125 | 35.5875 | 0.37896 | 7.4 | 6.8 | 58 | 240 | 360 | 358.4977 | 0.41731 | 75.8333 | 299.2488 | 80.6181 | 99 | 49 | 29 | 2.4045 | 4.5 | 6.9045 | 6.9045 | 0.42349 | 0.34826 | 14.4273 | 14.4273 | 3.2946 | 41.7054 | 0.34593 | 6.8 | 6.7 | 100 | 360 | 560 | 498.9293 | 10.9055 | 58.3333 | 429.4646 | 76.7152
[11 empty] | 1990-06-01 |  | 2385.5 | 24 | 145 | 49 | 57 | 0 | 6.76 | 4.43 |  | 11.19 | 11.19 | 0.60411 | 0 | 13.52 | 13.52 | 3.0147 | 36.9853 | 0.36555 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 500.9391 | 10.5466 | 71.25 | 370.4695 | 81.375 | 145 | 99 | 84 | 4.4042 | 6.7858 | 11.19 | 11.19 | 0.33375 | 0.39359 | 13.2127 | 13.2127 | 2.4106 | 35.5894 | 0.37125 | 7.4 | 6.8 | 58 | 240 | 360 | 358.1257 | 0.52065 | 75.8333 | 299.0628 | 80.6061 | 99 | 49 | 30 | 2.3558 | 4.43 | 6.7858 | 6.7858 | 0.41648 | 0.34716 | 14.1345 | 14.1345 | 3.2913 | 40.7087 | 0.34721 | 6.8 | 6.7 | 100 | 360 | 560 | 498.2612 | 11.0248 | 58.3333 | 429.1306 | 76.6971
[11 empty] | 1990-06-04 |  | 2454 | 24 | 145 | 49 | 55.5 | 0 | 6.857 | 4.48 |  | 11.337 | 11.337 | 0.60483 | 0 | 13.714 | 13.714 | 3.0186 | 38.4814 | 0.35638 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 501.7292 | 10.4055 | 71.25 | 370.8646 | 81.3948 | 145 | 98 | 83 | 4.5362 | 6.8008 | 11.337 | 11.337 | 0.33676 | 0.40012 | 13.6085 | 13.6085 | 2.427 | 36.073 | 0.37725 | 7.4 | 6.8 | 58 | 240 | 360 | 361.3944 | -0.38733 | 75.8333 | 300.6972 | 80.7115 | 98 | 49 | 28 | 2.3208 | 4.48 | 6.8008 | 6.8008 | 0.4189 | 0.34126 | 13.925 | 13.925 | 3.2735 | 42.2265 | 0.32977 | 6.8 | 6.7 | 100 | 360 | 560 | 494.6911 | 11.6623 | 58.3333 | 427.3455 | 76.5997
[11 empty] | 1990-06-05 |  | 2477.2 | 24 | 145 | 49 | 55.5 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 2.9925 | 38.5075 | 0.34279 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 496.5 | 11.3393 | 71.25 | 368.25 | 81.2627 | 145 | 98 | 83 | 4.3662 | 6.6338 | 11 | 11 | 0.3274 | 0.39692 | 13.0985 | 13.0985 | 2.4189 | 36.0811 | 0.36303 | 7.4 | 6.8 | 58 | 240 | 360 | 359.7857 | 0.059524 | 75.8333 | 299.8929 | 80.6598 | 98 | 49 | 28 | 2.2338 | 4.4 | 6.6338 | 6.6338 | 0.40973 | 0.33673 | 13.4031 | 13.4031 | 3.26 | 42.24 | 0.31731 | 6.8 | 6.7 | 100 | 360 | 560 | 492 | 12.1429 | 58.3333 | 426 | 76.5258
[11 empty] | 1990-06-06 |  | 2499.2 | 24 | 145 | 49 | 57.5 | 0 | 6.86 | 4.36 |  | 11.22 | 11.22 | 0.61141 | 0 | 13.72 | 13.72 | 3.0553 | 36.4447 | 0.37646 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 509.0505 | 9.0981 | 71.25 | 374.5252 | 81.5767 | 145 | 100 | 85 | 4.5733 | 6.6467 | 11.22 | 11.22 | 0.33173 | 0.40761 | 13.72 | 13.72 | 2.4461 | 35.0539 | 0.3914 | 7.4 | 6.8 | 58 | 240 | 360 | 365.2277 | -1.4521 | 75.8333 | 302.6138 | 80.8337 | 100 | 49 | 30 | 2.2867 | 4.36 | 6.6467 | 6.6467 | 0.40872 | 0.34403 | 13.72 | 13.72 | 3.2818 | 41.2182 | 0.33286 | 6.8 | 6.7 | 100 | 360 | 560 | 496.3609 | 11.3641 | 58.3333 | 428.1804 | 76.6454
[11 empty] | 1990-06-07 |  | 2523.6 | 24 | 145 | 49 | 57.5 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 3.0702 | 36.4298 | 0.3843 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 512.0455 | 8.5633 | 71.25 | 376.0227 | 81.65 | 145 | 98 | 85 | 4.5938 | 6.8063 | 11.4 | 11.4 | 0.33803 | 0.40296 | 13.7812 | 13.7812 | 2.4342 | 34.0658 | 0.40455 | 7.4 | 6.8 | 58 | 240 | 360 | 362.8375 | -0.78818 | 75.8333 | 301.4187 | 80.7577 | 98 | 49 | 30 | 2.4062 | 4.4 | 6.8063 | 6.8063 | 0.41613 | 0.35354 | 14.4375 | 14.4375 | 3.3109 | 40.1891 | 0.35924 | 6.8 | 6.7 | 100 | 360 | 560 | 502.1875 | 10.3237 | 58.3333 | 431.0938 | 76.8032
[11 empty] | 1990-06-08 |  | 2546.7 | 24 | 145 | 49 | 54.5 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 3.0702 | 39.4298 | 0.35506 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 512.0455 | 8.5633 | 71.25 | 376.0227 | 81.65 | 145 | 98 | 82 | 4.6308 | 6.7692 | 11.4 | 11.4 | 0.33734 | 0.40621 | 13.8923 | 13.8923 | 2.4425 | 37.0575 | 0.37489 | 7.4 | 6.8 | 58 | 240 | 360 | 364.5045 | -1.2513 | 75.8333 | 302.2523 | 80.8107 | 98 | 49 | 27 | 2.3692 | 4.4 | 6.7692 | 6.7692 | 0.41475 | 0.35 | 14.2154 | 14.2154 | 3.3 | 43.2 | 0.32906 | 6.8 | 6.7 | 100 | 360 | 560 | 500 | 10.7143 | 58.3333 | 430 | 76.7442
[11 empty] | 1990-06-11 |  | 2615.5 | 24 | 144 | 48 | 52 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 3.0702 | 40.9298 | 0.34205 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 512.0455 | 8.5633 | 71.25 | 376.0227 | 81.65 | 144 | 97 | 80 | 4.6324 | 6.7676 | 11.4 | 11.4 | 0.33731 | 0.40635 | 13.8971 | 13.8971 | 2.4429 | 38.0571 | 0.36516 | 7.4 | 6.8 | 58 | 240 | 360 | 364.5763 | -1.2712 | 75.8333 | 302.2881 | 80.813 | 97 | 48 | 24 | 2.3676 | 4.4 | 6.7676 | 6.7676 | 0.41469 | 0.34985 | 14.2059 | 14.2059 | 3.2995 | 45.2005 | 0.31429 | 6.8 | 6.7 | 100 | 360 | 560 | 499.9064 | 10.731 | 58.3333 | 429.9532 | 76.7417
[11 empty] | 1990-06-12 |  | 2641.7 | 24 | 144 | 46 | 52.5 | 0 | 6.86 | 4.29 |  | 11.15 | 11.15 | 0.61525 | 0 | 13.72 | 13.72 | 3.0772 | 39.4228 | 0.34802 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 513.4406 | 8.3142 | 71.25 | 376.7203 | 81.684 | 144 | 96 | 80 | 4.5019 | 6.6481 | 11.15 | 11.15 | 0.33045 | 0.40376 | 13.5056 | 13.5056 | 2.4362 | 37.5638 | 0.35954 | 7.4 | 6.8 | 58 | 240 | 360 | 363.244 | -0.9011 | 75.8333 | 301.622 | 80.7706 | 96 | 46 | 25 | 2.3581 | 4.29 | 6.6481 | 6.6481 | 0.40617 | 0.35471 | 14.1487 | 14.1487 | 3.3146 | 42.6854 | 0.33147 | 6.8 | 6.7 | 100 | 360 | 560 | 502.9167 | 10.1935 | 58.3333 | 431.4583 | 76.8228
[11 empty] | 1990-06-13 |  | 2663.6 | 24 | 143 | 49 | 54.5 | 0 | 6.6 | 4.3 |  | 10.9 | 10.9 | 0.6055 | 0 | 13.2 | 13.2 | 3.0223 | 38.4777 | 0.34306 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 502.4651 | 10.2741 | 71.25 | 371.2326 | 81.4133 | 143 | 97 | 82 | 4.4 | 6.5 | 10.9 | 10.9 | 0.32306 | 0.40367 | 13.2 | 13.2 | 2.436 | 35.564 | 0.37116 | 7.4 | 6.8 | 58 | 240 | 360 | 363.2 | -0.88889 | 75.8333 | 301.6 | 80.7692 | 97 | 49 | 27 | 2.2 | 4.3 | 6.5 | 6.5 | 0.40104 | 0.33846 | 13.2 | 13.2 | 3.2651 | 42.7349 | 0.30888 | 6.8 | 6.7 | 100 | 360 | 560 | 493.0233 | 11.9601 | 58.3333 | 426.5116 | 76.554
[11 empty] | 1990-06-14 |  | 2686.3 | 24 | 144 | 47 | 54.5 | 0 | 6.4 | 4.3 |  | 10.7 | 10.7 | 0.59813 | 0 | 12.8 | 12.8 | 2.9826 | 38.0174 | 0.33669 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 494.5116 | 11.6944 | 71.25 | 367.2558 | 81.212 | 144 | 97 | 82 | 4.2 | 6.5 | 10.7 | 10.7 | 0.31935 | 0.39252 | 12.6 | 12.6 | 2.408 | 36.092 | 0.34911 | 7.4 | 6.8 | 58 | 240 | 360 | 357.6 | 0.66667 | 75.8333 | 298.8 | 80.589 | 97 | 47 | 27 | 2.2 | 4.3 | 6.5 | 6.5 | 0.40104 | 0.33846 | 13.2 | 13.2 | 3.2651 | 41.7349 | 0.31628 | 6.8 | 6.7 | 100 | 360 | 560 | 493.0233 | 11.9601 | 58.3333 | 426.5116 | 76.554
[11 empty] | 1990-06-15 |  | 2708.9 | 24 | 143 | 47 | 54.5 | 0 | 6.5 | 4.2 |  | 10.7 | 10.7 | 0.60748 | 0 | 13 | 13 | 3.0332 | 37.4668 | 0.34697 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 504.6429 | 9.8852 | 71.25 | 372.3214 | 81.4676 | 143 | 96 | 82 | 4.2656 | 6.4344 | 10.7 | 10.7 | 0.31813 | 0.39866 | 12.7969 | 12.7969 | 2.4233 | 35.0767 | 0.36483 | 7.4 | 6.8 | 58 | 240 | 360 | 360.6557 | -0.18213 | 75.8333 | 300.3278 | 80.6878 | 96 | 47 | 27 | 2.2344 | 4.2 | 6.4344 | 6.4344 | 0.39489 | 0.34726 | 13.4062 | 13.4062 | 3.2916 | 41.2084 | 0.32533 | 6.8 | 6.7 | 100 | 360 | 560 | 498.3185 | 11.0146 | 58.3333 | 429.1592 | 76.6986
[11 empty] | 1990-06-18 |  | 2776 | 24 | 144 | 46 | 54.5 | 0 | 6.4 | 4.3 |  | 10.7 | 10.7 | 0.59813 | 0 | 12.8 | 12.8 | 2.9826 | 37.5174 | 0.34117 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 494.5116 | 11.6944 | 71.25 | 367.2558 | 81.212 | 144 | 97 | 82 | 4.2 | 6.5 | 10.7 | 10.7 | 0.31935 | 0.39252 | 12.6 | 12.6 | 2.408 | 36.092 | 0.34911 | 7.4 | 6.8 | 58 | 240 | 360 | 357.6 | 0.66667 | 75.8333 | 298.8 | 80.589 | 97 | 46 | 27 | 2.2 | 4.3 | 6.5 | 6.5 | 0.40104 | 0.33846 | 13.2 | 13.2 | 3.2651 | 41.2349 | 0.32012 | 6.8 | 6.7 | 100 | 360 | 560 | 493.0233 | 11.9601 | 58.3333 | 426.5116 | 76.554
[11 empty] | 1990-06-19 |  | 2799.7 | 24 | 143 | 45 | 54 | 0 | 6.3 | 4.3 |  | 10.6 | 10.6 | 0.59434 | 0 | 12.6 | 12.6 | 2.9627 | 37.0373 | 0.3402 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 490.5349 | 12.4045 | 71.25 | 365.2674 | 81.1097 | 143 | 95 | 81 | 4.2 | 6.4 | 10.6 | 10.6 | 0.31563 | 0.39623 | 12.6 | 12.6 | 2.4172 | 35.5828 | 0.3541 | 7.4 | 6.8 | 58 | 240 | 360 | 359.4375 | 0.15625 | 75.8333 | 299.7188 | 80.6485 | 95 | 45 | 27 | 2.1 | 4.3 | 6.4 | 6.4 | 0.39733 | 0.32812 | 12.6 | 12.6 | 3.2349 | 39.7651 | 0.31686 | 6.8 | 6.7 | 100 | 360 | 560 | 486.9767 | 13.0399 | 58.3333 | 423.4884 | 76.3866
[11 empty] | 1990-06-20 |  | 2823.4 | 24 | 140 | 47 | 51 | 0 | 6.4 | 4.2 |  | 10.6 | 10.6 | 0.60377 | 0 | 12.8 | 12.8 | 3.0129 | 39.4871 | 0.32416 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 500.5714 | 10.6122 | 71.25 | 370.2857 | 81.3657 | 140 | 93 | 78 | 4.2 | 6.4 | 10.6 | 10.6 | 0.31563 | 0.39623 | 12.6 | 12.6 | 2.4172 | 36.0828 | 0.3492 | 7.4 | 6.8 | 58 | 240 | 360 | 359.4375 | 0.15625 | 75.8333 | 299.7188 | 80.6485 | 93 | 47 | 24 | 2.2 | 4.2 | 6.4 | 6.4 | 0.39361 | 0.34375 | 13.2 | 13.2 | 3.281 | 42.719 | 0.309 | 6.8 | 6.7 | 100 | 360 | 560 | 496.1905 | 11.3946 | 58.3333 | 428.0952 | 76.6407
[11 empty] | 1990-06-21 |  | 2846.2 | 24 | 141 | 45 | 52.5 | 0 | 6.4 | 4.2 |  | 10.6 | 10.6 | 0.60377 | 0 | 12.8 | 12.8 | 3.0129 | 37.4871 | 0.34145 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 500.5714 | 10.6122 | 71.25 | 370.2857 | 81.3657 | 141 | 94 | 79 | 4.2667 | 6.3333 | 10.6 | 10.6 | 0.3144 | 0.40252 | 12.8 | 12.8 | 2.4331 | 36.0669 | 0.3549 | 7.4 | 6.8 | 58 | 240 | 360 | 362.6105 | -0.72515 | 75.8333 | 301.3053 | 80.7504 | 94 | 45 | 26 | 2.1333 | 4.2 | 6.3333 | 6.3333 | 0.39114 | 0.33684 | 12.8 | 12.8 | 3.2603 | 40.2397 | 0.31809 | 6.8 | 6.7 | 100 | 360 | 560 | 492.0635 | 12.1315 | 58.3333 | 426.0317 | 76.5276
[11 empty] | 1990-06-22 |  | 2869.5 | 24 | 141 | 45 | 51.5 | 0 | 6.4 | 4.3 |  | 10.7 | 10.7 | 0.59813 | 0 | 12.8 | 12.8 | 2.9826 | 38.5174 | 0.33232 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 494.5116 | 11.6944 | 71.25 | 367.2558 | 81.212 | 141 | 94 | 78 | 4.2667 | 6.4333 | 10.7 | 10.7 | 0.31811 | 0.39875 | 12.8 | 12.8 | 2.4235 | 37.0765 | 0.34523 | 7.4 | 6.8 | 58 | 240 | 360 | 360.7047 | -0.19574 | 75.8333 | 300.3523 | 80.6893 | 94 | 45 | 25 | 2.1333 | 4.3 | 6.4333 | 6.4333 | 0.39857 | 0.33161 | 12.8 | 12.8 | 3.245 | 41.255 | 0.31027 | 6.8 | 6.7 | 100 | 360 | 560 | 488.9922 | 12.68 | 58.3333 | 424.4961 | 76.4427
[11 empty] | 1990-06-25 |  | 2938.6 | 24 | 140 | 44 | 52.5 | 0 | 6.3 | 4.1 |  | 10.4 | 10.4 | 0.60577 | 0 | 12.6 | 12.6 | 3.0238 | 36.4762 | 0.34543 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 502.7561 | 10.2221 | 71.25 | 371.378 | 81.4205 | 140 | 94 | 79 | 4.2328 | 6.1672 | 10.4 | 10.4 | 0.3076 | 0.407 | 12.6984 | 12.6984 | 2.4446 | 35.5554 | 0.35714 | 7.4 | 6.8 | 58 | 240 | 360 | 364.9146 | -1.3652 | 75.8333 | 302.4573 | 80.8237 | 94 | 44 | 26 | 2.0672 | 4.1 | 6.1672 | 6.1672 | 0.38126 | 0.33519 | 12.4031 | 12.4031 | 3.2554 | 39.7446 | 0.31207 | 6.8 | 6.7 | 100 | 360 | 560 | 491.0899 | 12.3054 | 58.3333 | 425.545 | 76.5007
[11 empty] | 1990-06-26 |  | 2963 | 24 | 148 | 49 | 51 | 0 | 6.3 | 4.1 |  | 10.4 | 10.4 | 0.60577 | 0 | 12.6 | 12.6 | 3.0238 | 44.4762 | 0.2833 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 502.7561 | 10.2221 | 71.25 | 371.378 | 81.4205 | 148 | 105 | 82 | 4.2 | 6.2 | 10.4 | 10.4 | 0.30821 | 0.40385 | 12.6 | 12.6 | 2.4365 | 42.0635 | 0.29955 | 7.4 | 6.8 | 58 | 240 | 360 | 363.2903 | -0.91398 | 75.8333 | 301.6452 | 80.7721 | 105 | 49 | 20 | 2.1 | 4.1 | 6.2 | 6.2 | 0.38247 | 0.33871 | 12.6 | 12.6 | 3.2659 | 53.7341 | 0.23449 | 6.8 | 6.7 | 100 | 360 | 560 | 493.1707 | 11.9338 | 58.3333 | 426.5854 | 76.558
[11 empty] | 1990-06-27 |  | 2987.7 | 24 | 139 | 42 | 49 | 0 | 6.3 | 4.1 |  | 10.4 | 10.4 | 0.60577 | 0 | 12.6 | 12.6 | 3.0238 | 38.4762 | 0.32748 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 502.7561 | 10.2221 | 71.25 | 371.378 | 81.4205 | 139 | 92 | 78 | 4.2 | 6.2 | 10.4 | 10.4 | 0.30821 | 0.40385 | 12.6 | 12.6 | 2.4365 | 35.0635 | 0.35935 | 7.4 | 6.8 | 58 | 240 | 360 | 363.2903 | -0.91398 | 75.8333 | 301.6452 | 80.7721 | 92 | 42 | 20 | 2.1 | 4.1 | 6.2 | 6.2 | 0.38247 | 0.33871 | 12.6 | 12.6 | 3.2659 | 43.7341 | 0.2881 | 6.8 | 6.7 | 100 | 360 | 560 | 493.1707 | 11.9338 | 58.3333 | 426.5854 | 76.558
[11 empty] | 1990-06-28 |  | 3010 | 24 | 146 | 49 | 54 | 0 | 6.4 | 4.4 |  | 10.8 | 10.8 | 0.59259 | 0 | 12.8 | 12.8 | 2.9536 | 40.5464 | 0.31569 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 488.7273 | 12.7273 | 71.25 | 364.3636 | 81.0629 | 146 | 99 | 80 | 4.2667 | 6.5333 | 10.8 | 10.8 | 0.32182 | 0.39506 | 12.8 | 12.8 | 2.4143 | 40.0857 | 0.31932 | 7.4 | 6.8 | 58 | 240 | 360 | 358.8571 | 0.31746 | 75.8333 | 299.4286 | 80.6298 | 99 | 49 | 28 | 2.1333 | 4.4 | 6.5333 | 6.5333 | 0.40599 | 0.32653 | 12.8 | 12.8 | 3.2303 | 42.7697 | 0.29928 | 6.8 | 6.7 | 100 | 360 | 560 | 486.0606 | 13.2035 | 58.3333 | 423.0303 | 76.361
[11 empty] | 1990-06-29 |  | 3031.5 | 24 | 145 | 47 | 53 | 0 | 6.6 | 4.3 |  | 10.9 | 10.9 | 0.6055 | 0 | 13.2 | 13.2 | 3.0223 | 39.9777 | 0.33018 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 502.4651 | 10.2741 | 71.25 | 371.2326 | 81.4133 | 145 | 97 | 81 | 4.3343 | 6.5657 | 10.9 | 10.9 | 0.32428 | 0.39764 | 13.003 | 13.003 | 2.4207 | 37.5793 | 0.34601 | 7.4 | 6.8 | 58 | 240 | 360 | 360.1473 | -0.040918 | 75.8333 | 300.0737 | 80.6714 | 97 | 47 | 25 | 2.2657 | 4.3 | 6.5657 | 6.5657 | 0.40348 | 0.34508 | 13.594 | 13.594 | 3.285 | 43.715 | 0.31097 | 6.8 | 6.7 | 100 | 360 | 560 | 496.9941 | 11.2511 | 58.3333 | 428.497 | 76.6626
[11 empty] | 1990-07-03 |  | 3098.6 | 24 | 146 | 50 | 55.5 | 0 | 6.7 | 4.7 |  | 11.4 | 11.4 | 0.58772 | 0 | 13.4 | 13.4 | 2.9288 | 39.5712 | 0.33863 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 483.766 | 13.6132 | 71.25 | 361.883 | 80.9331 | 146 | 100 | 85 | 4.4667 | 6.9333 | 11.4 | 11.4 | 0.34039 | 0.39181 | 13.4 | 13.4 | 2.4062 | 35.5938 | 0.37647 | 7.4 | 6.8 | 58 | 240 | 360 | 357.25 | 0.76389 | 75.8333 | 298.625 | 80.5776 | 100 | 50 | 26 | 2.2333 | 4.7 | 6.9333 | 6.9333 | 0.43199 | 0.32212 | 13.4 | 13.4 | 3.2177 | 45.7823 | 0.29269 | 6.8 | 6.7 | 100 | 360 | 560 | 483.5461 | 13.6525 | 58.3333 | 421.773 | 76.2906
[11 empty] | 1990-07-05 |  | 3146.9 | 24 | 146 | 55 | 54.5 | 0 | 6.6 | 4.6 |  | 11.2 | 11.2 | 0.58929 | 0 | 13.2 | 13.2 | 2.9367 | 43.0633 | 0.30653 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 485.3478 | 13.3307 | 71.25 | 362.6739 | 80.9746 | 146 | 100 | 84 | 4.3279 | 6.8721 | 11.2 | 11.2 | 0.33554 | 0.38642 | 12.9836 | 12.9836 | 2.3931 | 36.6069 | 0.35468 | 7.4 | 6.8 | 58 | 240 | 360 | 354.6183 | 1.4949 | 75.8333 | 297.3092 | 80.4917 | 100 | 55 | 25 | 2.2721 | 4.6 | 6.8721 | 6.8721 | 0.426 | 0.33063 | 13.6328 | 13.6328 | 3.2421 | 49.2579 | 0.27676 | 6.8 | 6.7 | 100 | 360 | 560 | 488.4248 | 12.7813 | 58.3333 | 424.2124 | 76.4269
[11 empty] | 1990-07-06 |  | 3169.6 | 24 | 145 | 55 | 52.5 | 0 | 6.5 | 4.6 |  | 11.1 | 11.1 | 0.58559 | 0 | 13 | 13 | 2.9182 | 44.5818 | 0.2916 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 481.6304 | 13.9946 | 71.25 | 360.8152 | 80.8766 | 145 | 98 | 80 | 4.3971 | 6.7029 | 11.1 | 11.1 | 0.33054 | 0.39613 | 13.1912 | 13.1912 | 2.417 | 39.083 | 0.33752 | 7.4 | 6.8 | 58 | 240 | 360 | 359.3901 | 0.16942 | 75.8333 | 299.695 | 80.647 | 98 | 55 | 25 | 2.1029 | 4.6 | 6.7029 | 6.7029 | 0.41972 | 0.31373 | 12.6176 | 12.6176 | 3.1943 | 48.3057 | 0.2612 | 6.8 | 6.7 | 100 | 360 | 560 | 478.8619 | 14.4889 | 58.3333 | 419.4309 | 76.1582
[11 empty] | 1990-07-09 |  | 3234.3 | 24 | 145 | 48 | 53.5 | 0 | 6.4 | 4.5 |  | 10.9 | 10.9 | 0.58716 | 0 | 12.8 | 12.8 | 2.926 | 40.074 | 0.31941 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 483.2 | 13.7143 | 71.25 | 361.6 | 80.9181 | 145 | 100 | 82 | 4.4 | 6.5 | 10.9 | 10.9 | 0.32306 | 0.40367 | 13.2 | 13.2 | 2.436 | 38.064 | 0.34678 | 7.4 | 6.8 | 58 | 240 | 360 | 363.2 | -0.88889 | 75.8333 | 301.6 | 80.7692 | 100 | 48 | 25 | 2 | 4.5 | 6.5 | 6.5 | 0.40847 | 0.30769 | 12 | 12 | 3.1778 | 45.8222 | 0.26188 | 6.8 | 6.7 | 100 | 360 | 560 | 475.5556 | 15.0794 | 58.3333 | 417.7778 | 76.0638
[11 empty] | 1990-07-10 |  | 3260.4 | 24 | 154 | 44 | 43.5 | 0 | 5.2 | 4.3 |  | 9.5 | 9.5 | 0.54737 | 0 | 10.4 | 10.4 | 2.744 | 52.756 | 0.19713 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 446.7907 | 20.2159 | 71.25 | 343.3953 | 79.9065 | 154 | 114 | 74 | 4.16 | 5.34 | 9.5 | 9.5 | 0.27553 | 0.43789 | 12.48 | 12.48 | 2.5289 | 57.4711 | 0.21715 | 7.4 | 6.8 | 58 | 240 | 360 | 381.7828 | -6.0508 | 75.8333 | 310.8914 | 81.344 | 114 | 44 | 13 | 1.04 | 4.3 | 5.34 | 5.34 | 0.35797 | 0.19476 | 6.24 | 6.24 | 2.9144 | 63.0856 | 0.098913 | 6.8 | 6.7 | 100 | 360 | 560 | 422.8837 | 24.485 | 58.3333 | 391.4419 | 74.4534
[11 empty] | 1990-07-11 |  | 3281.9 | 24 | 148 | 49 | 51 | 0 | 5.8 | 4.4 |  | 10.2 | 10.2 | 0.56863 | 0 | 11.6 | 11.6 | 2.837 | 44.663 | 0.25972 | 7.4 | 7.4 | 69 | 240 | 240 | 560 | 465.4091 | 16.8912 | 71.25 | 352.7045 | 80.4369 | 148 | 102 | 82 | 4.3254 | 5.8746 | 10.2 | 10.2 | 0.29845 | 0.42406 | 12.9763 | 12.9763 | 2.49 | 40.51 | 0.32032 | 7.4 | 6.8 | 58 | 240 | 360 | 374.0058 | -3.8905 | 75.8333 | 307.0029 | 81.1077 | 102 | 49 | 20 | 1.4746 | 4.4 | 5.8746 | 5.8746 | 0.38153 | 0.25101 | 8.8475 | 8.8475 | 3.0357 | 52.4643 | 0.16864 | 6.8 | 6.7 | 100 | 360 | 560 | 447.1341 | 20.1546 | 58.3333 | 403.567 | 75.221
[11 empty] | 1990-07-12 |  | 3306.6 | 24 | 148 | 49 | 51 | 0 | 5.8 | 4.3 |  | 10.1 | 10.1 | 0.57426 | 0 | 11.6 | 11.6 | 3.1144 | 44.3856 | 0.26135 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 510.8837 | -6.4341 | 71.5385 | 385.4419 | 80.8013 | 148 | 105 | 82 | 4.3254 | 5.7746 | 10.1 | 10.1 | 0.29474 | 0.42826 | 12.9763 | 12.9763 | 2.7765 | 41.7235 | 0.31101 | 7.4 | 6.8 | 58 | 260 | 380 | 411.3073 | -8.2388 | 77.6923 | 335.6537 | 82.7203 | 105 | 49 | 20 | 1.4746 | 4.3 | 5.7746 | 5.7746 | 0.3741 | 0.25536 | 8.8475 | 8.8475 | 3.3035 | 53.6965 | 0.16477 | 6.8 | 6.7 | 98 | 380 | 480 | 476.7048 | 0.68651 | 62.3077 | 428.3524 | 77.1216
[11 empty] | 1990-07-17 |  | 3330.7 | 24 | 146 | 50 | 53.5 | 0 | 6.3 | 4.5 |  | 10.8 | 10.8 | 0.58333 | 0 | 12.6 | 12.6 | 3.162 | 41.338 | 0.3048 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 520.4 | -8.4167 | 71.5385 | 390.2 | 81.0354 | 146 | 102 | 82 | 4.5443 | 6.2557 | 10.8 | 10.8 | 0.31667 | 0.42077 | 13.6328 | 13.6328 | 2.7537 | 39.2463 | 0.34736 | 7.4 | 6.8 | 58 | 260 | 380 | 406.7358 | -7.0357 | 77.6923 | 333.3679 | 82.6018 | 102 | 50 | 25 | 1.7557 | 4.5 | 6.2557 | 6.2557 | 0.3994 | 0.28066 | 10.5344 | 10.5344 | 3.3701 | 47.6299 | 0.22117 | 6.8 | 6.7 | 98 | 380 | 480 | 490.0262 | -2.0888 | 62.3077 | 435.0131 | 77.4719
[11 empty] | 1990-07-18 |  | 3352.5 | 24 | 147 | 52 | 51 | 0 | 6.1 | 4.8 |  | 10.9 | 10.9 | 0.55963 | 0 | 12.2 | 12.2 | 3.0419 | 45.4581 | 0.26838 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 496.375 | -3.4115 | 71.5385 | 378.1875 | 80.433 | 147 | 105 | 82 | 4.5492 | 6.3508 | 10.9 | 10.9 | 0.32029 | 0.41735 | 13.6475 | 13.6475 | 2.7435 | 41.2565 | 0.3308 | 7.4 | 6.8 | 58 | 260 | 380 | 404.6939 | -6.4984 | 77.6923 | 332.3469 | 82.5484 | 105 | 52 | 20 | 1.5508 | 4.8 | 6.3508 | 6.3508 | 0.41407 | 0.2442 | 9.3051 | 9.3051 | 3.2756 | 55.2244 | 0.1685 | 6.8 | 6.7 | 98 | 380 | 480 | 471.1123 | 1.8516 | 62.3077 | 425.5561 | 76.9713
[11 empty] | 1990-07-19 |  | 3375.4 | 24 | 166 | 50 | 8.5 | 0 | 2.5 | 4 |  | 6.5 | 6.5 | 0.38462 | 0 | 5 | 5 | 2.4413 | 97.0588 | 0.051515 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 376.25 | 21.6146 | 71.5385 | 318.125 | 76.7387 | 166 | 125 | 12 | 1.9565 | 4.5435 | 6.5 | 6.5 | 0.20504 | 0.301 | 5.8696 | 5.8696 | 2.4549 | 131.0451 | 0.04479 | 7.4 | 6.8 | 58 | 260 | 380 | 346.9856 | 8.688 | 77.6923 | 303.4928 | 80.8892 | 125 | 50 | 5 | 0.54348 | 4 | 4.5435 | 4.5435 | 0.31725 | 0.11962 | 3.2609 | 3.2609 | 3.0116 | 79.4884 | 0.041023 | 6.8 | 6.7 | 98 | 380 | 480 | 418.3152 | 12.851 | 62.3077 | 399.1576 | 75.4483
[11 empty] | 1990-07-24 |  | 3378 | 24 | 145 | 50 | 53 | 0 | 7.06 | 4.44 | X | 11.5 | 11.5 | 0.61391 | 0 | 14.12 | 14.12 | 3.3388 | 41.1612 | 0.34304 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 555.7568 | -15.7827 | 71.5385 | 407.8784 | 81.8573 | 145 | 100 | 76 | 4.7067 | 6.7933 | 11.5 | 11.5 | 0.33965 | 0.40928 | 14.12 | 14.12 | 2.7198 | 43.7802 | 0.32252 | 7.4 | 6.8 | 58 | 260 | 380 | 399.9529 | -5.2508 | 77.6923 | 329.9764 | 82.423 | 100 | 50 | 30 | 2.3533 | 4.44 | 6.7933 | 6.7933 | 0.41713 | 0.34642 | 14.12 | 14.12 | 3.5673 | 41.4327 | 0.34079 | 6.8 | 6.7 | 98 | 380 | 480 | 529.4685 | -10.3059 | 62.3077 | 454.7342 | 78.449
[11 empty] | 1990-07-25 |  | 3400.2 | 24 | 145 | 50 | 52.5 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 3.2973 | 41.7027 | 0.32612 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 547.4545 | -14.053 | 71.5385 | 403.7273 | 81.6708 | 145 | 100 | 77 | 4.675 | 6.525 | 11.2 | 11.2 | 0.3291 | 0.41741 | 14.025 | 14.025 | 2.7436 | 42.7564 | 0.32802 | 7.4 | 6.8 | 58 | 260 | 380 | 404.728 | -6.5074 | 77.6923 | 332.364 | 82.5493 | 100 | 50 | 28 | 2.125 | 4.4 | 6.525 | 6.525 | 0.40568 | 0.32567 | 12.75 | 12.75 | 3.501 | 43.499 | 0.29311 | 6.8 | 6.7 | 98 | 380 | 480 | 516.1932 | -7.5402 | 62.3077 | 448.0966 | 78.1297
[11 empty] | 1990-07-26 |  | 3422.3 | 24 | 146 | 50 | 53 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 3.255 | 41.745 | 0.31621 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 539 | -12.2917 | 71.5385 | 399.5 | 81.4768 | 146 | 100 | 78 | 4.5375 | 6.4625 | 11 | 11 | 0.32422 | 0.4125 | 13.6125 | 13.6125 | 2.7291 | 42.2709 | 0.32203 | 7.4 | 6.8 | 58 | 260 | 380 | 401.8298 | -5.7447 | 77.6923 | 330.9149 | 82.4728 | 100 | 50 | 28 | 2.0625 | 4.4 | 6.4625 | 6.4625 | 0.40336 | 0.31915 | 12.375 | 12.375 | 3.4809 | 43.5191 | 0.28436 | 6.8 | 6.7 | 98 | 380 | 480 | 512.1875 | -6.7057 | 62.3077 | 446.0938 | 78.0315
[11 empty] | 1990-07-27 |  | 3445.5 | 24 | 145 | 50 | 53 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 3.2339 | 41.2661 | 0.31503 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 534.7727 | -11.411 | 71.5385 | 397.3864 | 81.3783 | 145 | 100 | 78 | 4.4 | 6.5 | 10.9 | 10.9 | 0.32306 | 0.40367 | 13.2 | 13.2 | 2.7037 | 41.7963 | 0.31582 | 7.4 | 6.8 | 58 | 260 | 380 | 396.7385 | -4.4049 | 77.6923 | 328.3692 | 82.337 | 100 | 50 | 28 | 2.1 | 4.4 | 6.5 | 6.5 | 0.40476 | 0.32308 | 12.6 | 12.6 | 3.493 | 43.507 | 0.28961 | 6.8 | 6.7 | 98 | 380 | 480 | 514.5909 | -7.2064 | 62.3077 | 447.2955 | 78.0905
[11 empty] | 1990-07-30 |  | 3515.4 | 24 | 145 | 50 | 51.5 | 0 | 6.5 | 4.3 |  | 10.8 | 10.8 | 0.60185 | 0 | 13 | 13 | 3.2658 | 42.7342 | 0.30421 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 541.1628 | -12.7422 | 71.5385 | 400.5814 | 81.5269 | 145 | 100 | 73 | 4.4 | 6.4 | 10.8 | 10.8 | 0.31935 | 0.40741 | 13.2 | 13.2 | 2.7144 | 46.7856 | 0.28214 | 7.4 | 6.8 | 58 | 260 | 380 | 398.875 | -4.9671 | 77.6923 | 329.4375 | 82.3942 | 100 | 50 | 30 | 2.1 | 4.3 | 6.4 | 6.4 | 0.39733 | 0.32812 | 12.6 | 12.6 | 3.5086 | 41.4914 | 0.30368 | 6.8 | 6.7 | 98 | 380 | 480 | 517.7209 | -7.8585 | 62.3077 | 448.8605 | 78.1669
[11 empty] | 1990-07-31 |  | 3539.4 | 24 | 145 | 50 | 53 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 3.255 | 41.245 | 0.32004 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 539 | -12.2917 | 71.5385 | 399.5 | 81.4768 | 145 | 100 | 78 | 4.5375 | 6.4625 | 11 | 11 | 0.32422 | 0.4125 | 13.6125 | 13.6125 | 2.7291 | 41.7709 | 0.32589 | 7.4 | 6.8 | 58 | 260 | 380 | 401.8298 | -5.7447 | 77.6923 | 330.9149 | 82.4728 | 100 | 50 | 28 | 2.0625 | 4.4 | 6.4625 | 6.4625 | 0.40336 | 0.31915 | 12.375 | 12.375 | 3.4809 | 43.5191 | 0.28436 | 6.8 | 6.7 | 98 | 380 | 480 | 512.1875 | -6.7057 | 62.3077 | 446.0938 | 78.0315
[11 empty] | 1990-08-01 |  | 3560 | 24 | 146 | 49 | 52.5 | 0 | 6.4 | 4.4 |  | 10.8 | 10.8 | 0.59259 | 0 | 12.8 | 12.8 | 3.2127 | 41.7873 | 0.30631 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 530.5455 | -10.5303 | 71.5385 | 395.2727 | 81.2787 | 146 | 100 | 78 | 4.2667 | 6.5333 | 10.8 | 10.8 | 0.32182 | 0.39506 | 12.8 | 12.8 | 2.6796 | 42.3204 | 0.30245 | 7.4 | 6.8 | 58 | 260 | 380 | 391.9184 | -3.1364 | 77.6923 | 325.9592 | 82.2064 | 100 | 49 | 27 | 2.1333 | 4.4 | 6.5333 | 6.5333 | 0.40599 | 0.32653 | 12.8 | 12.8 | 3.5036 | 43.9964 | 0.29093 | 6.8 | 6.7 | 98 | 380 | 480 | 516.7273 | -7.6515 | 62.3077 | 448.3636 | 78.1427
[11 empty] | 1990-08-02 |  | 3583.9 | 24 | 145 | 50 | 55 | 0 | 6.4 | 4.2 |  | 10.6 | 10.6 | 0.60377 | 0 | 12.8 | 12.8 | 3.2771 | 39.2229 | 0.32634 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 543.4286 | -13.2143 | 71.5385 | 401.7143 | 81.5789 | 145 | 100 | 80 | 4.3294 | 6.2706 | 10.6 | 10.6 | 0.31323 | 0.40844 | 12.9882 | 12.9882 | 2.7173 | 39.7827 | 0.32648 | 7.4 | 6.8 | 58 | 260 | 380 | 399.4672 | -5.1229 | 77.6923 | 329.7336 | 82.41 | 100 | 50 | 30 | 2.0706 | 4.2 | 6.2706 | 6.2706 | 0.38881 | 0.33021 | 12.4235 | 12.4235 | 3.5151 | 41.4849 | 0.29947 | 6.8 | 6.7 | 98 | 380 | 480 | 519.0252 | -8.1303 | 62.3077 | 449.5126 | 78.1986
[11 empty] | 1990-08-03 |  | 3609.2 | 24 | 145 | 48 | 53 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 3.255 | 40.245 | 0.32799 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 539 | -12.2917 | 71.5385 | 399.5 | 81.4768 | 145 | 99 | 78 | 4.4677 | 6.5323 | 11 | 11 | 0.32552 | 0.40615 | 13.4031 | 13.4031 | 2.7108 | 41.2892 | 0.32461 | 7.4 | 6.8 | 58 | 260 | 380 | 398.1554 | -4.7777 | 77.6923 | 329.0777 | 82.375 | 99 | 48 | 28 | 2.1323 | 4.4 | 6.5323 | 6.5323 | 0.40595 | 0.32642 | 12.7938 | 12.7938 | 3.5033 | 41.9967 | 0.30464 | 6.8 | 6.7 | 98 | 380 | 480 | 516.6615 | -7.6378 | 62.3077 | 448.3308 | 78.1411
[11 empty] | 1990-08-06 |  | 3676.7 | 24 | 144 | 48 | 52 | 0 | 6.3 | 4.3 |  | 10.6 | 10.6 | 0.59434 | 0 | 12.6 | 12.6 | 3.2226 | 40.7774 | 0.30899 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 532.5116 | -10.9399 | 71.5385 | 396.2558 | 81.3252 | 144 | 98 | 77 | 4.2646 | 6.3354 | 10.6 | 10.6 | 0.31443 | 0.40232 | 12.7938 | 12.7938 | 2.6999 | 41.3001 | 0.30978 | 7.4 | 6.8 | 58 | 260 | 380 | 395.9747 | -4.2039 | 77.6923 | 327.9874 | 82.3164 | 98 | 48 | 27 | 2.0354 | 4.3 | 6.3354 | 6.3354 | 0.39493 | 0.32127 | 12.2123 | 12.2123 | 3.4874 | 42.5126 | 0.28726 | 6.8 | 6.7 | 98 | 380 | 480 | 513.4834 | -6.9757 | 62.3077 | 446.7417 | 78.0634
[11 empty] | 1990-08-07 |  | 3700.3 | 24 | 144 | 48 | 51.5 | 0 | 6.3 | 4.3 |  | 10.6 | 10.6 | 0.59434 | 0 | 12.6 | 12.6 | 3.2226 | 41.2774 | 0.30525 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 532.5116 | -10.9399 | 71.5385 | 396.2558 | 81.3252 | 144 | 98 | 76 | 4.3312 | 6.2687 | 10.6 | 10.6 | 0.3132 | 0.40861 | 12.9938 | 12.9938 | 2.7178 | 42.2822 | 0.30731 | 7.4 | 6.8 | 58 | 260 | 380 | 399.5673 | -5.1493 | 77.6923 | 329.7836 | 82.4127 | 98 | 48 | 27 | 1.9688 | 4.3 | 6.2687 | 6.2687 | 0.39245 | 0.31406 | 11.8125 | 11.8125 | 3.4656 | 42.5344 | 0.27772 | 6.8 | 6.7 | 98 | 380 | 480 | 509.1134 | -6.0653 | 62.3077 | 444.5567 | 77.9556
[11 empty] | 1990-08-08 |  | 3721.3 | 24 | 144 | 50 | 53 | 0 | 6.59 | 4.26 |  | 10.85 | 10.85 | 0.60737 | 0 | 13.18 | 13.18 | 3.2987 | 40.7013 | 0.32382 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 547.7324 | -14.1109 | 71.5385 | 403.8662 | 81.6771 | 144 | 99 | 77 | 4.4642 | 6.3858 | 10.85 | 10.85 | 0.32001 | 0.41145 | 13.3926 | 13.3926 | 2.7261 | 41.7739 | 0.3206 | 7.4 | 6.8 | 58 | 260 | 380 | 401.2143 | -5.5827 | 77.6923 | 330.6071 | 82.4565 | 99 | 50 | 29 | 2.1258 | 4.26 | 6.3858 | 6.3858 | 0.39532 | 0.3329 | 12.7548 | 12.7548 | 3.5236 | 41.9764 | 0.30386 | 6.8 | 6.7 | 98 | 380 | 480 | 520.7224 | -8.4838 | 62.3077 | 450.3612 | 78.2397
[11 empty] | 1990-08-10 |  | 3769.7 | 24 | 140 | 48 | 46 | 0 | 6.4 | 4.5 |  | 10.9 | 10.9 | 0.58716 | 0 | 12.8 | 12.8 | 3.1827 | 44.8173 | 0.2856 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 524.5333 | -9.2778 | 71.5385 | 392.2667 | 81.1353 | 140 | 96 | 72 | 4.4 | 6.5 | 10.9 | 10.9 | 0.32306 | 0.40367 | 13.2 | 13.2 | 2.7037 | 43.2963 | 0.30488 | 7.4 | 6.8 | 58 | 260 | 380 | 396.7385 | -4.4049 | 77.6923 | 328.3692 | 82.337 | 96 | 48 | 20 | 2 | 4.5 | 6.5 | 6.5 | 0.40847 | 0.30769 | 12 | 12 | 3.4467 | 48.5533 | 0.24715 | 6.8 | 6.7 | 98 | 380 | 480 | 505.3333 | -5.2778 | 62.3077 | 442.6667 | 77.8614
[11 empty] | 1990-08-13 |  | 3840 | 24 | 136 | 40 | 45 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 3.2339 | 39.7661 | 0.32691 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 534.7727 | -11.411 | 71.5385 | 397.3864 | 81.3783 | 136 | 90 | 70 | 4.4688 | 6.4313 | 10.9 | 10.9 | 0.32178 | 0.40998 | 13.4062 | 13.4062 | 2.7218 | 40.2782 | 0.33284 | 7.4 | 6.8 | 58 | 260 | 380 | 400.3596 | -5.3578 | 77.6923 | 330.1798 | 82.4338 | 90 | 40 | 20 | 2.0312 | 4.4 | 6.4313 | 6.4313 | 0.4022 | 0.31584 | 12.1875 | 12.1875 | 3.4709 | 41.5291 | 0.29347 | 6.8 | 6.7 | 98 | 380 | 480 | 510.1847 | -6.2885 | 62.3077 | 445.0923 | 77.9821
[11 empty] | 1990-08-14 |  | 3862.9 | 24 | 140 | 42 | 49.5 | 0 | 6 | 4.5 |  | 10.5 | 10.5 | 0.57143 | 0 | 12 | 12 | 3.1 | 38.4 | 0.3125 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 508 | -5.8333 | 71.5385 | 384 | 80.7292 | 140 | 92 | 74 | 4.1311 | 6.3689 | 10.5 | 10.5 | 0.3132 | 0.39344 | 12.3934 | 12.3934 | 2.6751 | 39.3249 | 0.31516 | 7.4 | 6.8 | 58 | 260 | 380 | 391.027 | -2.9018 | 77.6923 | 325.5135 | 82.182 | 92 | 42 | 25 | 1.8689 | 4.5 | 6.3689 | 6.3689 | 0.4036 | 0.29344 | 11.2131 | 11.2131 | 3.4056 | 38.5944 | 0.29054 | 6.8 | 6.7 | 98 | 380 | 480 | 497.1148 | -3.5656 | 62.3077 | 438.5574 | 77.654
[11 empty] | 1990-08-15 |  | 3884.2 | 24 | 136 | 40 | 42.5 | 0 | 6.4 | 4.4 |  | 10.8 | 10.8 | 0.59259 | 0 | 12.8 | 12.8 | 3.2127 | 42.2873 | 0.30269 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 530.5455 | -10.5303 | 71.5385 | 395.2727 | 81.2787 | 136 | 90 | 70 | 4.4066 | 6.3934 | 10.8 | 10.8 | 0.31923 | 0.40801 | 13.2197 | 13.2197 | 2.7161 | 40.2839 | 0.32816 | 7.4 | 6.8 | 58 | 260 | 380 | 399.2246 | -5.0591 | 77.6923 | 329.6123 | 82.4036 | 90 | 40 | 15 | 1.9934 | 4.4 | 6.3934 | 6.3934 | 0.4008 | 0.31179 | 11.9607 | 11.9607 | 3.4588 | 46.5412 | 0.25699 | 6.8 | 6.7 | 98 | 380 | 480 | 507.7615 | -5.7837 | 62.3077 | 443.8808 | 77.922
[11 empty] | 1990-08-16 |  | 3909.9 | 24 | 145 | 45 | 50 | 0 | 6.3 | 4.5 |  | 10.8 | 10.8 | 0.58333 | 0 | 12.6 | 12.6 | 3.162 | 41.838 | 0.30116 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 520.4 | -8.4167 | 71.5385 | 390.2 | 81.0354 | 145 | 95 | 75 | 4.3377 | 6.4623 | 10.8 | 10.8 | 0.3205 | 0.40164 | 13.0131 | 13.0131 | 2.6979 | 42.3021 | 0.30762 | 7.4 | 6.8 | 58 | 260 | 380 | 395.589 | -4.1024 | 77.6923 | 327.7945 | 82.306 | 95 | 45 | 25 | 1.9623 | 4.5 | 6.4623 | 6.4623 | 0.40707 | 0.30365 | 11.7738 | 11.7738 | 3.4349 | 41.5651 | 0.28326 | 6.8 | 6.7 | 98 | 380 | 480 | 502.9705 | -4.7855 | 62.3077 | 441.4852 | 77.8022
[11 empty] | 1990-08-17 |  | 3933.3 | 24 | 144 | 40 | 46 | 0 | 6.5 | 4.5 |  | 11 | 11 | 0.59091 | 0 | 13 | 13 | 3.2033 | 42.7967 | 0.30376 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 528.6667 | -10.1389 | 71.5385 | 394.3333 | 81.2342 | 144 | 92 | 72 | 4.4754 | 6.5246 | 11 | 11 | 0.32537 | 0.40686 | 13.4262 | 13.4262 | 2.7128 | 43.2872 | 0.31017 | 7.4 | 6.8 | 58 | 260 | 380 | 398.5578 | -4.8836 | 77.6923 | 329.2789 | 82.3858 | 92 | 40 | 20 | 2.0246 | 4.5 | 6.5246 | 6.5246 | 0.40938 | 0.3103 | 12.1475 | 12.1475 | 3.4544 | 42.5456 | 0.28552 | 6.8 | 6.7 | 98 | 380 | 480 | 506.8743 | -5.5988 | 62.3077 | 443.4372 | 77.8999
[11 empty] | 1990-08-20 |  | 4001.6 | 24 | 143 | 40 | 45.5 | 0 | 6.4 | 4.5 |  | 10.9 | 10.9 | 0.58716 | 0 | 12.8 | 12.8 | 3.1827 | 42.8173 | 0.29894 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 524.5333 | -9.2778 | 71.5385 | 392.2667 | 81.1353 | 143 | 91 | 71 | 4.339 | 6.561 | 10.9 | 10.9 | 0.32419 | 0.39807 | 13.0169 | 13.0169 | 2.6879 | 43.3121 | 0.30054 | 7.4 | 6.8 | 58 | 260 | 380 | 393.5882 | -3.5758 | 77.6923 | 326.7941 | 82.2518 | 91 | 40 | 20 | 2.061 | 4.5 | 6.561 | 6.561 | 0.41073 | 0.31413 | 12.3661 | 12.3661 | 3.4658 | 42.0342 | 0.29419 | 6.8 | 6.7 | 98 | 380 | 480 | 509.1571 | -6.0744 | 62.3077 | 444.5785 | 77.9567
[11 empty] | 1990-08-21 |  | 4022.3 | 24 | 145 | 35 | 49.5 | 0 | 6 | 4.4 |  | 10.4 | 10.4 | 0.57692 | 0 | 12 | 12 | 3.1282 | 37.3718 | 0.3211 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 513.6364 | -7.0076 | 71.5385 | 386.8182 | 80.8696 | 145 | 90 | 74 | 4.2857 | 6.1143 | 10.4 | 10.4 | 0.30662 | 0.41209 | 12.8571 | 12.8571 | 2.7279 | 40.7721 | 0.31534 | 7.4 | 6.8 | 58 | 260 | 380 | 401.5888 | -5.6813 | 77.6923 | 330.7944 | 82.4665 | 90 | 35 | 25 | 1.7143 | 4.4 | 6.1143 | 6.1143 | 0.39043 | 0.28037 | 10.2857 | 10.2857 | 3.3694 | 34.1306 | 0.30136 | 6.8 | 6.7 | 98 | 380 | 480 | 489.8701 | -2.0563 | 62.3077 | 434.9351 | 77.4679
[11 empty] | 1990-08-22 |  | 4048.5 | 24 | 146 | 40 | 48.5 | 0 | 5.9 | 4.4 |  | 10.3 | 10.3 | 0.57282 | 0 | 11.8 | 11.8 | 3.107 | 41.393 | 0.28507 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 509.4091 | -6.1269 | 71.5385 | 384.7045 | 80.7645 | 146 | 92 | 73 | 4.069 | 6.231 | 10.3 | 10.3 | 0.30693 | 0.39505 | 12.2069 | 12.2069 | 2.6795 | 43.3205 | 0.28178 | 7.4 | 6.8 | 58 | 260 | 380 | 391.9092 | -3.134 | 77.6923 | 325.9546 | 82.2061 | 92 | 40 | 24 | 1.831 | 4.4 | 6.231 | 6.231 | 0.39477 | 0.29386 | 10.9862 | 10.9862 | 3.4068 | 38.5932 | 0.28467 | 6.8 | 6.7 | 98 | 380 | 480 | 497.3527 | -3.6151 | 62.3077 | 438.6763 | 77.6601
[11 empty] | 1990-08-24 |  | 4094.3 | 24 | 145 | 38 | 44 | 0 | 6 | 4.4 |  | 10.4 | 10.4 | 0.57692 | 0 | 12 | 12 | 3.1282 | 44.3718 | 0.27044 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 513.6364 | -7.0076 | 71.5385 | 386.8182 | 80.8696 | 145 | 88 | 68 | 4.1311 | 6.2689 | 10.4 | 10.4 | 0.30949 | 0.39723 | 12.3934 | 12.3934 | 2.6856 | 45.8144 | 0.27051 | 7.4 | 6.8 | 58 | 260 | 380 | 393.1172 | -3.4519 | 77.6923 | 326.5586 | 82.239 | 88 | 38 | 20 | 1.8689 | 4.4 | 6.2689 | 6.2689 | 0.39617 | 0.29812 | 11.2131 | 11.2131 | 3.4189 | 39.5811 | 0.28329 | 6.8 | 6.7 | 98 | 380 | 480 | 499.7765 | -4.1201 | 62.3077 | 439.8882 | 77.7216
[11 empty] | 1990-08-27 |  | 4096.7 | 24 | 145 | 40 | 49 | 0 | 6.2 | 4.6 |  | 10.8 | 10.8 | 0.57407 | 0 | 12.4 | 12.4 | 3.1135 | 40.3865 | 0.30703 | 7.4 | 7.4 | 74 | 250 | 260 | 480 | 510.6957 | -6.3949 | 71.5385 | 385.3478 | 80.7966 | 145 | 93 | 73 | 4.2689 | 6.5311 | 10.8 | 10.8 | 0.32178 | 0.39526 | 12.8066 | 12.8066 | 2.6802 | 43.3198 | 0.29563 | 7.4 | 6.8 | 58 | 260 | 380 | 392.0301 | -3.1658 | 77.6923 | 326.0151 | 82.2094 | 93 | 40 | 25 | 1.9311 | 4.6 | 6.5311 | 6.5311 | 0.41334 | 0.29568 | 11.5869 | 11.5869 | 3.4119 | 38.0881 | 0.30421 | 6.8 | 6.7 | 98 | 380 | 480 | 498.3877 | -3.8308 | 62.3077 | 439.1939 | 77.6864
[11 empty] | 1990-08-28 |  | 4120.4 | 24 | 145 | 38 | 48 | 0 | 6 | 4.5 |  | 10.5 | 10.5 | 0.57143 | 0 | 12 | 12 | 2.9333 | 40.5667 | 0.29581 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 484.6667 | 1.0884 | 70.4 | 367.3333 | 79.8548 | 145 | 90 | 72 | 4.1379 | 6.3621 | 10.5 | 10.5 | 0.31307 | 0.39409 | 12.4138 | 12.4138 | 2.6239 | 42.8761 | 0.28953 | 7.4 | 6.8 | 52 | 250 | 370 | 378.7805 | -2.3731 | 79.2 | 314.3902 | 83.46 | 90 | 38 | 24 | 1.8621 | 4.5 | 6.3621 | 6.3621 | 0.40335 | 0.29268 | 11.1724 | 11.1724 | 3.2828 | 36.7172 | 0.30428 | 6.8 | 6.7 | 98 | 370 | 490 | 482.5517 | 1.5201 | 60.8 | 426.2759 | 77.0102
[11 empty] | 1990-08-29 |  | 4144.3 | 24 | 146 | 38 | 48 | 0 | 6 | 4.5 |  | 10.5 | 10.5 | 0.57143 | 0 | 12 | 12 | 2.9333 | 41.0667 | 0.29221 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 484.6667 | 1.0884 | 70.4 | 367.3333 | 79.8548 | 146 | 90 | 72 | 4.1379 | 6.3621 | 10.5 | 10.5 | 0.31307 | 0.39409 | 12.4138 | 12.4138 | 2.6239 | 43.3761 | 0.28619 | 7.4 | 6.8 | 52 | 250 | 370 | 378.7805 | -2.3731 | 79.2 | 314.3902 | 83.46 | 90 | 38 | 24 | 1.8621 | 4.5 | 6.3621 | 6.3621 | 0.40335 | 0.29268 | 11.1724 | 11.1724 | 3.2828 | 36.7172 | 0.30428 | 6.8 | 6.7 | 98 | 370 | 490 | 482.5517 | 1.5201 | 60.8 | 426.2759 | 77.0102
[11 empty] | 1990-08-30 |  | 4166 | 24 | 145 | 38 | 47 | 0 | 6.1 | 4.6 |  | 10.7 | 10.7 | 0.57009 | 0 | 12.2 | 12.2 | 2.927 | 41.573 | 0.29346 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 483.3913 | 1.3487 | 70.4 | 366.6957 | 79.8198 | 145 | 90 | 70 | 4.27 | 6.43 | 10.7 | 10.7 | 0.31805 | 0.39907 | 12.81 | 12.81 | 2.6374 | 44.8626 | 0.28554 | 7.4 | 6.8 | 52 | 250 | 370 | 381.4868 | -3.1045 | 79.2 | 315.7434 | 83.5309 | 90 | 38 | 24 | 1.83 | 4.6 | 6.43 | 6.43 | 0.40958 | 0.2846 | 10.98 | 10.98 | 3.261 | 36.739 | 0.29887 | 6.8 | 6.7 | 98 | 370 | 490 | 478.2087 | 2.4064 | 60.8 | 424.1043 | 76.8925
[11 empty] | 1990-08-31 |  | 4192.8 | 24 | 145 | 35 | 46.5 | 0 | 6 | 4.5 |  | 10.5 | 10.5 | 0.57143 | 0 | 12 | 12 | 2.9333 | 40.5667 | 0.29581 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 484.6667 | 1.0884 | 70.4 | 367.3333 | 79.8548 | 145 | 87 | 68 | 4.2 | 6.3 | 10.5 | 10.5 | 0.31192 | 0.4 | 12.6 | 12.6 | 2.64 | 45.36 | 0.27778 | 7.4 | 6.8 | 52 | 250 | 370 | 382 | -3.2432 | 79.2 | 316 | 83.5443 | 87 | 35 | 25 | 1.8 | 4.5 | 6.3 | 6.3 | 0.40104 | 0.28571 | 10.8 | 10.8 | 3.264 | 32.736 | 0.32991 | 6.8 | 6.7 | 98 | 370 | 490 | 478.8 | 2.2857 | 60.8 | 424.4 | 76.9086
[11 empty] | 1990-09-04 |  | 4281.6 | 24 | 145 | 35 | 41.5 | 0 | 6.1 | 4.4 |  | 10.5 | 10.5 | 0.58095 | 0 | 12.2 | 12.2 | 2.98 | 45.52 | 0.26801 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 494 | -0.81633 | 70.4 | 372 | 80.1075 | 145 | 85 | 65 | 4.27 | 6.23 | 10.5 | 10.5 | 0.31062 | 0.40667 | 12.81 | 12.81 | 2.6585 | 47.3415 | 0.27059 | 7.4 | 6.8 | 52 | 250 | 370 | 385.7079 | -4.2454 | 79.2 | 317.8539 | 83.6403 | 85 | 35 | 18 | 1.83 | 4.4 | 6.23 | 6.23 | 0.39473 | 0.29374 | 10.98 | 10.98 | 3.2856 | 38.7144 | 0.28362 | 6.8 | 6.7 | 98 | 370 | 490 | 483.1273 | 1.4026 | 60.8 | 426.5636 | 77.0257
[11 empty] | 1990-09-05 |  | 4304.9 | 24 | 146 | 35 | 44 | 0 | 6 | 4.4 |  | 10.4 | 10.4 | 0.57692 | 0 | 12 | 12 | 2.96 | 43.54 | 0.27561 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 490 | 0 | 70.4 | 370 | 80 | 146 | 87 | 68 | 4.2105 | 6.1895 | 10.4 | 10.4 | 0.30801 | 0.40486 | 12.6316 | 12.6316 | 2.6535 | 45.8465 | 0.27552 | 7.4 | 6.8 | 52 | 250 | 370 | 384.6939 | -3.9713 | 79.2 | 317.3469 | 83.6141 | 87 | 35 | 20 | 1.7895 | 4.4 | 6.1895 | 6.1895 | 0.39322 | 0.28912 | 10.7368 | 10.7368 | 3.2731 | 37.7269 | 0.28459 | 6.8 | 6.7 | 98 | 370 | 490 | 480.622 | 1.9139 | 60.8 | 425.311 | 76.958
[11 empty] | 1990-09-06 |  | 4331 | 24 | 145 | 33 | 40 | 0 | 5.9 | 4.4 |  | 10.3 | 10.3 | 0.57282 | 0 | 11.8 | 11.8 | 2.94 | 46.06 | 0.25619 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 486 | 0.81633 | 70.4 | 368 | 79.8913 | 145 | 85 | 65 | 4.069 | 6.231 | 10.3 | 10.3 | 0.30693 | 0.39505 | 12.2069 | 12.2069 | 2.6265 | 47.3735 | 0.25767 | 7.4 | 6.8 | 52 | 250 | 370 | 379.2972 | -2.5128 | 79.2 | 314.6486 | 83.4736 | 85 | 33 | 15 | 1.831 | 4.4 | 6.231 | 6.231 | 0.39477 | 0.29386 | 10.9862 | 10.9862 | 3.286 | 40.714 | 0.26984 | 6.8 | 6.7 | 98 | 370 | 490 | 483.1912 | 1.3895 | 60.8 | 426.5956 | 77.0274
[11 empty] | 1990-09-10 |  | 4420 | 24 | 145 | 35 | 40 | 0 | 6.1 | 4.5 |  | 10.6 | 10.6 | 0.57547 | 0 | 12.2 | 12.2 | 2.9529 | 47.0471 | 0.25931 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 488.5778 | 0.29025 | 70.4 | 369.2889 | 79.9615 | 145 | 85 | 65 | 4.3717 | 6.2283 | 10.6 | 10.6 | 0.31245 | 0.41242 | 13.115 | 13.115 | 2.6749 | 47.3251 | 0.27713 | 7.4 | 6.8 | 52 | 250 | 370 | 388.9762 | -5.1287 | 79.2 | 319.4881 | 83.724 | 85 | 35 | 15 | 1.7283 | 4.5 | 6.2283 | 6.2283 | 0.39838 | 0.2775 | 10.37 | 10.37 | 3.2423 | 41.7577 | 0.24834 | 6.8 | 6.7 | 98 | 370 | 490 | 474.4681 | 3.1698 | 60.8 | 422.2341 | 76.7901
[11 empty] | 1990-09-11 |  | 4445.8 | 24 | 145 | 35 | 43.5 | 0 | 6 | 4.4 |  | 10.4 | 10.4 | 0.57692 | 0 | 12 | 12 | 2.96 | 43.54 | 0.27561 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 490 | 0 | 70.4 | 370 | 80 | 145 | 85 | 70 | 4.1379 | 6.2621 | 10.4 | 10.4 | 0.30936 | 0.39788 | 12.4138 | 12.4138 | 2.6342 | 42.3658 | 0.29301 | 7.4 | 6.8 | 52 | 250 | 370 | 380.837 | -2.9289 | 79.2 | 315.4185 | 83.514 | 85 | 35 | 17 | 1.8621 | 4.4 | 6.2621 | 6.2621 | 0.39592 | 0.29736 | 11.1724 | 11.1724 | 3.2955 | 39.7045 | 0.28139 | 6.8 | 6.7 | 98 | 370 | 490 | 485.1097 | 0.99802 | 60.8 | 427.5549 | 77.079
[11 empty] | 1990-09-12 |  | 4466.4 | 24 | 145 | 35 | 45 | 0 | 6 | 4.3 |  | 10.3 | 10.3 | 0.58252 | 0 | 12 | 12 | 2.9879 | 42.0121 | 0.28563 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 495.5814 | -1.1391 | 70.4 | 372.7907 | 80.1497 | 145 | 85 | 70 | 4.3279 | 5.9721 | 10.3 | 10.3 | 0.30212 | 0.42018 | 12.9836 | 12.9836 | 2.6974 | 42.3026 | 0.30692 | 7.4 | 6.8 | 52 | 250 | 370 | 393.4861 | -6.3476 | 79.2 | 321.7431 | 83.838 | 85 | 35 | 20 | 1.6721 | 4.3 | 5.9721 | 5.9721 | 0.38144 | 0.27999 | 10.0328 | 10.0328 | 3.2489 | 36.7511 | 0.27299 | 6.8 | 6.7 | 98 | 370 | 490 | 475.772 | 2.9037 | 60.8 | 422.886 | 76.8259
[11 empty] | 1990-09-13 |  | 4491.1 | 24 | 145 | 35 | 45 | 0 | 6 | 4.3 |  | 10.3 | 10.3 | 0.58252 | 0 | 12 | 12 | 2.9879 | 42.0121 | 0.28563 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 495.5814 | -1.1391 | 70.4 | 372.7907 | 80.1497 | 145 | 85 | 70 | 4.3279 | 5.9721 | 10.3 | 10.3 | 0.30212 | 0.42018 | 12.9836 | 12.9836 | 2.6974 | 42.3026 | 0.30692 | 7.4 | 6.8 | 52 | 250 | 370 | 393.4861 | -6.3476 | 79.2 | 321.7431 | 83.838 | 85 | 35 | 20 | 1.6721 | 4.3 | 5.9721 | 5.9721 | 0.38144 | 0.27999 | 10.0328 | 10.0328 | 3.2489 | 36.7511 | 0.27299 | 6.8 | 6.7 | 98 | 370 | 490 | 475.772 | 2.9037 | 60.8 | 422.886 | 76.8259
[11 empty] | 1990-09-20 |  | 4515.4 | 24 | 145 | 40 | 51 | 0 | 6.68 | 4.46 | X | 11.14 | 11.14 | 0.59964 | 0 | 13.36 | 13.36 | 3.078 | 38.422 | 0.34772 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 513.6054 | -4.8174 | 70.4 | 381.8027 | 80.6183 | 145 | 95 | 77 | 4.5252 | 6.6148 | 11.14 | 11.14 | 0.32965 | 0.40621 | 13.5755 | 13.5755 | 2.6573 | 40.3427 | 0.3365 | 7.4 | 6.8 | 52 | 250 | 370 | 385.4503 | -4.1758 | 79.2 | 317.7252 | 83.6337 | 95 | 40 | 25 | 2.1548 | 4.46 | 6.6148 | 6.6148 | 0.41125 | 0.32576 | 12.929 | 12.929 | 3.3771 | 39.1229 | 0.33047 | 6.8 | 6.7 | 98 | 370 | 490 | 501.4162 | -2.3298 | 60.8 | 435.7081 | 77.5079
[11 empty] | 1990-09-20 |  | 4516.6 | 24 | 145 | 42 | 52 | 0 | 6.58 | 4.56 |  | 11.14 | 11.14 | 0.59066 | 0 | 13.16 | 13.16 | 3.0298 | 38.4702 | 0.34208 | 7.4 | 7.4 | 74 | 260 | 250 | 490 | 503.9649 | -2.85 | 70.4 | 376.9825 | 80.3704 | 145 | 94 | 78 | 4.3867 | 6.7533 | 11.14 | 11.14 | 0.33222 | 0.39378 | 13.16 | 13.16 | 2.6231 | 38.8769 | 0.3385 | 7.4 | 6.8 | 52 | 250 | 370 | 378.612 | -2.3276 | 79.2 | 314.306 | 83.4556 | 94 | 42 | 26 | 2.1933 | 4.56 | 6.7533 | 6.7533 | 0.4201 | 0.32478 | 13.16 | 13.16 | 3.3742 | 38.6258 | 0.3407 | 6.8 | 6.7 | 98 | 370 | 490 | 500.8304 | -2.2103 | 60.8 | 435.4152 | 77.4927
[11 empty] | 1990-09-21 |  | 4537.2 | 24 | 146 | 42 | 51.5 | 0 | 6.4 | 4.4 |  | 10.8 | 10.8 | 0.59259 | 0 | 12.8 | 12.8 | 4.4564 | 38.0436 | 0.33646 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 715.2727 | -11.7614 | 75.8824 | 527.6364 | 84.459 | 146 | 94 | 78 | 5.0087 | 5.7913 | 10.8 | 10.8 | 0.30805 | 0.46377 | 15.0261 | 15.0261 | 3.4951 | 38.5049 | 0.39024 | 6.2 | 6.1 | 96 | 340 | 440 | 551.027 | -25.2334 | 71.7647 | 445.5135 | 78.4518 | 94 | 42 | 25 | 1.3913 | 4.4 | 5.7913 | 5.7913 | 0.37844 | 0.24024 | 8.3478 | 8.3478 | 3.8217 | 39.1783 | 0.21307 | 6.1 | 5.8 | 110 | 440 | 640 | 544.3478 | 14.9457 | 67.6471 | 492.1739 | 77.6502
[11 empty] | 1990-09-24 |  | 4607.3 | 24 | 145 | 40 | 52.5 | 0 | 6.5 | 4.3 |  | 10.8 | 10.8 | 0.60185 | 0 | 13 | 13 | 4.53 | 35.47 | 0.36651 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 730 | -14.0625 | 75.8824 | 535 | 84.6729 | 145 | 90 | 80 | 4.3333 | 6.4667 | 10.8 | 10.8 | 0.32059 | 0.40123 | 13 | 13 | 3.2575 | 34.2425 | 0.37965 | 6.2 | 6.1 | 96 | 340 | 440 | 503.5052 | -14.433 | 71.7647 | 421.7526 | 77.2378 | 90 | 40 | 25 | 2.1667 | 4.3 | 6.4667 | 6.4667 | 0.3998 | 0.33505 | 13 | 13 | 4.1314 | 35.8686 | 0.36243 | 6.1 | 5.8 | 110 | 440 | 640 | 606.2791 | 5.2689 | 67.6471 | 523.1395 | 78.9731
[11 empty] | 1990-09-25 |  | 4632.7 | 24 | 145 | 40 | 53.5 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 4.4857 | 34.5143 | 0.37666 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 721.1364 | -12.6776 | 75.8824 | 530.5682 | 84.5449 | 145 | 93 | 80 | 4.4032 | 6.4968 | 10.9 | 10.9 | 0.323 | 0.40397 | 13.2097 | 13.2097 | 3.2669 | 35.7331 | 0.36968 | 6.2 | 6.1 | 96 | 340 | 440 | 505.3724 | -14.8574 | 71.7647 | 422.6862 | 77.2881 | 93 | 40 | 27 | 2.0968 | 4.4 | 6.4968 | 6.4968 | 0.40464 | 0.32274 | 12.5806 | 12.5806 | 4.0863 | 35.4137 | 0.35525 | 6.1 | 5.8 | 110 | 440 | 640 | 597.2581 | 6.6784 | 67.6471 | 518.629 | 78.7902
[11 empty] | 1990-09-26 |  | 4655.4 | 24 | 145 | 40 | 53.5 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 4.4857 | 34.5143 | 0.37666 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 721.1364 | -12.6776 | 75.8824 | 530.5682 | 84.5449 | 145 | 93 | 80 | 4.3333 | 6.5667 | 10.9 | 10.9 | 0.3243 | 0.39755 | 13 | 13 | 3.2451 | 35.7549 | 0.36359 | 6.2 | 6.1 | 96 | 340 | 440 | 501.0152 | -13.8671 | 71.7647 | 420.5076 | 77.1704 | 93 | 40 | 27 | 2.1667 | 4.4 | 6.5667 | 6.5667 | 0.40723 | 0.32995 | 13 | 13 | 4.1125 | 35.3875 | 0.36736 | 6.1 | 5.8 | 110 | 440 | 640 | 602.5 | 5.8594 | 67.6471 | 521.25 | 78.8969
[11 empty] | 1990-09-27 |  | 4679.9 | 24 | 146 | 40 | 53.5 | 0 | 6.5 | 4.3 |  | 10.8 | 10.8 | 0.60185 | 0 | 13 | 13 | 4.53 | 34.97 | 0.37175 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 730 | -14.0625 | 75.8824 | 535 | 84.6729 | 146 | 92 | 80 | 4.4032 | 6.3968 | 10.8 | 10.8 | 0.31929 | 0.40771 | 13.2097 | 13.2097 | 3.2798 | 35.7202 | 0.36981 | 6.2 | 6.1 | 96 | 340 | 440 | 507.9576 | -15.4449 | 71.7647 | 423.9788 | 77.3574 | 92 | 40 | 27 | 2.0968 | 4.3 | 6.3968 | 6.3968 | 0.39721 | 0.32779 | 12.5806 | 12.5806 | 4.1046 | 34.8954 | 0.36052 | 6.1 | 5.8 | 110 | 440 | 640 | 600.9152 | 6.107 | 67.6471 | 520.4576 | 78.8648
[11 empty] | 1990-09-28 |  | 4704.9 | 24 | 146 | 40 | 53.5 | 0 | 6.5 | 4.3 |  | 10.8 | 10.8 | 0.60185 | 0 | 13 | 13 | 4.53 | 34.97 | 0.37175 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 730 | -14.0625 | 75.8824 | 535 | 84.6729 | 146 | 93 | 80 | 4.4032 | 6.3968 | 10.8 | 10.8 | 0.31929 | 0.40771 | 13.2097 | 13.2097 | 3.2798 | 36.2202 | 0.3647 | 6.2 | 6.1 | 96 | 340 | 440 | 507.9576 | -15.4449 | 71.7647 | 423.9788 | 77.3574 | 93 | 40 | 27 | 2.0968 | 4.3 | 6.3968 | 6.3968 | 0.39721 | 0.32779 | 12.5806 | 12.5806 | 4.1046 | 35.3954 | 0.35543 | 6.1 | 5.8 | 110 | 440 | 640 | 600.9152 | 6.107 | 67.6471 | 520.4576 | 78.8648
[11 empty] | 1990-10-02 |  | 4798.4 | 24 | 145 | 40 | 53 | 0 | 6.6 | 4.3 |  | 10.9 | 10.9 | 0.6055 | 0 | 13.2 | 13.2 | 4.56 | 34.94 | 0.37779 | 7.4 | 6.2 | 82 | 220 | 340 | 640 | 736 | -15 | 75.8824 | 538 | 84.7584 | 145 | 92 | 79 | 4.471 | 6.429 | 10.9 | 10.9 | 0.32174 | 0.41018 | 13.4129 | 13.4129 | 3.2884 | 36.2116 | 0.3704 | 6.2 | 6.1 | 96 | 340 | 440 | 509.6859 | -15.8377 | 71.7647 | 424.843 | 77.4034 | 92 | 40 | 27 | 2.129 | 4.3 | 6.429 | 6.429 | 0.39841 | 0.33116 | 12.7742 | 12.7742 | 4.117 | 34.883 | 0.3662 | 6.1 | 5.8 | 110 | 440 | 640 | 603.3908 | 5.7202 | 67.6471 | 521.6954 | 78.9149
[11 empty] | 1990-10-03 |  | 4822.2 | 24 | 145 | 40 | 53.5 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 4.69 | 34.31 | 0.38473 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 752 | -4.4444 | 76.5714 | 551 | 85.118 | 145 | 93 | 80 | 4.471 | 6.529 | 11 | 11 | 0.32546 | 0.40645 | 13.4129 | 13.4129 | 4.0003 | 34.9997 | 0.38323 | 5.8 | 5.7 | 52 | 350 | 510 | 554.0652 | -8.6402 | 85.1429 | 452.0326 | 88.4964 | 93 | 40 | 27 | 2.129 | 4.4 | 6.529 | 6.529 | 0.40583 | 0.32609 | 12.7742 | 12.7742 | 5.2906 | 34.2094 | 0.37341 | 6 | 5.7 | 84 | 510 | 720 | 716.129 | 0.53763 | 76 | 613.0645 | 86.2983
[11 empty] | 1990-10-05 |  | 4868.2 | 24 | 145 | 40 | 53.5 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 4.6595 | 34.3405 | 0.37856 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 745.9091 | -3.5985 | 76.5714 | 547.9545 | 85.0353 | 145 | 94 | 80 | 4.4032 | 6.4968 | 10.9 | 10.9 | 0.323 | 0.40397 | 13.2097 | 13.2097 | 3.9899 | 35.5101 | 0.372 | 5.8 | 5.7 | 52 | 350 | 510 | 551.9712 | -8.2296 | 85.1429 | 450.9856 | 88.4697 | 94 | 40 | 27 | 2.0968 | 4.4 | 6.4968 | 6.4968 | 0.40464 | 0.32274 | 12.5806 | 12.5806 | 5.275 | 34.725 | 0.36229 | 6 | 5.7 | 84 | 510 | 720 | 713.0059 | 0.97141 | 76 | 611.5029 | 86.2634
[11 empty] | 1990-10-08 |  | 4941.9 | 24 | 145 | 40 | 52.5 | 0 | 6.4 | 4.3 |  | 10.7 | 10.7 | 0.59813 | 0 | 12.8 | 12.8 | 4.6744 | 35.3256 | 0.36234 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 748.8837 | -4.0116 | 76.5714 | 549.4419 | 85.0758 | 145 | 93 | 79 | 4.3355 | 6.3645 | 10.7 | 10.7 | 0.31683 | 0.40519 | 13.0065 | 13.0065 | 3.995 | 36.005 | 0.36124 | 5.8 | 5.7 | 52 | 350 | 510 | 552.9965 | -8.4307 | 85.1429 | 451.4982 | 88.4828 | 93 | 40 | 26 | 2.0645 | 4.3 | 6.3645 | 6.3645 | 0.39601 | 0.32438 | 12.3871 | 12.3871 | 5.2827 | 35.2173 | 0.35173 | 6 | 5.7 | 84 | 510 | 720 | 714.5311 | 0.75956 | 76 | 612.2656 | 86.2805
[11 empty] | 1990-10-09 |  | 4964.9 | 24 | 146 | 40 | 52.5 | 0 | 6.4 | 4.3 |  | 10.7 | 10.7 | 0.59813 | 0 | 12.8 | 12.8 | 4.6744 | 35.8256 | 0.35729 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 748.8837 | -4.0116 | 76.5714 | 549.4419 | 85.0758 | 146 | 94 | 79 | 4.3355 | 6.3645 | 10.7 | 10.7 | 0.31683 | 0.40519 | 13.0065 | 13.0065 | 3.995 | 37.005 | 0.35148 | 5.8 | 5.7 | 52 | 350 | 510 | 552.9965 | -8.4307 | 85.1429 | 451.4982 | 88.4828 | 94 | 40 | 26 | 2.0645 | 4.3 | 6.3645 | 6.3645 | 0.39601 | 0.32438 | 12.3871 | 12.3871 | 5.2827 | 35.7173 | 0.34681 | 6 | 5.7 | 84 | 510 | 720 | 714.5311 | 0.75956 | 76 | 612.2656 | 86.2805
[11 empty] | 1990-10-10 |  | 4987.2 | 24 | 147 | 40 | 53.5 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 4.69 | 35.31 | 0.37383 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 752 | -4.4444 | 76.5714 | 551 | 85.118 | 147 | 93 | 80 | 4.471 | 6.529 | 11 | 11 | 0.32546 | 0.40645 | 13.4129 | 13.4129 | 4.0003 | 35.9997 | 0.37258 | 5.8 | 5.7 | 52 | 350 | 510 | 554.0652 | -8.6402 | 85.1429 | 452.0326 | 88.4964 | 93 | 40 | 27 | 2.129 | 4.4 | 6.529 | 6.529 | 0.40583 | 0.32609 | 12.7742 | 12.7742 | 5.2906 | 34.2094 | 0.37341 | 6 | 5.7 | 84 | 510 | 720 | 716.129 | 0.53763 | 76 | 613.0645 | 86.2983
[11 empty] | 1990-10-12 |  | 5035.3 | 24 | 146 | 40 | 53.5 | 0 | 6.5 | 4.3 |  | 10.8 | 10.8 | 0.60185 | 0 | 13 | 13 | 4.7056 | 34.7944 | 0.37362 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 755.1163 | -4.8773 | 76.5714 | 552.5581 | 85.1599 | 146 | 94 | 80 | 4.4032 | 6.3968 | 10.8 | 10.8 | 0.31929 | 0.40771 | 13.2097 | 13.2097 | 4.0056 | 35.9944 | 0.36699 | 5.8 | 5.7 | 52 | 350 | 510 | 555.1286 | -8.8487 | 85.1429 | 452.5643 | 88.5099 | 94 | 40 | 27 | 2.0968 | 4.3 | 6.3968 | 6.3968 | 0.39721 | 0.32779 | 12.5806 | 12.5806 | 5.2986 | 34.7014 | 0.36254 | 6 | 5.7 | 84 | 510 | 720 | 717.7269 | 0.3157 | 76 | 613.8635 | 86.3162
[11 empty] | 1990-10-15 |  | 5106.5 | 24 | 145 | 40 | 52.5 | 0 | 6.5 | 4.4 |  | 10.9 | 10.9 | 0.59633 | 0 | 13 | 13 | 4.6595 | 35.3405 | 0.36785 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 745.9091 | -3.5985 | 76.5714 | 547.9545 | 85.0353 | 145 | 94 | 79 | 4.4032 | 6.4968 | 10.9 | 10.9 | 0.323 | 0.40397 | 13.2097 | 13.2097 | 3.9899 | 36.5101 | 0.36181 | 5.8 | 5.7 | 52 | 350 | 510 | 551.9712 | -8.2296 | 85.1429 | 450.9856 | 88.4697 | 94 | 40 | 26 | 2.0968 | 4.4 | 6.4968 | 6.4968 | 0.40464 | 0.32274 | 12.5806 | 12.5806 | 5.275 | 35.725 | 0.35215 | 6 | 5.7 | 84 | 510 | 720 | 713.0059 | 0.97141 | 76 | 611.5029 | 86.2634
[11 empty] | 1990-10-16 |  | 5128.4 | 24 | 145 | 45 | 55.5 | 0 | 6.77 | 4.31 |  | 11.08 | 11.08 | 0.61101 | 0 | 13.54 | 13.54 | 4.7848 | 34.7152 | 0.39003 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 770.9652 | -7.0785 | 76.5714 | 560.4826 | 85.3698 | 145 | 95 | 81 | 4.5133 | 6.5667 | 11.08 | 11.08 | 0.32764 | 0.40734 | 13.54 | 13.54 | 4.0041 | 34.9959 | 0.3869 | 5.8 | 5.7 | 52 | 350 | 510 | 554.8183 | -8.7879 | 85.1429 | 452.4091 | 88.506 | 95 | 45 | 30 | 2.2567 | 4.31 | 6.5667 | 6.5667 | 0.40389 | 0.34365 | 13.54 | 13.54 | 5.3752 | 34.6248 | 0.39105 | 6 | 5.7 | 84 | 510 | 720 | 733.0487 | -1.8123 | 76 | 621.5244 | 86.4848
[11 empty] | 1990-10-17 |  | 5152.4 | 24 | 143 | 45 | 54 | 0 | 6.6 | 4.4 |  | 11 | 11 | 0.6 | 0 | 13.2 | 13.2 | 4.69 | 35.31 | 0.37383 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 752 | -4.4444 | 76.5714 | 551 | 85.118 | 143 | 94 | 80 | 4.4344 | 6.5656 | 11 | 11 | 0.32614 | 0.40313 | 13.3031 | 13.3031 | 3.9863 | 34.5137 | 0.38545 | 5.8 | 5.7 | 52 | 350 | 510 | 551.267 | -8.0916 | 85.1429 | 450.6335 | 88.4607 | 94 | 45 | 28 | 2.1656 | 4.4 | 6.5656 | 6.5656 | 0.40719 | 0.32984 | 12.9938 | 12.9938 | 5.3084 | 36.1916 | 0.35903 | 6 | 5.7 | 84 | 510 | 720 | 719.6719 | 0.045573 | 76 | 614.8359 | 86.3378
[11 empty] | 1990-10-18 |  | 5176.6 | 24 | 144 | 45 | 54 | 0 | 6.6 | 4.3 |  | 10.9 | 10.9 | 0.6055 | 0 | 13.2 | 13.2 | 4.7367 | 35.7633 | 0.36909 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 761.3488 | -5.7429 | 76.5714 | 555.6744 | 85.2432 | 144 | 94 | 80 | 4.4 | 6.5 | 10.9 | 10.9 | 0.32306 | 0.40367 | 13.2 | 13.2 | 3.9886 | 35.0114 | 0.37702 | 5.8 | 5.7 | 52 | 350 | 510 | 551.7231 | -8.181 | 85.1429 | 450.8615 | 88.4665 | 94 | 45 | 28 | 2.2 | 4.3 | 6.5 | 6.5 | 0.40104 | 0.33846 | 13.2 | 13.2 | 5.3498 | 36.1502 | 0.36514 | 6 | 5.7 | 84 | 510 | 720 | 727.9535 | -1.1047 | 76 | 618.9767 | 86.4292
[11 empty] | 1990-10-19 |  | 5198.4 | 24 | 144 | 45 | 54 | 0 | 6.6 | 4.2 |  | 10.8 | 10.8 | 0.61111 | 0 | 13.2 | 13.2 | 4.7857 | 35.7143 | 0.3696 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 771.1429 | -7.1032 | 76.5714 | 560.5714 | 85.3721 | 144 | 95 | 80 | 4.3312 | 6.4688 | 10.8 | 10.8 | 0.32062 | 0.40104 | 12.9938 | 12.9938 | 3.9777 | 35.5223 | 0.36579 | 5.8 | 5.7 | 52 | 350 | 510 | 549.5304 | -7.7511 | 85.1429 | 449.7652 | 88.4384 | 95 | 45 | 28 | 2.2687 | 4.2 | 6.4688 | 6.4688 | 0.39617 | 0.35072 | 13.6125 | 13.6125 | 5.4106 | 36.5894 | 0.37203 | 6 | 5.7 | 84 | 510 | 720 | 740.1161 | -2.7939 | 76 | 625.058 | 86.5612
[11 empty] | 1990-10-23 |  | 5295.9 | 24 | 141 | 45 | 54 | 0 | 6.5 | 4.3 |  | 10.8 | 10.8 | 0.60185 | 0 | 13 | 13 | 4.7056 | 34.2944 | 0.37907 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 755.1163 | -4.8773 | 76.5714 | 552.5581 | 85.1599 | 141 | 94 | 80 | 4.4032 | 6.3968 | 10.8 | 10.8 | 0.31929 | 0.40771 | 13.2097 | 13.2097 | 4.0056 | 33.4944 | 0.39439 | 5.8 | 5.7 | 52 | 350 | 510 | 555.1286 | -8.8487 | 85.1429 | 452.5643 | 88.5099 | 94 | 45 | 28 | 2.0968 | 4.3 | 6.3968 | 6.3968 | 0.39721 | 0.32779 | 12.5806 | 12.5806 | 5.2986 | 36.2014 | 0.34752 | 6 | 5.7 | 84 | 510 | 720 | 717.7269 | 0.3157 | 76 | 613.8635 | 86.3162
[11 empty] | 1990-10-24 |  | 5318.7 | 24 | 142 | 45 | 53.5 | 0 | 6.5 | 4.2 |  | 10.7 | 10.7 | 0.60748 | 0 | 13 | 13 | 4.7538 | 35.2462 | 0.36883 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 764.7619 | -6.2169 | 76.5714 | 557.381 | 85.2883 | 142 | 94 | 80 | 4.4032 | 6.2968 | 10.7 | 10.7 | 0.31557 | 0.41152 | 13.2097 | 13.2097 | 4.0219 | 33.9781 | 0.38877 | 5.8 | 5.7 | 52 | 350 | 510 | 558.3863 | -9.4875 | 85.1429 | 454.1931 | 88.5511 | 94 | 45 | 27 | 2.0968 | 4.2 | 6.2968 | 6.2968 | 0.38978 | 0.33299 | 12.5806 | 12.5806 | 5.3234 | 37.1766 | 0.3384 | 6 | 5.7 | 84 | 510 | 720 | 722.6728 | -0.37122 | 76 | 616.3364 | 86.3711
[11 empty] | 1990-10-25 |  | 5342 | 24 | 142 | 46 | 55.5 | 0 | 6.5 | 4.2 | X | 10.7 | 10.7 | 0.60748 | 0 | 13 | 13 | 4.7538 | 33.7462 | 0.38523 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 764.7619 | -6.2169 | 76.5714 | 557.381 | 85.2883 | 142 | 95 | 81 | 4.3333 | 6.3667 | 10.7 | 10.7 | 0.31687 | 0.40498 | 13 | 13 | 3.9941 | 33.5059 | 0.38799 | 5.8 | 5.7 | 52 | 350 | 510 | 552.8272 | -8.3975 | 85.1429 | 451.4136 | 88.4806 | 95 | 46 | 30 | 2.1667 | 4.2 | 6.3667 | 6.3667 | 0.39238 | 0.34031 | 13 | 13 | 5.3588 | 35.1412 | 0.36994 | 6 | 5.7 | 84 | 510 | 720 | 729.7619 | -1.3558 | 76 | 619.881 | 86.449
[11 empty] | 1990-10-25 |  | 5342.2 | 24 | 139 | 49 | 56.5 | 0 | 7.01 | 4.4 |  | 11.41 | 11.41 | 0.61437 | 0 | 14.02 | 14.02 | 4.8149 | 32.6851 | 0.42894 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 776.9727 | -7.9129 | 76.5714 | 563.4864 | 85.4477 | 139 | 87 | 79 | 4.4609 | 6.9491 | 11.41 | 11.41 | 0.34087 | 0.39096 | 13.3827 | 13.3827 | 3.9365 | 30.0635 | 0.44515 | 5.8 | 5.7 | 52 | 350 | 510 | 541.2985 | -6.137 | 85.1429 | 445.6493 | 88.3316 | 87 | 49 | 34 | 2.5491 | 4.4 | 6.9491 | 6.9491 | 0.42143 | 0.36682 | 15.2945 | 15.2945 | 5.494 | 28.506 | 0.53654 | 6 | 5.7 | 84 | 510 | 720 | 756.7983 | -5.1109 | 76 | 633.3992 | 86.7382
[11 empty] | 1990-10-26 |  | 5366.1 | 24 | 139 | 48 | 54.5 | 0 | 6.9 | 4.3 |  | 11.2 | 11.2 | 0.61607 | 0 | 13.8 | 13.8 | 4.8302 | 34.1698 | 0.40387 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 780.0465 | -8.3398 | 76.5714 | 565.0233 | 85.4873 | 139 | 87 | 77 | 4.3125 | 6.8875 | 11.2 | 11.2 | 0.33583 | 0.38504 | 12.9375 | 12.9375 | 3.9129 | 32.0871 | 0.4032 | 5.8 | 5.7 | 52 | 350 | 510 | 536.588 | -5.2133 | 85.1429 | 443.294 | 88.2696 | 87 | 48 | 32 | 2.5875 | 4.3 | 6.8875 | 6.8875 | 0.41543 | 0.37568 | 15.525 | 15.525 | 5.5417 | 29.9583 | 0.51822 | 6 | 5.7 | 84 | 510 | 720 | 766.343 | -6.4365 | 76 | 638.1715 | 86.8374
[11 empty] | 1990-10-29 |  | 5437.2 | 24 | 138 | 49 | 55 | 0 | 6.8 | 4.3 |  | 11.1 | 11.1 | 0.61261 | 0 | 13.6 | 13.6 | 4.7991 | 33.7009 | 0.40355 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 773.814 | -7.4742 | 76.5714 | 561.907 | 85.4068 | 138 | 86 | 78 | 4.25 | 6.85 | 11.1 | 11.1 | 0.33327 | 0.38288 | 12.75 | 12.75 | 3.9045 | 30.0955 | 0.42365 | 5.8 | 5.7 | 52 | 350 | 510 | 534.8905 | -4.8805 | 85.1429 | 442.4453 | 88.2471 | 86 | 49 | 32 | 2.55 | 4.3 | 6.85 | 6.85 | 0.41404 | 0.37226 | 15.3 | 15.3 | 5.5231 | 29.9769 | 0.51039 | 6 | 5.7 | 84 | 510 | 720 | 762.6279 | -5.9205 | 76 | 636.314 | 86.799
[11 empty] | 1990-10-30 |  | 5457.8 | 24 | 138 | 49 | 55 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.7509 | 33.7491 | 0.40297 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 764.1818 | -6.1364 | 76.5714 | 557.0909 | 85.2807 | 138 | 86 | 78 | 4.25 | 6.95 | 11.2 | 11.2 | 0.33699 | 0.37946 | 12.75 | 12.75 | 3.8912 | 30.1088 | 0.42346 | 5.8 | 5.7 | 52 | 350 | 510 | 532.2302 | -4.3589 | 85.1429 | 441.1151 | 88.2117 | 86 | 49 | 32 | 2.55 | 4.4 | 6.95 | 6.95 | 0.42147 | 0.36691 | 15.3 | 15.3 | 5.4944 | 30.0056 | 0.50991 | 6 | 5.7 | 84 | 510 | 720 | 756.8864 | -5.1231 | 76 | 633.4432 | 86.7391
[11 empty] | 1990-10-31 |  | 5481.8 | 24 | 138 | 48 | 55 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.7509 | 33.2491 | 0.40903 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 764.1818 | -6.1364 | 76.5714 | 557.0909 | 85.2807 | 138 | 86 | 78 | 4.25 | 6.95 | 11.2 | 11.2 | 0.33699 | 0.37946 | 12.75 | 12.75 | 3.8912 | 30.1088 | 0.42346 | 5.8 | 5.7 | 52 | 350 | 510 | 532.2302 | -4.3589 | 85.1429 | 441.1151 | 88.2117 | 86 | 48 | 32 | 2.55 | 4.4 | 6.95 | 6.95 | 0.42147 | 0.36691 | 15.3 | 15.3 | 5.4944 | 29.5056 | 0.51855 | 6 | 5.7 | 84 | 510 | 720 | 756.8864 | -5.1231 | 76 | 633.4432 | 86.7391
[11 empty] | 1990-11-05 |  | 5598.6 | 24 | 140 | 55 | 57.5 | 0 | 7.2 | 4.2 |  | 11.4 | 11.4 | 0.63158 | 0 | 14.4 | 14.4 | 4.9771 | 35.0229 | 0.41116 | 7.3 | 5.8 | 82 | 250 | 350 | 720 | 809.4286 | -12.4206 | 76.5714 | 579.7143 | 85.8551 | 140 | 90 | 80 | 4.5818 | 6.8182 | 11.4 | 11.4 | 0.33825 | 0.40191 | 13.7455 | 13.7455 | 3.9813 | 31.0187 | 0.44313 | 5.8 | 5.7 | 52 | 350 | 510 | 550.256 | -7.8933 | 85.1429 | 450.128 | 88.4477 | 90 | 55 | 35 | 2.6182 | 4.2 | 6.8182 | 6.8182 | 0.40914 | 0.384 | 15.7091 | 15.7091 | 5.5878 | 31.9122 | 0.49226 | 6 | 5.7 | 84 | 510 | 720 | 775.5584 | -7.7165 | 76 | 642.7792 | 86.9317
[11 empty] | 1990-11-06 |  | 5619.9 | 24 | 141 | 56 | 57 | 0 | 7 | 4.4 |  | 11.4 | 11.4 | 0.61404 | 0 | 14 | 14 | 4.7041 | 36.7959 | 0.38048 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 736.8182 | -8.3556 | 81.875 | 528.4091 | 89.0237 | 141 | 90 | 80 | 4.4545 | 6.9455 | 11.4 | 11.4 | 0.34062 | 0.39075 | 13.3636 | 13.3636 | 3.6979 | 31.8021 | 0.42021 | 6.2 | 6.1 | 40 | 320 | 550 | 499.5812 | 9.1671 | 87.5 | 409.7906 | 90.2389 | 90 | 56 | 34 | 2.5455 | 4.4 | 6.9455 | 6.9455 | 0.4213 | 0.36649 | 15.2727 | 15.2727 | 5.879 | 33.121 | 0.46112 | 6.1 | 6.4 | 94 | 550 | 680 | 813.8017 | -19.6767 | 70.625 | 681.9008 | 86.215
[11 empty] | 1990-11-07 |  | 5644.7 | 24 | 140 | 55 | 57 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.6445 | 35.8555 | 0.3793 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 724.9091 | -6.6043 | 81.875 | 522.4545 | 88.8986 | 140 | 90 | 80 | 4.3273 | 6.8727 | 11.2 | 11.2 | 0.33555 | 0.38636 | 12.9818 | 12.9818 | 3.6815 | 31.3185 | 0.41451 | 6.2 | 6.1 | 40 | 320 | 550 | 496.2963 | 9.7643 | 87.5 | 408.1481 | 90.1996 | 90 | 55 | 34 | 2.4727 | 4.4 | 6.8727 | 6.8727 | 0.4186 | 0.35979 | 14.8364 | 14.8364 | 5.8413 | 32.6587 | 0.45429 | 6.1 | 6.4 | 94 | 550 | 680 | 806.2645 | -18.5683 | 70.625 | 678.1322 | 86.1384
[11 empty] | 1990-11-08 |  | 5666.7 | 24 | 138 | 50 | 54 | 0 | 6.7 | 4.3 |  | 11 | 11 | 0.60909 | 0 | 13.4 | 13.4 | 4.6612 | 35.3388 | 0.37919 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 728.2326 | -7.093 | 81.875 | 524.1163 | 88.9338 | 138 | 86 | 78 | 4.2636 | 6.7364 | 11 | 11 | 0.32931 | 0.3876 | 12.7909 | 12.7909 | 3.6861 | 30.3139 | 0.42195 | 6.2 | 6.1 | 40 | 320 | 550 | 497.22 | 9.5964 | 87.5 | 408.61 | 90.2107 | 86 | 50 | 30 | 2.4364 | 4.3 | 6.7364 | 6.7364 | 0.40982 | 0.36167 | 14.6182 | 14.6182 | 5.8518 | 32.1482 | 0.45471 | 6.1 | 6.4 | 94 | 550 | 680 | 808.3679 | -18.8776 | 70.625 | 679.1839 | 86.1599
[11 empty] | 1990-11-09 |  | 5692.9 | 24 | 138 | 51 | 55 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.5996 | 34.9004 | 0.38968 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 715.9111 | -5.281 | 81.875 | 517.9556 | 88.8021 | 138 | 87 | 78 | 4.3273 | 6.9727 | 11.3 | 11.3 | 0.33927 | 0.38294 | 12.9818 | 12.9818 | 3.6688 | 30.8312 | 0.42106 | 6.2 | 6.1 | 40 | 320 | 550 | 493.7679 | 10.224 | 87.5 | 406.884 | 90.1692 | 87 | 51 | 32 | 2.4727 | 4.5 | 6.9727 | 6.9727 | 0.42602 | 0.35463 | 14.8364 | 14.8364 | 5.8128 | 31.1872 | 0.47572 | 6.1 | 6.4 | 94 | 550 | 680 | 800.5697 | -17.7308 | 70.625 | 675.2848 | 86.0799
[11 empty] | 1990-11-14 |  | 5808.7 | 24 | 148 | 54 | 56.5 | 0 | 6.8 | 4.5 |  | 11.3 | 11.3 | 0.60177 | 0 | 13.6 | 13.6 | 4.5996 | 39.9004 | 0.34085 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 715.9111 | -5.281 | 81.875 | 517.9556 | 88.8021 | 148 | 92 | 80 | 4.3273 | 6.9727 | 11.3 | 11.3 | 0.33927 | 0.38294 | 12.9818 | 12.9818 | 3.6688 | 36.3312 | 0.35732 | 6.2 | 6.1 | 40 | 320 | 550 | 493.7679 | 10.224 | 87.5 | 406.884 | 90.1692 | 92 | 54 | 33 | 2.4727 | 4.5 | 6.9727 | 6.9727 | 0.42602 | 0.35463 | 14.8364 | 14.8364 | 5.8128 | 34.1872 | 0.43397 | 6.1 | 6.4 | 94 | 550 | 680 | 800.5697 | -17.7308 | 70.625 | 675.2848 | 86.0799
[11 empty] | 1990-11-15 |  | 5830.9 | 24 | 149 | 56 | 62 | 0 | 6.82 | 4.65 |  | 11.47 | 11.47 | 0.59459 | 0 | 13.64 | 13.64 | 4.5413 | 35.9587 | 0.37932 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 704.2667 | -3.5686 | 81.875 | 512.1333 | 88.6748 | 149 | 94 | 82 | 4.5467 | 6.9233 | 11.47 | 11.47 | 0.3415 | 0.3964 | 13.64 | 13.64 | 3.7194 | 35.7806 | 0.38121 | 6.2 | 6.1 | 40 | 320 | 550 | 503.8806 | 8.3853 | 87.5 | 411.9403 | 90.2899 | 94 | 56 | 42 | 2.2733 | 4.65 | 6.9233 | 6.9233 | 0.42976 | 0.32836 | 13.64 | 13.64 | 5.6747 | 27.3253 | 0.49917 | 6.1 | 6.4 | 94 | 550 | 680 | 772.9333 | -13.6667 | 70.625 | 661.4667 | 85.7892
[11 empty] | 1990-11-16 |  | 5856 | 24 | 148 | 54 | 57 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.642 | 39.358 | 0.36079 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 724.3913 | -6.5281 | 81.875 | 522.1957 | 88.8931 | 148 | 92 | 77 | 4.5877 | 7.1123 | 11.7 | 11.7 | 0.34928 | 0.39211 | 13.7631 | 13.7631 | 3.703 | 39.297 | 0.35023 | 6.2 | 6.1 | 40 | 320 | 550 | 500.61 | 8.98 | 87.5 | 410.305 | 90.2512 | 92 | 54 | 37 | 2.5123 | 4.6 | 7.1123 | 7.1123 | 0.43492 | 0.35323 | 15.0738 | 15.0738 | 5.8052 | 30.1948 | 0.49922 | 6.1 | 6.4 | 94 | 550 | 680 | 799.0462 | -17.5068 | 70.625 | 674.5231 | 86.0642
[11 empty] | 1990-11-19 |  | 5928.3 | 24 | 147 | 54 | 57.5 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.642 | 38.358 | 0.3702 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 724.3913 | -6.5281 | 81.875 | 522.1957 | 88.8931 | 147 | 90 | 78 | 4.5877 | 7.1123 | 11.7 | 11.7 | 0.34928 | 0.39211 | 13.7631 | 13.7631 | 3.703 | 36.797 | 0.37403 | 6.2 | 6.1 | 40 | 320 | 550 | 500.61 | 8.98 | 87.5 | 410.305 | 90.2512 | 90 | 54 | 37 | 2.5123 | 4.6 | 7.1123 | 7.1123 | 0.43492 | 0.35323 | 15.0738 | 15.0738 | 5.8052 | 29.1948 | 0.51632 | 6.1 | 6.4 | 94 | 550 | 680 | 799.0462 | -17.5068 | 70.625 | 674.5231 | 86.0642
[11 empty] | 1990-11-20 |  | 5951.7 | 24 | 145 | 54 | 57 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.642 | 37.858 | 0.37509 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 724.3913 | -6.5281 | 81.875 | 522.1957 | 88.8931 | 145 | 91 | 76 | 4.7333 | 6.9667 | 11.7 | 11.7 | 0.34658 | 0.40456 | 14.2 | 14.2 | 3.7512 | 38.2488 | 0.37125 | 6.2 | 6.1 | 40 | 320 | 550 | 510.2392 | 7.2292 | 87.5 | 415.1196 | 90.3642 | 91 | 54 | 38 | 2.3667 | 4.6 | 6.9667 | 6.9667 | 0.42951 | 0.33971 | 14.2 | 14.2 | 5.733 | 28.767 | 0.49362 | 6.1 | 6.4 | 94 | 550 | 680 | 784.6087 | -15.3836 | 70.625 | 667.3043 | 85.9135
[11 empty] | 1990-11-21 |  | 5974.5 | 24 | 144 | 54 | 58 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.642 | 36.358 | 0.39056 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 724.3913 | -6.5281 | 81.875 | 522.1957 | 88.8931 | 144 | 91 | 77 | 4.7333 | 6.9667 | 11.7 | 11.7 | 0.34658 | 0.40456 | 14.2 | 14.2 | 3.7512 | 36.7488 | 0.38641 | 6.2 | 6.1 | 40 | 320 | 550 | 510.2392 | 7.2292 | 87.5 | 415.1196 | 90.3642 | 91 | 54 | 39 | 2.3667 | 4.6 | 6.9667 | 6.9667 | 0.42951 | 0.33971 | 14.2 | 14.2 | 5.733 | 27.767 | 0.5114 | 6.1 | 6.4 | 94 | 550 | 680 | 784.6087 | -15.3836 | 70.625 | 667.3043 | 85.9135
[11 empty] | 1990-11-27 |  | 6115.6 | 24 | 144 | 54 | 57.5 | 0 | 7.1 | 4.59 |  | 11.69 | 11.69 | 0.60736 | 0 | 14.2 | 14.2 | 4.6464 | 36.8536 | 0.38531 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 725.2723 | -6.6577 | 81.875 | 522.6362 | 88.9024 | 144 | 91 | 76 | 4.7333 | 6.9567 | 11.69 | 11.69 | 0.34621 | 0.4049 | 14.2 | 14.2 | 3.7526 | 37.7474 | 0.37618 | 6.2 | 6.1 | 40 | 320 | 550 | 510.5127 | 7.1795 | 87.5 | 415.2563 | 90.3674 | 91 | 54 | 39 | 2.3667 | 4.59 | 6.9567 | 6.9567 | 0.42877 | 0.3402 | 14.2 | 14.2 | 5.7356 | 27.7644 | 0.51145 | 6.1 | 6.4 | 94 | 550 | 680 | 785.1198 | -15.4588 | 70.625 | 667.5599 | 85.9189
[11 empty] | 1990-11-28 |  | 6140.5 | 24 | 144 | 53 | 56 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.6578 | 37.8422 | 0.36996 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 727.5556 | -6.9935 | 81.875 | 523.7778 | 88.9266 | 144 | 90 | 76 | 4.6667 | 6.8333 | 11.5 | 11.5 | 0.34039 | 0.4058 | 14 | 14 | 3.7561 | 37.2439 | 0.3759 | 6.2 | 6.1 | 40 | 320 | 550 | 511.2195 | 7.051 | 87.5 | 415.6098 | 90.3756 | 90 | 53 | 36 | 2.3333 | 4.5 | 6.8333 | 6.8333 | 0.42085 | 0.34146 | 14 | 14 | 5.7422 | 29.7578 | 0.47047 | 6.1 | 6.4 | 94 | 550 | 680 | 786.4444 | -15.6536 | 70.625 | 668.2222 | 85.9328
[11 empty] | 1990-11-29 |  | 6165.4 | 24 | 144 | 53 | 57 | 0 | 7 | 4.6 |  | 11.6 | 11.6 | 0.60345 | 0 | 14 | 14 | 4.6135 | 36.8865 | 0.37954 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 718.6957 | -5.6905 | 81.875 | 519.3478 | 88.8321 | 144 | 91 | 76 | 4.6667 | 6.9333 | 11.6 | 11.6 | 0.3441 | 0.4023 | 14 | 14 | 3.7423 | 37.7577 | 0.37079 | 6.2 | 6.1 | 40 | 320 | 550 | 508.4615 | 7.5524 | 87.5 | 414.2308 | 90.3435 | 91 | 53 | 38 | 2.3333 | 4.6 | 6.9333 | 6.9333 | 0.42827 | 0.33654 | 14 | 14 | 5.7165 | 28.2835 | 0.49499 | 6.1 | 6.4 | 94 | 550 | 680 | 781.3043 | -14.8977 | 70.625 | 665.6522 | 85.8785
[11 empty] | 1990-11-30 |  | 6188 | 24 | 144 | 52 | 56 | 0 | 7.1 | 4.5 |  | 11.6 | 11.6 | 0.61207 | 0 | 14.2 | 14.2 | 4.6869 | 37.3131 | 0.38056 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 733.3778 | -7.8497 | 81.875 | 526.6889 | 88.9878 | 144 | 91 | 76 | 4.7333 | 6.8667 | 11.6 | 11.6 | 0.34287 | 0.40805 | 14.2 | 14.2 | 3.765 | 37.735 | 0.37631 | 6.2 | 6.1 | 40 | 320 | 550 | 513.0097 | 6.7255 | 87.5 | 416.5049 | 90.3963 | 91 | 52 | 36 | 2.3667 | 4.5 | 6.8667 | 6.8667 | 0.42208 | 0.34466 | 14.2 | 14.2 | 5.7591 | 29.7409 | 0.47746 | 6.1 | 6.4 | 94 | 550 | 680 | 789.8222 | -16.1503 | 70.625 | 669.9111 | 85.9683
[11 empty] | 1990-12-03 |  | 6258.9 | 24 | 144 | 53 | 56.5 | 0 | 7.4 | 4.4 |  | 11.8 | 11.8 | 0.62712 | 0 | 14.8 | 14.8 | 4.8232 | 37.1768 | 0.3981 | 7.5 | 6.2 | 58 | 240 | 320 | 680 | 760.6364 | -11.8583 | 81.875 | 540.3182 | 89.2656 | 144 | 90 | 76 | 4.8597 | 6.9403 | 11.8 | 11.8 | 0.34795 | 0.41184 | 14.5791 | 14.5791 | 3.7803 | 37.2197 | 0.3917 | 6.2 | 6.1 | 40 | 320 | 550 | 516.0602 | 6.1709 | 87.5 | 418.0301 | 90.4313 | 90 | 53 | 37 | 2.5403 | 4.4 | 6.9403 | 6.9403 | 0.4211 | 0.36602 | 15.2418 | 15.2418 | 5.8763 | 28.6237 | 0.53249 | 6.1 | 6.4 | 94 | 550 | 680 | 813.2673 | -19.5981 | 70.625 | 681.6336 | 86.2096
[11 empty] | 1990-12-05 |  | 6306.6 | 24 | 144 | 52 | 57 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.6065 | 36.3935 | 0.39018 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 721.3043 | 1.1912 | 81.25 | 520.6522 | 88.476 | 144 | 91 | 78 | 4.7333 | 6.9667 | 11.7 | 11.7 | 0.34658 | 0.40456 | 14.2 | 14.2 | 3.8048 | 35.6952 | 0.39781 | 5.9 | 6 | 36 | 320 | 500 | 512.9569 | -2.5914 | 88.75 | 416.4785 | 91.3561 | 91 | 52 | 36 | 2.3667 | 4.6 | 6.9667 | 6.9667 | 0.42951 | 0.33971 | 14.2 | 14.2 | 5.0541 | 30.4459 | 0.4664 | 6 | 6.2 | 98 | 500 | 730 | 706.8261 | 3.1745 | 69.375 | 603.413 | 83.7591
[11 empty] | 1990-12-06 |  | 6329.4 | 24 | 144 | 52 | 57 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.6065 | 36.3935 | 0.39018 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 721.3043 | 1.1912 | 81.25 | 520.6522 | 88.476 | 144 | 92 | 76 | 4.7333 | 6.9667 | 11.7 | 11.7 | 0.34658 | 0.40456 | 14.2 | 14.2 | 3.8048 | 38.1952 | 0.37177 | 5.9 | 6 | 36 | 320 | 500 | 512.9569 | -2.5914 | 88.75 | 416.4785 | 91.3561 | 92 | 52 | 38 | 2.3667 | 4.6 | 6.9667 | 6.9667 | 0.42951 | 0.33971 | 14.2 | 14.2 | 5.0541 | 28.9459 | 0.49057 | 6 | 6.2 | 98 | 500 | 730 | 706.8261 | 3.1745 | 69.375 | 603.413 | 83.7591
[11 empty] | 1990-12-07 |  | 6354 | 24 | 144 | 52 | 56.5 | 0 | 7.1 | 4.6 |  | 11.7 | 11.7 | 0.60684 | 0 | 14.2 | 14.2 | 4.6065 | 36.8935 | 0.38489 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 721.3043 | 1.1912 | 81.25 | 520.6522 | 88.476 | 144 | 91 | 76 | 4.7333 | 6.9667 | 11.7 | 11.7 | 0.34658 | 0.40456 | 14.2 | 14.2 | 3.8048 | 37.6952 | 0.37671 | 5.9 | 6 | 36 | 320 | 500 | 512.9569 | -2.5914 | 88.75 | 416.4785 | 91.3561 | 91 | 52 | 37 | 2.3667 | 4.6 | 6.9667 | 6.9667 | 0.42951 | 0.33971 | 14.2 | 14.2 | 5.0541 | 29.4459 | 0.48224 | 6 | 6.2 | 98 | 500 | 730 | 706.8261 | 3.1745 | 69.375 | 603.413 | 83.7591
[11 empty] | 1990-12-10 |  | 6425.8 | 24 | 144 | 53 | 56.5 | 0 | 7.4 | 4.5 |  | 11.9 | 11.9 | 0.62185 | 0 | 14.8 | 14.8 | 4.7378 | 37.2622 | 0.39719 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 747.5556 | -2.4049 | 81.25 | 533.7778 | 88.7594 | 144 | 91 | 77 | 4.8597 | 7.0403 | 11.9 | 11.9 | 0.35166 | 0.40838 | 14.5791 | 14.5791 | 3.8202 | 36.6798 | 0.39747 | 5.9 | 6 | 36 | 320 | 500 | 516.0365 | -3.2073 | 88.75 | 418.0182 | 91.3879 | 91 | 53 | 36 | 2.5403 | 4.5 | 7.0403 | 7.0403 | 0.42853 | 0.36082 | 15.2418 | 15.2418 | 5.1547 | 30.8453 | 0.49414 | 6 | 6.2 | 98 | 500 | 730 | 726.9333 | 0.42009 | 69.375 | 613.4667 | 84.0252
[11 empty] | 1990-12-11 |  | 6449 | 24 | 144 | 52 | 57 | 0 | 7.2 | 4.5 |  | 11.7 | 11.7 | 0.61538 | 0 | 14.4 | 14.4 | 4.68 | 36.32 | 0.39648 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 736 | -0.82192 | 81.25 | 528 | 88.6364 | 144 | 90 | 77 | 4.8 | 6.9 | 11.7 | 11.7 | 0.34534 | 0.41026 | 14.4 | 14.4 | 3.8278 | 36.1722 | 0.3981 | 5.9 | 6 | 36 | 320 | 500 | 517.5652 | -3.513 | 88.75 | 418.7826 | 91.4037 | 90 | 52 | 37 | 2.4 | 4.5 | 6.9 | 6.9 | 0.42332 | 0.34783 | 14.4 | 14.4 | 5.092 | 28.908 | 0.49813 | 6 | 6.2 | 98 | 500 | 730 | 714.4 | 2.137 | 69.375 | 607.2 | 83.8603
[11 empty] | 1990-12-12 |  | 6472.4 | 24 | 143 | 52 | 56 | 0 | 7 | 4.7 |  | 11.7 | 11.7 | 0.59829 | 0 | 14 | 14 | 4.5362 | 36.9638 | 0.37875 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 707.234 | 3.1186 | 81.25 | 513.617 | 88.3181 | 143 | 90 | 75 | 4.6667 | 7.0333 | 11.7 | 11.7 | 0.34782 | 0.39886 | 14 | 14 | 3.7822 | 37.7178 | 0.37118 | 5.9 | 6 | 36 | 320 | 500 | 508.436 | -1.6872 | 88.75 | 414.218 | 91.3089 | 90 | 52 | 37 | 2.3333 | 4.7 | 7.0333 | 7.0333 | 0.4357 | 0.33175 | 14 | 14 | 5.0179 | 28.9821 | 0.48306 | 6 | 6.2 | 98 | 500 | 730 | 699.5745 | 4.1679 | 69.375 | 599.7872 | 83.6609
[11 empty] | 1990-12-14 |  | 6493.4 | 24 | 145 | 56 | 57 | 0 | 7 | 4.5 |  | 11.5 | 11.5 | 0.6087 | 0 | 14 | 14 | 4.6222 | 38.8778 | 0.3601 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 724.4444 | 0.76104 | 81.25 | 522.2222 | 88.5106 | 145 | 94 | 76 | 4.597 | 6.903 | 11.5 | 11.5 | 0.34168 | 0.39974 | 13.791 | 13.791 | 3.7856 | 39.7144 | 0.34726 | 5.9 | 6 | 36 | 320 | 500 | 509.1286 | -1.8257 | 88.75 | 414.5643 | 91.3162 | 94 | 56 | 38 | 2.403 | 4.5 | 6.903 | 6.903 | 0.42343 | 0.34811 | 14.4179 | 14.4179 | 5.0933 | 31.9067 | 0.45188 | 6 | 6.2 | 98 | 500 | 730 | 714.6667 | 2.1005 | 69.375 | 607.3333 | 83.8639
[11 empty] | 1990-12-18 |  | 6591 | 24 | 143 | 53 | 56.5 | 0 | 6.9 | 4.4 |  | 11.3 | 11.3 | 0.61062 | 0 | 13.8 | 13.8 | 4.6386 | 36.8614 | 0.37438 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 727.7273 | 0.31133 | 81.25 | 523.8636 | 88.5466 | 143 | 89 | 76 | 4.5343 | 6.7657 | 11.3 | 11.3 | 0.33542 | 0.40126 | 13.6029 | 13.6029 | 3.7917 | 36.2083 | 0.37568 | 5.9 | 6 | 36 | 320 | 500 | 510.3328 | -2.0666 | 88.75 | 415.1664 | 91.3288 | 89 | 53 | 37 | 2.3657 | 4.4 | 6.7657 | 6.7657 | 0.41462 | 0.34966 | 14.1943 | 14.1943 | 5.1007 | 28.8993 | 0.49116 | 6 | 6.2 | 98 | 500 | 730 | 716.1403 | 1.8986 | 69.375 | 608.0701 | 83.8834
[11 empty] | 1990-12-19 |  | 6612.7 | 24 | 142 | 53 | 56 | 0 | 6.8 | 4.3 |  | 11.1 | 11.1 | 0.61261 | 0 | 13.6 | 13.6 | 4.6558 | 36.8442 | 0.36912 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 731.1628 | -0.15929 | 81.25 | 525.5814 | 88.5841 | 142 | 89 | 76 | 4.4686 | 6.6314 | 11.1 | 11.1 | 0.32921 | 0.40257 | 13.4057 | 13.4057 | 3.7969 | 35.7031 | 0.37548 | 5.9 | 6 | 36 | 320 | 500 | 511.3727 | -2.2745 | 88.75 | 415.6863 | 91.3396 | 89 | 53 | 36 | 2.3314 | 4.3 | 6.6314 | 6.6314 | 0.40592 | 0.35157 | 13.9886 | 13.9886 | 5.1098 | 29.8902 | 0.468 | 6 | 6.2 | 98 | 500 | 730 | 717.9615 | 1.6491 | 69.375 | 608.9807 | 83.9075
[11 empty] | 1990-12-20 |  | 6635.7 | 24 | 143 | 54 | 55 | 0 | 6.8 | 4.3 |  | 11.1 | 11.1 | 0.61261 | 0 | 13.6 | 13.6 | 4.6558 | 38.8442 | 0.35012 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 731.1628 | -0.15929 | 81.25 | 525.5814 | 88.5841 | 143 | 90 | 75 | 4.5333 | 6.5667 | 11.1 | 11.1 | 0.32801 | 0.40841 | 13.6 | 13.6 | 3.8203 | 37.6797 | 0.36094 | 5.9 | 6 | 36 | 320 | 500 | 516.0609 | -3.2122 | 88.75 | 418.0305 | 91.3882 | 90 | 54 | 35 | 2.2667 | 4.3 | 6.5667 | 6.5667 | 0.40352 | 0.34518 | 13.6 | 13.6 | 5.0795 | 31.9205 | 0.42606 | 6 | 6.2 | 98 | 500 | 730 | 711.907 | 2.4785 | 69.375 | 605.9535 | 83.8271
[11 empty] | 1990-12-26 |  | 6779.1 | 24 | 143 | 53 | 54.5 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.6091 | 38.8909 | 0.3497 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 721.8182 | 1.1208 | 81.25 | 520.9091 | 88.4817 | 143 | 90 | 75 | 4.5333 | 6.6667 | 11.2 | 11.2 | 0.33173 | 0.40476 | 13.6 | 13.6 | 3.8056 | 37.6944 | 0.3608 | 5.9 | 6 | 36 | 320 | 500 | 513.12 | -2.624 | 88.75 | 416.56 | 91.3578 | 90 | 53 | 34 | 2.2667 | 4.4 | 6.6667 | 6.6667 | 0.41094 | 0.34 | 13.6 | 13.6 | 5.0555 | 32.4445 | 0.41918 | 6 | 6.2 | 98 | 500 | 730 | 707.0909 | 3.1382 | 69.375 | 603.5455 | 83.7626
[11 empty] | 1990-12-28 |  | 6824.7 | 24 | 140 | 55 | 55 | 0 | 6.8 | 4.4 |  | 11.2 | 11.2 | 0.60714 | 0 | 13.6 | 13.6 | 4.6091 | 37.8909 | 0.35893 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 721.8182 | 1.1208 | 81.25 | 520.9091 | 88.4817 | 140 | 90 | 75 | 4.5333 | 6.6667 | 11.2 | 11.2 | 0.33173 | 0.40476 | 13.6 | 13.6 | 3.8056 | 36.1944 | 0.37575 | 5.9 | 6 | 36 | 320 | 500 | 513.12 | -2.624 | 88.75 | 416.56 | 91.3578 | 90 | 55 | 35 | 2.2667 | 4.4 | 6.6667 | 6.6667 | 0.41094 | 0.34 | 13.6 | 13.6 | 5.0555 | 32.4445 | 0.41918 | 6 | 6.2 | 98 | 500 | 730 | 707.0909 | 3.1382 | 69.375 | 603.5455 | 83.7626
[11 empty] | 1991-01-02 |  | 6946.2 | 24 | 143 | 53 | 54.5 | 0 | 6.9 | 4.3 |  | 11.2 | 11.2 | 0.61607 | 0 | 13.8 | 13.8 | 4.686 | 38.814 | 0.35554 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 737.2093 | -0.98758 | 81.25 | 528.6047 | 88.6494 | 143 | 90 | 75 | 4.6 | 6.6 | 11.2 | 11.2 | 0.33049 | 0.41071 | 13.8 | 13.8 | 3.8297 | 37.6703 | 0.36634 | 5.9 | 6 | 36 | 320 | 500 | 517.9394 | -3.5879 | 88.75 | 418.9697 | 91.4075 | 90 | 53 | 34 | 2.3 | 4.3 | 6.6 | 6.6 | 0.40476 | 0.34848 | 13.8 | 13.8 | 5.0951 | 32.4049 | 0.42586 | 6 | 6.2 | 98 | 500 | 730 | 715.0233 | 2.0516 | 69.375 | 607.5116 | 83.8686
[11 empty] | 1991-01-03 |  | 6966.1 | 24 | 142 | 55 | 55 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.5933 | 38.9067 | 0.35469 | 7.2 | 5.9 | 60 | 230 | 320 | 730 | 718.6667 | 1.5525 | 81.25 | 519.3333 | 88.4467 | 142 | 90 | 75 | 4.6 | 6.8 | 11.4 | 11.4 | 0.33791 | 0.40351 | 13.8 | 13.8 | 3.8006 | 37.1994 | 0.37097 | 5.9 | 6 | 36 | 320 | 500 | 512.1176 | -2.4235 | 88.75 | 416.0588 | 91.3474 | 90 | 55 | 35 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 5.0473 | 32.4527 | 0.42523 | 6 | 6.2 | 98 | 500 | 730 | 705.4667 | 3.3607 | 69.375 | 602.7333 | 83.7407
[11 empty] | 1991-01-04 |  | 6992.3 | 24 | 141 | 54 | 55 | 0 | 6.3 | 4.4 |  | 10.7 | 10.7 | 0.58879 | 0 | 12.6 | 12.6 | 4.1182 | 38.3818 | 0.32828 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 663.6364 | 9.0909 | 75 | 491.8182 | 83.7338 | 141 | 89 | 75 | 4.2 | 6.5 | 10.7 | 10.7 | 0.31935 | 0.39252 | 12.6 | 12.6 | 3.4665 | 36.5335 | 0.34489 | 6.2 | 6.4 | 58 | 320 | 490 | 489.2923 | 0.14443 | 81.875 | 404.6462 | 85.6665 | 89 | 54 | 35 | 2.1 | 4.4 | 6.5 | 6.5 | 0.40476 | 0.32308 | 12.6 | 12.6 | 4.8307 | 31.6693 | 0.39786 | 6.4 | 6.5 | 100 | 490 | 730 | 676.1364 | 7.3786 | 68.75 | 583.0682 | 82.8493
[11 empty] | 1991-01-07 |  | 7063.3 | 24 | 140 | 54 | 55.5 | 0 | 6.2 | 4.3 |  | 10.5 | 10.5 | 0.59048 | 0 | 12.4 | 12.4 | 4.1302 | 37.3698 | 0.33182 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 666.0465 | 8.7608 | 75 | 493.0233 | 83.7736 | 140 | 89 | 75 | 4.1333 | 6.3667 | 10.5 | 10.5 | 0.31316 | 0.39365 | 12.4 | 12.4 | 3.4705 | 36.0295 | 0.34416 | 6.2 | 6.4 | 58 | 320 | 490 | 490.0942 | -0.019233 | 81.875 | 405.0471 | 85.6807 | 89 | 54 | 36 | 2.0667 | 4.3 | 6.3667 | 6.3667 | 0.39609 | 0.32461 | 12.4 | 12.4 | 4.8372 | 30.6628 | 0.4044 | 6.4 | 6.5 | 100 | 490 | 730 | 677.4419 | 7.1997 | 68.75 | 583.7209 | 82.8685
[11 empty] | 1991-01-08 |  | 7084.8 | 24 | 141 | 55 | 55 | 0 | 6.2 | 4.3 |  | 10.5 | 10.5 | 0.59048 | 0 | 12.4 | 12.4 | 4.1302 | 38.8698 | 0.31901 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 666.0465 | 8.7608 | 75 | 493.0233 | 83.7736 | 141 | 90 | 75 | 4.1333 | 6.3667 | 10.5 | 10.5 | 0.31316 | 0.39365 | 12.4 | 12.4 | 3.4705 | 37.0295 | 0.33487 | 6.2 | 6.4 | 58 | 320 | 490 | 490.0942 | -0.019233 | 81.875 | 405.0471 | 85.6807 | 90 | 55 | 35 | 2.0667 | 4.3 | 6.3667 | 6.3667 | 0.39609 | 0.32461 | 12.4 | 12.4 | 4.8372 | 32.6628 | 0.37964 | 6.4 | 6.5 | 100 | 490 | 730 | 677.4419 | 7.1997 | 68.75 | 583.7209 | 82.8685
[11 empty] | 1991-01-10 |  | 7133.5 | 24 | 141 | 54 | 53.5 | 0 | 6.2 | 4.4 |  | 10.6 | 10.6 | 0.58491 | 0 | 12.4 | 12.4 | 4.0909 | 39.9091 | 0.31071 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 658.1818 | 9.8381 | 75 | 489.0909 | 83.6431 | 141 | 89 | 73 | 4.1333 | 6.4667 | 10.6 | 10.6 | 0.31687 | 0.38994 | 12.4 | 12.4 | 3.4573 | 38.5427 | 0.32172 | 6.2 | 6.4 | 58 | 320 | 490 | 487.4639 | 0.51757 | 81.875 | 403.732 | 85.634 | 89 | 54 | 34 | 2.0667 | 4.4 | 6.4667 | 6.4667 | 0.40352 | 0.31959 | 12.4 | 12.4 | 4.8159 | 32.6841 | 0.37939 | 6.4 | 6.5 | 100 | 490 | 730 | 673.1818 | 7.7833 | 68.75 | 581.5909 | 82.8058
[11 empty] | 1991-01-14 |  | 7228.3 | 24 | 141 | 55 | 54.5 | 0 | 7.2 | 4.3 |  | 11.5 | 11.5 | 0.62609 | 0 | 14.4 | 14.4 | 4.4093 | 39.0907 | 0.36837 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 721.8605 | 1.115 | 75 | 520.9302 | 84.6429 | 141 | 90 | 74 | 4.7284 | 6.7716 | 11.5 | 11.5 | 0.33924 | 0.41116 | 14.1851 | 14.1851 | 3.5347 | 37.9653 | 0.37363 | 6.2 | 6.4 | 58 | 320 | 490 | 502.9438 | -2.6416 | 81.875 | 411.4719 | 85.9043 | 90 | 55 | 35 | 2.4716 | 4.3 | 6.7716 | 6.7716 | 0.41113 | 0.365 | 14.8299 | 14.8299 | 5.0209 | 32.4791 | 0.4566 | 6.4 | 6.5 | 100 | 490 | 730 | 714.1722 | 2.1682 | 68.75 | 602.0861 | 83.3911
[11 empty] | 1991-01-15 |  | 7250.5 | 24 | 141 | 55 | 54.5 | 0 | 7 | 4.55 |  | 11.55 | 11.55 | 0.60606 | 0 | 14 | 14 | 4.2462 | 39.2538 | 0.35665 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 689.2308 | 5.5848 | 75 | 504.6154 | 84.1463 | 141 | 89 | 74 | 4.6667 | 6.8833 | 11.55 | 11.55 | 0.34225 | 0.40404 | 14 | 14 | 3.5081 | 37.4919 | 0.37341 | 6.2 | 6.4 | 58 | 320 | 490 | 497.6271 | -1.5566 | 81.875 | 408.8136 | 85.8126 | 89 | 55 | 35 | 2.3333 | 4.55 | 6.8833 | 6.8833 | 0.42456 | 0.33898 | 14 | 14 | 4.9 | 32.1 | 0.43614 | 6.4 | 6.5 | 100 | 490 | 730 | 690 | 5.4795 | 68.75 | 590 | 83.0508
[11 empty] | 1991-01-16 |  | 7276.6 | 24 | 140 | 55 | 58 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.24 | 35.26 | 0.39138 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 688 | 5.7534 | 75 | 504 | 84.127 | 140 | 91 | 76 | 4.6 | 6.8 | 11.4 | 11.4 | 0.33791 | 0.40351 | 13.8 | 13.8 | 3.5062 | 35.9938 | 0.3834 | 6.2 | 6.4 | 58 | 320 | 490 | 497.2353 | -1.4766 | 81.875 | 408.6176 | 85.8058 | 91 | 55 | 40 | 2.3 | 4.5 | 6.8 | 6.8 | 0.41961 | 0.33824 | 13.8 | 13.8 | 4.8967 | 28.1033 | 0.49104 | 6.4 | 6.5 | 100 | 490 | 730 | 689.3333 | 5.5708 | 68.75 | 589.6667 | 83.0413
[11 empty] | 1991-01-17 |  | 7300.5 | 24 | 143 | 56 | 60 | 0 | 6.9 | 4.5 |  | 11.4 | 11.4 | 0.60526 | 0 | 13.8 | 13.8 | 4.24 | 35.26 | 0.39138 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 688 | 5.7534 | 75 | 504 | 84.127 | 143 | 94 | 78 | 4.6343 | 6.7657 | 11.4 | 11.4 | 0.33728 | 0.40652 | 13.903 | 13.903 | 3.5173 | 36.9827 | 0.37593 | 6.2 | 6.4 | 58 | 320 | 490 | 499.4639 | -1.9314 | 81.875 | 409.732 | 85.8444 | 94 | 56 | 42 | 2.2657 | 4.5 | 6.7657 | 6.7657 | 0.41833 | 0.33488 | 13.594 | 13.594 | 4.8818 | 28.1182 | 0.48346 | 6.4 | 6.5 | 100 | 490 | 730 | 686.3582 | 5.9783 | 68.75 | 588.1791 | 82.9984
[11 empty] | 1991-01-22 |  | 7422 | 24 | 141 | 55 | 54.5 | 0 | 7.66 | 4.36 |  | 12.02 | 12.02 | 0.63727 | 0 | 15.32 | 15.32 | 4.5083 | 38.9917 | 0.3929 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 741.6514 | -1.5961 | 75 | 530.8257 | 84.9291 | 141 | 90 | 74 | 5.1067 | 6.9133 | 12.02 | 12.02 | 0.35153 | 0.42485 | 15.32 | 15.32 | 3.5877 | 37.9123 | 0.40409 | 6.2 | 6.4 | 58 | 320 | 490 | 513.5313 | -4.8023 | 81.875 | 416.7657 | 86.0833 | 90 | 55 | 35 | 2.5533 | 4.36 | 6.9133 | 6.9133 | 0.41862 | 0.36933 | 15.32 | 15.32 | 5.042 | 32.458 | 0.47199 | 6.4 | 6.5 | 100 | 490 | 730 | 718.3945 | 1.5898 | 68.75 | 604.1972 | 83.4491
[11 empty] | 1991-01-30 |  | 7489 | 24 | 146 | 60 | 64 | 0 | 6.9 | 4.2 |  | 11.1 | 11.1 | 0.62162 | 0 | 13.8 | 13.8 | 4.3714 | 34.6286 | 0.39851 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 714.2857 | 2.1526 | 75 | 517.1429 | 84.5304 | 146 | 97 | 82 | 4.5313 | 6.5687 | 11.1 | 11.1 | 0.32805 | 0.40823 | 13.594 | 13.594 | 3.5237 | 35.9763 | 0.37786 | 6.2 | 6.4 | 58 | 320 | 490 | 500.7389 | -2.1916 | 81.875 | 410.3695 | 85.8664 | 97 | 60 | 46 | 2.3687 | 4.2 | 6.5687 | 6.5687 | 0.39988 | 0.3606 | 14.2119 | 14.2119 | 4.9997 | 27.5003 | 0.51679 | 6.4 | 6.5 | 100 | 490 | 730 | 709.9467 | 2.747 | 68.75 | 599.9733 | 83.3326
[11 empty] | 1991-01-31 |  | 7515.7 | 24 | 144 | 60 | 55.5 | 0 | 6.9 | 4.2 |  | 11.1 | 11.1 | 0.62162 | 0 | 13.8 | 13.8 | 4.3714 | 42.1286 | 0.32757 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 714.2857 | 2.1526 | 75 | 517.1429 | 84.5304 | 144 | 93 | 75 | 4.5313 | 6.5687 | 11.1 | 11.1 | 0.32805 | 0.40823 | 13.594 | 13.594 | 3.5237 | 39.9763 | 0.34005 | 6.2 | 6.4 | 58 | 320 | 490 | 500.7389 | -2.1916 | 81.875 | 410.3695 | 85.8664 | 93 | 60 | 36 | 2.3687 | 4.2 | 6.5687 | 6.5687 | 0.39988 | 0.3606 | 14.2119 | 14.2119 | 4.9997 | 35.5003 | 0.40033 | 6.4 | 6.5 | 100 | 490 | 730 | 709.9467 | 2.747 | 68.75 | 599.9733 | 83.3326
[11 empty] | 1991-02-01 |  | 7537.6 | 24 | 143 | 58 | 56 | 0 | 7.4 | 4.2 |  | 11.6 | 11.6 | 0.63793 | 0 | 14.8 | 14.8 | 4.5143 | 39.9857 | 0.37013 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 742.8571 | -1.7613 | 75 | 531.4286 | 84.9462 | 143 | 93 | 75 | 4.8629 | 6.7371 | 11.6 | 11.6 | 0.34046 | 0.41921 | 14.5886 | 14.5886 | 3.5656 | 39.4344 | 0.36994 | 6.2 | 6.4 | 58 | 320 | 490 | 509.1111 | -3.9002 | 81.875 | 414.5556 | 86.0091 | 93 | 58 | 37 | 2.5371 | 4.2 | 6.7371 | 6.7371 | 0.40613 | 0.37659 | 15.2229 | 15.2229 | 5.078 | 33.422 | 0.45547 | 6.4 | 6.5 | 100 | 490 | 730 | 725.5918 | 0.60386 | 68.75 | 607.7959 | 83.5471
Note on T8: C. Hill (9/7/99): While these were not measured, they represent the average temperature. This utility uses ground water which typically has relatively stable temperatures.
Note on AA117: TSC_ADM: Reviewer changed cleaning notation from 2336 to 3378 hours based on Operations Description in the Summary Report
Note on AJ111: C. Hill (9/7/99): The consultant stated, "The pilot unit lost power at 3260 and 3375 hours of operation due to thunderstorms. The inorganic salts precipitated on the feed side of the membrane surface. The membranes were cleaned to dissolve the inorganic salts and the MTCw was restored to the same value as was recorded before the individual event."
Note on AJ116: C. Hill (9/7/99): The consultant stated, "The pilot unit lost power at 3260 and 3375 hours of operation due to thunderstorms. The inorganic salts precipitated on the feed side of the membrane surface. The membranes were cleaned to dissolve the inorganic salts and the MTCw was restored to the same value as was recorded before the individual event."
Note on DQ39: C. Hill (9/7/99): The consultant stated, "The permeate DCAA for sample period 6/12/90 was verified as 6 ug/L."
Note on DR33: C. Hill (9/7/99): The consultant stated, "The feed CHCl3 value was verified as 31 ug/L for the 6/12/90 sample date. This sample event produced a very low value for CHCl3 and like the 3/14/91 that measured BMRL is non-representative and considered an outlier."

## Sheet2. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Sampling Event 7 | [9 empty] | Field 2-7: System And Stage Water Quality For Sampling Event 7 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Sampling Event 8 | [9 empty] | Field 2-8: System And Stage Water Quality For Sampling Event 8 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Sampling Event 9 | [9 empty] | Field 2-9: System And Stage Water Quality For Sampling Event 9 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Sampling Event 10 | [9 empty] | Field 2-10: System And Stage Water Quality For Sampling Event 10 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Sampling Event 11 | [9 empty] | Field 2-11: System And Stage Water Quality For Sampling Event 11 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Pinellas County Utilities | Membrane manufacturer | DOW USA, (FilmTec) | Average yearly temperature of feed water, TavgoC (oC) | 24 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.63 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.41 | [6 empty] | System recovery during sample collection (decimal) | 0.61 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.4 | [6 empty] | System recovery during sample collection (decimal) | 0.65 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.43 | [6 empty] | System recovery during sample collection (decimal) | 0.65 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.43 | [6 empty] | System recovery during sample collection (decimal) | 0.63 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.42 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL6521405 | Membrane trade name | NF-70 | Temperature normalized MTCW (gfd/psi) | 0.33981 | Calcium Hardness (mg/L as CaCO3) | 190 | Cartridge filtration | 5 mm exclusion size | Pilot-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 11.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.86 | [6 empty] | System feed flow rate during sample collection (gpm) | 11.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.6 | [6 empty] | System feed flow rate during sample collection (gpm) | 11.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5 | [6 empty] | System feed flow rate during sample collection (gpm) | 12 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.2 | [6 empty] | System feed flow rate during sample collection (gpm) | 11.48 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.85 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%)
Water Industry Data Base Number (optional) |  | Membrane element model number | NF-70, 4040 |  |  | LSI | 0.02 | Sulfuric acid addition | approx. dose 110 mg/L to pH = 6.0 | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 11.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 11.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 11.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 12 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12 | [6 empty] | System influent flow rate during sample collection (gpm) | 11.48 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 11.48 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years)
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.08 | (or) Flocon 100, anti-scalent | 2 ppm | Pilot-scale | 1991-02-04 |  | 7607.5 | 24 | 144 | 60 | 56 | 0 | 7.5 | 4.1 |  | 11.6 | 11.6 | 0.64655 | 0 | 15 | 15 | 4.5951 | 41.4049 | 0.36228 | 7.3 | 6.2 | 80 | 260 | 320 | 730 | 759.0244 | -3.9759 | 75 | 539.5122 | 85.1718 | 144 | 93 | 75 | 5 | 6.6 | 11.6 | 11.6 | 0.33791 | 0.43103 | 15 | 15 | 3.6124 | 39.8876 | 0.37606 | 6.2 | 6.4 | 58 | 320 | 490 | 518.4848 | -5.8132 | 81.875 | 419.2424 | 86.1655 | 93 | 60 | 37 | 2.5 | 4.1 | 6.6 | 6.6 | 0.39733 | 0.37879 | 15 | 15 | 5.089 | 34.411 | 0.43591 | 6.4 | 6.5 | 100 | 490 | 730 | 727.8049 | 0.3007 | 68.75 | 608.9024 | 83.577 | [108 empty] | Overhead & Profit Factor (% of construction costs)
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.6 | Total iron (mg/L) | 0.08 |  |  |  | 1991-02-05 |  | 7633 | 24 | 144 | 58 | 56 | 0 | 7.4 | 4.1 |  | 11.5 | 11.5 | 0.64348 | 0 | 14.8 | 14.8 | 4.8512 | 40.1488 | 0.36863 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 770.2439 | -0.031676 | 82.2581 | 540.122 | 89.8171 | 144 | 93 | 75 | 4.8629 | 6.6371 | 11.5 | 11.5 | 0.33675 | 0.42286 | 14.5886 | 14.5886 | 3.7711 | 39.7289 | 0.3672 | 5.9 | 6 | 34 | 310 | 480 | 512.2178 | -6.712 | 89.0323 | 411.1089 | 91.7297 | 93 | 58 | 37 | 2.5371 | 4.1 | 6.6371 | 6.6371 | 0.39871 | 0.38226 | 15.2229 | 15.2229 | 5.2638 | 33.2362 | 0.45802 | 6 | 6.1 | 78 | 480 | 770 | 728.7638 | 5.3554 | 74.8387 | 604.3819 | 87.0943 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs)
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1991-02-06 |  | 7657.9 | 24 | 144 | 59 | 56 | 0 | 7.4 | 4.1 |  | 11.5 | 11.5 | 0.64348 | 0 | 14.8 | 14.8 | 4.8512 | 40.6488 | 0.36409 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 770.2439 | -0.031676 | 82.2581 | 540.122 | 89.8171 | 144 | 94 | 75 | 4.8629 | 6.6371 | 11.5 | 11.5 | 0.33675 | 0.42286 | 14.5886 | 14.5886 | 3.7711 | 40.2289 | 0.36264 | 5.9 | 6 | 34 | 310 | 480 | 512.2178 | -6.712 | 89.0323 | 411.1089 | 91.7297 | 94 | 59 | 37 | 2.5371 | 4.1 | 6.6371 | 6.6371 | 0.39871 | 0.38226 | 15.2229 | 15.2229 | 5.2638 | 34.2362 | 0.44464 | 6 | 6.1 | 78 | 480 | 770 | 728.7638 | 5.3554 | 74.8387 | 604.3819 | 87.0943 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs)
|  | Membrane hydrophobicity | Hydrophobic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | NA |  |  |  | 1991-02-07 |  | 7679.5 | 24 | 144 | 58 | 55 | 0 | 7.1 | 4.1 |  | 11.2 | 11.2 | 0.63393 | 0 | 14.2 | 14.2 | 4.7579 | 41.2421 | 0.34431 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 751.5854 | 2.3915 | 82.2581 | 530.7927 | 89.6381 | 144 | 93 | 75 | 4.6657 | 6.5343 | 11.2 | 11.2 | 0.32927 | 0.41658 | 13.9971 | 13.9971 | 3.7454 | 39.7546 | 0.35209 | 5.9 | 6 | 34 | 310 | 480 | 507.0739 | -5.6404 | 89.0323 | 408.5369 | 91.6776 | 93 | 58 | 35 | 2.4343 | 4.1 | 6.5343 | 6.5343 | 0.39489 | 0.37254 | 14.6057 | 14.6057 | 5.2134 | 35.2866 | 0.41392 | 6 | 6.1 | 78 | 480 | 770 | 718.6787 | 6.6651 | 74.8387 | 599.3394 | 86.9857 | Sampling date | MM/DD/YY | 1990-12-03 | 1990-12-03 | 1990-12-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1990-12-03 | 1990-12-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-01-03 | 1991-01-03 | 1991-01-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-01-03 | 1991-01-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-02-04 | 1991-02-04 | 1991-02-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-02-04 | 1991-02-04 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-03-14 | 1991-03-14 | 1991-03-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-03-14 | 1991-03-14 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-04-04 | 1991-04-04 | 1991-04-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1991-04-04 | 1991-04-04 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs)
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.2 |  |  |  | 1991-02-08 |  | 7703 | 24 | 144 | 58 | 56 | 0 | 7.5 | 4.1 |  | 11.6 | 11.6 | 0.64655 | 0 | 15 | 15 | 4.8823 | 40.1177 | 0.3739 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 776.4634 | -0.8394 | 82.2581 | 543.2317 | 89.8754 | 144 | 93 | 75 | 4.9286 | 6.6714 | 11.6 | 11.6 | 0.33924 | 0.42488 | 14.7857 | 14.7857 | 3.7795 | 39.7205 | 0.37224 | 5.9 | 6 | 34 | 310 | 480 | 513.8972 | -7.0619 | 89.0323 | 411.9486 | 91.7465 | 93 | 58 | 37 | 2.5714 | 4.1 | 6.6714 | 6.6714 | 0.39998 | 0.38544 | 15.4286 | 15.4286 | 5.2806 | 33.2194 | 0.46444 | 6 | 6.1 | 78 | 480 | 770 | 732.1254 | 4.9188 | 74.8387 | 606.0627 | 87.13 | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.2 |  |  |  | 1991-02-11 |  | 7774.4 | 24 | 144 | 60 | 56 | 0 | 7.5 | 4.1 |  | 11.6 | 11.6 | 0.64655 | 0 | 15 | 15 | 4.8823 | 41.1177 | 0.36481 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 776.4634 | -0.8394 | 82.2581 | 543.2317 | 89.8754 | 144 | 93 | 75 | 5 | 6.6 | 11.6 | 11.6 | 0.33791 | 0.43103 | 15 | 15 | 3.8055 | 39.6945 | 0.37789 | 5.9 | 6 | 34 | 310 | 480 | 519.0909 | -8.1439 | 89.0323 | 414.5455 | 91.7982 | 93 | 60 | 37 | 2.5 | 4.1 | 6.6 | 6.6 | 0.39733 | 0.37879 | 15 | 15 | 5.2456 | 34.2544 | 0.4379 | 6 | 6.1 | 78 | 480 | 770 | 725.122 | 5.8283 | 74.8387 | 602.561 | 87.0553 | Operation time | hh.hh | 6258.9 | 6258.9 | 6258.9 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6258.9 | 6258.9 | --- | --- | --- | --- | Operation time | hh.hh | 6966.1 | 6966.1 | 6966.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6966.1 | 6966.1 | --- | --- | --- | --- | Operation time | hh.hh | 7607.5 | 7607.5 | 7607.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 7607.5 | 7607.5 | --- | --- | --- | --- | Operation time | hh.hh | 8510.1 | 8510.1 | 8510.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 8510.1 | 8510.1 | --- | --- | --- | --- | Operation time | hh.hh | 9007.1 | 9007.1 | 9007.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 9007.1 | 9007.1 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.83333 | Sulfate (mg/L) | 1.5 |  |  |  | 1991-02-13 |  | 7822.7 | 24 | 144 | 58 | 55 | 0 | 7.4 | 4.1 |  | 11.5 | 11.5 | 0.64348 | 0 | 14.8 | 14.8 | 4.8512 | 41.1488 | 0.35967 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 770.2439 | -0.031676 | 82.2581 | 540.122 | 89.8171 | 144 | 93 | 75 | 4.9333 | 6.5667 | 11.5 | 11.5 | 0.33544 | 0.42899 | 14.8 | 14.8 | 3.7968 | 39.7032 | 0.37277 | 5.9 | 6 | 34 | 310 | 480 | 517.3503 | -7.7813 | 89.0323 | 413.6751 | 91.781 | 93 | 58 | 35 | 2.4667 | 4.1 | 6.5667 | 6.5667 | 0.39609 | 0.37563 | 14.8 | 14.8 | 5.2293 | 35.2707 | 0.41961 | 6 | 6.1 | 78 | 480 | 770 | 721.8537 | 6.2528 | 74.8387 | 600.9268 | 87.0201 | pH | --- | 5.6 | 6.2 | 6.4 | --- | --- | --- | --- | --- | pH | --- | 5.4 | 6.2 | --- | --- | --- | --- | pH | --- | 5.6 | 5.9 | 6.2 | --- | --- | --- | --- | --- | pH | --- | 5.5 | 5.9 | --- | --- | --- | --- | pH | --- | 5.8 | 6.2 | 6.5 | --- | --- | --- | --- | --- | pH | --- | 5.7 | 6.2 | --- | --- | --- | --- | pH | --- | 5.4 | 5.9 | 6.1 | --- | --- | --- | --- | --- | pH | --- | 5.4 | 5.9 | --- | --- | --- | --- | pH | --- | 5.4 | 6 | 6.1 | --- | --- | --- | --- | --- | pH | --- | 5.4 | 6 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour)
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.5 | Calcium (mg/L) | 76 |  |  |  | 1991-02-14 |  | 7866.1 | 24 | 144 | 58 | 56.5 | 0 | 7.3 | 4.1 |  | 11.4 | 11.4 | 0.64035 | 0 | 14.6 | 14.6 | 4.8201 | 39.6799 | 0.36794 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 764.0244 | 0.77605 | 82.2581 | 537.0122 | 89.7581 | 144 | 94 | 75 | 4.8667 | 6.5333 | 11.4 | 11.4 | 0.33296 | 0.4269 | 14.6 | 14.6 | 3.788 | 40.212 | 0.36308 | 5.9 | 6 | 34 | 310 | 480 | 515.5918 | -7.415 | 89.0323 | 412.7959 | 91.7635 | 94 | 58 | 38 | 2.4333 | 4.1 | 6.5333 | 6.5333 | 0.39485 | 0.37245 | 14.6 | 14.6 | 5.2129 | 32.7871 | 0.4453 | 6 | 6.1 | 78 | 480 | 770 | 718.5854 | 6.6772 | 74.8387 | 599.2927 | 86.9847 | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC | NA | 24 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor)
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5 | Barium (mg/L) | NA |  |  |  | 1991-02-15 |  | 7870.3 | 24 | 143 | 58 | 55.5 | 0 | 7.3 | 4.1 |  | 11.4 | 11.4 | 0.64035 | 0 | 14.6 | 14.6 | 4.8201 | 40.1799 | 0.36337 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 764.0244 | 0.77605 | 82.2581 | 537.0122 | 89.7581 | 143 | 93 | 75 | 4.8667 | 6.5333 | 11.4 | 11.4 | 0.33296 | 0.4269 | 14.6 | 14.6 | 3.788 | 39.212 | 0.37233 | 5.9 | 6 | 34 | 310 | 480 | 515.5918 | -7.415 | 89.0323 | 412.7959 | 91.7635 | 93 | 58 | 36 | 2.4333 | 4.1 | 6.5333 | 6.5333 | 0.39485 | 0.37245 | 14.6 | 14.6 | 5.2129 | 34.2871 | 0.42582 | 6 | 6.1 | 78 | 480 | 770 | 718.5854 | 6.6772 | 74.8387 | 599.2927 | 86.9847 | Alkalinity | mg/L as CaCO3 | 36 | 99 | 200 | 206.2703 | -3.1351 | 63.6364 | 152.6351 | 76.4143 | Alkalinity | mg/L as CaCO3 | 25 | 99 | 150.8213 | 74.7475 | 124.9107 | 79.9857 | Alkalinity | mg/L as CaCO3 | 34 | 82 | 170 | 157.0769 | 7.6018 | 58.5366 | 119.5385 | 71.5573 | Alkalinity | mg/L as CaCO3 | 27 | 82 | 119.2059 | 67.0732 | 100.6029 | 73.1618 | Alkalinity | mg/L as CaCO3 | 48 | 130 | 270 | 282.2857 | -4.5503 | 63.0769 | 206.1429 | 76.7152 | Alkalinity | mg/L as CaCO3 | 32 | 130 | 204.2424 | 75.3846 | 167.1212 | 80.8522 | Alkalinity | mg/L as CaCO3 | 29 | 76 | 160 | 163.2857 | -2.0536 | 61.8421 | 119.6429 | 75.7612 | Alkalinity | mg/L as CaCO3 | 23 | 76 | 116.5294 | 69.7368 | 96.2647 | 76.1075 | Alkalinity | mg/L as CaCO3 | 28 | 83 | 170 | 176.6486 | -3.911 | 66.2651 | 129.8243 | 78.4324 | Alkalinity | mg/L as CaCO3 | 24 | 83 | 126.1599 | 71.0843 | 104.5799 | 77.051 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h)
Mailing Address |  | Design flux, FW (gfd) | 15 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.5 | Strontium (mg/L) | NA |  |  |  | 1991-02-19 |  | 7969.9 | 24 | 143 | 57 | 56 | 0 | 7.3 | 4.1 |  | 11.4 | 11.4 | 0.64035 | 0 | 14.6 | 14.6 | 4.8201 | 39.1799 | 0.37264 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 764.0244 | 0.77605 | 82.2581 | 537.0122 | 89.7581 | 143 | 92 | 75 | 4.8667 | 6.5333 | 11.4 | 11.4 | 0.33296 | 0.4269 | 14.6 | 14.6 | 3.788 | 38.712 | 0.37714 | 5.9 | 6 | 34 | 310 | 480 | 515.5918 | -7.415 | 89.0323 | 412.7959 | 91.7635 | 92 | 57 | 37 | 2.4333 | 4.1 | 6.5333 | 6.5333 | 0.39485 | 0.37245 | 14.6 | 14.6 | 5.2129 | 32.2871 | 0.45219 | 6 | 6.1 | 78 | 480 | 770 | 718.5854 | 6.6772 | 74.8387 | 599.2927 | 86.9847 | Total dissolved solids | mg/L | 58 | 320 | 680 | 766.1081 | -12.663 | 81.875 | 543.0541 | 89.3197 | Total dissolved solids | mg/L | 40 | 320 | 516.0807 | 87.5 | 418.0403 | 90.4315 | Total dissolved solids | mg/L | 60 | 320 | 730 | 726.6667 | 0.45662 | 81.25 | 523.3333 | 88.535 | Total dissolved solids | mg/L | 36 | 320 | 512.1176 | 88.75 | 416.0588 | 91.3474 | Total dissolved solids | mg/L | 80 | 320 | 730 | 765.7143 | -4.8924 | 75 | 542.8571 | 85.2632 | Total dissolved solids | mg/L | 58 | 320 | 518.4848 | 81.875 | 419.2424 | 86.1655 | Total dissolved solids | mg/L | 55 | 310 | 770 | 783.5714 | -1.7625 | 82.2581 | 546.7857 | 89.9412 | Total dissolved solids | mg/L | 34 | 310 | 521.0588 | 89.0323 | 415.5294 | 91.8177 | Total dissolved solids | mg/L | 70 | 330 | 760 | 772.7027 | -1.6714 | 78.7879 | 551.3514 | 87.3039 | Total dissolved solids | mg/L | 50 | 330 | 534.8265 | 84.8485 | 432.4133 | 88.437 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal)
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 7.5 | Reactive silica (mg/L as SiO2) | 15 |  |  |  | 1991-02-20 |  | 7988.1 | 24 | 144 | 58 | 55 | 0 | 7.2 | 4 |  | 11.2 | 11.2 | 0.64286 | 0 | 14.4 | 14.4 | 4.845 | 41.155 | 0.3499 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 769 | 0.12987 | 82.2581 | 539.5 | 89.8054 | 144 | 94 | 75 | 4.8 | 6.4 | 11.2 | 11.2 | 0.32677 | 0.42857 | 14.4 | 14.4 | 3.795 | 40.205 | 0.35816 | 5.9 | 6 | 34 | 310 | 480 | 517 | -7.7083 | 89.0323 | 413.5 | 91.7775 | 94 | 58 | 35 | 2.4 | 4 | 6.4 | 6.4 | 0.38619 | 0.375 | 14.4 | 14.4 | 5.226 | 35.774 | 0.40253 | 6 | 6.1 | 78 | 480 | 770 | 721.2 | 6.3377 | 74.8387 | 600.6 | 87.013 | Total hardness | mg/L as CaCO3 | 38 | 220 | 470 | 529.8919 | -12.743 | 82.7273 | 374.9459 | 89.8652 | Total hardness | mg/L as CaCO3 | 26 | 220 | 355.8559 | 88.1818 | 287.928 | 90.97 | Total hardness | mg/L as CaCO3 | 53 | 230 | 520 | 506.8462 | 2.5296 | 76.9565 | 368.4231 | 85.6144 | Total hardness | mg/L as CaCO3 | 32 | 230 | 363.9412 | 86.087 | 296.9706 | 89.2245 | Total hardness | mg/L as CaCO3 | 40 | 210 | 500 | 525.7143 | -5.1429 | 80.9524 | 367.8571 | 89.1262 | Total hardness | mg/L as CaCO3 | 34 | 210 | 343.3333 | 83.8095 | 276.6667 | 87.7108 | Total hardness | mg/L as CaCO3 | 35 | 210 | 510 | 535 | -4.902 | 83.3333 | 372.5 | 90.604 | Total hardness | mg/L as CaCO3 | 26 | 210 | 350.7059 | 87.619 | 280.3529 | 90.726 | Total hardness | mg/L as CaCO3 | 37 | 210 | 500 | 504.5676 | -0.91351 | 82.381 | 357.2838 | 89.6441 | Total hardness | mg/L as CaCO3 | 27 | 210 | 343.8688 | 87.1429 | 276.9344 | 90.2504 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3)
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.35 | Feed flow rate to system, QF-sys (gpm) | 12.5 | Turbidity (ntu) | 0.2 |  |  |  | 1991-02-21 |  | 8011.3 | 24 | 145 | 58 | 55.5 | 0 | 7.3 | 4.1 |  | 11.4 | 11.4 | 0.64035 | 0 | 14.6 | 14.6 | 4.8201 | 41.1799 | 0.35454 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 764.0244 | 0.77605 | 82.2581 | 537.0122 | 89.7581 | 145 | 94 | 75 | 4.8667 | 6.5333 | 11.4 | 11.4 | 0.33296 | 0.4269 | 14.6 | 14.6 | 3.788 | 40.712 | 0.35862 | 5.9 | 6 | 34 | 310 | 480 | 515.5918 | -7.415 | 89.0323 | 412.7959 | 91.7635 | 94 | 58 | 36 | 2.4333 | 4.1 | 6.5333 | 6.5333 | 0.39485 | 0.37245 | 14.6 | 14.6 | 5.2129 | 34.7871 | 0.4197 | 6 | 6.1 | 78 | 480 | 770 | 718.5854 | 6.6772 | 74.8387 | 599.2927 | 86.9847 | Calcium hardness | mg/L as CaCO3 | 35 | 210 | 460 | 507.973 | -10.4289 | 83.3333 | 358.9865 | 90.2503 | Calcium hardness | mg/L as CaCO3 | 26 | 210 | 338.853 | 87.619 | 274.4265 | 90.5257 | Calcium hardness | mg/L as CaCO3 | 39 | 200 | 450 | 451.8205 | -0.40456 | 80.5 | 325.9103 | 88.0335 | Calcium hardness | mg/L as CaCO3 | 25 | 200 | 318.3824 | 87.5 | 259.1912 | 90.3546 | Calcium hardness | mg/L as CaCO3 | 36 | 190 | 440 | 476 | -8.1818 | 81.0526 | 333 | 89.1892 | Calcium hardness | mg/L as CaCO3 | 27 | 190 | 313.4848 | 85.7895 | 251.7424 | 89.2748 | Calcium hardness | mg/L as CaCO3 | 30 | 190 | 470 | 487.1429 | -3.6474 | 84.2105 | 338.5714 | 91.1392 | Calcium hardness | mg/L as CaCO3 | 24 | 190 | 316.9412 | 87.3684 | 253.4706 | 90.5314 | Calcium hardness | mg/L as CaCO3 | 29 | 190 | 460 | 464.1351 | -0.89894 | 84.7368 | 327.0676 | 91.1333 | Calcium hardness | mg/L as CaCO3 | 23 | 190 | 312.1644 | 87.8947 | 251.0822 | 90.8397 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal)
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 5 | SDI | 2.0 & 2.3 |  |  |  | 1991-02-22 |  | 8035.1 | 24 | 144 | 58 | 55.5 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.789 | 40.711 | 0.35371 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 757.8049 | 1.5838 | 82.2581 | 533.9024 | 89.6985 | 144 | 93 | 75 | 4.8 | 6.5 | 11.3 | 11.3 | 0.33049 | 0.42478 | 14.4 | 14.4 | 3.7791 | 39.7209 | 0.36253 | 5.9 | 6 | 34 | 310 | 480 | 513.8154 | -7.0449 | 89.0323 | 411.9077 | 91.7457 | 93 | 58 | 36 | 2.4 | 4.1 | 6.5 | 6.5 | 0.39361 | 0.36923 | 14.4 | 14.4 | 5.1966 | 34.3034 | 0.41978 | 6 | 6.1 | 78 | 480 | 770 | 715.3171 | 7.1017 | 74.8387 | 597.6585 | 86.9491 | Turbidity | ntu | 0.38 | 0.24 | 1.3 | 0.0016216 | 99.8753 | -58.3333 | 0.12081 | -214.5414 | Turbidity | ntu | 0.06 | 0.24 | 0.36605 | 75 | 0.30303 | 80.1997 | Turbidity | ntu | 0.08 | 0.12 | 0.4 | 0.18256 | 54.359 | 33.3333 | 0.15128 | 47.1186 | Turbidity | ntu | 0.08 | 0.12 | 0.14706 | 33.3333 | 0.13353 | 40.0881 | Turbidity | ntu | 0.25 | 0.22 | 0.36 | 0.16429 | 54.3651 | -13.6364 | 0.19214 | -30.1115 | Turbidity | ntu | 0.06 | 0.22 | 0.34121 | 72.7273 | 0.28061 | 78.6177 | Turbidity | ntu | BMRL | 4.3 | 7.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 4.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.14 | 3.4 | 0.22 | 8.9508 | -3968.5504 | 95.8824 | 6.1754 | 97.7329 | Turbidity | ntu | 1.3 | 3.4 | 4.9362 | 61.7647 | 4.1681 | 68.8107 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs)
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI |  |  |  |  | 1991-03-01 |  | 8201.5 | 24 | 143 | 57 | 54.5 | 0 | 7.1 | 4.1 |  | 11.2 | 11.2 | 0.63393 | 0 | 14.2 | 14.2 | 4.7579 | 40.7421 | 0.34853 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 751.5854 | 2.3915 | 82.2581 | 530.7927 | 89.6381 | 143 | 92 | 74 | 4.6657 | 6.5343 | 11.2 | 11.2 | 0.32927 | 0.41658 | 13.9971 | 13.9971 | 3.7454 | 39.7546 | 0.35209 | 5.9 | 6 | 34 | 310 | 480 | 507.0739 | -5.6404 | 89.0323 | 408.5369 | 91.6776 | 92 | 57 | 35 | 2.4343 | 4.1 | 6.5343 | 6.5343 | 0.39489 | 0.37254 | 14.6057 | 14.6057 | 5.2134 | 34.2866 | 0.42599 | 6 | 6.1 | 78 | 480 | 770 | 718.6787 | 6.6651 | 74.8387 | 599.3394 | 86.9857 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1991-03-04 |  | 8273.9 | 24 | 144 | 58 | 55.5 | 0 | 7.3 | 4.2 |  | 11.5 | 11.5 | 0.63478 | 0 | 14.6 | 14.6 | 4.7661 | 40.7339 | 0.35842 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 753.2143 | 2.18 | 82.2581 | 531.6071 | 89.654 | 144 | 93 | 75 | 4.8667 | 6.6333 | 11.5 | 11.5 | 0.33668 | 0.42319 | 14.6 | 14.6 | 3.7725 | 39.7275 | 0.3675 | 5.9 | 6 | 34 | 310 | 480 | 512.4925 | -6.7693 | 89.0323 | 411.2462 | 91.7324 | 93 | 58 | 36 | 2.4333 | 4.2 | 6.6333 | 6.6333 | 0.40228 | 0.36683 | 14.6 | 14.6 | 5.1845 | 34.3155 | 0.42546 | 6 | 6.1 | 78 | 480 | 770 | 712.9048 | 7.415 | 74.8387 | 596.4524 | 86.9227 | Total organic carbon | mg/L | BMRL | 3 | 7.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 2.9 | 7.8 | 6.9667 | 10.6838 | 89.6552 | 4.9333 | 93.9189 | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.8 | 8.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.1 | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.8 | 7.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Keller Plant 2 | Total width of all membrane envelopes in the element, w (ft) | 12 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 9.1667 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1991-03-05 |  | 8297.2 | 24 | 144 | 58 | 55 | 0 | 7.4 | 4.2 |  | 11.6 | 11.6 | 0.63793 | 0 | 14.8 | 14.8 | 4.7964 | 41.2036 | 0.35919 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 759.2857 | 1.3915 | 82.2581 | 534.6429 | 89.7128 | 144 | 93 | 75 | 4.9333 | 6.6667 | 11.6 | 11.6 | 0.33915 | 0.42529 | 14.8 | 14.8 | 3.7812 | 39.7188 | 0.37262 | 5.9 | 6 | 34 | 310 | 480 | 514.24 | -7.1333 | 89.0323 | 412.12 | 91.75 | 93 | 58 | 35 | 2.4667 | 4.2 | 6.6667 | 6.6667 | 0.40352 | 0.37 | 14.8 | 14.8 | 5.2005 | 35.2995 | 0.41927 | 6 | 6.1 | 78 | 480 | 770 | 716.0952 | 7.0006 | 74.8387 | 598.0476 | 86.9576 | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | (11) Other/GW | Feed spacer thickness, T (ft) | 0.0025 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.8333 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1991-03-06 |  | 8320.1 | 24 | 143 | 57 | 55 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.789 | 40.211 | 0.35811 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 757.8049 | 1.5838 | 82.2581 | 533.9024 | 89.6985 | 143 | 93 | 75 | 4.8 | 6.5 | 11.3 | 11.3 | 0.33049 | 0.42478 | 14.4 | 14.4 | 3.7791 | 39.2209 | 0.36715 | 5.9 | 6 | 34 | 310 | 480 | 513.8154 | -7.0449 | 89.0323 | 411.9077 | 91.7457 | 93 | 57 | 35 | 2.4 | 4.1 | 6.5 | 6.5 | 0.39361 | 0.36923 | 14.4 | 14.4 | 5.1966 | 34.8034 | 0.41375 | 6 | 6.1 | 78 | 480 | 770 | 715.3171 | 7.1017 | 74.8387 | 597.6585 | 86.9491 | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | Cascade Aeration | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [7 empty] | 1991-03-07 |  | 8342.4 | 24 | 144 | 57 | 54.5 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.789 | 41.211 | 0.34942 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 757.8049 | 1.5838 | 82.2581 | 533.9024 | 89.6985 | 144 | 92 | 74 | 4.8 | 6.5 | 11.3 | 11.3 | 0.33049 | 0.42478 | 14.4 | 14.4 | 3.7791 | 40.2209 | 0.35802 | 5.9 | 6 | 34 | 310 | 480 | 513.8154 | -7.0449 | 89.0323 | 411.9077 | 91.7457 | 92 | 57 | 35 | 2.4 | 4.1 | 6.5 | 6.5 | 0.39361 | 0.36923 | 14.4 | 14.4 | 5.1966 | 34.3034 | 0.41978 | 6 | 6.1 | 78 | 480 | 770 | 715.3171 | 7.1017 | 74.8387 | 597.6585 | 86.9491 | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 717 | Purchase price for an equivalent 8" x 40 " element ($) | 500 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1991-03-08 |  | 8364 | 24 | 144 | 58 | 54.5 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.789 | 41.711 | 0.34523 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 757.8049 | 1.5838 | 82.2581 | 533.9024 | 89.6985 | 144 | 93 | 74 | 4.8 | 6.5 | 11.3 | 11.3 | 0.33049 | 0.42478 | 14.4 | 14.4 | 3.7791 | 40.7209 | 0.35363 | 5.9 | 6 | 34 | 310 | 480 | 513.8154 | -7.0449 | 89.0323 | 411.9077 | 91.7457 | 93 | 58 | 35 | 2.4 | 4.1 | 6.5 | 6.5 | 0.39361 | 0.36923 | 14.4 | 14.4 | 5.1966 | 35.3034 | 0.40789 | 6 | 6.1 | 78 | 480 | 770 | 715.3171 | 7.1017 | 74.8387 | 597.6585 | 86.9491 | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) |  |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -1.1667 | [5 empty] | 1991-03-11 |  | 8439.3 | 24 | 144 | 58 | 56 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.789 | 40.211 | 0.35811 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 757.8049 | 1.5838 | 82.2581 | 533.9024 | 89.6985 | 144 | 92 | 75 | 4.7314 | 6.5686 | 11.3 | 11.3 | 0.33176 | 0.41871 | 14.1943 | 14.1943 | 3.754 | 39.246 | 0.36168 | 5.9 | 6 | 34 | 310 | 480 | 508.8064 | -6.0013 | 89.0323 | 409.4032 | 91.6952 | 92 | 58 | 37 | 2.4686 | 4.1 | 6.5686 | 6.5686 | 0.39616 | 0.37582 | 14.8114 | 14.8114 | 5.2302 | 32.7698 | 0.45198 | 6 | 6.1 | 78 | 480 | 770 | 722.0404 | 6.2285 | 74.8387 | 601.0202 | 87.0221 | SDS-Free Cl2 residual | mg/L | 4 | 5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.37 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 2.2 | 1.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.34 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.7 | 2.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.38 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 2 | 2.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.38 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | 0.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.37 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 22 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -1.8333 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1991-03-13 |  | 8484.5 | 24 | 143 | 57 | 55 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.789 | 40.211 | 0.35811 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 757.8049 | 1.5838 | 82.2581 | 533.9024 | 89.6985 | 143 | 92 | 75 | 4.8 | 6.5 | 11.3 | 11.3 | 0.33049 | 0.42478 | 14.4 | 14.4 | 3.7791 | 38.7209 | 0.37189 | 5.9 | 6 | 34 | 310 | 480 | 513.8154 | -7.0449 | 89.0323 | 411.9077 | 91.7457 | 92 | 57 | 35 | 2.4 | 4.1 | 6.5 | 6.5 | 0.39361 | 0.36923 | 14.4 | 14.4 | 5.1966 | 34.3034 | 0.41978 | 6 | 6.1 | 78 | 480 | 770 | 715.3171 | 7.1017 | 74.8387 | 597.6585 | 86.9491 | SDS-Cl2 demand | mg/L | 1 | 7.5 | --- | 18.5676 | --- | 86.6667 | 13.0338 | 92.3276 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.54 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.8 | 11.3 | --- | 24.5949 | --- | 75.2212 | 17.9474 | 84.3989 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.3 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.3 | 10.1 | --- | 22.7286 | --- | 67.3267 | 16.4143 | 79.8956 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 3 | 10.2 | --- | 23.5714 | --- | 70.5882 | 16.8857 | 82.2335 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.6 | 12.2 | --- | 26.8432 | --- | 70.4918 | 19.5216 | 81.5589 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.42 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 24 | Design cross-flow velocity (fps) | 0.257 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1991-03-14 |  | 8510.1 | 24 | 143 | 57 | 55 | 0 | 7.8 | 4.2 |  | 12 | 12 | 0.65 | 0 | 15.6 | 15.6 | 4.9179 | 40.0821 | 0.3892 | 7.3 | 5.9 | 55 | 250 | 310 | 770 | 783.5714 | -1.7625 | 82.2581 | 546.7857 | 89.9412 | 143 | 92 | 75 | 5.2 | 6.8 | 12 | 12 | 0.34905 | 0.43333 | 15.6 | 15.6 | 3.8153 | 38.6847 | 0.40326 | 5.9 | 6 | 34 | 310 | 480 | 521.0588 | -8.5539 | 89.0323 | 415.5294 | 91.8177 | 92 | 57 | 35 | 2.6 | 4.2 | 6.8 | 6.8 | 0.40847 | 0.38235 | 15.6 | 15.6 | 5.2643 | 34.2357 | 0.45566 | 6 | 6.1 | 78 | 480 | 770 | 728.8571 | 5.3432 | 74.8387 | 604.4286 | 87.0952 | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.94 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.8 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.6 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.8 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 6.63 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1991-03-19 |  | 8628.6 | 24 | 143 | 58 | 55 | 0 | 7.3 | 4.2 |  | 11.5 | 11.5 | 0.63478 | 0 | 14.6 | 14.6 | 4.8595 | 40.6405 | 0.35925 | 7.3 | 6 | 70 | 260 | 330 | 760 | 781.9048 | -2.8822 | 78.7879 | 555.9524 | 87.409 | 143 | 92 | 75 | 4.8667 | 6.6333 | 11.5 | 11.5 | 0.33668 | 0.42319 | 14.6 | 14.6 | 3.8271 | 38.6729 | 0.37753 | 6 | 5.9 | 50 | 330 | 490 | 535.4271 | -9.2708 | 84.8485 | 432.7136 | 88.445 | 92 | 58 | 35 | 2.4333 | 4.2 | 6.6333 | 6.6333 | 0.40228 | 0.36683 | 14.6 | 14.6 | 5.0427 | 34.9573 | 0.41765 | 5.9 | 6.1 | 99 | 490 | 760 | 716.5317 | 5.7195 | 70 | 603.2659 | 83.5893 | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 1991-03-21 |  | 8676.9 | 24 | 142 | 58 | 54.5 | 0 | 7.68 | 4.13 |  | 11.81 | 11.81 | 0.6503 | 0 | 15.36 | 15.36 | 5.0174 | 40.4826 | 0.37942 | 7.3 | 6 | 70 | 260 | 330 | 760 | 813.4867 | -7.0377 | 78.7879 | 571.7433 | 87.7567 | 142 | 92 | 74 | 5.12 | 6.69 | 11.81 | 11.81 | 0.34348 | 0.43353 | 15.36 | 15.36 | 3.8714 | 39.1286 | 0.39255 | 6 | 5.9 | 50 | 330 | 490 | 544.29 | -11.0796 | 84.8485 | 437.145 | 88.5621 | 92 | 58 | 35 | 2.56 | 4.13 | 6.69 | 6.69 | 0.40178 | 0.38266 | 15.36 | 15.36 | 5.1218 | 34.8782 | 0.44039 | 5.9 | 6.1 | 99 | 490 | 760 | 732.3632 | 3.6364 | 70 | 611.1816 | 83.8019 | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 96 | 96 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) |  | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1991-03-22 |  | 8699.3 | 24 | 143 | 56 | 53.5 | 0 | 7.4 | 4 |  | 11.4 | 11.4 | 0.64912 | 0 | 14.8 | 14.8 | 5.005 | 40.995 | 0.36102 | 7.3 | 6 | 70 | 260 | 330 | 760 | 811 | -6.7105 | 78.7879 | 570.5 | 87.7301 | 143 | 92 | 74 | 4.9333 | 6.4667 | 11.4 | 11.4 | 0.33173 | 0.43275 | 14.8 | 14.8 | 3.868 | 39.632 | 0.37344 | 6 | 5.9 | 50 | 330 | 490 | 543.6082 | -10.9405 | 84.8485 | 436.8041 | 88.5532 | 92 | 56 | 33 | 2.4667 | 4 | 6.4667 | 6.4667 | 0.38866 | 0.38144 | 14.8 | 14.8 | 5.1156 | 35.8844 | 0.41244 | 5.9 | 6.1 | 99 | 490 | 760 | 731.1167 | 3.8004 | 70 | 610.5583 | 83.7853 | SDS-TOX | mg Cl- /L | 49 | 580 | --- | 1484.1351 | --- | 91.5517 | 1032.0676 | 95.2522 | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 28 | 350 | --- | 853.641 | --- | 92 | 601.8205 | 95.3475 | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 28 | 470 | --- | 1290.8571 | --- | 94.0426 | 880.4286 | 96.8197 | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 49 | 410 | --- | 1080.4286 | --- | 88.0488 | 745.2143 | 93.4247 | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 47 | 410 | --- | 1028.0811 | --- | 88.5366 | 719.0405 | 93.4635 | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95 % at 2000 ppm | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 19.5 | [5 empty] | 1991-03-25 |  | 8770.4 | 24 | 144 | 58 | 54 | 0 | 7.1 | 4 |  | 11.1 | 11.1 | 0.63964 | 0 | 14.2 | 14.2 | 4.9075 | 42.0925 | 0.33735 | 7.3 | 6 | 70 | 260 | 330 | 760 | 791.5 | -4.1447 | 78.7879 | 560.75 | 87.5167 | 144 | 92 | 75 | 4.7333 | 6.3667 | 11.1 | 11.1 | 0.3243 | 0.42643 | 14.2 | 14.2 | 3.8408 | 39.1592 | 0.36262 | 6 | 5.9 | 50 | 330 | 490 | 538.1675 | -9.8301 | 84.8485 | 434.0838 | 88.4815 | 92 | 58 | 33 | 2.3667 | 4 | 6.3667 | 6.3667 | 0.38495 | 0.37173 | 14.2 | 14.2 | 5.0667 | 36.9333 | 0.38448 | 5.9 | 6.1 | 99 | 490 | 760 | 721.3417 | 5.0866 | 70 | 605.6708 | 83.6545 | SDS-CHCl3 | mg/L | 11 | 82 | --- | 202.8919 | --- | 86.5854 | 142.4459 | 92.2778 | Sampling date | MM/DD/YY | 1990-12-03 | 1990-12-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 7 | 73 | --- | 176.2308 | --- | 90.411 | 124.6154 | 94.3827 | Sampling date | MM/DD/YY | 1991-01-03 | 1991-01-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4 | 66 | --- | 181.1429 | --- | 93.9394 | 123.5714 | 96.763 | Sampling date | MM/DD/YY | 1991-02-04 | 1991-02-04 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1991-03-14 | 1991-03-14 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 67 | --- | 175.973 | --- | 95.5224 | 121.4865 | 97.5306 | Sampling date | MM/DD/YY | 1991-04-04 | 1991-04-04 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | MgSO4 solution | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 8.5 | [5 empty] | 1991-03-26 |  | 8792.9 | 24 | 143 | 58 | 53.5 | 0 | 7.1 | 4.1 |  | 11.2 | 11.2 | 0.63393 | 0 | 14.2 | 14.2 | 4.8512 | 42.1488 | 0.3369 | 7.3 | 6 | 70 | 260 | 330 | 760 | 780.2439 | -2.6637 | 78.7879 | 555.122 | 87.3902 | 143 | 92 | 74 | 4.7333 | 6.4667 | 11.2 | 11.2 | 0.32801 | 0.42262 | 14.2 | 14.2 | 3.8247 | 39.6753 | 0.35791 | 6 | 5.9 | 50 | 330 | 490 | 534.9485 | -9.1732 | 84.8485 | 432.4742 | 88.4386 | 92 | 58 | 33 | 2.3667 | 4.1 | 6.4667 | 6.4667 | 0.39238 | 0.36598 | 14.2 | 14.2 | 5.0385 | 36.9615 | 0.38418 | 5.9 | 6.1 | 99 | 490 | 760 | 715.6992 | 5.8291 | 70 | 602.8496 | 83.578 | SDS-BDCM | mg/L | 6 | 17 | --- | 35.7297 | --- | 64.7059 | 26.3649 | 77.2424 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 6 | 16 | --- | 31.641 | --- | 62.5 | 23.8205 | 74.8116 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 3 | 14 | --- | 34.4286 | --- | 78.5714 | 24.2143 | 87.6106 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 3 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L | 3 | 11 | --- | 24.6216 | --- | 72.7273 | 17.8108 | 83.1563 | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | [8 empty] | 1991-03-28 |  | 8842.3 | 24 | 145 | 57 | 55.5 | 0 | 7.45 | 4.23 |  | 11.68 | 11.68 | 0.63784 | 0 | 14.9 | 14.9 | 4.8896 | 40.6104 | 0.3669 | 7.3 | 6 | 70 | 260 | 330 | 760 | 787.9196 | -3.6736 | 78.7879 | 558.9598 | 87.4767 | 145 | 93 | 75 | 4.9667 | 6.7133 | 11.68 | 11.68 | 0.3415 | 0.42523 | 14.9 | 14.9 | 3.8357 | 40.1643 | 0.37098 | 6 | 5.9 | 50 | 330 | 490 | 537.15 | -9.6224 | 84.8485 | 433.575 | 88.468 | 93 | 57 | 36 | 2.4833 | 4.23 | 6.7133 | 6.7133 | 0.40636 | 0.36991 | 14.9 | 14.9 | 5.0577 | 33.9423 | 0.43898 | 5.9 | 6.1 | 99 | 490 | 760 | 719.5469 | 5.3228 | 70 | 604.7734 | 83.6302 | SDS-DBCM | mg/L | 2 | 2 | --- | 2 | --- | 0 | 2 | 0 | Operation time | hh.hh | 6258.9 | 6258.9 | --- | --- | --- | --- | SDS-DBCM | mg/L | 3 | 2 | --- | 0.4359 | --- | -50 | 1.2179 | -146.3158 | Operation time | hh.hh | 6966.1 | 6966.1 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | 2 | --- | 2 | --- | 0 | 2 | 0 | Operation time | hh.hh | 7607.5 | 7607.5 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 8510.1 | 8510.1 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2 | 1 | --- | -0.7027 | --- | -100 | 0.14865 | -1245.4545 | Operation time | hh.hh | 9007.1 | 9007.1 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1991-04-01 |  | 8935.9 | 24 | 145 | 58 | 56.5 | 0 | 7.3 | 4.1 |  | 11.4 | 11.4 | 0.64035 | 0 | 14.6 | 14.6 | 4.9146 | 40.0854 | 0.36422 | 7.3 | 6 | 70 | 260 | 330 | 760 | 792.9268 | -4.3325 | 78.7879 | 561.4634 | 87.5326 | 145 | 93 | 76 | 4.8667 | 6.5333 | 11.4 | 11.4 | 0.33296 | 0.4269 | 14.6 | 14.6 | 3.8429 | 39.1571 | 0.37286 | 6 | 5.9 | 50 | 330 | 490 | 538.5714 | -9.9125 | 84.8485 | 434.2857 | 88.4868 | 93 | 58 | 37 | 2.4333 | 4.1 | 6.5333 | 6.5333 | 0.39485 | 0.37245 | 14.6 | 14.6 | 5.0703 | 33.4297 | 0.43674 | 5.9 | 6.1 | 99 | 490 | 760 | 722.0569 | 4.9925 | 70 | 606.0285 | 83.6641 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.1 | 5.6 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6 | 5.7 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.4 | 5.9 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6 | 5.5 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.9 | 5.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1991-04-02 |  | 8962.8 | 24 | 145 | 60 | 57.5 | 0 | 7.27 | 4.21 |  | 11.48 | 11.48 | 0.63328 | 0 | 14.54 | 14.54 | 4.8449 | 40.1551 | 0.3621 | 7.3 | 6 | 70 | 260 | 330 | 760 | 778.9786 | -2.4972 | 78.7879 | 554.4893 | 87.3758 | 145 | 94 | 75 | 4.8467 | 6.6333 | 11.48 | 11.48 | 0.33631 | 0.42218 | 14.54 | 14.54 | 3.8229 | 40.6771 | 0.35745 | 6 | 5.9 | 50 | 330 | 490 | 534.5829 | -9.0986 | 84.8485 | 432.2915 | 88.4337 | 94 | 60 | 40 | 2.4233 | 4.21 | 6.6333 | 6.6333 | 0.40265 | 0.36533 | 14.54 | 14.54 | 5.0353 | 31.9647 | 0.45488 | 5.9 | 6.1 | 99 | 490 | 760 | 715.0649 | 5.9125 | 70 | 602.5325 | 83.5694 | SDS-THM4 | mg/L | 19 | 101 | --- | 240.6216 | --- | 81.1881 | 170.8108 | 88.8766 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 18 | 91 | --- | 205.1795 | --- | 80.2198 | 148.0897 | 87.8452 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 9 | 82 | --- | 217.5714 | --- | 89.0244 | 149.7857 | 93.9914 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 7 | 1 | --- | -10.1429 | --- | -600 | -4.5714 | 253.125 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 8 | 79 | --- | 199.8919 | --- | 89.8734 | 139.4459 | 94.263 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 - 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 8.5 | [5 empty] | 1991-04-04 |  | 9007.1 | 24 | 145 | 60 | 57.5 | 0 | 7.27 | 4.21 |  | 11.48 | 11.48 | 0.63328 | 0 | 14.54 | 14.54 | 4.8449 | 40.1551 | 0.3621 | 7.3 | 6 | 70 | 260 | 330 | 760 | 778.9786 | -2.4972 | 78.7879 | 554.4893 | 87.3758 | 145 | 94 | 75 | 4.8467 | 6.6333 | 11.48 | 11.48 | 0.33631 | 0.42218 | 14.54 | 14.54 | 3.8229 | 40.6771 | 0.35745 | 6 | 5.9 | 50 | 330 | 490 | 534.5829 | -9.0986 | 84.8485 | 432.2915 | 88.4337 | 94 | 60 | 40 | 2.4233 | 4.21 | 6.6333 | 6.6333 | 0.40265 | 0.36533 | 14.54 | 14.54 | 5.0353 | 31.9647 | 0.45488 | 5.9 | 6.1 | 99 | 490 | 760 | 715.0649 | 5.9125 | 70 | 602.5325 | 83.5694 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 52 | 140 | 190.8 | 47.4747 | 165.4 | 68.5611 | SDS-MCAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 68 | 140 | 176.8 | 17.0732 | 158.4 | 57.0707 | SDS-MCAA* | mg/L | 17 | 16 | --- | 14.1429 | --- | -6.25 | 15.0714 | -12.7962 | Alkalinity | mg/L as CaCO3 | 55 | 180 | 256.2195 | 57.6923 | 218.1098 | 74.7833 | SDS-MCAA* | mg/L | 13 | 15 | --- | 18.7143 | --- | 13.3333 | 16.8571 | 22.8814 | Alkalinity | mg/L as CaCO3 | 36 | 100 | 139.619 | 52.6316 | 119.8095 | 69.9523 | SDS-MCAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 39 | 120 | 166.5606 | 53.012 | 143.2803 | 72.7806 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 3 - 9 | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1991-04-05 |  | 9030.1 | 24 | 145 | 57 | 56.5 | 0 | 7 | 4.2 |  | 11.2 | 11.2 | 0.625 | 0 | 14 | 14 | 4.7667 | 39.7333 | 0.35235 | 7.3 | 6 | 70 | 260 | 330 | 760 | 763.3333 | -0.4386 | 78.7879 | 546.6667 | 87.1951 | 145 | 94 | 75 | 4.6667 | 6.5333 | 11.2 | 11.2 | 0.32925 | 0.41667 | 14 | 14 | 3.8 | 40.7 | 0.34398 | 6 | 5.9 | 50 | 330 | 490 | 530 | -8.1633 | 84.8485 | 430 | 88.3721 | 94 | 57 | 38 | 2.3333 | 4.2 | 6.5333 | 6.5333 | 0.39857 | 0.35714 | 14 | 14 | 4.9961 | 32.5039 | 0.43072 | 5.9 | 6.1 | 99 | 490 | 760 | 707.2222 | 6.9444 | 70 | 598.6111 | 83.4617 | SDS-DCAA* | mg/L | 3 | 49 | --- | 127.3243 | --- | 93.8776 | 88.1622 | 96.5972 | Total dissolved solids | mg/L | 94 | 550 | 813.2364 | 70.625 | 681.6182 | 86.2093 | SDS-DCAA* | mg/L | 2 | 22 | --- | 53.2821 | --- | 90.9091 | 37.641 | 94.6866 | Total dissolved solids | mg/L | 98 | 500 | 705.4667 | 69.375 | 602.7333 | 83.7407 | SDS-DCAA* | mg/L | 2 | 37 | --- | 102 | --- | 94.5946 | 69.5 | 97.1223 | Total dissolved solids | mg/L | 100 | 490 | 727.8049 | 68.75 | 608.9024 | 83.577 | SDS-DCAA* | mg/L | 2 | 37 | --- | 102 | --- | 94.5946 | 69.5 | 97.1223 | Total dissolved solids | mg/L | 78 | 480 | 728.8571 | 74.8387 | 604.4286 | 87.0952 | SDS-DCAA* | mg/L | 2 | 30 | --- | 77.6757 | --- | 93.3333 | 53.8378 | 96.2851 | Total dissolved solids | mg/L | 99 | 490 | 714.7553 | 70 | 602.3777 | 83.5651 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 12.5 | [5 empty] | 1991-04-08 |  | 9099.7 | 24 | 155 | 60 | 56 | 0 | 7 | 4.3 |  | 11.3 | 11.3 | 0.61947 | 0 | 14 | 14 | 4.7163 | 46.7837 | 0.29925 | 7.3 | 6 | 70 | 260 | 330 | 760 | 753.2558 | 0.88739 | 78.7879 | 541.6279 | 87.076 | 155 | 94 | 75 | 4.6667 | 6.6333 | 11.3 | 11.3 | 0.33296 | 0.41298 | 14 | 14 | 3.7849 | 45.7151 | 0.30624 | 6 | 5.9 | 50 | 330 | 490 | 526.9849 | -7.5479 | 84.8485 | 428.4925 | 88.3312 | 94 | 60 | 37 | 2.3333 | 4.3 | 6.6333 | 6.6333 | 0.40599 | 0.35176 | 14 | 14 | 4.9709 | 35.0291 | 0.39967 | 5.9 | 6.1 | 99 | 490 | 760 | 702.1705 | 7.6091 | 70 | 596.0853 | 83.3916 | SDS-TCAA* | mg/L | 1 | 60 | --- | 160.4595 | --- | 98.3333 | 110.2297 | 99.0928 | Total hardness | mg/L as CaCO3 | 60 | 310 | 454.3182 | 72.7273 | 382.1591 | 84.2997 | SDS-TCAA* | mg/L | 1 | 26 | --- | 65.1026 | --- | 96.1538 | 45.5513 | 97.8047 | Total hardness | mg/L as CaCO3 | 72 | 360 | 507.2 | 68.6957 | 433.6 | 83.3948 | SDS-TCAA* | mg/L | 1 | 50 | --- | 141 | --- | 98 | 95.5 | 98.9529 | Total hardness | mg/L as CaCO3 | 62 | 330 | 493.4146 | 70.4762 | 411.7073 | 84.9408 | SDS-TCAA* | mg/L | 1 | 61 | --- | 172.4286 | --- | 98.3607 | 116.7143 | 99.1432 | Total hardness | mg/L as CaCO3 | 51 | 320 | 486.5238 | 75.7143 | 403.2619 | 87.3531 | SDS-TCAA* | mg/L | 1 | 36 | --- | 95.5946 | --- | 97.2222 | 65.7973 | 98.4802 | Total hardness | mg/L as CaCO3 | 56 | 330 | 487.5012 | 73.3333 | 408.7506 | 86.2997 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [5 empty] | 1991-04-09 |  | 9124.3 | 24 | 145 | 59 | 58 | 0 | 7.3 | 4.3 |  | 11.6 | 11.6 | 0.62931 | 0 | 14.6 | 14.6 | 4.807 | 39.193 | 0.37252 | 7.3 | 6 | 70 | 260 | 330 | 760 | 771.3953 | -1.4994 | 78.7879 | 550.6977 | 87.2889 | 145 | 94 | 76 | 4.8667 | 6.7333 | 11.6 | 11.6 | 0.34039 | 0.41954 | 14.6 | 14.6 | 3.8119 | 39.6881 | 0.36787 | 6 | 5.9 | 50 | 330 | 490 | 532.3762 | -8.6482 | 84.8485 | 431.1881 | 88.4041 | 94 | 59 | 40 | 2.4333 | 4.3 | 6.7333 | 6.7333 | 0.40971 | 0.36139 | 14.6 | 14.6 | 5.0163 | 31.4837 | 0.46373 | 5.9 | 6.1 | 99 | 490 | 760 | 711.2636 | 6.4127 | 70 | 600.6318 | 83.5174 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 56 | 270 | 393.5364 | 73.3333 | 331.7682 | 83.1207 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 61 | 330 | 467.4889 | 69.5 | 398.7444 | 84.702 | SDS-MBAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 52 | 280 | 419.0244 | 72.6316 | 349.5122 | 85.1221 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 46 | 290 | 441.0476 | 75.7895 | 365.5238 | 87.4153 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 46 | 300 | 446.0048 | 75.7895 | 373.0024 | 87.6676 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | not reported | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1991-04-10 |  | 9146.6 | 24 | 145 | 60 | 57 | 0 | 7.2 | 4.3 |  | 11.5 | 11.5 | 0.62609 | 0 | 14.4 | 14.4 | 4.7767 | 40.7233 | 0.35361 | 7.3 | 6 | 70 | 260 | 330 | 760 | 765.3488 | -0.70379 | 78.7879 | 547.6744 | 87.2187 | 145 | 94 | 75 | 4.8 | 6.7 | 11.5 | 11.5 | 0.33791 | 0.41739 | 14.4 | 14.4 | 3.803 | 40.697 | 0.35383 | 6 | 5.9 | 50 | 330 | 490 | 530.597 | -8.2851 | 84.8485 | 430.2985 | 88.3802 | 94 | 60 | 39 | 2.4 | 4.3 | 6.7 | 6.7 | 0.40847 | 0.35821 | 14.4 | 14.4 | 5.0012 | 32.9988 | 0.43638 | 5.9 | 6.1 | 99 | 490 | 760 | 708.2326 | 6.8115 | 70 | 599.1163 | 83.4757 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.28 | 3.7 | 5.6743 | -16.6667 | 4.6871 | 94.0262 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.08 | 0.36 | 0.50311 | 33.3333 | 0.43156 | 81.4624 | SDS-DBAA* | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.16 | 0.46 | 0.64293 | 27.2727 | 0.55146 | 70.9863 | SDS-DBAA* | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 2 | 0.32 | -0.72 | 53.4884 | -0.2 | 1100 | SDS-DBAA* | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 2.2 | 0.12 | -1.0756 | 35.2941 | -0.47781 | 560.4295 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 free chlorine | maximum system recycle flow rates. | [6 empty] | 1991-04-11 |  | 9173.4 | 24 | 144 | 59 | 58 | 0 | 6.9 | 4.2 |  | 11.1 | 11.1 | 0.62162 | 0 | 13.8 | 13.8 | 4.7357 | 38.7643 | 0.356 | 7.3 | 6 | 70 | 260 | 330 | 760 | 757.1429 | 0.37594 | 78.7879 | 543.5714 | 87.1222 | 144 | 94 | 76 | 4.6 | 6.5 | 11.1 | 11.1 | 0.32677 | 0.41441 | 13.8 | 13.8 | 3.7908 | 39.2092 | 0.35196 | 6 | 5.9 | 50 | 330 | 490 | 528.1538 | -7.7865 | 84.8485 | 429.0769 | 88.3471 | 94 | 59 | 40 | 2.3 | 4.2 | 6.5 | 6.5 | 0.39733 | 0.35385 | 13.8 | 13.8 | 4.9806 | 31.5194 | 0.43783 | 5.9 | 6.1 | 99 | 490 | 760 | 704.119 | 7.3528 | 70 | 597.0595 | 83.4187 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.4 | 4.6 | 7.0245 | 86.6667 | 5.8123 | 93.118 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.5 | 4.7 | 6.8467 | 82.7586 | 5.7733 | 91.3395 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.3 | 4.7 | 7.2292 | 89.2857 | 5.9646 | 94.9703 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1991-04-12 |  | 9195.5 | 24 | 145 | 58 | 57.5 | 0 | 7.1 | 4.2 |  | 11.3 | 11.3 | 0.62832 | 0 | 14.2 | 14.2 | 4.7976 | 39.2024 | 0.36222 | 7.3 | 6 | 70 | 260 | 330 | 760 | 769.5238 | -1.2531 | 78.7879 | 549.7619 | 87.2672 | 145 | 94 | 77 | 4.7333 | 6.5667 | 11.3 | 11.3 | 0.33173 | 0.41888 | 14.2 | 14.2 | 3.8091 | 38.6909 | 0.36701 | 6 | 5.9 | 50 | 330 | 490 | 531.8274 | -8.5362 | 84.8485 | 430.9137 | 88.3967 | 94 | 58 | 38 | 2.3667 | 4.2 | 6.5667 | 6.5667 | 0.3998 | 0.36041 | 14.2 | 14.2 | 5.0116 | 32.9884 | 0.43045 | 5.9 | 6.1 | 99 | 490 | 760 | 710.3254 | 6.5361 | 70 | 600.1627 | 83.5045 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1991-04-15 |  | 9266.3 | 24 | 145 | 58 | 57 | 0 | 7.2 | 4.1 |  | 11.3 | 11.3 | 0.63717 | 0 | 14.4 | 14.4 | 4.8829 | 39.6171 | 0.36348 | 7.3 | 6 | 70 | 260 | 330 | 760 | 786.5854 | -3.4981 | 78.7879 | 558.2927 | 87.4618 | 145 | 93 | 76 | 4.8 | 6.5 | 11.3 | 11.3 | 0.33049 | 0.42478 | 14.4 | 14.4 | 3.8338 | 39.1662 | 0.36766 | 6 | 5.9 | 50 | 330 | 490 | 536.7692 | -9.5447 | 84.8485 | 433.3846 | 88.4629 | 93 | 58 | 38 | 2.4 | 4.1 | 6.5 | 6.5 | 0.39361 | 0.36923 | 14.4 | 14.4 | 5.0544 | 32.4456 | 0.44382 | 5.9 | 6.1 | 99 | 490 | 760 | 718.878 | 5.4108 | 70 | 604.439 | 83.6212 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 12.5 | [5 empty] | 1991-04-16 |  | 9290.6 | 24 | 145 | 60 | 58 | 0 | 7.1 | 4.3 |  | 11.4 | 11.4 | 0.62281 | 0 | 14.2 | 14.2 | 4.7465 | 39.7535 | 0.3572 | 7.3 | 6 | 70 | 260 | 330 | 760 | 759.3023 | 0.091799 | 78.7879 | 544.6512 | 87.1477 | 145 | 94 | 76 | 4.7333 | 6.6667 | 11.4 | 11.4 | 0.33544 | 0.4152 | 14.2 | 14.2 | 3.794 | 39.706 | 0.35763 | 6 | 5.9 | 50 | 330 | 490 | 528.8 | -7.9184 | 84.8485 | 429.4 | 88.3558 | 94 | 60 | 40 | 2.3667 | 4.3 | 6.6667 | 6.6667 | 0.40723 | 0.355 | 14.2 | 14.2 | 4.986 | 32.014 | 0.44356 | 5.9 | 6.1 | 99 | 490 | 760 | 705.2016 | 7.2103 | 70 | 597.6008 | 83.4338 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 5 | [5 empty] | 1991-04-17 |  | 9313.8 | 24 | 144 | 60 | 57.5 | 0 | 7.1 | 4.2 |  | 11.3 | 11.3 | 0.62832 | 0 | 14.2 | 14.2 | 4.7976 | 39.7024 | 0.35766 | 7.3 | 6 | 70 | 260 | 330 | 760 | 769.5238 | -1.2531 | 78.7879 | 549.7619 | 87.2672 | 144 | 94 | 75 | 4.7333 | 6.5667 | 11.3 | 11.3 | 0.33173 | 0.41888 | 14.2 | 14.2 | 3.8091 | 40.1909 | 0.35331 | 6 | 5.9 | 50 | 330 | 490 | 531.8274 | -8.5362 | 84.8485 | 430.9137 | 88.3967 | 94 | 60 | 40 | 2.3667 | 4.2 | 6.5667 | 6.5667 | 0.3998 | 0.36041 | 14.2 | 14.2 | 5.0116 | 31.9884 | 0.44391 | 5.9 | 6.1 | 99 | 490 | 760 | 710.3254 | 6.5361 | 70 | 600.1627 | 83.5045 | SDS-HAA5 | mg/L | 4 | 109 | --- | 287.7838 | --- | 96.3303 | 198.3919 | 97.9838 | [8 empty] | SDS-HAA5 | mg/L | 3 | 51 | --- | 126.0769 | --- | 94.1176 | 88.5385 | 96.6116 | [8 empty] | SDS-HAA5 | mg/L | 21 | 105 | --- | 261 | --- | 80 | 183 | 88.5246 | [8 empty] | SDS-HAA5 | mg/L | 17 | 113 | --- | 291.2857 | --- | 84.9558 | 202.1429 | 91.5901 | [8 empty] | SDS-HAA5 | mg/L | 4 | 68 | --- | 176.973 | --- | 94.1176 | 122.4865 | 96.7343 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 7.5 | [5 empty] | 1991-04-19 |  | 9360.1 | 24 | 145 | 60 | 57 | 0 | 6.8 | 4.2 |  | 11 | 11 | 0.61818 | 0 | 13.6 | 13.6 | 4.7048 | 40.7952 | 0.33337 | 7.3 | 6 | 70 | 260 | 330 | 760 | 750.9524 | 1.1905 | 78.7879 | 540.4762 | 87.0485 | 145 | 93 | 75 | 4.5333 | 6.4667 | 11 | 11 | 0.3243 | 0.41212 | 13.6 | 13.6 | 3.7814 | 40.2186 | 0.33815 | 6 | 5.9 | 50 | 330 | 490 | 526.2887 | -7.4058 | 84.8485 | 428.1443 | 88.3217 | 93 | 60 | 39 | 2.2667 | 4.2 | 6.4667 | 6.4667 | 0.39609 | 0.35052 | 13.6 | 13.6 | 4.9651 | 32.5349 | 0.41801 | 5.9 | 6.1 | 99 | 490 | 760 | 701.0159 | 7.7611 | 70 | 595.5079 | 83.3755 | SDS-HAA6 | mg/L | 4 | 109 | --- | 287.7838 | --- | 96.3303 | 198.3919 | 97.9838 | [8 empty] | SDS-HAA6 | mg/L | 3 | 51 | --- | 126.0769 | --- | 94.1176 | 88.5385 | 96.6116 | [8 empty] | SDS-HAA6 | mg/L | 21 | 105 | --- | 261 | --- | 80 | 183 | 88.5246 | [8 empty] | SDS-HAA6 | mg/L | 17 | 113 | --- | 291.2857 | --- | 84.9558 | 202.1429 | 91.5901 | [8 empty] | SDS-HAA6 | mg/L | 4 | 68 | --- | 176.973 | --- | 94.1176 | 122.4865 | 96.7343 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 7.5 | [5 empty] | 1991-04-22 |  | 9432.3 | 24 | 145 | 60 | 57 | 0 | 7.1 | 4.1 |  | 11.2 | 11.2 | 0.63393 | 0 | 14.2 | 14.2 | 4.8512 | 40.6488 | 0.34933 | 7.3 | 6 | 70 | 260 | 330 | 760 | 780.2439 | -2.6637 | 78.7879 | 555.122 | 87.3902 | 145 | 95 | 76 | 4.7687 | 6.4313 | 11.2 | 11.2 | 0.32736 | 0.42577 | 14.306 | 14.306 | 3.8381 | 40.1619 | 0.35621 | 6 | 5.9 | 50 | 330 | 490 | 537.612 | -9.7167 | 84.8485 | 433.806 | 88.4741 | 95 | 60 | 38 | 2.3313 | 4.1 | 6.4313 | 6.4313 | 0.39107 | 0.3625 | 13.9881 | 13.9881 | 5.0217 | 34.4783 | 0.40571 | 5.9 | 6.1 | 99 | 490 | 760 | 712.3305 | 6.2723 | 70 | 601.1653 | 83.532 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.5 | [5 empty] | 1991-04-23 |  | 9457 | 24 | 144 | 60 | 56 | 0 | 7.1 | 4.2 |  | 11.3 | 11.3 | 0.62832 | 0 | 14.2 | 14.2 | 4.7976 | 41.2024 | 0.34464 | 7.3 | 6 | 70 | 260 | 330 | 760 | 769.5238 | -1.2531 | 78.7879 | 549.7619 | 87.2672 | 144 | 95 | 75 | 4.6627 | 6.6373 | 11.3 | 11.3 | 0.33304 | 0.41263 | 13.9881 | 13.9881 | 3.7835 | 40.7165 | 0.34355 | 6 | 5.9 | 50 | 330 | 490 | 526.6989 | -7.4896 | 84.8485 | 428.3494 | 88.3273 | 95 | 60 | 37 | 2.4373 | 4.2 | 6.6373 | 6.6373 | 0.40243 | 0.36721 | 14.6239 | 14.6239 | 5.0445 | 35.4555 | 0.41246 | 5.9 | 6.1 | 99 | 490 | 760 | 716.9023 | 5.6708 | 70 | 603.4511 | 83.5944 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 5 | [5 empty] | 1991-04-24 |  | 9480.5 | 24 | 145 | 62 | 57 | 0 | 7.2 | 4.2 |  | 11.4 | 11.4 | 0.63158 | 0 | 14.4 | 14.4 | 4.8286 | 41.6714 | 0.34556 | 7.3 | 6 | 70 | 260 | 330 | 760 | 775.7143 | -2.0677 | 78.7879 | 552.8571 | 87.3385 | 145 | 94 | 76 | 4.7647 | 6.6353 | 11.4 | 11.4 | 0.33486 | 0.41796 | 14.2941 | 14.2941 | 3.8053 | 39.6947 | 0.3601 | 6 | 5.9 | 50 | 330 | 490 | 531.0638 | -8.3804 | 84.8485 | 430.5319 | 88.3865 | 94 | 62 | 38 | 2.4353 | 4.2 | 6.6353 | 6.6353 | 0.40235 | 0.36702 | 14.6118 | 14.6118 | 5.0436 | 34.9564 | 0.418 | 5.9 | 6.1 | 99 | 490 | 760 | 716.7143 | 5.6955 | 70 | 603.3571 | 83.5918
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1991-04-25 |  | 9504.4 | 24 | 145 | 61 | 58 | 0 | 7.2 | 4.2 |  | 11.4 | 11.4 | 0.63158 | 0 | 14.4 | 14.4 | 4.8286 | 40.1714 | 0.35846 | 7.3 | 6 | 70 | 260 | 330 | 760 | 775.7143 | -2.0677 | 78.7879 | 552.8571 | 87.3385 | 145 | 95 | 76 | 4.8 | 6.6 | 11.4 | 11.4 | 0.3342 | 0.42105 | 14.4 | 14.4 | 3.8182 | 40.1818 | 0.35837 | 6 | 5.9 | 50 | 330 | 490 | 533.6364 | -8.9054 | 84.8485 | 431.8182 | 88.4211 | 95 | 61 | 40 | 2.4 | 4.2 | 6.6 | 6.6 | 0.40104 | 0.36364 | 14.4 | 14.4 | 5.0271 | 32.9729 | 0.43672 | 5.9 | 6.1 | 99 | 490 | 760 | 713.4286 | 6.1278 | 70 | 601.7143 | 83.547 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 5 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 7.5 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 12.5 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4), % | 35.3659 | 79.2683 |  | Qp/QT (HAA5), % | 52.381 | 78.0952 | [11 empty] | Qp/QT (THM4), % | 26.0274 | 75.3425 |  | Qp/QT (HAA5), % | -6.25 | 50 | [11 empty] | Qp/QT (THM4), % | 13.6986 | 63.0137 |  | Qp/QT (HAA5), % | 60.7143 | 92.8571 | [11 empty] | Qp/QT (THM4), % | 1183.3333 | 583.3333 |  | Qp/QT (HAA5), % | 61.4583 | 89.5833 | [11 empty] | Qp/QT (THM4), % | 9.8592 | 60.5634 |  | Qp/QT (HAA5), % | 21.875 | 64.0625 | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 58.0476 | 36.9619 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 54.5 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 37.6786 | 14.2143 | [11 empty] | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | 4.6875 | 6.375 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 63.4688 | 33.5156 | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA5b, mg/L | 71.8659 | 25.7683 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 38.5068 | 14.8356 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | 93.4932 | 52.0685 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 61.6901 | 29.2394 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.3 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TOXb, mg Cl- /L | 392.2073 | 159.0854 |  | SDS-TOXb, mg Cl- /L | 301.8571 | 165.3143 | [11 empty] | SDS-TOXb, mg Cl- /L | 266.1918 | 107.3973 |  | SDS-TOXb, mg Cl- /L | NA | 189 | [11 empty] | SDS-TOXb, mg Cl- /L | 409.4521 | 191.4795 |  | SDS-TOXb, mg Cl- /L | 201.6429 | 59.5714 | [11 empty] | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | 188.1354 | 86.6042 | [11 empty] | SDS-TOXb, mg Cl- /L | 374.2113 | 190.1549 |  | SDS-TOXb, mg Cl- /L | 330.5938 | 177.4531 | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 7 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CDb, mg/L | 5.2012 | 2.3476 |  | SDS-CDb, mg/L | 4.0952 | 2.4238 | [11 empty] | SDS-CDb, mg/L | 9.0877 | 4.8959 |  | SDS-CDb, mg/L | NA | 7.05 | [11 empty] | SDS-CDb, mg/L | 9.1685 | 5.8151 |  | SDS-CDb, mg/L | 5.9714 | 3.7857 | [11 empty] | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | 5.775 | 3.75 | [11 empty] | SDS-CDb, mg/L | 11.3521 | 6.9915 |  | SDS-CDb, mg/L | 10.3187 | 6.6906 | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 15 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | 2.2233 | 0.9411 |  | TOCb, mg/L | NA | 1.6 | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | NA | NA |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 60 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 24 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Alkb, mg/L CaCO3 | 76.7195 | 49.061 |  | Alkb, mg/L CaCO3 | 66 | 49.8 | [11 empty] | Alkb, mg/L CaCO3 | 69.5068 | 45.8356 |  | Alkb, mg/L CaCO3 | NA | 58 | [11 empty] | Alkb, mg/L CaCO3 | 118.7671 | 78.3288 |  | Alkb, mg/L CaCO3 | 80.2143 | 53.8571 | [11 empty] | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | 47.1146 | 33.8958 | [11 empty] | Alkb, mg/L CaCO3 | 77.5775 | 49.6901 |  | Alkb, mg/L CaCO3 | 70.9688 | 47.7656 | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 44.1429 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | T-Hdb, mg/L CaCO3 | 155.6341 | 75.7317 |  | T-Hdb, mg/L CaCO3 | 124.6667 | 77.8667 | [11 empty] | T-Hdb, mg/L CaCO3 | 183.9315 | 96.6438 |  | T-Hdb, mg/L CaCO3 | NA | 141.5 | [11 empty] | T-Hdb, mg/L CaCO3 | 186.7123 | 102.8767 |  | T-Hdb, mg/L CaCO3 | 106.7857 | 52.1429 | [11 empty] | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | 102.4479 | 53.2292 | [11 empty] | T-Hdb, mg/L CaCO3 | 192.9437 | 105.2254 |  | T-Hdb, mg/L CaCO3 | 172.1562 | 99.1719 | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 33.2 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Ca-Hdb, mg/L CaCO3 | 148.1098 | 71.2805 |  | Ca-Hdb, mg/L CaCO3 | 118.3333 | 73.3333 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 158.0959 | 78.6986 |  | Ca-Hdb, mg/L CaCO3 | NA | 119.5 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 168.9041 | 92.9589 |  | Ca-Hdb, mg/L CaCO3 | 96.5 | 47 | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | 91.6667 | 46.6667 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 174.1268 | 92.493 |  | Ca-Hdb, mg/L CaCO3 | 154.7812 | 86.8594 | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 137.3429 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on CX33: C. Hill (9/7/99): The consultant stated, "The CHCl3 values were verified and do decrease with time of operation. The feed and interstage CHCl3 values show a similar decreasing trend. In addition, the NPDOC results indicated a decreasing trend. One possible explanation is that more intense pumping which occurs during the winter dry period caused a slight increase in the NPDOC. The reduced demand and subsequent reduced pumping with the spring wet period reduced the NPDOC. In addition, the well field associated with the Keller Plants has approximately 57 wells that are operationally rotated and produces small variations in water quality."
Note on DR33: C. Hill (9/7/99): The consultant stated, "The CHCl3 values were verified and do decrease with time of operation. The feed and interstage CHCl3 values show a similar decreasing trend. In addition, the NPDOC results indicated a decreasing trend. One possible explanation is that more intense pumping which occurs during the winter dry period caused a slight increase in the NPDOC. The reduced demand and subsequent reduced pumping with the spring wet period reduced the NPDOC. In addition, the well field associated with the Keller Plants has approximately 57 wells that are operationally rotated and produces small variations in water quality."
Note on EK38: C. Hill (9/7/99): The consultant offered no explanation for the high MCAA permeate values reported for Week 16 and Week 18.
Note on EL33: C. Hill (9/7/99): The consultant stated, "The CHCl3 values were verified and do decrease with time of operation. The feed and interstage CHCl3 values show a similar decreasing trend. In addition, the NPDOC results indicated a decreasing trend. One possible explanation is that more intense pumping which occurs during the winter dry period caused a slight increase in the NPDOC. The reduced demand and subsequent reduced pumping with the spring wet period reduced the NPDOC. In addition, the well field associated with the Keller Plants has approximately 57 wells that are operationally rotated and produces small variations in water quality."
Note on FE38: C. Hill (9/7/99): The consultant offered no explanation for the high MCAA permeate values reported for Week 16 and Week 18.
Note on FF33: C. Hill (9/7/99): The consultant stated, "The CHCl3 values were verified and do decrease with time of operation. The feed and interstage CHCl3 values show a similar decreasing trend. In addition, the NPDOC results indicated a decreasing trend. One possible explanation is that more intense pumping which occurs during the winter dry period caused a slight increase in the NPDOC. The reduced demand and subsequent reduced pumping with the spring wet period reduced the NPDOC. In addition, the well field associated with the Keller Plants has approximately 57 wells that are operationally rotated and produces small variations in water quality."
Note on FZ33: C. Hill (9/7/99): The consultant stated, "The CHCl3 values were verified and do decrease with time of operation. The feed and interstage CHCl3 values show a similar decreasing trend. In addition, the NPDOC results indicated a decreasing trend. One possible explanation is that more intense pumping which occurs during the winter dry period caused a slight increase in the NPDOC. The reduced demand and subsequent reduced pumping with the spring wet period reduced the NPDOC. In addition, the well field associated with the Keller Plants has approximately 57 wells that are operationally rotated and produces small variations in water quality."

## Sheet3. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Pinellas County Utilities | Membrane manufacturer | DOW USA, (FilmTec) | Average yearly temperature of feed water, TavgoC (oC) | 24 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL6521405 | Membrane trade name | NF-70 | Temperature normalized MTCW (gfd/psi) | 0.33981 | Calcium Hardness (mg/L as CaCO3) | 190 | Cartridge filtration | 5 mm exclusion size | Pilot-scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%)
Water Industry Data Base Number (optional) |  | Membrane element model number | NF-70, 4040 |  |  | LSI | 0.02 | Sulfuric acid addition | approx. dose 110 mg/L to pH = 6.0 | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years)
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.08 | (or) Flocon 100, anti-scalent | 2 ppm | Pilot-scale | [11 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [118 empty] | Overhead & Profit Factor (% of construction costs)
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.6 | Total iron (mg/L) | 0.08 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs)
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 (dup) | CF-sys-30 (dup) | CC-sys-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 (dup) | CI-s1-30 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs)
|  | Membrane hydrophobicity | Hydrophobic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | NA | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs)
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.2 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.2 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.72917 | Sulfate (mg/L) | 1.5 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour)
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.1875 | Calcium (mg/L) | 76 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor)
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 70 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.375 | Barium (mg/L) | NA | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h)
Mailing Address |  | Design flux, FW (gfd) | 15 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1875 | Strontium (mg/L) | NA | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal)
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from system, Qp-sys (gpm) | 6.5625 | Reactive silica (mg/L as SiO2) | 15 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3)
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.35 | Feed flow rate to system, QF-sys (gpm) | 10.9375 | Turbidity (ntu) | 0.2 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal)
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 4.375 | SDI | 2.0 & 2.3 | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs)
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  |  | MFI | [15 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [13 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Keller Plant 2 | Total width of all membrane envelopes in the element, w (ft) | 12 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 8.0208 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [13 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | (11) Other/GW | Feed spacer thickness, T (ft) | 0.0025 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.1042 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. | [13 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | Cascade Aeration | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | [18 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 717 | Purchase price for an equivalent 8" x 40 " element ($) | 1000 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) |  |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -0.020833 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 22 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -1.1042 | 1: Only those foulants and fouling indices relevant to the water being tested need to | [15 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 24 | Design cross-flow velocity (fps) | 0.257 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. | [15 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 | meet the manufacturer's minimum flow requirement. | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [18 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) |  | Calculate the Maximum Recycle Flow Rates for Each Stage | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 95 % at 2000 ppm | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 21.0625 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | MgSO4 solution | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 9.4375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | [19 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 15 | Select the Design System Recycle Flow Rate2 | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 7 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 - 250 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 9.4375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 3 - 9 | Design system recycle flow rate, QR-sys (gpm) | 0 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 10.9375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | not reported | 2: The design system recycle flow rate must fall between the minimum and | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 free chlorine | maximum system recycle flow rates. | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [19 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 10.9375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 6.5625 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 6.5625 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1875 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 4.375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 6.5625 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
|  |  |  | System feed flow rate, QF-sys (gpm) | 10.9375 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! | [11 empty] | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Calculate the Required System Influent Pressure | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.3 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! | [11 empty] | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 7 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 15 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! | [11 empty] | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
|  |  |  | Design permeate pressure, Pp (psi) | 60 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! | [11 empty] | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 24 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 44.1429 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 33.2 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
|  |  |  | Required influent pressure to the system, PI (psi) | 137.3429 | [16 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes:
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [17 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [11 empty] | QF: 0; QI: 0; vc: 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!