## NF70. Cleaning Event
Cleaning Event
1998-12-15
Sample | Dilution | Alkalinity | Ca | TOC | TPO4 | Mn (mg/L) (by AA) | Mn (mg/L) (by DR2000) | Fe (mg/L) (by AA) | Fe (mg/L) (by DR2000) | Al (ug/L)
HCl cleaning solution | 29 gals (approx.) - Recirculated solution | --- | 4 | 21.1 | 3.455 | 1.888 | --- | 2.015 | --- | 59.44
NaOH cleaning solution | 2 gals (approx.) - First flush | --- | 0.8 | 102.8 | 0.375 | 0.174 | --- | 0.314 | --- | <7.5
Raw Feed |  | 15 | 16 | 270 | <0.4 | 0.018 | 0.007 | <0.016 | 0 | <7.5
Treated Feed |  | 18 | 22.4 | --- | --- | --- | --- | --- | --- | ---
Concentrate |  | --- | --- | 739 | 0.134 | 0.073 | 0.047 | 0.036 | 0 | <7.5

## NF70. 90% Recovery
Sampling preps for 90% Recovery Test
SDI
| pH |  |  | Alkalinity |  |  | Calcium |  |  | Phosphorus |  |  | Raw Feed |  | Treated Feed
| Raw Feed | Conc | Perm | Raw Feed | Conc | Perm | Raw Feed | Conc | Perm | Raw Feed | Conc | Perm | SDI | to | SDI | to
1998-09-01 | 6.9 | 7.61 | 6.32 | 84 | 70 | 6 | 8 | 29 | 0.25 |  |  |  | 4 | 65.5 | 2.6 | 41.8
1998-09-03 | 9.69 | 9.48 | 9.95 | 36 | 112 | 11 | 7.2 | 26 | 2.4 |  |  |  | 5 |  | 3.1 | 41.6
1998-09-08 | 8.29 | 8.16 | 8.01 | 23 | 85 | 5 | 6.4 | 30 | 2 |  |  |  | 3.4 | 30 | 2.2 | 38.8
1998-09-09 | [9 empty] | <0.04 | 0.162 | 0.042
1998-09-10 | 7.63 | 6.93 | 6.46 | 22 | 32 | 3 | 6.4 | 14 | 0.4 |  |  |  | 4.4 | 32.5 | 2.8 | 31
1998-09-15 | [12 empty] | 4.5 | 42.2 | 3.1 | 33.7
1998-09-17 | [12 empty] | 4.2 | 30.3 | 3.4 | 25

## NF70. Anions Cations
Sample Date: |  | 1998-06-09
Sample Time: |  | 900
Raw
|  | Permeate | Concentrate |  | Feed
Ca |  | 0.4 | 58 |  | 11
Mg |  | 1.46 | 12.15 |  | 5.47
Na |  | 0.834 | 16.19 |  | 4.32
K |  | 0.742 | 7.597 |  | 2.411
Sr | < | 0.005 | 0.213 |  | 0.062
sum of cations
HCO3 |  | 0.244 | 34.16 |  | 10.98
SO4 | < | 5 |  |  | 32.5 | 6/25 - missing from 6/9
Cl |  | 0.3 | 3.25 |  | 1.07
F |  | 0.05 | 0.17 |  | 0.09
Reactive Si | < | 2 | 3 | < | 2
TDS (summation) |  | 11.035 | 134.73 |  | 69.903
TDS (gravimetric) |  | 10.913 | 117.65 |  | 64.413
Alk |  | 0.2 | 28 |  | 9
total hardness |  | 7 | 195 |  | 50
Conductivity |  | 13 | 320 |  | 132

## NF70. SEBST Monitoring
City of Norfolk, VA
SDWAA Response Program
ICR SEBST
SEBST Monitoring
ICR? | PARAMETER |  | FREQUENCY | LAB | SAMPLE LOCATIONS
|  |  | D = Daily 2X/W = semi-weekly M = Monthly BW = Biweekly Q = Quarterly | D = Data Logger N = Norfolk C = Contract Lab | Raw | Settled | Treated Feed | RO Feed | Permeate | Concentrate | Recycle
* | Conductivity |  | D | D |  |  | X |  | X | X
* | Temperature |  | D | D |  |  |  | X
* | Pressure |  | D | D |  |  |  | X | X | X
* | pH |  | D | D |  |  | X |  | X | X
* | Flow |  | D | D |  |  |  |  | X | X | X
| HPC |  | 2X/W | N |  | X | X | X | X | X
| SDI |  | 2X/W | N |  |  | X
| TDS |  | 2X/W | N |  |  | X |  | X | X
* | Alkalinity |  | BW | N |  |  | X |  | X | X
| Dissolved Oxygen |  | BW | N |  |  | X |  | X | X
* | Total Hardness |  | BW | N |  |  | X |  | X | X
* | Ca Hardness |  | BW | N |  |  | X |  | X | X
* | Ammonia |  | BW | C |  |  | X |  | X | X
* | Turbidity |  | BW | N |  |  | X |  | X | X
* | TOC |  | BW | N |  |  | X |  | X | X
* | UV254 |  | BW | N |  |  | X |  | X | X
| Mn (Total, Dissolved) |  | BW | N |  |  | X |  | X | X
| Al (Total, Dissolved) |  | BW | N | T,only |  | X |  | X | X
* | Bromide |  | BW | C |  |  | X |  | X
* | Cl2 Demand |  | BW | N |  |  | X |  | X
* | SDS Setup |  | BW | C |  |  | X |  | X
* | TOX |  | BW | N |  |  | X |  | X
* | THM (4) |  | BW | C |  |  | X |  | X
* | HAA (6) |  | BW | C |  |  | X |  | X
| Barium |  | M | N |  |  | X |  | X
| Sulfate |  | M | N |  |  | X |  | X
| Reactive Silica |  | M | C |  |  | X |  | X
| BOD |  | Q | C | [5 empty] | X
| COD |  | Q | C | [5 empty] | X
| Phosphorus (Total, Elemental) |  | Q | N | [5 empty] | X
| Toxicity |  | Q | C | [5 empty] | X
| Metals: |  | Q | [6 empty] | X
|  | Arsenic (Total, Dissolved) |  | N
|  | Cadmium (Total, Dissolved) |  | N
|  | Chromium VI (Total, Dissolved) |  | C
|  | Copper (Total, Dissolved) |  | N
|  | Lead (Total, Dissolved) |  | N
|  | Mercury (Total, Dissolved) |  | C
|  | Selenium (Total, Dissolved) |  | N
|  | Silver (Total, Dissolved) |  | N
|  | Zinc (Total, Dissolved) |  | N
1 | Clean Metals |  | Q | C | [5 empty] | X
*** | Other Regulated Chemicals (listed below) |  | Q | C | [5 empty] | X
1 | Conduct will depend on results of Metals testing

## NF70. Events
Date | Time | Runtime (hrs) | Description | event plot
| 0 | 294.58 |  | 0.05 | 0
1998-05-27 | 2350 | 294.58 | System down due to pilot filter blowup. | 0.4 | 6
| 0 | 593.93 |  | 0.05 | 0
1998-06-11 | 1100 | 593.93 | NaOH Cleaning | 0.4 | 6
| 0 | 715.43 |  | 0.05 | 0
1998-06-16 | 2000 | 715.43 | System down due to loss of raw water to WTP | 0.4 | 5.5
| 0 | 836.7633 |  | 0.05 | 0
1998-06-22 | 830 | 836.7633 | Citric acid & NaOH cleaning | 0.4 | 5.5
| 0 | 926.5967 |  | 0.05 | 0
1998-06-26 | 1020 | 926.5967 | H3PO4 cleaning & NaOH cleaning; 1 um CF installed | 0.4 | 5.5
|  | 1005.1 |  | 0.05 | 0
1998-06-30 | 1820 | 1005.1 | On - replaced with new 1 um cartridge filter | 0.4 | 5.5
|  | 1025.1 |  | 0.05 | 0
1998-07-01 | 1630 | 1025.1 | On -changed cartridge filter to 0.2 um | 0.4 | 5.5 | 1027.4?
|  | 1129.1 |  | 0.05 | 0
1998-07-06 | 00:30 | 1129.1 | Off - system down due to pilot filter underdrain nozzle failure | 0.4 | 5.5
|  | 1131.4 |  | 0.05 | 0
1998-07-06 | 1830 | 1131.4 | Off - system down for membrane inspection. | 0.4 | 5.5
|  | 1154.6 |  | 0.05 | 0
1998-07-07 | 1645 | 1154.6 | On -changed cartridge filter to new 0.2 um | 0.4 | 5.5
|  | 1364.1467 |  | 0.05 | 0
1998-07-16 | 930 | 1364.1467 | Off - system down for NaOH cleaning and chloramine startup | 0.4 | 5.5
|  | 1408.47 |  | 0.05 | 0
1998-07-18 | 1730 | 1408.47 | RO Pump off for 12.5 hours due to power outage | 0.4 | 5.5
|  | 1420.97 |  | 0.05 | 0
1998-07-19 | 800 | 1420.97 | RO Pump back on | 0.4 | 5.5
|  | 1454.47 |  | 0.05 | 0
1998-07-20 | 1630 | 1454.47 | Adjusted temperature probe | 0.4 | 5.5
|  | 1520 |  | 0.05 | 0
1998-07-23 | 645 | 1520 | NH2Cl feed off for 4.5-5 hrs (awaiting biweekly sample collection) | 0.4 | 5.5
|  | 1859 |  | 0.05 | 0
1998-08-06 | 1500 | 1859 | NaOH Cleaning | 0.4 | 5.5
|  | 2087 |  | 0.05 | 0
1998-08-18 | 1630 | 2087 | NaOH Feed Begun - Also - anti-scalant feed on full throttle (approx. 22 mg/L) for approx. 17 hrs. | 0.4 | 5.5
|  | 2104 |  | 0.05 | 0
1998-08-19 | 940 | 2104 | NaOH Cleaning - NaOH Feed Begun | 0.4 | 5.5
|  | 2420 |  | 0.05 | 0
1998-09-01 | 1300 | 2420 | Concentrate conductivity transmitter replaced | 0.4 | 5.5
|  | 2812 |  | 0.05 | 0
1998-09-18 | 1030 | 2812 | Chloramine feed stopped | 0.4 | 5.5
|  | 3114 |  | 0.05 | 0
1998-10-01 | 900 | 3114 | Quarterly testing - SEBST operated at 90% recovery. | 0.4 | 5.5
|  | 3629 |  | 0.05 | 0
1998-10-24 | 2100 | 3629 | Full scale plant rapid mix lime feed begun. | 0.4 | 5.5
|  | 3739 |  | 0.05 | 0
1998-10-28 | 1100 | 3739 | Full scale plant rapid mix lime feed stopped. | 0.4 | 5.5
|  | 4098 |  | 0.05 | 0
1998-11-13 | 930 | 4098 | HCl & NaOH Cleaning | 0.4 | 5.5
|  | 4357 |  | 0.05 | 0
1998-11-13 | 1520 | 4357 | Calibrated probes - Feed & Conc. Conductivities off by approx. 15 | 0.4 | 5.5
|  | 4734 |  | 0.05 | 0
1998-12-10 | 900 | 4734 | Quarterly testing - SEBST operated at 90% recovery. | 0.4 | 5.5
|  | 4855 |  | 0.05 | 0
1999-12-15 | 1020 | 4855 | HCl and NaOH Cleaning | 0.4 | 5.5
|  | 4856 |  | 0.05 | 0
1999-12-15 | 2000 | 4856 | Reduced recovery to 50% - exceeded pilot filter capacity | 0.4 | 5.5
|  | 4872 |  | 0.05 | 0
1999-12-16 | 1230 | 4872 | Changed recovery to 60% - not significant enough difference from 75% | 0.4 | 5.5
|  | 4893 |  | 0.05 | 0
1999-12-17 | 1200 | 4893 | Changed to flux of 9 gfd | 0.4 | 5.5
|  | 5559 |  | 0.05 | 0
1999-01-14 | 1100 | 5559 | Cleaned membrane. Dropped pH to 4.0 | 0.4 | 5.5
1999-02-09 | 900 | 6148 | Terminated testing

## NF70. Run Time
|  | DIGITAL |  | ANALOG |  |  |  | DOWNTIME
DATE | TIME | RUN TIME |  | HOUR METER
1998-05-15 | 1345 | 0 | Startup | 341.1
1998-05-15 | 1530 | 1.75 | SDI
1998-05-15 | 1600 | 2.25 | Data | 343.35
1998-05-16 | 1400 | 25.25 | Data | 366.35
1998-05-16 | 1500 | 26.25 | Off | 367.35
1998-05-16 | 1930 | 26.25 | On | 367.35 |  |  |  | 4.5
1998-05-17 | 1600 | 46.75 | Data
1998-05-18 | 1540 | 70.42 | SDI
1998-05-18 | 1600 | 70.75 | Data
1998-05-19 | 1311 | 91.9167 | SDI
1998-05-19 | 1600 | 94.75 | Data
1998-05-20 | 1250 | 115.9167 | SDI
1998-05-20 | 1600 | 118.75 | Data
1998-05-21 | 1600 | 142.75 | Data
1998-05-22 | 0900 | 159.75 | SDI
1998-05-22 | 1600 | 166.75 | Data
1998-05-23 | 1600 | 190.75 | Data
1998-05-24 | 1600 | 214.75 | Data
1998-05-25 | 1600 | 238.75 | Data
1998-05-26 | 1035 | 257.3333 | SDI
1998-05-26 | 1600 | 262.75 | Data
1998-05-27 | 830 | 279.25 | Samples | (est.) |  |  | 279.25
1998-05-27 | 1600 | 286.75 | Data
1998-05-27 | 2350 | 294.58 | Off | 635.68
1998-05-29 | 1030 | 294.58 | On | 635.68 |  |  |  | 34.6667
1998-05-29 | 1600 | 300.08 | Data
1998-05-29 | 2030 | 304.58 | Off | 645.68
1998-05-29 | 2100 | 304.58 | On | 645.68 |  |  |  | 0.5
1998-05-29 | 2150 | 305.4133 | Off | 646.5133
1998-05-30 | 0050 | 305.4133 | On | 646.5133 |  |  |  | 3
1998-05-30 | 0530 | 310.0833 | Off | 651.1833
1998-05-30 | 0650 | 310.0833 | On | 651.1833 |  |  |  | 1.33
1998-05-30 | 0900 | 312.25 | Off | 653.35
1998-05-30 | 0930 | 312.25 | On | 653.35 |  |  |  | 0.5
1998-05-30 | 1010 | 312.92 | Off | 654.02
1998-05-30 | 1200 | 312.92 | On | 654.02 |  |  |  | 1.8333
1998-05-30 | 1440 | 315.59 | Off | 656.69
1998-05-30 | 1500 | 315.59 | On | 656.69 |  |  |  | 0.33
1998-05-30 | 1530 | 316.09 | Data
1998-05-30 | 1540 | 316.26 | Off | 657.36
1998-05-30 | 1630 | 316.26 | On | 657.36 |  |  |  | 0.83333
1998-05-30 | 1640 | 316.4267 | Off | 657.5267
1998-05-30 | 1750 | 316.4267 | On | 657.5267 |  |  |  | 1.1667
1998-05-31 | 0740 | 330.26 | Off | 671.36
|  | 3.3 | (Correction)
1998-05-31 | 1420 | 333.6 | On | 671.36 |  |  |  | 6.67
1998-05-31 | 1440 | 333.93 | Sample
1998-05-31 | 1600 | 334.93 | Data
1998-06-01 | 1600 | 358.93 | Data
1998-06-02 | 0830 | 375.43 | Sample
1998-06-02 | 1630 | 383.43 | Data
1998-06-03 | 1630 | 407.43 | Data
1998-06-04 | 1502 | 429.4967 | Sample | 792.4 | 121.04 | analog
1998-06-04 | 1530 | 430.43 | Data
1998-06-05 | 1530 | 454.43 | Data
1998-06-06 | 1630 | 479.43 | Data
1998-06-07 | 1530 | 502.43 | Data
1998-06-08 | 1530 | 526.43 | Data
1998-06-09 | 1530 | 550.43 | Data
1998-06-10 | 1530 | 574.43 | Data
1998-06-11 | 0830 | 591.43 | Samples
1998-06-11 | 1030 | 593.43 | Data
1998-06-11 | 1100 | 593.93 | Off - Cleaning
1998-06-11 | 1830 | 593.93 | On |  |  |  |  | 7.5
1998-06-12 | 1600 | 615.43 | Data
1998-06-13 | 1600 | 639.43 | Data
1998-06-14 | 1600 | 663.43 | Data
1998-06-15 | 1300 | 684.43 | Data
1998-06-16 | 1600 | 711.43 | Data
1998-06-16 | 2000 | 715.43 | Off - Raw water lost to WTP
1998-06-17 | 730 | 715.43 | On |  |  |  |  | 11.5
1998-06-17 | 1600 | 723.93 | Data
1998-06-18 | 1600 | 747.93 | Data
1998-06-19 | 1600 | 771.93 | Data
1998-06-20 | 1600 | 795.93 | Data
1998-06-21 | 1600 | 819.93 | Data
1998-06-22 | 830 | 836.43 | Data
1998-06-22 | 850 | 836.7633 | Off - Cleaning
1998-06-22 | 1630 | 836.7633 | On |  |  |  |  | 7.67
1998-06-22 | 1900 | 839.2633 | Data
1998-06-23 | 1600 | 860.2633 | Data
1998-06-24 | 1600 | 884.2633 | Data
1998-06-25 | 730 | 899.7633 | Samples
1998-06-25 | 1600 | 908.2633 | Data
1998-06-26 | 930 | 925.7633 | Data
1998-06-26 | 1020 | 926.5967 | Off - Cleaning
|  | 1.5 | (Correction)
1998-06-27 | 1300 | 928.0967 | On - changed cartridge filter to 1 um
1998-06-27 | 1600 | 931.0967 | Data
1998-06-28 | 1600 | 955.0967 | Data
1998-06-29 | 1600 | 979.0967 | Data
1998-06-30 | 1600 | 1003.0967 | Data
1998-06-30 | 1800 | 1005.0967 | Off
1998-06-30 | 1820 | 1005.0967 | On - replaced with new 1 um cartridge filter
1998-07-01 | 1600 | 1026.7967 | Data
1998-07-01 | 1630 | 1027.2967 | On -changed cartridge filter to 0.2 um
1998-07-02 | 1600 | 1050.7967 | Data
1998-07-03 | 1600 | 1074.7967 | Data
1998-07-04 | 1600 | 1098.7967 | Data
1998-07-05 | 1600 | 1122.7967 | Data
1998-07-06 | 00:30 | 1131.2967 | Off - system down due to pilot filter underdrain nozzle failure
1998-07-06 | 1610 | 1131.2967 | On - repaired/modified nozzle; refilled filter media.
1998-07-06 | 1830 | 1133.5967 | Off - system down for membrane inspection.
1998-07-06 | 1940 | 1133.5967 | On
1998-07-06 | 2200 | 1135.8967 | Data
1998-07-07 | 1600 | 1153.8967 | Data
1998-07-07 | 1645 | 1154.6467 | Off- system down to replace CF with a new 0.2 um CF
1998-07-07 | 1710 | 1154.6467 | On
1998-07-08 | 1600 | 1178.6467 | Data
1998-07-09 | 700 | 1193.6467 | Samples
1998-07-09 | 1600 | 1202.6467 | Data
1998-07-10 | 1600 | 1226.6467 | Data
1998-07-11 | 1600 | 1250.6467 | Data
1998-07-12 | 1600 | 1274.6467 | Data
1998-07-13 | 1600 | 1298.6467 | Data
1998-07-14 | 1600 | 1322.6467 | Data
1998-07-15 | 1600 | 1346.6467 | Data
1998-07-16 | 930 | 1364.1467 | Off - System down to clean and start up chloramine feed
1998-07-16 | 1930 | 1364.1467 | On
1998-07-16 | 2100 | 1365.6467 | Data
1998-07-17 | 850 | 1375.8 | hour meter checkpoint
1998-07-17 | 1530 | 1382.47 | Data
1998-07-18 | 1500 | 1405.97 | Data
1998-07-18 | 1730 | 1408.47 | RO Pump off for 12.5 hours due to power outage
1998-07-19 | 800 | 1420.97 | RO Pump back on
1998-07-19 | 1457 | 1429.9 | hour meter checkpoint
1998-07-19 | 1530 | 1430.47 | Data
1998-07-20 | 1530 | 1454.47 | Data
1998-07-22 | 1600 | 1501 | Data
1998-07-23 | 1100 | 1520
1998-08-22

## NF70. Quarterly
DATE | TIME | BOD | COD | PHOSPHORUS |  | ARSENIC |  | CADMIUM |  | CHROMIUM VI |  | COPPER |  | LEAD |  | MERCURY |  | SELENIUM |  | SILVER |  | ZINC
|  |  |  | Total | Elemental | Total | Dissolved | Total | Dissolved | Total | Dissolved | Total | Dissolved | Total | Dissolved | Total | Dissolved | Total | Dissolved | Total | Dissolved | Total | Dissolved
1998-10-01 | 1700 | <1.0 | <2.0 |  |  | 0.0015 | 0.0014 | <0.0001 | <0.0001 | <0.005 |  | >0.025 | >0.025 | <0.0025 | <0.0025 | <0.0002 |  | <0.0005 | <0.0005 | <0.0001 | <0.0001 | <0.003 | <0.003

## NF70. Monthly
DATE | TIME | BARIUM (ug/L) |  |  | SULFATE (mg/L) |  |  |  | REACTIVE SILICA (mg/L)
|  | Raw Feed |  | Permeate | Raw Feed |  | Permeate |  | Raw Feed |  | Permeate
1998-06-11 | 900 | 37 |  | ND | 32.5 | < | 5 |  | 2 | < | 2
1998-07-09 | 1194 | 33 |  | 12 | 22.5 | < | 5 | < | 2 | < | 2
1998-07-23 |  | NA |  | NA | NA |  | NA
1998-08-06 |  | 21.27 | < | 5 | 31.27 | < | 5 |  | 2 | < | 2
1998-09-04 | 915 | 16 |  | 11 | 20.542 | < | 5
1998-10-01 |  | 19 |  | 11 | 22.422 | < | 5
1999-11-24 | 715 |  |  |  | 21.16 | < | 5
1998-12-22 |  |  |  |  | 23 | < | 2
1998-01-19 |  |  |  |  | 23 | < | 2
AVERAGE |  | 25.254 |  | 9.75 | 24.5493 |  | 4.25 |  | 2 |  | 2
MAXIMUM |  | 37 |  | 12 | 32.5 |  | 5 |  | 2 |  | 2
MINIMUM |  | 16 |  | 5 | 20.542 |  | 2 |  | 2 |  | 2
STD DEV |  | 9.2004 |  | 3.2016 | 4.6207 |  | 1.3887 |  | 0 |  | 0

## NF70. Bi-weekly
[17 empty] | c |  |  | c |  |  | c | [5 empty] | c
DATE | TIME | [30 empty] | MANGANESE (mg/L) | [11 empty] | ALUMINUM (mg/L) | [13 empty] | SDS
|  | RUN | pH |  |  | Temperature |  |  | ALKALINITY (mg/L as CaCO3) |  |  | DISSOLVED OXYGEN (mg/L) |  |  | CALCIUM HARDNESS (mg/L as CaCO3) |  |  | TOTAL HARDNESS (mg/L as CaCO3) |  |  | TURBIDITY (ntu) |  |  | TOC (mg/L) |  |  |  |  | UV254 (cm-1) |  |  | Total | [5 empty] | Dissolved | [5 empty] | Total | [7 empty] | Dissolved | [5 empty] | Chlorine Dose (mg/L) |  | Free Chlorine Residual (mg/L) |  | Chlorine Demand (mg/L) |  | Chlorination Temperature |  |  |  | Chlorination pH |  | Incubation Time (hrs) |  |  | SDS-TOX (6) (ug/L) |  |  | SDS-THM4 (ug/L) |  |  | SDS-HAA5 (ug/L) |  | SDS-HAA6 (ug/L) |  |  |  | BROMIDE (mg/L) | [5 empty] | AMMONIA (mg/L)
|  | TIME (hrs) | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate |  | Permeate | Feed | Concentrate |  | Permeate | Feed | Concentrate |  | Permeate |  | Feed |  | Concentrate |  | Permeate |  | Feed |  | Concentrate |  | Raw |  | Permeate |  | Feed |  | Concentrate |  | Permeate |  | Feed |  | Concentrate | Permeate | Feed | Permeate | Feed | Permeate | Feed | Permeate (deg F) | Permeate (deg C) | Feed (deg F) | Feed (deg C) | Permeate | Feed | Permeate | Feed |  | Permeate | Feed |  | Permeate | Feed |  | Permeate | Feed | Permeate | Feed |  | Permeate |  | Feed | Concentrate |  | Permeate |  | Feed |  | Concentrate
1998
1998-05-27 | 800 | 280 | 5.66 | 6.53 | n/a | 23.1667 | 23.2222 | n/a | 2 | 10 | 29 | 8.21 | 9.26 | 9.3 | 2 | 32 | 127 | 7 | 51 | 174 | 0.12 | 0.27 | 0.22 | < | 0.5 | 2.56 | 9.48 |  | 0 | 0.041 | 0.176 | < | 0.003 | < | 0.003 |  | 0.037 | < | 0.003 | < | 0.003 |  | 0.028 |  |  | < | 0.13 | < | 0.13 |  | 0.18 | < | 0.13 | < | 0.13 | < | 0.13 | 5.13 | 3.2 | 4.15 | 0.84 | 0.98 | 2.36 | 70 | 21.1111 | 70.7 | 21.5 | 7.16 | 6.54 | 24 | 24 | < | 50 | 179.5 |  | 2.9 | 39 |  | 1 | 39 | 1 | 42.2 | < | 0.02 | < | 0.02 |  | < | 0.05 | < | 0.05 |  | 0.07
1998-06-11 | 830 | 591.8 | 5.7 | 6.6 | 7 | 22.6667 | 19.8333 | 18.2778 | 3 | 13 | 42 | 7.3 | 8.34 | 8.32 | 0 | 35 | 138 | 11 | 37 | 186 | 0.09 | 0.14 | 0.16 | < | 0.5 | 2.7 | 9.7 |  | 0.004 | 0.05 | 0.192 |  | 0.008 |  | 0.031 |  | 0.099 | < | 0.003 |  | 0.028 |  | 0.095 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | 2.3 | 2.3 | 1.16 | 0.15 | 1.14 | 2.15 | 69.8 | 21 | 69.9 | 21.0556 | 7.11 | 6.96 | 24 | 24 | < | 50 | 268.2 | < | 0.5 | 46 | < | 1 | 33 |  | 35.9 | < | 0.02 |  | 0.02 |  |  | 0.15 |  | 0.17 |  | 0.11
1998-06-25 | 730 | 899.7633 | 5.82 | 6.39 | 6.67 | 25.3889 | 26 | 25.5 | 1 | 10 | 29 | 6.84 | 7.27 | 6.95 | 0 | 32 | 162 | 9 | 50 | 173 | 0.08 | 0.14 | 0.16 | < | 0.5 | 2.7 | 9.73 |  | 0.009 | 0.056 | 0.189 | < | 0.003 |  | 0.021 |  | 0.045 | < | 0.003 |  | 0.018 |  | 0.044 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | 2.04 | 2.04 | 1.53 | 0.12 | 0.51 | 1.92 | 72.7 | 22.6111 | 73.3 | 22.9444 | 7 | 7 | 23.8 | 23.8 | < | 50 | 136.9 |  | 5.1 | 39 |  | 3.3 | 35 |  | 38.2 | < | 0.02 |  | 0.02 |  | < | 0.05 | < | 0.05 | < | 0.05
1998-07-09 | 700 | 1185 | 5.67 | 6.11 | 6.83 | 21.8333 | 21.8889 | n/a | 4 | 8 | 21 | 5.03 | 5.6 | 5.68 | 0 | 19 | 80 | 2 | 37 | 123 | 0.09 | 0.16 | 0.15 | < | 0.5 | 2.79 | 10.54 |  | 0 | 0.052 | 0.204 | < | 0.003 |  | 0.022 |  | 0.022 | < | 0.003 |  | 0.017 |  | 0.102 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | < | 0.13 | 2.13 | 3.2 | 1.43 | 0.43 | 0.7 | 2.77 | 75 | 23.8889 | 75.4 | 24.1111 | 6.9 | 6.91 | 23.9 | 24.1 | < | 50 | 195.7 |  | 1.6 | 59.4 | < | 1 | 46 |  | 49.4 | < | 0.02 |  | 0.026 |  | < | 0.05 | < | 0.05 | < |  | THMs by City
1998-07-23 | 1100 | 1519 | 5.9 | 6.11 | 6.4 | 30.5 | 29.4 | 30.5 | 3 | 7 | 15 | 6.3 | 6.54 | 6.54 | 0 | 19 | 70 | 5 | 33 | 114 | 0.13 | 0.14 | 0.17 | < | 0.5 | 2.83 | 10.27 | < | 0.009 | 0.047 | 0.188 |  | 0.039 |  | 0.016 |  | 0.055 |  | 0.034 |  | 0.009 |  | 0.068 | < | 0.17 | < | 0.17 | < | 0.17 |  | 0.19 | < | 0.17 | < | 0.17 | < | 0.017 | 1.95 | 4.88 | 1.39 | 1.64 | 0.56 | 3.24 |  | 24.7 |  | 24.4 | 7.05 | 7.04 | 23.3 | 23 | < | 50 | 136.4 |  | 0.9 | 72.5 | < | 1 | 49 |  | 52.7 | < | 0.02 | < | 0.026 |  | < | 0.05 | < | 0.05 | < | 0.05
|  |  | 5.9 | 6.1 | 6.4 | 30.5 | 29.4 | 30.5 | 3 | 7 | 15 | 6.1 | 6.49 | 6.45 | 0 | 19 | 71 | 5 | 33 | 114 | 0.12 | 0.14 | 0.17 | < | 0.5 | 2.82 | 10.2 | < | 0.009 | 0.047 | 0.188 |  | 0.044 |  | 0.018 |  | 0.055 |  | 0.032 |  | 0.01 |  | 0.068 | < | 0.17 | < | 0.17 | < | 0.17 |  | 0.18 | < | 0.17 | < | 0.17 | < | 0.17 | 1.95 | 4.88 | 1.3 | 1.67 | 0.65 | 3.21 |  | 24.7 |  | 24.9 | 7.01 | 7.03 |  |  | < | 50 | 136.9 |  | 0.7 | 73.5 | < | 1 | 48 |  | 51.5 | < | 0.02 |  | 0.028 |  | < | 0.05 | < | 0.05 | < | 0.05
1998-08-06 | 1130 | 1856 | 5.8 | 6.12 | 6.49 | 28.7778 | 27.8333 | 29.2222 | 3 | 6 | 18 | 6.92 | 7.39 | 7.32 | 0 | 17 | 72 | 8 | 39 | 120 | 0.15 | 0.44 | 0.29 | < | 0.5 | 2.9 | 10.9 | < | 0.009 | 0.046 | 0.199 | < | 0.003 |  | 0.022 |  | 0.11 | < | 0.003 |  | 0.021 |  | 0.105 | < | 0.17 | < | 0.17 | < | 0.17 |  | 0.19 | < | 0.17 | < | 0.17 | < | 0.17 | 2.04 | 4.59 | 1.21 | 1.24 | 0.83 | 3.35 | 76.5 | 24.7222 | 76.6 | 24.7778 | 7.05 | 6.7 | 23.1 | 23 |  |  |  |  | 4.2 | 46 |  | 2.2 | 44 |  | 47.7 | < | 0.02 |  | 0.032 |  | < | 0.05 | < | 0.05 | < | 0.05
1998-08-20 | 1330 | 2145 | 6.6 | 6.93 | 7.58 | 27.8333 | 28.3333 | 27.6667 | 3 | 18 | 67 | 6.25 | 6.52 | 7.2 | 0 | 19 | 70 | 10 | 38 | 97 | 0.06 | 0.07 | 0.38 | < | 0.5 | 2.65 | 9.17 |  | 0.005 | 0.046 | 0.166 | < | 0.003 |  | 0.025 |  | 0.11 | < | 0.003 |  | 0.016 |  | 0.099 | < | 0.17 | < | 0.17 | < | 0.17 | < | 0.17 | < | 0.17 | < | 0.17 | < | 0.17 | 2.13 | 4.79 | 1.08 | 1.1 | 1.05 | 3.69 | 76.3 | 24.6111 | 76.8 | 24.8889 | 7.18 | 7 | 24.0833 | 24.0833 | < | 25 | 235 |  | 1.7 | 59.9 |  | 1 | 54 |  | 57.8 | < | 0.02 |  | 0.03 |  |  | 0.1 | < | 0.05 | < | 0.05
1998-09-04 | 915 | 2488 | 6.84 | 7.39 | 8.22 | 28.3889 | 27.8889 | 28.5556 | 5 | 18 | 74 | 6.94 | 7.3 | 7.2 | 0 | 18 | 59 | 10 | 38 | 97 | 0.06 | 0.11 | 0.13 | < | 0.5 | 2.58 | 9.25 |  |  |  |  | < | 0.003 |  | 0.01 |  | 0.053 | < | 0.003 |  | 0.009 |  | 0.05 | < | 0.008 | < | 0.008 | < | 0.008 |  | 1.11 | < | 0.008 | < | 0.008 | < | 0.008 | 2.04 | 5.1 | 1.34 | 2.09 | 0.7 | 3.01 |  | 23.8 |  | 23.9 | 7.17 | 5.62 | 23.9167 | 24.1667 | < | 25 | 215 |  | 3.3 | 31.4 | < | 1 | 41 |  | 44 | < | 0.02 |  | 0.029 |  | < | 0.05 | < | 0.05 | < | 0.05
1998-09-17 | 900 | 2786 | 6.93 | 6.75 | 6.81 | 26.7222 | 26.4444 | 26.6667 | 3 | 13 | 72 | 6 | 7.3 | 7.12 | 0 | 18 | 70 | 3 | 40 | 112 | 0.25 | 0.2 | 0.22 | < | 0.5 | 2.6 | 9.48 |  | 0.001 | 0.039 | 0.151 | < | 0.003 |  | 0.018 |  | 0.089 | < | 0.003 |  | 0.015 |  | 0.085 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | 1.95 | 4.39 | 0.78 | 1.15 | 1.17 | 3.24 | 75.5 | 24.1667 | 75.8 | 24.3333 | 7.21 | 7.26 | 23.5 | 23.8333 | < | 25 | 168.6 |  | 3.3 | 60.3 | < | 1 | 40 |  | 43.7 | < | 0.02 | < | 0.02 |  |  | 0.11 | < | 0.05 |  | 0.23
1998-10-01 | 1330 | 3118 | 6.94 | 6.89 | 8.36 | 28 | 27.6 | 28.8 | 5 | 17 | 127 | 7.74 | 8.07 | 8.66 | 0 | 14 | 109 | 3 | 27 | 184 | 0.11 | 0.12 | 0.14 | < | 0.5 | 2.25 | 15.14 |  | 0.002 | 0.04 | 0.264 | < | 0.003 |  | 0.025 |  | 0.061 | < | 0.003 |  | 0.014 |  | 0.005 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | 1.95 | 4.88 | 1.75 | 0.96 | 0.2 | 3.92 |  | 23.1 |  | 23.4 | 7.39 | 7.27 | 24.4 | 23.7 |  | 40.8 | 139.1 | < | 0.5 | 38.5 | < | 1 | 35 |  | 38.6 | < | 0.02 |  | 0.04 | 0.264 | < | 0.05 | < | 0.05 | < | 0.05
|  |  | 6.95 | 6.91 |  | 28 | 27.4 |  | 5 | 17 |  | 7.51 | 8.07 |  | 0 | 15 |  | 3 | 27 |  | 0.13 | 0.13 |  | < | 0.5 | 2.32 |  |  | 0.002 | 0.041 |  | < | 0.003 |  | 0.022 |  |  | < | 0.003 |  | 0.017 |  |  | < | 0.008 | < | 0.008 | < | 0.008 |  |  | < | 0.008 | < | 0.008 |  |  | 1.95 | 4.88 |  | 1.51 | 1.95 | 3.37 |  | 23.1 |  | 23.3 | 7.28 | 7.26 |  |  |  | 38.5 | 150 | < | 0.5 | 43.9 | [5 empty] | < | 0.02 |  | 0.029 |  |  | 0.11 | < | 0.05
1998-10-15 | 735 | 3415 | 9.1 | 9.15 | 8.72 | 23.3 | 23 | 22.9 | 4 | 16 | 70 | 8.96 | 9.34 | 9.34 | 0 | 15 | 53 | 6 | 28 | 101 | 0.07 | 0.08 | 0.1 | < | 0.5 | 2.38 | 8.52 |  | 0.002 | 0.041 | 0.149 | < | 0.003 |  | 0.01 |  | 0.028 | < | 0.003 |  | 0.01 |  | 0.027 | < | 0.008 | < | 0.008 |  | 0.234 |  | 0.191 | < | 0.008 |  | 0.181 |  | 0.072 | 3.1 | 6.2 | 2.05 | 3.1 | 1.05 | 3.1 |  | 22.5 |  | 22.5 | 7.22 | 7.5 | 24 | 23.9167 | < | 25 | 162 | < | 0.5 | 89.9 | < | 1 | 38 |  | 42.3 | < | 0.02 |  | 0.032 |  | < | 0.05 | < | 0.05 | < | 0.05
1998-10-29
1998-11-12
1998-11-24
1998-12-10
1998-12-24
1999
1998-01-07
1998-01-21
1998-02-04
1998-02-18
1998-03-04
1998-03-18
1998-04-01
1998-04-15
1998-04-29
1998-05-13
1998-10-29 | 740 | 3735 | 6.58 | 6.86 | 7.59 | 21.3 | 20.3 | 21.4 | 3 | 15 | 62 | 7.4 | 7.81 | 8.13 | 0 | 15 | 58 | 2 | 31 | 120 | 0.06 | 0.11 | 0.11 | < | 0.5 | 2.18 | 8.95 | < | 0.009 | 0.048 | 0.179 | < | 0.003 |  | 0.007 |  | 0.098 | < | 0.003 |  | 0.003 |  | 0.016 |  |  | < | 0.008 |  | 0.181 |  | 0.418 | > | 0.008 |  | 0.234 |  | 0.113 | 1.86 | 3.72 | 0.49 |  | 1.37 | 3.72 |  | 19.4 |  | 19.4 | 7.02 | 7.07 | 24 | 24 |  | 49.8 | 166.2 |  | 0.9 | 33.7 | < | 1 | 31.5 |  | 34.6 | < | 0.02 |  | 0.036 |  | < | 0.05 | < | 0.05 | < | 0.05
1998-11-12 | 920 | 4075 | 7.7 | 7.07 | 9.96 | 20.3 | 18.1 | 20.9 | 3 | 16 | 79 | 8.53 | 8.74 | 8.67 | 0 | 14 | 61 | 2 | 35 | 113 | 0.13 | 0.1 | 0.2 | < | 0.5 | 2.29 | 9.88 |  | 0 | 0.041 | 0.171 | < | 0.003 | < | 0.003 |  | 0.025 | < | 0.003 | < | 0.003 |  | 0.028 |  | 0.03 | < | 0.008 |  | 0.019 |  | 0.197 | < | 0.008 |  | 0.008 |  | 0.137 | 2.57 | 3.86 | 0.62 | 1.44 | 1.95 | 2.42 |  | 16.9 |  | 16.8 | 7.09 | 7.29 | 24 | 24 | < | 25 | 180 | < | 0.5 | 26.2 |  | 3 | 31 |  | 35.3 | < | 0.02 |  | 0.036 |  | < | 0.05 | < | 0.05 | < | 0.05
1999-11-24 | 713 | 4349 | 8.13 | 8.28 | 8.41 | 21.1111 | 21 | 18.8889 | 1 | 21 | 66 | 8.81 | 9.54 | 9.65 | 7 | 16 | 62 | 8 | 32 | 104 | 0.28 | 0.36 | 0.42 | < | 0.5 | 2.43 | 8.94 |  | 0.003 | 0.049 | 0.158 | < | 0.003 |  | 0.02 |  | 0.063 | < | 0.003 |  | 0.011 |  | 0.055 | < | 0.008 | < | 0.008 |  | 0.011 |  | 0.055 | [6 empty] | 0.67 | 3.99 | 0.35 | 1.31 | 0.32 | 2.68 |  | 18.2 |  | 18.1 | 5.37 | 7.52 | 25 | 24.0833 | < | 25 | 164.2 | < | 0.5 | 47.5 |  | 1 | 29 |  | 32.4 | < | 0.02 |  | 0.04 |  | < | 0.05 | < | 0.05 | < | 0.05
[44 empty] | < | 0.0075 | < | 0.0075 | < | 0.0075 | < | 0.0075
1999-12-10 | 1220 | 4738 | 8.85 | 7.52 | 8.6 | 20.4 | 18.2 | 20.9 | 7 | 19 | 221 | 8.57 | 8.92 | 9.39 | 0 | 15 | 183 | 2 | 31 | 308 | 0.09 | 0.1 | 0.17 | < | 0.5 | 2.54 | 27.78 |  | 0 | 0.041 | 0.504 |  | 0.008 |  | 0.046 |  | 0.188 | < | 0.003 |  | 0.031 |  | 0.154 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.008 | < | 0.003 |  | 0.031 |  | 0.154 | 2 | 3.99 | 0.56 | 1.19 | 1.44 | 2.8 |  | 17.6 |  | 17.4 | 7.05 | 7.12 | 24 | 24 |  | 27 | 174.9 |  | 0.5 | 37.2 | < | 1 | 49 |  | 54.1 | < | 0.02 |  | 0.03 |  | < | 0.05 | < | 0.05 |  | 0.05
| 1200 | 4738 | 8.98 | 7.47 |  | 20.5 | 18.1 |  | 7 | 19 |  | 8.45 | 8.81 |  | 0 | 15 |  | 2 | 30 |  | 0.08 | 0.1 |  | < | 0.5 | 2.64 |  |  | 0.002 | 0.041 |  |  | 0.01 |  | 0.048 |  |  |  | 0.004 |  | 0.038 |  |  | < | 0.008 | < | 0.008 | < | 0.008 | [8 empty] | 2 | 3.99 | 1.18 | 1.28 | 0.82 | 2.71 |  | 17.5 |  | 17.3 | 7.41 | 7.12 |  |  |  | 61 | 168.9 | < | 0.5 | 54.4 | < | 1 | 32 |  | 35 | < | 0.02 |  | 0.03 |  | < | 0.05 | < | 0.05
1999-12-22 | 1040 | 5010 | 8.9 | 7.4 | 8.3 | 17.7 | 15.8333 | 18.1 | 4 | 18 | 72 | 9.95 | 10.04 | 9.96 | 0 | 13 | 64 | 3 | 30 | 108 | 0.1 | 0.2 | 0.22 | < | 0.5 | 2.36 | 9.43 |  | 0.002 | 0.038 | 0.167 | < | 0.014 |  | 0.018 |  | 0.086 | < | 0.14 |  | 0.017 |  | 0.081 |  | 0.514 |  | 0.123 |  | 0.11 |  | 0.258 |  | 0.1 |  | 0.182 |  | 0.241 | 2 | 3.99 | 1.2 | 1.35 | 0.8 | 2.64 |  | 17.3 |  | 17.3 | 4.21 | 7.07 | 24 | 24 | < | 25 | 189.3 | < | 0.5 | 37.4 | < | 1 | 34 |  | 37.6 | < | 0.02 |  | 0.029 |  | < | 0.05 | < | 0.05 |  | 0.07
1999
1999-01-05 | 815 | 5343 | 7.06 | 7.2 | 8.21 | 13.7 | 11.7 | 13.8 | 1 | 15 | 74 | 10.6 | 10.1 | 10.4 | 0 | 14 | 62 | 1 | 28 | 105 | 0.07 | 0.09 | 0.12 | < | 0.5 | 2.21 | 10.1 |  | 0.001 | 0.04 | 0.168 | < | 0.014 | < | 0.014 |  | 0.027 | < | 0.014 | < | 0.014 | < | 0.014 |  | 0.015 |  | 0.254 |  | 0.124 |  | 0.264 |  | 0.137 |  | 0.1 |  | 0.273 | 2 | 3.99 | 1.3 | 1.3 | 0.7 | 2.69 |  | 14.4 |  | 13.7 | 6.97 | 7.22 | 24 | 23.9167 | < | 25 | 127.9 | [8 empty] | < | 0.02 |  | 0.032 |  |  | 0.11 |  | 0.05 | < | 0.05
1999-01-19 | 1045 | 5654 | 5.78 | 5.57 | 4.84 | 14 | 12.6 | 14.9 | 2 | 2 | 0 | 11.7 | 11.8 | 11.4 | 0 | 11 | 55 | 1 | 27 | 98 | 0.09 | 0.11 | 0.12 | [5 empty] | 0.002 | 0.031 | 0.14 | < | 0.014 | < | 0.014 |  | 0.024 | < | 0.014 | < | 0.014 |  | 0.025 |  | 0.185 |  | 0.092 |  | 0.128 |  | 0.325 |  | 0.067 |  | 0.166 |  | 0.309 | 2 | 3.99 | 1.14 | 1.41 | 0.86 | 2.58 |  | 16.2 |  | 15.4 | 7 | 6.98 | 26.75 | 26.5833 | [11 empty] | < | 0.02 |  | 0.033 |  | < | 0.05 | < | 0.05 | < | 0.05
1999-02-02 | 1105 | 5961 | 5.48 | 5.93 | 4.52 | 15.5 | 15.2 | 16.2 | 1 | 4 | 0 | 8.76 | 8.8 | 9.43 | [6 empty] | 0.11 | 0.14 | 0.15 | [5 empty] | 0.001 | 0.031 | 0.135 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | [14 empty] | 2 | 3.99 | 1.23 | 1.29 | 0.77 | 2.7 |  | 15.7 |  | 15.2 | 7.09 | 6.99 | 24 | 24 | [11 empty] | < | 0.02 |  | 0.03
AVERAGE |  |  | 7.0005 | 6.989 | 7.6794 | 24.0044 | 23.0739 | 23.9111 | 3.5 | 14.15 | 64.0556 | 7.6205 | 8.0725 | 8.1267 | 0.45 | 18.7 | 87.2778 | 5.1 | 34.75 | 136.2778 | 0.1135 | 0.16 | 0.19611 |  | 0.5 | 2.5365 | 10.97 |  | 0.0036316 | 0.044421 | 0.20076 |  | 0.0088 |  | 0.01995 |  | 0.0695 |  | 0.01345 |  | 0.0152 |  | 0.062444 |  | 0.0895 |  | 0.079262 |  | 0.092119 |  | 0.20129 |  | 0.083111 |  | 0.10933 |  | 0.12124 | 2.188 | 4.143 | 1.3089 | 1.2563 | 0.9445 | 2.9495 | 73.6857 | 21.2656 | 74.0714 | 21.3006 | 6.8925 | 7.025 | 23.9412 | 23.8588 |  | 37.7421 | 173.4053 |  | 1.5316 | 49.2474 |  | 1.3056 | 39.3611 | 1 | 42.9444 |  | 0.02 |  | 0.02925 | 0.264 |  | 0.0665 |  | 0.056 |  | 0.066471
MAXIMUM |  |  | 9.1 | 9.15 | 9.96 | 30.5 | 29.4 | 30.5 | 7 | 21 | 221 | 10.6 | 10.1 | 10.4 | 7 | 35 | 183 | 11 | 51 | 308 | 0.28 | 0.44 | 0.42 |  | 0.5 | 2.9 | 27.78 |  | 0.009 | 0.056 | 0.504 |  | 0.044 |  | 0.048 |  | 0.188 |  | 0.14 |  | 0.038 |  | 0.154 |  | 0.514 |  | 0.254 |  | 0.234 |  | 1.11 |  | 0.17 |  | 0.234 |  | 0.273 | 5.13 | 6.2 | 4.15 | 3.1 | 1.95 | 3.92 | 76.5 | 24.7222 | 76.8 | 24.9 | 7.41 | 7.52 | 25 | 24.1667 |  | 61 | 268.2 |  | 5.1 | 89.9 |  | 3.3 | 54 | 1 | 57.8 |  | 0.02 |  | 0.04 | 0.264 |  | 0.15 |  | 0.17 |  | 0.23
MINIMUM |  |  | 5.66 | 6.1 | 6.4 | 13.7 | 11.7 | 13.8 | 1 | 6 | 15 | 5.03 | 5.6 | 5.68 | 0 | 13 | 53 | 1 | 27 | 97 | 0.06 | 0.07 | 0.1 |  | 0.5 | 2.18 | 8.52 |  | 0 | 0.038 | 0.149 |  | 0.003 |  | 0.003 |  | 0.022 |  | 0.003 |  | 0.003 |  | 0.005 |  | 0.0075 |  | 0.0075 |  | 0.0075 |  | 0.0075 |  | 0.003 |  | 0.008 |  | 0.008 | 0.67 | 2.04 | 0.35 | 0.12 | 0.2 | 1.92 | 69.8 | 14.4 | 69.9 | 13.7 | 4.21 | 5.62 | 23.1 | 23 |  | 25 | 127.9 |  | 0.5 | 26.2 |  | 1 | 29 | 1 | 32.4 |  | 0.02 |  | 0.02 | 0.264 |  | 0.05 |  | 0.05 |  | 0.05
STD DEV |  |  | 1.2142 | 0.76556 | 1.0232 | 4.5341 | 5.0867 | 5.1843 | 1.7014 | 4.6257 | 49.0647 | 1.4009 | 1.2707 | 1.3718 | 1.6051 | 6.4816 | 39.2261 | 3.259 | 6.7736 | 52.5747 | 0.058515 | 0.095422 | 0.087859 |  | 0 | 0.22205 | 4.4295 |  | 0.0035467 | 0.0050257 | 0.082494 |  | 0.011799 |  | 0.011821 |  | 0.041929 |  | 0.031211 |  | 0.0091283 |  | 0.039891 |  | 0.12472 |  | 0.08112 |  | 0.077753 |  | 0.24363 |  | 0.071985 |  | 0.076679 |  | 0.078248 | 0.81287 | 0.9726 | 0.81326 | 0.66768 | 0.46779 | 0.53107 | 2.8702 | 3.2527 | 2.8271 | 3.4269 | 0.75488 | 0.40427 | 0.41194 | 0.34319 |  | 12.9359 | 36.1193 |  | 1.4735 | 16.5025 |  | 0.7296 | 7.4593 |  | 7.6788 |  | 0 |  | 0.0061205 |  |  | 0.030655 |  | 0.026833 |  | 0.044853
7.495

## NF70. Weekly
City of Norfolk, VA
ICR SEBST
LEGEND
|  | Feed: | Treated Feed (post SI & CF) from 5/15 to 6/8
Raw Feed (pre-SI & CF) from 6/9 on
|  | Influent: | RO Feed
SEMI-WEEKLY DATA:
FROM DATA LOGGER: | [17 empty] | CALCULATED VALUES: | [9 empty] | DATE | TIME | SDI |  |  |  | HPC | [9 empty] | TDS (mg/L) |  |  | Conductivity (uS/cm) |  |  | Ratio of TDS/Conductivity |  |  | % SALT REJECTION
DATE | TIME | RUN TIME | CONDUCTIVITY |  |  | Adjusted TEMP | Original TEMP | PRESSURE |  |  | pH |  |  | FLOW | [9 empty] | TDS (based on Conductivity) where TDS: | [5 empty] | Raw Feed |  | Treated Feed |  | Permeate |  | Raw Feed |  | Influent (RO Feed) |  | Settled Water |  | Concentrate |  | Permeate | Raw Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | (based on Measured TDS)
|  |  | REJECT | FEED | PERMEATE | PERMEATE | PERMEATE | FEED | REJECT | PERMEATE | FEED | PERMEATE | REJECT | PERMEATE | REJECT | RECYCLE |  | RECOVERY | DIFFERENTIAL PRESSURE | 150% of DP24 | NET DRIVING PRESSURE (NDP) (psi) | 80% of MTCw AT 20 DEG C | TEMPERATURE CORRECTION FACTOR (TCF) AT 20 DEG C | (= Cond. X 0.5) Permeate | (= Cond. X 0.6) Feed | (= Cond. X 0.8) Reject | % SALT REJECTION |  |  | Result | to | Result | to | Count | Dilution | Count | Dilution | Count | Dilution | Count | Dilution | Count |  | Dilution
15/5/98 | 13:45 pm | 0 | 183.16 | 127.78 | 5.5 | 16.52 | 21.52 | 82.25 | 79.81 | 30.29 | 6.11 | 4.65 | 5.95 | 0.78 | 0.23 | 3.97 |  | 77.23% | 2.44 | 3.21 |  | 0.29149 | [5 empty] | 15/5/98 | 1530 |  | FP |  |  | 145 | 0 | TNTC | 0 | TNTC | 0 | 331 | 0 | TNTC | 0 |  |  |  | 306.79 | 129.61 | 306.79
15/5/98 | 16:00:00pm | 2.25 | 242.69 | 130.99 | 9.16 | 18.15 | 23.15 | 78.13 | 76.3 | 30.35 | 6.51 | 4.97 | 6.54 | 0.73 | 0.23 | 3.97 |  | 76.04% | 1.83 | 3.21 | 46.865 | 0.29149 | 1.0677 | 4.58 | 78.594 | 194.152 | 96.6416 | 15/5/98
16/5/98 | 14:00:00pm | 25.25 | 297.63 | 127.78 | 8.7 | 19.19 | 24.19 | 79.2 | 77.06 | 30.77 | 6.29 | 4.97 | 6.35 | 0.73 | 0.23 | 3.97 |  | 76.04% | 2.14 | 3.21 | 47.36 | 0.29149 | 1.029 | 4.35 | 76.668 | 238.104 | 97.2361 | 16/5/98 | 7:00 | [17 empty] | 10.99 | 130.53 | 256.42
17/5/98 | 16:00:00pm | 46.75 | 279.32 | 125.03 | 11.91 | 20.35 | 25.35 | 79.2 | 76.91 | 30.1 | 6.43 | 5 | 6.46 | 0.73 | 0.11 | 3.97 |  | 86.9% | 2.29 | 3.21 | 47.955 | 0.29149 | 0.98778 | 5.955 | 75.018 | 223.456 | 96.0097 | 17/5/98 | 7:00 | [17 empty] | 11.45 | 125.03 | 311.37
18/5/98 | 16:00:00pm | 70.75 | 238.11 | 123.66 | 8.7 | 20.27 | 25.27 | 78.13 | 75.69 | 30.47 | 6.19 | 4.94 | 6.3 | 0.73 | 0.28 | 3.97 |  | 72.28% | 2.44 | 3.21 | 46.44 | 0.29149 | 0.99056 | 4.35 | 74.196 | 190.488 | 96.7131 | 18/5/98 | 1540 | 4.9 | 31.7 | [15 empty] | 9.62 | 125.49 | 219.79
19/5/98 | 16:00:00pm | 94.75 | 261 | 121.37 | 10.53 | 21.64 | 26.64 | 78.44 | 76.45 | 30.8 | 6.05 | 4.95 | 6.14 | 0.73 | 0.23 | 3.97 |  | 76.04% | 1.99 | 3.21 | 46.645 | 0.29149 | 0.94424 | 5.265 | 72.822 | 208.8 | 96.2609 | 19/5/98 | 1311 | 3.6 | 46.8
20/5/98 | 16:00:00pm | 118.75 | 283.9 | 123.2 | 10.99 | 22.57 | 27.57 | 77.83 | 75.99 | 31.51 | 6.21 | 5 | 6.3 | 0.73 | 0.17 | 3.97 |  | 81.11% | 1.84 | 3.21 | 45.4 | 0.29149 | 0.91428 | 5.495 | 73.92 | 227.12 | 96.3493 | 20/5/98 | 1250 | 3.8 | 37.6 |  |  | 35 |  | 200 |  | 1300 |  | 75 |  | 2850 |  | 17 | 87 | 298 | 7.79 | 125.49 | 297.63 | 2.1823 | 0.69328 | 1.0012 | 91.1688
21/5/98 | 16:00:00pm | 142.75 | 306.79 | 129.61 | 10.99 | 23.49 | 28.49 | 77.98 | 75.69 | 31.2 | 6.36 | 5.06 | 6.46 | 0.78 | 0.23 | 3.97 |  | 77.23% | 2.29 | 3.21 | 45.635 | 0.29149 | 0.88574 | 5.495 | 77.766 | 245.432 | 96.5996 | 21/5/98
22/5/98 | 16:00:00pm | 159.75 | 274.74 | 129.16 | 11.45 | 21.9 | 26.9 | 79.2 | 76.91 | 32.33 | 6.36 | 4.99 | 6.36 | 0.73 | 0.17 | 3.97 |  | 81.11% | 2.29 | 3.21 | 45.725 | 0.29149 | 0.93575 | 5.725 | 77.496 | 219.792 | 96.1485 | 22/5/98 | 900 | 3.3 | 58.3 |  |  | 10 |  | 920 |  | 1335 |  | 220 |  | 2140 |  | 21 | 82 | 304 | 12.37 | 131.45 | 274.74 | 1.6977 | 0.62381 | 1.1065 | 89.1192
23/5/98 | 16:00:00pm | 166.75 | 288.48 | 127.78 | 10.53 | 20.09 | 25.09 | 79.05 | 77.22 | 31.45 | 6.23 | 4.98 | 6.26 | 0.78 | 0.17 | 3.97 |  | 82.11% | 1.83 | 3.21 | 46.685 | 0.29149 | 0.99684 | 5.265 | 76.668 | 230.784 | 96.5751 | 23/5/98
24/5/98 | 16:00:00pm | 190.75 | 334.27 | 130.53 | 9.62 | 19.81 | 24.81 | 79.05 | 76.3 | 30.07 | 6.4 | 5.01 | 6.43 | 0.73 | 0.17 | 3.97 |  | 81.11% | 2.75 | 3.21 | 47.605 | 0.29149 | 1.0067 | 4.81 | 78.318 | 267.416 | 97.2175 | 24/5/98
25/5/98 | 16:00:00pm | 214.75 | 279.32 | 127.32 | 10.53 | 21.32 | 26.32 | 78.89 | 76.3 | 30.56 | 6.28 | 5 | 6.33 | 0.73 | 0.23 | 3.97 |  | 76.04% | 2.59 | 3.21 | 47.035 | 0.29149 | 0.95483 | 5.265 | 76.392 | 223.456 | 96.4882 | 25/5/98
26/5/98 | 16:00:00pm | 238.75 | 247.27 | 125.95 | 10.53 | 22.33 | 27.33 | 77.67 | 75.38 | 30.71 | 6.27 | 5.02 | 6.32 | 0.73 | 0.23 | 3.87 |  | 76.04% | 2.29 | 3.21 | 45.815 | 0.29149 | 0.9219 | 5.265 | 75.57 | 197.816 | 96.1483 | 26/5/98 | 1035 | 2.9 | 72 |  |  | 207 | 0 | TNTC | 0 | 3000 | 10-2 | TNTC | 10-1 | 5600 | 10-2 |  | Sampling Error - No Samples
27/5/98 | 16:00:00pm | 257.3333 | 238.11 | 125.95 | 10.99 | 21.7 | 26.7 | 78.59 | 76.3 | 31.11 | 6.37 | 5.01 | 6.36 | 0.73 | 0.23 | 3.97 |  | 76.04% | 2.29 | 3.21 | 46.335 | 0.29149 | 0.94228 | 5.495 | 75.57 | 190.488 | 95.8693 | 27/5/98
28/5/98 |  | 278.7067 | [17 empty] | 3.21 |  | 0.29149 | [5 empty] | 28/5/98
29/5/98 | 16:00:00pm | 300.08 | 357.16 | 125.49 | 13.74 | 22.94 | 27.94 | 75.99 | 73.4 | 30.9 | 6.49 | 5.12 | 6.48 | 0.73 | 0.17 | 4.08 |  | 81.11% | 2.59 | 3.21 | 43.795 | 0.29149 | 0.90267 | 6.87 | 75.294 | 285.728 | 96.1941 | 29/5/98
30/5/98 | 15:30:00pm | 316.09 | 279.32 | 119.54 | 15.11 | 24.62 | 29.62 | 63.02 | 60.28 | 24.43 | 6.64 | 5.27 | 6.66 | 0.63 | 0.17 | 4.18 |  | 78.75% | 2.74 | 3.21 | 37.22 | 0.29149 | 0.85214 | 7.555 | 71.724 | 223.456 | 94.8811 | 30/5/98
31/5/98 | 16:00:00pm | 334.93 | 288.48 | 128.24 | 10.53 | 23.7 | 28.7 | 74.47 | 72.03 | 30.93 | 6.31 | 5.1 | 6.39 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.44 | 3.21 | 42.32 | 0.29149 | 0.87938 | 5.265 | 76.944 | 230.784 | 96.5781 | 31/5/98 | 1440 | 5.1 | 32.4
1998-01-06 | 16:00:00pm | 358.93 | 238.11 | 122.29 | 10.53 | 23.81 | 28.81 | 77.83 | 75.38 | 32.97 | 6.35 | 5.07 | 6.37 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.45 | 3.21 | 43.635 | 0.29149 | 0.87607 | 5.265 | 73.374 | 190.488 | 96.0093 | 1998-01-06
1998-02-06 | 16:30:00pm | 375.43 | 338.85 | 120.45 | 12.82 | 24.27 | 29.27 | 77.67 | 75.23 | 31.72 | 6.37 | 5.08 | 6.36 | 0.73 | 0.17 | 4.08 |  | 81.11% | 2.44 | 3.21 | 44.73 | 0.29149 | 0.86239 | 6.41 | 72.27 | 271.08 | 96.2662 | 1998-02-06 | 830 | 5.2 |  |  |  | 16 |  | 800 |  | 400 |  | 25 |  | 2000 |  | 20 | 82 | 308 | 12.37 | 125.03 | 288.48 | 1.6168 | 0.65584 | 1.0677 | 89.7436
1998-03-06 | 16:30:00pm | 407.43 | 338.85 | 125.49 | 13.28 | 24.74 | 29.74 | 77.98 | 74.93 | 31.32 | 6.28 | 5.07 | 6.3 | 0.73 | 0.23 | 3.97 |  | 76.04% | 3.05 | 3.21 | 45.135 | 0.29149 | 0.84867 | 6.64 | 75.294 | 271.08 | 96.166 | 1998-03-06
1998-04-06 | 15:30:00pm | 430.43 | 270.16 | 128.7 | 13.28 | 23.83 | 28.83 | 76.91 | 74.47 | 30.8 | 6.56 | 5.14 | 6.59 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.44 | 3.21 | 44.89 | 0.29149 | 0.87547 | 6.64 | 77.22 | 216.128 | 95.473 | 1998-04-06
1998-05-06 | 15:30:00pm | 454.43 | 297.63 | 124.58 | 13.28 | 23.12 | 28.12 | 78.59 | 76.15 | 30.5 | 6.4 | 5.08 | 6.41 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.44 | 3.21 | 46.87 | 0.29149 | 0.89709 | 6.64 | 74.748 | 238.104 | 95.7552 | 1998-05-06 | 725 | 4.6 |  |  |  | 5 |  | 500 |  | 400 |  | 300 |  | 1400 |  | 5 | 79 | 289 | 11.91 | 127.32 | 315.95 | 0.41982 | 0.62048 | 0.9147 | 97.2826
1998-06-06 | 16:30:00pm | 479.43 | 288.48 | 128.24 | 13.28 | 22.57 | 27.57 | 79.05 | 76.15 | 30.99 | 6.45 | 5.09 | 6.43 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 46.61 | 0.29149 | 0.91428 | 6.64 | 76.944 | 230.784 | 95.6845 | 1998-06-06
1998-07-06 | 15:30:00pm | 502.43 | 256.42 | 125.95 | 12.82 | 22.67 | 27.67 | 79.2 | 76.3 | 30.16 | 6.46 | 5.09 | 6.47 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 47.59 | 0.29149 | 0.91112 | 6.41 | 75.57 | 205.136 | 95.4329 | 1998-07-06
1998-08-06 | 15:30:00pm | 526.43 | 242.69 | 125.03 | 13.28 | 23.37 | 28.37 | 78.74 | 75.69 | 29.74 | 6.24 | 5.04 | 6.19 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.05 | 3.21 | 47.475 | 0.29149 | 0.88941 | 6.64 | 75.018 | 194.152 | 95.0663 | 1998-08-06
1998-09-06 | 15:30:00pm | 550.43 | 265.58 | 129.61 | 9.62 | 23.66 | 28.66 | 81.18 | 78.59 | 32.3 | 6.29 | 5.3 | 6.63 | 0.73 | 0.28 | 3.97 |  | 72.28% | 2.59 | 3.21 | 47.585 | 0.29149 | 0.88059 | 4.81 | 77.766 | 212.464 | 96.6854 | 1998-09-06 | 750 | 3.8 |  |  |  | 25 |  | 1250 |  | 1550 |  | 270 |  | 1150 |  | 29 | 209 | 381 | 13.74 | 129.16 | 297.63 | 2.1106 | 1.6181 | 1.2801 | 90.1695 | Raw Feed Analyses begun
|  | 562.43 | [17 empty] | 3.21 |  | 0.29149 | [6 empty] | 915 | 5.4 | 26.2 | [12 empty] | 10 | 40 | 240 | 13.74 | 129.16 | 297.63 | 0.7278 | 0.30969 | 0.80637 | 92.8571
1998-10-06 | 15:30:00pm | 574.43 | 238.11 | 131.45 | 11.91 | 22.68 | 27.68 | 79.66 | 76.76 | 30.19 | 6.11 | 5.23 | 6.38 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.9 | 3.21 | 48.02 | 0.29149 | 0.91081 | 5.955 | 78.87 | 190.488 | 95.5784 | 1998-10-06
1998-11-06 | 10:30:00am | 593.43 | 315.95 | 135.57 | 14.66 | 21.89 | 26.89 | 82.25 | 79.81 | 30.01 | 6.37 | 5.25 | 6.61 | 0.68 | 0.28 | 3.97 |  | 70.83% | 2.44 | 3.21 | 51.02 | 0.29149 | 0.93607 | 7.33 | 81.342 | 252.76 | 95.6121 | 1998-11-06
1998-12-06 | 16:00:00pm | 615.43 | 233.53 | 120.91 | 15.11 | 24.33 | 29.33 | 72.33 | 69.89 | 29.52 | 6.07 | 5.27 | 6.35 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.44 | 3.21 | 41.59 | 0.29149 | 0.86062 | 7.555 | 72.546 | 186.824 | 94.1743 | 1998-12-06 | 750 | 5.4 |  |  |  | 185 |  | 100 |  | 2100 |  | 600 |  | 450 |  | 4 | 91 | 229 | 12.82 | 134.19 | 251.84 | 0.31201 | 0.67814 | 0.90931 | 97.5
13/6/98 | 16:00:00pm | 639.43 | 261 | 125.03 | 14.2 | 25.37 | 30.37 | 73.25 | 70.35 | 30.07 | 6.06 | 5.26 | 6.33 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 41.73 | 0.29149 | 0.83068 | 7.1 | 75.018 | 208.8 | 94.9968 | 13/6/98
14/6/98 | 16:00:00pm | 663.43 | 242.69 | 127.32 | 12.82 | 25 | 30 | 73.4 | 70.65 | 29.8 | 6.03 | 5.26 | 6.35 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 42.225 | 0.29149 | 0.84119 | 6.41 | 76.392 | 194.152 | 95.2614 | 14/6/98
15/6/98 | 16:00:00pm | 684.43 | 306.79 | 124.12 | 15.11 | 26.1 | 31.1 | 72.94 | 70.5 | 29.31 | 6.05 | 5.26 | 6.36 | 0.68 | 0.11 | 4.08 |  | 86.08% | 2.44 | 3.21 | 42.41 | 0.29149 | 0.81041 | 7.555 | 74.472 | 245.432 | 95.2767 | 15/6/98
16/6/98 | 16:00:00pm | 711.43 | 311.37 | 132.36 | 16.03 | 25.72 | 30.72 | 74.47 | 71.72 | 29.62 | 6.35 | 5.29 | 6.62 | 0.68 | 0.11 | 4.08 |  | 86.08% | 2.75 | 3.21 | 43.475 | 0.29149 | 0.82089 | 8.015 | 79.416 | 249.096 | 95.1204 | 16/6/98 | 810 | 3.5 |  |  |  | 135 |  | 1100 |  | 15350 |  | 2565 |  | 3850 |  | 9 | 223 | 400 | 14.66 | 130.07 | 315.95 | 0.61392 | 1.7145 | 1.266 | 97.1108
17/6/98 | 16:00:00pm | 723.93 | 320.53 | 127.78 | 15.57 | 25.46 | 30.46 | 72.79 | 70.35 | 31.11 | 6.22 | 5.25 | 6.45 | 0.73 | 0.23 | 3.87 |  | 76.04% | 2.44 | 3.21 | 40.46 | 0.29149 | 0.82815 | 7.785 | 76.668 | 256.424 | 95.3256 | 17/6/98
18/6/98 | 16:00:00pm | 747.93 | 288.48 | 127.78 | 12.82 | 26.79 | 31.79 | 72.79 | 70.35 | 31.11 | 6.22 | 5.32 | 6.47 | 0.73 | 0.17 | 3.97 |  | 81.11% | 2.44 | 3.21 | 40.46 | 0.29149 | 0.7918 | 6.41 | 76.668 | 230.784 | 95.8302 | 18/6/98
19/6/98 | 16:00:00pm | 771.93 | 238.11 | 125.95 | 12.82 | 25.55 | 30.55 | 73.1 | 70.2 | 30.59 | 6.14 | 5.25 | 6.33 | 0.68 | 0.34 | 3.97 |  | 66.67% | 2.9 | 3.21 | 41.06 | 0.29149 | 0.82563 | 6.41 | 75.57 | 190.488 | 95.1815 | 19/6/98 | 720 | 3.7 | 77.5
20/6/98 | 16:00:00pm | 795.93 | 256.42 | 129.61 | 13.74 | 26.16 | 31.16 | 73.1 | 70.35 | 30.26 | 6.19 | 5.28 | 6.43 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.75 | 3.21 | 41.465 | 0.29149 | 0.80877 | 6.87 | 77.766 | 205.136 | 95.1432 | 20/6/98
21/6/98 | 16:00:00pm | 819.93 | 279.32 | 128.24 | 13.74 | 27.17 | 32.17 | 72.33 | 69.74 | 29.65 | 6.12 | 5.27 | 6.38 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.59 | 3.21 | 41.385 | 0.29149 | 0.78176 | 6.87 | 76.944 | 223.456 | 95.4261 | 21/6/98
22/6/98 | 08:30:00am | 836.43 | 242.69 | 124.58 | 10.53 | 26.36 | 31.36 | 72.18 | 69.43 | 29.22 | 6.1 | 5.25 | 6.35 | 0.68 | 0.28 | 3.87 |  | 70.83% | 2.75 | 3.21 | 41.585 | 0.29149 | 0.80334 | 5.265 | 74.748 | 194.152 | 96.084 | 22/6/98
22/6/98 | 19:00:00pm | 839.2633 | 247.27 | 123.66 | 16.95 | 26.57 | 31.57 | 71.26 | 68.82 | 31.29 | 6.13 | 5.14 | 6.33 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.44 | 3.21 | 38.75 | 0.29149 | 0.79768 | 8.475 | 74.196 | 197.816 | 93.7687 | 22/6/98
23/6/98 | 16:00:00pm | 860.2633 | 279.32 | 125.95 | 14.2 | 27.15 | 32.15 | 72.18 | 70.35 | 32.21 | 6.27 | 5.33 | 6.47 | 0.68 | 0.17 | 3.97 |  | 80% | 1.83 | 3.21 | 39.055 | 0.29149 | 0.78229 | 7.1 | 75.57 | 223.456 | 95.2512 | 23/6/98 | 759 | 5.5 |  |  |  | 3720 |  | 47300 |  | 13300 |  | 950 |  | 4900 |  | 10 | 20 | 294 | 16.49 | 127.78 | 261 | 0.60643 | 0.15652 | 1.1264 | 93.6306
24/6/98 | 16:00:00pm | 884.2633 | 215.21 | 122.29 | 13.28 | 26.47 | 31.47 | 72.18 | 69.74 | 31.32 | 6.16 | 5.3 | 6.43 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.44 | 3.21 | 39.64 | 0.29149 | 0.80037 | 6.64 | 73.374 | 172.168 | 94.5916 | 24/6/98
25/6/98 | 16:00:00pm | 908.2633 | 228.95 | 120 | 13.74 | 27.49 | 32.49 | 72.33 | 69.74 | 31.51 | 6.16 | 5.3 | 6.39 | 0.73 | 0.17 | 4.08 |  | 81.11% | 2.59 | 3.21 | 39.525 | 0.29149 | 0.77343 | 6.87 | 72 | 183.16 | 94.6151 | 25/6/98 | 750 | 4.6 | 30.2 |  |  | 30 |  | 100 |  | 1350 |  | <100 |  | 700 |  | 12 | 64 | 312 | 15.11 | 119.08 | 256.42 | 0.79418 | 0.53745 | 1.2168 | 93.617
26/6/98 | 09:30:00am | 925.7633 | 238.11 | 115.87 | 14.2 | 26.24 | 31.24 | 72.03 | 69.43 | 30.53 | 6.13 | 5.33 | 6.36 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.6 | 3.21 | 40.2 | 0.29149 | 0.8066 | 7.1 | 69.522 | 190.488 | 94.5387 | 26/6/98
27/6/98 | 16:00:00pm | 931.0967 | 251.84 | 122.74 | 19.24 | 28.56 | 33.56 | 70.5 | 68.21 | 32.76 | 6.23 | 5.38 | 6.53 | 0.73 | 0.11 | 4.08 |  | 86.9% | 2.29 | 3.21 | 36.595 | 0.29149 | 0.74634 | 9.62 | 73.644 | 201.472 | 93.0066 | 27/6/98 | 1311 |  | 39
28/6/98 | 16:00:00pm | 955.0967 | 261 | 120.45 | 15.11 | 27.81 | 32.81 | 71.26 | 69.74 | 32.12 | 6.11 | 5.33 | 6.36 | 0.68 | 0.23 | 4.08 |  | 74.73% | 1.52 | 3.21 | 38.38 | 0.29149 | 0.76521 | 7.555 | 72.27 | 208.8 | 94.6241 | 28/6/98
29/6/98 | 16:00:00pm | 979.0967 | 279.32 | 125.95 | 16.03 | 27.47 | 32.47 | 71.26 | 68.98 | 31.51 | 6.18 | 5.33 | 6.48 | 0.68 | 0.17 | 4.18 |  | 80% | 2.28 | 3.21 | 38.61 | 0.29149 | 0.77395 | 8.015 | 75.57 | 223.456 | 94.6393 | 29/6/98
30/6/98 | 16:00:00pm | 1003.0967 | 288.48 | 127.78 | 15.11 | 28.62 | 33.62 | 70.65 | 68.52 | 31.41 | 6.15 | 5.23 | 6.41 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.13 | 3.21 | 38.175 | 0.29149 | 0.74485 | 7.555 | 76.668 | 230.784 | 95.0854 | 30/6/98 | 7:00 | 4.3 |  |  |  | TNTC |  | 1850 |  | 59150 |  | 2750 |  | 4900 |  | 10 | 71 | 294 | 15.11 | 126.41 | 279.32 | 0.66181 | 0.56166 | 1.0526 | 94.5205
1998-01-07 | 16:00:00pm | 1026.7967 | 224.37 | 112.67 | 16.49 | 28.53 | 33.53 | 69.43 | 66.99 | 31.23 | 5.83 | 5.25 | 6.07 | 0.68 | 0.28 | 3.97 |  | 70.83% | 2.44 | 3.21 | 36.98 | 0.29149 | 0.74708 | 8.245 | 67.602 | 179.496 | 93.3265 | 1998-01-07 | 1700
1998-02-07 | 16:00:00pm | 1050.7967 | 206.05 | 107.17 | 16.03 | 28.48 | 33.48 | 70.65 | 68.06 | 29.86 | 5.8 | 5.21 | 6.09 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.59 | 3.21 | 39.495 | 0.29149 | 0.74832 | 8.015 | 64.302 | 164.84 | 93.0043 | 1998-02-07 | 7:00 |  |  |  |  | 195 |  | 450 |  | 2500 |  | <10 |  | 3500 |  | 8 | 24 | 158 | 12.82 | 107.63 | 210.63 | 0.62402 | 0.22299 | 0.75013 | 91.2088
1998-03-07 | 16:00:00pm | 1074.7967 | 224.37 | 114.04 | 17.4 | 28.14 | 33.14 | 70.2 | 67.45 | 28.12 | 6.19 | 5.27 | 6.45 | 0.68 | 0.17 | 4.08 |  | 80% | 2.75 | 3.21 | 40.705 | 0.29149 | 0.75684 | 8.7 | 68.424 | 179.496 | 92.9816 | 1998-03-07
1998-04-07 | 16:00:00pm | 1098.7967 | 288.48 | 104.88 | 23.36 | 28.13 | 33.13 | 69.59 | 66.84 | 28.03 | 5.94 | 5.43 | 6.41 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 40.185 | 0.29149 | 0.75709 | 11.68 | 62.928 | 230.784 | 92.0466 | 1998-04-07
1998-05-07 | 16:00:00pm | 1122.7967 | 251.84 | 113.13 | 16.03 | 27.6 | 32.6 | 69.13 | 66.23 | 26.23 | 6.36 | 5.29 | 6.58 | 0.68 | 0.17 | 4.08 |  | 80% | 2.9 | 3.21 | 41.45 | 0.29149 | 0.77059 | 8.015 | 67.878 | 201.472 | 94.0486 | 1998-05-07
1998-06-07 | 22:00:00pm | 1135.8967 | 196.9 | 108.55 | 13.28 | 27.11 | 32.11 | 70.35 | 67.45 | 30.38 | 6.08 | 5.28 | 6.35 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 38.52 | 0.29149 | 0.78334 | 6.64 | 65.13 | 157.52 | 94.0355 | 1998-06-07
1998-07-07 | 16:00:00pm | 1153.8967 | 233.53 | 106.26 | 14.66 | 27.03 | 32.03 | 70.35 | 67.6 | 30.07 | 5.79 | 5.21 | 6.01 | 0.68 | 0.28 | 4.18 |  | 70.83% | 2.75 | 3.21 | 38.905 | 0.29149 | 0.78544 | 7.33 | 63.756 | 186.824 | 94.1496 | 1998-07-07 | 7:00 |  | FP |  |  | 2280 |  | 20300 |  | 33600 |  | 2100 |  | 9150 |  | 5 | 62 | 210 | 13.74 | 102.13 | 183.16 | 0.3639 | 0.60707 | 1.1465 | 96.3235
1998-08-07 | 16:00:00pm | 1178.6467 | 215.21 | 105.34 | 14.2 | 26.98 | 31.98 | 73.4 | 70.2 | 29.89 | 5.79 | 5.2 | 6.06 | 0.73 | 0.28 | 4.08 |  | 72.28% | 3.2 | 3.21 | 41.91 | 0.29149 | 0.78676 | 7.1 | 63.204 | 172.168 | 93.967 | 1998-08-07
1998-09-07 | [21 empty] | 0.29149 | [5 empty] | 1998-09-07 | 7:00 | 4.8 |  |  |  | 2455 |  | 13000 |  | 28100 |  | 2575 |  | 7050 |  | 5 | 79 | 237 | 14.2 | 100.3 | 228.95 | 0.35211 | 0.78764 | 1.0352 | 96.8354 | ALARM
1998-09-07 | 16:00:00pm | 1202.6467 | 224.37 | 105.34 | 16.03 | 27.82 | 32.82 | 74.77 | 71.87 | 31.41 | 5.83 | 5.23 | 6.08 | 0.68 | 0.17 | 4.08 |  | 80% | 2.9 | 3.21 | 41.91 | 0.29149 | 0.76495 | 8.015 | 63.204 | 179.496 | 93.3951 | 1998-09-07 | 900 | [14 empty] | 10 | 70 | 260 | 15.11 | 104.88 | 247.27 | 0.66181 | 0.66743 | 1.0515 | 93.9394 | outside lab
1998-10-07 | 16:00:00pm | 1226.6467 | 279.32 | 102.13 | 14.66 | 28.13 | 33.13 | 77.52 | 74.93 | 32.67 | 5.85 | 5.24 | 6.08 | 0.73 | 0.17 | 3.97 |  | 81.11% | 2.59 | 3.21 | 43.555 | 0.29149 | 0.75709 | 7.33 | 61.278 | 223.456 | 94.8513 | 1998-10-07
1998-11-07 | 16:00:00pm | 1250.6467 | 210.63 | 99.84 | 14.2 | 27.92 | 32.92 | 73.86 | 71.57 | 30.23 | 5.86 | 5.28 | 6.14 | 0.68 | 0.28 | 3.97 |  | 70.83% | 2.29 | 3.21 | 42.485 | 0.29149 | 0.76241 | 7.1 | 59.904 | 168.504 | 93.7831 | 1998-11-07
1998-12-07 | 16:00:00pm | 1274.6467 | 297.63 | 102.59 | 17.4 | 29.41 | 34.41 | 74.62 | 72.03 | 30.29 | 6.06 | 5.34 | 6.32 | 0.68 | 0.11 | 4.08 |  | 86.08% | 2.59 | 3.21 | 43.035 | 0.29149 | 0.72562 | 8.7 | 61.554 | 238.104 | 94.1934 | 1998-12-07
13/7/98 | 16:00:00pm | 1298.6467 | 238.11 | 100.3 | 14.2 | 28.45 | 33.45 | 74.47 | 70.65 | 28.85 | 5.89 | 5.29 | 6.15 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.82 | 3.21 | 43.71 | 0.29149 | 0.74907 | 7.1 | 60.18 | 190.488 | 94.3351 | 13/7/98
14/7/98 | 16:00:00pm | 1322.6467 | 233.53 | 102.13 | 13.74 | 28.21 | 33.21 | 79.81 | 76.3 | 30.84 | 5.91 | 5.3 | 6.14 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.51 | 3.21 | 47.215 | 0.29149 | 0.75507 | 6.87 | 61.278 | 186.824 | 94.462 | 14/7/98 | 805 | 4.8 | 30.7 |  |  | 890 |  | 200 |  | 2350 |  | 30 |  | 250 |  |  |  | 229 |  |  | 206.05 |  |  | 1.1114 | 100
15/7/98 | 16:00:00pm | 1346.6467 | 247.27 | 100.76 | 12.82 | 28.02 | 33.02 | 81.03 | 77.37 | 30.04 | 5.93 | 5.27 | 6.24 | 0.63 | 0.17 | 4.08 |  | 78.75% | 3.66 | 3.21 | 49.16 | 0.29149 | 0.75987 | 6.41 | 60.456 | 197.816 | 95.0362 | 15/7/98
16/7/98 | 9:00:00am | 1364.1467 | 265.58 | 100.3 | 14.66 | 27.72 | 32.72 | 85.76 | 82.1 | 31.48 | 5.87 | 5.27 | 6.09 | 0.73 | 0.28 | 3.97 |  | 72.28% | 3.66 | 3.21 | 52.45 | 0.29149 | 0.76751 | 7.33 | 60.18 | 212.464 | 94.623 | 16/7/98 | 6:24 |  | FP |  |  | 130 |  | 5050 |  | 6150 |  | 30 |  | 300 |  | 9 | 70 | 222 | 15.11 | 99.84 | 270.16 | 0.59563 | 0.70112 | 0.82174 | 93.8356
17/7/98 | 15:30:00pm | 1382.47 | 288.48 | 98.93 | 16.03 | 28.19 | 33.19 | 77.98 | 74.77 | 30.9 | 6.11 | 5.3 | 6.35 | 0.73 | 0.11 | 4.08 |  | 86.9% | 3.21 | 3.21 | 45.475 | 0.29149 | 0.75558 | 8.015 | 59.358 | 230.784 | 94.4751 | 17/7/98
18/7/98 | 15:00:00pm | 1405.97 | 215.21 | 95.26 | 13.28 | 29.24 | 34.24 | 76.61 | 73.86 | 30.62 | 6.01 | 5.28 | 6.26 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.75 | 3.21 | 44.615 | 0.29149 | 0.72971 | 6.64 | 57.156 | 172.168 | 94.2091 | 18/7/98
19/7/98 | 15:30:00pm | 1430.47 | 256.42 | 96.18 | 10.99 | 30.39 | 35.39 | 76.15 | 72.94 | 30.29 | 5.99 | 5.33 | 6.27 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.21 | 3.21 | 44.255 | 0.29149 | 0.70259 | 5.495 | 57.708 | 205.136 | 95.8188 | 19/7/98
20/7/98 | 16:00:00pm | 1454.47 | 265.58 | 98.93 | 11.91 | 30.4 | 35.4 | 75.69 | 72.33 | 29.83 | 5.98 | 5.32 | 6.33 | 0.68 | 0.17 | 4.08 |  | 80% | 3.36 | 3.21 | 44.18 | 0.29149 | 0.70236 | 5.955 | 59.358 | 212.464 | 95.6185 | 20/7/98 | 1805 | 5.6
21/7/98 | 15:30:00pm | 1476 | 242.69 | 96.64 | 12.37 | 31.71 | 31.71 | 75.99 | 72.33 | 30.47 | 5.97 | 5.31 | 6.26 | 0.68 | 0.17 | 4.08 |  | 80% | 3.66 | 3.21 | 43.69 | 0.29149 | 0.67294 | 6.185 | 57.984 | 194.152 | 95.0939 | 21/7/98 | 6:30 | 4.6 |  |  |  | 250 |  | 2550 |  | 108400 |  | 1065 |  | 16600 |  | 15 | 74 | 227 | 12.82 | 99.84 | 265.58 | 1.17 | 0.74119 | 0.85473 | 90.0332
22/7/98 | 16:00:00pm | 1501 | 196.9 | 97.55 | 13.74 | 32.41 | 32.41 | 75.99 | 72.18 | 29.92 | 5.94 | 5.32 | 6.22 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.81 | 3.21 | 44.165 | 0.29149 | 0.65782 | 6.87 | 58.53 | 157.52 | 93.6404 | 22/7/98
23/7/98 | 16:00:00pm | 1525 | 242.69 | 99.39 | 11.91 | 32.43 | 32.43 | 75.84 | 71.72 | 29.55 | 5.99 | 5.33 | 6.24 | 0.63 | 0.23 | 4.08 |  | 73.26% | 4.12 | 3.21 | 44.23 | 0.29149 | 0.6574 | 5.955 | 59.634 | 194.152 | 95.3071 | 23/7/98 | 1100 | 5.4 | 35.2 |  |  | 308 |  | 390 |  | 1090 |  | <1 |  | 2490 |  |  | 62 | 179 |  | 98.47 | 233.53 |  | 0.62963 | 0.7665 | 100
[22 empty] | 0.29149 | [5 empty] | 23/7/98 | 7:00 |  |  |  |  | 240 |  | 100 |  | 2500 |  | 300 |  | 550 |  | 9 | 64 | 238 | 12.82 | 96.64 | 242.69 | 0.70203 | 0.66225 | 0.98067 | 94.0397
24/7/98 | 16:00:00pm | 1549 | 265.58 | 100.76 | 14.66 | 31.74 | 31.74 | 74.77 | 71.72 | 28.82 | 5.94 | 5.35 | 6.23 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.05 | 3.21 | 44.425 | 0.29149 | 0.67228 | 7.33 | 60.456 | 212.464 | 94.6285 | 24/7/98
25/7/98 | 16:00:00pm | 1573 | 238.11 | 97.55 | 12.37 | 31.22 | 31.22 | 76.45 | 72.79 | 28.85 | 6.04 | 5.34 | 6.31 | 0.63 | 0.17 | 3.97 |  | 78.75% | 3.66 | 3.21 | 45.77 | 0.29149 | 0.68377 | 6.185 | 58.53 | 190.488 | 95.0325 | 25/7/98
26/7/98 | 16:00:00pm | 1597 | 210.63 | 101.68 | 10.99 | 30.15 | 30.15 | 76.76 | 73.1 | 27.72 | 5.98 | 5.3 | 6.28 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.66 | 3.21 | 47.21 | 0.29149 | 0.70815 | 5.495 | 61.008 | 168.504 | 95.2116 | 26/7/98
27/7/98 | 16:00:00pm | 1621 | 238.11 | 97.1 | 14.66 | 30.29 | 30.29 | 76.91 | 73.55 | 27.33 | 5.98 | 5.32 | 6.25 | 0.63 | 0.17 | 3.97 |  | 78.75% | 3.36 | 3.21 | 47.9 | 0.29149 | 0.7049 | 7.33 | 58.26 | 190.488 | 94.1065 | 27/7/98
28/7/98 | 16:00:00pm | 1645 | 251.84 | 99.84 | 11.45 | 30.66 | 30.66 | 76.3 | 73.1 | 27.02 | 5.92 | 5.34 | 6.2 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.2 | 3.21 | 47.68 | 0.29149 | 0.6964 | 5.725 | 59.904 | 201.472 | 95.6193 | 28/7/98 | 7:30 | 5.4 |  |  |  | 160 |  | 1950 |  | 1750 |  | 1770 |  | 3050 |  | 5 | 71 | 218 | 10.08 | 98.01 | 219.79 | 0.49603 | 0.72442 | 0.99186 | 96.5398
29/7/98 | 16:00:00pm | 1669 | 210.63 | 96.64 | 10.99 | 31.83 | 31.83 | 86.83 | 82.86 | 30.23 | 5.99 | 5.37 | 6.32 | 0.73 | 0.28 | 4.08 |  | 72.28% | 3.97 | 3.21 | 54.615 | 0.29149 | 0.67032 | 5.495 | 57.984 | 168.504 | 95.1476 | 29/7/98
30/7/98 | 16:00:00pm | 1693 | 247.27 | 96.64 | 11.45 | 32.98 | 32.98 | 87.9 | 83.78 | 29.92 | 5.99 | 5.4 | 6.27 | 0.73 | 0.23 | 4.08 |  | 76.04% | 4.12 | 3.21 | 55.92 | 0.29149 | 0.64582 | 5.725 | 57.984 | 197.816 | 95.5238 | 30/7/98 | 8:00 | 5.1 | 33 |  |  | 5 |  | 800 |  | TNTC |  | 150 |  | 1600 |  |  | 55 | 213 |  | 99.84 | 251.84 |  | 0.55088 | 0.84578 | 100
31/7/98 | 16:00:00pm | 1717 | 283.9 | 96.18 | 11.45 | 30.78 | 30.78 | 88.97 | 84.85 | 29.22 | 6.23 | 5.39 | 6.52 | 0.68 | 0.11 | 4.08 |  | 86.08% | 4.12 | 3.21 | 57.69 | 0.29149 | 0.69367 | 5.725 | 57.708 | 227.12 | 95.98 | 31/7/98
1998-01-08 | 15:30:00pm | 1741 | 256.42 | 100.76 | 10.99 | 30.61 | 30.61 | 93.39 | 89.42 | 30.35 | 5.9 | 5.35 | 6.12 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.97 | 3.21 | 61.055 | 0.29149 | 0.69754 | 5.495 | 60.456 | 205.136 | 95.8621 | 1998-01-08
1998-02-08 | 16:00:00pm | 1765 | 270.16 | 101.22 | 13.74 | 29.36 | 29.36 | 97.51 | 93.85 | 30.62 | 6.04 | 5.37 | 6.32 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.66 | 3.21 | 65.06 | 0.29149 | 0.72682 | 6.87 | 60.732 | 216.128 | 95.0372 | 1998-02-08
1998-03-08 | 16:00:00pm | 1789 | 219.79 | 97.1 | 11.91 | 29.12 | 29.12 | 96.44 | 92.78 | 28.73 | 6.01 | 5.33 | 6.33 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.66 | 3.21 | 65.88 | 0.29149 | 0.73261 | 5.955 | 58.26 | 175.832 | 94.9123 | 1998-03-08
1998-04-08 | 16:00:00pm | 1813 | 238.11 | 100.76 | 10.99 | 28.98 | 28.98 | 96.9 | 92.48 | 27.27 | 6.05 | 5.33 | 6.33 | 0.68 | 0.23 | 3.87 |  | 74.73% | 4.42 | 3.21 | 67.42 | 0.29149 | 0.73601 | 5.495 | 60.456 | 190.488 | 95.6205 | 1998-04-08 | 7:00 | 4.8 | 33.2 |  |  | 275 |  | 7200 |  | 4200 |  | 12050 |  | 6450 |  | 12 | 32 | 225 | 10.99 | 99.39 | 219.79 | 1.0919 | 0.32196 | 1.0237 | 90.6615
1998-05-08 | 16:00:00pm | 1837 | 256.42 | 102.59 | 13.28 | 29.27 | 29.27 | 95.53 | 91.71 | 25.22 | 6.01 | 5.37 | 6.27 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.82 | 3.21 | 68.4 | 0.29149 | 0.72899 | 6.64 | 61.554 | 205.136 | 95.0204 | 1998-05-08
1998-06-08 | 14:30:00pm | 1859 | 256.42 | 95.26 | 10.99 | 29.22 | 29.22 | 108.04 | 103.92 | 29.8 | 6.09 | 5.38 | 6.39 | 0.73 | 0.23 | 4.08 |  | 76.04% | 4.12 | 3.21 | 76.18 | 0.29149 | 0.73019 | 5.495 | 57.156 | 205.136 | 95.81 | 1998-06-08 | 7:00 |  |  |  |  | 95 |  | 3800 |  | 1650 |  | 10350 |  | 19650 |  | 5 | 74 | 166 | 8.24 | 98.01 | 265.58 | 0.6068 | 0.75502 | 0.62505 | 95.8333
1998-07-08 | 16:00:00pm | 1860 | 270.16 | 97.55 | 11.91 | 27.91 | 27.91 | 72.33 | 69.89 | 31.41 | 6.09 | 5.28 | 6.38 | 0.73 | 0.17 | 3.97 |  | 81.11% | 2.44 | 3.21 | 39.7 | 0.29149 | 0.76266 | 5.955 | 58.53 | 216.128 | 95.6637 | 1998-07-08
1998-08-08 | 16:00:00pm | 1884 | 297.63 | 99.39 | 13.28 | 29.22 | 29.22 | 72.64 | 69.89 | 30.13 | 6.19 | 5.37 | 6.52 | 0.73 | 0.11 | 4.08 |  | 86.9% | 2.75 | 3.21 | 41.135 | 0.29149 | 0.73019 | 6.64 | 59.634 | 238.104 | 95.5397 | 1998-08-08
1998-09-08 | 16:00:00pm | 1908 | 187.74 | 99.84 | 8.7 | 29.65 | 29.65 | 70.35 | 67.45 | 28.58 | 5.99 | 5.35 | 6.31 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 40.32 | 0.29149 | 0.7199 | 4.35 | 59.904 | 150.192 | 95.859 | 1998-09-08
1998-10-08 | 16:00:00pm | 1932 | 261 | 97.55 | 11.91 | 29.96 | 29.96 | 72.03 | 69.43 | 28.61 | 6 | 5.38 | 6.32 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.6 | 3.21 | 42.12 | 0.29149 | 0.71259 | 5.955 | 58.53 | 208.8 | 95.5448 | 1998-10-08
1998-11-08 | 16:00:00pm | 1944 | 265.58 | 100.76 | 12.37 | 30.28 | 30.28 | 73.25 | 69.89 | 33.7 | 6.06 | 5.45 | 6.37 | 0.63 | 0.23 | 4.08 |  | 73.26% | 3.36 | 3.21 | 37.87 | 0.29149 | 0.70513 | 6.185 | 60.456 | 212.464 | 95.4675 | 1998-11-08
1998-12-08 | 16:00:00pm | 1968 | 196.9 | 98.47 | 14.2 | 30.86 | 30.86 | 73.4 | 69.89 | 33.85 | 5.98 | 5.45 | 6.3 | 0.58 | 0.17 | 3.97 |  | 77.33% | 3.51 | 3.21 | 37.795 | 0.29149 | 0.69185 | 7.1 | 59.082 | 157.52 | 93.4442 | 1998-12-08
13/8/98 | 16:00:00pm | 1990 | 256.42 | 100.3 | 13.74 | 30.9 | 30.9 | 74.93 | 71.11 | 30.23 | 6.15 | 5.45 | 6.49 | 0.73 | 0.17 | 4.08 |  | 81.11% | 3.82 | 3.21 | 42.79 | 0.29149 | 0.69095 | 6.87 | 60.18 | 205.136 | 94.8213 | 13/8/98 | 7:00 | 5.4 |  |  |  | 10725 |  | 4550 |  | 7750 |  | 18900 |  | 4050 |  | 2 | 19 | 199 | 11.91 | 102.59 | 174 | 0.16793 | 0.1852 | 1.1437 | 98.1651
14/8/98 | 16:00:00pm | 2014 | 137.37 | 100.76 | 10.53 | 29.85 | 29.85 | 75.54 | 72.33 | 29.34 | 6.04 | 5.42 | 6.27 | 0.73 | 0.28 | 4.08 |  | 72.28% | 3.21 | 3.21 | 44.595 | 0.29149 | 0.71517 | 5.265 | 60.456 | 109.896 | 93.8187 | 14/8/98
15/8/98 | 16:00:00pm | 2038 | 251.84 | 104.42 | 12.82 | 29.47 | 29.47 | 74.93 | 71.11 | 27.11 | 6.14 | 5.42 | 6.42 | 0.73 | 0.23 | 4.08 |  | 76.04% | 3.82 | 3.21 | 45.91 | 0.29149 | 0.72419 | 6.41 | 62.652 | 201.472 | 95.1462 | 15/8/98
16/8/98 | 16:00:00pm | 2062 | 256.42 | 105.34 | 12.37 | 29.73 | 29.73 | 75.84 | 70.96 | 28.24 | 6.16 | 5.46 | 6.45 | 0.68 | 0.28 | 4.08 |  | 70.83% | 4.88 | 3.21 | 45.16 | 0.29149 | 0.718 | 6.185 | 63.204 | 205.136 | 95.3902 | 16/8/98
17/8/98 | 16:00:00pm | 2086 | 261 | 100.76 | 12.37 | 30.81 | 30.81 | 75.99 | 70.65 | 27.72 | 6.2 | 5.51 | 6.52 | 0.63 | 0.23 | 4.08 |  | 73.26% | 5.34 | 3.21 | 45.6 | 0.29149 | 0.69299 | 6.185 | 60.456 | 208.8 | 95.4059 | 17/8/98
18/8/98 | 16:00:00pm | 2110 | 306.79 | 128.24 | 11.91 | 32.23 | 32.23 | 81.79 | 77.52 | 30.59 | 7.58 | 6.28 | 7.87 | 0.68 | 0.28 | 3.87 |  | 70.83% | 4.27 | 3.21 | 49.065 | 0.29149 | 0.66167 | 5.955 | 76.944 | 245.432 | 96.3056 | 18/8/98 | 7:00 | 5.3 |  |  |  | 100 |  | 1250 |  | 2150 |  | 11750 |  | 9800 |  | 15 | 75 | 153 | 12.37 | 102.13 | 261 | 1.2126 | 0.73436 | 0.58621 | 86.8421
19/8/98 | 9:30:00am | 2127 | 315.95 | 131.9 | 12.37 | 30.63 | 30.63 | 86.68 | 82.86 | 30.74 | 8.03 | 8.59 | 8.3 | 0.73 | 0.23 | 3.97 | 2127 | 76.04% | 3.82 | 3.21 | 54.03 | 0.29149 | 0.69708 | 6.185 | 79.14 | 252.76 | 96.273 | 19/8/98
20/8/98 | 16:00:00pm | 2148 | 293.06 | 125.49 | 13.28 | 29.53 | 29.53 | 72.03 | 68.98 | 30.23 | 7.9 | 7.96 | 8.15 | 0.73 | 0.28 | 4.08 |  | 72.28% | 3.05 | 3.21 | 40.275 | 0.29149 | 0.72275 | 6.64 | 75.294 | 234.448 | 95.7126 | 20/8/98 | 7:00 |  |  |  |  | 100 |  | 4250 |  | <100 |  | 1725 |  | 9900 |  | 11 | 66 | 178 | 9.16 | 130.99 | 242.69 | 1.2009 | 0.50386 | 0.73345 | 90.9836
21/8/98 | 16:00:00pm | 2172 | 352.58 | 134.19 | 13.74 | 29.54 | 29.54 | 71.87 | 69.59 | 30.77 | 7.97 | 8.22 | 8.24 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.28 | 3.21 | 39.96 | 0.29149 | 0.72252 | 6.87 | 80.514 | 282.064 | 96.2105 | 21/8/98
22/8/98 | 16:00:00pm | 2196 | 306.79 | 132.36 | 13.28 | 30.28 | 30.28 | 72.03 | 70.2 | 30.68 | 8.03 | 8.52 | 8.28 | 0.73 | 0.23 | 3.97 |  | 76.04% | 1.83 | 3.21 | 40.435 | 0.29149 | 0.70513 | 6.64 | 79.416 | 245.432 | 95.9119 | 22/8/98
23/8/98 | 16:00:00pm | 2220 | 375.48 | 134.65 | 16.03 | 30.84 | 30.84 | 72.33 | 69.74 | 30.5 | 8.19 | 8.99 | 8.42 | 0.73 | 0.17 | 3.97 |  | 81.11% | 2.59 | 3.21 | 40.535 | 0.29149 | 0.69231 | 8.015 | 80.79 | 300.384 | 95.7946 | 23/8/98
24/8/98 | 16:00:00pm | 2244 | 352.58 | 130.53 | 16.49 | 31.12 | 31.12 | 72.18 | 68.67 | 29.92 | 8.51 | 9.3 | 8.78 | 0.73 | 0.23 | 3.97 |  | 76.04% | 3.51 | 3.21 | 40.505 | 0.29149 | 0.686 | 8.245 | 78.318 | 282.064 | 95.4243 | 24/8/98
25/8/98 | 16:00:00pm | 2268 | 329.69 | 136.03 | 13.74 | 30.92 | 30.92 | 71.72 | 68.98 | 30.13 | 8.09 | 8.84 | 8.32 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.74 | 3.21 | 40.22 | 0.29149 | 0.6905 | 6.87 | 81.618 | 263.752 | 96.0217 | 25/8/98 | 7:00 | 5.1 | 31.3 |  |  | 10 |  | 2950 |  | 650 |  | 2350 |  | 40000 |  | 11 | 60 | 247 | 14.66 | 139.69 | 256.42 | 0.75034 | 0.42952 | 0.96326 | 92.8339
26/8/98 | 16:00:00pm | 2286 | 371.845 | 139.69 | 31.6 | 31.05 | 31.05 | 69.89 | 67.3 | 29.95 | 9.15 | 9.83 | 9.42 | 0.68 | 0.28 | 4.08 |  | 70.83% | 2.59 | 3.21 | 38.645 | 0.29149 | 0.68757 | 15.8 | 83.814 | 297.476 | 91.7123 | 26/8/98
27/8/98 | 16:00:00pm | 2306.5 | 285.302 | 127.32 | 11.45 | 28.83 | 28.83 | 65.92 | 63.48 | 27.88 | 7.44 | 6.39 | 7.64 | 0.63 | 0.23 | 3.97 |  | 73.26% | 2.44 | 3.21 | 36.82 | 0.29149 | 0.73968 | 5.725 | 76.392 | 228.2416 | 96.2414 | 27/8/98 | 7:00 | 4.5 | 30.1 |  |  | 10 |  | 300 |  | 1750 |  | 3500 |  | 2300 |  | 8 | 44 | 280 | 25.19 | 138.77 | 296.261 | 0.31759 | 0.31707 | 0.94511 | 95.0617
28/8/98 | 16:00:00pm | 2326 | 389.245 | 145.64 | 17.4 | 29.71 | 29.71 | 71.26 | 68.52 | 29.95 | 8.21 | 9.28 | 8.54 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.74 | 3.21 | 39.94 | 0.29149 | 0.71848 | 8.7 | 87.384 | 311.396 | 95.6367 | 28/8/98
29/8/98 | 16:00:00pm | 2353 | 387.414 | 138.77 | 21.98 | 31.25 | 31.25 | 71.11 | 68.98 | 31.05 | 8.7 | 9.58 | 8.94 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.13 | 3.21 | 38.995 | 0.29149 | 0.6831 | 10.99 | 83.262 | 309.9312 | 94.4099 | 29/8/98
30/8/98 | 16:00:00pm | 2377 | 342.54 | 126.41 | 10.53 | 30.28 | 30.28 | 70.5 | 67.6 | 30.87 | 7.76 | 7.05 | 8.09 | 0.68 | 0.28 | 4.08 |  | 70.83% | 2.9 | 3.21 | 38.18 | 0.29149 | 0.70513 | 5.265 | 75.846 | 274.032 | 96.9904 | 30/8/98
31/8/98 | 16:00:00pm | 2400 | 358.566 | 138.77 | 10.08 | 30.6 | 30.6 | 71.26 | 68.82 | 30.23 | 7.84 | 5.99 | 7.57 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.44 | 3.21 | 39.81 | 0.29149 | 0.69777 | 5.04 | 83.262 | 286.8528 | 97.2765 | 31/8/98
1998-01-09 | 16:00:00pm | 2423 | 389.673 | 126.87 | 13.74 | 29.94 | 29.94 | 72.18 | 70.2 | 32.57 | 7.75 | 7.59 | 8.13 | 0.68 | 0.23 | 3.97 |  | 74.73% | 1.98 | 3.21 | 38.62 | 0.29149 | 0.71306 | 6.87 | 76.122 | 311.7384 | 96.4575 | 1998-01-09 | 7:51 | 4 | 65.5 | 2.6 | 41.8 | 945 |  | 3550 |  | 3100 |  | 39400 |  | 12000 |  | 12 | 117 | 283 | 11.91 | 119.54 | 272.45 | 1.0076 | 0.97875 | 1.0387 | 94
1998-02-09 | 16:00:00pm | 2447 | 380.973 | 126.87 | 13.28 | 29.96 | 29.96 | 72.18 | 69.43 | 31.38 | 7.79 | 7.35 | 8.18 | 0.73 | 0.23 | 3.97 |  | 76.04% | 2.75 | 3.21 | 39.425 | 0.29149 | 0.71259 | 6.64 | 76.122 | 304.7784 | 96.5135 | 1998-02-09
1998-03-09 | 16:00:00pm | 2471 | 239.024 | 114.96 | 8.7 | 30.52 | 30.52 | 66.23 | 63.33 | 28.55 | 7.22 | 6.76 | 7.59 | 0.63 | 0.17 | 4.08 |  | 78.75% | 2.9 | 3.21 | 36.23 | 0.29149 | 0.6996 | 4.35 | 68.976 | 191.2192 | 96.6564 | 1998-03-09 | 7:39 | 5 |  | 3.1 | 41.6 | 35 |  | <100 |  | 2850 |  | 14500 |  | 14650 |  | 3 | 63 | 274 | 39.39 | 151.14 | 424.931 | 0.076161 | 0.41683 | 0.64481 | 98.2196
1998-04-09 | 16:00:00pm | 2495 | 358.536 | 128.7 | 12.82 | 29.07 | 29.07 | 74.32 | 71.57 | 30.87 | 8.22 | 9.12 | 8.59 | 0.68 | 0.28 | 3.97 |  | 70.83% | 2.75 | 3.21 | 42.075 | 0.29149 | 0.73383 | 6.41 | 77.22 | 286.8288 | 96.4785 | 1998-04-09
1998-05-09 | 16:00:00pm | 2519 | 382.346 | 131.9 | 14.66 | 29.15 | 29.15 | 74.01 | 71.26 | 30.9 | 8.13 | 8.98 | 8.41 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.75 | 3.21 | 41.735 | 0.29149 | 0.73189 | 7.33 | 79.14 | 305.8768 | 96.1924 | 1998-05-09
1998-06-09 | 16:00:00pm | 2543 | 375.478 | 128.24 | 16.95 | 29.86 | 29.86 | 74.16 | 71.42 | 31.05 | 8.15 | 9.15 | 8.5 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.74 | 3.21 | 41.74 | 0.29149 | 0.71494 | 8.475 | 76.944 | 300.3824 | 95.5079 | 1998-06-09
1998-07-09 | 16:00:00pm | 2567 | 387.383 | 127.78 | 16.49 | 30.95 | 30.95 | 73.25 | 70.04 | 30.71 | 8.25 | 9.16 | 8.54 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.21 | 3.21 | 40.935 | 0.29149 | 0.68982 | 8.245 | 76.668 | 309.9064 | 95.7343 | 1998-07-09
1998-08-09 | 16:30:00pm | 2592 | 343.96 | 103.05 | 14.2 | 28.38 | 28.38 | 75.08 | 71.72 | 30.96 | 6.48 | 5.68 | 6.87 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.36 | 3.21 | 42.44 | 0.29149 | 0.75082 | 7.1 | 61.83 | 275.168 | 95.7863 | 1998-08-09 | 7:56 | 3.4 | 30 | 2.2 | 38.8 | 50 |  | 1550 |  | <100 |  | 1500 |  | 4850 |  | 10 | 68 | 294 | 14.2 | 122.29 | 402.036 | 0.70423 | 0.55606 | 0.73128 | 94.4751
1998-09-09 | 16:00:00pm | 2615 | 261.52 | 123.2 | 9.62 | 26.38 | 26.38 | 73.71 | 70.65 | 29.83 | 7.68 | 6.47 | 7.94 | 0.73 | 0.23 | 4.08 |  | 76.04% | 3.06 | 3.21 | 42.35 | 0.29149 | 0.8028 | 4.81 | 73.92 | 209.216 | 96.6023 | 1998-09-09
1998-10-09 | 16:00:00pm | 2639 | 359.07 | 125.49 | 14.66 | 27.06 | 27.06 | 75.54 | 72.94 | 29.89 | 8.06 | 8.99 | 8.34 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.6 | 3.21 | 44.35 | 0.29149 | 0.78465 | 7.33 | 75.294 | 287.256 | 95.9564 | 1998-10-09 | 7:14 | 4.4 | 32.5 | 2.8 | 31 | 20 |  | 23800 |  | 650 |  | 2700 |  | 2850 |  | 12 | 114 | 153 | 10.53 | 126.87 | 319.23 | 1.1396 | 0.89856 | 0.47928 | 91.0112
1998-11-09 | 16:00:00pm | 2650 | 364.57 | 127.78 | 14.2 | 27.56 | 27.56 | 74.32 | 72.03 | 30.19 | 7.99 | 8.97 | 8.34 | 0.73 | 0.23 | 4.18 |  | 76.04% | 2.29 | 3.21 | 42.985 | 0.29149 | 0.77162 | 7.1 | 76.668 | 291.656 | 96.1447 | 1998-11-09
1998-12-09 | 16:00:00pm | 2674 | 391.59 | 122.29 | 13.74 | 27.85 | 27.85 | 74.62 | 72.03 | 30.16 | 8.18 | 9.1 | 8.49 | 0.68 | 0.17 | 4.08 |  | 80% | 2.59 | 3.21 | 43.165 | 0.29149 | 0.76419 | 6.87 | 73.374 | 313.272 | 96.4464 | 1998-12-09
13/9/98 | 16:00:00pm | 2698 | 429.15 | 122.29 | 13.74 | 28.31 | 28.31 | 75.99 | 72.33 | 29.98 | 7.92 | 8.73 | 8.3 | 0.73 | 0.17 | 4.08 |  | 81.11% | 3.66 | 3.21 | 44.18 | 0.29149 | 0.75257 | 6.87 | 73.374 | 343.32 | 96.7026 | 13/9/98
14/9/98 | 16:00:00pm | 2722 | 338.92 | 125.49 | 12.82 | 28.58 | 28.58 | 74.32 | 71.11 | 29.31 | 8.21 | 9.18 | 8.53 | 0.68 | 0.28 | 3.97 |  | 70.83% | 3.21 | 3.21 | 43.405 | 0.29149 | 0.74584 | 6.41 | 75.294 | 271.136 | 96.2994 | 14/9/98
15/9/98 | 16:00:00pm | 2746 | 382.43 | 129.61 | 13.74 | 28.54 | 28.54 | 74.62 | 71.72 | 29.1 | 8.06 | 9.09 | 8.4 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 44.07 | 0.29149 | 0.74683 | 6.87 | 77.766 | 305.944 | 96.4192 | 15/9/98 | 6:40 | 4.5 | 42.2 | 3.1 | 33.7 | 3095 |  | 74000 |  | 3900 |  | 49400 |  | 85250
16/9/98 | 16:00:00pm | 2770 | 373.27 | 126.87 | 14.2 | 29.47 | 29.47 | 74.77 | 72.03 | 31.66 | 7.98 | 8.87 | 8.33 | 0.68 | 0.17 | 4.08 |  | 80% | 2.74 | 3.21 | 41.74 | 0.29149 | 0.72419 | 7.1 | 76.122 | 298.616 | 96.2107 | 16/9/98
17/9/98 | 16:00:00pm | 2794 | 356.32 | 125.95 | 10.99 | 29.19 | 29.19 | 77.52 | 74.62 | 31.41 | 7.85 | 8.24 | 8.19 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.9 | 3.21 | 44.66 | 0.29149 | 0.73092 | 5.495 | 75.57 | 285.056 | 96.9525 | 17/9/98 | 8:30 | 4.2 | 30.3 | 3.4 | 25 | 1500 |  | 5700 |  | 2700 |  | 5950 |  | 12550 |  | 12 | 86 | 245 | 5.95 | 141.06 | 316.94 | 2.0168 | 0.60967 | 0.77302 | 92.7492
18/9/98 | 16:00:00pm | 2817 | 327.93 | 132.36 | 16.03 | 28.7 | 28.7 | 73.71 | 71.11 | 30.59 | 8.36 | 9.24 | 8.71 | 0.68 | 0.28 | 4.08 |  | 70.83% | 2.6 | 3.21 | 41.82 | 0.29149 | 0.74288 | 8.015 | 79.416 | 262.344 | 95.3096 | 18/9/98
19/9/98 | 16:00:00pm | 2841 | 352.66 | 137.4 | 12.82 | 28.17 | 28.17 | 74.93 | 71.87 | 30.1 | 8 | 8.81 | 8.35 | 0.63 | 0.28 | 4.08 |  | 69.23% | 3.06 | 3.21 | 43.3 | 0.29149 | 0.75608 | 6.41 | 82.44 | 282.128 | 96.4835 | 19/9/98
20/9/98 | 16:00:00pm | 2865 | 363.65 | 135.11 | 12.37 | 28.6 | 28.6 | 74.47 | 71.87 | 30.71 | 8.07 | 8.94 | 8.45 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.6 | 3.21 | 42.46 | 0.29149 | 0.74535 | 6.185 | 81.066 | 290.92 | 96.6746 | 20/9/98
21/9/98 | 16:00:00pm | 2889 | 351.29 | 131.9 | 13.74 | 29.3 | 29.3 | 73.4 | 70.96 | 30.74 | 7.94 | 8.87 | 8.29 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.44 | 3.21 | 41.44 | 0.29149 | 0.72826 | 6.87 | 79.14 | 281.032 | 96.1852 | 21/9/98
22/9/98 | 16:00:00pm | 2913 | 356.32 | 132.36 | 12.82 | 29.16 | 29.16 | 74.32 | 71.57 | 31.32 | 8.01 | 8.85 | 8.34 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 41.625 | 0.29149 | 0.73164 | 6.41 | 79.416 | 285.056 | 96.4826 | 22/9/98 | 7:04 | 5.2 | FP |  |  | 380 |  | 2850 |  | 36450 |  | 11500 |  | 17000 |  | 7 | 71 | 277 | 13.28 | 134.65 | 357.7 | 0.52711 | 0.52729 | 0.77439 | 95.977
23/9/98 | 16:00:00pm | 2937 | 347.62 | 127.78 | 12.37 | 27.25 | 27.25 | 75.54 | 72.79 | 31.81 | 8.17 | 9.1 | 8.49 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.75 | 3.21 | 42.355 | 0.29149 | 0.77967 | 6.185 | 76.668 | 278.096 | 96.5132 | 23/9/98
24/9/98 | 16:00:00pm | 2961 | 340.29 | 129.16 | 10.99 | 27.39 | 27.39 | 76.76 | 74.47 | 30.99 | 8.07 | 8.95 | 8.39 | 0.73 | 0.28 | 4.08 |  | 72.28% | 2.29 | 3.21 | 44.625 | 0.29149 | 0.77603 | 5.495 | 77.496 | 272.232 | 96.8576 | 24/9/98 | 7:10 | 6.4 | 14.3 |  |  | 355 |  | 15000 |  | 34500 |  | 93750 |  | 4500 |  | 21 | 82 | 150 | 10.08 | 106.71 | 308.69 | 2.0833 | 0.76844 | 0.48592 | 81.8966
25/9/98 | 16:00:00pm | 2985 | 351.29 | 132.36 | 11.91 | 27.42 | 27.42 | 76.76 | 74.01 | 30.74 | 7.93 | 8.8 | 8.34 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.75 | 3.21 | 44.645 | 0.29149 | 0.77525 | 5.955 | 79.416 | 281.032 | 96.6958 | 25/9/98
26/9/98 | 16:00:00pm | 3008 | 293.58 | 124.58 | 9.62 | 27.44 | 27.44 | 76.61 | 74.16 | 30.71 | 7.03 | 5.97 | 7.3 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.45 | 3.21 | 44.675 | 0.29149 | 0.77473 | 4.81 | 74.748 | 234.864 | 96.8929 | 26/9/98
27/9/98 | 16:00:00pm | 3025 | 380.14 | 129.16 | 15.11 | 28.96 | 28.96 | 76.15 | 73.55 | 31.9 | 8.3 | 9.23 | 8.64 | 0.73 | 0.17 | 4.18 |  | 81.11% | 2.6 | 3.21 | 42.95 | 0.29149 | 0.7365 | 7.555 | 77.496 | 304.112 | 96.0404 | 27/9/98
28/9/98 | 16:30:00pm | 3049 | 331.59 | 127.32 | 13.28 | 28.61 | 28.61 | 76.61 | 73.71 | 31.54 | 8.15 | 9.12 | 8.47 | 0.73 | 0.28 | 4.18 |  | 72.28% | 2.9 | 3.21 | 43.62 | 0.29149 | 0.7451 | 6.64 | 76.392 | 265.272 | 96.1131 | 28/9/98
29/9/98 | 16:00:00pm | 3073 | 362.28 | 131.9 | 11.91 | 28.23 | 28.23 | 75.84 | 73.4 | 30.26 | 8.15 | 9.1 | 8.54 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.44 | 3.21 | 44.36 | 0.29149 | 0.75457 | 5.955 | 79.14 | 289.824 | 96.772 | 29/9/98 | 8:40 | 4.2 |  |  |  | 55 |  | 900 |  | 32550 |  | 300 |  | 33500 |  | 10 | 53 | 244 | 17.4 | 132.82 | 349.91 | 0.57471 | 0.39904 | 0.69732 | 93.266
30/9/98 | 16:00:00pm | 3097 | 374.64 | 127.78 | 12.37 | 27.94 | 27.94 | 75.38 | 73.1 | 29.19 | 8.15 | 9.09 | 8.52 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.28 | 3.21 | 45.05 | 0.29149 | 0.7619 | 6.185 | 76.668 | 299.712 | 96.7134 | 30/9/98
1998-01-10 | 16:00:00pm | 3121 | 356.32 | 131.45 | 13.28 | 28.43 | 28.43 | 76.15 | 73.1 | 30.87 | 7.96 | 8.85 | 8.39 | 0.73 | 0.23 | 3.97 |  | 76.04% | 3.05 | 3.21 | 43.755 | 0.29149 | 0.74957 | 6.64 | 78.87 | 285.056 | 96.3509 | 1998-01-10 | [5 empty] | 10 |  | 850 |  | 42500 |  | 2500 |  | 28500 |  | 3 | 75 | 292 | 13.28 | 131.9 | 381.97 | 0.2259 | 0.56861 | 0.76446 | 98.3651
[28 empty] | 1998-01-10 | [15 empty] | 14 | 85
1998-02-10 | 16:00:00pm | 3145 | 350.83 | 139.23 | 16.95 | 26.37 | 26.37 | 76.91 | 74.16 | 30.62 | 8.66 | 9.59 | 9.12 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 44.915 | 0.29149 | 0.80307 | 8.475 | 83.538 | 280.664 | 95.346 | 1998-02-10
1998-03-10 | 16:00:00pm | 3169 | 343.96 | 128.24 | 11.45 | 26.17 | 26.17 | 77.22 | 74.16 | 30.74 | 7.91 | 8.62 | 8.32 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.06 | 3.21 | 44.95 | 0.29149 | 0.8085 | 5.725 | 76.944 | 275.168 | 96.7482 | 1998-03-10
1998-04-10 | 16:00:00pm | 3193 | 348.54 | 129.61 | 10.99 | 24.92 | 24.92 | 76.61 | 74.01 | 29.74 | 7.98 | 8.94 | 8.42 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.6 | 3.21 | 45.57 | 0.29149 | 0.84348 | 5.495 | 77.766 | 278.832 | 96.9181 | 1998-04-10
1998-05-10 | 16:00:00pm | 3217 | 363.65 | 132.36 | 12.82 | 23.88 | 23.88 | 77.06 | 74.32 | 29.07 | 8.4 | 9.35 | 8.76 | 0.63 | 0.17 | 4.08 |  | 78.75% | 2.74 | 3.21 | 46.62 | 0.29149 | 0.87397 | 6.41 | 79.416 | 290.92 | 96.5383 | 1998-05-10
1998-06-10 | 16:00:00pm | 3241 | 363.65 | 131.45 | 10.08 | 24.89 | 24.89 | 77.52 | 74.62 | 29.49 | 7.95 | 8.85 | 8.34 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 46.58 | 0.29149 | 0.84434 | 5.04 | 78.87 | 290.92 | 97.2741 | 1998-06-10 | 9:05 | 5.9 |  |  |  | 27 |  | 2300 |  | 62500 |  | 250 |  | 2000 |  | 4 | 104 |  | 10.08 | 130.99 | 361.82 | 0.39683 | 0.79395 |  | 92.3077
1998-07-10 | 16:00:00pm | 3265 | 382.43 | 132.82 | 13.28 | 25.09 | 25.09 | 75.99 | 73.25 | 25.83 | 8.42 | 9.3 | 8.81 | 0.68 | 0.17 | 4.08 |  | 80% | 2.74 | 3.21 | 48.79 | 0.29149 | 0.83862 | 6.64 | 79.692 | 305.944 | 96.5563 | 1998-07-10
1998-08-10 | 16:00:00pm | 3289 | 403.04 | 136.03 | 12.37 | 24.51 | 24.51 | 77.06 | 72.94 | 26.57 | 8.15 | 9.07 | 8.56 | 0.68 | 0.23 | 4.08 |  | 74.73% | 4.12 | 3.21 | 48.43 | 0.29149 | 0.85535 | 6.185 | 81.618 | 322.432 | 96.9385 | 1998-08-10 | 7:22 | 6.6 |  |  |  | 11 |  | 4200 |  | 54000 |  | 15100 |  | 2400 |  | 14 | 74 | 275 | 7.79 | 128.24 | 329.76 | 1.7972 | 0.57704 | 0.83394 | 91.9771
1998-09-10 | 16:00:00pm | 3311 | 353.58 | 120 | 8.7 | 23.65 | 23.65 | 80.27 | 78.13 | 30.93 | 7.94 | 8.55 | 8.16 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.14 | 3.21 | 48.27 | 0.29149 | 0.88089 | 4.35 | 72 | 282.864 | 97.5484 | 1998-09-10
1998-10-10 | 16:00:00pm | 3335 | 329.76 | 116.79 | 11.45 | 23.13 | 23.13 | 80.11 | 77.52 | 31.51 | 8.19 | 8.92 | 8.44 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.59 | 3.21 | 47.305 | 0.29149 | 0.89678 | 5.725 | 70.074 | 263.808 | 96.5706 | 1998-10-10
1998-11-10 | 03:30:00am | 3347 | 339.38 | 117.25 | 19.69 | 22.94 | 22.94 | 79.5 | 76.76 | 31.14 | 8.91 | 9.54 | 9.21 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.74 | 3.21 | 46.99 | 0.29149 | 0.90267 | 9.845 | 70.35 | 271.504 | 94.2402 | 1998-11-10
1998-12-10 | 16:00:00pm | 3351 | 330.22 | 106.71 | 5.04 | 22.94 | 22.94 | 77.22 | 75.23 | 30.07 | 7.71 | 8.38 | 8.06 | 0.73 | 0.23 | 4.08 |  | 76.04% | 1.99 | 3.21 | 46.155 | 0.29149 | 0.90267 | 2.52 | 64.026 | 264.176 | 98.4644 | 1998-12-10
13/10/98 | 16:00:00pm | 3375 | 361.82 | 108.55 | 8.7 | 23.29 | 23.29 | 77.22 | 74.93 | 30.1 | 8.08 | 8.87 | 8.32 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.29 | 3.21 | 45.975 | 0.29149 | 0.89186 | 4.35 | 65.13 | 289.456 | 97.5464 | 13/10/98 | 7:30 | 4.3 | 61.3 |  |  | 537 |  | 3850 |  | 388500 |  | 50500 |  | 34600 |  | 5 | 72 | 279 | 9.16 | 108.55 | 346.25 | 0.54585 | 0.66329 | 0.80578 | 97.151
14/10/98 | 16:00:00pm | 3399 | 297.24 | 106.71 | 8.7 | 23.41 | 23.41 | 77.22 | 74.16 | 29.58 | 7.94 | 8.64 | 8.2 | 0.73 | 0.23 | 4.08 |  | 76.04% | 3.06 | 3.21 | 46.11 | 0.29149 | 0.88818 | 4.35 | 64.026 | 237.792 | 97.1175 | 14/10/98
15/10/98 | 16:00:00pm | 3423 | 312.36 | 109.92 | 8.24 | 22.75 | 22.75 | 77.83 | 75.23 | 30.9 | 8.08 | 8.83 | 8.34 | 0.63 | 0.23 | 3.97 |  | 73.26% | 2.6 | 3.21 | 45.63 | 0.29149 | 0.90861 | 4.12 | 65.952 | 249.888 | 97.3911 | 15/10/98 | 7:00 |  | 36 |  |  | 9 |  | 5900 |  | 31500 |  | 3000 |  | 31200 |  | 9 | 80 | 262 | 9.62 | 110.84 | 321.52 | 0.93555 | 0.72176 | 0.81488 | 94.7368
16/10/98 | 16:00:00pm | 3447 | 327.47 | 111.75 | 12.37 | 22.34 | 22.34 | 78.28 | 75.23 | 30.65 | 8.24 | 8.89 | 8.56 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.05 | 3.21 | 46.105 | 0.29149 | 0.92158 | 6.185 | 67.05 | 261.976 | 96.2404 | 16/10/98
17/10/98 | 16:00:00pm | 3471 | 331.59 | 109.92 | 6.41 | 22.26 | 22.26 | 77.67 | 75.54 | 30.44 | 7.93 | 8.51 | 8.2 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.13 | 3.21 | 46.165 | 0.29149 | 0.92414 | 3.205 | 65.952 | 265.272 | 98.0648 | 17/10/98
18/10/98 | 16:00:00pm | 3495 | 291.75 | 112.67 | 8.24 | 22.34 | 22.34 | 76.76 | 74.62 | 29.74 | 8.26 | 8.87 | 8.51 | 0.63 | 0.28 | 4.08 |  | 69.23% | 2.14 | 3.21 | 45.95 | 0.29149 | 0.92158 | 4.12 | 67.602 | 233.4 | 97.2625 | 18/10/98
19/10/98 | 16:00:00pm | 3519 | 331.59 | 104.42 | 7.79 | 23.09 | 23.09 | 87.29 | 82.4 | 29.25 | 7.64 | 7.65 | 7.93 | 0.83 | 0.28 | 4.7 |  | 74.77% | 4.89 | 3.21 | 55.595 | 0.29149 | 0.89802 | 3.895 | 62.652 | 265.272 | 97.6244 | 19/10/98
20/10/98 | 16:00:00pm | 3543 | 313.27 | 110.38 | 9.16 | 22.92 | 22.92 | 81.49 | 78.13 | 29.46 | 8.24 | 8.88 | 8.5 | 0.68 | 0.28 | 3.97 |  | 70.83% | 3.36 | 3.21 | 50.35 | 0.29149 | 0.90329 | 4.58 | 66.228 | 250.616 | 97.109 | 20/10/98 |  | 5.4 |  |  |  | 468 |  | 29500 |  | 2250 |  | 26200 |  | 17600 |  | 6 | 76 | 292 | 11.45 | 113.13 | 352.66 | 0.52402 | 0.67179 | 0.82799 | 96.7391
21/10/98 | 16:00:00pm | 3567 | 331.59 | 112.21 | 10.53 | 20.6 | 20.6 | 84.08 | 81.18 | 30.44 | 8.16 | 8.79 | 8.42 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 52.19 | 0.29149 | 0.97916 | 5.265 | 67.326 | 265.272 | 96.834 | 21/10/98
22/10/98 | 16:00:00pm | 3591 | 353.12 | 118.62 | 17.4 | 19.93 | 19.93 | 84.08 | 81.64 | 30.23 | 8.89 | 9.37 | 9.09 | 0.68 | 0.17 | 4.08 |  | 80% | 2.44 | 3.21 | 52.63 | 0.29149 | 1.0025 | 8.7 | 71.172 | 282.496 | 95.0801 | 22/10/98 | 6:58 | 4.7 | 36.3 |  |  | 116 |  | 5750 |  | 21500 |  | 36500 |  | 15500 |  | 9 | 70 | 265 | 9.16 | 109.46 | 345.33 | 0.98253 | 0.6395 | 0.76738 | 94.6269
23/10/98 | 16:00:00pm | 3600 | 406.7 | 111.29 | 10.53 | 19.43 | 19.43 | 84.08 | 81.64 | 29.95 | 8.02 | 8.62 | 8.24 | 0.68 | 0.17 | 4.08 |  | 80% | 2.44 | 3.21 | 52.91 | 0.29149 | 1.0203 | 5.265 | 66.774 | 325.36 | 97.3147 | 23/10/98
24/10/98 | 16:00:00pm | 3624 | 324.26 | 113.58 | 9.62 | 19.65 | 19.65 | 83.62 | 80.73 | 29.31 | 8.22 | 8.87 | 8.52 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.89 | 3.21 | 52.865 | 0.29149 | 1.0124 | 4.81 | 68.148 | 259.408 | 97.0631 | 24/10/98
25/10/98 | 16:00:00pm | 3648 | 380.6 | 124.58 | 8.7 | 19.47 | 19.47 | 87.9 | 84.85 | 29.92 | 8.11 | 8.65 | 8.27 | 0.73 | 0.23 | 3.97 |  | 76.04% | 3.05 | 3.21 | 56.455 | 0.29149 | 1.0189 | 4.35 | 74.748 | 304.48 | 97.7059 | 25/10/98
26/10/98 | 16:00:00pm | 3672 | 352.66 | 120.45 | 9.16 | 19.47 | 19.47 | 88.36 | 85.15 | 31.2 | 7.92 | 8.42 | 8.17 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.21 | 3.21 | 55.555 | 0.29149 | 1.0189 | 4.58 | 72.27 | 282.128 | 97.4153 | 26/10/98
27/10/98 | 16:00:00pm | 3696 | 350.37 | 121.37 | 10.99 | 18.94 | 18.94 | 88.05 | 85.76 | 30.32 | 8.33 | 8.93 | 8.52 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.29 | 3.21 | 56.585 | 0.29149 | 1.0381 | 5.495 | 72.822 | 280.296 | 96.8877 | 27/10/98 |  | 4.8 | 48.2 |  |  | 23 |  | 1650 |  | 105000 |  | 293500 |  | 6750 |  | 4 | 78 | 274
28/10/98 | 16:00:00pm | 3720 | 349.45 | 109.92 | 6.41 | 19.4 | 19.4 | 88.51 | 85.76 | 30.1 | 7.21 | 5.5 | 7.51 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.75 | 3.21 | 57.035 | 0.29149 | 1.0214 | 3.205 | 65.952 | 279.56 | 98.1448 | 28/10/98
29/10/98 | 16:00:00pm | 3745 | 301.82 | 109 | 6.87 | 19.27 | 19.27 | 93.09 | 90.19 | 30.9 | 7.83 | 8.18 | 8.05 | 0.73 | 0.28 | 4.08 |  | 72.28% | 2.9 | 3.21 | 60.74 | 0.29149 | 1.0261 | 3.435 | 65.4 | 241.456 | 97.7612 | 29/10/98 | 650 | 5.4 | 35.4 | 2.9 | 36.1 | 5 |  | 650 |  | 3500 |  | 2500 |  | 1300 |  | 2 | 57 | 261 | 5.95 | 107.63 | 329.76 | 0.33613 | 0.52959 | 0.79148
30/10/98 | 16:00:00pm | 3769 | 343.96 | 109.92 | 7.79 | 18.83 | 18.83 | 93.85 | 91.1 | 29.71 | 8.01 | 8.45 | 8.25 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 62.765 | 0.29149 | 1.0422 | 3.895 | 65.952 | 275.168 | 97.7163 | 30/10/98
31/10/98 | 16:00:00pm | 3793 | 344.42 | 111.75 | 7.33 | 19 | 19 | 97.51 | 94 | 32.91 | 8.06 | 8.58 | 8.27 | 0.68 | 0.23 | 4.18 |  | 74.73% | 3.51 | 3.21 | 62.845 | 0.29149 | 1.0359 | 3.665 | 67.05 | 275.536 | 97.8604 | 31/10/98
1998-01-11 | 16:00:00pm | 3817 | 305.03 | 111.29 | 8.24 | 18.28 | 18.28 | 96.9 | 93.54 | 30.47 | 8.33 | 8.82 | 8.57 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.36 | 3.21 | 64.75 | 0.29149 | 1.0628 | 4.12 | 66.774 | 244.024 | 97.3488 | 1998-01-11
1998-02-11 | 16:00:00pm | 3841 | 321.06 | 114.04 | 9.16 | 17.81 | 17.81 | 99.8 | 96.44 | 30.99 | 8.12 | 8.76 | 8.31 | 0.63 | 0.28 | 3.97 |  | 69.23% | 3.36 | 3.21 | 67.13 | 0.29149 | 1.0807 | 4.58 | 68.424 | 256.848 | 97.1839 | 1998-02-11
1998-03-11 | 16:00:00pm | 3865 | 324.26 | 113.58 | 7.79 | 18.45 | 18.45 | 99.5 | 96.9 | 29.68 | 8.09 | 8.53 | 8.28 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.6 | 3.21 | 68.52 | 0.29149 | 1.0563 | 3.895 | 68.148 | 259.408 | 97.6218 | 1998-03-11 | 825 | 5.4 | 10.4 | 2.7 | 33 | 14 |  | 1300 |  | 19950 |  | 37200 |  | 25700 |  | 12 | 80 | 165 | 3.21 | 105.8 | 305.03 | 3.7383 | 0.75614 | 0.54093
1998-04-11 | 16:00:00pm | 3889 | 325.64 | 118.16 | 6.41 | 18.63 | 18.63 | 100.11 | 97.21 | 29.83 | 8.01 | 8.42 | 8.22 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.9 | 3.21 | 68.83 | 0.29149 | 1.0496 | 3.205 | 70.896 | 260.512 | 98.0658 | 1998-04-11
1998-05-11 | 16:00:00pm | 3913 | 330.68 | 117.71 | 16.49 | 18.08 | 18.08 | 100.56 | 97.82 | 28.76 | 8.95 | 9.35 | 9.18 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.74 | 3.21 | 70.43 | 0.29149 | 1.0704 | 8.245 | 70.626 | 264.544 | 95.0801 | 1998-05-11 | 607 | 5 | 33.8 | 2.3 | 31.1 | 18 |  | 250 |  | 1250 |  | 1000 |  | 250 |  | 6 | 67 | 270 | 8.7 | 114.04 | 327.01 | 0.68966 | 0.58751 | 0.82566
1998-06-11 | 16:00:00pm | 3937 | 299.53 | 112.67 | 11.45 | 18.22 | 18.22 | 101.48 | 97.66 | 29.34 | 8.44 | 9.02 | 8.74 | 0.63 | 0.23 | 4.08 |  | 73.26% | 3.82 | 3.21 | 70.23 | 0.29149 | 1.065 | 5.725 | 67.602 | 239.624 | 96.2731 | 1998-06-11
1998-07-11 | 16:00:00pm | 3961 | 277.09 | 105.34 | 2.75 | 17.98 | 17.98 | 114.91 | 112.01 | 32.76 | 6.89 | 5.16 | 7.27 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.9 | 3.21 | 80.7 | 0.29149 | 1.0742 | 1.375 | 63.204 | 221.672 | 99.0347 | 1998-07-11
1998-08-11 | 16:00:00pm | 3985 | 308.69 | 106.71 | 5.04 | 17.35 | 17.35 | 122.23 | 119.49 | 30.74 | 7.13 | 5.41 | 7.51 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.74 | 3.21 | 90.12 | 0.29149 | 1.0986 | 2.52 | 64.026 | 246.952 | 98.3793 | 1998-08-11
1998-09-11 | 16:00:00pm | 4009 | 290.37 | 112.21 | 3.66 | 17.32 | 17.32 | 121.47 | 118.57 | 30.84 | 7.41 | 5.88 | 7.81 | 0.63 | 0.23 | 3.97 |  | 73.26% | 2.9 | 3.21 | 89.18 | 0.29149 | 1.0998 | 1.83 | 67.326 | 232.296 | 98.7785 | 1998-09-11
1998-10-11 | 16:00:00pm | 4033 | 305.49 | 115.42 | 6.87 | 17 | 17 | 127.73 | 124.98 | 31.32 | 8.23 | 8.85 | 8.52 | 0.63 | 0.28 | 4.08 |  | 69.23% | 2.75 | 3.21 | 95.035 | 0.29149 | 1.1125 | 3.435 | 69.252 | 244.392 | 97.8096 | 1998-10-11 | 618 | 3.8 | 41.2 | 2.5 | 31.4 | 24 |  | 6350 |  | 3550 |  | 28150 |  | 3950 |  | 35 | 102 | 288 | 6.41 | 118.16 | 301.36 | 5.4602 | 0.86324 | 0.95567
1998-11-11 | 16:00:00pm | 4057 | 303.65 | 116.79 | 7.79 | 17.12 | 17.12 | 127.57 | 124.22 | 30.01 | 8.31 | 9.04 | 8.62 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.35 | 3.21 | 95.885 | 0.29149 | 1.1077 | 3.895 | 70.074 | 242.92 | 97.5111 | 1998-11-11
1998-12-11 | 16:00:00pm | 4081 | 326.55 | 114.5 | 6.87 | 17.03 | 17.03 | 145.73 | 141.92 | 26.72 | 7.93 | 8.54 | 8.24 | 0.63 | 0.17 | 4.18 |  | 78.75% | 3.81 | 3.21 | 117.105 | 0.29149 | 1.1113 | 3.435 | 68.7 | 261.24 | 97.9178 | 1998-12-11 | 718 | 3.9 | 33.4 | 2.7 | 32.3 | 112 |  | 250 |  | 4100 |  | 2800 |  | 1250 |  | 17 | 60 | 284 | 5.5 | 115.42 | 369.61 | 3.0909 | 0.51984 | 0.76838
13/11/98 | 9:00:00am | 4098 | 317.39 | 116.33 | 5.04 | 16.57 | 16.57 | 163.13 | 160.08 | 27.82 | 8.26 | 8.95 | 8.57 | 0.68 | 0.28 | 3.97 |  | 70.83% | 3.05 | 3.21 | 133.785 | 0.29149 | 1.1299 | 2.52 | 69.798 | 253.912 | 98.4431 | 13/11/98
14/11/98 | 16:00:00pm | 4120 | 313.27 | 114.5 | 6.87 | 15.52 | 15.52 | 84.54 | 81.49 | 29.95 | 7.98 | 8.65 | 8.24 | 0.68 | 0.23 | 4.18 |  | 74.73% | 3.05 | 3.21 | 53.065 | 0.29149 | 1.1736 | 3.435 | 68.7 | 250.616 | 97.8485 | 14/11/98
15/11/98 | 16:00:00pm | 4144 | 303.65 | 114.04 | 6.41 | 15.92 | 15.92 | 87.9 | 84.85 | 31.84 | 7.72 | 8.25 | 8.01 | 0.68 | 0.28 | 3.97 |  | 70.83% | 3.05 | 3.21 | 54.535 | 0.29149 | 1.1567 | 3.205 | 68.424 | 242.92 | 97.9412 | 15/11/98
16/11/98 | 16:00:00pm | 4168 | 320.14 | 115.42 | 9.16 | 15.69 | 15.69 | 88.2 | 86.37 | 31.6 | 8.13 | 8.98 | 8.39 | 0.68 | 0.28 | 4.08 |  | 70.83% | 1.83 | 3.21 | 55.685 | 0.29149 | 1.1664 | 4.58 | 69.252 | 256.112 | 97.1847 | 16/11/98
17/11/98 | 16:00:00pm | 4192 | 319.23 | 109.92 | 5.04 | 16.62 | 16.62 | 87.9 | 85 | 31.9 | 7.96 | 8.64 | 8.23 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.9 | 3.21 | 54.55 | 0.29149 | 1.1278 | 2.52 | 65.952 | 255.384 | 98.4315 | 17/11/98 | 845 | 3.9 | 34.9 | 2.6 | 49.1 | 40 |  | 350 |  | 4100 |  | 19000 |  | 5700 |  |  |  |  | 12.82 | 117.71 | 322.89 | 0 | 0 | 0
18/11/98 | 16:00:00pm | 4216 | 326.1 | 111.29 | 9.62 | 16.04 | 16.04 | 88.2 | 85.61 | 31.72 | 8.37 | 9.16 | 8.73 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.59 | 3.21 | 55.185 | 0.29149 | 1.1517 | 4.81 | 66.774 | 260.88 | 97.064 | 18/11/98
19/11/98 | 16:00:00pm | 4240 | 329.76 | 113.58 | 8.24 | 16.85 | 16.85 | 87.29 | 85.61 | 31.05 | 8.28 | 9.04 | 8.63 | 0.68 | 0.23 | 3.97 |  | 74.73% | 1.68 | 3.21 | 55.4 | 0.29149 | 1.1185 | 4.12 | 68.148 | 263.808 | 97.5177 | 19/11/98 | 740 | 3.9 | 35.9 | 1.8 | 31.8 | 13 |  | 600 |  | 25150 |  | 25050 |  | 4700 |  | 10 | 63 | 274 | 4.58 | 112.67 | 332.05 | 2.1834 | 0.55916 | 0.82518
20/11/98 | 16:00:00pm | 4262 | 296.33 | 109 | 6.87 | 16.89 | 16.89 | 87.29 | 84.39 | 31.14 | 7.77 | 8.42 | 8.07 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.9 | 3.21 | 54.7 | 0.29149 | 1.1169 | 3.435 | 65.4 | 237.064 | 97.7287 | 20/11/98
21/11/98 | 16:00:00pm | 4286 | 299.99 | 106.71 | 4.12 | 16.85 | 16.85 | 88.05 | 85.91 | 31.2 | 7.86 | 8.48 | 8.14 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.14 | 3.21 | 55.78 | 0.29149 | 1.1185 | 2.06 | 64.026 | 239.992 | 98.6448 | 21/11/98
22/11/98 | 16:00:00pm | 4310 | 304.11 | 116.33 | 6.87 | 16.24 | 16.24 | 87.9 | 86.22 | 30.32 | 8.15 | 8.9 | 8.46 | 0.68 | 0.28 | 3.97 |  | 70.83% | 1.68 | 3.21 | 56.74 | 0.29149 | 1.1434 | 3.435 | 69.798 | 243.288 | 97.8057 | 22/11/98
23/11/98 | 16:00:00pm | 4334 | 313.27 | 115.42 | 7.79 | 16.31 | 16.31 | 97.36 | 95.68 | 34.22 | 7.99 | 8.69 | 8.28 | 0.73 | 0.23 | 4.08 |  | 76.04% | 1.68 | 3.21 | 62.3 | 0.29149 | 1.1405 | 3.895 | 69.252 | 250.616 | 97.5646 | 23/11/98
24/11/98 | 16:30:00pm | 4358 | 311.44 | 124.12 | 5.95 | 17.58 | 17.58 | 90.8 | 88.05 | 29.13 | 7.95 | 8.02 | 7.87 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.75 | 3.21 | 60.295 | 0.29149 | 1.0896 | 2.975 | 74.472 | 249.152 | 98.1614 | 24/11/98 | 655 | 5.1 | 35.1 | 2.2 | 32.7 | 6 |  | 50 |  | 450 |  | 800 |  | 550 |  | 10 | 59 | 230 | 4.12 | 108.55 | 312.81 | 2.4272 | 0.54353 | 0.73527
25/11/98 | 16:00:00pm | 4381 | 306.4 | 129.61 | 5.5 | 16.18 | 16.18 | 92.63 | 89.88 | 30.01 | 8.31 | 8.89 | 8.32 | 0.63 | 0.23 | 3.97 |  | 73.26% | 2.75 | 3.21 | 61.245 | 0.29149 | 1.1459 | 2.75 | 77.766 | 245.12 | 98.2966 | 25/11/98 | [5 empty] | 1 |  | 150 |  | 150 |  | 100 |  | 7300
26/11/98 | 16:00:00pm | 4405 | 320.6 | 130.53 | 5.95 | 16.86 | 16.86 | 93.7 | 90.64 | 29.86 | 8.29 | 8.87 | 8.26 | 0.63 | 0.28 | 4.08 |  | 69.23% | 3.06 | 3.21 | 62.31 | 0.29149 | 1.1181 | 2.975 | 78.318 | 256.48 | 98.2228 | 26/11/98
27/11/98 | 16:00:00pm | 4429 | 304.57 | 129.61 | 5.5 | 16.3 | 16.3 | 95.99 | 93.24 | 30.41 | 7.71 | 7.06 | 7.71 | 0.68 | 0.28 | 3.87 |  | 70.83% | 2.75 | 3.21 | 64.205 | 0.29149 | 1.1409 | 2.75 | 77.766 | 243.656 | 98.2889 | 27/11/98
28/11/98 | 16:00:00pm | 4453 | 321.52 | 130.07 | 5.5 | 16.44 | 16.44 | 96.29 | 93.39 | 29.77 | 7.97 | 8.33 | 8.01 | 0.68 | 0.28 | 4.08 |  | 70.83% | 2.9 | 3.21 | 65.07 | 0.29149 | 1.1352 | 2.75 | 78.042 | 257.216 | 98.3595 | 28/11/98
29/11/98 | 16:00:00pm | 4477 | 328.84 | 129.61 | 3.21 | 15.72 | 15.72 | 99.19 | 95.68 | 29.98 | 7.72 | 7.09 | 7.69 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.51 | 3.21 | 67.455 | 0.29149 | 1.1651 | 1.605 | 77.766 | 263.072 | 99.0582 | 29/11/98
30/11/98 | 16:00:00pm | 4501 | 316.02 | 130.99 | 6.87 | 16.28 | 16.28 | 100.87 | 97.36 | 30.84 | 7.88 | 7.78 | 7.85 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.51 | 3.21 | 68.275 | 0.29149 | 1.1417 | 3.435 | 78.594 | 252.816 | 97.927 | 30/11/98
1998-01-12 | 16:00:00pm | 4525 | 322.43 | 128.7 | 4.12 | 16.45 | 16.45 | 104.84 | 102.7 | 31.54 | 7.97 | 8 | 7.89 | 0.68 | 0.23 | 4.18 |  | 74.73% | 2.14 | 3.21 | 72.23 | 0.29149 | 1.1348 | 2.06 | 77.22 | 257.944 | 98.7708 | 1998-01-12 | 749 | 4.8 | 47 | 2.5 | 35 | 1 |  | 700 |  | 6450 |  | 40800 |  | 450 |  | 26 | 92 | 285 | 7.33 | 129.16 | 313.73 | 3.5471 | 0.71229 | 0.90842
1998-02-12 | 16:00:00pm | 4549 | 346.25 | 136.48 | 5.04 | 15.96 | 15.96 | 105.75 | 103.46 | 30.77 | 7.95 | 8.1 | 7.97 | 0.68 | 0.23 | 4.18 |  | 74.73% | 2.29 | 3.21 | 73.835 | 0.29149 | 1.155 | 2.52 | 81.888 | 277 | 98.5957 | 1998-02-12
1998-03-12 | 16:00:00pm | 4573 | 375.56 | 142.44 | 8.24 | 15.53 | 15.53 | 115.82 | 112.31 | 30.71 | 8.24 | 8.54 | 8.21 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.51 | 3.21 | 83.355 | 0.29149 | 1.1731 | 4.12 | 85.464 | 300.448 | 97.8648 | 1998-03-12 | 707 | 5.2 | 31 | 0.9 | 79.5 | 1 |  | 5550 |  | 13950 |  | 30000 |  | 1050 |  | 15 | 93 | 305 | 6.41 | 137.86 | 365.94 | 2.3401 | 0.6746 | 0.83347
1998-04-12 | 16:00:00pm | 4597 | 413.12 | 135.57 | 10.99 | 18.6 | 18.6 | 114.3 | 111.4 | 30.62 | 8.52 | 8.92 | 8.52 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 82.23 | 0.29149 | 1.0507 | 5.495 | 81.342 | 330.496 | 97.3315 | 1998-04-12
1998-05-12 | 16:00:00pm | 4621 | 395.25 | 135.57 | 5.95 | 16.31 | 16.31 | 114.91 | 111.7 | 27.79 | 8.1 | 8.4 | 8.1 | 0.63 | 0.23 | 4.08 |  | 73.26% | 3.21 | 3.21 | 85.515 | 0.29149 | 1.1405 | 2.975 | 81.342 | 316.2 | 98.5033 | 1998-05-12
1998-06-12 | 16:00:00pm | 4645 | 359.53 | 142.44 | 8.24 | 17.35 | 17.35 | 115.82 | 111.86 | 31.66 | 8.53 | 8.93 | 8.48 | 0.63 | 0.23 | 4.08 |  | 73.26% | 3.96 | 3.21 | 82.18 | 0.29149 | 1.0986 | 4.12 | 85.464 | 287.624 | 97.7914 | 1998-06-12
1998-07-12 | 16:00:00pm | 4669 | 329.76 | 135.11 | 5.04 | 17.76 | 17.76 | 117.96 | 113.99 | 31.81 | 7.96 | 7.96 | 7.92 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.97 | 3.21 | 84.165 | 0.29149 | 1.0826 | 2.52 | 81.066 | 263.808 | 98.5386 | 1998-07-12
1998-08-12 | 16:00:00pm | 4693 | 330.68 | 136.94 | 6.41 | 17.93 | 17.93 | 126.05 | 122.54 | 33.58 | 7.97 | 8.07 | 7.93 | 0.68 | 0.28 | 3.97 |  | 70.83% | 3.51 | 3.21 | 90.715 | 0.29149 | 1.0761 | 3.205 | 82.164 | 264.544 | 98.1512 | 1998-08-12 | 1037 | 4.7 | 37.8 |  |  | 1 |  | 1500 |  | 12000 |  | 64000 |  | 900 |  | 10 | 70 | 248 | 6.87 | 135.57 | 343.5 | 1.4556 | 0.51634 | 0.72198
1998-09-12 | 16:00:00pm | 4717 | 344.42 | 137.4 | 3.66 | 16.89 | 16.89 | 131.54 | 128.95 | 30.96 | 7.91 | 7.86 | 7.89 | 0.68 | 0.28 | 4.08 |  | 70.83% | 2.59 | 3.21 | 99.285 | 0.29149 | 1.1169 | 1.83 | 82.44 | 275.536 | 98.9776 | 1998-09-12
1998-10-12 | 16:00:00pm | 4741 | 478.15 | 141.98 | 8.24 | 17.11 | 17.11 | 145.12 | 141.31 | 31.14 | 8.48 | 8.95 | 8.39 | 0.68 | 0.17 | 3.97 |  | 80% | 3.81 | 3.21 | 112.075 | 0.29149 | 1.1081 | 4.12 | 85.188 | 382.52 | 98.2382 | 1998-10-12 | [5 empty] | 4 |  | 200 |  | 450 |  | 300 |  | 550 |  | 24 | 89 | 819 | [7 empty] | Increased to 95% recovery
1998-11-12 | 16:00:00pm | 4765 | 375.1 | 141.06 | 5.04 | 16.21 | 16.21 | 147.56 | 145.89 | 29.77 | 8.21 | 8.57 | 8.17 | 0.68 | 0.17 | 4.08 |  | 80% | 1.67 | 3.21 | 116.955 | 0.29149 | 1.1446 | 2.52 | 84.636 | 300.08 | 98.6899 | 1998-11-12
1998-12-12 | 16:30:00pm | 4790 | 368.23 | 144.27 | 5.95 | 16.4 | 16.4 | 159.31 | 155.65 | 28.4 | 7.95 | 5.99 | 7.73 | 0.73 | 0.23 | 4.08 |  | 76.04% | 3.66 | 3.21 | 129.08 | 0.29149 | 1.1368 | 2.975 | 86.562 | 294.584 | 98.4389 | 1998-12-12
13/12/98 | 16:00:00pm | 4813 | 309.61 | 129.16 | 2.75 | 16.98 | 16.98 | 159.77 | 155.96 | 28.21 | 7.26 | 5.39 | 7.29 | 0.63 | 0.23 | 3.97 |  | 73.26% | 3.81 | 3.21 | 129.655 | 0.29149 | 1.1133 | 1.375 | 77.496 | 247.688 | 99.1543 | 13/12/98
14/12/98 | 16:00:00pm | 4837 | 311.9 | 134.65 | 5.04 | 16.8 | 16.8 | 168.32 | 164.81 | 29.71 | 7.99 | 8.14 | 8.01 | 0.63 | 0.23 | 4.08 |  | 73.26% | 3.51 | 3.21 | 136.855 | 0.29149 | 1.1205 | 2.52 | 80.79 | 249.52 | 98.4742 | 14/12/98
15/12/98 | 9:30:00am | 4855 | 312.81 | 132.82 | 4.58 | 16.18 | 16.18 | 188 | 185.87 | 27.39 | 7.2 | 5.41 | 7.22 | 0.63 | 0.28 | 3.97 |  | 69.23% | 2.13 | 3.21 | 159.545 | 0.29149 | 1.1459 | 2.29 | 79.692 | 250.248 | 98.6119 | 15/12/98 | 826 | 3.8 | 36.1 | 2.8 | 28.3 | 20 |  | 300 |  | 550 |  | 800 |  | 5500 |  | 13 | 74 | 246 | 3.21 | 132.36 | 320.6 | 4.0498 | 0.55908 | 0.76731
16/12/98 | 16:00:00pm | 4876 | 238.16 | 119.08 | 5.5 | 16.9 | 13.9 | 92.63 | 90.19 | 29.83 | 8.36 | 9.08 | 8.55 | 0.68 | 0.4 | 3.76 |  | 62.96% | 2.44 | 3.21 | 61.58 | 0.29149 | 1.1165 | 2.75 | 71.448 | 190.528 | 97.9006 | 16/12/98
17/12/98 | 16:00:00pm | 4897 | 338 | 120.91 | 9.16 | 16.81 | 13.81 | 74.47 | 71.57 | 30.93 | 8.26 | 9.08 | 8.41 | 0.49 | 0.17 | 4.29 |  | 74.24% | 2.9 | 3.21 | 42.09 | 0.29149 | 1.1201 | 4.58 | 72.546 | 270.4 | 97.329 | 17/12/98 |  | 0.6 | 159.1 | 0.9 | 49.7 | 215 |  | 100 |  | 900 |  | 350 |  | 750 |  | 16 | 87 | 209
18/12/98 | 16:00:00pm | 4919 | 363.19 | 115.87 | 6.41 | 16.38 | 13.38 | 75.54 | 72.79 | 30.87 | 8.09 | 9 | 8.27 | 0.49 | 0.11 | 4.39 |  | 81.67% | 2.75 | 3.21 | 43.295 | 0.29149 | 1.1376 | 3.205 | 69.522 | 290.552 | 98.2198 | 18/12/98
19/12/98 | 16:00:00pm | 4943 | 368.23 | 119.54 | 7.33 | 16.02 | 13.02 | 74.77 | 72.03 | 30.41 | 8.06 | 8.95 | 8.3 | 0.49 | 0.11 | 4.39 |  | 81.67% | 2.74 | 3.21 | 42.99 | 0.29149 | 1.1525 | 3.665 | 71.724 | 294.584 | 97.999 | 19/12/98
20/12/98 | 16:00:00pm | 4967 | 321.97 | 122.29 | 8.7 | 16.7 | 13.7 | 74.32 | 71.87 | 31.08 | 8.29 | 9.18 | 8.54 | 0.49 | 0.11 | 4.29 |  | 81.67% | 2.45 | 3.21 | 42.015 | 0.29149 | 1.1246 | 4.35 | 73.374 | 257.576 | 97.3712 | 20/12/98
21/12/98 | 16:00:00pm | 4991 | 336.63 | 122.29 | 7.79 | 16.67 | 13.67 | 74.93 | 72.18 | 31.11 | 8.19 | 9.04 | 8.38 | 0.44 | 0.17 | 4.39 |  | 72.13% | 2.75 | 3.21 | 42.445 | 0.29149 | 1.1258 | 3.895 | 73.374 | 269.304 | 97.7267 | 21/12/98
22/12/98 | 16:00:00pm | 5015 | 374.64 | 127.78 | 10.99 | 16.32 | 13.32 | 74.77 | 72.64 | 31.26 | 8.26 | 9.12 | 8.46 | 0.49 | 0.11 | 4.39 |  | 81.67% | 2.13 | 3.21 | 42.445 | 0.29149 | 1.1401 | 5.495 | 76.668 | 299.712 | 97.0801 | 22/12/98 |  | FP |  | 3.6 | 37.5 | 20 |  | 200 |  | 800 |  | 200 |  | 400 |  | 2 | 65 | 263
23/12/98 | 16:00:00pm | 5039 | 376.48 | 124.12 | 8.7 | 15.04 | 12.04 | 75.08 | 71.87 | 30.35 | 8.32 | 9.04 | 8.39 | 0.44 | 0.11 | 4.39 |  | 80% | 3.21 | 3.21 | 43.125 | 0.29149 | 1.1942 | 4.35 | 74.472 | 301.184 | 97.6841 | 23/12/98
24/12/98 | 16:00:00pm | 5063 | 361.82 | 123.66 | 11.45 | 13.54 | 10.54 | 75.69 | 72.48 | 29.58 | 8.47 | 9.51 | 8.65 | 0.44 | 0.17 | 4.39 |  | 72.13% | 3.21 | 3.21 | 44.505 | 0.29149 | 1.2616 | 5.725 | 74.196 | 289.456 | 96.8514 | 24/12/98
25/12/98 | 16:00:00pm | 5087 | 322.43 | 121.37 | 5.04 | 13.91 | 10.91 | 75.69 | 72.48 | 30.23 | 7.84 | 8.35 | 7.94 | 0.44 | 0.17 | 4.39 |  | 72.13% | 3.21 | 3.21 | 43.855 | 0.29149 | 1.2446 | 2.52 | 72.822 | 257.944 | 98.4763 | 25/12/98
26/12/98 | 16:00:00pm | 5111 | 286.25 | 119.54 | 3.21 | 13.04 | 10.04 | 75.08 | 72.03 | 30.29 | 7.33 | 5.92 | 7.59 | 0.44 | 0.17 | 4.39 |  | 72.13% | 3.05 | 3.21 | 43.265 | 0.29149 | 1.285 | 1.605 | 71.724 | 229 | 98.9326 | 26/12/98
27/12/98 | 16:00:00pm | 5135 | 335.71 | 123.2 | 7.33 | 13.58 | 10.58 | 75.99 | 72.94 | 29.49 | 8.32 | 9.12 | 8.45 | 0.44 | 0.11 | 4.29 |  | 80% | 3.05 | 3.21 | 44.975 | 0.29149 | 1.2597 | 3.665 | 73.92 | 268.568 | 97.8598 | 27/12/98
28/12/98 | 16:00:00pm | 5159 | 344.87 | 125.49 | 8.24 | 13.64 | 10.64 | 75.54 | 72.79 | 29.07 | 8.31 | 9.15 | 8.44 | 0.44 | 0.06 | 4.39 |  | 88% | 2.75 | 3.21 | 45.095 | 0.29149 | 1.257 | 4.12 | 75.294 | 275.896 | 97.6537 | 28/12/98
29/12/98 | 16:00:00pm | 5183 | 356.78 | 120 | 5.04 | 13.27 | 10.27 | 83.78 | 81.18 | 30.84 | 8.12 | 8.86 | 8.24 | 0.49 | 0.11 | 4.39 |  | 81.67% | 2.6 | 3.21 | 51.64 | 0.29149 | 1.2742 | 2.52 | 72 | 285.424 | 98.5899 | 29/12/98 |  | FP |  |  |  | 2 |  | 850 |  | 22500 |  | 245 |  | 51000 |  | 7 | 76 | 324
30/12/98 | 16:00:00pm | 5207 | 322.43 | 118.16 | 5.04 | 12.71 | 9.71 | 84.24 | 80.73 | 31.02 | 8.23 | 9.02 | 8.41 | 0.49 | 0.17 | 4.39 |  | 74.24% | 3.51 | 3.21 | 51.465 | 0.29149 | 1.3008 | 2.52 | 70.896 | 257.944 | 98.4673 | 30/12/98
31/12/98 | 16:00:00pm | 5231 | 316.94 | 118.62 | 4.12 | 11.41 | 8.41 | 83.78 | 80.73 | 29.71 | 8.37 | 9.07 | 8.46 | 0.44 | 0.17 | 4.39 |  | 72.13% | 3.05 | 3.21 | 52.545 | 0.29149 | 1.3652 | 2.06 | 71.172 | 253.552 | 98.7312 | 31/12/98 |  | 5.2 |  | 3.5 |  | 5 |  | 100 |  | 24900 |  | <100 |  | 30550 |  | 3 | 67 | 272
1999-01-01 | 16:00:00pm | 5255 | 304.57 | 114.96 | 4.12 | 11.3 | 8.3 | 83.78 | 79.96 | 29.49 | 7.93 | 8.43 | 8.07 | 0.44 | 0.17 | 4.29 |  | 72.13% | 3.82 | 3.21 | 52.38 | 0.29149 | 1.3708 | 2.06 | 68.976 | 243.656 | 98.6822 | 1999-01-01
1999-01-02 | 16:00:00pm | 5279 | 325.64 | 118.62 | 5.04 | 10.97 | 7.97 | 83.93 | 80.73 | 28.52 | 8.33 | 8.98 | 8.46 | 0.44 | 0.11 | 4.29 |  | 80% | 3.2 | 3.21 | 53.81 | 0.29149 | 1.3879 | 2.52 | 71.172 | 260.512 | 98.4805 | 1999-01-02
1999-01-03 | 16:00:00pm | 5303 | 385.18 | 118.62 | 6.87 | 12.78 | 9.78 | 83.62 | 79.66 | 29.62 | 8.28 | 8.96 | 8.39 | 0.44 | 0.06 | 4.39 |  | 88% | 3.96 | 3.21 | 52.02 | 0.29149 | 1.2975 | 3.435 | 71.172 | 308.144 | 98.1888 | 1999-01-03
1999-01-04 | 16:00:00pm | 5326 | 374.64 | 115.42 | 4.58 | 12.37 | 9.37 | 86.98 | 83.32 | 31.17 | 8.22 | 8.85 | 8.27 | 0.44 | 0.06 | 4.29 |  | 88% | 3.66 | 3.21 | 53.98 | 0.29149 | 1.3173 | 2.29 | 69.252 | 299.712 | 98.7587 | 1999-01-04
1999-01-05 | 16:00:00pm | 5350 | 334.8 | 113.13 | 7.79 | 12.89 | 9.89 | 87.29 | 83.78 | 31.57 | 8.53 | 9.23 | 8.74 | 0.44 | 0.11 | 4.39 |  | 80% | 3.51 | 3.21 | 53.965 | 0.29149 | 1.2922 | 3.895 | 67.878 | 267.84 | 97.6796 | 1999-01-05 | 730 | 3.7 | 40.4 |  | 29.4 | 75 |  | 3200 |  | 11400 |  | 1750 |  | 16950 |  | 14 | 90 | 327 | 8.7 | 120.45 | 382.43 | 1.6092 | 0.7472 | 0.85506
1999-01-06 | 16:00:00pm | 5374 | 302.74 | 114.04 | 3.21 | 11.59 | 8.59 | 87.29 | 82.56 | 30.74 | 7.8 | 7.74 | 7.9 | 0.44 | 0.11 | 4.29 |  | 80% | 4.73 | 3.21 | 54.185 | 0.29149 | 1.3561 | 1.605 | 68.424 | 242.192 | 98.9666 | 1999-01-06
1999-01-07 | 16:00:00pm | 5398 | 295.41 | 116.79 | 2.75 | 13 | -2.85 | 88.81 | 85 | 31.41 | 7.92 | 8.43 | 8.09 | 0.44 | 0.17 | 4.39 |  | 72.13% | 3.81 | 3.21 | 55.495 | 0.29149 | 1.2869 | 1.375 | 70.074 | 236.328 | 99.1025 | 1999-01-07 | 827 | 4.4 | 35.2 | 0.8 | 114.5 | 920 |  | 700 |  | 8200 |  | 28800 |  | 9300 |  | 21 | 74 | 298 | 5.04 | 114.04 | 321.52 | 4.1667 | 0.6489 | 0.92685
1999-01-08 | 16:00:00pm | 5420 | 352.2 | 116.33 | 5.04 | 12.5 | 49.99 | 89.12 | 85.61 | 30.93 | 8.1 | 8.61 | 8.2 | 0.49 | 0.11 | 4.39 |  | 81.67% | 3.51 | 3.21 | 56.435 | 0.29149 | 1.311 | 2.52 | 69.798 | 281.76 | 98.5664 | 1999-01-08
1999-01-09 | 16:00:00pm | 5444 | 293.58 | 118.16 | 4.12 | 13 | 49.99 | 87.74 | 84.39 | 30.35 | 7.9 | 8.07 | 7.96 | 0.44 | 0.11 | 4.39 |  | 80% | 3.35 | 3.21 | 55.715 | 0.29149 | 1.2869 | 2.06 | 70.896 | 234.864 | 98.6525 | 1999-01-09
1999-01-10 | 16:00:00pm | 5468 | 307.78 | 123.66 | 5.04 | 12.1 | 49.99 | 88.66 | 85.15 | 29.77 | 8.24 | 8.82 | 8.41 | 0.44 | 0.17 | 4.39 |  | 72.13% | 3.51 | 3.21 | 57.135 | 0.29149 | 1.3306 | 2.52 | 74.196 | 246.224 | 98.4271 | 1999-01-10
1999-01-11 | 16:00:00pm | 5492 | 318.77 | 109 | 3.66 | 11.8 | 49.99 | 81.95 | 77.67 | 25.83 | 8.07 | 8.58 | 8.21 | 0.39 | 0.11 | 4.39 |  | 78% | 4.28 | 3.21 | 53.98 | 0.29149 | 1.3455 | 1.83 | 65.4 | 255.016 | 98.8577 | 1999-01-11
1999-01-12 | 16:00:00pm | 5516 | 325.18 | 118.62 | 5.5 | 12.5 | 49.99 | 89.12 | 85.76 | 30.71 | 7.99 | 8.46 | 8.12 | 0.44 | 0.11 | 4.39 |  | 80% | 3.36 | 3.21 | 56.73 | 0.29149 | 1.311 | 2.75 | 71.172 | 260.144 | 98.34 | 1999-01-12 | 900 | 4.7 | 44.1 | 1.9 | 45.1 | 100 |  | <100 |  | 1400 |  | 50 |  | 2700 |  | 2 | 72 | 269 | 3.66 | 116.79 | 323.35 | 0.54645 | 0.61649 | 0.83192
1999-01-13 | 16:00:00pm | 5540 | 301.36 | 111.75 | 1.83 | 12.8 | 21.64 | 87.44 | 83.32 | 30.53 | 7.86 | 7.63 | 7.95 | 0.44 | 0.11 | 4.29 |  | 80% | 4.12 | 3.21 | 54.85 | 0.29149 | 1.2965 | 0.915 | 67.05 | 241.088 | 99.4061 | 1999-01-13
1999-01-14 | 11:00:00pm | 5559 | 321.97 | 112.67 | 4.12 | 14 | 24.03 | 92.63 | 88.05 | 31.84 | 8.12 | 8.72 | 8.31 | 0.44 | 0.06 | 4.49 |  | 88% | 4.58 | 3.21 | 58.5 | 0.29149 | 1.2405 | 2.06 | 67.602 | 257.576 | 98.733 | 1999-01-14 | 801 | 3.7 | 91.7 |  |  | 155 |  | 395 |  | 6750 |  | 4610 |  | 500 |  | 10 | 78 | 730 | 5.95 | 118.62 | 328.84 | 1.6807 | 0.65756 | 2.2199
1999-01-15 | 16:00:00pm | 5566 | 304.11 | 109.92 | 10.08 | 14.47 | 14.47 | 93.09 | 89.58 | 29.4 | 4 | 5 | 4.32 | 0.73 | 0.28 | 4.08 |  | 72.28% | 3.51 | 3.21 | 61.935 | 0.29149 | 1.2193 | 5.04 | 65.952 | 243.288 | 96.7404 | 1999-01-15
1999-01-16 | 16:00:00pm | 5590 | 306.4 | 109.92 | 6.87 | 14.76 | 14.76 | 94.46 | 91.71 | 26.96 | 4.41 | 5.01 | 4.72 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 66.125 | 0.29149 | 1.2065 | 3.435 | 65.952 | 245.12 | 97.7915 | 1999-01-16
1999-01-17 | 16:00:00pm | 5614 | 428.23 | 138.77 | 13.74 | 14.74 | 14.74 | 102.7 | 100.26 | 29.92 | 3.23 | 4.59 | 3.38 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.44 | 3.21 | 71.56 | 0.29149 | 1.2073 | 6.87 | 83.262 | 342.584 | 96.7735 | 1999-01-17
1999-01-18 | 16:00:00pm | 5635 | 324.72 | 112.21 | 5.04 | 15.29 | 15.29 | 102.39 | 99.5 | 32.36 | 4.06 | 4.95 | 4.33 | 0.73 | 0.23 | 3.97 |  | 76.04% | 2.89 | 3.21 | 68.585 | 0.29149 | 1.1834 | 2.52 | 67.326 | 259.776 | 98.4592 | 1999-01-18
1999-01-19 | 16:00:00pm | 5659 | 341.67 | 113.13 | 9.62 | 15.2 | 15.2 | 103.16 | 100.26 | 31.48 | 3.89 | 4.89 | 4.14 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 70.23 | 0.29149 | 1.1873 | 4.81 | 67.878 | 273.336 | 97.1807 | 1999-01-19 | 842 | 2 | 55.7 | 2.4 | 40.2 | 163 |  | 1340 |  | 650 |  | TNTC |  | 2600 |  | 10 | 73 | 259 | 6.87 | 102.59 | 330.22 | 1.4556 | 0.71157 | 0.78433
1999-01-20 | 16:00:00pm | 5683 | 325.18 | 104.42 | 6.41 | 15.4 | 15.4 | 103.16 | 99.95 | 30.77 | 4.64 | 4.99 | 4.92 | 0.68 | 0.23 | 4.08 |  | 74.73% | 3.21 | 3.21 | 70.785 | 0.29149 | 1.1787 | 3.205 | 62.652 | 260.144 | 98.0142 | 1999-01-20
1999-01-21 | 16:00:00pm | 5706 | 445.18 | 136.94 | 16.03 | 16.05 | 16.05 | 103 | 99.95 | 30.53 | 3.24 | 4.44 | 3.37 | 0.73 | 0.17 | 4.08 |  | 81.11% | 3.05 | 3.21 | 70.945 | 0.29149 | 1.1513 | 8.015 | 82.164 | 356.144 | 96.3428 | 1999-01-21 | 840 | 3.5 | 38.1 | 3.2 | 36.3 | <10 |  | 1500 |  | 4200 |  | 11400 |  | <100 |  | 5 | 65 | 258 | 9.62 | 113.58 | 360.45 | 0.51975 | 0.57228 | 0.71577
1999-01-22 | 16:00:00pm | 5730 | 360.45 | 111.29 | 6.41 | 15.99 | 15.99 | 103.62 | 101.17 | 29.62 | 3.85 | 4.85 | 4.02 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.45 | 3.21 | 72.775 | 0.29149 | 1.1538 | 3.205 | 66.774 | 288.36 | 98.195 | 1999-01-22
1999-01-23 | 16:00:00pm | 5754 | 360.45 | 104.42 | 7.33 | 15.31 | 15.31 | 105.6 | 103 | 30.01 | 4.12 | 4.86 | 4.29 | 0.68 | 0.23 | 4.18 |  | 74.73% | 2.6 | 3.21 | 74.29 | 0.29149 | 1.1825 | 3.665 | 62.652 | 288.36 | 97.9118 | 1999-01-23
1999-01-24 | 16:00:00pm | 5778 | 345.79 | 106.26 | 5.5 | 14.41 | 14.41 | 106.06 | 103.62 | 29.28 | 3.85 | 4.8 | 4.07 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.44 | 3.21 | 75.56 | 0.29149 | 1.222 | 2.75 | 63.756 | 276.632 | 98.3842 | 1999-01-24
1999-01-25 | 16:00:00pm | 5802 | 369.61 | 110.38 | 5.5 | 14.66 | 14.66 | 106.36 | 103.62 | 30.1 | 3.76 | 4.76 | 3.91 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.74 | 3.21 | 74.89 | 0.29149 | 1.2109 | 2.75 | 66.228 | 295.688 | 98.4803 | 1999-01-25
1999-01-26 | 16:00:00pm | 5826 | 354.95 | 105.8 | 6.41 | 16.3 | 16.3 | 105.75 | 104.07 | 29.95 | 4.24 | 4.82 | 4.44 | 0.68 | 0.17 | 4.08 |  | 80% | 1.68 | 3.21 | 74.96 | 0.29149 | 1.1409 | 3.205 | 63.48 | 283.96 | 98.1551 | 1999-01-26 | 756 | 3 | 37.7 | 3.8 | 27.7 | 67 |  | 200 |  | 2250 |  | 56000 |  | 3290 |  | 24 | 94 | 270 | 6.87 | 104.88 | 342.13 | 3.4934 | 0.89626 | 0.78917
1999-01-27 | 16:00:00pm | 5850 | 364.11 | 109.46 | 5.95 | 15.5 | 15.5 | 106.21 | 104.53 | 29.8 | 3.96 | 4.81 | 4.18 | 0.68 | 0.23 | 4.08 |  | 74.73% | 1.68 | 3.21 | 75.57 | 0.29149 | 1.1744 | 2.975 | 65.676 | 291.288 | 98.3332 | 1999-01-27
1999-01-28 | 16:00:00pm | 5870 | 408.08 | 121.37 | 10.08 | 16.08 | 16.08 | 104.53 | 102.39 | 32.18 | 3.39 | 4.6 | 3.56 | 0.73 | 0.23 | 4.08 |  | 76.04% | 2.14 | 3.21 | 71.28 | 0.29149 | 1.15 | 5.04 | 72.822 | 326.464 | 97.4755 | 1999-01-28 | 748 | 1 | 111.3 | 1.2 | 66 | 1125 |  | 700 |  | 1300 |  | 2050 |  | 6900 |  | 23 | 86 | 237 | 8.7 | 112.21 | 351.74 | 2.6437 | 0.76642 | 0.67379
1999-01-29 | 16:00:00pm | 5894 | 357.7 | 101.22 | 7.33 | 16.08 | 17.61 | 104.07 | 101.17 | 31.99 | 4.03 | 4.84 | 4.25 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 70.63 | 0.29149 | 1.15 | 3.665 | 60.732 | 286.16 | 97.887 | 1999-01-29
1999-01-30 | 16:00:00pm | 5918 | 345.33 | 107.63 | 7.79 | 16.08 | 16.31 | 104.68 | 101.78 | 31.14 | 3.93 | 4.8 | 4.13 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.9 | 3.21 | 72.09 | 0.29149 | 1.15 | 3.895 | 64.578 | 276.264 | 97.7145 | 1999-01-30
1999-01-31 | 16:00:00pm | 5942 | 310.98 | 105.8 | 6.87 | 16.08 | 15.99 | 104.23 | 101.78 | 30.01 | 4.21 | 4.85 | 4.44 | 0.63 | 0.23 | 4.08 |  | 73.26% | 2.45 | 3.21 | 72.995 | 0.29149 | 1.15 | 3.435 | 63.48 | 248.784 | 97.7999 | 1999-01-31
1999-02-01 | 16:00:00pm | 5966 | 350.83 | 108.55 | 5.04 | 16.08 | 15.67 | 104.84 | 101.78 | 30.1 | 4.03 | 4.81 | 4.23 | 0.63 | 0.23 | 4.08 |  | 73.26% | 3.06 | 3.21 | 73.21 | 0.29149 | 1.15 | 2.52 | 65.13 | 280.664 | 98.5425 | 1999-02-01
1999-02-02 | 16:00:00pm | 5990 | 358.61 | 107.63 | 7.79 | 16.76 | 16.76 | 105.14 | 101.94 | 29.92 | 4.27 | 4.89 | 4.47 | 0.68 | 0.23 | 3.97 |  | 74.73% | 3.2 | 3.21 | 73.62 | 0.29149 | 1.1222 | 3.895 | 64.578 | 286.888 | 97.7836 | 1999-02-02 | 800 | 4 | 28 | 1.9 | 37.8 | 65 |  | 350 |  | 550 |  | 2650 |  | 1150 |  | 3 | 57 |  | 8.7 | 99.84 | 358.16 | 0.34483 | 0.57091 | 0
1899-12-31 | 16:00:00pm | 6011 | 351.74 | 109.92 | 9.16 | 16.59 | 16.59 | 104.68 | 102.09 | 30.84 | 3.83 | 4.77 | 3.99 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.59 | 3.21 | 72.545 | 0.29149 | 1.129 | 4.58 | 65.952 | 281.392 | 97.3628 | 1999-02-03
1999-02-04 | 16:00:00pm | 6035 | 355.41 | 106.26 | 8.7 | 15.92 | 15.92 | 104.53 | 101.94 | 30.19 | 3.82 | 4.79 | 3.98 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.59 | 3.21 | 73.045 | 0.29149 | 1.1567 | 4.35 | 63.756 | 284.328 | 97.5006 | 1999-02-04 | 704 | 3.2 | 42.1 | 2.5 | 40.4 | 160 |  | 150 |  | 7300 |  | 8800 |  | 4200 |  | 3 | 51 | 254
1999-02-05 | 16:00:00pm | 6059 | 319.23 | 107.17 | 6.41 | 17.21 | 17.21 | 104.23 | 102.39 | 31.2 | 4.05 | 4.84 | 4.25 | 0.68 | 0.28 | 4.08 |  | 70.83% | 1.84 | 3.21 | 72.11 | 0.29149 | 1.1042 | 3.205 | 64.302 | 255.384 | 97.9949 | 1999-02-05
1999-02-06 | 16:00:00pm | 6083 | 381.51 | 116.33 | 9.16 | 16.74 | 16.74 | 103 | 101.02 | 29.74 | 3.51 | 4.62 | 3.64 | 0.68 | 0.28 | 4.08 |  | 70.83% | 1.98 | 3.21 | 72.27 | 0.29149 | 1.123 | 4.58 | 69.798 | 305.208 | 97.5574 | 1999-02-06
1999-02-07 | 16:00:00pm | 6107 | 353.12 | 105.8 | 6.41 | 16.37 | 16.37 | 105.14 | 102.39 | 30.35 | 4.02 | 4.81 | 4.18 | 0.68 | 0.23 | 4.08 |  | 74.73% | 2.75 | 3.21 | 73.415 | 0.29149 | 1.138 | 3.205 | 63.48 | 282.496 | 98.1473 | 1999-02-07
1999-02-08 | 16:00:00pm | 6132 | 376.02 | 115.87 | 8.7 | 16.42 | 16.42 | 104.99 | 101.63 | 30.13 | 3.83 | 4.78 | 3.97 | 0.68 | 0.17 | 4.08 |  | 80% | 3.36 | 3.21 | 73.18 | 0.29149 | 1.136 | 4.35 | 69.522 | 300.816 | 97.6508 | 1999-02-08
1999-02-09 | 09:00:00am | 6148 | 343.96 | 106.26 | 6.87 | 15.7 | 15.7 | 105.29 | 102.85 | 28.97 | 4.14 | 4.82 | 4.3 | 0.68 | 0.23 | 3.97 |  | 74.73% | 2.44 | 3.21 | 75.1 | 0.29149 | 1.1659 | 3.435 | 63.756 | 275.168 | 97.973 | 1999-02-09 | 930 | 3.5 | 35.3 | 2.2 | 35.3 | 5 |  | 250 |  | 1950 |  | 24100 |  | 1250 |  | 3 | 30 | 130
[20 empty] | average | 54.477 |  |  | 5.2704 | 71.0889 | 249.7037 |  | Average: |  | 4.4235 |  | 2.4483 | [11 empty] | 10.8286 | 74.8333 | 268.8857 | 10.9119 | 117.7831 | 301.0015 | 1.3125 | 0.63298 | 0.8599 | 94.0308
[20 empty] | max | 159.545 | [6 empty] | Max: |  | 6.6 |  | 3.8
[20 empty] | min | 36.23 | [6 empty] | Min: |  | 0.6 |  | 0.8

## NF70. Weeks 1-10
FIELD-SET 1: LT-SEBST RESULTS: WEEKS 1-10 (FILE: ltsebst.xls)
Field 1-1: PWS And Treatment Plant Data |  |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  |  | Field 1-3: SEBST Design Parameters |  |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [47 empty] | Field 1-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 1-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 6 | [9 empty] | Field 1-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 8 | [9 empty] | Field 1-11: Permeate, Feed, Concentrate And Blended Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 10 | [9 empty] | Field 1-13: Membrane Cost Parameters
|  |  | General Information |  |  | Calculate Temperature Normalized MTCW |  |  | Parameters Evaluated Prior to Pretreatment |  | (see cell A47) | [49 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | City of Norfolk |  | Membrane manufacturer | FilmTec |  | Average yearly temperature of feed water, TavgoC (oC) | 20 |  | PLANT FILTERED WATER: |  |  | Day No. | Date | Time | Operation time | Permeate | PI | PC | PP | QR | Qp | QW | Cleaning | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.76 | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.8 | [8 empty] | Recovery during sample collection (decimal) | 0.8 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | VA37010100 |  | Membrane trade name | NF70 |  | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.30143 |  | Alkalinity (mg/L as CaCO3) | 10.5 |  |  | MM/DD/YY | hh:mm | hh.hh | Temp.(oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Event | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.96 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.96 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.85 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.85 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA |  | Membrane element model number | NF70-4040 |  |  |  |  | pH (units) | 6.44 |  | 1 | 1998-05-15 | 16:00 | 2.3 | 18.15 | 78.13 | 76.3 | 30.35 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 16.0336 | 2.8606 | 44.0044 | 0.36436 | 4.97 | 6.51 | 6.54 | 4.58 | 78.594 | 194.152 | 313.508 | -61.4755 | 94.1726 | 290.636 | 98.4241 | [17 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.04 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.88 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.99 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.93 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.93 | [7 empty] | Capital Recovery Period (years) | 20
|  |  | Molecular weight cutoff (Daltons) | 200 |  | Calculate System Flow Rates1 |  |  | Total Dissolved Solids | 73 mg/L |  | 2 | 1998-05-16 | 14:00 | 25.3 | 19.19 | 79.2 | 77.06 | 30.77 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 15.4524 | 2.795 | 44.565 | 0.34674 | 4.97 | 6.29 | 6.35 | 4.35 | 76.668 | 238.104 | 306.199 | -28.5989 | 94.3262 | 283.8512 | 98.4675 | [76 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide |  | Design recovery, R (decimal) | 0.75 |  | Conductivity | 129 umhos/cm |  | 3 | 1998-05-17 | 16:00 | 46.8 | 20.35 | 79.2 | 76.91 | 30.1 | 3.97 | 0.73 | 0.11 |  | 0.84 | 4.81 | 0.33958 | 0.86905 | 4.7262 | 15.0171 | 14.8336 | 4.8737 | 43.0813 | 0.34432 | 5 | 6.43 | 6.46 | 5.955 | 75.018 | 223.456 | 533.3452 | -138.6802 | 92.0619 | 493.3249 | 98.7929 | [16 empty] | Permeate, Feed and Concentrate Water Quality |  |  | (Feed influenced by recycle) | [6 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  |  | Membrane construction (e.g., thin-film composite) | Thin-film composite |  | Design flux, FW (gfd) | 14.4 |  | SDI | 5.8 |  | 4 | 1998-05-18 | 16:00 | 70.8 | 20.27 | 78.13 | 75.69 | 30.47 | 3.97 | 0.73 | 0.28 |  | 1.01 | 4.98 | 0.35257 | 0.72277 | 3.9307 | 15.0171 | 14.8753 | 2.3348 | 44.1052 | 0.33727 | 4.94 | 6.19 | 6.3 | 4.35 | 74.196 | 190.488 | 256.2945 | -34.5463 | 94.1372 | 237.8287 | 98.171 | [16 empty] | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-6 | CF-6 | CC-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-8 | CF-8 | CC-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-10 | CF-10 | CC-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-10 (dup) | CF-10 (dup) | CC-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 15
|  |  | Membrane hydrophobicity | Hydrophobic |  | Permeate flow rate, Qp (gpm) | 0.7 |  | Turbidity (ntu) | 0.26 |  | 5 | 1998-05-19 | 16:00 | 94.8 | 21.64 | 78.44 | 76.45 | 30.8 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 14.1798 | 2.611 | 44.034 | 0.32202 | 4.95 | 6.05 | 6.14 | 5.265 | 72.822 | 208.8 | 287.242 | -37.568 | 92.77 | 266.3654 | 98.0234 | [16 empty] | Sampling date | MM/DD/YY | 1998-05-27 | 1998-05-27 | 1998-05-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-11 | 1998-06-11 | 1998-06-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-25 | 1998-06-25 | 1998-06-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-09 | 1998-07-09 | 1998-07-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-23 | 1998-07-23 | 1998-07-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-23 | 1998-07-23 | 1998-07-23 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 9
Phone Number |  |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative |  | Feed flow rate, QF (gpm) | 0.93333 |  | Dissolved aluminum (mg/L) | <0.044 |  | 6 | 1998-05-20 | 16:00 | 118.8 | 22.57 | 77.83 | 75.99 | 31.51 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 13.7298 | 3.351 | 42.049 | 0.32652 | 5 | 6.21 | 6.3 | 5.495 | 73.92 | 227.12 | 367.745 | -61.9166 | 92.5663 | 340.5948 | 98.3866 | [16 empty] | Sampling time (approx.) | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:35 | 8:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:30 | 7:45 | 7:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:00 | 7:00 | 7:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:20 | 10:40 | 10:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:20 | 10:40 | 10:55 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | Concentrate-waste flow rate, QW (gpm) | 0.23333 |  | Total aluminum (mg/L) | 0.074 |  | 7 | 1998-05-21 | 16:00 | 142.8 | 23.49 | 77.98 | 75.69 | 31.2 | 3.97 | 0.78 | 0.23 |  | 1.01 | 4.98 | 0.35066 | 0.77228 | 3.9307 | 16.0457 | 14.2124 | 2.9251 | 42.7099 | 0.33277 | 5.06 | 6.36 | 6.46 | 5.495 | 77.766 | 245.432 | 322.859 | -31.5472 | 92.9339 | 298.0052 | 98.1561 | [16 empty] | Operation time | hh.hh | 279.3 | 279.3 | 279.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 591.8 | 591.8833 | 591.9667 | --- | --- | --- | --- | --- | Operation time | hh.hh | 899.8 | 900.05 | 899.8833 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1193.6 | 1193.6 | 1193.6 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1519 | 1519 | 1519 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1519 | 1519 | 1519 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131.8
E-Mail Address (optional) |  |  | Design Parameters |  |  | Minimum influent flow rate, QI, min (gpm) | 4 |  | PILOT FILTERED: Sulfate (mg/L) | 43 |  | 8 | 1998-05-22 | 16:00 | 166.8 | 21.9 | 79.2 | 76.91 | 32.33 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 14.0523 | 3.5149 | 42.2101 | 0.33291 | 4.99 | 6.36 | 6.36 | 5.725 | 77.496 | 219.792 | 385.6891 | -75.4791 | 92.6125 | 357.2113 | 98.3973 | [16 empty] | pH | --- | 5.66 | 6.53 | NA | --- | --- | --- | --- | --- | pH | --- | 5.7 | 6.6 | 7 | --- | --- | --- | --- | --- | pH | --- | 5.82 | 6.39 | 6.67 | --- | --- | --- | --- | --- | pH | --- | 5.67 | 6.11 | 6.83 | --- | --- | --- | --- | --- | pH | --- | 5.9 | 6.11 | 6.4 | --- | --- | --- | --- | --- | pH | --- | 5.9 | 6.11 | 6.4 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.65
|  |  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" |  | Maximum influent flow rate, QI, max (gpm) | 18 |  | RAW WATER: |  |  | 9 | 1998-05-23 | 16:00 | 190.8 | 20.09 | 79.05 | 77.22 | 31.45 | 3.97 | 0.78 | 0.17 |  | 0.95 | 4.92 | 0.34607 | 0.82105 | 4.1789 | 16.0457 | 15.995 | 3.6739 | 43.0111 | 0.37188 | 4.98 | 6.23 | 6.26 | 5.265 | 76.668 | 230.784 | 404.2818 | -75.1776 | 93.1327 | 372.6524 | 98.5872 | [16 empty] | Temperature | oC | 23.2222 | 23.1667 | NA | --- | --- | --- | --- | --- | Temperature | oC | 22.6667 | 19.8333 | 18.2778 | --- | --- | --- | --- | --- | Temperature | oC | 25.3889 | 26 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 21.8333 | 21.8889 | NA | --- | --- | --- | --- | --- | Temperature | oC | 30.5 | 29.4 | 30.5 | --- | --- | --- | --- | --- | Temperature | oC | 30.5 | 29.4 | 30.5 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 30
Technical ICR Contact Person |  |  | Active membrane area of membrane element used, A (ft2) | 70 |  | Design influent flow rate2, QI (gpm) | 4.93 |  | Dissolved iron (mg/L) | 0.2 |  | 10 | 1998-05-24 | 16:00 | 214.8 | 19.81 | 79.05 | 76.3 | 30.07 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 15.1179 | 3.5999 | 44.0051 | 0.34355 | 5.01 | 6.4 | 6.43 | 4.81 | 78.318 | 267.416 | 393.97 | -47.3248 | 93.8584 | 364.803 | 98.6815 | [16 empty] | Alkalinity | mg/L as CaCO3 | 2 | 10 | 29 | 35.3333 | -21.8391 | 80 | 32.8157 | 93.9054 | Alkalinity | mg/L as CaCO3 | 3 | 13 | 42 | 37.4828 | 10.7553 | 76.9231 | 35.1511 | 91.4654 | Alkalinity | mg/L as CaCO3 | 1 | 10 | 29 | 37 | -27.5862 | 90 | 34.4826 | 97.1 | Alkalinity | mg/L as CaCO3 | 4 | 8 | 21 | 20 | 4.7619 | 50 | 18.9058 | 78.8425 | Alkalinity | mg/L as CaCO3 | 3 | 7 | 15 | 23 | -53.3333 | 57.1429 | 21.6207 | 86.1244 | Alkalinity | mg/L as CaCO3 | 3 | 7 | 15 | 23 | -53.3333 | 57.1429 | 21.6207 | 86.1244 | Electric Rate ($/kW-h) | 0.049
Mailing Address |  |  | Design flux, FW (gfd) | 14.4 |  | Design recycle flow rate, QR (gpm) | 3.9967 |  | Total iron (mg/L) | 0.6 |  | 11 | 1998-05-25 | 16:00 | 238.8 | 21.32 | 78.89 | 76.3 | 30.56 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 14.3387 | 2.749 | 44.286 | 0.32378 | 5 | 6.28 | 6.33 | 5.265 | 76.392 | 223.456 | 302.1429 | -35.2136 | 93.1079 | 280.1631 | 98.1207 | [16 empty] | Total dissolved solids | mg/L | 5.955 | 77.766 | 212.464 | 305.1675 | -43.6326 | -173.2094 | 282.5686 | 24.8098 | Total dissolved solids | mg/L | 6.185 | 82.164 | 201.472 | 268.1816 | -33.1111 | 92.4724 | 250.4656 | 97.5306 | Total dissolved solids | mg/L | 6.185 | 72.27 | 157.52 | 270.525 | -71.7401 | 91.4418 | 252.0402 | 97.546 | Total dissolved solids | mg/L | 7.555 | 60.456 | 190.488 | 219.159 | -15.0513 | 87.5033 | 204.6881 | 96.309 | Total dissolved solids | mg/L | 6.87 | 56.334 | 175.832 | 254.19 | -44.5641 | 87.8049 | 237.1334 | 97.1029 | Total dissolved solids | mg/L | 6.87 | 56.334 | 175.832 | 254.19 | -44.5641 | 87.8049 | 237.1334 | 97.1029 | Fuel Oil Rate ($/gal) | NA
|  |  | Net driving pressure at the design flux, NDP (psi) | 45.7 |  | Recycle ratio, r | 4.2821 |  | Dissolved aluminum (mg/L) | 0.12 |  | 12 | 1998-05-26 | 16:00 | 262.8 | 22.33 | 77.67 | 75.38 | 30.71 | 3.87 | 0.73 | 0.23 |  | 0.96 | 4.83 | 0.34111 | 0.76042 | 4.0312 | 15.0171 | 13.8443 | 2.7127 | 43.1023 | 0.3212 | 5.02 | 6.27 | 6.32 | 5.265 | 75.57 | 197.816 | 298.712 | -51.005 | 93.0329 | 276.5364 | 98.0961 | [16 empty] | Total hardness | mg/L as CaCO3 | 7 | 51 | 174 | 190.3333 | -9.387 | 86.2745 | 176.4865 | 96.0337 | Total hardness | mg/L as CaCO3 | 11 | 37 | 186 | 100.6552 | 45.8843 | 70.2703 | 94.5928 | 88.3712 | Total hardness | mg/L as CaCO3 | 9 | 50 | 173 | 173 | 0 | 82 | 161.5318 | 94.4283 | Total hardness | mg/L as CaCO3 | 2 | 37 | 123 | 142 | -15.4472 | 94.5946 | 132.4259 | 98.4897 | Total hardness | mg/L as CaCO3 | 5 | 33 | 114 | 145 | -27.193 | 84.8485 | 135.3448 | 96.3057 | Total hardness | mg/L as CaCO3 | 5 | 33 | 114 | 145 | -27.193 | 84.8485 | 135.3448 | 96.3057 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.3151 |  | 1: Flow rates and pressures may need to be adjusted in order to obtain |  |  | Total aluminum (mg/L) | 0.38 |  | 13 | 1998-05-27 | 16:00 | 286.8 | 21.7 | 78.59 | 76.3 | 31.11 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 14.1503 | 2.7083 | 43.6267 | 0.32435 | 5.01 | 6.37 | 6.36 | 5.495 | 75.57 | 190.488 | 297.982 | -56.4308 | 92.7286 | 276.3272 | 98.0114 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 2 | 32 | 127 | 127 | 0 | 93.75 | 117.559 | 98.2987 | Calcium hardness | mg/L as CaCO3 | BMRL | 35 | 138 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 32 | 162 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 19 | 80 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 19 | 70 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 19 | 71 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 0.49
FAX Number |  |  | Temperature at which the MTCW was determined, ToC (oC) | 21.5 |  | the desired operating conditions. |  |  | Fluoride (mg/L) | ND |  | 14 | 1998-05-29 | 16:00 | 300.1 | 22.94 | 75.99 | 73.4 | 30.9 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35257 | 0.81111 | 4.5333 | 15.0171 | 13.5556 | 3.3569 | 40.4381 | 0.33522 | 5.12 | 6.49 | 6.48 | 6.87 | 75.294 | 285.728 | 369.1147 | -29.1839 | 90.8758 | 342.5646 | 97.9945 | [16 empty] | Turbidity | ntu | 0.12 | 0.27 | 0.22 | 0.745 | -238.6364 | 55.5556 | 0.6978 | 82.803 | Turbidity | ntu | 0.09 | 0.14 | 0.16 | 0.26241 | -64.0086 | 35.7143 | 0.25076 | 64.1084 | Turbidity | ntu | 0.08 | 0.14 | 0.16 | 0.32 | -100 | 42.8571 | 0.30322 | 73.6163 | Turbidity | ntu | 0.09 | 0.16 | 0.15 | 0.37 | -146.6667 | 43.75 | 0.35085 | 74.3481 | Turbidity | ntu | 0.13 | 0.14 | 0.17 | 0.18 | -5.8824 | 7.1429 | 0.17655 | 26.3672 | Turbidity | ntu | 0.12 | 0.14 | 0.17 | 0.22 | -29.4118 | 14.2857 | 0.2131 | 43.6893 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  | Maximum flow rate to the element, QI, max (gpm) | 18 |  | 2: The design influent flow rate must be within the range established by the |  |  | Sulfate (mg/L) | 13.2 |  | 15 | 1998-05-30 | 15:30 | 315.6 | 24.62 | 63.02 | 60.28 | 24.43 | 4.18 | 0.63 | 0.17 |  | 0.8 | 4.98 | 0.35639 | 0.7875 | 5.225 | 12.96 | 11.0438 | 2.8287 | 34.3913 | 0.32112 | 5.27 | 6.64 | 6.66 | 7.555 | 71.724 | 223.456 | 309.5268 | -38.518 | 89.4666 | 290.4261 | 97.3987 | [16 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | 0.07 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.15 | 0.17 | 0.11 | 0.21897 | -99.0596 | 11.7647 | 0.2143 | 30.0054 | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Minimum flow rate to the element, QI, min (gpm) | 4 |  | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  |  | Calcium (mg/L) | 8.4 |  | 16 | 1998-05-31 | 16:00 | 335.3 | 23.7 | 74.47 | 72.03 | 30.93 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 13.2058 | 2.7751 | 39.5449 | 0.33395 | 5.1 | 6.31 | 6.39 | 5.265 | 76.944 | 230.784 | 304.4469 | -31.9186 | 93.1574 | 282.78 | 98.1381 | [16 empty] | Total organic carbon | mg/L | BMRL | 2.56 | 9.48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.7 | 9.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.7 | 9.73 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.79 | 10.54 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.83 | 10.27 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.82 | 10.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | 37th Street WTP |  | Total width of all membrane envelopes in the element, w (ft) | 12.68 |  |  |  |  | Barium (mg/L) | 0.037 |  | 17 | 1998-06-01 | 16:00 | 359.3 | 23.81 | 77.83 | 75.38 | 32.97 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 13.1561 | 2.6369 | 40.9981 | 0.3209 | 5.07 | 6.35 | 6.37 | 5.265 | 73.374 | 190.488 | 289.546 | -52.0022 | 92.8244 | 268.9582 | 98.0424 | [16 empty] | UV254 | cm-1 | BMRL | 0.041 | 0.176 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.05 | 0.192 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.056 | 0.189 | 0.197 | -4.2328 | 83.9286 | 0.18385 | 95.1048 | UV254 | cm-1 | BMRL | 0.052 | 0.204 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.047 | 0.188 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.047 | 0.188 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Treatment Plant Category | Conventional |  | Feed spacer thickness, T (ft) | 0.0023 |  | Estimate the Osmotic Pressure Gradient |  |  | Strontium (mg/L) | 0.051 |  | 18 | 1998-06-02 | 16:00 | 383.3 | 24.27 | 77.67 | 75.23 | 31.72 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35257 | 0.81111 | 4.5333 | 15.0171 | 12.9506 | 3.2312 | 41.4988 | 0.31207 | 5.08 | 6.37 | 6.36 | 6.41 | 72.27 | 271.08 | 355.0806 | -30.9874 | 91.1305 | 329.5254 | 98.0548 | [16 empty] | SUVA | L/(mg*m) | NR | 1.6016 | 1.8565 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.8519 | 1.9794 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.0741 | 1.9424 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.8638 | 1.9355 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6608 | 1.8306 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6667 | 1.8431 | --- | --- | --- | --- | ---
Process Train Name | West |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 |  | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.7 |  | Reactive silica (mg/L as SiO2) | 3.7 |  | 19 | 1998-06-03 | 16:00 | 407.3 | 24.74 | 77.98 | 74.93 | 31.32 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 12.7445 | 2.6534 | 42.4816 | 0.3 | 5.07 | 6.28 | 6.3 | 6.64 | 75.294 | 271.08 | 293.1958 | -8.1584 | 91.1812 | 271.9802 | 97.5586 | [16 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 26 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 26 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 677 |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 |  | Feed TDS, TDSF (mg/L) | 70 |  |  |  |  | 20 | 1998-06-04 | 16:00 | 430.43 | 23.83 | 76.91 | 74.47 | 30.8 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 13.1471 | 2.7326 | 42.1574 | 0.31186 | 5.14 | 6.56 | 6.59 | 6.64 | 77.22 | 216.128 | 301.2348 | -39.378 | 91.4012 | 279.9 | 97.6277 | [16 empty] | SDS-Cl2 dose** | mg/L | 5.13 | 3.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.3 | 2.3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.04 | 2.04 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.13 | 3.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.95 | 4.88 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.95 | 4.88 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | VA3710150 |  |  |  |  | Waste TDS, TDSW (mg/L) | 154.99 |  |  |  |  | 21 | 1998-06-05 | 16:00 | 454.43 | 23.12 | 78.59 | 76.15 | 30.5 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 12.549 | 2.507 | 44.363 | 0.28287 | 5.08 | 6.4 | 6.41 | 6.64 | 74.748 | 238.104 | 276.1108 | -15.9623 | 91.1168 | 257.3362 | 97.4197 | [16 empty] | SDS-Free Cl2 residual** | mg/L | 4.15 | 0.84 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.16 | 0.15 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.53 | 0.12 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.43 | 0.43 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.39 | 1.64 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | 1.67 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 9 |  | Additional Information |  |  | Permeate TDS, TDSp (mg/L) | 41.67 |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  | 22 | 1998-06-06 | 16:00 | 479.43 | 22.57 | 79.05 | 76.15 | 30.99 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.7894 | 2.5921 | 44.0179 | 0.29055 | 5.09 | 6.45 | 6.43 | 6.64 | 76.944 | 230.784 | 284.7993 | -23.4051 | 91.3703 | 265.8466 | 97.5023 | [16 empty] | SDS-Cl2 demand | mg/L | 0.98 | 2.36 | --- | 6.73 | --- | 58.4746 | 6.2957 | 84.4339 | SDS-Cl2 demand | mg/L | 1.14 | 2.15 | --- | 4.6228 | --- | 46.9767 | 4.3873 | 74.0157 | SDS-Cl2 demand | mg/L | 0.51 | 1.92 | --- | 6.15 | --- | 73.4375 | 5.7556 | 91.1391 | SDS-Cl2 demand | mg/L | 0.7 | 2.77 | --- | 8.98 | --- | 74.7292 | 8.4138 | 91.6803 | SDS-Cl2 demand | mg/L | 0.56 | 3.24 | --- | 13.96 | --- | 82.716 | 13.0359 | 95.7042 | SDS-Cl2 demand | mg/L | 0.65 | 3.21 | --- | 13.45 | --- | 79.7508 | 12.5672 | 94.8278
Historical Average Water Temperature (oC) | 32 |  | Design cross-flow velocity (fps) | 0.34989 |  | Influent TDS, TDSI (mg/L) | 138.9 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  | 23 | 1998-06-07 | 16:00 | 502.43 | 22.67 | 79.2 | 76.3 | 30.16 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.7453 | 2.5499 | 45.0401 | 0.28298 | 5.09 | 6.46 | 6.47 | 6.41 | 75.57 | 205.136 | 280.043 | -36.5158 | 91.5178 | 261.3987 | 97.5478 | [16 empty] | SDS-Chlorination temp. | oC | 21.1111 | 21.5 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 21 | 21.0556 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 22.6111 | 22.9444 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23.8889 | 24.1111 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24.7 | 24.4 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24.7 | 24.9 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 28 |  | Required influent flow to permeate flow rate ratio, QI:Qp | n/a |  | Osmotic pressure gradient, Dp (psi) | 1.0528 |  |  |  |  | 24 | 1998-06-08 | 16:00 | 526.43 | 23.37 | 78.74 | 75.69 | 29.74 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.4415 | 2.5211 | 44.9539 | 0.27676 | 5.04 | 6.24 | 6.19 | 6.64 | 75.018 | 194.152 | 277.179 | -42.7639 | 91.1488 | 258.7455 | 97.4338 | [16 empty] | SDS-Chlorination pH | --- | 7.16 | 6.54 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.11 | 6.96 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 6.9 | 6.91 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.05 | 7.04 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.01 | 7.03 | --- | --- | --- | --- | --- | ---
|  |  | Maximum element recovery (%) | 15 | [7 empty] | 25 | 1998-06-09 | 16:00 | 550.43 | 23.66 | 81.18 | 78.59 | 32.3 | 3.97 | 0.73 | 0.28 |  | 1.01 | 4.98 | 0.35257 | 0.72277 | 3.9307 | 15.0171 | 13.2239 | 2.4387 | 45.1463 | 0.29291 | 5.3 | 6.29 | 6.63 | 4.81 | 77.766 | 212.464 | 267.9727 | -26.1262 | 93.8148 | 248.6847 | 98.0658 | [16 empty] | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.8833 | 23.8833 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.75 | 25.05 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.75 | 25.05 | --- | --- | --- | --- | --- | ---
|  |  | Variability of design flux (%) | 20 |  | Estimate the Required Influent Pressure | [5 empty] | 26 | 1998-06-10 | 16:00 | 574.43 | 22.68 | 79.66 | 76.76 | 30.19 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 12.7409 | 2.6839 | 45.3361 | 0.28103 | 5.23 | 6.11 | 6.38 | 5.955 | 78.87 | 190.488 | 294.4448 | -54.5739 | 92.4496 | 274.3451 | 97.8294 | [16 empty] | SDS-TOX | mg Cl- /L | BMRL | 179.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 268.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 136.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 195.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 136.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 136.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Rejection of reference solute and conditions of test | 99.6 |  | Estimated system pressure losses, DPloss (psi) | 2 |  |  |  |  | 27 | 1998-06-11 | 10:30 | 593.43 | 21.89 | 82.25 | 79.81 | 30.01 | 3.97 | 0.68 | 0.28 | X | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 13.0943 | 2.3626 | 48.6574 | 0.26911 | 5.25 | 6.37 | 6.61 | 7.33 | 81.342 | 252.76 | 261.0854 | -3.2938 | 90.9887 | 243.5851 | 96.9908 | [16 empty] | SDS-CHCl3 | mg/L | 2.9 | 32 | --- | 124.15 | --- | 90.9375 | 114.9922 | 97.4781 | SDS-CHCl3 | mg/L | 2 | 36 | --- | 119.2414 | --- | 94.4444 | 111.3136 | 98.2033 | SDS-CHCl3 | mg/L | 4 | 32 | --- | 116 | --- | 87.5 | 108.168 | 96.302 | SDS-CHCl3 | mg/L | 1.6 | 49.6 | --- | 193.6 | --- | 96.7742 | 180.4697 | 99.1134 | SDS-CHCl3 | mg/L | 0.9 | 61.9 | --- | 305.9 | --- | 98.546 | 284.8655 | 99.6841 | SDS-CHCl3 | mg/L | 0.7 | 62.6 | --- | 310.2 | --- | 98.8818 | 288.8552 | 99.7577
|  |  | (e.g., solute type and concentration) | (mg/L MgSO4) |  | Design permeate pressure, Pp (psi) | 30 |  |  |  |  | 28 | 1998-06-12 | 16:00 | 615.43 | 24.33 | 72.33 | 69.89 | 29.52 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.0388 | 2.3962 | 39.1938 | 0.30716 | 5.27 | 6.07 | 6.35 | 7.555 | 72.546 | 186.824 | 264.6933 | -41.6806 | 89.5859 | 247.1729 | 96.9434 | [16 empty] | SDS-BDCM | mg/L | BMRL | 6.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 8.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.1 | 6.6 | --- | 23.1 | --- | 83.3333 | 21.5616 | 94.8983 | SDS-BDCM | mg/L | BMRL | 8.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 9.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 9.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Variability of rejection of reference solute (%) | 95 min. |  | Required influent pressure, PI (psi) | 80.8246 |  |  |  |  | 29 | 1998-06-13 | 16:00 | 639.43 | 25.37 | 73.25 | 70.35 | 30.07 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 11.6201 | 2.5041 | 39.2259 | 0.29623 | 5.26 | 6.06 | 6.33 | 7.1 | 75.018 | 208.8 | 275.819 | -32.0972 | 90.5356 | 257.5095 | 97.2428 | [16 empty] | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 0.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing recovery (%) | 15 | [7 empty] | 30 | 1998-06-14 | 16:00 | 663.43 | 25 | 73.4 | 70.65 | 29.8 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 11.767 | 2.5802 | 39.6448 | 0.29681 | 5.26 | 6.03 | 6.35 | 6.41 | 76.392 | 194.152 | 283.2953 | -45.9142 | 91.6091 | 264.4294 | 97.5759 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing pH | 8 | [7 empty] | 31 | 1998-06-15 | 16:00 | 684.43 | 26.1 | 72.94 | 70.5 | 29.31 | 4.08 | 0.68 | 0.11 |  | 0.79 | 4.87 | 0.34607 | 0.86076 | 5.1646 | 13.9886 | 11.3365 | 4.4703 | 37.9397 | 0.2988 | 5.26 | 6.05 | 6.36 | 7.555 | 74.472 | 245.432 | 488.1407 | -98.8904 | 89.8552 | 454.5885 | 98.3381 | [16 empty] | SDS-THM4 | mg/L | 2.9 | 38.8 | --- | 152.4833 | --- | 92.5258 | 141.1856 | 97.946 | SDS-THM4 | mg/L | 2 | 45.5 | --- | 152 | --- | 95.6044 | 141.8571 | 98.5901 | SDS-THM4 | mg/L | 5.1 | 38.6 | --- | 139.1 | --- | 86.7876 | 129.7296 | 96.0687 | SDS-THM4 | mg/L | 1.6 | 59.4 | --- | 232.8 | --- | 97.3064 | 216.989 | 99.2626 | SDS-THM4 | mg/L | 0.9 | 72.5 | --- | 358.9 | --- | 98.7586 | 334.2103 | 99.7307 | SDS-THM4 | mg/L | 0.7 | 73.5 | --- | 364.7 | --- | 99.0476 | 339.5966 | 99.7939
|  |  | Acceptable range of operating pressures | 250 max. | [7 empty] | 32 | 1998-06-16 | 16:00 | 711.43 | 25.72 | 74.47 | 71.72 | 29.62 | 4.08 | 0.68 | 0.11 |  | 0.79 | 4.87 | 0.34607 | 0.86076 | 5.1646 | 13.9886 | 11.4831 | 4.7699 | 38.7051 | 0.29668 | 5.29 | 6.35 | 6.62 | 8.015 | 79.416 | 249.096 | 520.804 | -109.0776 | 89.9076 | 485.0035 | 98.3474 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Acceptable range of operating pH values | 3 - 9 | [7 empty] | 33 | 1998-06-17 | 16:00 | 723.93 | 25.46 | 72.79 | 70.35 | 31.11 | 3.87 | 0.73 | 0.23 |  | 0.96 | 4.83 | 0.34111 | 0.76042 | 4.0312 | 15.0171 | 12.4365 | 2.6578 | 37.8022 | 0.32899 | 5.25 | 6.22 | 6.45 | 7.785 | 76.668 | 256.424 | 295.2967 | -15.1595 | 89.8458 | 273.5696 | 97.1543 | [16 empty] | SDS-DCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 15 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 3.3 | 16 | --- | 54.1 | --- | 79.375 | 50.5476 | 93.4715 | SDS-DCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Typical pressure drop across a single element (psi) | 3 - 5 | [7 empty] | 34 | 1998-06-18 | 16:00 | 747.93 | 26.79 | 72.79 | 70.35 | 31.11 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 11.8905 | 3.4408 | 37.0192 | 0.3212 | 5.32 | 6.22 | 6.47 | 6.41 | 76.668 | 230.784 | 378.3641 | -63.9473 | 91.6393 | 350.4867 | 98.1711 | [16 empty] | SDS-TCAA* | mg/L | 1 | 23 | --- | 92.6667 | --- | 95.6522 | 85.7433 | 98.8337 | SDS-TCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible SDI | 5 | [7 empty] | 35 | 1998-06-19 | 16:00 | 771.93 | 25.55 | 73.1 | 70.2 | 30.59 | 3.97 | 0.68 | 0.34 |  | 1.02 | 4.99 | 0.35524 | 0.66667 | 3.8922 | 13.9886 | 11.5494 | 1.9334 | 39.1266 | 0.29518 | 5.25 | 6.14 | 6.33 | 6.41 | 75.57 | 190.488 | 213.89 | -12.2853 | 91.5178 | 199.7531 | 96.791 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 36 | 1998-06-20 | 16:00 | 795.93 | 26.16 | 73.1 | 70.35 | 30.26 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 11.3136 | 2.6096 | 38.8554 | 0.29117 | 5.28 | 6.19 | 6.43 | 6.87 | 77.766 | 205.136 | 287.3716 | -40.0883 | 91.1658 | 267.8284 | 97.4349 | [16 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | [7 empty] | 37 | 1998-06-21 | 16:00 | 819.93 | 27.17 | 72.33 | 69.74 | 29.65 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.9358 | 2.5793 | 38.8057 | 0.28181 | 5.27 | 6.12 | 6.38 | 6.87 | 76.944 | 223.456 | 284.1193 | -27.1478 | 91.0714 | 264.8028 | 97.4056 | [16 empty] | SDS-BCAA* | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 38 | 1998-06-22 | 8:30 | 836.43 | 26.36 | 72.18 | 69.43 | 29.22 | 3.87 | 0.68 | 0.28 | X | 0.96 | 4.83 | 0.34302 | 0.70833 | 4.0312 | 13.9886 | 11.2376 | 2.2146 | 39.3704 | 0.28543 | 5.25 | 6.1 | 6.35 | 5.265 | 74.748 | 194.152 | 243.4924 | -25.4133 | 92.9563 | 226.7228 | 97.6778 | [16 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 39 | 1998-06-22 | 19:00 | 839.2633 | 26.57 | 71.26 | 68.82 | 31.29 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 11.9788 | 2.5445 | 36.2055 | 0.33086 | 5.14 | 6.13 | 6.33 | 8.475 | 74.196 | 197.816 | 282.7887 | -42.9554 | 88.5776 | 262.9228 | 96.7766 | [16 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 40 | 1998-06-23 | 16:00 | 860.2633 | 27.15 | 72.18 | 70.35 | 32.21 | 3.97 | 0.68 | 0.17 |  | 0.85 | 4.82 | 0.34225 | 0.8 | 4.6706 | 13.9886 | 10.9431 | 3.182 | 35.873 | 0.30505 | 5.33 | 6.27 | 6.47 | 7.1 | 75.57 | 223.456 | 349.45 | -56.3843 | 90.6047 | 325.3008 | 97.8174 | [16 empty] | SDS-DCBAA | mg/L | BMRL | 6.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 3.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 3.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Field 1-5: Pretreatment Used Prior To Membranes1 | [11 empty] | 41 | 1998-06-24 | 16:00 | 884.2633 | 26.47 | 72.18 | 69.74 | 31.32 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 12.0192 | 2.5837 | 37.0563 | 0.32435 | 5.3 | 6.16 | 6.43 | 6.64 | 73.374 | 172.168 | 285.1819 | -65.6416 | 90.9505 | 265.0097 | 97.4944 | [16 empty] | SDS-HAA5 | mg/L | 1 | 39 | --- | 159.3333 | --- | 97.4359 | 147.3747 | 99.3215 | SDS-HAA5 | mg/L | 0 | 33 | --- | 113.7931 | --- | 100 | 106.0985 | 100 | SDS-HAA5 | mg/L | 3.3 | 35 | --- | 130.1 | --- | 90.5714 | 121.2331 | 97.278 | SDS-HAA5 | mg/L | 0 | 46 | --- | 184 | --- | 100 | 171.4168 | 100 | SDS-HAA5 | mg/L | 0 | 49 | --- | 245 | --- | 100 | 228.1034 | 100 | SDS-HAA5 | mg/L | 0 | 48 | --- | 240 | --- | 100 | 223.4483 | 100
[12 empty] | 42 | 1998-06-25 | 16:00 | 908.2633 | 27.49 | 72.33 | 69.74 | 31.51 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35257 | 0.81111 | 4.5333 | 15.0171 | 11.6148 | 3.1953 | 36.3297 | 0.3197 | 5.3 | 6.16 | 6.39 | 6.87 | 72 | 183.16 | 351.6759 | -92.0047 | 90.4583 | 326.404 | 97.8952 | [16 empty] | SDS-HAA6 | mg/L | 1 | 42.2 | --- | 172.6667 | --- | 97.6303 | 159.701 | 99.3738 | SDS-HAA6 | mg/L | 0 | 35.9 | --- | 123.7931 | --- | 100 | 115.4223 | 100 | SDS-HAA6 | mg/L | 3.3 | 38.2 | --- | 142.9 | --- | 91.3613 | 133.138 | 97.5214 | SDS-HAA6 | mg/L | 0 | 49.4 | --- | 197.6 | --- | 100 | 184.0868 | 100 | SDS-HAA6 | mg/L | 0 | 52.7 | --- | 263.5 | --- | 100 | 245.3276 | 100 | SDS-HAA6 | mg/L | 0 | 51.5 | --- | 257.5 | --- | 100 | 239.7414 | 100
Process | Description | [8 empty] | Scale |  | 43 | 1998-06-26 | 9:30 | 925.7633 | 26.24 | 72.03 | 69.43 | 30.53 | 4.08 | 0.68 | 0.23 | X | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 11.2831 | 2.3015 | 37.8985 | 0.29772 | 5.33 | 6.13 | 6.36 | 7.1 | 69.522 | 190.488 | 254.074 | -33.3806 | 89.7874 | 237.2461 | 97.0073 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Rapid Mix | Type: | Mechanical | [7 empty] | Full |  | 44 | 1998-06-27 | 16:00 | 931.0967 | 28.56 | 70.5 | 68.21 | 32.76 | 4.08 | 0.73 | 0.11 |  | 0.84 | 4.92 | 0.34798 | 0.86905 | 4.8571 | 15.0171 | 11.2079 | 4.5264 | 32.0686 | 0.3495 | 5.38 | 6.23 | 6.53 | 9.62 | 73.644 | 201.472 | 498.5305 | -147.4441 | 86.9372 | 462.2597 | 97.9189 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
| Chemical Name: | Alum |  |  |  | Powdered Activated Carbon (PAC) | [5 empty] | 45 | 1998-06-28 | 16:00 | 955.0967 | 27.81 | 71.26 | 69.74 | 32.12 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.7042 | 2.386 | 35.994 | 0.29739 | 5.33 | 6.11 | 6.36 | 7.555 | 72.27 | 208.8 | 263.6013 | -26.2458 | 89.5461 | 246.1553 | 96.9308 | [16 empty] | ** Misdosed chlorine for Permeate SDS
| Chemical Formula: | Al2(SO4)3*14H2O | [9 empty] | 46 | 1998-06-29 | 16:00 | 979.0967 | 27.47 | 71.26 | 68.98 | 31.51 | 4.18 | 0.68 | 0.17 |  | 0.85 | 5.03 | 0.3583 | 0.8 | 4.9176 | 13.9886 | 10.8265 | 3.1494 | 35.4606 | 0.30531 | 5.33 | 6.18 | 6.48 | 8.015 | 75.57 | 223.456 | 345.79 | -54.7463 | 89.3939 | 322.9583 | 97.5183 | [26 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
| Dose: | AVG | MAX | MIN | STD DEV | AVG | MAX | MIN | STD DEV |  |  | 47 | 1998-06-30 | 16:00 | 1003.0967 | 28.62 | 70.65 | 68.52 | 31.41 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.4194 | 2.5482 | 35.6268 | 0.29246 | 5.23 | 6.15 | 6.41 | 7.555 | 76.668 | 230.784 | 281.0021 | -21.7598 | 90.1458 | 262.3704 | 97.1205 | [16 empty] | Blending Calculations For D-DBP MCLs | [10 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  | 30.1 | 49.7 | 20.6 | 7.15 | 2.36 | 6.47 | 0 | 1.36 |  |  | 48 | 1998-07-01 | 16:00 | 1026.7967 | 28.53 | 69.43 | 66.99 | 31.23 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 10.4506 | 1.8947 | 35.0853 | 0.29786 | 5.25 | 5.83 | 6.07 | 8.245 | 67.602 | 179.496 | 211.7547 | -17.9718 | 87.8036 | 197.7196 | 95.83 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
Flocculation | Type: | Mechanical | [7 empty] | Full |  | 49 | 1998-07-02 | 16:00 | 1050.7967 | 28.48 | 70.65 | 68.06 | 29.86 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 11.2377 | 2.1792 | 37.3158 | 0.30115 | 5.21 | 5.8 | 6.09 | 8.015 | 64.302 | 164.84 | 242.952 | -47.3866 | 87.5354 | 225.9378 | 96.4526 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Qp/QT (THM4), % | -60.9195 | 21.8391 |  | Qp/QT (HAA5), % | -63.6364 | 18.1818 |  |  |  | Qp/QT (THM4), % | -99.7015 | 7.7612 |  | Qp/QT (HAA5), % | -59.9369 | 25.2366 |  |  |  | Qp/QT (THM4), % | -21.7993 | 40.4844 |  | Qp/QT (HAA5), % | -17.3913 | 41.3043 |  |  |  | Qp/QT (THM4), % | 0.69832 | 50.9777 |  | Qp/QT (HAA5), % | -10.2041 | 44.898 |  |  |  | Qp/QT (THM4), % | 2.0604 | 51.511 |  | Qp/QT (HAA5), % | -12.5 | 43.75
Sedimentation | Type: | Conventional | [7 empty] | Full |  | 50 | 1998-07-03 | 16:00 | 1074.7967 | 28.14 | 70.2 | 67.45 | 28.12 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 10.5871 | 2.7803 | 37.9247 | 0.27916 | 5.27 | 6.19 | 6.45 | 8.7 | 68.424 | 179.496 | 307.32 | -71.2127 | 87.2852 | 286.7255 | 96.9657 | [16 empty] | Qp/QT (THM4), % | -92.4791 | 7.7994 |  | Qp/QT (HAA5), % | -39.4737 | 31.5789 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 37.5909 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 30.1457 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 35.5261 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 40.3531 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 41.65
Filtration | Type: | Dual Media - Anthracite/Sand | [7 empty] | Pilot |  | 51 | 1998-07-04 | 16:00 | 1098.7967 | 28.13 | 69.59 | 66.84 | 28.03 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.5906 | 1.8895 | 38.2955 | 0.27655 | 5.43 | 5.94 | 6.41 | 11.68 | 62.928 | 230.784 | 214.4438 | 7.0803 | 81.4391 | 200.6283 | 94.1783 | [16 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 27.4632 |  |  |  | SDS-HAA5b, mg/L | NA | 25.7931 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 32.5397 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 27.3772 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | 48.6578 | 24.0209 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | 47.011 | 23.2747 |  | SDS-HAA5b, mg/L | NA | 27
[12 empty] | 52 | 1998-07-05 | 16:00 | 1122.7967 | 27.6 | 69.13 | 66.23 | 26.23 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 10.7795 | 2.7867 | 38.6633 | 0.2788 | 5.29 | 6.36 | 6.58 | 8.015 | 67.878 | 201.472 | 307.33 | -52.5423 | 88.1921 | 286.6876 | 97.2043 | [16 empty] | SDS-HAA5b, mg/L | NA | 36.0362 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE!
1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [11 empty] | 53 | 1998-07-06 | 22:00 | 1135.8967 | 27.11 | 70.35 | 67.45 | 30.38 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.9578 | 2.1565 | 36.3635 | 0.30134 | 5.28 | 6.08 | 6.35 | 6.64 | 65.13 | 157.52 | 238.057 | -51.1281 | 89.805 | 222.2891 | 97.0129 | [16 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-CDb, mg/L | NA | 1.9294 |  | SDS-CDb, mg/L | NA | 1.9664 |  |  |  | SDS-CDb, mg/L | NA | 1.8106 |  | SDS-CDb, mg/L | NA | 1.5642 |  |  |  | SDS-CDb, mg/L | NA | 1.932 |  | SDS-CDb, mg/L | NA | 1.915 |  |  |  | SDS-CDb, mg/L | 3.2213 | 1.8738 |  | SDS-CDb, mg/L | NA | 2.0367 |  |  |  | SDS-CDb, mg/L | 3.1573 | 1.8913 |  | SDS-CDb, mg/L | NA | 2.09
the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [11 empty] | 54 | 1998-07-07 | 16:00 | 1153.8967 | 27.03 | 70.35 | 67.6 | 30.07 | 4.18 | 0.68 | 0.28 |  | 0.96 | 5.14 | 0.3667 | 0.70833 | 4.3542 | 13.9886 | 10.9872 | 1.8066 | 37.0984 | 0.29616 | 5.21 | 5.79 | 6.01 | 7.33 | 63.756 | 186.824 | 200.7906 | -7.4758 | 88.503 | 187.9936 | 96.1009 | [16 empty] | SDS-CDb, mg/L | NA | 2.2524 |  | SDS-CDb, mg/L | NA | 1.9242 |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE!
is to list the pretreatment processes used in this particular Long-Term SEBST run. | [11 empty] | 55 | 1998-07-08 | 16:00 | 1178.6467 | 26.98 | 73.4 | 70.2 | 29.89 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 11.8149 | 1.8786 | 40.0314 | 0.29514 | 5.2 | 5.79 | 6.06 | 7.1 | 63.204 | 172.168 | 209.4751 | -21.669 | 88.7665 | 194.963 | 96.3583 | [16 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | 0.052352 |  | UV254 b, cm-1 | NA | 0.044139 |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE!
[12 empty] | 56 | 1998-07-09 | 16:00 | 1202.6467 | 27.82 | 74.77 | 71.87 | 31.41 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 10.7006 | 2.5691 | 39.3409 | 0.272 | 5.23 | 5.83 | 6.08 | 8.015 | 63.204 | 179.496 | 283.96 | -58.1985 | 87.3188 | 264.9293 | 96.9747 | [16 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE!
[12 empty] | 57 | 1998-07-10 | 16:00 | 1226.6467 | 28.13 | 77.52 | 74.93 | 32.67 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 11.3693 | 2.642 | 40.913 | 0.27789 | 5.24 | 5.85 | 6.08 | 7.33 | 61.278 | 223.456 | 292.9371 | -31.0938 | 88.0381 | 271.5312 | 97.3005 | [16 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | 10.8161 |  | Alkb, mg/L CaCO3 | NA | 11.1818 |  |  |  | Alkb, mg/L CaCO3 | NA | 9.3015 |  | Alkb, mg/L CaCO3 | NA | 7.7287 |  |  |  | Alkb, mg/L CaCO3 | NA | 6.3806 |  | Alkb, mg/L CaCO3 | NA | 6.3478 |  |  |  | Alkb, mg/L CaCO3 | 6.9721 | 4.9609 |  | Alkb, mg/L CaCO3 | NA | 5.2041 |  |  |  | Alkb, mg/L CaCO3 | 6.9176 | 4.9396 |  | Alkb, mg/L CaCO3 | NA | 5.25
[12 empty] | 58 | 1998-07-11 | 16:00 | 1250.6467 | 27.92 | 73.86 | 71.57 | 30.23 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 10.665 | 1.6856 | 40.7994 | 0.2614 | 5.28 | 5.86 | 6.14 | 7.1 | 59.904 | 168.504 | 188.1423 | -11.6545 | 88.1477 | 175.6566 | 95.958 | [16 empty] | Alkb, mg/L CaCO3 | NA | 9.376 |  | Alkb, mg/L CaCO3 | NA | 7.4737 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 31.3218 |  | T-Hdb, mg/L CaCO3 | NA | 32.2727 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 46.8179 |  | T-Hdb, mg/L CaCO3 | NA | 39.653 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 22.8304 |  | T-Hdb, mg/L CaCO3 | NA | 22.5435 |  |  |  | T-Hdb, mg/L CaCO3 | 32.8045 | 18.7263 |  | T-Hdb, mg/L CaCO3 | NA | 20.4286 |  |  |  | T-Hdb, mg/L CaCO3 | 32.4231 | 18.5769 |  | T-Hdb, mg/L CaCO3 | NA | 20.75
[12 empty] | 59 | 1998-07-12 | 16:00 | 1274.6467 | 29.41 | 74.62 | 72.03 | 30.29 | 4.08 | 0.68 | 0.11 |  | 0.79 | 4.87 | 0.34607 | 0.86076 | 5.1646 | 13.9886 | 10.1504 | 3.5309 | 39.5041 | 0.25695 | 5.34 | 6.06 | 6.32 | 8.7 | 61.554 | 238.104 | 388.2878 | -63.0749 | 85.8661 | 361.7868 | 97.5953 | [16 empty] | T-Hdb, mg/L CaCO3 | NA | 47.5682 |  | T-Hdb, mg/L CaCO3 | NA | 37.1053 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE!
[12 empty] | 60 | 1998-07-13 | 16:00 | 1298.6467 | 28.45 | 74.47 | 70.65 | 28.85 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.4784 | 1.9538 | 41.7562 | 0.25094 | 5.29 | 5.89 | 6.15 | 7.1 | 60.18 | 190.488 | 217.1122 | -13.9768 | 88.2021 | 202.4802 | 96.4935 | [16 empty] | Ca-Hdb, mg/L CaCO3 | NA | 29.6602 |  | Ca-Hdb, mg/L CaCO3 | NA | 22.5263 | [13 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[12 empty] | 61 | 1998-07-14 | 16:00 | 1322.6467 | 28.21 | 79.81 | 76.3 | 30.84 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.5624 | 2.006 | 45.209 | 0.23363 | 5.3 | 5.91 | 6.14 | 6.87 | 61.278 | 186.824 | 222.1364 | -18.9014 | 88.7888 | 207.469 | 96.6887 | [26 empty] | Notes: | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[12 empty] | 62 | 1998-07-15 | 16:00 | 1346.6467 | 28.02 | 81.03 | 77.37 | 30.04 | 4.08 | 0.63 | 0.17 |  | 0.8 | 4.88 | 0.34875 | 0.7875 | 5.1 | 12.96 | 9.8479 | 2.3792 | 46.7808 | 0.21051 | 5.27 | 5.93 | 6.24 | 6.41 | 60.456 | 197.816 | 260.7441 | -31.8114 | 89.3972 | 244.3271 | 97.3765 | [26 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[12 empty] | 63 | 1998-07-16 | 9:00 | 1364.1467 | 27.72 | 85.76 | 82.1 | 31.48 | 3.97 | 0.73 | 0.28 | X | 1.01 | 4.98 | 0.35257 | 0.72277 | 3.9307 | 15.0171 | 11.5258 | 1.7667 | 50.6833 | 0.22741 | 5.27 | 5.87 | 6.09 | 7.33 | 60.18 | 212.464 | 197.9675 | 6.823 | 87.8199 | 183.9951 | 96.0162 | [16 empty] | Notes: | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[12 empty] | 64 | 1998-07-17 | 15:30 | 1382.47 | 28.19 | 77.98 | 74.77 | 30.9 | 4.08 | 0.73 | 0.11 |  | 0.84 | 4.92 | 0.34798 | 0.86905 | 4.8571 | 15.0171 | 11.3466 | 3.6299 | 41.8451 | 0.27116 | 5.3 | 6.11 | 6.35 | 8.015 | 59.358 | 230.784 | 400.0888 | -73.3607 | 86.4972 | 371.002 | 97.8396 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[12 empty] | 65 | 1998-07-18 | 15:00 | 1405.97 | 29.24 | 76.61 | 73.86 | 30.62 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 10.9582 | 1.9558 | 42.6592 | 0.25688 | 5.28 | 6.01 | 6.26 | 6.64 | 57.156 | 172.168 | 217.4894 | -26.3239 | 88.3827 | 202.2195 | 96.7164 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[12 empty] | 66 | 1998-07-19 | 13:30 | 1430.47 | 30.39 | 76.15 | 72.94 | 30.29 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 9.8282 | 1.9219 | 42.3331 | 0.23216 | 5.33 | 5.99 | 6.27 | 5.495 | 57.708 | 205.136 | 212.0769 | -3.3835 | 90.4779 | 197.6839 | 97.2203 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[12 empty] | 67 | 1998-07-20 | 14:30 | 1454.47 | 30.4 | 75.69 | 72.33 | 29.83 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 9.825 | 2.486 | 41.694 | 0.23565 | 5.32 | 5.98 | 6.33 | 5.955 | 59.358 | 212.464 | 272.97 | -28.4782 | 89.9677 | 254.5552 | 97.6606 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[12 empty] | 68 | 1998-07-21 | 15:30 | 1476 | 31.71 | 75.99 | 72.33 | 30.47 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 9.4134 | 2.4113 | 41.2787 | 0.22805 | 5.31 | 5.97 | 6.26 | 6.185 | 57.984 | 194.152 | 265.18 | -36.5837 | 89.3333 | 247.3183 | 97.4992 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[12 empty] | 69 | 1998-07-22 | 16:00 | 1501 | 32.41 | 75.99 | 72.18 | 29.92 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 9.202 | 1.9015 | 42.2635 | 0.21773 | 5.32 | 5.94 | 6.22 | 6.87 | 58.53 | 157.52 | 211.2639 | -34.1188 | 88.2624 | 197.0234 | 96.5131 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[12 empty] | 70 | 1998-07-23 | 16:00 | 1525 | 32.43 | 75.84 | 71.72 | 29.55 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 8.5199 | 1.8791 | 42.3509 | 0.20117 | 5.33 | 5.99 | 6.24 | 5.955 | 59.634 | 194.152 | 206.6678 | -6.4464 | 90.0141 | 193.8693 | 96.9283 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[61 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on K13: C. Rice: Consultant verified the decrease in aluminum concentration from the raw to the filtered water; no explanation was given.
Note on K14: C. Rice: The "Pilot Filtered" sulfate is higher than the raw water concentration because aluminum sulfate was added for coagulation.
Note on AA74: S Allgeier (8/15/99): Temp. probe corrected
Note on AS5: TSC_ADM: Operational TDS data is based on an empirical factor applied to the on-line conductivity measurements (compared to the biweekly TDS data, which are based on lab measurements); therefore, there may be discrepancies between the operational and biweekly TDS data.
Note on CB32: C. Rice: Consultant verified value; no explanation given.
Note on CJ33: C. Rice: Consultant verified the increase in feed CHCl3 concentration between weeks 6 and 10; no explanation was given.
Note on CU33: C. Rice: Consultant verified the increase in feed CHCl3 concentration between weeks 6 and 10; no explanation was given.
Note on DF33: C. Rice: Consultant verified the increase in feed CHCl3 concentration between weeks 6 and 10; no explanation was given.

## NF70. Weeks 11-20
FIELD-SET 2: LT-SEBST RESULTS: WEEKS 11-20 (FILE: ltsebst.xls)
Field 2-1: PWS And Treatment Plant Data |  |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  |  | Field 2-3: SEBST Design Parameters |  |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [47 empty] | Field 2-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 12 | [9 empty] | Field 2-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 14 | [9 empty] | Field 2-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 16 | [9 empty] | Field 2-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 18 | [9 empty] | Field 2-11: Permeate, Feed, Concentrate And Blended Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 20 | [9 empty] | Field 2-13: Membrane Cost Parameters
|  |  | General Information |  |  | Calculate Temperature Normalized MTCW |  |  | Parameters Evaluated Prior to Pretreatment |  | (see cell A47) | [49 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | City of Norfolk |  | Membrane manufacturer | FilmTec |  | Average yearly temperature of feed water, TavgoC (oC) | 20 |  | PLANT FILTERED WATER: |  |  | Day No. | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.79 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.92 | [8 empty] | Recovery during sample collection (decimal) | 0.92 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | VA37010100 |  | Membrane trade name | NF70 |  | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.30143 |  | Alkalinity (mg/L as CaCO3) | 10.5 |  |  | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.8 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.74 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.74 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA |  | Membrane element model number | NF70-4040 |  |  |  |  | pH (units) | 6.44 |  | 71 | 1998-07-24 | 16:00 | 1549 | 31.74 | 74.77 | 71.72 | 28.82 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 8.7128 | 1.8569 | 42.5681 | 0.20468 | 5.35 | 5.94 | 6.23 | 7.33 | 60.456 | 212.464 | 205.975 | 3.0541 | 87.8755 | 193.0199 | 96.2025 | [17 empty] | Influent flow rate during sample collection (gpm) | 4.88 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.88 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.88 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.99 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.82 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.82 | [7 empty] | Capital Recovery Period (years) | 20
|  |  | Molecular weight cutoff (Daltons) | 200 |  | Calculate System Flow Rates1 |  |  | Total Dissolved Solids | 73 mg/L |  | 72 | 1998-07-25 | 16:00 | 1573 | 31.22 | 76.45 | 72.79 | 28.85 | 3.97 | 0.63 | 0.17 |  | 0.8 | 4.77 | 0.34034 | 0.7875 | 4.9625 | 12.96 | 8.7128 | 2.3006 | 43.4694 | 0.20043 | 5.34 | 6.04 | 6.31 | 6.185 | 58.53 | 190.488 | 252.5144 | -32.5618 | 89.4328 | 236.2474 | 97.382 | [76 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide |  | Design recovery, R (decimal) | 0.75 |  | Conductivity | 129 umhos/cm |  | 73 | 1998-07-26 | 16:00 | 1597 | 30.15 | 76.76 | 73.1 | 27.72 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 9.5649 | 2.0467 | 45.1633 | 0.21178 | 5.3 | 5.98 | 6.28 | 5.495 | 61.008 | 168.504 | 225.1334 | -33.6071 | 90.993 | 210.1681 | 97.3854 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  |  | Membrane construction (e.g., thin-film composite) | Thin-film composite |  | Design flux, FW (gfd) | 14.4 |  | SDI | 5.8 |  | 74 | 1998-07-27 | 16:00 | 1621 | 30.29 | 76.91 | 73.55 | 27.33 | 3.97 | 0.63 | 0.17 |  | 0.8 | 4.77 | 0.34034 | 0.7875 | 4.9625 | 12.96 | 9.1776 | 2.2384 | 45.6616 | 0.20099 | 5.32 | 5.98 | 6.25 | 7.33 | 58.26 | 190.488 | 247.0006 | -29.6673 | 87.4185 | 231.1733 | 96.8292 | [16 empty] | Parameter | Units | Cp-12 | CF-12 | CC-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-14 | CF-14 | CC-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-16 | CF-16 | CC-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-18 | CF-18 | CC-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-20 | CF-20 | CC-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-20 (dup) | CF-20 (dup) | CC-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 15
|  |  | Membrane hydrophobicity | Hydrophobic |  | Permeate flow rate, Qp (gpm) | 0.7 |  | Turbidity (ntu) | 0.26 |  | 75 | 1998-07-28 | 16:00 | 1645 | 30.66 | 76.3 | 73.1 | 27.02 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 9.1355 | 1.8937 | 45.7863 | 0.19952 | 5.34 | 5.92 | 6.2 | 5.725 | 59.904 | 201.472 | 208.3073 | -3.3927 | 90.443 | 195.0955 | 97.0655 | [16 empty] | Sampling date | MM/DD/YY | 1998-08-06 | 1998-08-06 | 1998-08-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-20 | 1998-08-20 | 1998-08-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-04 | 1998-09-04 | 1998-09-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-17 | 1998-09-17 | 1998-09-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-01 | 1998-10-01 | 1998-10-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-01 | 1998-10-01 | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 9
Phone Number |  |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative |  | Feed flow rate, QF (gpm) | 0.93333 |  | Dissolved aluminum (mg/L) | <0.044 |  | 76 | 1998-07-29 | 16:00 | 1669 | 31.83 | 86.83 | 82.86 | 30.23 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 10.4579 | 1.7576 | 52.8574 | 0.19785 | 5.37 | 5.99 | 6.32 | 5.495 | 57.984 | 168.504 | 194.8303 | -15.6236 | 90.5232 | 181.2532 | 96.9683 | [16 empty] | Sampling time | hh:mm | 11:10 | 11:20 | 11:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:10 | 13:20 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:15 | 9:25 | 9:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:30 | 13:50 | 14:10 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:30 | 13:50 | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | Concentrate-waste flow rate, QW (gpm) | 0.23333 |  | Total aluminum (mg/L) | 0.074 |  | 77 | 1998-07-30 | 16:00 | 1693 | 32.98 | 87.9 | 83.78 | 29.92 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 10.0662 | 2.0233 | 53.8967 | 0.18677 | 5.4 | 5.99 | 6.27 | 5.725 | 57.984 | 197.816 | 223.8495 | -13.1605 | 90.1266 | 208.0528 | 97.2483 | [16 empty] | Operation time | hh.hh | 1856 | 1856 | 1856 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2145 | 2145 | 2145 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2488 | 2488 | 2488 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2786 | 2786 | 2786 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3118 | 3118 | 3118 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3118 | 3118 | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131.8
E-Mail Address (optional) |  |  | Design Parameters |  |  | Minimum influent flow rate, QI, min (gpm) | 4 |  | PILOT FILTERED: Sulfate (mg/L) | 43 |  | 78 | 1998-07-31 | 16:00 | 1717 | 30.78 | 88.97 | 84.85 | 29.22 | 4.08 | 0.68 | 0.11 |  | 0.79 | 4.87 | 0.34607 | 0.86076 | 5.1646 | 13.9886 | 9.034 | 3.4727 | 54.2173 | 0.16663 | 5.39 | 6.23 | 6.52 | 5.725 | 57.708 | 227.12 | 379.0575 | -66.8974 | 90.0794 | 352.9932 | 98.3782 | [16 empty] | pH | --- | 5.8 | 6.12 | 6.49 | --- | --- | --- | --- | --- | pH | --- | 6.6 | 6.93 | 7.58 | --- | --- | --- | --- | --- | pH | --- | 6.84 | 7.39 | 8.22 | --- | --- | --- | --- | --- | pH | --- | 6.93 | 6.75 | 6.81 | --- | --- | --- | --- | --- | pH | --- | 6.94 | 6.89 | 8.36 | --- | --- | --- | --- | --- | pH | --- | 6.95 | 6.91 | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.65
|  |  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" |  | Maximum influent flow rate, QI, max (gpm) | 16 |  | RAW WATER: |  |  | 79 | 1998-08-01 | 16:00 | 1741 | 30.61 | 93.39 | 89.42 | 30.35 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 9.7034 | 2.0264 | 59.0286 | 0.16439 | 5.35 | 5.9 | 6.12 | 5.495 | 60.456 | 205.136 | 222.9494 | -8.6837 | 90.9107 | 208.1329 | 97.3599 | [16 empty] | Temperature | oC | 28.7778 | 27.8333 | 29.2222 | --- | --- | --- | --- | --- | Temperature | oC | 27.8333 | 28.3333 | 27.6667 | --- | --- | --- | --- | --- | Temperature | oC | 28.3889 | 27.8889 | 28.5556 | --- | --- | --- | --- | --- | Temperature | oC | 26.7222 | 26.4444 | 26.6667 | --- | --- | --- | --- | --- | Temperature | oC | 28 | 27.6 | 28.8 | --- | --- | --- | --- | --- | Temperature | oC | 28 | 27.4 | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 30
Technical ICR Contact Person |  |  | Active membrane area of membrane element used, A (ft2) | 70 |  | Design influent flow rate2, QI (gpm) | 4.93 |  | Dissolved iron (mg/L) | 0.2 |  | 80 | 1998-08-02 | 16:00 | 1765 | 29.36 | 97.51 | 93.85 | 30.62 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 9.7576 | 1.9826 | 63.0774 | 0.15469 | 5.37 | 6.04 | 6.32 | 6.87 | 60.732 | 216.128 | 219.9762 | -1.7805 | 88.688 | 205.1286 | 96.6509 | [16 empty] | Alkalinity | mg/L as CaCO3 | 3 | 6 | 18 | 17.2857 | 3.9683 | 50 | 16.3607 | 81.6633 | Alkalinity | mg/L as CaCO3 | 3 | 18 | 67 | 63 | 5.9701 | 83.3333 | 58.8043 | 94.8983 | Alkalinity | mg/L as CaCO3 | 5 | 18 | 74 | 57 | 22.973 | 72.2222 | 53.3637 | 90.6303 | Alkalinity | mg/L as CaCO3 | 3 | 13 | 72 | 43 | 40.2778 | 76.9231 | 40.2645 | 92.5493 | Alkalinity | mg/L as CaCO3 | 5 | 17 | 127 | 155 | -22.0472 | 70.5882 | 144.4066 | 96.5376 | Alkalinity | mg/L as CaCO3 | 5 | 17 | NA | 155 | #VALUE! | 70.5882 | 144.4066 | 96.5376 | Electric Rate ($/kW-h) | 0.049
Mailing Address |  |  | Design flux, FW (gfd) | 14.4 |  | Design recycle flow rate, QR (gpm) | 3.9967 |  | Total iron (mg/L) | 0.6 |  | 81 | 1998-08-03 | 16:00 | 1789 | 29.12 | 96.44 | 92.78 | 28.73 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.1672 | 1.9253 | 63.9547 | 0.15898 | 5.33 | 6.01 | 6.33 | 5.955 | 58.26 | 175.832 | 212.9009 | -21.082 | 89.7786 | 198.4825 | 96.9997 | [16 empty] | Total dissolved solids | mg/L | 5.725 | 60.456 | 205.136 | 266.3488 | -29.8401 | 90.5303 | 249.4723 | 97.7052 | Total dissolved solids | mg/L | 6.41 | 81.342 | 238.104 | 306.138 | -28.5732 | 92.1197 | 285.1785 | 97.7523 | Total dissolved solids | mg/L | 5.955 | 76.944 | 264.8496 | 289.911 | -9.4625 | 92.2606 | 270.0544 | 97.7949 | Total dissolved solids | mg/L | 5.725 | 74.748 | 273.336 | 281.817 | -3.1028 | 92.3409 | 262.936 | 97.8227 | Total dissolved solids | mg/L | 7.33 | 78.318 | 418.064 | 894.68 | -114.0055 | 90.6407 | 832.0132 | 99.119 | Total dissolved solids | mg/L | 7.33 | 78.318 | NA | 894.68 | #VALUE! | 90.6407 | 832.0132 | 99.119 | Fuel Oil Rate ($/gal) | NA
|  |  | Net driving pressure at the design flux, NDP (psi) | 45.7 |  | Recycle ratio, r | 4.2821 |  | Dissolved aluminum (mg/L) | 0.12 |  | 82 | 1998-08-04 | 16:00 | 1813 | 28.98 | 96.9 | 92.48 | 27.27 | 3.87 | 0.68 | 0.23 |  | 0.91 | 4.78 | 0.3392 | 0.74725 | 4.2527 | 13.9886 | 10.2482 | 2.0199 | 65.4001 | 0.1567 | 5.33 | 6.05 | 6.33 | 5.495 | 60.456 | 190.488 | 222.9494 | -17.0412 | 90.9107 | 207.4819 | 97.3516 | [16 empty] | Total hardness | mg/L as CaCO3 | 8 | 39 | 120 | 155.619 | -29.6825 | 79.4872 | 146.0601 | 94.5228 | Total hardness | mg/L as CaCO3 | 10 | 38 | 97 | 122 | -25.7732 | 73.6842 | 114.168 | 91.241 | Total hardness | mg/L as CaCO3 | 10 | 38 | 97 | 122 | -25.7732 | 73.6842 | 114.168 | 91.241 | Total hardness | mg/L as CaCO3 | 3 | 40 | 112 | 151 | -34.8214 | 92.5 | 140.8788 | 97.8705 | Total hardness | mg/L as CaCO3 | 3 | 27 | 184 | 303 | -64.6739 | 88.8889 | 281.8133 | 98.9355 | Total hardness | mg/L as CaCO3 | 3 | 27 | NA | 303 | #VALUE! | 88.8889 | 281.8133 | 98.9355 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.3151 |  | 1: Flow rates and pressures may need to be adjusted in order to obtain |  |  | Total aluminum (mg/L) | 0.38 |  | 83 | 1998-08-05 | 16:00 | 1837 | 29.27 | 95.53 | 91.71 | 25.22 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 9.5388 | 1.9194 | 66.4806 | 0.14348 | 5.37 | 6.01 | 6.27 | 6.64 | 61.554 | 205.136 | 211.9706 | -3.3317 | 89.2127 | 198.5795 | 96.6563 | [16 empty] | Calcium hardness | mg/L as CaCO3 | BMRL | 17 | 72 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 19 | 70 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 18 | 59 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 18 | 70 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 14 | 109 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 0.49
FAX Number |  |  | Temperature at which the MTCW was determined, ToC (oC) | 21.5 |  | the desired operating conditions. |  |  | Fluoride (mg/L) | ND |  | 84 | 1998-08-06 | 14:30 | 1859 | 29.22 | 108.04 | 103.92 | 29.8 | 4.08 | 0.73 | 0.23 | X | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 10.9473 | 2.0001 | 74.1799 | 0.14758 | 5.38 | 6.09 | 6.39 | 5.495 | 57.156 | 205.136 | 221.1235 | -7.7936 | 90.386 | 205.5076 | 97.3261 | [16 empty] | Turbidity | ntu | 0.15 | 0.435 | 0.29 | 1.5071 | -419.7044 | 65.5172 | 1.4193 | 89.4311 | Turbidity | ntu | 0.06 | 0.07 | 0.38 | 0.1 | 73.6842 | 14.2857 | 0.097203 | 38.2734 | Turbidity | ntu | 0.06 | 0.11 | 0.13 | 0.26 | -100 | 45.4545 | 0.24601 | 75.6112 | Turbidity | ntu | 0.25 | 0.2 | 0.22 | 0.05 | 77.2727 | -25 | 0.063677 | -292.6042 | Turbidity | ntu | 0.11 | 0.12 | 0.14 | 0.235 | -67.8571 | 8.3333 | 0.22617 | 51.3645 | Turbidity | ntu | 0.13 | 0.13 | NA | 0.13 | #VALUE! | 0 | 0.13 | -2.135e-14 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  | 2: The design influent flow rate must be within the range established by the |  |  | Sulfate (mg/L) | 13.2 |  | 85 | 1998-08-07 | 16:00 | 1860 | 27.91 | 72.33 | 69.89 | 31.41 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 10.9654 | 2.5748 | 37.1252 | 0.29536 | 5.28 | 6.09 | 6.38 | 5.955 | 58.53 | 216.128 | 284.2932 | -31.5393 | 89.8257 | 263.4322 | 97.7395 | [16 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.1 | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.11 | BMRL | 0.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.11 | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Minimum flow rate to the element, QI, min (gpm) | 4 |  | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  |  | Calcium (mg/L) | 8.4 |  | 86 | 1998-08-08 | 16:00 | 1884 | 29.22 | 72.64 | 69.89 | 30.13 | 4.08 | 0.73 | 0.11 |  | 0.84 | 4.92 | 0.34798 | 0.86905 | 4.8571 | 15.0171 | 11.453 | 3.7466 | 37.3884 | 0.30632 | 5.37 | 6.19 | 6.52 | 6.64 | 59.634 | 238.104 | 411.3215 | -72.7487 | 88.8654 | 381.2994 | 98.2586 | [16 empty] | Total organic carbon | mg/L | BMRL | 2.9 | 10.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.65 | 9.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.58 | 9.25 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.6 | 9.48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.25 | 15.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.32 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | 37th Street WTP |  | Total width of all membrane envelopes in the element, w (ft) | 12.68 |  |  |  |  | Barium (mg/L) | 0.037 |  | 87 | 1998-08-09 | 16:00 | 1908 | 29.65 | 70.35 | 67.45 | 28.58 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.2144 | 2.0482 | 38.2718 | 0.26689 | 5.35 | 5.99 | 6.31 | 4.35 | 59.904 | 150.192 | 224.1506 | -49.2427 | 92.7384 | 209.1742 | 97.9204 | [16 empty] | UV254 | cm-1 | BMRL | 0.046 | 0.199 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.046 | 0.166 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.039 | 0.151 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.04 | 0.264 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.002 | 0.041 | NA | 0.4895 | #VALUE! | 95.122 | 0.45507 | 99.5605
Treatment Plant Category | Conventional |  | Feed spacer thickness, T (ft) | 0.0023 |  | Estimate the Osmotic Pressure Gradient |  |  | Strontium (mg/L) | 0.051 |  | 88 | 1998-08-10 | 16:00 | 1932 | 29.96 | 72.03 | 69.43 | 28.61 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 9.3299 | 1.8405 | 40.2795 | 0.23163 | 5.38 | 6 | 6.32 | 5.955 | 58.53 | 208.8 | 202.5398 | 2.9982 | 89.8257 | 190.0045 | 96.8659 | [16 empty] | SUVA | L/(mg*m) | NR | 1.5862 | 1.8257 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7358 | 1.8103 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NA | NA | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.5 | 1.5928 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7778 | 1.7437 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7672 | NA | --- | --- | --- | --- | ---
Process Train Name | West |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 |  | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.7 |  | Reactive silica (mg/L as SiO2) | 3.7 |  | 89 | 1998-08-11 | 16:00 | 1944 | 30.28 | 73.25 | 69.89 | 33.7 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 9.2351 | 1.8999 | 35.9701 | 0.25674 | 5.45 | 6.06 | 6.37 | 6.185 | 60.456 | 212.464 | 209.1113 | 1.578 | 89.7694 | 196.1717 | 96.8471 | [16 empty] | Bromide | mg/L | BMRL | 32 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 29 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 31 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 29 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 677 |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 |  | Feed TDS, TDSF (mg/L) | 70 |  |  |  |  | 90 | 1998-08-12 | 16:00 | 1968 | 30.86 | 73.4 | 69.89 | 33.85 | 3.97 | 0.58 | 0.17 |  | 0.75 | 4.72 | 0.33843 | 0.77333 | 5.2933 | 11.9314 | 8.4132 | 2.1524 | 35.6426 | 0.23604 | 5.45 | 5.98 | 6.3 | 7.1 | 59.082 | 157.52 | 236.4324 | -50.0967 | 87.9828 | 222.342 | 96.8067 | [16 empty] | SDS-Cl2 dose | mg/L | 2.04 | 4.59 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.13 | 4.79 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.04 | 5.1 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.95 | 4.39 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.95 | 4.88 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.95 | 4.88 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | VA3710150 |  |  |  |  | Waste TDS, TDSW (mg/L) | 154.99 |  |  |  |  | 91 | 1998-08-13 | 16:00 | 1990 | 30.9 | 74.93 | 71.11 | 30.23 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35257 | 0.81111 | 4.5333 | 15.0171 | 10.3897 | 2.6154 | 40.1746 | 0.25861 | 5.45 | 6.15 | 6.49 | 6.87 | 60.18 | 205.136 | 289.0994 | -40.9306 | 88.5842 | 268.4139 | 97.4405 | [16 empty] | SDS-Free Cl2 residual | mg/L | 1.21 | 1.24 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.08 | 1.1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.34 | 2.09 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.78 | 1.15 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.75 | 0.96 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.68 | 1.51 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 9 |  | Additional Information |  |  | Permeate TDS, TDSp (mg/L) | 41.67 |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  | 92 | 1998-08-14 | 16:00 | 2014 | 29.85 | 75.54 | 72.33 | 29.34 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 10.3761 | 1.8481 | 42.7469 | 0.24273 | 5.42 | 6.04 | 6.27 | 5.265 | 60.456 | 109.896 | 204.3468 | -85.9456 | 91.2912 | 190.0708 | 97.23 | [16 empty] | SDS-Cl2 demand | mg/L | 0.83 | 3.35 | --- | 12.83 | --- | 75.2239 | 12.053 | 93.1137 | SDS-Cl2 demand | mg/L | 1.05 | 3.69 | --- | 11.61 | --- | 71.5447 | 10.8716 | 90.3418 | SDS-Cl2 demand | mg/L | 0.7 | 3.01 | --- | 9.94 | --- | 76.7442 | 9.2939 | 92.4681 | SDS-Cl2 demand | mg/L | 1.17 | 3.24 | --- | 9.45 | --- | 63.8889 | 8.8838 | 86.8299 | SDS-Cl2 demand | mg/L | 0.2 | 3.92 | --- | 46.7 | --- | 94.898 | 43.4161 | 99.5393 | SDS-Cl2 demand | mg/L | 0.27 | 3.37 | --- | 39.02 | --- | 91.9881 | 36.2834 | 99.2559
Historical Average Water Temperature (oC) | 32 |  | Design cross-flow velocity (fps) | 0.34989 |  | Influent TDS, TDSI (mg/L) | 138.9 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  | 93 | 1998-08-15 | 16:00 | 2038 | 29.47 | 74.93 | 71.11 | 27.11 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 10.7398 | 2.1775 | 43.7325 | 0.24558 | 5.42 | 6.14 | 6.42 | 6.41 | 62.652 | 201.472 | 241.1592 | -19.6986 | 89.7689 | 224.1585 | 97.1404 | [16 empty] | SDS-Chlorination temp. | oC | 24.7222 | 24.7778 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24.6111 | 24.8889 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23.8 | 23.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24.1667 | 24.3333 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23.1 | 23.4 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 23.1 | 23.3 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 28 |  | Required influent flow to permeate flow rate ratio, QI:Qp | n/a |  | Osmotic pressure gradient, Dp (psi) | 1.0528 |  |  |  |  | 94 | 1998-08-16 | 16:00 | 2062 | 29.73 | 75.84 | 70.96 | 28.24 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 10.1303 | 1.8231 | 43.3369 | 0.23376 | 5.46 | 6.16 | 6.45 | 6.185 | 63.204 | 205.136 | 201.6787 | 1.6854 | 90.2142 | 188.4906 | 96.7187 | [16 empty] | SDS-Chlorination pH | --- | 7.05 | 6.7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.18 | 7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.17 | 5.62 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.21 | 7.26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.39 | 7.27 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.28 | 7.26 | --- | --- | --- | --- | --- | ---
|  |  | Maximum element recovery (%) | n/a | [7 empty] | 95 | 1998-08-17 | 16:00 | 2086 | 30.81 | 75.99 | 70.65 | 27.72 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 9.3053 | 1.8999 | 43.7001 | 0.21294 | 5.51 | 6.2 | 6.52 | 6.185 | 60.456 | 208.8 | 209.1113 | -0.14911 | 89.7694 | 196.1717 | 96.8471 | [16 empty] | SDS-Incubation time | hours | 23.1 | 23 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 25 | 25 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.9167 | 23.8 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.5 | 23.2 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 23.8 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 23.8 | --- | --- | --- | --- | --- | ---
|  |  | Variability of design flux (%) | 20 |  | Estimate the Required Influent Pressure | [5 empty] | 96 | 1998-08-18 | 16:00 | 2110 | 32.23 | 81.79 | 77.52 | 30.59 | 3.87 | 0.68 | 0.28 |  | 0.96 | 4.83 | 0.34302 | 0.70833 | 4.0312 | 13.9886 | 9.6939 | 2.2626 | 46.8024 | 0.20712 | 6.28 | 7.58 | 7.87 | 5.955 | 76.944 | 245.432 | 249.3459 | -1.5947 | 92.2606 | 232.2128 | 97.4355 | [16 empty] | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 235 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 215 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 168.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 40.8 | 139.1 | --- | 1269.55 | --- | 70.6686 | 1182.7727 | 96.5505 | SDS-TOX | mg Cl- /L | 38.5 | 150 | --- | 1432.25 | --- | 74.3333 | 1333.82 | 97.1136
|  |  | Rejection of reference solute and conditions of test | 99.6 |  | Estimated system pressure losses, DPloss (psi) | 2 |  |  |  |  | 97 | 1998-08-19 | 9:30 | 2127 | 30.63 | 86.68 | 82.86 | 30.74 | 3.97 | 0.73 | 0.23 | X | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 9.9364 | 2.8196 | 51.2104 | 0.19403 | 8.59 | 8.03 | 8.3 | 6.185 | 79.14 | 252.76 | 310.6928 | -22.9201 | 92.1847 | 288.1481 | 97.8535 | [16 empty] | SDS-CHCl3 | mg/L | 3.4 | 35.8 | --- | 157.6857 | --- | 90.5028 | 147.6951 | 97.698 | SDS-CHCl3 | mg/L | 1.2 | 47.6 | --- | 186.8 | --- | 97.479 | 173.8213 | 99.3096 | SDS-CHCl3 | mg/L | 2.6 | 24.3 | --- | 89.4 | --- | 89.3004 | 83.3302 | 96.8799 | SDS-CHCl3 | mg/L | 2.6 | 45.7 | --- | 175 | --- | 94.3107 | 163.2101 | 98.407 | SDS-CHCl3 | mg/L | BMRL | 32.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 38.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | (e.g., solute type and concentration) | (mg/L MgSO4) |  | Design permeate pressure, Pp (psi) | 30 |  |  |  |  | 98 | 1998-08-20 | 16:00 | 2148 | 29.53 | 72.03 | 68.98 | 30.23 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 10.4682 | 2.2989 | 37.9761 | 0.27565 | 7.96 | 7.9 | 8.15 | 6.64 | 75.294 | 234.448 | 254.2848 | -8.4611 | 91.1812 | 236.5264 | 97.1927 | [16 empty] | SDS-BDCM | mg/L | 0.8 | 9 | --- | 39.8476 | --- | 91.1111 | 37.3191 | 97.8563 | SDS-BDCM | mg/L | 0.5 | 11 | --- | 42.5 | --- | 95.4545 | 39.563 | 98.7362 | SDS-BDCM | mg/L | 0.7 | 6.2 | --- | 22.7 | --- | 88.7097 | 21.1616 | 96.6921 | SDS-BDCM | mg/L | 0.7 | 12.5 | --- | 47.9 | --- | 94.4 | 44.6721 | 98.433 | SDS-BDCM | mg/L | BMRL | 5.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 5.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Variability of rejection of reference solute (%) | 95 min. |  | Required influent pressure, PI (psi) | 80.8246 |  |  |  |  | 99 | 1998-08-21 | 16:00 | 2172 | 29.54 | 71.87 | 69.59 | 30.77 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.1103 | 2.7152 | 37.2448 | 0.27146 | 8.22 | 7.97 | 8.24 | 6.87 | 80.514 | 282.064 | 298.2441 | -5.7363 | 91.4673 | 278.3909 | 97.5322 | [16 empty] | SDS-DBCM | mg/L | BMRL | 1.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 0.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 2.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing recovery (%) | 15 | [7 empty] | 100 | 1998-08-22 | 16:00 | 2196 | 30.28 | 72.03 | 70.2 | 30.68 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 10.8501 | 2.8127 | 37.6223 | 0.2884 | 8.52 | 8.03 | 8.28 | 6.64 | 79.416 | 245.432 | 310.4007 | -26.4712 | 91.639 | 287.9113 | 97.6937 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing pH | 8 | [7 empty] | 101 | 1998-08-23 | 16:00 | 2220 | 30.84 | 72.33 | 69.74 | 30.5 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34416 | 0.81111 | 4.4111 | 15.0171 | 10.589 | 3.564 | 36.971 | 0.28642 | 8.99 | 8.19 | 8.42 | 8.015 | 80.79 | 300.384 | 393.2944 | -30.9305 | 90.0792 | 364.4182 | 97.8006 | [16 empty] | SDS-THM4 | mg/L | 4.2 | 46 | --- | 203.2476 | --- | 90.8696 | 190.3585 | 97.7936 | SDS-THM4 | mg/L | 1.7 | 59.9 | --- | 234.5 | --- | 97.1619 | 218.2207 | 99.221 | SDS-THM4 | mg/L | 3.3 | 31.4 | --- | 115.7 | --- | 89.4904 | 107.8401 | 96.9399 | SDS-THM4 | mg/L | 3.3 | 60.3 | --- | 231.3 | --- | 94.5274 | 215.7078 | 98.4702 | SDS-THM4 | mg/L | 0 | 38.5 | --- | 481.25 | --- | 100 | 447.263 | 100 | SDS-THM4 | mg/L | 0 | 43.9 | --- | 548.75 | --- | 100 | 509.996 | 100
|  |  | Acceptable range of operating pressures | 250 max. | [7 empty] | 102 | 1998-08-24 | 16:00 | 2244 | 31.12 | 72.18 | 68.67 | 29.92 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 10.3965 | 2.7082 | 37.7968 | 0.27506 | 9.3 | 8.51 | 8.78 | 8.245 | 78.318 | 282.064 | 300.7236 | -6.6154 | 89.4724 | 279.0695 | 97.0455 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 4.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Acceptable range of operating pH values | 3 - 9 | [7 empty] | 103 | 1998-08-25 | 16:00 | 2268 | 30.92 | 71.72 | 68.98 | 30.13 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 9.5962 | 2.7514 | 37.4686 | 0.25611 | 8.84 | 8.09 | 8.32 | 6.87 | 81.618 | 263.752 | 302.6121 | -14.7336 | 91.5827 | 282.0071 | 97.5639 | [16 empty] | SDS-DCAA* | mg/L | 2.2 | 17 | --- | 72.6762 | --- | 87.0588 | 68.1126 | 96.7701 | SDS-DCAA* | mg/L | 1 | 23 | --- | 89 | --- | 95.6522 | 82.8463 | 98.7929 | SDS-DCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Typical pressure drop across a single element (psi) | 3 - 5 | [7 empty] | 104 | 1998-08-26 | 16:00 | 2286 | 31.05 | 69.89 | 67.3 | 29.95 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 9.6591 | 2.1746 | 36.4704 | 0.26485 | 9.83 | 9.15 | 9.42 | 15.8 | 83.814 | 297.476 | 248.9909 | 16.2988 | 81.1487 | 233.2597 | 93.2264 | [16 empty] | SDS-TCAA* | mg/L | BMRL | 27 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 31 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible SDI | 5 | [7 empty] | 105 | 1998-08-27 | 16:00 | 2306.5 | 28.83 | 65.92 | 63.48 | 27.88 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 8.9109 | 2.47 | 34.35 | 0.25942 | 6.39 | 7.44 | 7.64 | 5.725 | 76.392 | 228.2416 | 269.9581 | -18.2774 | 92.5058 | 252.7255 | 97.7347 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 106 | 1998-08-28 | 11:30 | 2326 | 29.71 | 71.26 | 68.52 | 29.95 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.3471 | 2.8962 | 37.0438 | 0.27932 | 9.28 | 8.21 | 8.54 | 8.7 | 87.384 | 311.396 | 320.015 | -2.7678 | 90.0439 | 298.325 | 97.0837 | [16 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | [7 empty] | 107 | 1998-08-29 | 16:00 | 2353 | 31.25 | 71.11 | 68.98 | 31.05 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.0505 | 2.6602 | 36.3348 | 0.27661 | 9.58 | 8.7 | 8.94 | 10.99 | 83.262 | 309.9312 | 296.9357 | 4.193 | 86.8007 | 277.0133 | 96.0327 | [16 empty] | SDS-BCAA* | mg/L | BMRL | 3.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 108 | 1998-08-30 | 16:00 | 2377 | 30.28 | 70.5 | 67.6 | 30.87 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 9.5555 | 2.2567 | 35.9233 | 0.266 | 7.05 | 7.76 | 8.09 | 5.265 | 75.846 | 274.032 | 247.257 | 9.7708 | 93.0583 | 230.9321 | 97.7201 | [16 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 109 | 1998-08-31 | 16:00 | 2400 | 30.6 | 71.26 | 68.82 | 30.23 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 9.8638 | 2.884 | 36.926 | 0.26712 | 5.99 | 7.84 | 7.57 | 5.04 | 83.262 | 286.8528 | 314.527 | -9.6475 | 93.9468 | 293.4397 | 98.2824 | [16 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 110 | 1998-09-01 | 16:00 | 2423 | 29.94 | 72.18 | 70.2 | 32.57 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 9.7608 | 2.5491 | 36.0709 | 0.2706 | 7.59 | 7.75 | 8.13 | 6.87 | 76.122 | 311.7384 | 280.867 | 9.903 | 90.975 | 261.7771 | 97.3756 | [16 empty] | SDS-DCBAA | mg/L | BMRL | 6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 5.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Field 2-5: Pretreatment Used Prior To Membranes1 | [11 empty] | 111 | 1998-09-02 | 16:00 | 2447 | 29.96 | 72.18 | 69.43 | 31.38 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 10.7081 | 2.6854 | 36.7396 | 0.29146 | 7.35 | 7.79 | 8.18 | 6.64 | 76.122 | 304.7784 | 296.6518 | 2.6664 | 91.2772 | 275.1804 | 97.587 | [16 empty] | SDS-HAA5 | mg/L | 2.2 | 44 | --- | 201.2476 | --- | 95 | 188.3585 | 98.832 | SDS-HAA5 | mg/L | 1 | 54 | --- | 213 | --- | 98.1481 | 198.1752 | 99.4954 | SDS-HAA5 | mg/L | 0 | 41.1 | --- | 164.4 | --- | 100 | 152.9038 | 100 | SDS-HAA5 | mg/L | 0 | 40 | --- | 160 | --- | 100 | 149.0581 | 100 | SDS-HAA5 | mg/L | 0 | 35 | --- | 437.5 | --- | 100 | 406.6027 | 100 | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 112 | 1998-09-03 | 16:00 | 2471 | 30.52 | 66.23 | 63.33 | 28.55 | 4.08 | 0.63 | 0.17 |  | 0.8 | 4.88 | 0.34875 | 0.7875 | 5.1 | 12.96 | 9.2351 | 2.8449 | 33.3851 | 0.27662 | 6.76 | 7.22 | 7.59 | 4.35 | 68.976 | 191.2192 | 308.4724 | -61.3187 | 93.6935 | 288.8415 | 98.494 | [16 empty] | SDS-HAA6 | mg/L | 2.2 | 47.7 | --- | 218.8667 | --- | 95.3878 | 204.8366 | 98.926 | SDS-HAA6 | mg/L | 1 | 57.8 | --- | 228.2 | --- | 98.2699 | 212.3123 | 99.529 | SDS-HAA6 | mg/L | 0 | 44 | --- | 176 | --- | 100 | 163.6926 | 100 | SDS-HAA6 | mg/L | 0 | 43.7 | --- | 174.8 | --- | 100 | 162.846 | 100 | SDS-HAA6 | mg/L | 0 | 38.6 | --- | 482.5 | --- | 100 | 448.4247 | 100 | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Process | Description | [8 empty] | Scale |  | 113 | 1998-09-04 | 16:00 | 2495 | 29.07 | 74.32 | 71.57 | 30.87 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 9.7864 | 2.2603 | 39.8147 | 0.2458 | 9.12 | 8.22 | 8.59 | 6.41 | 77.22 | 286.8288 | 249.1871 | 13.1234 | 91.699 | 232.4439 | 97.2423 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Rapid Mix | Type: | Mechanical | [7 empty] | Full |  | 114 | 1998-09-05 | 16:00 | 2519 | 29.15 | 74.01 | 71.26 | 30.9 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 11.02 | 2.7802 | 38.9548 | 0.28289 | 8.98 | 8.13 | 8.41 | 7.33 | 79.14 | 305.8768 | 307.0587 | -0.3864 | 90.7379 | 285.3522 | 97.4312 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
| Chemical Name: | Alum |  |  |  | Powdered Activated Carbon (PAC) | [5 empty] | 115 | 1998-09-06 | 16:00 | 2543 | 29.86 | 74.16 | 71.42 | 31.05 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 10.9908 | 2.6509 | 39.0891 | 0.28117 | 9.15 | 8.15 | 8.5 | 8.475 | 76.944 | 300.3824 | 294.2587 | 2.0387 | 88.9855 | 273.562 | 96.902 | [66 empty] | 10/1/99 Duplicate HAA samples not analyzed - ran duplicates on 10/29 HAAs instead.
| Chemical Formula: | Al2(SO4)3*14H2O | [9 empty] | 116 | 1998-09-07 | 16:00 | 2567 | 30.95 | 73.25 | 70.04 | 30.71 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.0009 | 2.5186 | 38.4164 | 0.26033 | 9.16 | 8.25 | 8.54 | 8.245 | 76.668 | 309.9064 | 278.9621 | 9.9851 | 89.2458 | 260.1007 | 96.8301 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
| Dose: | AVG | MAX | MIN | STD DEV | AVG | MAX | MIN | STD DEV |  |  | 117 | 1998-09-08 | 16:00 | 2592 | 28.38 | 75.08 | 71.72 | 30.96 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 9.6496 | 2.0179 | 40.4221 | 0.23872 | 5.68 | 6.48 | 6.87 | 7.1 | 61.83 | 275.168 | 223.6404 | 18.7259 | 88.5169 | 208.8862 | 96.601 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Blending Calculations For D-DBP MCLs
|  | 30.1 | 49.7 | 20.6 | 7.15 | 2.36 | 6.47 | 0 | 1.36 |  |  | 118 | 1998-09-09 | 16:00 | 2615 | 26.38 | 73.71 | 70.65 | 29.83 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 11.2751 | 2.6757 | 39.6743 | 0.28419 | 6.47 | 7.68 | 7.94 | 4.81 | 73.92 | 209.216 | 293.2691 | -40.1753 | 93.493 | 272.3787 | 98.2341 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | THM4 Controls |  |  |  | HAA5 Controls
Flocculation | Type: | Mechanical | [7 empty] | Full |  | 119 | 1998-09-10 | 16:00 | 2639 | 27.06 | 75.54 | 72.94 | 29.89 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 11.23 | 2.5017 | 41.8483 | 0.26835 | 8.99 | 8.06 | 8.34 | 7.33 | 75.294 | 287.256 | 276.231 | 3.838 | 90.2648 | 257.4961 | 97.1534 | [16 empty] | Qp/QT (THM4), % | -62.201 | 23.9234 |  | Qp/QT (HAA5), % | -23.9234 | 40.6699 |  |  |  | Qp/QT (THM4), % | -20.7904 | 41.0653 |  | Qp/QT (HAA5), % | 0 | 50.9434 |  |  |  | Qp/QT (THM4), % | -144.484 | -16.3701 |  | Qp/QT (HAA5), % | -31.3869 | 34.3066 |  |  |  | Qp/QT (THM4), % | -20.5263 | 42.6316 |  | Qp/QT (HAA5), % | -35 | 32.5 |  |  |  | Qp/QT (THM4), % | -87.013 | 6.4935 |  | Qp/QT (HAA5), % | -54.2857 | 22.8571 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
Sedimentation | Type: | Conventional | [7 empty] | Full |  | 120 | 1998-09-11 | 16:00 | 2650 | 27.56 | 74.32 | 72.03 | 30.19 | 4.18 | 0.73 | 0.23 |  | 0.96 | 5.14 | 0.36479 | 0.76042 | 4.3542 | 15.0171 | 11.7832 | 2.6975 | 40.2875 | 0.29248 | 8.97 | 7.99 | 8.34 | 7.1 | 76.668 | 291.656 | 297.4708 | -1.9937 | 90.7393 | 276.8511 | 97.4354 | [16 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 29 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 30.2509 |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | 21.7599 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 41.775 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 29.7 |  |  |  | Qp/QT (THM4), % | -64.0091 | 17.9954 |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
Filtration | Type: | Dual Media - Anthracite/Sand | [7 empty] | Pilot |  | 121 | 1998-09-12 | 16:00 | 2674 | 27.85 | 74.62 | 72.03 | 30.16 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 10.7939 | 3.0959 | 40.0691 | 0.26938 | 9.1 | 8.18 | 8.49 | 6.87 | 73.374 | 313.272 | 339.39 | -8.3372 | 90.637 | 316.4576 | 97.8291 | [16 empty] | SDS-HAA5b, mg/L | NA | 34 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 32.2354 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 22.9474 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 32.7273 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[12 empty] | 122 | 1998-09-13 | 16:00 | 2698 | 28.31 | 75.99 | 72.33 | 29.98 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35257 | 0.81111 | 4.5333 | 15.0171 | 11.4759 | 3.2627 | 40.9173 | 0.28047 | 8.73 | 7.92 | 8.3 | 6.87 | 73.374 | 343.32 | 358.95 | -4.5526 | 90.637 | 333.1449 | 97.9378 | [16 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | 132.7169 |  | SDS-TOXb, mg Cl- /L | NA | 116.6314 |  |  |  | SDS-HAA5b, mg/L | NA | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [11 empty] | 123 | 1998-09-14 | 16:00 | 2722 | 28.58 | 74.32 | 71.11 | 29.31 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 10.5273 | 2.1989 | 41.2061 | 0.25548 | 9.18 | 8.21 | 8.53 | 6.41 | 75.294 | 271.136 | 242.5837 | 10.5306 | 91.4867 | 226.2959 | 97.1674 | [16 empty] | SDS-CDb, mg/L | NA | 2.7471 |  | SDS-CDb, mg/L | NA | 2.3251 |  |  |  | SDS-CDb, mg/L | NA | 2.6059 |  | SDS-CDb, mg/L | NA | 2.3451 |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | 2.2175 |  |  |  | SDS-CDb, mg/L | NA | 2.3575 |  | SDS-CDb, mg/L | NA | 2.5673 |  |  |  | SDS-CDb, mg/L | NA | 3.6784 |  | SDS-CDb, mg/L | NA | 3.0697 |  |  |  | SDS-TOXb, mg Cl- /L | NA | 129.9351 |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [11 empty] | 124 | 1998-09-15 | 16:00 | 2746 | 28.54 | 74.62 | 71.72 | 29.1 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.4333 | 2.6139 | 41.4561 | 0.25167 | 9.09 | 8.06 | 8.4 | 6.87 | 77.766 | 305.944 | 287.3716 | 6.0705 | 91.1658 | 268.2592 | 97.439 | [16 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | SDS-CDb, mg/L | NA | 2.8121 |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
is to list the pretreatment processes used in this particular Long-Term SEBST run. | [11 empty] | 125 | 1998-09-16 | 16:00 | 2770 | 29.47 | 74.77 | 72.03 | 31.66 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 10.4471 | 3.2131 | 38.5269 | 0.27116 | 8.87 | 7.98 | 8.33 | 7.1 | 76.122 | 298.616 | 352.21 | -17.9475 | 90.6729 | 328.4093 | 97.8381 | [16 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[12 empty] | 126 | 1998-09-17 | 16:00 | 2794 | 29.19 | 77.52 | 74.62 | 31.41 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 10.8752 | 2.713 | 41.947 | 0.25926 | 8.24 | 7.85 | 8.19 | 5.495 | 75.57 | 285.056 | 297.982 | -4.5345 | 92.7286 | 276.7999 | 98.0148 | [16 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | 0.033982 |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[12 empty] | 127 | 1998-09-18 | 16:00 | 2817 | 28.7 | 73.71 | 71.11 | 30.59 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 10.2245 | 2.2829 | 39.5371 | 0.2586 | 9.24 | 8.36 | 8.71 | 8.015 | 79.416 | 262.344 | 252.8184 | 3.6309 | 89.9076 | 236.3039 | 96.6082 | [16 empty] | Alkb, mg/L CaCO3 | NA | 5.2823 |  | Alkb, mg/L CaCO3 | NA | 4.7799 |  |  |  | Alkb, mg/L CaCO3 | NA | 11.8402 |  | Alkb, mg/L CaCO3 | NA | 10.3585 |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | 13.5401 |  |  |  | Alkb, mg/L CaCO3 | NA | 8.7368 |  | Alkb, mg/L CaCO3 | NA | 9.75 |  |  |  | Alkb, mg/L CaCO3 | NA | 16.2208 |  | Alkb, mg/L CaCO3 | NA | 14.2571 |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[12 empty] | 128 | 1998-09-19 | 16:00 | 2841 | 28.17 | 74.93 | 71.87 | 30.1 | 4.08 | 0.63 | 0.28 |  | 0.91 | 4.99 | 0.35715 | 0.69231 | 4.4835 | 12.96 | 9.6277 | 2.315 | 40.985 | 0.23491 | 8.81 | 8 | 8.35 | 6.41 | 82.44 | 282.128 | 253.5075 | 10.1445 | 92.2246 | 237.9092 | 97.3057 | [16 empty] | T-Hdb, mg/L CaCO3 | NA | 31.5837 |  | T-Hdb, mg/L CaCO3 | NA | 26.3923 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 26.5017 |  | T-Hdb, mg/L CaCO3 | NA | 23.7358 |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | 28.3942 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 24.2263 |  | T-Hdb, mg/L CaCO3 | NA | 27.975 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 25.4416 |  | T-Hdb, mg/L CaCO3 | NA | 21.5143 |  |  |  | Alkb, mg/L CaCO3 | NA | 14.8405 |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[12 empty] | 129 | 1998-09-20 | 16:00 | 2865 | 28.6 | 74.47 | 71.87 | 30.71 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 9.7988 | 2.6214 | 39.8386 | 0.24596 | 8.94 | 8.07 | 8.45 | 6.185 | 81.066 | 290.92 | 286.1748 | 1.6311 | 92.3704 | 268.3212 | 97.6949 | [16 empty] | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | NA | 22.6811 |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[12 empty] | 130 | 1998-09-21 | 16:00 | 2889 | 29.3 | 73.4 | 70.96 | 30.74 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.4263 | 2.6646 | 38.7754 | 0.26889 | 8.87 | 7.94 | 8.29 | 6.87 | 79.14 | 281.032 | 292.8078 | -4.1902 | 91.3192 | 273.3251 | 97.4865 | [26 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[12 empty] | 131 | 1998-09-22 | 16:00 | 2913 | 29.16 | 74.32 | 71.57 | 31.32 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.1874 | 2.6917 | 38.9333 | 0.26166 | 8.85 | 8.01 | 8.34 | 6.41 | 79.416 | 285.056 | 295.2598 | -3.5796 | 91.9286 | 275.5787 | 97.674 | [16 empty] | Notes: | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | Notes:
[12 empty] | 132 | 1998-09-23 | 16:00 | 2937 | 27.25 | 75.54 | 72.79 | 31.81 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 9.4821 | 2.4674 | 39.8876 | 0.23772 | 9.1 | 8.17 | 8.49 | 6.185 | 76.668 | 278.096 | 269.7301 | 3.0083 | 91.9327 | 252.9251 | 97.5546 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[12 empty] | 133 | 1998-09-24 | 16:00 | 2961 | 27.39 | 76.76 | 74.47 | 30.99 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 11.7084 | 2.4109 | 42.2141 | 0.27736 | 8.95 | 8.07 | 8.39 | 5.495 | 77.496 | 272.232 | 265.2129 | 2.5784 | 92.9093 | 246.5887 | 97.7716 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[12 empty] | 134 | 1998-09-25 | 16:00 | 2985 | 27.42 | 76.76 | 74.01 | 30.74 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 11.6537 | 2.8441 | 41.8009 | 0.27879 | 8.8 | 7.93 | 8.34 | 5.955 | 79.416 | 281.032 | 312.5748 | -11.2239 | 92.5015 | 290.3692 | 97.9492 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[12 empty] | 135 | 1998-09-26 | 16:00 | 3008 | 27.44 | 76.61 | 74.16 | 30.71 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 11.642 | 2.7077 | 41.9673 | 0.27741 | 5.97 | 7.03 | 7.3 | 4.81 | 74.748 | 234.864 | 296.7251 | -26.3391 | 93.565 | 275.5845 | 98.2546 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[12 empty] | 136 | 1998-09-27 | 16:00 | 3025 | 28.96 | 76.15 | 73.55 | 31.9 | 4.18 | 0.73 | 0.17 |  | 0.9 | 5.08 | 0.36021 | 0.81111 | 4.6444 | 15.0171 | 11.6342 | 3.4367 | 39.5133 | 0.29444 | 9.23 | 8.3 | 8.64 | 7.555 | 77.496 | 304.112 | 377.8309 | -24.2407 | 90.2511 | 351.2264 | 97.849 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[12 empty] | 137 | 1998-09-28 | 16:00 | 3049 | 28.61 | 76.61 | 73.71 | 31.54 | 4.18 | 0.73 | 0.28 |  | 1.01 | 5.19 | 0.36861 | 0.72277 | 4.1386 | 15.0171 | 11.0602 | 2.3391 | 41.2809 | 0.26792 | 9.12 | 8.15 | 8.47 | 6.64 | 76.392 | 265.272 | 258.2454 | 2.6488 | 91.308 | 240.5506 | 97.2397 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[12 empty] | 138 | 1998-09-29 | 16:00 | 3073 | 28.23 | 75.84 | 73.4 | 30.26 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.4229 | 2.6938 | 41.6662 | 0.25015 | 9.1 | 8.15 | 8.54 | 5.955 | 79.14 | 289.824 | 295.513 | -1.9629 | 92.4754 | 275.3389 | 97.8372 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[12 empty] | 139 | 1998-09-30 | 16:00 | 3097 | 27.94 | 75.38 | 73.1 | 29.19 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 10.5554 | 2.5944 | 42.4556 | 0.24862 | 9.09 | 8.15 | 8.52 | 6.185 | 76.668 | 299.712 | 285.0525 | 4.8912 | 91.9327 | 265.6232 | 97.6715 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[12 empty] | 140 | 1998-10-01 | 16:00 | 3121 | 28.43 | 76.15 | 73.1 | 30.87 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 11.4415 | 2.7916 | 40.9634 | 0.27931 | 8.85 | 7.96 | 8.39 | 6.64 | 78.87 | 285.056 | 308.1217 | -8.0917 | 91.5811 | 285.8011 | 97.6767 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[61 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [49 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on K13: C. Rice: Consultant verified the decrease in aluminum concentration from the raw to the filtered water; no explanation was given.
Note on K14: C. Rice: The "Pilot Filtered" sulfate is higher than the raw water concentration because aluminum sulfate was added for coagulation.
Note on AA46: S Allgeier (8/15/99): Concentrate conductivity transmitter replaced.
Note on AS5: TSC_ADM: Operational TDS data is based on an empirical factor applied to the on-line conductivity measurements (compared to the biweekly TDS data, which are based on lab measurements); therefore, there may be discrepancies between the operational and biweekly TDS data.
Note on CM30: C. Rice: Consultant verified value; no explanation given.
Note on CM33: C. Rice: Consultant verified value; no explanation given.
Note on DH5: C. Rice: Consultant verified that the recovery was indeed at 0.92 during the 10/1/98 sampling.
Note on DH28: C. Rice: Consultant verified value; no explanation given.
Note on DI32: C. Rice: Consultant verified the low feed TOX values reported for week 20 (primary and duplicate); no explanations given.
Note on DJ10: TSC_ADM: Reported concentrate concentrations are relatively higher, compared to previous weeks, because system was operating at 92% recovery.
Note on DS28: C. Rice: Consultant verified value; no explanation given.
Note on DT32: C. Rice: Consultant verified the low feed TOX values reported for week 20 (primary and duplicate); no explanations given.
Note on DU10: TSC_ADM: Reported concentrate concentrations are relatively higher, compared to previous weeks, because system was operating at 92% recovery.

## NF70. Weeks 21-30
FIELD-SET 3: LT-SEBST RESULTS: WEEKS 21-30 (FILE: ltsebst.xls)
Field 3-1: PWS And Treatment Plant Data |  |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  |  | Field 3-3: SEBST Design Parameters |  |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [47 empty] | Field 3-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 22 | [9 empty] | Field 3-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 24 | [9 empty] | Field 3-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 26 | [9 empty] | Field 3-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 28 | [9 empty] | Field 3-11: Permeate, Feed, Concentrate And Blended Water Quality For Week 30 | [9 empty] | Field 3-12: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 30 | [9 empty] | Field 3-13: Membrane Cost Parameters
|  |  | General Information |  |  | Calculate Temperature Normalized MTCW |  |  | Parameters Evaluated Prior to Pretreatment |  | (see cell A47) | [49 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | City of Norfolk |  | Membrane manufacturer | FilmTec |  | Average yearly temperature of feed water, TavgoC (oC) | 20 |  | PLANT FILTERED WATER: |  |  | Day No. | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.69 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.8 | [8 empty] | Recovery during sample collection (decimal) | 0.76 | [8 empty] | Recovery during sample collection (decimal) | 0.92 | [8 empty] | Recovery during sample collection (decimal) | 0.92 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | VA37010100 |  | Membrane trade name | NF70 |  | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.30143 |  | Alkalinity (mg/L as CaCO3) | 10.5 |  |  | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.85 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.96 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.79 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.79 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA |  | Membrane element model number | NF70-4040 |  |  |  |  | pH (units) | 6.44 |  | 141 | 1998-10-02 | 16:00 | 3145 | 26.37 | 76.91 | 74.16 | 30.62 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 10.4854 | 2.7675 | 42.1475 | 0.24878 | 9.59 | 8.66 | 9.12 | 8.475 | 83.538 | 280.664 | 305.4634 | -8.836 | 89.8549 | 285.2277 | 97.0287 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Influent flow rate during sample collection (gpm) | 4.99 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.88 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.93 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.04 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.87 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.87 | [7 empty] | Capital Recovery Period (years) | 20
|  |  | Molecular weight cutoff (Daltons) | 200 |  | Calculate System Flow Rates1 |  |  | Total Dissolved Solids | 73 mg/L |  | 142 | 1998-10-03 | 16:00 | 3169 | 26.17 | 77.22 | 74.16 | 30.74 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 11.2338 | 2.6258 | 42.3242 | 0.26542 | 8.62 | 7.91 | 8.32 | 5.725 | 76.944 | 275.168 | 287.5045 | -4.4833 | 92.5595 | 268.3051 | 97.8662 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [60 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide |  | Design recovery, R (decimal) | 0.75 |  | Conductivity | 129 umhos/cm |  | 143 | 1998-10-04 | 16:00 | 3193 | 24.92 | 76.61 | 74.01 | 29.74 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 11.3098 | 2.6646 | 42.9054 | 0.2636 | 8.94 | 7.98 | 8.42 | 5.495 | 77.766 | 278.832 | 291.4368 | -4.5206 | 92.9339 | 271.9538 | 97.9794 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  |  | Membrane construction (e.g., thin-film composite) | Thin-film composite |  | Design flux, FW (gfd) | 14.4 |  | SDI | 5.8 |  | 144 | 1998-10-05 | 16:00 | 3217 | 23.88 | 77.06 | 74.32 | 29.07 | 4.08 | 0.63 | 0.17 |  | 0.8 | 4.88 | 0.34875 | 0.7875 | 5.1 | 12.96 | 10.9315 | 3.2138 | 43.4062 | 0.25184 | 9.35 | 8.4 | 8.76 | 6.41 | 79.416 | 290.92 | 349.9676 | -20.2969 | 91.9286 | 327.7913 | 98.0445 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Parameter | Units | Cp-22 | CF-22 | CC-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-24 | CF-24 | CC-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-26 | CF-26 | CC-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-28 | CF-28 | CC-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-30 | CF-30 | CC-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-30 (dup) | CF-30 (dup) | CC-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 15
|  |  | Membrane hydrophobicity | Hydrophobic |  | Permeate flow rate, Qp (gpm) | 0.7 |  | Turbidity (ntu) | 0.26 |  | 145 | 1998-10-06 | 16:00 | 3241 | 24.89 | 77.52 | 74.62 | 29.49 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.2256 | 2.7221 | 43.8579 | 0.27876 | 8.85 | 7.95 | 8.34 | 5.04 | 78.87 | 290.92 | 297.15 | -2.1415 | 93.6097 | 277.2467 | 98.1821 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Sampling date | MM/DD/YY | 1998-10-15 | 1998-10-15 | 1998-10-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-29 | 1998-10-29 | 1998-10-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-12 | 1998-11-12 | 1998-11-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-10 | 1998-12-10 | 1998-12-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-10 | 1998-12-10 | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 9
Phone Number |  |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative |  | Feed flow rate, QF (gpm) | 0.93333 |  | Dissolved aluminum (mg/L) | <0.044 |  | 146 | 1998-10-07 | 16:00 | 3265 | 25.09 | 75.99 | 73.25 | 25.83 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 11.8111 | 3.4007 | 45.3893 | 0.26022 | 9.3 | 8.42 | 8.81 | 6.64 | 79.692 | 305.944 | 371.9 | -21.5582 | 91.6679 | 346.7097 | 98.0849 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Sampling time | hh:mm | 7:35 | 7:50 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:40 | 7:25 | 7:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:20 | 9:40 | 9:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:15 | 7:15 | 7:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:20 | 14:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:20 | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | Concentrate-waste flow rate, QW (gpm) | 0.23333 |  | Total aluminum (mg/L) | 0.074 |  | 147 | 1998-10-08 | 16:00 | 3289 | 24.51 | 77.06 | 72.94 | 26.57 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 11.7311 | 2.7812 | 45.6488 | 0.25699 | 9.07 | 8.15 | 8.56 | 6.185 | 81.618 | 322.432 | 304.6373 | 5.5189 | 92.422 | 284.3019 | 97.8245 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Operation time | hh.hh | 3415 | 3415 | 3415 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3735 | 3735 | 3735 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4075 | 4075 | 4075 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4349 | 4349 | 4349 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4738 | 4738 | 4738 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5010 | 5010 | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131.8
E-Mail Address (optional) |  |  | Design Parameters |  |  | Minimum influent flow rate, QI, min (gpm) | 4 |  | PILOT FILTERED: Sulfate (mg/L) | 43 |  | 148 | 1998-10-09 | 16:00 | 3311 | 23.65 | 80.27 | 78.13 | 30.93 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 11.9651 | 2.4901 | 45.7799 | 0.26136 | 8.55 | 7.94 | 8.16 | 4.35 | 72 | 282.864 | 272.0087 | 3.8376 | 93.9583 | 253.3603 | 98.2831 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | pH | --- | 9.1 | 9.15 | 8.72 | --- | --- | --- | --- | --- | pH | --- | 6.58 | 6.86 | 7.59 | --- | --- | --- | --- | --- | pH | --- | 7.7 | 7.07 | 7.96 | --- | --- | --- | --- | --- | pH | --- | 8.13 | 8.28 | 8.41 | --- | --- | --- | --- | --- | pH | --- | 8.85 | 7.52 | 8.6 | --- | --- | --- | --- | --- | pH | --- | 8.98 | 7.47 | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.65
|  |  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" |  | Maximum influent flow rate, QI, max (gpm) | 16 |  | RAW WATER: |  |  | 149 | 1998-10-10 | 16:00 | 3335 | 23.13 | 80.11 | 77.52 | 31.51 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.3224 | 2.3725 | 44.9325 | 0.27424 | 8.92 | 8.19 | 8.44 | 5.725 | 70.074 | 263.808 | 260.3232 | 1.321 | 91.8301 | 242.9758 | 97.6438 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Temperature | oC | 23.3 | 23 | 22.9 | --- | --- | --- | --- | --- | Temperature | oC | 21.3 | 20.3 | 21.4 | --- | --- | --- | --- | --- | Temperature | oC | 20.3 | 18.1 | 20.9 | --- | --- | --- | --- | --- | Temperature | oC | 21.5556 | 20.4444 | 20.9444 | --- | --- | --- | --- | --- | Temperature | oC | 20.4 | 18.2 | 20.9 | --- | --- | --- | --- | --- | Temperature | oC | 20.5 | 18.1 | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 30
Technical ICR Contact Person |  |  | Active membrane area of membrane element used, A (ft2) | 70 |  | Design influent flow rate2, QI (gpm) | 4.93 |  | Dissolved iron (mg/L) | 0.2 |  | 150 | 1998-10-11 | 16:00 | 3347 | 22.94 | 79.5 | 76.76 | 31.14 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.5447 | 2.2308 | 44.7592 | 0.28027 | 9.54 | 8.91 | 9.21 | 9.845 | 70.35 | 271.504 | 249.2343 | 8.2023 | 86.0057 | 232.9232 | 95.7733 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Alkalinity | mg/L as CaCO3 | 4 | 16 | 70 | 42.7097 | 38.9862 | 75 | 40.2742 | 90.0681 | Alkalinity | mg/L as CaCO3 | 3 | 15 | 62 | 51 | 17.7419 | 80 | 47.6434 | 93.7032 | Alkalinity | mg/L as CaCO3 | 3 | 16 | 79 | 68 | 13.9241 | 81.25 | 63.5172 | 95.2769 | Alkalinity | mg/L as CaCO3 | 1 | 21 | 66 | 84.3333 | -27.7778 | 95.2381 | 78.3016 | 98.7229 | Alkalinity | mg/L as CaCO3 | 7 | 19 | 221 | 157 | 28.9593 | 63.1579 | 145.807 | 95.1991 | Alkalinity | mg/L as CaCO3 | 7 | 19 | NA | 157 | #VALUE! | 63.1579 | 145.807 | 95.1991 | Electric Rate ($/kW-h) | 0.049
Mailing Address |  |  | Design flux, FW (gfd) | 14.4 |  | Design recycle flow rate, QR (gpm) | 3.9967 |  | Total iron (mg/L) | 0.6 |  | 151 | 1998-10-12 | 16:00 | 3351 | 22.94 | 77.22 | 75.23 | 30.07 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 13.5556 | 2.3813 | 43.7737 | 0.30967 | 8.38 | 7.71 | 8.06 | 2.52 | 64.026 | 264.176 | 259.2407 | 1.8682 | 96.0641 | 240.6488 | 98.9528 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Total dissolved solids | mg/L | 6.185 | 68.148 | 267.472 | 206.0656 | 22.958 | 90.9242 | 193.49 | 96.8035 | Total dissolved solids | mg/L | 2 | 57 | 261 | 222 | 14.9425 | 96.4912 | 206.6158 | 99.032 | Total dissolved solids | mg/L | 17 | 60 | 284 | 232 | 18.3099 | 71.6667 | 217.1724 | 92.1721 | Total dissolved solids | mg/L | 10 | 59 | 230 | 214.1667 | 6.8841 | 83.0508 | 199.3889 | 94.9847 | Total dissolved solids | mg/L | 24 | 89 | 819 | 836.5 | -2.1368 | 73.0337 | 775.8711 | 96.9067 | Total dissolved solids | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  |  | Net driving pressure at the design flux, NDP (psi) | 45.7 |  | Recycle ratio, r | 4.2821 |  | Dissolved aluminum (mg/L) | 0.12 |  | 152 | 1998-10-13 | 16:00 | 3375 | 23.29 | 77.22 | 74.93 | 30.1 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.6271 | 2.2409 | 43.7341 | 0.28872 | 8.87 | 8.08 | 8.32 | 4.35 | 65.13 | 289.456 | 244.8274 | 15.4181 | 93.3211 | 228.4422 | 98.0958 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Total hardness | mg/L as CaCO3 | 6 | 28 | 101 | 76.9677 | 23.7943 | 78.5714 | 72.5027 | 91.7245 | Total hardness | mg/L as CaCO3 | 2 | 31 | 120 | 118 | 1.6667 | 93.5484 | 109.8883 | 98.18 | Total hardness | mg/L as CaCO3 | 2 | 35 | 113 | 167 | -47.7876 | 94.2857 | 155.6207 | 98.7148 | Total hardness | mg/L as CaCO3 | 8 | 32 | 104 | 108 | -3.8462 | 75 | 100.7619 | 92.0605 | Total hardness | mg/L as CaCO3 | 2 | 31 | 308 | 364.5 | -18.3442 | 93.5484 | 337.4502 | 99.4073 | Total hardness | mg/L as CaCO3 | 2 | 30 | NA | 352 | #VALUE! | 93.3333 | 325.883 | 99.3863 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.3151 |  | 1: Flow rates and pressures may need to be adjusted in order to obtain |  |  | Total aluminum (mg/L) | 0.38 |  | 153 | 1998-10-14 | 16:00 | 3399 | 23.41 | 77.22 | 74.16 | 29.58 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 13.3931 | 2.3104 | 43.7996 | 0.30578 | 8.64 | 7.94 | 8.2 | 4.35 | 64.026 | 237.792 | 253.4324 | -6.5774 | 93.2059 | 235.3937 | 98.152 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 53 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 58 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 14 | 61 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 7 | 16 | 62 | 44.5 | 28.2258 | 56.25 | 41.7857 | 83.2479 | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 183 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 0.49
FAX Number |  |  | Temperature at which the MTCW was determined, ToC (oC) | 21.5 |  | the desired operating conditions. |  |  | Fluoride (mg/L) | ND |  | 154 | 1998-10-15 | 16:00 | 3423 | 22.75 | 77.83 | 75.23 | 30.9 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 11.5109 | 2.1612 | 43.4688 | 0.26481 | 8.83 | 8.08 | 8.34 | 4.12 | 65.952 | 249.888 | 235.3179 | 5.8306 | 93.753 | 220.2398 | 98.1293 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Turbidity | ntu | 0.07 | 0.08 | 0.1 | 0.10226 | -2.2581 | 12.5 | 0.10023 | 30.1596 | Turbidity | ntu | 0.06 | 0.11 | 0.11 | 0.26 | -136.3636 | 45.4545 | 0.24601 | 75.6112 | Turbidity | ntu | 0.13 | 0.1 | 0.2 | -0.02 | 110 | -30 | -0.0096552 | 1446.4286 | Turbidity | ntu | 0.28 | 0.36 | 0.42 | 0.61333 | -46.0317 | 22.2222 | 0.58921 | 52.4784 | Turbidity | ntu | 0.09 | 0.1 | 0.17 | 0.215 | -26.4706 | 10 | 0.20567 | 56.2411 | Turbidity | ntu | 0.08 | 0.1 | NA | 0.33 | #VALUE! | 20 | 0.31134 | 74.305 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  | 2: The design influent flow rate must be within the range established by the |  |  | Sulfate (mg/L) | 13.2 |  | 155 | 1998-10-16 | 16:00 | 3447 | 22.34 | 78.28 | 75.23 | 30.65 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 11.7756 | 2.1274 | 43.9776 | 0.26776 | 8.89 | 8.24 | 8.56 | 6.185 | 67.05 | 261.976 | 233.7672 | 10.7677 | 90.7755 | 218.9249 | 97.1748 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | 0.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Minimum flow rate to the element, QI, min (gpm) | 4 |  | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  |  | Calcium (mg/L) | 8.4 |  | 156 | 1998-10-17 | 16:00 | 3471 | 22.26 | 77.67 | 75.54 | 30.44 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 11.9437 | 2.1966 | 43.9684 | 0.27164 | 8.51 | 7.93 | 8.2 | 3.205 | 65.952 | 265.272 | 237.8242 | 10.347 | 95.1404 | 222.8637 | 98.5619 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Total organic carbon | mg/L | BMRL | 2.38 | 8.52 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.18 | 8.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.29 | 9.88 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.43 | 8.94 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.54 | 27.78 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.64 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | 37th Street WTP |  | Total width of all membrane envelopes in the element, w (ft) | 12.68 |  |  |  |  | Barium (mg/L) | 0.037 |  | 157 | 1998-10-18 | 16:00 | 3495 | 22.34 | 76.76 | 74.62 | 29.74 | 4.08 | 0.63 | 0.28 |  | 0.91 | 4.99 | 0.35715 | 0.69231 | 4.4835 | 12.96 | 11.9768 | 1.9329 | 44.0171 | 0.2721 | 8.87 | 8.26 | 8.51 | 4.12 | 67.602 | 233.4 | 210.4365 | 9.8387 | 93.9055 | 197.4125 | 97.913 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | UV254 | cm-1 | BMRL | 0.041 | 0.149 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.048 | 0.179 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.041 | 0.171 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.049 | 0.158 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.041 | 0.504 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.041 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Treatment Plant Category | Conventional |  | Feed spacer thickness, T (ft) | 0.0023 |  | Estimate the Osmotic Pressure Gradient |  |  | Strontium (mg/L) | 0.051 |  | 158 | 1998-10-19 | 16:00 | 3519 | 23.09 | 87.29 | 82.4 | 29.25 | 4.7 | 0.83 | 0.28 |  | 1.11 | 5.81 | 0.41216 | 0.74775 | 4.2342 | 17.0743 | 15.7353 | 2.1629 | 53.4321 | 0.29449 | 7.65 | 7.64 | 7.93 | 3.895 | 62.652 | 265.272 | 236.8245 | 10.7239 | 93.7831 | 220.1867 | 98.231 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SUVA | L/(mg*m) | NR | 1.7227 | 1.7488 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.2018 | 2 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.7904 | 1.7308 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.0165 | 1.7673 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.6142 | 1.8143 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.553 | NR | --- | --- | --- | --- | ---
Process Train Name | West |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 |  | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.7 |  | Reactive silica (mg/L as SiO2) | 3.7 |  | 159 | 1998-10-20 | 16:00 | 3543 | 22.92 | 81.49 | 78.13 | 29.46 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 12.562 | 1.9679 | 48.3821 | 0.25964 | 8.88 | 8.24 | 8.5 | 4.58 | 66.228 | 250.616 | 215.9446 | 13.8345 | 93.0845 | 201.3677 | 97.7256 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Bromide | mg/L | BMRL | 32 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 36 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 36 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 40 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 677 |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 |  | Feed TDS, TDSF (mg/L) | 70 |  |  |  |  | 160 | 1998-10-21 | 16:00 | 3567 | 20.6 | 84.08 | 81.18 | 30.44 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 12.6358 | 2.2882 | 49.9018 | 0.25321 | 8.79 | 8.16 | 8.42 | 5.265 | 67.326 | 265.272 | 250.8107 | 5.4515 | 92.1798 | 234.0801 | 97.7508 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Cl2 dose | mg/L | 3.1 | 6.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.86 | NR | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.57 | 3.86 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 0.67 | 3.99 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | 3.99 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | 3.99 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | VA3710150 |  |  |  |  | Waste TDS, TDSW (mg/L) | 154.99 |  |  |  |  | 161 | 1998-10-22 | 16:00 | 3591 | 19.93 | 84.08 | 81.64 | 30.23 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 13.697 | 2.9082 | 49.7218 | 0.27547 | 9.37 | 8.89 | 9.09 | 8.7 | 71.172 | 282.496 | 321.06 | -13.6512 | 87.7761 | 299.5179 | 97.0953 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Free Cl2 residual | mg/L | 2.05 | 3.1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.49 | NA | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.62 | 1.44 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.35 | 1.31 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.56 | 1.19 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.18 | 1.28 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 9 |  | Additional Information |  |  | Permeate TDS, TDSp (mg/L) | 41.67 |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  | 162 | 1998-10-23 | 16:00 | 3600 | 19.43 | 84.08 | 81.64 | 29.95 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 14.0231 | 2.8634 | 50.0466 | 0.2802 | 8.62 | 8.02 | 8.24 | 5.265 | 66.774 | 325.36 | 312.81 | 3.8573 | 92.1152 | 291.6 | 98.1944 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Cl2 demand | mg/L | 1.05 | 3.1 | --- | 7.6629 | --- | 66.129 | 7.2468 | 85.5109 | SDS-Cl2 demand | mg/L | 1.37 | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 1.95 | 2.42 | --- | 4.3 | --- | 19.4215 | 4.1379 | 52.875 | SDS-Cl2 demand | mg/L | 0.32 | 2.68 | --- | 10.1533 | --- | 88.0597 | 9.4416 | 96.6107 | SDS-Cl2 demand | mg/L | 1.44 | 2.8 | --- | 18.44 | --- | 48.5714 | 17.1715 | 91.614 | SDS-Cl2 demand | mg/L | 0.82 | 2.71 | --- | 24.445 | --- | 69.7417 | 22.6821 | 96.3848
Historical Average Water Temperature (oC) | 32 |  | Design cross-flow velocity (fps) | 0.34989 |  | Influent TDS, TDSI (mg/L) | 138.9 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  | 163 | 1998-10-24 | 16:00 | 3624 | 19.65 | 83.62 | 80.73 | 29.31 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 14.2725 | 2.3352 | 50.5298 | 0.28246 | 8.87 | 8.22 | 8.52 | 4.81 | 68.148 | 259.408 | 255.4082 | 1.5419 | 92.9418 | 238.3333 | 97.9818 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Chlorination temp. | oC | 22.5 | 22.5 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 19.4 | NR | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 16.9 | 16.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 18.2 | 18.1 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 17.6 | 17.4 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 17.5 | 17.3 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 28 |  | Required influent flow to permeate flow rate ratio, QI:Qp | n/a |  | Osmotic pressure gradient, Dp (psi) | 1.0528 |  |  |  |  | 164 | 1998-10-25 | 16:00 | 3648 | 19.47 | 87.9 | 84.85 | 29.92 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 15.2034 | 2.7208 | 53.7342 | 0.28294 | 8.65 | 8.11 | 8.27 | 4.35 | 74.748 | 304.48 | 298.1851 | 2.0674 | 94.1804 | 276.4306 | 98.4264 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Chlorination pH | --- | 7.22 | 7.5 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.02 | NR | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.09 | 7.29 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 5.37 | 7.52 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.05 | 7.12 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.41 | 7.12 | --- | --- | --- | --- | --- | ---
|  |  | Maximum element recovery (%) | n/a | [7 empty] | 165 | 1998-10-26 | 16:00 | 3672 | 19.47 | 88.36 | 85.15 | 31.2 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 14.2523 | 2.4957 | 53.0593 | 0.26861 | 8.42 | 7.92 | 8.17 | 4.58 | 72.27 | 282.128 | 272.397 | 3.4492 | 93.6627 | 254.1489 | 98.1979 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Incubation time | hours | 24 | 23.9167 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | NR | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23 | 23.0833 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | ---
|  |  | Variability of design flux (%) | 20 |  | Estimate the Required Influent Pressure | [5 empty] | 166 | 1998-10-27 | 16:00 | 3696 | 18.94 | 88.05 | 85.76 | 30.32 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 14.2523 | 2.4782 | 54.1068 | 0.26341 | 8.93 | 8.33 | 8.52 | 5.495 | 72.822 | 280.296 | 271.8757 | 3.0041 | 92.4542 | 253.3164 | 97.8308 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TOX | mg Cl- /L | BMRL | 162 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 49.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 180 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 164.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 27 | 174.9 | --- | 1875.75 | --- | 84.5626 | 1737.796 | 98.4463 | SDS-TOX | mg Cl- /L | 61 | 168.9 | --- | 1409.75 | --- | 63.884 | 1309.1061 | 95.3403
|  |  | Rejection of reference solute and conditions of test | 99.6 |  | Estimated system pressure losses, DPloss (psi) | 2 |  |  |  |  | 167 | 1998-10-28 | 16:00 | 3720 | 19.4 | 88.51 | 85.76 | 30.1 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 14.522 | 2.3096 | 54.7254 | 0.26536 | 5.5 | 7.21 | 7.51 | 3.205 | 65.952 | 279.56 | 251.4649 | 10.0498 | 95.1404 | 234.1681 | 98.6313 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CHCl3 | mg/L | BMRL | 79.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 0.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 19.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | 37.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 0.5 | 31.7 | --- | 390.5 | --- | 98.4227 | 361.3982 | 99.8616 | SDS-CHCl3 | mg/L | BMRL | 46.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | (e.g., solute type and concentration) | (mg/L MgSO4) |  | Design permeate pressure, Pp (psi) | 30 |  |  |  |  | 168 | 1998-10-29 | 16:00 | 3745 | 19.27 | 93.09 | 90.19 | 30.9 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 15.3381 | 2.0749 | 58.6651 | 0.26145 | 8.18 | 7.83 | 8.05 | 3.435 | 65.4 | 241.456 | 226.9516 | 6.0071 | 94.7477 | 210.9234 | 98.3714 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-BDCM | mg/L | BMRL | 9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 8.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 5.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 7.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Variability of rejection of reference solute (%) | 95 min. |  | Required influent pressure, PI (psi) | 80.8246 |  |  |  |  | 169 | 1998-10-30 | 16:00 | 3769 | 18.83 | 93.85 | 91.1 | 29.71 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 14.3534 | 2.288 | 60.477 | 0.23734 | 8.45 | 8.01 | 8.25 | 3.895 | 65.952 | 275.168 | 249.4249 | 9.3554 | 94.0942 | 232.6954 | 98.3261 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DBCM | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 0.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing recovery (%) | 15 | [7 empty] | 170 | 1998-10-31 | 16:00 | 3793 | 19 | 97.51 | 94 | 32.91 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36288 | 0.74725 | 4.5934 | 13.9886 | 14.5787 | 2.3403 | 60.5047 | 0.24095 | 8.58 | 8.06 | 8.27 | 3.665 | 67.05 | 275.536 | 254.4491 | 7.653 | 94.5339 | 237.6973 | 98.4581 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing pH | 8 | [7 empty] | 171 | 1998-11-01 | 16:00 | 3817 | 18.28 | 96.9 | 93.54 | 30.47 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 13.4256 | 2.1899 | 62.5601 | 0.2146 | 8.82 | 8.33 | 8.57 | 4.12 | 66.774 | 244.024 | 238.3915 | 2.3082 | 93.8299 | 223.1129 | 98.1534 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-THM4 | mg/L | 0 | 89.9 | --- | 290 | --- | 100 | 271.7544 | 100 | SDS-THM4 | mg/L | 0.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 0 | 26.2 | --- | 131 | --- | 100 | 121.9655 | 100 | SDS-THM4 | mg/L | 0 | 47.5 | --- | 197.9167 | --- | 100 | 183.5913 | 100 | SDS-THM4 | mg/L | 0.5 | 37.2 | --- | 459.25 | --- | 98.6559 | 425.018 | 99.8824 | SDS-THM4 | mg/L | 0 | 54.4 | --- | 680 | --- | 100 | 629.2583 | 100
|  |  | Acceptable range of operating pressures | 250 max. | [7 empty] | 172 | 1998-11-02 | 16:00 | 3841 | 17.81 | 99.8 | 96.44 | 30.99 | 3.97 | 0.63 | 0.28 |  | 0.91 | 4.88 | 0.34875 | 0.69231 | 4.3626 | 12.96 | 13.7733 | 1.941 | 65.189 | 0.21128 | 8.76 | 8.12 | 8.31 | 4.58 | 68.424 | 256.848 | 212.073 | 17.4325 | 93.3064 | 198.6795 | 97.6948 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 4.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 2.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Acceptable range of operating pH values | 3 - 9 | [7 empty] | 173 | 1998-11-03 | 16:00 | 3865 | 18.45 | 99.5 | 96.9 | 29.68 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 15.1176 | 2.3651 | 66.1549 | 0.22852 | 8.53 | 8.09 | 8.28 | 3.895 | 68.148 | 259.408 | 258.1134 | 0.49906 | 94.2845 | 240.4015 | 98.3798 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DCAA* | mg/L | BMRL | 15 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Typical pressure drop across a single element (psi) | 3 - 5 | [7 empty] | 174 | 1998-11-04 | 16:00 | 3889 | 18.63 | 100.11 | 97.21 | 29.83 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 13.6902 | 2.3697 | 66.4603 | 0.20599 | 8.42 | 8.01 | 8.22 | 3.205 | 70.896 | 260.512 | 256.3105 | 1.6128 | 95.4793 | 240.1712 | 98.6655 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TCAA* | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible SDI | 5 | [7 empty] | 175 | 1998-11-05 | 16:00 | 3913 | 18.08 | 100.56 | 97.82 | 28.76 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 13.603 | 2.1838 | 68.2462 | 0.19932 | 9.35 | 8.95 | 9.18 | 8.245 | 70.626 | 264.544 | 241.4957 | 8.7125 | 88.3258 | 226.6224 | 96.3618 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 176 | 1998-11-06 | 16:00 | 3937 | 18.22 | 101.48 | 97.66 | 29.34 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 13.8718 | 2.1661 | 68.0639 | 0.20381 | 9.02 | 8.44 | 8.74 | 5.725 | 67.602 | 239.624 | 237.0912 | 1.057 | 91.5313 | 222.3381 | 97.4251 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 3 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | [7 empty] | 177 | 1998-11-07 | 16:00 | 3961 | 17.98 | 114.91 | 112.01 | 32.76 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 13.8027 | 2.1645 | 78.5355 | 0.17575 | 5.16 | 6.89 | 7.27 | 1.375 | 63.204 | 221.672 | 232.5617 | -4.9125 | 97.8245 | 217.82 | 99.3687 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-BCAA* | mg/L | BMRL | 4.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 7.7 | 4.3 | --- | -9.3 | --- | -79.0698 | -8.1276 | 194.7391 | SDS-BCAA* | mg/L | BMRL | 3.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 178 | 1998-11-08 | 16:00 | 3985 | 17.35 | 122.23 | 119.49 | 30.74 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 15.0262 | 2.2677 | 87.8523 | 0.17104 | 5.41 | 7.13 | 7.51 | 2.52 | 64.026 | 246.952 | 245.8698 | 0.43821 | 96.0641 | 229.2889 | 98.9009 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 179 | 1998-11-09 | 16:00 | 4009 | 17.32 | 121.47 | 118.57 | 30.84 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 14.2384 | 2.2893 | 86.8907 | 0.16387 | 5.88 | 7.41 | 7.81 | 1.83 | 67.326 | 232.296 | 246.7281 | -6.2128 | 97.2819 | 230.7565 | 99.207 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 180 | 1998-11-10 | 16:00 | 4033 | 17 | 127.73 | 124.98 | 31.32 | 4.08 | 0.63 | 0.28 |  | 0.91 | 4.99 | 0.35715 | 0.69231 | 4.4835 | 12.96 | 14.2537 | 2.004 | 93.031 | 0.15321 | 8.85 | 8.23 | 8.52 | 3.435 | 69.252 | 244.392 | 217.3402 | 11.069 | 95.0399 | 203.8372 | 98.3148 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DCBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 7.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 8.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 4.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Field 3-5: Pretreatment Used Prior To Membranes1 | [11 empty] | 181 | 1998-11-11 | 16:00 | 4057 | 17.12 | 127.57 | 124.22 | 30.01 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 14.4182 | 2.3131 | 93.5719 | 0.15409 | 9.04 | 8.31 | 8.62 | 3.895 | 70.074 | 242.92 | 251.3469 | -3.469 | 94.4416 | 235.2087 | 98.344 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-HAA5 | mg/L | 0 | 38 | --- | 122.5806 | --- | 100 | 114.8684 | 100 | SDS-HAA5 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 3 | 31 | --- | 143 | --- | 90.3226 | 133.3448 | 97.7502 | SDS-HAA5 | mg/L | 0 | 29 | --- | 120.8333 | --- | 100 | 112.0873 | 100 | SDS-HAA5 | mg/L | 0 | 49.1 | --- | 613.75 | --- | 100 | 567.9519 | 100 | SDS-HAA5 | mg/L | 0 | 31.7 | --- | 396.25 | --- | 100 | 366.6818 | 100
[12 empty] | 182 | 1998-11-12 | 16:00 | 4081 | 17.03 | 145.73 | 141.92 | 26.72 | 4.18 | 0.63 | 0.17 |  | 0.8 | 4.98 | 0.35639 | 0.7875 | 5.225 | 12.96 | 14.3563 | 2.877 | 114.228 | 0.12568 | 8.54 | 7.93 | 8.24 | 3.435 | 68.7 | 261.24 | 310.5644 | -18.8809 | 95 | 291.1376 | 98.8201 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-HAA6 | mg/L | 0 | 42.3 | --- | 136.4516 | --- | 100 | 127.8666 | 100 | SDS-HAA6 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 10.7 | 35.3 | --- | 133.7 | --- | 69.6884 | 125.2172 | 91.4549 | SDS-HAA6 | mg/L | 0 | 32.4 | --- | 135 | --- | 100 | 125.2286 | 100 | SDS-HAA6 | mg/L | 0 | 54.1 | --- | 676.25 | --- | 100 | 625.7881 | 100 | SDS-HAA6 | mg/L | 0 | 35 | --- | 437.5 | --- | 100 | 404.8537 | 100
Process | Description | [8 empty] | Scale |  | 183 | 1998-11-13 | 9:00 | 4098 | 16.57 | 163.13 | 160.08 | 27.82 | 3.97 | 0.68 | 0.28 | X | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 15.5458 | 2.1476 | 131.6374 | 0.1181 | 8.95 | 8.26 | 8.57 | 2.52 | 69.798 | 253.912 | 233.1874 | 8.1621 | 96.3896 | 217.2793 | 98.8402 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Rapid Mix | Type: | Mechanical | [7 empty] | Full |  | 184 | 1998-11-14 | 16:00 | 4120 | 15.52 | 84.54 | 81.49 | 29.95 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36288 | 0.74725 | 4.5934 | 13.9886 | 15.8051 | 2.4097 | 50.6553 | 0.31201 | 8.65 | 7.98 | 8.24 | 3.435 | 68.7 | 250.616 | 261.6574 | -4.4057 | 95 | 244.4087 | 98.5946 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
| Chemical Name: | Alum |  |  |  | Powdered Activated Carbon (PAC) | [5 empty] | 185 | 1998-11-15 | 16:00 | 4144 | 15.92 | 87.9 | 84.85 | 31.84 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 16.4165 | 2.0819 | 52.4531 | 0.31297 | 8.25 | 7.72 | 8.01 | 3.205 | 68.424 | 242.92 | 226.813 | 6.6306 | 95.316 | 211.3918 | 98.4839 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Chemical Formula: | Al2(SO4)3*14H2O | [9 empty] | 186 | 1998-11-16 | 16:00 | 4168 | 15.69 | 88.2 | 86.37 | 31.6 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 16.1803 | 2.0677 | 53.6173 | 0.30177 | 8.98 | 8.13 | 8.39 | 4.58 | 69.252 | 256.112 | 226.3126 | 11.6353 | 93.3865 | 211.3544 | 97.833 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
| Dose: | AVG | MAX | MIN | STD DEV | AVG | MAX | MIN | STD DEV |  |  | 187 | 1998-11-17 | 16:00 | 4192 | 16.62 | 87.9 | 85 | 31.9 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 16.3156 | 2.3348 | 52.2152 | 0.31247 | 8.64 | 7.96 | 8.23 | 2.52 | 65.952 | 255.384 | 253.4901 | 0.74159 | 96.179 | 236.0045 | 98.9322 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  | 30.1 | 49.7 | 20.6 | 7.15 | 2.36 | 6.47 | 0 | 1.36 |  |  | 188 | 1998-11-18 | 16:00 | 4216 | 16.04 | 88.2 | 85.61 | 31.72 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 15.7766 | 2.2808 | 52.9042 | 0.29821 | 9.16 | 8.37 | 8.73 | 4.81 | 66.774 | 260.88 | 249.9719 | 4.1813 | 92.7966 | 232.891 | 97.9347 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
Flocculation | Type: | Mechanical | [7 empty] | Full |  | 189 | 1998-11-19 | 16:00 | 4240 | 16.85 | 87.29 | 85.61 | 31.05 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 16.1102 | 2.3568 | 53.0432 | 0.30372 | 9.04 | 8.28 | 8.63 | 4.12 | 68.148 | 263.808 | 257.4482 | 2.4108 | 93.9543 | 239.7983 | 98.2819 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Qp/QT (THM4), % | 19.911 | 59.9555 |  | Qp/QT (HAA5), % | -42.1053 | 28.9474 |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | -174.8092 | -37.4046 |  | Qp/QT (HAA5), % | -82.1429 | 14.2857 |  |  |  | Qp/QT (THM4), % | -51.5789 | 24.2105 |  | Qp/QT (HAA5), % | -86.2069 | 6.8966 |  |  |  | Qp/QT (THM4), % | -94.8229 | 3.2698 |  | Qp/QT (HAA5), % | -9.9796 | 45.0102 |  |  |  | Qp/QT (THM4), % | -32.3529 | 33.8235 |  | Qp/QT (HAA5), % | -70.347 | 14.8265
Sedimentation | Type: | Conventional | [7 empty] | Full |  | 190 | 1998-11-20 | 16:00 | 4262 | 16.89 | 87.29 | 84.39 | 31.14 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 15.6466 | 2.2808 | 52.4192 | 0.29849 | 8.42 | 7.77 | 8.07 | 3.435 | 65.4 | 237.064 | 248.6009 | -4.8666 | 94.7477 | 231.5196 | 98.5163 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 63.8763 |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | 22.4571 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 44.2241 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 20.6813 |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 46.3344
Filtration | Type: | Dual Media - Anthracite/Sand | [7 empty] | Pilot |  | 191 | 1998-11-21 | 16:00 | 4286 | 16.85 | 88.05 | 85.91 | 31.2 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 15.6242 | 2.2809 | 53.4991 | 0.29205 | 8.48 | 7.86 | 8.14 | 2.06 | 64.026 | 239.992 | 247.2298 | -3.0159 | 96.7826 | 230.1483 | 99.1049 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-HAA5b, mg/L | 30.4338 | 15.2169 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 21.9789 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 47.4946 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | NA | 20.9779 |  | SDS-HAA5b, mg/L | NA | 27
[12 empty] | 192 | 1998-11-22 | 16:00 | 4310 | 16.24 | 87.9 | 86.22 | 30.32 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 15.6466 | 2.1184 | 54.6216 | 0.28645 | 8.9 | 8.15 | 8.46 | 3.435 | 69.798 | 243.288 | 230.9653 | 5.0651 | 95.0787 | 215.2735 | 98.4044 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | 170.064 |  | SDS-TOXb, mg Cl- /L | NA | 108.3299 |  |  |  | SDS-TOXb, mg Cl- /L | NA | 132.4044 |  | SDS-TOXb, mg Cl- /L | NA | 152.9022
1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [11 empty] | 193 | 1998-11-23 | 16:00 | 4334 | 16.31 | 97.36 | 95.68 | 34.22 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 17.1703 | 2.5304 | 59.7696 | 0.28727 | 8.69 | 7.99 | 8.28 | 3.895 | 69.252 | 250.616 | 276.6894 | -10.4037 | 94.3756 | 256.9335 | 98.484 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CDb, mg/L | 2.6918 | 1.8709 |  | SDS-CDb, mg/L | NA | 2.5066 |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | 2.3529 |  |  |  | SDS-CDb, mg/L | NA | 2.1086 |  | SDS-CDb, mg/L | NA | 2.5172 |  |  |  | SDS-CDb, mg/L | NA | 2.7555 |  | SDS-CDb, mg/L | NA | 2.1879 |  |  |  | SDS-CDb, mg/L | NA | 2.0707 |  | SDS-CDb, mg/L | NA | 2.4298
the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [11 empty] | 194 | 1998-11-24 | 16:00 | 4358 | 17.58 | 90.8 | 88.05 | 29.13 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 17.127 | 2.7681 | 57.5269 | 0.29772 | 8.02 | 7.95 | 7.87 | 2.975 | 74.472 | 249.152 | 301.3973 | -20.9692 | 96.0052 | 279.7853 | 98.9367 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE!
is to list the pretreatment processes used in this particular Long-Term SEBST run. | [11 empty] | 195 | 1998-11-25 | 16:00 | 4381 | 16.18 | 92.63 | 89.88 | 30.01 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 14.1216 | 2.622 | 58.623 | 0.24089 | 8.89 | 8.31 | 8.32 | 2.75 | 77.766 | 245.12 | 283.2446 | -15.5534 | 96.4638 | 264.9515 | 98.9621 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE!
[12 empty] | 196 | 1998-11-26 | 16:00 | 4405 | 16.86 | 93.7 | 90.64 | 29.86 | 4.08 | 0.63 | 0.28 |  | 0.91 | 4.99 | 0.35715 | 0.69231 | 4.4835 | 12.96 | 14.8503 | 2.2941 | 60.0159 | 0.24744 | 8.87 | 8.29 | 8.26 | 2.975 | 78.318 | 256.48 | 247.8398 | 3.3688 | 96.2014 | 232.3824 | 98.7198 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE!
[12 empty] | 197 | 1998-11-27 | 16:00 | 4429 | 16.3 | 95.99 | 93.24 | 30.41 | 3.87 | 0.68 | 0.28 |  | 0.96 | 4.83 | 0.34302 | 0.70833 | 4.0312 | 13.9886 | 15.641 | 2.3909 | 61.8141 | 0.25303 | 7.06 | 7.71 | 7.71 | 2.75 | 77.766 | 243.656 | 259.9477 | -6.6864 | 96.4638 | 241.8427 | 98.8629 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Alkb, mg/L CaCO3 | 13.6107 | 8.8053 |  | Alkb, mg/L CaCO3 | NA | 12.5263 |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | 14.1429 |  |  |  | Alkb, mg/L CaCO3 | NA | 16.1579 |  | Alkb, mg/L CaCO3 | NA | 19.6207 |  |  |  | Alkb, mg/L CaCO3 | NA | 18.6076 |  | Alkb, mg/L CaCO3 | NA | 13.5988 |  |  |  | Alkb, mg/L CaCO3 | NA | 14.9412 |  | Alkb, mg/L CaCO3 | NA | 17.2208
[12 empty] | 198 | 1998-11-28 | 16:00 | 4453 | 16.44 | 96.29 | 93.39 | 29.77 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 15.9597 | 2.4073 | 62.6627 | 0.25469 | 8.33 | 7.97 | 8.01 | 2.75 | 78.042 | 257.216 | 260.894 | -1.4299 | 96.4763 | 243.4795 | 98.8705 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | T-Hdb, mg/L CaCO3 | 23.6196 | 14.8098 |  | T-Hdb, mg/L CaCO3 | NA | 21.6316 |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | 30.2857 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 26.1895 |  | T-Hdb, mg/L CaCO3 | NA | 30.3448 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 30.0518 |  | T-Hdb, mg/L CaCO3 | NA | 17.947 |  |  |  | T-Hdb, mg/L CaCO3 | NA | 20.5294 |  | T-Hdb, mg/L CaCO3 | NA | 25.8486
[12 empty] | 199 | 1998-11-29 | 16:00 | 4477 | 15.72 | 99.19 | 95.68 | 29.98 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 15.8793 | 2.808 | 64.647 | 0.24563 | 7.09 | 7.72 | 7.69 | 1.605 | 77.766 | 263.072 | 302.9377 | -15.1539 | 97.9361 | 282.406 | 99.4317 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | 13.8211 |  | Ca-Hdb, mg/L CaCO3 | NA | 15.3793 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE!
[13 empty] | 1998-11-30 | 16:00 | 4501 | 16.28 | 100.87 | 97.36 | 30.84 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.2979 | 2.7711 | 65.5039 | 0.24881 | 7.78 | 7.88 | 7.85 | 3.435 | 78.594 | 252.816 | 300.8032 | -18.9811 | 95.6294 | 280.5417 | 98.7756 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[12 empty] | 201 | 1998-12-01 | 16:00 | 4525 | 16.45 | 104.84 | 102.7 | 31.54 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36288 | 0.74725 | 4.5934 | 13.9886 | 15.9712 | 2.7751 | 69.4549 | 0.22995 | 8 | 7.97 | 7.89 | 2.06 | 77.22 | 257.944 | 299.4322 | -16.0842 | 97.3323 | 279.5684 | 99.2631 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[12 empty] | 202 | 1998-12-02 | 16:00 | 4549 | 15.96 | 105.75 | 103.46 | 30.77 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36288 | 0.74725 | 4.5934 | 13.9886 | 15.8736 | 2.9305 | 70.9045 | 0.22387 | 8.1 | 7.95 | 7.97 | 2.52 | 81.888 | 277 | 316.5412 | -14.2748 | 96.9226 | 295.5653 | 99.1474 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[12 empty] | 203 | 1998-12-03 | 16:00 | 4573 | 15.53 | 115.82 | 112.31 | 30.71 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.1569 | 2.9991 | 80.3559 | 0.20107 | 8.54 | 8.24 | 8.21 | 4.12 | 85.464 | 300.448 | 325.9593 | -8.4911 | 95.1793 | 304.0304 | 98.6449 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[12 empty] | 204 | 1998-12-04 | 16:00 | 4597 | 18.6 | 114.3 | 111.4 | 30.62 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.4105 | 2.7964 | 79.4336 | 0.20659 | 8.92 | 8.52 | 8.52 | 5.495 | 81.342 | 330.496 | 305.5853 | 7.5374 | 93.2446 | 285.1383 | 98.0729 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[12 empty] | 205 | 1998-12-05 | 16:00 | 4621 | 16.31 | 114.91 | 111.7 | 27.79 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 13.6175 | 2.7434 | 82.7716 | 0.16452 | 8.4 | 8.1 | 8.1 | 2.975 | 81.342 | 316.2 | 295.9994 | 6.3885 | 96.3426 | 277.3147 | 98.9272 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[12 empty] | 206 | 1998-12-06 | 16:00 | 4645 | 17.35 | 115.82 | 111.86 | 31.66 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 14.7808 | 2.8476 | 79.3324 | 0.18632 | 8.93 | 8.53 | 8.48 | 4.12 | 85.464 | 287.624 | 308.2758 | -7.1801 | 95.1793 | 288.8813 | 98.5738 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[12 empty] | 207 | 1998-12-07 | 16:00 | 4669 | 17.76 | 117.96 | 113.99 | 31.81 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 15.3684 | 2.8959 | 81.2691 | 0.18911 | 7.96 | 7.96 | 7.92 | 2.52 | 81.066 | 263.808 | 313.289 | -18.7564 | 96.8914 | 292.1143 | 99.1373 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[12 empty] | 208 | 1998-12-08 | 16:00 | 4693 | 17.93 | 126.05 | 122.54 | 33.58 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35066 | 0.70833 | 4.1354 | 13.9886 | 15.1446 | 2.5205 | 88.1945 | 0.17172 | 8.07 | 7.97 | 7.93 | 3.205 | 82.164 | 264.544 | 273.9216 | -3.5448 | 96.0993 | 255.2515 | 98.7444 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[12 empty] | 209 | 1998-12-09 | 16:00 | 4717 | 16.89 | 131.54 | 128.95 | 30.96 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 15.053 | 2.5773 | 96.7077 | 0.15565 | 7.86 | 7.91 | 7.89 | 1.83 | 82.44 | 275.536 | 278.2071 | -0.96944 | 97.7802 | 259.5627 | 99.295 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[12 empty] | 210 | 1998-12-10 | 16:00 | 4741 | 17.11 | 145.12 | 141.31 | 31.14 | 3.97 | 0.68 | 0.17 |  | 0.85 | 4.82 | 0.34225 | 0.8 | 4.6706 | 13.9886 | 15.6242 | 3.7675 | 108.3075 | 0.14426 | 8.95 | 8.48 | 8.39 | 4.12 | 85.188 | 382.52 | 409.46 | -7.0428 | 95.1636 | 380.8676 | 98.9183 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on K13: C. Rice: Consultant verified the decrease in aluminum concentration from the raw to the filtered water; no explanation was given.
Note on K14: C. Rice: The "Pilot Filtered" sulfate is higher than the raw water concentration because aluminum sulfate was added for coagulation.
Note on AS5: TSC_ADM: Operational TDS data is based on an empirical factor applied to the on-line conductivity measurements (compared to the biweekly TDS data, which are based on lab measurements); therefore, there may be discrepancies between the operational and biweekly TDS data.
Note on BQ33: C. Rice: Consultant verified value; no explanation given.
Note on CB26: TSC_ADM: Changed reported value from 3.72 to NR because chlorine residual was NA
Note on CB29: TSC_ADM: Changed reported value from 19.4 to NR because chlorine residual was NA
Note on CB30: TSC_ADM: Changed reported value from 7.07 to NR because chlorine residual was NA
Note on CB31: TSC_ADM: Changed reported value from 24 to NR because chlorine residual was NA
Note on CB32: TSC_ADM: Changed reported value from 166 to NR because chlorine residual was NA
Note on CB33: TSC_ADM: Changed reported value from 25 to NR because chlorine residual was NA
Note on CB34: TSC_ADM: Changed reported value from 7.9 to NR because chlorine residual was NA
Note on CB35: TSC_ADM: Changed reported value from 0.8 to NR because chlorine residual was NA
Note on CB36: TSC_ADM: Changed reported value from BMRL to NR because chlorine residual was NA
Note on CB38: TSC_ADM: Changed reported value from BMRL to NR because chlorine residual was NA
Note on CB39: TSC_ADM: Changed reported value from 12 to NR because chlorine residual was NA
Note on CB40: TSC_ADM: Changed reported value from 19 to NR because chlorine residual was NA
Note on CB41: TSC_ADM: Changed reported value from BMRL to NR because chlorine residual was NA
Note on CB42: TSC_ADM: Changed reported value from BMRL to NR because chlorine residual was NA
Note on CB43: TSC_ADM: Changed reported value from 3.8 to NR because chlorine residual was NA
Note on CB44: TSC_ADM: Changed reported value from BMRL to NR because chlorine residual was NA
Note on CB45: TSC_ADM: Changed reported value from 3.5 to NR because chlorine residual was NA
Note on CB46: TSC_ADM: Changed reported value from 9.3 to NR because chlorine residual was NA
Note on CJ18: C. Rice: Consultant verified the total hardness data for weeks 26 and 30 but provided no explanation for the high MB closure errors.
Note on CL42: C. Rice: The DBAA and BCAA permeate concentrations for Week 26 are much higher than the permeate concentrations reported for the other weeks. The feed concentration, however, remained relatively constant. The consultant verified the permeate values reported for week 26; however, no explanation was provided.
Note on CW26: C. Rice: Consultant verified value; no explanation given.
Note on CW28: C. Rice: Consultant verified value; no explanation given.
Note on CW30: C. Rice: Consultant verified value; no explanation given.
Note on DF16: C. Rice: Consultant verified the alkalinity data for week 30 but provided no explanation for the high MB closure error.
Note on DH5: C. Rice: Consultant verified that the recovery was indeed 0.92 during the 12/10/98 sample.
Note on DJ10: C. Rice: Reported concentrate concentrations are relatively higher for week 30 because the recovery was 0.92.

## NF70. 102999 - Duplicate HAAs
Field 3-8: Duplicate Analysis of Permeate, Feed, Concentrate And Blended Water Quality For Week 24
Operating Parameters During Sample Collection
| Recovery during sample collection (decimal) | 0.75
| Feed flow rate during sample collection (gpm) | 0.91
| Influent flow rate during sample collection (gpm) | 4.88
Permeate, Feed and Concentrate Water Quality
Parameter | Units | Cp-24 | CF-24 | CC-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%)
Sampling date | MM/DD/YY | 1998-10-29 | 1998-10-29 | --- | --- | --- | --- | --- | ---
Sampling time | hh:mm | 7:40 | 7:25 | --- | --- | --- | --- | --- | ---
Operation time | hh.hh | 3735 | 3735 | --- | --- | --- | --- | --- | ---
pH | --- |  |  | --- | --- | --- | --- | --- | ---
Temperature | oC |  |  | --- | --- | --- | --- | --- | ---
Alkalinity | mg/L as CaCO3 |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
Total dissolved solids | mg/L |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
Total hardness | mg/L as CaCO3 |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
Calcium hardness | mg/L as CaCO3 |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
Turbidity | ntu |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
Ammonia | mg NH3-N / L |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
Total organic carbon | mg/L |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
UV254 | cm-1 |  |  | --- | 0 | #VALUE! | #DIV/0! | 0 | #DIV/0!
SUVA | L/(mg*m) |  |  |  | --- | --- | --- | --- | ---
Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-Cl2 dose | mg/L | 1.86 | 3.72 | --- | --- | --- | --- | --- | ---
SDS-Free Cl2 residual | mg/L | 0.49 | NA | --- | --- | --- | --- | --- | ---
SDS-Cl2 demand | mg/L | 1.37 | #VALUE! | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-Chlorination temp. | oC | 19.4 | 19.4 | --- | --- | --- | --- | --- | ---
SDS-Chlorination pH | --- | 7.02 | 7.07 | --- | --- | --- | --- | --- | ---
SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | ---
SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0!
SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-DCAA* | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-TCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-BCAA* | mg/L | BMRL | 3.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-CDBAA | mg/L | BMRL | 3.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-DCBAA | mg/L | BMRL | 9.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-HAA5 | mg/L | 0 | 32 | --- | 128 | --- | 100 | 119.0492 | 100
SDS-HAA6 | mg/L | 0 | 35.4 | --- | 141.6 | --- | 100 | 131.6982 | 100
BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
*: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Blending Calculations For D-DBP MCLs
| THM4 Controls |  |  |  | HAA5 Controls
| Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | -68.75 | 15.625
SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | NA | 0
SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | NA | 27
SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | NA | 0
SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | NA | #VALUE!
TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | NA | 0
UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | NA | 0
Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | NA | 0
Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | NA | 0
T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | NA | 0
Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | NA | 0
Notes:
This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
The maximum (Qp/QT) ratio controls the design.
Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
The subscript "b" refers to the blended water quality for a given blend ratio.
If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.

## NF70. Weeks 31-40
FIELD-SET 4: LT-SEBST RESULTS: WEEKS 21-30 (FILE: ltsebst.xls)
Field 4-1: PWS And Treatment Plant Data |  |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  |  | Field 4-3: SEBST Design Parameters |  |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [47 empty] | Field 4-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 32 | [10 empty] | Field 4-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 34 | [9 empty] | Field 4-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 36 | [9 empty] | Field 4-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 38 | [9 empty] | Field 4-11: Permeate, Feed, Concentrate And Blended Water Quality For Week 40 | [9 empty] | Field 4-12: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 40 | [9 empty] | Field 4-13: Membrane Cost Parameters
|  |  | General Information |  |  | Calculate Temperature Normalized MTCW |  |  | Parameters Evaluated Prior to Pretreatment |  | (see cell A47) | [49 empty] | Operating Parameters During Sample Collection | [10 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | City of Norfolk |  | Membrane manufacturer | FilmTec |  | Average yearly temperature of feed water, TavgoC (oC) | 20 |  | PLANT FILTERED WATER: |  |  | Day No. | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.82 | [9 empty] | Recovery during sample collection (decimal) | 0.89 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.8 | [8 empty] | Recovery during sample collection (decimal) | [9 empty] | Recovery during sample collection (decimal) | [8 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | VA37010100 |  | Membrane trade name | NF70 |  | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.30143 |  | Alkalinity (mg/L as CaCO3) | 10.5 |  |  | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.6 | [9 empty] | Feed flow rate during sample collection (gpm) | 0.55 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.85 | [8 empty] | Feed flow rate during sample collection (gpm) | [9 empty] | Feed flow rate during sample collection (gpm) | [8 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA |  | Membrane element model number | NF70-4040 |  |  |  |  | pH (units) | 6.44 |  | 211 | 1998-12-11 | 16:00 | 4765 | 16.21 | 147.56 | 145.89 | 29.77 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 15.5012 | 3.8226 | 113.1324 | 0.13702 | 8.57 | 8.21 | 8.17 | 2.52 | 84.636 | 300.08 | 413.1 | -37.6633 | 97.0225 | 384.7841 | 99.3451 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Influent flow rate during sample collection (gpm) | 4.99 | [9 empty] | Influent flow rate during sample collection (gpm) | 4.94 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.99 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.82 | [8 empty] | Influent flow rate during sample collection (gpm) | [9 empty] | Influent flow rate during sample collection (gpm) | [8 empty] | Capital Recovery Period (years) | 20
|  |  | Molecular weight cutoff (Daltons) | 200 |  | Calculate System Flow Rates1 |  |  | Total Dissolved Solids | 73 mg/L |  | 212 | 1998-12-12 | 16:00 | 4790 | 16.4 | 159.31 | 155.65 | 28.4 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 17.1889 | 3.2362 | 125.8438 | 0.13659 | 5.99 | 7.95 | 7.73 | 2.975 | 86.562 | 294.584 | 351.8599 | -19.443 | 96.5632 | 326.5934 | 99.0891 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [61 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide |  | Design recovery, R (decimal) | 0.75 |  | Conductivity | 129 umhos/cm |  | 213 | 1998-12-13 | 16:00 | 4813 | 16.98 | 159.77 | 155.96 | 28.21 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34493 | 0.73256 | 4.6163 | 12.96 | 14.7329 | 2.6606 | 126.9944 | 0.11601 | 5.39 | 7.26 | 7.29 | 1.375 | 77.496 | 247.688 | 286.0013 | -15.4684 | 98.2257 | 267.4388 | 99.4859 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Permeate, Feed and Concentrate Water Quality | [10 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  |  | Membrane construction (e.g., thin-film composite) | Thin-film composite |  | Design flux, FW (gfd) | 14.4 |  | SDI | 5.8 |  | 214 | 1998-12-14 | 16:00 | 4837 | 16.8 | 168.32 | 164.81 | 29.71 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 14.4286 | 2.74 | 134.115 | 0.10758 | 8.14 | 7.99 | 8.01 | 2.52 | 80.79 | 249.52 | 295.1817 | -18.2998 | 96.8808 | 276.5201 | 99.0887 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Parameter | Units | Cp-32 | CF-32 | CC-32 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  | Parameter | Units | Cp-34 | CF-34 | CC-34 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-26 | CF-26 | CC-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-28 | CF-28 | CC-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-30 | CF-30 | CC-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-30 (dup) | CF-30 (dup) | CC-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 15
|  |  | Membrane hydrophobicity | Hydrophobic |  | Permeate flow rate, Qp (gpm) | 0.7 |  | Turbidity (ntu) | 0.26 |  | 215 | 1998-12-15 | 20:00 | 4855 | 16.18 | 188 | 185.87 | 27.39 | 3.97 | 0.63 | 0.28 | X | 0.91 | 4.88 | 0.34875 | 0.69231 | 4.3626 | 12.96 | 14.5222 | 2.3532 | 157.1918 | 0.092385 | 5.41 | 7.2 | 7.22 | 2.29 | 79.692 | 250.248 | 253.8465 | -1.438 | 97.1264 | 237.6087 | 99.0362 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Sampling date | MM/DD/YY | 1998-12-22 | 1998-12-22 | 1998-12-22 | --- | --- | --- | --- | --- |  | Sampling date | MM/DD/YY | 1999-01-05 | 1999-01-05 | 1999-01-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-02 | 1999-02-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 9
Phone Number |  |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative |  | Feed flow rate, QF (gpm) | 0.93333 |  | Dissolved aluminum (mg/L) | <0.044 |  | 216 | 1998-12-16 | 16:00 | 4876 | 16.9 | 92.63 | 90.19 | 29.83 | 3.76 | 0.68 | 0.4 |  | 1.08 | 4.84 | 0.34378 | 0.62963 | 3.4815 | 13.9886 | 16.0289 | 1.7245 | 59.8555 | 0.26779 | 9.08 | 8.36 | 8.55 | 2.75 | 71.448 | 190.528 | 188.2346 | 1.2037 | 96.151 | 175.2047 | 98.4304 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Sampling time | hh:mm | 10:40 | 11:02 | 11:10 | --- | --- | --- | --- | --- |  | Sampling time | hh:mm | 8:15 | 8:30 | 8:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:45 | 11:00 | 11:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:05 | 10:40 | 9:10 | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | Concentrate-waste flow rate, QW (gpm) | 0.23333 |  | Total aluminum (mg/L) | 0.074 |  | 217 | 1998-12-17 | 16:00 | 4897 | 16.81 | 74.47 | 71.57 | 30.93 | 4.29 | 0.49 | 0.17 |  | 0.66 | 4.95 | 0.35944 | 0.74242 | 6.5 | 10.08 | 11.2545 | 2.5081 | 39.5819 | 0.28434 | 9.08 | 8.26 | 8.41 | 4.58 | 72.546 | 270.4 | 268.448 | 0.72189 | 93.6868 | 255.3879 | 98.2066 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Operation time | hh.hh | 5010 | 5010 | 5010 | --- | --- | --- | --- | --- |  | Operation time | hh.hh | 5343 | 5343 | 5343 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5654 | 5654 | 5654 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5961 | 5961 | 5961 | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131.8
E-Mail Address (optional) |  |  | Design Parameters |  |  | Minimum influent flow rate, QI, min (gpm) | 4 |  | PILOT FILTERED: Sulfate (mg/L) | 43 |  | 218 | 1998-12-18 | 16:00 | 4919 | 16.38 | 75.54 | 72.79 | 30.87 | 4.39 | 0.49 | 0.11 |  | 0.6 | 4.99 | 0.3625 | 0.81667 | 7.3167 | 10.08 | 11.291 | 3.4397 | 39.8553 | 0.2833 | 9 | 8.09 | 8.27 | 3.205 | 69.522 | 290.552 | 364.9341 | -25.6003 | 95.3899 | 347.1738 | 99.0768 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | pH | --- | 8.9 | 7.4 | 8.3 | --- | --- | --- | --- | --- |  | pH | --- | 7.06 | 7.2 | 8.21 | --- | --- | --- | --- | --- | pH | --- | 5.78 | 5.57 | 4.84 | --- | --- | --- | --- | --- | pH | --- | 5.48 | 5.93 | 4.52 | --- | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.65
|  |  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" |  | Maximum influent flow rate, QI, max (gpm) | 16 |  | RAW WATER: |  |  | 219 | 1998-12-19 | 16:00 | 4943 | 16.02 | 74.77 | 72.03 | 30.41 | 4.39 | 0.49 | 0.11 |  | 0.6 | 4.99 | 0.3625 | 0.81667 | 7.3167 | 10.08 | 11.4672 | 3.53 | 39.46 | 0.2906 | 8.95 | 8.06 | 8.3 | 3.665 | 71.724 | 294.584 | 374.8959 | -27.2628 | 94.8901 | 356.6691 | 98.9724 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Temperature | oC | 17.7 | 15.8333 | 18.1 | --- | --- | --- | --- | --- |  | Temperature | oC | 13.7 | 11.7 | 13.8 | --- | --- | --- | --- | --- | Temperature | oC | 14 | 12.6 | 14.9 | --- | --- | --- | --- | --- | Temperature | oC | 15.5 | 15.2 | 16.2 | --- | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 30
Technical ICR Contact Person |  |  | Active membrane area of membrane element used, A (ft2) | 70 |  | Design influent flow rate2, QI (gpm) | 4.93 |  | Dissolved iron (mg/L) | 0.2 |  | 220 | 1998-12-20 | 16:00 | 4967 | 16.7 | 74.32 | 71.87 | 31.08 | 4.29 | 0.49 | 0.11 |  | 0.6 | 4.89 | 0.35486 | 0.81667 | 7.15 | 10.08 | 11.6172 | 3.5763 | 38.4387 | 0.30223 | 9.18 | 8.29 | 8.54 | 4.35 | 73.374 | 257.576 | 380.8445 | -47.8572 | 94.0715 | 361.9813 | 98.7983 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Alkalinity | mg/L as CaCO3 | 4 | 18 | 72 | 81.7778 | -13.5802 | 77.7778 | 77.9434 | 94.8681 |  | Alkalinity | mg/L as CaCO3 | 1 | 15 | 74 | 128.2727 | -73.3415 | 93.3333 | 121.9671 | 99.1801 | Alkalinity | mg/L as CaCO3 | 2 | 2 | 0 | 2 | #DIV/0! | 0 | 2 | 0 | Alkalinity | mg/L as CaCO3 | 1 | 4 | 0 | 16 | #DIV/0! | 75 | 14.9419 | 93.3074 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.049
Mailing Address |  |  | Design flux, FW (gfd) | 14.4 |  | Design recycle flow rate, QR (gpm) | 3.9967 |  | Total iron (mg/L) | 0.6 |  | 221 | 1998-12-21 | 16:00 | 4991 | 16.67 | 74.93 | 72.18 | 31.11 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 10.1791 | 2.3834 | 40.0616 | 0.25409 | 9.04 | 8.19 | 8.38 | 3.895 | 73.374 | 269.304 | 253.202 | 5.9791 | 94.6916 | 242.2325 | 98.392 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Total dissolved solids | mg/L | 2 | 65 | 263 | 352 | -33.8403 | 96.9231 | 334.7455 | 99.4025 |  | Total dissolved solids | mg/L | 14 | 90 | 327 | 704.9091 | -115.5685 | 84.4444 | 670.6783 | 97.9126 | Total dissolved solids | mg/L | 10 | 63 | 259 | 222 | 14.2857 | 84.127 | 207.502 | 95.1808 | Total dissolved solids | mg/L | 3 | 51 | 254 | 243 | 4.3307 | 94.1176 | 226.0705 | 98.673 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | NA
|  |  | Net driving pressure at the design flux, NDP (psi) | 45.7 |  | Recycle ratio, r | 4.2821 |  | Dissolved aluminum (mg/L) | 0.12 |  | 222 | 1998-12-22 | 16:00 | 5015 | 16.32 | 74.77 | 72.64 | 31.26 | 4.39 | 0.49 | 0.11 |  | 0.6 | 4.99 | 0.3625 | 0.81667 | 7.3167 | 10.08 | 11.348 | 3.6916 | 38.7534 | 0.29283 | 9.12 | 8.26 | 8.46 | 5.495 | 76.668 | 299.712 | 393.7114 | -31.3632 | 92.8327 | 374.6506 | 98.5333 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Total hardness | mg/L as CaCO3 | 3 | 30 | 108 | 153 | -41.6667 | 90 | 145.6052 | 97.9396 |  | Total hardness | mg/L as CaCO3 | 1 | 28 | 105 | 246.4545 | -134.7186 | 96.4286 | 234.2936 | 99.5732 | Total hardness | mg/L as CaCO3 | 1 | 27 | 98 | 105 | -7.1429 | 96.2963 | 97.8878 | 98.9784 | Total hardness | mg/L as CaCO3 | 2 | 33 | 107 | 157 | -46.729 | 93.9394 | 146.0664 | 98.6308 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.3151 |  | 1: Flow rates and pressures may need to be adjusted in order to obtain |  |  | Total aluminum (mg/L) | 0.38 |  | 223 | 1998-12-23 | 16:00 | 5039 | 15.04 | 75.08 | 71.87 | 30.35 | 4.39 | 0.44 | 0.11 |  | 0.55 | 4.94 | 0.36059 | 0.8 | 7.9818 | 9.0514 | 10.3194 | 3.35 | 39.775 | 0.25944 | 9.04 | 8.32 | 8.39 | 4.35 | 74.472 | 301.184 | 354.96 | -17.8549 | 94.1589 | 339.3458 | 98.7181 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Calcium hardness | mg/L as CaCO3 | BMRL | 13 | 64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Calcium hardness | mg/L as CaCO3 | BMRL | 14 | 62 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 11 | 55 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 63 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 0.49
FAX Number |  |  | Temperature at which the MTCW was determined, ToC (oC) | 21.5 |  | the desired operating conditions. |  |  | Fluoride (mg/L) | ND |  | 224 | 1998-12-24 | 16:00 | 5063 | 13.54 | 75.69 | 72.48 | 29.58 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 10.8093 | 2.3488 | 42.1562 | 0.25641 | 9.51 | 8.47 | 8.65 | 5.725 | 74.196 | 289.456 | 251.4151 | 13.1422 | 92.284 | 240.6047 | 97.6206 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Turbidity | ntu | 0.1 | 0.2 | 0.22 | 0.65556 | -197.9798 | 50 | 0.62817 | 84.0807 |  | Turbidity | ntu | 0.07 | 0.09 | 0.12 | 0.25182 | -109.8485 | 22.2222 | 0.24281 | 71.1709 | Turbidity | ntu | 0.09 | 0.11 | 0.12 | 0.17 | -41.6667 | 18.1818 | 0.16453 | 45.2984 | Turbidity | ntu | 0.11 | 0.14 | 0.15 | 0.26 | -73.3333 | 21.4286 | 0.24942 | 55.8975 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  | Maximum flow rate to the element, QI, max (gpm) | 16 |  | 2: The design influent flow rate must be within the range established by the |  |  | Sulfate (mg/L) | 13.2 |  | 225 | 1998-12-25 | 16:00 | 5087 | 13.91 | 75.69 | 72.48 | 30.23 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 11.4192 | 2.4116 | 41.4434 | 0.27554 | 8.35 | 7.84 | 7.94 | 2.52 | 72.822 | 257.944 | 254.7801 | 1.2266 | 96.5395 | 243.6807 | 98.9659 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Ammonia | mg NH3-N / L | BMRL | BMRL | 0.07 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Ammonia | mg NH3-N / L | 0.11 | 0.05 | BMRL | -0.43545 | #VALUE! | -120 | -0.40843 | 126.9324 | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Minimum flow rate to the element, QI, min (gpm) | 4 |  | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  |  | Calcium (mg/L) | 8.4 |  | 226 | 1998-12-26 | 16:00 | 5111 | 13.04 | 75.08 | 72.03 | 30.29 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 11.265 | 2.4053 | 40.8597 | 0.2757 | 5.92 | 7.33 | 7.59 | 1.605 | 71.724 | 229 | 253.2085 | -10.5714 | 97.7623 | 242.1379 | 99.3372 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Total organic carbon | mg/L | BMRL | 2.36 | 9.43 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total organic carbon | mg/L | BMRL | 2.21 | 10.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.3 | 8.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.4 | 8.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | 37th Street WTP |  | Total width of all membrane envelopes in the element, w (ft) | 12.68 |  |  |  |  | Barium (mg/L) | 0.037 |  | 227 | 1998-12-27 | 16:00 | 5135 | 13.58 | 75.99 | 72.94 | 29.49 | 4.29 | 0.44 | 0.11 |  | 0.55 | 4.84 | 0.35295 | 0.8 | 7.8 | 9.0514 | 11.6315 | 3.3531 | 41.6219 | 0.27946 | 9.12 | 8.32 | 8.45 | 3.665 | 73.92 | 268.568 | 354.94 | -32.1602 | 95.0419 | 338.973 | 98.9188 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | UV254 | cm-1 | BMRL | 0.038 | 0.167 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | UV254 | cm-1 | BMRL | 0.04 | 0.168 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.031 | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.031 | 0.135 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Treatment Plant Category | Conventional |  | Feed spacer thickness, T (ft) | 0.0023 |  | Estimate the Osmotic Pressure Gradient |  |  | Strontium (mg/L) | 0.051 |  | 228 | 1998-12-28 | 16:00 | 5159 | 13.64 | 75.54 | 72.79 | 29.07 | 4.39 | 0.44 | 0.06 |  | 0.5 | 4.89 | 0.35677 | 0.88 | 8.78 | 9.0514 | 11.4024 | 5.6643 | 39.4307 | 0.28918 | 9.15 | 8.31 | 8.44 | 4.12 | 75.294 | 275.896 | 597.2367 | -116.4717 | 94.5281 | 570.5525 | 99.2779 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SUVA | L/(mg*m) | NR | 1.6102 | 1.7709 | --- | --- | --- | --- | --- |  | SUVA | L/(mg*m) | NR | 1.81 | 1.6634 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.3478 | 1.6092 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.2917 | 1.5517 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | West |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 |  | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.7 |  | Reactive silica (mg/L as SiO2) | 3.7 |  | 229 | 1998-12-29 | 16:00 | 5183 | 13.27 | 83.78 | 81.18 | 30.84 | 4.39 | 0.49 | 0.11 |  | 0.6 | 4.99 | 0.3625 | 0.81667 | 7.3167 | 10.08 | 12.6702 | 3.6037 | 48.0363 | 0.26376 | 8.86 | 8.12 | 8.24 | 2.52 | 72 | 285.424 | 381.5018 | -33.6614 | 96.5 | 362.8945 | 99.3056 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Bromide | mg/L | BMRL | 29 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | Bromide | mg/L | BMRL | 32 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 33 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 677 |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 |  | Feed TDS, TDSF (mg/L) | 70 |  |  |  |  | 230 | 1998-12-30 | 16:00 | 5207 | 12.71 | 84.24 | 80.73 | 31.02 | 4.39 | 0.49 | 0.17 |  | 0.66 | 5.05 | 0.36708 | 0.74242 | 6.6515 | 10.08 | 12.8439 | 2.5258 | 48.9392 | 0.26245 | 9.02 | 8.23 | 8.41 | 2.52 | 70.896 | 257.944 | 267.9798 | -3.8907 | 96.4455 | 255.101 | 99.0122 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Cl2 dose | mg/L | 2 | 3.99 |  | --- | --- | --- | --- | --- |  | SDS-Cl2 dose | mg/L | 1.73 | 2.58 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | 3.99 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | 3.99 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | VA3710150 |  |  |  |  | Waste TDS, TDSW (mg/L) | 154.99 |  |  |  |  | 231 | 1998-12-31 | 16:00 | 5231 | 11.41 | 83.78 | 80.73 | 29.71 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 11.7742 | 2.3708 | 50.1742 | 0.23467 | 9.07 | 8.37 | 8.46 | 2.06 | 71.172 | 253.552 | 250.0501 | 1.3811 | 97.1056 | 239.1386 | 99.1386 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Free Cl2 residual | mg/L | 1.2 | 1.35 |  | --- | --- | --- | --- | --- |  | SDS-Free Cl2 residual | mg/L | 1.3 | 1.3 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.14 | 1.41 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.23 | 1.29 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 9 |  | Additional Information |  |  | Permeate TDS, TDSp (mg/L) | 41.67 |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  | 232 | 1999-01-01 | 16:00 | 5255 | 11.3 | 83.78 | 79.96 | 29.49 | 4.29 | 0.44 | 0.17 |  | 0.61 | 4.9 | 0.35753 | 0.72131 | 7.0328 | 9.0514 | 12.3571 | 2.2933 | 50.0867 | 0.24671 | 8.43 | 7.93 | 8.07 | 2.06 | 68.976 | 243.656 | 242.1704 | 0.60973 | 97.0135 | 231.3899 | 99.1097 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Cl2 demand | mg/L | 0.8 | 2.64 |  | 11.0222 | --- | 69.697 | 10.5183 | 92.3942 |  | SDS-Cl2 demand | mg/L | 0.43 | 1.28 | --- | 8.1573 | --- | 66.4062 | 7.7744 | 94.469 | SDS-Cl2 demand | mg/L | 0.86 | 2.58 | --- | 7.74 | --- | 66.6667 | 7.2695 | 88.1697 | SDS-Cl2 demand | mg/L | 0.77 | 2.7 | --- | 10.42 | --- | 71.4815 | 9.7393 | 92.0939 | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
Historical Average Water Temperature (oC) | 32 |  | Design cross-flow velocity (fps) | 0.34989 |  | Influent TDS, TDSI (mg/L) | 138.9 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  | 233 | 1999-01-02 | 16:00 | 5279 | 10.97 | 83.93 | 80.73 | 28.52 | 4.29 | 0.44 | 0.11 |  | 0.55 | 4.84 | 0.35295 | 0.8 | 7.8 | 9.0514 | 12.4079 | 3.2766 | 50.5334 | 0.24554 | 8.98 | 8.33 | 8.46 | 2.52 | 71.172 | 260.512 | 345.78 | -32.7309 | 96.4593 | 330.1773 | 99.2368 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Chlorination temp. | oC | 17.3 | 17.3 |  | --- | --- | --- | --- | --- |  | SDS-Chlorination temp. | oC | 14.4 | 13.7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 16.2 | 15.4 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15.7 | 15.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 28 |  | Required influent flow to permeate flow rate ratio, QI:Qp | n/a |  | Osmotic pressure gradient, Dp (psi) | 1.0528 |  |  |  |  | 234 | 1999-01-03 | 16:00 | 5303 | 12.78 | 83.62 | 79.66 | 29.62 | 4.39 | 0.44 | 0.06 |  | 0.5 | 4.89 | 0.35677 | 0.88 | 8.78 | 9.0514 | 12.5621 | 5.3908 | 46.6292 | 0.2694 | 8.96 | 8.28 | 8.39 | 3.435 | 71.172 | 308.144 | 567.91 | -84.3002 | 95.1737 | 542.5144 | 99.3668 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Chlorination pH | --- | 4.21 | 7.07 |  | --- | --- | --- | --- | --- |  | SDS-Chlorination pH | --- | 6.97 | 7.22 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7 | 6.98 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.09 | 6.99 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  |  | Maximum element recovery (%) | n/a | [7 empty] | 235 | 1999-01-04 | 16:00 | 5326 | 12.37 | 86.98 | 83.32 | 31.17 | 4.29 | 0.44 | 0.06 |  | 0.5 | 4.79 | 0.34913 | 0.88 | 8.58 | 9.0514 | 11.7438 | 5.3239 | 48.6561 | 0.24136 | 8.85 | 8.22 | 8.27 | 2.29 | 69.252 | 299.712 | 560.3067 | -86.9484 | 96.6932 | 534.6775 | 99.5717 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-Incubation time | hours | 24 | 24 |  | --- | --- | --- | --- | --- |  | SDS-Incubation time | hours | 24 | 23.9167 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 26.75 | 26.5833 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | ---
|  |  | Variability of design flux (%) | 20 |  | Estimate the Required Influent Pressure | [5 empty] | 236 | 1999-01-05 | 16:00 | 5350 | 12.89 | 87.29 | 83.78 | 31.57 | 4.39 | 0.44 | 0.11 |  | 0.55 | 4.94 | 0.36059 | 0.8 | 7.9818 | 9.0514 | 11.9235 | 3.0567 | 50.9083 | 0.23421 | 9.23 | 8.53 | 8.74 | 3.895 | 67.878 | 267.84 | 323.81 | -20.8968 | 94.2618 | 309.5628 | 98.7418 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TOX | mg Cl- /L | BMRL | 189.3 |  | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-TOX | mg Cl- /L | BMRL | 127.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 133.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 126.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Rejection of reference solute and conditions of test | 99.6 |  | Estimated system pressure losses, DPloss (psi) | 2 |  |  |  |  | 237 | 1999-01-06 | 16:00 | 5374 | 11.59 | 87.29 | 82.56 | 30.74 | 4.29 | 0.44 | 0.11 |  | 0.55 | 4.84 | 0.35295 | 0.8 | 7.8 | 9.0514 | 11.6961 | 3.1891 | 50.9959 | 0.22935 | 7.74 | 7.8 | 7.9 | 1.605 | 68.424 | 242.192 | 335.7 | -38.609 | 97.6543 | 320.5139 | 99.4992 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CHCl3 | mg/L | BMRL | 30.7 |  | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-CHCl31 | mg/L | 1.8 | 33.7 | --- | 291.8 | --- | 94.6588 | 277.4321 | 99.3512 | SDS-CHCl31 | mg/L | 3.3 | 28.2 | --- | 102.9 | --- | 88.2979 | 96.0887 | 96.5657 | SDS-CHCl3 | mg/L | 0.9 | 22.9 | --- | 110.9 | --- | 96.0699 | 103.1407 | 99.1274 | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | (e.g., solute type and concentration) | (mg/L MgSO4) |  | Design permeate pressure, Pp (psi) | 30 |  |  |  |  | 238 | 1999-01-07 | 16:00 | 5398 | 13 | 88.81 | 85 | 31.41 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 12.2744 | 2.3566 | 53.1384 | 0.23099 | 8.43 | 7.92 | 8.09 | 1.375 | 70.074 | 236.328 | 247.8832 | -4.8895 | 98.0378 | 237.0368 | 99.4199 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-BDCM | mg/L | BMRL | 6.7 |  | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-BDCM | mg/L | BMRL | 7.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 2 | 7 | --- | 22 | --- | 71.4286 | 20.6323 | 90.3064 | SDS-BDCM | mg/L | BMRL | 6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Variability of rejection of reference solute (%) | 95 min. |  | Required influent pressure, PI (psi) | 80.8246 |  |  |  |  | 239 | 1999-01-08 | 16:00 | 5420 | 12.5 | 89.12 | 85.61 | 30.93 | 4.39 | 0.49 | 0.11 |  | 0.6 | 4.99 | 0.3625 | 0.81667 | 7.3167 | 10.08 | 12.9724 | 3.4895 | 52.9455 | 0.24501 | 8.61 | 8.1 | 8.2 | 2.52 | 69.798 | 281.76 | 369.4909 | -31.1368 | 96.3896 | 351.4733 | 99.283 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DBCM | mg/L | BMRL | BMRL |  | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-DBCM | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Standard testing recovery (%) | 15 | [7 empty] | 240 | 1999-01-09 | 16:00 | 5444 | 13 | 87.74 | 84.39 | 30.35 | 4.39 | 0.44 | 0.11 |  | 0.55 | 4.94 | 0.36059 | 0.8 | 7.9818 | 9.0514 | 11.8661 | 3.2885 | 52.4265 | 0.22634 | 8.07 | 7.9 | 7.96 | 2.06 | 70.896 | 234.864 | 346.24 | -47.4215 | 97.0943 | 330.9121 | 99.3775 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CHBr3 | mg/L | BMRL | BMRL |  | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Standard testing pH | 8 | [7 empty] | 241 | 1999-01-10 | 16:00 | 5468 | 12.1 | 88.66 | 85.15 | 29.77 | 4.39 | 0.44 | 0.17 |  | 0.61 | 5 | 0.36517 | 0.72131 | 7.1967 | 9.0514 | 11.6487 | 2.4587 | 54.6763 | 0.21305 | 8.82 | 8.24 | 8.41 | 2.52 | 74.196 | 246.224 | 259.7104 | -5.4773 | 96.6036 | 248.394 | 98.9855 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-THM4 | mg/L | 0 | 37.4 | --- | 207.7778 | --- | 100 | 197.5346 | 100 |  | SDS-THM4 | mg/L | 1.8 | 44.6 | --- | 390.8909 | --- | 95.9641 | 371.6136 | 99.5156 | SDS-THM4 | mg/L | 5.3 | 38.4 | --- | 137.7 | --- | 86.1979 | 128.6456 | 95.8802 | SDS-THM4 | mg/L | 0.9 | 31.8 | --- | 155.4 | --- | 97.1698 | 144.5017 | 99.3772 | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Acceptable range of operating pressures | 250 max. | [7 empty] | 242 | 1999-01-11 | 16:00 | 5492 | 11.8 | 81.95 | 77.67 | 25.83 | 4.39 | 0.39 | 0.11 |  | 0.5 | 4.89 | 0.35868 | 0.78 | 8.78 | 8.0229 | 10.675 | 2.7743 | 51.2057 | 0.20847 | 8.58 | 8.07 | 8.21 | 1.83 | 65.4 | 255.016 | 290.7845 | -14.026 | 97.2018 | 279.2618 | 99.3447 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Acceptable range of operating pH values | 3 - 9 | [7 empty] | 243 | 1999-01-12 | 16:00 | 5516 | 12.5 | 89.12 | 85.76 | 30.71 | 4.39 | 0.44 | 0.11 |  | 0.55 | 4.94 | 0.36059 | 0.8 | 7.9818 | 9.0514 | 12.1787 | 3.2687 | 53.4613 | 0.2278 | 8.46 | 7.99 | 8.12 | 2.75 | 71.172 | 260.144 | 344.86 | -32.565 | 96.1361 | 329.6243 | 99.1657 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DCAA* | mg/L | BMRL | 14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 3.2 | 14 | --- | 46.4 | --- | 77.1429 | 43.4457 | 92.6345 | SDS-DCAA* | mg/L | BMRL | 10 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Typical pressure drop across a single element (psi) | 3 - 5 | [7 empty] | 244 | 1999-01-13 | 16:00 | 5540 | 12.8 | 87.44 | 83.32 | 30.53 | 4.29 | 0.44 | 0.11 |  | 0.55 | 4.84 | 0.35295 | 0.8 | 7.8 | 9.0514 | 11.8661 | 3.1564 | 51.6936 | 0.22955 | 7.63 | 7.86 | 7.95 | 0.915 | 67.05 | 241.088 | 331.59 | -37.539 | 98.6353 | 316.5593 | 99.711 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TCAA* | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 15 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Maximum permissible SDI | 5 | [7 empty] | 245 | 1999-01-14 | 11:00 | 5559 | 14 | 92.63 | 88.05 | 31.84 | 4.49 | 0.44 | 0.06 | X | 0.5 | 4.99 | 0.36441 | 0.88 | 8.98 | 9.0514 | 11.7351 | 5.221 | 53.279 | 0.22026 | 8.72 | 8.12 | 8.31 | 2.06 | 67.602 | 257.576 | 548.2433 | -112.8472 | 96.9528 | 524.1631 | 99.607 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 246 | 1999-01-15 | 16:00 | 5566 | 14.47 | 93.09 | 89.58 | 29.4 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36097 | 0.72277 | 4.0396 | 15.0171 | 18.6281 | 2.0396 | 59.8954 | 0.31101 | 5 | 4 | 4.32 | 5.04 | 65.952 | 243.288 | 224.7583 | 7.6164 | 92.3581 | 209.0025 | 97.5885 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 | [7 empty] | 247 | 1999-01-16 | 16:00 | 5590 | 14.76 | 94.46 | 91.71 | 26.96 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 17.0563 | 2.305 | 63.82 | 0.26726 | 5.01 | 4.41 | 4.72 | 3.435 | 65.952 | 245.12 | 250.7849 | -2.3111 | 94.7917 | 233.9314 | 98.5316 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-BCAA* | mg/L | BMRL | 3.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 248 | 1999-01-17 | 16:00 | 5614 | 14.74 | 102.7 | 100.26 | 29.92 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 18.1176 | 2.9576 | 68.6024 | 0.2641 | 4.59 | 3.23 | 3.38 | 6.87 | 83.262 | 342.584 | 325.7236 | 4.9215 | 91.7489 | 302.632 | 97.7299 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 2 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 249 | 1999-01-18 | 16:00 | 5635 | 15.29 | 102.39 | 99.5 | 32.36 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.34875 | 0.76042 | 4.1354 | 15.0171 | 18.1308 | 2.5047 | 66.0803 | 0.27438 | 4.95 | 4.06 | 4.33 | 2.52 | 67.326 | 259.776 | 273.0146 | -5.0962 | 96.257 | 252.9881 | 99.0039 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | 250 | 1999-01-19 | 16:00 | 5659 | 15.2 | 103.16 | 100.26 | 31.48 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.5541 | 2.3253 | 67.9047 | 0.24378 | 4.89 | 3.89 | 4.14 | 4.81 | 67.878 | 273.336 | 254.3399 | 6.9497 | 92.9138 | 237.3379 | 97.9734 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-DCBAA | mg/L | BMRL | 6.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | 3.2 | 5.9 | --- | 14 | --- | 45.7627 | 13.2614 | 75.8699 | SDS-DCBAA | mg/L | BMRL | 5.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
Field 4-5: Pretreatment Used Prior To Membranes1 | [11 empty] | 251 | 1999-01-20 | 16:00 | 5683 | 15.4 | 103.16 | 99.95 | 30.77 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.6084 | 2.1918 | 68.5932 | 0.24213 | 4.99 | 4.64 | 4.92 | 3.205 | 62.652 | 260.144 | 238.4083 | 8.3552 | 94.8844 | 222.3825 | 98.5588 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-HAA5 | mg/L | 0 | 34 | --- | 188.8889 | --- | 100 | 179.5769 | 100 |  | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 3.2 | 31.1 | --- | 114.8 | --- | 89.7106 | 107.168 | 97.014 | SDS-HAA5 | mg/L | 0 | 25 | --- | 125 | --- | 100 | 116.1826 | 100 | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
[12 empty] | 252 | 1999-01-21 | 16:00 | 5706 | 16.05 | 103 | 99.95 | 30.53 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35257 | 0.81111 | 4.5333 | 15.0171 | 17.7005 | 3.6378 | 67.3072 | 0.26298 | 4.44 | 3.24 | 3.37 | 8.015 | 82.164 | 356.144 | 400.5685 | -12.4738 | 90.2451 | 371.797 | 97.8443 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-HAA6 | mg/L | 0 | 37.6 | --- | 208.8889 | --- | 100 | 198.591 | 100 |  | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 3.2 | 34.6 | --- | 128.8 | --- | 90.7514 | 120.2106 | 97.338 | SDS-HAA6 | mg/L | 0 | 27.9 | --- | 139.5 | --- | 100 | 129.6598 | 100 | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
Process | Description | [8 empty] | Scale |  | 253 | 1999-01-22 | 16:00 | 5730 | 15.99 | 103.62 | 101.17 | 29.62 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 16.1044 | 2.3399 | 70.4351 | 0.22864 | 4.85 | 3.85 | 4.02 | 3.205 | 66.774 | 288.36 | 254.7171 | 11.667 | 95.2002 | 237.1937 | 98.6488 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Rapid Mix | Type: | Mechanical | [7 empty] | Full |  | 254 | 1999-01-23 | 16:00 | 5754 | 15.31 | 105.6 | 103 | 30.01 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36288 | 0.74725 | 4.5934 | 13.9886 | 16.1394 | 2.1779 | 72.1121 | 0.22381 | 4.86 | 4.12 | 4.29 | 3.665 | 62.652 | 288.36 | 237.0483 | 17.7943 | 94.1502 | 221.4589 | 98.3451 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
| Chemical Name: | Alum |  |  |  | Powdered Activated Carbon (PAC) | [5 empty] | 255 | 1999-01-24 | 16:00 | 5778 | 14.41 | 106.06 | 103.62 | 29.28 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 17.7584 | 2.3619 | 73.1981 | 0.24261 | 4.8 | 3.85 | 4.07 | 2.75 | 63.756 | 276.632 | 257.3837 | 6.9581 | 95.6867 | 238.943 | 98.8491 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [11 empty] | 1Analyzed out of holding time. | [9 empty] | 1Analyzed out of holding time.
| Chemical Formula: | Al2(SO4)3*14H2O | [9 empty] | 256 | 1999-01-25 | 16:00 | 5802 | 14.66 | 106.36 | 103.62 | 30.1 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 18.3506 | 2.4576 | 72.4324 | 0.25335 | 4.76 | 3.76 | 3.91 | 2.75 | 66.228 | 295.688 | 267.7017 | 9.4648 | 95.8477 | 248.5137 | 98.8934 | [16 empty] | Blending Calculations For D-DBP MCLs | [10 empty] | 21/5/99 HAA bottles broke in shipment. | [19 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
| Dose: | AVG | MAX | MIN | STD DEV | AVG | MAX | MIN | STD DEV |  |  | 257 | 1999-01-26 | 16:00 | 5826 | 16.3 | 105.75 | 104.07 | 29.95 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 16.9383 | 2.8059 | 72.1541 | 0.23475 | 4.82 | 4.24 | 4.44 | 3.205 | 63.48 | 283.96 | 304.58 | -7.2616 | 94.9512 | 283.7955 | 98.8707 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [15 empty] | Blending Calculations For D-DBP MCLs | [10 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
|  | 30.1 | 49.7 | 20.6 | 7.15 | 2.36 | 6.47 | 0 | 1.36 |  |  | 258 | 1999-01-27 | 16:00 | 5850 | 15.5 | 106.21 | 104.53 | 29.8 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 15.9597 | 2.3117 | 73.2583 | 0.21785 | 4.81 | 3.96 | 4.18 | 2.975 | 65.676 | 291.288 | 251.0529 | 13.8128 | 95.4702 | 234.1498 | 98.7294 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Blending Calculations For D-DBP MCLs | [10 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
Flocculation | Type: | Mechanical | [7 empty] | Full |  | 259 | 1999-01-28 | 16:00 | 5870 | 16.08 | 104.53 | 102.39 | 32.18 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.35715 | 0.76042 | 4.25 | 15.0171 | 17.6364 | 2.6243 | 68.6557 | 0.25688 | 4.6 | 3.39 | 3.56 | 5.04 | 72.822 | 326.464 | 287.9562 | 11.7954 | 93.079 | 267.4672 | 98.1157 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Qp/QT (THM4), % | -92.5134 | 3.7433 |  | Qp/QT (HAA5), % | -58.8235 | 20.5882 | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Qp/QT (THM4), % | -130.0971 | -13.5922 |  | Qp/QT (HAA5), % | -116 | -8 |  |  |  | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
Sedimentation | Type: | Conventional | [7 empty] | Full |  | 260 | 1999-01-29 | 16:00 | 5894 | 16.08 | 104.07 | 101.17 | 31.99 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.087 | 2.104 | 68.526 | 0.23476 | 4.84 | 4.03 | 4.25 | 3.665 | 60.732 | 286.16 | 229.4518 | 19.8169 | 93.9653 | 214.0676 | 98.2879 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 29.7 | [5 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Qp/QT (THM4), % | -101.5106 | 7.2508 |  | Qp/QT (HAA5), % | -82.0789 | 14.6953 |  |  |  | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
Filtration | Type: | Dual Media - Anthracite/Sand | [7 empty] | Pilot |  | 261 | 1999-01-30 | 16:00 | 5918 | 16.08 | 104.68 | 101.78 | 31.14 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 16.087 | 2.2373 | 69.8527 | 0.2303 | 4.8 | 3.93 | 4.13 | 3.895 | 64.578 | 276.264 | 243.9886 | 11.6828 | 93.9685 | 227.6295 | 98.2889 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-HAA5b, mg/L | NA | 32.7273 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  |  | Qp/QT (THM4), % | -64.0187 | 20.0935 |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 33.5358 |  |  |  | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
[12 empty] | 262 | 1999-01-31 | 16:00 | 5942 | 16.08 | 104.23 | 101.78 | 30.01 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 14.9041 | 2.102 | 70.893 | 0.21023 | 4.85 | 4.21 | 4.44 | 3.435 | 63.48 | 248.784 | 227.9511 | 8.3739 | 94.5888 | 213.6348 | 98.3921 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | NA | 29.077 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [11 empty] | 263 | 1999-02-01 | 16:00 | 5966 | 16.08 | 104.84 | 101.78 | 30.1 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35333 | 0.73256 | 4.7442 | 12.96 | 14.9041 | 2.1918 | 71.0182 | 0.20986 | 4.81 | 4.03 | 4.23 | 2.52 | 65.13 | 280.664 | 236.627 | 15.6903 | 96.1308 | 221.6991 | 98.8633 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | SDS-CDb, mg/L | NA | 2.5711 |  | SDS-CDb, mg/L | NA | 2.2612 |  |  |  |  | SDS-HAA5b, mg/L | NA | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [11 empty] | 264 | 1999-02-02 | 16:00 | 5990 | 16.76 | 105.14 | 101.94 | 29.92 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 16.087 | 2.2337 | 71.3863 | 0.22535 | 4.89 | 4.27 | 4.47 | 3.895 | 64.578 | 286.888 | 243.9886 | 14.9534 | 93.9685 | 227.2608 | 98.2861 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | NA | 2.4553 |  | SDS-CDb, mg/L | NA | 2.3272 |  |  |  | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
is to list the pretreatment processes used in this particular Long-Term SEBST run. | [11 empty] | 265 | 1999-02-03 | 16:00 | 6011 | 16.59 | 104.68 | 102.09 | 30.84 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 15.6974 | 2.259 | 70.286 | 0.22334 | 4.77 | 3.83 | 3.99 | 4.58 | 65.952 | 281.392 | 247.3997 | 12.0801 | 93.0556 | 230.4819 | 98.0129 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  |  | SDS-CDb, mg/L | NA | 1.1092 |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
[12 empty] | 266 | 1999-02-04 | 16:00 | 6035 | 15.92 | 104.53 | 101.94 | 30.19 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 15.7937 | 2.1903 | 70.8547 | 0.2229 | 4.79 | 3.82 | 3.98 | 4.35 | 63.756 | 284.328 | 239.3911 | 15.8046 | 93.1771 | 223.3763 | 98.0526 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
[12 empty] | 267 | 1999-02-05 | 16:00 | 6059 | 17.21 | 104.23 | 102.39 | 31.2 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 16.1803 | 1.9534 | 70.1566 | 0.23063 | 4.84 | 4.05 | 4.25 | 3.205 | 64.302 | 255.384 | 212.6804 | 16.7213 | 95.0157 | 198.5491 | 98.3858 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Alkb, mg/L CaCO3 | NA | 17.4759 |  | Alkb, mg/L CaCO3 | NA | 15.1176 |  |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
[12 empty] | 268 | 1999-02-06 | 16:00 | 6083 | 16.74 | 103 | 101.02 | 29.74 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.35906 | 0.70833 | 4.25 | 13.9886 | 15.4457 | 2.0852 | 70.1848 | 0.22007 | 4.62 | 3.51 | 3.64 | 4.58 | 69.798 | 305.208 | 228.1846 | 25.2364 | 93.4382 | 213.1001 | 97.8508 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | T-Hdb, mg/L CaCO3 | NA | 28.9893 |  | T-Hdb, mg/L CaCO3 | NA | 24.4412 |  |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | 2 |  | Alkb, mg/L CaCO3 | NA | 2 |  |  |  | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
[12 empty] | 269 | 1999-02-07 | 16:00 | 6107 | 16.37 | 105.14 | 102.39 | 30.35 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.35524 | 0.74725 | 4.4835 | 13.9886 | 15.7086 | 2.2223 | 71.1927 | 0.22065 | 4.81 | 4.02 | 4.18 | 3.205 | 63.48 | 282.496 | 241.6843 | 14.4468 | 94.9512 | 225.4353 | 98.5783 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  |  | Alkb, mg/L CaCO3 | NA | 12.1869 |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | NA | 25.1148 |  | T-Hdb, mg/L CaCO3 | NA | 23.1792 |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
[12 empty] | 270 | 1999-02-08 | 16:00 | 6132 | 16.42 | 104.99 | 101.63 | 30.13 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35066 | 0.8 | 4.8 | 13.9886 | 15.9194 | 3.0339 | 70.1461 | 0.22695 | 4.78 | 3.83 | 3.97 | 4.35 | 69.522 | 300.816 | 330.21 | -9.7714 | 93.743 | 307.7369 | 98.5865 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Notes: | [10 empty] | T-Hdb, mg/L CaCO3 | NA | 22.5748 |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[12 empty] | 271 | 1999-02-09 | 9:00 | 6148 | 15.7 | 105.29 | 102.85 | 28.97 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.34684 | 0.74725 | 4.3626 | 13.9886 | 15.8907 | 2.2203 | 72.8797 | 0.21804 | 4.82 | 4.14 | 4.3 | 3.435 | 63.756 | 275.168 | 242.0963 | 12.0187 | 94.6123 | 225.4683 | 98.4765 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [10 empty] | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Notes: | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[12 empty] | 272 | [32 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [10 empty] | Notes: | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[12 empty] | 273 | [32 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [10 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[12 empty] | 274 | [32 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[12 empty] | 275 | [48 empty] | The maximum (Qp/QT) ratio controls the design. | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[12 empty] | 276 | [48 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[12 empty] | 277 | [48 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[12 empty] | 278 | [48 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[12 empty] | 279 | [48 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[12 empty] | 280 | [48 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[72 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on K13: C. Rice: Consultant verified the decrease in aluminum concentration from the raw to the filtered water; no explanation was given.
Note on K14: C. Rice: The "Pilot Filtered" sulfate is higher than the raw water concentration because aluminum sulfate was added for coagulation.
Note on AS5: TSC_ADM: Operational TDS data is based on an empirical factor applied to the on-line conductivity measurements (compared to the biweekly TDS data, which are based on lab measurements); therefore, there may be discrepancies between the operational and biweekly TDS data.
Note on BN17: C. Rice: Consultant verified the TDS and total hardness data for week 32; no explanations provided for the high MB closure errors.
Note on BN18: C. Rice: Consultant verified the TDS and total hardness data for week 34; no explanations provided for the high MB closure errors.
Note on BP30: C. Rice: Consultant verified value; no explanation given.
Note on BY16: C. Rice: Consultant verified the alkalinity, total hardness, and TDS data for week 34; no explanations were provided for the high MB closure errors.
Note on BY17: C. Rice: Consultant verified the alkalinity, total hardness, and TDS data for week 34; no explanations were provided for the high MB closure errors.
Note on BY18: C. Rice: Consultant verified the alkalinity, total hardness and TDS data for week 34; no explanations provided for the high MB closure errors.
Note on BY38: C. Rice: HAAs are reported as "NA" due to bottle breakage during shipment.
Note on CB26: C. Rice: Consultant verified value; no explanation given.
Note on CB28: C. Rice: Consultant verified value; no explanation given.
Note on CJ16: TSC_ADM: Consultant verified low alkalinities, which are probably due to low pH of these samples
Note on CU16: C. Rice: Consultant verified the feed and concentrate alkalinity values for week 38 - these are probably due to low pH of these samples
Note on CU18: C. Rice: Consultant verified the total hardness data for week 38; no explanation provided for the high MB closure error.

## LFC1. Events
Date | Time | Runtime (hrs) | Description | event plot
| 0 | 1328 |  | 0 | 0
1999-04-06 | 930 | 1328 | Cleaned membrane with NaOH. Stopped acid addition to feedwater | 0.25 | 5
(was running at pH 4; now running at pH 6)
1027.4?

## LFC1. Bi-weekly
[17 empty] | c |  |  | c |  |  | c |  |  |  |  | c
DATE | TIME | [29 empty] | MANGANESE (mg/L) | [11 empty] | ALUMINUM (mg/L) | [11 empty] | SDS
|  | RUN | pH |  |  | Temperature |  |  | ALKALINITY (mg/L as CaCO3) |  |  | DISSOLVED OXYGEN (mg/L) |  |  | CALCIUM HARDNESS (mg/L as CaCO3) |  |  | TOTAL HARDNESS (mg/L as CaCO3) |  |  | TURBIDITY (ntu) |  |  | TOC (mg/L) |  |  |  | UV254 (cm-1) |  |  | Total | [5 empty] | Dissolved | [5 empty] | Total | [6 empty] | Dissolved |  |  |  |  | Chlorine Dose (mg/L) |  | Free Chlorine Residual (mg/L) |  | Chlorine Demand (mg/L) |  | Chlorination Temperature |  |  |  | Chlorination pH |  | Incubation Time (hrs) |  |  | SDS-TOX (6) (ug/L) |  | SDS-THM4 (ug/L) |  | SDS-HAA5 (ug/L) |  | SDS-HAA6 (ug/L) |  |  |  | BROMIDE (mg/L) | [5 empty] | AMMONIA (mg/L) |  |  | ORTHO PHOSPHOROUS (mg/L) | [5 empty] | TOTAL PHOSPHOROUS (mg/L) |  |  |  |  | BARIUM (mg/L) |  |  | SULFATE (mg/L)
|  | TIME (hrs) | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate |  | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate |  | Permeate |  | Feed |  | Concentrate |  | Permeate |  | Feed |  | Concentrate |  | Raw |  | Permeate |  | Feed | Concentrate |  | Permeate |  | Feed | Concentrate | Permeate | Feed | Permeate | Feed | Permeate | Feed | Permeate (deg F) | Permeate (deg C) | Feed (deg F) | Feed (deg C) | Permeate | Feed | Permeate | Feed |  | Permeate | Feed | Permeate | Feed | Permeate | Feed | Permeate | Feed |  | Permeate |  | Feed | Concentrate |  | Permeate |  | Feed |  | Concentrate |  | Raw Feed |  | Treated Feed |  | Concentrate |  | Raw Feed |  | Treated Feed | Concentrate | Raw Feed |  | Permeate | Raw Feed |  | Permeate
1999 | [99 empty] | 0.025 | < | 0.005 | 21.63 | < | 5
1999-02-16 | 910 |  | 5.35 | 5.69 | 3.99 | 16.8 | 13.6 | 16.2 | 1 | 3 | 0 | 8.68 | 8.9 |  | 0 | 15 | 59 | 1 | 26 | 104 | 0.06 | 0.09 | 0.16 | < | 0.05 | 2.44 | 9.46 | 0.002 | 0.039 | 0.154 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 |  |  |  | 0.093 |  | 0.125 | 0.256 |  | 0.062 |  | 0.121 | 0.235 | 1.86 | 3.72 | 1.3 | 1.32 | 0.56 | 2.4 |  | 15.6 |  | 15.2 | 7.09 | 6.98 | 23.6667 | 23.4167 | < | 25 | 113.3 | 1 | 37.8 | 0 | 28 | 0 | 31.1 | < | 0.02 |  | 0.02 |  | < | 0.05 | < | 0.05 | < | 0.05 | [6 empty] | < | 0.04 | < | 0.04 | 0.116
|  |  | 5.32 | 5.64 |  | 16.5 | 13.3 |  | 1 | 3 |  | 9.08 | 8.97 |  | 0 | 15 |  | 1 | 26 |  | 0.06 | 0.11 |  | < | 0.05 | 2.5 |  | 0.002 | 0.039 |  | < | 0.014 | < | 0.014 |  |  | < | 0.014 | < | 0.014 |  |  |  | 0.229 |  | 0.091 |  | 0.13 |  |  | 0.075 |  | 0.115 |  | 1.86 | 3.72 | 1.16 | 1.35 | 0.7 | 2.37 |  | 16 |  | 15.4 | 7 | 7.02 |  |  | < | 25 | 120.8 | 0.9 | 36.2 | 0 | 30 | 0 | 33.2 | < | 0.02 |  | 0.03 |  | < | 0.05 | < | 0.05
1999-03-09 | 950 |  | 5.49 | 5.32 | 4.6 | 15.5 | 13.1 | 15.6 | 1 | 1 | 0 |  |  |  | 0 | 14 | 53 | 1 | 27 | 94 | 0.08 | 0.1 | 0.23 | < | 0.5 | 2.47 | 8.52 | 0 | 0.036 | 0.136 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 |  | 0.123 |  | 0.086 |  | 0.164 | 0.341 |  | 0.076 |  | 0.132 | 0.329 | 1.6 | 3.2 | 1.32 | 1.52 | 0.28 | 1.68 |  | 14.7 |  | 14.8 | 6.91 | 6.95 | 24.0833 | 23.8333 | < | 25 | 121.1 | 2.9 | 36.4 | 0 | 25.3 | 0 | 28.3 | < | 0.02 |  | 0.03 |  | < | 0.05 | < | 0.05 | < | 0.05
1999-03-16 | 900 |  | 5.63 | 4.97 | 4.68 | 14.8 | 12.5 | 15.1 | 1 | 1 | 0 | 10.43 | 10.99 | 10.6 | 0 | 15 | 58 | 1 | 27 | 91 | 0.1 | 0.13 | 0.27 | < | 0.05 | 2.39 | 8.23 | 0 | 0.033 | 0.129 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 | < | 0.014 |  | 0.165 |  | 0.082 |  | 0.13 | 0.288 |  | 0.084 |  | 0.132 | 0.266 | 1.67 | 3.33 | 1.26 | 1.37 | 0.41 | 1.96 |  | 15.6 |  | 15.7 | 7.01 | 6.94 | 24.25 | 24.0833 | < | 25 | 139.5 | 2.6 | 38.3 | 0 | 25.4 | 0 | 28 | < | 0.02 |  | 0.03 |  | < | 0.05 | < | 0.05 |  | 0.23 | [11 empty] | 0.025 | < | 0.005 | 21.69 | < | 17.98
1999-04-01 | 925 |  | 5.62 | 6.03 | 4.63 | 17.2222 | 15.2 | 17.5 | 3 | 4 | 0 |  |  |  | 0 | 15 | 67 | 2 | 33 | 106 | 0.16 | 0.13 | 0.21 | < | 0.5 | 2.65 | 9.89 | 0.002 | 0.034 | 0.155 | [24 empty] | 1.73 | 3.45 | 1.3 | 1.27 | 0.43 | 2.18 |  | 17.8 |  | 17.7 | 7.06 | 6.99 | 24.0833 | 24 | < | 25 | 150.9 | 2.9 | 46 | 0 | 31 | 0 | 34.1 | [5 empty] | < | 0.05 | < | 0.05 | < | 0.05
1999-04-06 | 905 |  | 6.01 | 6.07 | 6.67 |  |  |  | 2 | 7 | 24 |  |  |  | 0 | 15 | 62 |  |  |  | 0.08 | 0.14 | 0.38 | < | 0.5 | 2.48 | 9.75 |  |  |  | < | 0.014 | < | 0.014 |  | 0.054 | < | 0.014 | < | 0.014 |  | 0.053 |  | 0.12 | < | 0.05 |  | 0.08 | 0.26 | < | 0.05 | < | 0.05 | 0.238 | [34 empty] | < | 0.02 | < | 0.02 | < | 0.02 | < | 0.04 | < | 0.04 | 0.219 | 0.032 | < | 0.005 | 22.64 | < | 5
1999-04-13 | 910 |  | 5.93 | 6.6 | 6.67 |  |  |  | 2 | 10 | 29 |  |  |  | 0 | 15 | 71 |  |  |  | 0.1 | 0.16 | 0.21 | < | 0.5 | 2.59 | 10.26 |  |  |  | < | 0.014 |  | 0.028 |  | 0.113 | < | 0.014 |  | 0.025 |  | 0.109 |  | 0.089 | < | 0.05 | < | 0.05 | 0.155 | < | 0.05 | < | 0.05 | 0.16 | [34 empty] | < | 0.02 | < | 0.02 | < | 0.02 | < | 0.04 | < | 0.04 | 0.229 | 0.032 | < | 0.005 | 21.49 | < | 5
1999-04-20 | 820 |  | 5.92 | 6.14 | 6.51 |  |  |  | 3 | 6 | 19 |  |  |  | 0 | 15 | 61 |  |  |  | 0.1 | 0.14 | 0.18 | < | 0.5 | 2.74 | 8.48 |  |  |  | < | 0.014 | < | 0.014 |  | 0.022 | < | 0.014 | < | 0.014 |  | 0.021 |  | 0.175 |  | 0.063 |  | 0.142 | 0.306 |  | 0.078 |  | 0.094 | 0.246 | [34 empty] | < | 0.02 | < | 0.02 | < | 0.02 | < | 0.04 | < | 0.04 |  | 0.03 | < | 0.005 | 23.04 | < | 5
1999-04-28 | 900 |  | 5.81 | 6.14 | 6.54 |  |  |  | 2 | 8 | 22 |  |  |  | 0 | 16 | 59 |  |  |  | 0.1 | 0.13 | 0.02 | [65 empty] | < | 0.02 | < | 0.02 | < | 0.02 | < | 0.04 | < | 0.04 | 0.211 |  |  |  | 22.64 |  | 5
1999-05-04 | 1000 |  | 5.9 | 6.31 | 6.57 |  |  |  | 2 | 8 | 24 |  |  |  | 0 | 16 | 56 |  |  |  | 0.11 | 0.12 | 0.16 | [71 empty] | < | 0.04 | < | 0.04 | 0.198
AVERAGE |  |  | 5.698 | 5.891 | 5.6511 | 16.1644 | 13.54 | 16.1 | 1.8 | 5.1 | 13.1111 | 9.3967 | 9.62 | 10.6 | 0 | 15.1 | 60.6667 | 1.2 | 27.8 | 98.75 | 0.095 | 0.125 | 0.20222 |  | 0.33125 | 2.5325 | 9.2271 | 0.0012 | 0.0362 | 0.1435 |  | 0.014 |  | 0.016 |  | 0.0385 |  | 0.014 |  | 0.015571 |  | 0.0375 |  | 0.15017 |  | 0.073571 |  | 0.11729 | 0.26767 |  | 0.067857 |  | 0.099143 | 0.24567 | 1.744 | 3.484 | 1.268 | 1.366 | 0.476 | 2.118 |  | 15.94 |  | 15.76 | 7.014 | 6.976 | 24.0208 | 23.8333 |  | 25 | 129.12 | 2.06 | 38.94 | 0 | 27.94 | 0 | 30.94 |  | 0.02 |  | 0.0275 |  |  | 0.05 |  | 0.05 |  | 0.095 |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.04 |  | 0.04 | 0.1946 | 0.02975 |  | 0.005 | 22.3 |  | 7.596
MAXIMUM |  |  | 6.01 | 6.6 | 6.67 | 17.2222 | 15.2 | 17.5 | 3 | 10 | 29 | 10.43 | 10.99 | 10.6 | 0 | 16 | 71 | 2 | 33 | 106 | 0.16 | 0.16 | 0.38 |  | 0.5 | 2.74 | 10.26 | 0.002 | 0.039 | 0.155 |  | 0.014 |  | 0.028 |  | 0.113 |  | 0.014 |  | 0.025 |  | 0.109 |  | 0.229 |  | 0.093 |  | 0.164 | 0.341 |  | 0.084 |  | 0.132 | 0.329 | 1.86 | 3.72 | 1.32 | 1.52 | 0.7 | 2.4 |  | 17.8 |  | 17.7 | 7.09 | 7.02 | 24.25 | 24.0833 |  | 25 | 150.9 | 2.9 | 46 | 0 | 31 | 0 | 34.1 |  | 0.02 |  | 0.03 |  |  | 0.05 |  | 0.05 |  | 0.23 |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.04 |  | 0.04 | 0.229 | 0.032 |  | 0.005 | 23.04 |  | 17.98
MINIMUM |  |  | 5.32 | 4.97 | 3.99 | 14.8 | 12.5 | 15.1 | 1 | 1 | 0 | 8.68 | 8.9 | 10.6 | 0 | 14 | 53 | 1 | 26 | 91 | 0.06 | 0.09 | 0.02 |  | 0.05 | 2.39 | 8.23 | 0 | 0.033 | 0.129 |  | 0.014 |  | 0.014 |  | 0.014 |  | 0.014 |  | 0.014 |  | 0.014 |  | 0.089 |  | 0.05 |  | 0.05 | 0.155 |  | 0.05 |  | 0.05 | 0.16 | 1.6 | 3.2 | 1.16 | 1.27 | 0.28 | 1.68 |  | 14.7 |  | 14.8 | 6.91 | 6.94 | 23.6667 | 23.4167 |  | 25 | 113.3 | 0.9 | 36.2 | 0 | 25.3 | 0 | 28 |  | 0.02 |  | 0.02 |  |  | 0.05 |  | 0.05 |  | 0.05 |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.04 |  | 0.04 | 0.116 | 0.025 |  | 0.005 | 21.49 |  | 5
STD. DEV. |  |  | 0.25205 | 0.48663 | 1.1346 | 0.9923 | 1.0114 | 1.036 | 0.78881 | 3.1429 | 12.7028 | 0.91697 | 1.187 | #DIV/0! | 0 | 0.56765 | 5.5 | 0.44721 | 2.9496 | 7.3655 | 0.028771 | 0.020683 | 0.096408 |  | 0.2329 | 0.11756 | 0.80481 | 0.0010954 | 0.0027749 | 0.013026 |  | 0 |  | 0.0052915 |  | 0.039657 |  | 0 |  | 0.0041576 |  | 0.038161 |  | 0.049882 |  | 0.01884 |  | 0.03893 | 0.063481 |  | 0.013862 |  | 0.035928 | 0.054533 | 0.11546 | 0.23287 | 0.064187 | 0.093968 | 0.15978 | 0.30153 |  | 1.1437 |  | 1.1327 | 0.068775 | 0.032094 | 0.24884 | 0.29659 |  | 0 | 15.5397 | 1.0213 | 4.047 | 0 | 2.5996 | 0 | 2.7718 |  | 0 |  | 0.005 |  |  | 6.5854e-10 |  | 6.5854e-10 |  | 0.09 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0.04538 | 0.003304 |  | 0 | 0.67212 |  | 5.8048
6.0521

## LFC1. Weekly
City of Norfolk, VA
ICR SEBST
LEGEND
|  | Feed: | Treated Feed (post SI & CF) from 5/15 to 6/8
Raw Feed (pre-SI & CF) from 6/9 on
|  | Influent: | RO Feed
SEMI-WEEKLY DATA:
FROM DATA LOGGER: | [15 empty] | CALCULATED VALUES: | [11 empty] | DATE | TIME | SDI |  |  |  | HPC | [8 empty] | TDS (mg/L) |  |  | Conductivity (uS/cm) |  |  | Ratio of TDS/Conductivity |  |  | % SALT REJECTION
DATE | TIME | RUN TIME | CONDUCTIVITY |  |  | TEMP | PRESSURE |  |  | pH |  |  | FLOW | [10 empty] | TDS (based on Conductivity) where TDS: | [5 empty] | Raw Feed |  | Treated Feed |  | Permeate |  | Raw Feed |  | Influent (RO Feed) |  | Settled Water |  | Concentrate | Permeate | Raw Feed | Concentrate | Permeate | Feed | Concentrate | Permeate | Feed | Concentrate | (based on Measured TDS)
|  |  | REJECT | FEED | PERMEATE | PERMEATE | FEED | REJECT | PERMEATE | FEED | PERMEATE | REJECT | PERMEATE | REJECT | RECYCLE | RECOVERY | DIFFERENTIAL PRESSURE | 150% of DP24 | NET DRIVING PRESSURE (NDP) (psi) | NORMALIZED PERMEATE FLOW (NPF) (gpm) | 80% of NPF | 80% of MTCw AT 20 DEG C | TEMPERATURE CORRECTION FACTOR (TCF) AT 20 DEG C | (= Cond. X 0.5) Permeate | (= Cond. X 0.6) Feed | (= Cond. X 0.8) Reject | % SALT REJECTION |  |  | Result | to | Result | to | Count | Dilution | Count | Dilution | Count | Dilution | Count | Dilution | Count | Dilution
|  | 0 | [15 empty] | 3.21 |  | 45.7 |  | 0.082896
1999-09-02 | 16:00:00pm | 6 | 321.52 | 101.68 | 1.83 | 17.35 | 164.35 | 162.21 | 29.83 | 4.42 | 4.49 | 4.48 | 0.73 | 0.23 | 4.08 | 76.04% | 2.14 | 3.21 | 133.45 | #REF! | #REF! | 0.082896 | 1.0986 | 0.915 | 61.008 | 257.216 | 99.4249 | 1999-09-02 | 930 | 3.5 | 35.3 | 2.2 | 35.3 | 5 |  | 250 |  | 1950 |  | 24100 |  | 1250 | 3 | 30 | 130 | 5.95 | 103.05 | 339.38 | 0.5042 | 0.29112 | 0.38305 | 96.25
1999-10-02 | 16:00:00pm | 30 | 321.06 | 101.22 | 2.75 | 17.5 | 163.43 | 162.67 | 30.1 | 4.11 | 4.62 | 4.28 | 0.68 | 0.23 | 4.08 | 74.73% | 0.76 | 3.21 | 132.95 | #REF! | #REF! | 0.082896 | 1.0928 | 1.375 | 60.732 | 256.848 | 99.1341 | 1999-10-02
1999-11-02 | 16:00:00pm | 54 | 335.26 | 102.13 | 1.37 | 17.26 | 163.43 | 163.13 | 30.38 | 4.11 | 4.64 | 4.23 | 0.73 | 0.23 | 4.08 | 76.04% | 0.3 | 3.21 | 132.9 | #REF! | #REF! | 0.082896 | 1.1022 | 0.685 | 61.278 | 268.208 | 99.5842 | 1999-11-02 | 755 |  | FP | 3 | 34.9 | 10 |  | 100 |  | 1850 |  | 1050 |  | 100 | 5 | 69 | 227 | 5.04 | 103.05 | 328.84
1999-12-02 | 16:00:00pm | 78 | 349.91 | 100.3 | 2.75 | 17.14 | 163.59 | 161.91 | 30.29 | 4.21 | 4.67 | 4.32 | 0.73 | 0.23 | 4.08 | 76.04% | 1.68 | 3.21 | 132.46 | #REF! | #REF! | 0.082896 | 1.1069 | 1.375 | 60.18 | 279.928 | 99.1914 | 1999-12-02
13/2/99 | 16:00:00pm | 102 | 352.2 | 99.39 | 5.04 | 17.4 | 162.82 | 161.3 | 29.95 | 3.93 | 4.65 | 4 | 0.73 | 0.17 | 4.08 | 81.11% | 1.52 | 3.21 | 132.11 | #REF! | #REF! | 0.082896 | 1.0967 | 2.52 | 59.634 | 281.76 | 98.5237 | 13/2/99
14/2/99 | 16:00:00pm | 123 | 419.07 | 125.03 | 7.33 | 17.01 | 163.74 | 161.76 | 32.21 | 3.29 | 4.29 | 3.27 | 0.68 | 0.28 | 4.08 | 70.83% | 1.98 | 3.21 | 130.54 | #REF! | #REF! | 0.082896 | 1.1121 | 3.665 | 75.018 | 335.256 | 98.2134 | 14/2/99
15/2/99 | 15:00:00pm | 146 | 349 | 99.84 | 4.12 | 17.34 | 163.59 | 161.15 | 31.57 | 4 | 4.68 | 4.12 | 0.73 | 0.17 | 4.08 | 81.11% | 2.44 | 3.21 | 130.8 | #REF! | #REF! | 0.082896 | 1.099 | 2.06 | 59.904 | 279.2 | 98.785 | 15/2/99
16/2/99 | 16:00:00pm | 170 | 349.91 | 103.05 | 5.04 | 17.52 | 162.98 | 159.01 | 32.06 | 3.89 | 4.67 | 3.99 | 0.68 | 0.23 | 4.08 | 74.73% | 3.97 | 3.21 | 128.935 | #REF! | #REF! | 0.082896 | 1.092 | 2.52 | 61.83 | 279.928 | 98.5253 | 16/2/99 | 830 | 4.2 | 41.3 | 3.3 | 36 | 255 |  | 20 |  | 2000 |  | 100 |  | 3850 | 3 | 75 | 246 | 5.04 | 108.55 | 355.87 | 0.59524 | 0.69093 | 0.69126 | 98.1308
17/2/99 | 16:00:00pm | 194 | 308.23 | 100.3 | 2.75 | 17.12 | 163.43 | 161.6 | 32.27 | 4 | 4.63 | 4.1 | 0.73 | 0.28 | 4.08 | 72.28% | 1.83 | 3.21 | 130.245 | #REF! | #REF! | 0.082896 | 1.1077 | 1.375 | 60.18 | 246.584 | 99.1035 | 17/2/99
18/2/99 | 16:00:00pm | 218 | 325.64 | 104.88 | 5.04 | 16.82 | 163.43 | 161.76 | 31.84 | 3.99 | 4.69 | 4.09 | 0.68 | 0.23 | 4.08 | 74.73% | 1.67 | 3.21 | 130.755 | #REF! | #REF! | 0.082896 | 1.1197 | 2.52 | 62.928 | 260.512 | 98.4418 | 18/2/99 |  | 1.3 | 57.3 | 2.2 | 62.2 | 80 |  | 245 |  | 3600 |  | 39700 |  | 12350 | 0 | 60 | 255 | 4.12 | 92.52 | 317.39 |  | 0.64851 | 0.80343
19/2/99 | 16:00:00pm | 238 | 325.64 | 97.55 | 5.95 | 17.08 | 164.96 | 164.81 | 30.38 | 4.05 | 4.6 | 4.16 | 0.78 | 0.23 | 3.97 | 77.23% | 0.15 | 3.21 | 134.505 | #REF! | #REF! | 0.082896 | 1.1093 | 2.975 | 58.53 | 260.512 | 98.135 | 19/2/99
20/2/99 | 16:00:00pm | 262 | 298.62 | 102.59 | 2.75 | 16.92 | 163.74 | 161.45 | 29.37 | 4.17 | 4.61 | 4.31 | 0.73 | 0.23 | 4.08 | 76.04% | 2.29 | 3.21 | 133.225 | #REF! | #REF! | 0.082896 | 1.1157 | 1.375 | 61.554 | 238.896 | 99.0847 | 20/2/99
21/2/99 | 16:00:00pm | 285 | 315.56 | 101.22 | 3.21 | 16.77 | 163.89 | 161.76 | 28.88 | 3.91 | 4.6 | 4.03 | 0.73 | 0.28 | 4.08 | 72.28% | 2.13 | 3.21 | 133.945 | #REF! | #REF! | 0.082896 | 1.1218 | 1.605 | 60.732 | 252.448 | 98.975 | 21/2/99
22/2/99 | 16:00:00pm | 309 | 320.14 | 99.84 | 2.75 | 16.44 | 164.04 | 161.45 | 28.61 | 3.9 | 4.6 | 3.96 | 0.73 | 0.23 | 4.08 | 76.04% | 2.59 | 3.21 | 134.135 | #REF! | #REF! | 0.082896 | 1.1352 | 1.375 | 59.904 | 256.112 | 99.1298 | 22/2/99
23/2/99 | 16:00:00pm | 333 | 318.77 | 105.8 | 5.5 | 15.58 | 164.5 | 162.82 | 30.65 | 3.89 | 4.65 | 4 | 0.68 | 0.23 | 3.97 | 74.73% | 1.68 | 3.21 | 133.01 | #REF! | #REF! | 0.082896 | 1.171 | 2.75 | 63.48 | 255.016 | 98.2731 | 23/2/99 | 635 | 2.5 | 52.5 | 2.7 | 37.7 | 1345 |  | 150 |  | 16050 |  | 12350 |  | 7650 | 2 | 68 | 244 | 3.66 | 103.05 | 299.07 | 0.54645 | 0.65987 | 0.81586 | 98.7179
24/2/99 | 16:00:00pm | 357 | 320.14 | 107.17 | 1.83 | 15.05 | 164.96 | 162.67 | 29.58 | 4.03 | 4.64 | 4.15 | 0.68 | 0.23 | 3.97 | 74.73% | 2.29 | 3.21 | 134.235 | #REF! | #REF! | 0.082896 | 1.1938 | 0.915 | 64.302 | 256.112 | 99.4289 | 24/2/99
25/2/99 | 16:00:00pm | 381 | 344.87 | 105.8 | 4.58 | 14.21 | 165.27 | 163.13 | 29.74 | 3.72 | 4.61 | 3.83 | 0.68 | 0.17 | 4.08 | 80% | 2.14 | 3.21 | 134.46 | #REF! | #REF! | 0.082896 | 1.231 | 2.29 | 63.48 | 275.896 | 98.6505 | 25/2/99 | 655 | 3.2 | 34.9 |  |  | 215 |  | 40 |  | 500 |  | 100 |  | 2600 | 7 | 76 | 250 | 3.66 | 102.13 | 308.69 | 1.9126 | 0.74415 | 0.80987 | 95.7055
26/2/99 | 16:00:00pm | 405 | 337.55 | 106.26 | 3.21 | 15.46 | 164.2 | 163.89 | 29.34 | 3.83 | 4.6 | 3.93 | 0.68 | 0.23 | 3.97 | 74.73% | 0.31 | 3.21 | 134.705 | #REF! | #REF! | 0.082896 | 1.1761 | 1.605 | 63.756 | 270.04 | 99.0383 | 26/2/99
27/2/99 | 16:00:00pm | 429 | 353.58 | 105.34 | 3.66 | 15.55 | 164.35 | 162.06 | 29.71 | 3.73 | 4.62 | 3.79 | 0.68 | 0.17 | 4.08 | 80% | 2.29 | 3.21 | 133.495 | #REF! | #REF! | 0.082896 | 1.1723 | 1.83 | 63.204 | 282.864 | 98.9424 | 27/2/99
28/2/99 | 16:00:00pm | 453 | 335.26 | 101.68 | 3.21 | 15.61 | 163.43 | 162.37 | 29.74 | 4.19 | 4.67 | 4.35 | 0.68 | 0.17 | 3.97 | 80% | 1.06 | 3.21 | 133.16 | #REF! | #REF! | 0.082896 | 1.1697 | 1.605 | 61.008 | 268.208 | 99.025 | 28/2/99
1999-01-03 | 16:00:00pm | 477 | 306.86 | 102.13 | 3.21 | 15.81 | 163.28 | 160.99 | 30.1 | 4.08 | 4.65 | 4.2 | 0.68 | 0.23 | 4.08 | 74.73% | 2.29 | 3.21 | 132.035 | #REF! | #REF! | 0.082896 | 1.1613 | 1.605 | 61.278 | 245.488 | 98.9536 | 1999-01-03
1999-02-03 | 16:00:00pm | 501 | 338.46 | 105.34 | 3.66 | 16.08 | 164.35 | 162.98 | 31.08 | 3.76 | 4.63 | 3.8 | 0.68 | 0.23 | 4.08 | 74.73% | 1.37 | 3.21 | 132.585 | #REF! | #REF! | 0.082896 | 1.15 | 1.83 | 63.204 | 270.768 | 98.9041 | 1999-02-03 | 730 | 3.3 | 62.1 |  |  | 1795 |  | 3005 |  | 15550 |  | 23200 |  | 14500 | 15 | 78 | 281 | 5.5 | 103.51 | 324.26 | 2.7273 | 0.75355 | 0.86659 | 91.6435
1999-03-03 | 16:00:00pm | 525 | 338 | 100.3 | 2.75 | 16.59 | 163.74 | 161.45 | 31.45 | 4 | 4.62 | 4.07 | 0.73 | 0.23 | 4.08 | 76.04% | 2.29 | 3.21 | 131.145 | #REF! | #REF! | 0.082896 | 1.129 | 1.375 | 60.18 | 270.4 | 99.1681 | 1999-03-03
1999-04-03 | 16:00:00pm | 548 | 318.77 | 109.46 | 4.58 | 16.05 | 164.04 | 161.3 | 30.74 | 3.73 | 4.59 | 3.8 | 0.73 | 0.23 | 3.97 | 76.04% | 2.74 | 3.21 | 131.93 | #REF! | #REF! | 0.082896 | 1.1513 | 2.29 | 65.676 | 255.016 | 98.5718 | 1999-04-03 | 936 | 0.8 | 56.9 |  |  | 90 |  | 100 |  | 10500 |  | 8950 |  | 7100 | 14 | 90 | 225 | 4.12 | 107.17 | 303.2 | 3.3981 | 0.83979 | 0.74208 | 91.1111
1999-05-03 | 16:00:00pm | 572 | 316.02 | 103.05 | 4.12 | 16.63 | 164.5 | 162.67 | 31.05 | 3.92 | 4.64 | 3.98 | 0.73 | 0.23 | 4.08 | 76.04% | 1.83 | 3.21 | 132.535 | #REF! | #REF! | 0.082896 | 1.1274 | 2.06 | 61.83 | 252.816 | 98.6906 | 1999-05-03
1999-06-03 | 16:00:00pm | 596 | 264.72 | 103.51 | 3.21 | 16.66 | 163.13 | 161.6 | 29.98 | 4.61 | 4.69 | 4.81 | 0.73 | 0.28 | 4.08 | 72.28% | 1.53 | 3.21 | 132.385 | #REF! | #REF! | 0.082896 | 1.1262 | 1.605 | 62.106 | 211.776 | 98.828 | 1999-06-03
1999-07-03 | 16:00:00pm | 620 | 303.65 | 105.8 | 0.92 | 16.62 | 164.04 | 162.21 | 30.47 | 3.92 | 4.63 | 4 | 0.73 | 0.23 | 4.08 | 76.04% | 1.83 | 3.21 | 132.655 |  |  | 0.082896 | 1.1278 | 0.46 | 63.48 | 242.92 | 99.6997 | 1999-07-03
1999-08-03 | 16:00:00pm | 642 | 278.01 | 97.55 | 3.66 | 16.5 | 159.92 | 158.09 | 31.96 | 4.19 | 4.68 | 4.3 | 0.68 | 0.23 | 4.08 | 74.73% | 1.83 | 3.21 | 127.045 | #REF! | #REF! | 0.082896 | 1.1327 | 1.83 | 58.53 | 222.408 | 98.6972 | 1999-08-03
1999-09-03 | 16:00:00pm | 666 | 300.91 | 106.71 | 2.75 | 15.9 | 159.01 | 156.72 | 30.84 | 3.93 | 4.66 | 4.06 | 0.63 | 0.23 | 3.97 | 73.26% | 2.29 | 3.21 | 127.025 | #REF! | #REF! | 0.082896 | 1.1575 | 1.375 | 64.026 | 240.728 | 99.0976 | 1999-09-03 | 945 | 2.8 | 41 |  |  | 50 |  | 150 |  | 5100 |  | 550 |  | 8200 | 9 | 79 | 250 | 4.12 | 99.84 | 293.58 | 2.1845 | 0.79127 | 0.85156 | 94.5289
1999-10-03 | 16:00:00pm | 690 | 314.65 | 104.42 | 2.29 | 16.1 | 159.77 | 158.4 | 30.84 | 3.83 | 4.64 | 3.97 | 0.68 | 0.17 | 4.08 | 80% | 1.37 | 3.21 | 128.245 | #REF! | #REF! | 0.082896 | 1.1492 | 1.145 | 62.652 | 251.72 | 99.2716 | 1999-10-03
1999-11-03 | 16:00:00pm | 714 | 316.94 | 102.13 | 1.83 | 15.41 | 163.13 | 161.76 | 30.9 | 4.09 | 4.64 | 4.23 | 0.63 | 0.23 | 4.08 | 73.26% | 1.37 | 3.21 | 131.545 | #REF! | #REF! | 0.082896 | 1.1783 | 0.915 | 61.278 | 253.552 | 99.4187 | 1999-11-03 | 900 | 2.2 | 66.3 |  |  | 20 |  | 300 |  | 20050 |  | 147500 |  | 6900 | 14 | 68 | 227 | 3.66 | 103.51 | 306.86 | 3.8251 | 0.65694 | 0.73975 | 90.5085
1999-12-03 | 16:00:00pm | 738 | 316.94 | 100.76 | 4.12 | 15.89 | 162.67 | 161.3 | 31.02 | 4.25 | 4.63 | 4.38 | 0.68 | 0.23 | 3.97 | 74.73% | 1.37 | 3.21 | 130.965 | #REF! | #REF! | 0.082896 | 1.1579 | 2.06 | 60.456 | 253.552 | 98.6879 | 1999-12-03
13/3/99 | 16:00:00pm | 762 | 278.46 | 103.05 | 4.58 | 15.95 | 165.11 | 163.59 | 31.57 | 4.04 | 4.61 | 4.17 | 0.68 | 0.28 | 4.08 | 70.83% | 1.52 | 3.21 | 132.78 | #REF! | #REF! | 0.082896 | 1.1554 | 2.29 | 61.83 | 222.768 | 98.3907 | 13/3/99
14/3/99 | 16:00:00pm | 783 | 267.01 | 108.09 | 2.29 | 15.61 | 169.23 | 168.01 | 32.45 | 4 | 4.64 | 4.13 | 0.68 | 0.34 | 4.18 | 66.67% | 1.22 | 3.21 | 136.17 | #REF! | #REF! | 0.082896 | 1.1697 | 1.145 | 64.854 | 213.608 | 99.1776 | 14/3/99
15/3/99 | 16:00:00pm | 807 | 304.57 | 103.05 | 2.75 | 15.75 | 170 | 166.64 | 32.39 | 3.85 | 4.59 | 3.96 | 0.73 | 0.23 | 4.18 | 76.04% | 3.36 | 3.21 | 135.93 | #REF! | #REF! | 0.082896 | 1.1638 | 1.375 | 61.83 | 243.656 | 99.0998 | 15/3/99
16/3/99 | 16:00:00pm | 831 | 318.77 | 96.64 | 5.04 | 15.49 | 170.15 | 168.01 | 32.82 | 4.06 | 4.62 | 4.18 | 0.68 | 0.23 | 4.08 | 74.73% | 2.14 | 3.21 | 136.26 | #REF! | #REF! | 0.082896 | 1.1748 | 2.52 | 57.984 | 255.016 | 98.3898 | 16/3/99 | 845 | 3.5 | 51.2 |  |  | 4 |  | 30 |  | 3600 |  | 100 |  | 50 | 16 | 63 | 154 | 2.75 | 103.05 | 305.94 | 5.8182 | 0.61135 | 0.50337 | 85.2535
17/3/99 | 16:00:00pm | 855 | 343.96 | 105.8 | 3.21 | 17.01 | 169.69 | 169.39 | 34.07 | 3.75 | 4.63 | 3.82 | 0.73 | 0.23 | 4.08 | 76.04% | 0.3 | 3.21 | 135.47 | #REF! | #REF! | 0.082896 | 1.1121 | 1.605 | 63.48 | 275.168 | 99.0521 | 17/3/99
18/3/99 | 16:00:00pm | 879 | 313.27 | 108.09 | 3.21 | 16.97 | 168.62 | 167.55 | 30.93 | 3.89 | 4.64 | 3.94 | 0.73 | 0.23 | 4.08 | 76.04% | 1.07 | 3.21 | 137.155 | #REF! | #REF! | 0.082896 | 1.1137 | 1.605 | 64.854 | 250.616 | 98.9825 | 18/3/99 | 1208 | 3.2 | 50.2 |  |  | 20 |  | 250 |  | 3250 |  | 755 |  | 3700 | 11 | 72 | 169 | 3.66 | 101.22 | 288.08 | 3.0055 | 0.71132 | 0.58664 | 90.8714
19/3/99 | 16:00:00pm | 903 | 323.35 | 101.22 | 3.66 | 16.63 | 168.62 | 166.03 | 30.74 | 4.38 | 4.64 | 4.5 | 0.73 | 0.23 | 4.18 | 76.04% | 2.59 | 3.21 | 136.585 | #REF! | #REF! | 0.082896 | 1.1274 | 1.83 | 60.732 | 258.68 | 98.8541 | 19/3/99
20/3/99 | 15:30:00pm | 926 | 327.01 | 103.05 | 3.66 | 17.32 | 167.86 | 165.88 | 30.8 | 4.25 | 4.65 | 4.36 | 0.73 | 0.23 | 4.08 | 76.04% | 1.98 | 3.21 | 136.07 | #REF! | #REF! | 0.082896 | 1.0998 | 1.83 | 61.83 | 261.608 | 98.8684 | 20/3/99
21/3/99 | 16:00:00pm | 951 | 321.06 | 105.34 | 4.12 | 16.94 | 163.89 | 163.74 | 29.8 | 3.94 | 4.61 | 4.05 | 0.73 | 0.23 | 4.08 | 76.04% | 0.15 | 3.21 | 134.015 | #REF! | #REF! | 0.082896 | 1.1149 | 2.06 | 63.204 | 256.848 | 98.7127 | 21/3/99
22/3/99 | 16:00:00pm | 975 | 336.17 | 105.34 | 2.75 | 17.12 | 164.66 | 161.6 | 29.86 | 4.01 | 4.59 | 4.12 | 0.73 | 0.23 | 4.08 | 76.04% | 3.06 | 3.21 | 133.27 | #REF! | #REF! | 0.082896 | 1.1077 | 1.375 | 63.204 | 268.936 | 99.172 | 22/3/99
23/3/99 | 16:00:00pm | 999 | 291.75 | 101.68 | 4.12 | 17.59 | 163.59 | 161.91 | 30.04 | 4.1 | 4.67 | 4.21 | 0.73 | 0.28 | 4.08 | 72.28% | 1.68 | 3.21 | 132.71 | #REF! | #REF! | 0.082896 | 1.0892 | 2.06 | 61.008 | 233.4 | 98.6006 | 23/3/99 | 807 | 3.7 | 41.8 |  |  | 54 |  | 150 |  | 7450 |  | 985 |  | 3650 | 15 | 68 | 224 | 3.66 | 103.51 | 284.42 | 4.0984 | 0.65694 | 0.78757
24/3/99 | 16:00:00pm | 1023 | 307.78 | 100.76 | 1.83 | 18.33 | 162.82 | 161.45 | 29.95 | 4.16 | 4.66 | 4.27 | 0.73 | 0.23 | 3.97 | 76.04% | 1.37 | 3.21 | 132.185 | #REF! | #REF! | 0.082896 | 1.0609 | 0.915 | 60.456 | 246.224 | 99.4033 | 24/3/99
25/3/99 | 16:00:00pm | 1047 | 316.94 | 104.42 | 5.04 | 17.85 | 162.98 | 161.91 | 31.75 | 3.86 | 4.65 | 3.97 | 0.73 | 0.23 | 4.08 | 76.04% | 1.07 | 3.21 | 130.695 | #REF! | #REF! | 0.082896 | 1.0792 | 2.52 | 62.652 | 253.552 | 98.4061 | 25/3/99 | 1140 | 3.9 | 35.1 |  |  | 65 |  | 200 |  | 12600 |  | 16650 |  | 2350 | 12 | 68 | 282 | 5.5 | 101.22 | 309.61 | 2.1818 | 0.6718 | 0.91082
26/3/99 | 16:00:00pm | 1071 | 328.84 | 99.39 | 2.75 | 17.84 | 163.89 | 161.6 | 32.09 | 3.94 | 4.63 | 4.04 | 0.68 | 0.23 | 3.97 | 74.73% | 2.29 | 3.21 | 130.655 | #REF! | #REF! | 0.082896 | 1.0796 | 1.375 | 59.634 | 263.072 | 99.1478 | 26/3/99
27/3/99 | 16:00:00pm | 1095 | 294.49 | 102.59 | 3.66 | 17.26 | 163.89 | 163.13 | 30.84 | 4.17 | 4.66 | 4.35 | 0.73 | 0.23 | 3.97 | 76.04% | 0.76 | 3.21 | 132.67 | #REF! | #REF! | 0.082896 | 1.1022 | 1.83 | 61.554 | 235.592 | 98.7683 | 27/3/99
28/3/99 | 16:00:00pm | 1119 | 330.68 | 100.76 | 4.12 | 18.3 | 163.74 | 161.45 | 32.94 | 3.86 | 4.62 | 3.96 | 0.73 | 0.23 | 3.97 | 76.04% | 2.29 | 3.21 | 129.655 | #REF! | #REF! | 0.082896 | 1.062 | 2.06 | 60.456 | 264.544 | 98.7323 | 28/3/99
29/3/99 | 16:00:00pm | 1143 | 379.68 | 103.05 | 3.66 | 17.78 | 164.04 | 163.13 | 32.06 | 3.74 | 4.58 | 3.81 | 0.73 | 0.17 | 3.97 | 81.11% | 0.91 | 3.21 | 131.525 | #REF! | #REF! | 0.082896 | 1.0819 | 1.83 | 61.83 | 303.744 | 98.9988 | 29/3/99
30/3/99 | 16:00:00pm | 1167 | 340.75 | 108.55 | 3.66 | 17.64 | 163.43 | 160.08 | 31.72 | 3.8 | 4.63 | 3.89 | 0.73 | 0.28 | 3.97 | 72.28% | 3.35 | 3.21 | 130.035 | #REF! | #REF! | 0.082896 | 1.0873 | 1.83 | 65.13 | 272.6 | 98.9163 | 30/3/99 | 805 | 5 | 37.9 |  |  | 86 |  | 85 |  | 6950 |  | 4100 |  | 3950 | 4 | 79 | 274 | 7.33 | 125.03 | 348.08 | 0.5457 | 0.63185 | 0.78718
31/3/99 | 16:00:00pm | 1191 | 325.18 | 97.1 | 4.58 | 17.52 | 162.82 | 160.08 | 31.75 | 3.98 | 4.62 | 4.09 | 0.73 | 0.23 | 4.08 | 76.04% | 2.74 | 3.21 | 129.7 | #REF! | #REF! | 0.082896 | 1.092 | 2.29 | 58.26 | 260.144 | 98.5616 | 31/3/99
1999-01-04 | 16:00:00pm | 1215 | 307.78 | 98.47 | 1.83 | 17.9 | 163.13 | 160.54 | 31.6 | 4.13 | 4.66 | 4.27 | 0.73 | 0.23 | 4.08 | 76.04% | 2.59 | 3.21 | 130.235 | #REF! | #REF! | 0.082896 | 1.0772 | 0.915 | 59.082 | 246.224 | 99.4006 | 1999-01-04 | 900 | 4 | 34 |  |  | 10 |  | 1450 |  | 1300 |  | 1850 |  | 2350 | 17 | 73 | 228 | 2.75 | 100.76 | 332.51 | 6.1818 | 0.72449 | 0.68569
1999-02-04 | 16:00:00pm | 1239 | 331.13 | 104.88 | 3.66 | 18.39 | 164.04 | 161.76 | 32.09 | 3.9 | 4.59 | 4 | 0.73 | 0.23 | 3.97 | 76.04% | 2.28 | 3.21 | 130.81 | #REF! | #REF! | 0.082896 | 1.0586 | 1.83 | 62.928 | 264.904 | 98.8836 | 1999-02-04
1999-03-04 | 16:00:00pm | 1263 | 304.57 | 106.71 | 4.58 | 17.98 | 164.5 | 161.3 | 31.54 | 4.08 | 4.64 | 4.24 | 0.73 | 0.28 | 3.97 | 72.28% | 3.2 | 3.21 | 131.36 | #REF! | #REF! | 0.082896 | 1.0742 | 2.29 | 64.026 | 243.656 | 98.5115 | 1999-03-04
1999-04-04 | 16:00:00pm | 1287 | 317.39 | 97.1 | 2.29 | 20.16 | 162.37 | 162.21 | 32.88 | 4.12 | 4.71 | 4.2 | 0.73 | 0.23 | 3.97 | 76.04% | 0.16 | 3.21 | 129.41 | #REF! | #REF! | 0.082896 | 0.99439 | 1.145 | 58.26 | 253.912 | 99.2664 | 1999-04-04
1999-05-04 | 16:00:00pm | 1311 | 344.42 | 101.68 | 2.29 | 18.05 | 164.2 | 162.06 | 32.36 | 4.1 | 4.62 | 4.21 | 0.73 | 0.17 | 4.08 | 81.11% | 2.14 | 3.21 | 130.77 | #REF! | #REF! | 0.082896 | 1.0715 | 1.145 | 61.008 | 275.536 | 99.3196 | 1999-05-04
1999-06-04 | 9:00:00am | 1328 | 310.07 | 95.72 | 3.21 | 18.74 | 164.35 | 162.98 | 29.1 | 6.02 | 4.69 | 6.33 | 0.68 | 0.17 | 3.97 | 80% | 1.37 | 3.21 | 134.565 | #REF! | #REF! | 0.082896 | 1.0455 | 1.605 | 57.432 | 248.056 | 98.9492 | 1999-06-04 | 830 | 4.8 | 39.8 |  |  | 27 |  | 365 |  |  |  | 550 |  | 3000
1999-07-04 | 16:00:00pm | 1356 | 285.79 | 100.3 | 1.37 | 19.75 | 150.92 | 148.63 | 30.68 | 5.98 | 4.71 | 6.34 | 0.68 | 0.23 | 4.08 | 74.73% | 2.29 | 3.21 | 119.095 |  |  | 0.082896 | 1.0088 | 0.685 | 60.18 | 228.632 | 99.5256 | 1999-07-04 | [24 empty] | ALARM
1999-08-04 | 16:00:00pm | 1380 | 299.99 | 91.14 | 2.29 | 21.68 | 150.16 | 147.11 | 31.75 | 6.09 | 4.77 | 6.37 | 0.73 | 0.17 | 4.18 | 81.11% | 3.05 | 3.21 | 116.885 | #REF! | #REF! | 0.082896 | 0.94293 | 1.145 | 54.684 | 239.992 | 99.2229 | 1999-08-04 | [24 empty] | outside lab
1999-09-04 | 16:00:00pm | 1404 | 280.75 | 95.26 | 1.83 | 21.81 | 150.46 | 149.85 | 32.76 | 6.04 | 4.81 | 6.34 | 0.78 | 0.23 | 4.08 | 77.23% | 0.61 | 3.21 | 117.395 | #REF! | #REF! | 0.082896 | 0.93868 | 0.915 | 57.156 | 224.6 | 99.3505 | 1999-09-04
1999-10-04 | 16:00:00pm | 1428 | 212.05 | 97.55 | 3.21 | 19.81 | 150.16 | 147.72 | 30.8 | 5.8 | 4.71 | 6.14 | 0.73 | 0.4 | 4.08 | 64.6% | 2.44 | 3.21 | 118.14 | #REF! | #REF! | 0.082896 | 1.0067 | 1.605 | 58.53 | 169.64 | 98.5932 | 1999-10-04
1999-11-04 | 16:00:00pm | 1450 | 265.18 | 94.81 | 1.83 | 19.07 | 151.68 | 150.01 | 30.8 | 5.94 | 4.7 | 6.31 | 0.73 | 0.28 | 4.08 | 72.28% | 1.67 | 3.21 | 120.045 | #REF! | #REF! | 0.082896 | 1.0334 | 0.915 | 56.886 | 212.144 | 99.3198 | 1999-11-04
1999-12-04 | 16:00:00pm | 1473 | 286.71 | 93.43 | 1.37 | 19.46 | 152.45 | 149.85 | 30.99 | 5.97 | 4.51 | 6.24 | 0.73 | 0.23 | 3.97 | 76.04% | 2.6 | 3.21 | 120.16 | #REF! | #REF! | 0.082896 | 1.0192 | 0.685 | 56.058 | 229.368 | 99.52 | 1999-12-04
13/4/99 | 16:00:00pm | 1497 | 255.11 | 93.89 | 2.29 | 19.15 | 151.84 | 150.16 | 30.71 | 6.1 | 4.71 | 6.4 | 0.73 | 0.23 | 3.97 | 76.04% | 1.68 | 3.21 | 120.29 | #REF! | #REF! | 0.082896 | 1.0304 | 1.145 | 56.334 | 204.088 | 99.1207 | 13/4/99
14/4/99 | 16:00:00pm | 1521 | 266.56 | 92.97 | 3.21 | 19.79 | 152.29 | 150.16 | 30.9 | 6.15 | 4.77 | 6.5 | 0.73 | 0.23 | 3.97 | 76.04% | 2.13 | 3.21 | 120.325 | #REF! | #REF! | 0.082896 | 1.0074 | 1.605 | 55.782 | 213.248 | 98.8068 | 14/4/99
15/4/99 | 16:00:00pm | 1545 | 266.1 | 89.31 | 2.75 | 20.19 | 151.38 | 148.33 | 30.65 | 6.17 | 4.78 | 6.51 | 0.73 | 0.23 | 3.97 | 76.04% | 3.05 | 3.21 | 119.205 | #REF! | #REF! | 0.082896 | 0.99334 | 1.375 | 53.586 | 212.88 | 98.968 | 15/4/99
16/4/99 | 16:00:00pm | 1569 | 272.97 | 89.77 | 0.46 | 20.94 | 150.62 | 149.4 | 30.56 | 6.1 | 4.78 | 6.41 | 0.73 | 0.23 | 3.97 | 76.04% | 1.22 | 3.21 | 119.45 | #REF! | #REF! | 0.082896 | 0.96758 | 0.23 | 53.862 | 218.376 | 99.831 | 16/4/99
17/4/99 | 16:00:00pm | 1590 | 279.38 | 92.97 | 0.46 | 20.19 | 151.84 | 149.55 | 32.54 | 6.02 | 4.75 | 6.39 | 0.73 | 0.23 | 4.08 | 76.04% | 2.29 | 3.21 | 118.155 | #REF! | #REF! | 0.082896 | 0.99334 | 0.23 | 55.782 | 223.504 | 99.8353 | 17/4/99
18/4/99 | 16:00:00pm | 1614 | 242.74 | 91.14 | 1.37 | 20.28 | 151.23 | 149.7 | 31.66 | 5.99 | 4.73 | 6.35 | 0.68 | 0.28 | 3.97 | 70.83% | 1.53 | 3.21 | 118.805 | #REF! | #REF! | 0.082896 | 0.99021 | 0.685 | 54.684 | 194.192 | 99.4495 | 18/4/99
19/4/99 | 16:00:00pm | 1638 | 259.23 | 94.35 | 4.12 | 20.65 | 151.99 | 150.01 | 32.06 | 5.86 | 4.69 | 6.2 | 0.73 | 0.23 | 4.08 | 76.04% | 1.98 | 3.21 | 118.94 | #REF! | #REF! | 0.082896 | 0.97744 | 2.06 | 56.61 | 207.384 | 98.4394 | 19/4/99
20/4/99 | 16:00:00pm | 1662 | 261.98 | 92.97 | 0.46 | 20.97 | 151.84 | 148.02 | 31.26 | 6.01 | 4.7 | 6.4 | 0.68 | 0.23 | 3.97 | 74.73% | 3.82 | 3.21 | 118.67 | #REF! | #REF! | 0.082896 | 0.96656 | 0.23 | 55.782 | 209.584 | 99.8267 | 20/4/99
21/4/99 | 16:00:00pm | 1686 | 258.77 | 92.06 | 2.75 | 20.25 | 151.53 | 149.4 | 30.99 | 5.9 | 4.67 | 6.25 | 0.68 | 0.23 | 4.08 | 74.73% | 2.13 | 3.21 | 119.475 | #REF! | #REF! | 0.082896 | 0.99125 | 1.375 | 55.236 | 207.016 | 98.9514 | 21/4/99
22/4/99 | 16:00:00pm | 1710 | 258.31 | 85.65 | 1.37 | 22.05 | 151.07 | 148.33 | 31.69 | 5.9 | 4.66 | 6.29 | 0.68 | 0.23 | 3.97 | 74.73% | 2.74 | 3.21 | 118.01 | #REF! | #REF! | 0.082896 | 0.93089 | 0.685 | 51.39 | 206.648 | 99.4691 | 22/4/99
23/4/99 | 15:30:00pm | 1734 | 261.52 | 87.94 | 1.37 | 23.03 | 150.31 | 147.87 | 32.42 | 5.96 | 4.78 | 6.31 | 0.68 | 0.23 | 3.87 | 74.73% | 2.44 | 3.21 | 116.67 | #REF! | #REF! | 0.082896 | 0.89988 | 0.685 | 52.764 | 209.216 | 99.4771 | 23/4/99
24/4/99 | 16:00:00pm | 1758 | 246.4 | 92.06 | 2.75 | 22.07 | 151.53 | 149.85 | 32.27 | 5.87 | 4.74 | 6.3 | 0.73 | 0.23 | 4.08 | 76.04% | 1.68 | 3.21 | 118.42 | #REF! | #REF! | 0.082896 | 0.93024 | 1.375 | 55.236 | 197.12 | 98.9103 | 24/4/99
25/4/99 | 16:00:00pm | 1782 | 250.53 | 92.06 | 1.37 | 21.62 | 152.91 | 151.23 | 32.02 | 5.96 | 4.74 | 6.32 | 0.73 | 0.23 | 4.08 | 76.04% | 1.68 | 3.21 | 120.05 | #REF! | #REF! | 0.082896 | 0.9449 | 0.685 | 55.236 | 200.424 | 99.4641 | 25/4/99
26/4/99 | 16:00:00pm | 1806 | 248.69 | 90.68 | 0.46 | 21.97 | 152.14 | 148.94 | 30.77 | 5.92 | 4.73 | 6.3 | 0.73 | 0.23 | 4.08 | 76.04% | 3.2 | 3.21 | 119.77 | #REF! | #REF! | 0.082896 | 0.93348 | 0.23 | 54.408 | 198.952 | 99.8184 | 26/4/99
27/4/99 | 16:00:00pm | 1821 | 245.49 | 90.23 | 1.37 | 21 | 152.6 | 148.78 | 30.16 | 5.95 | 4.71 | 6.33 | 0.68 | 0.23 | 4.08 | 74.73% | 3.82 | 3.21 | 120.53 | #REF! | #REF! | 0.082896 | 0.96555 | 0.685 | 54.138 | 196.392 | 99.4532 | 27/4/99 |  | 3.8 | 48.3 |  |  | 470 |  | 1150 |  |  |  | 4950 |  | 3650
28/4/99 | 16:00:00pm | 1854 | 252.36 | 95.26 | 1.83 | 21.15 | 152.45 | 150.31 | 29.95 | 5.96 | 4.75 | 6.33 | 0.73 | 0.23 | 4.08 | 76.04% | 2.14 | 3.21 | 121.43 | #REF! | #REF! | 0.082896 | 0.9605 | 0.915 | 57.156 | 201.888 | 99.2936 | 28/4/99
29/4/99 | 16:00:00pm | 1878 | 251.44 | 93.43 | 3.66 | 21.32 | 153.67 | 151.23 | 29.43 | 5.96 | 4.71 | 6.3 | 0.68 | 0.23 | 4.08 | 74.73% | 2.44 | 3.21 | 123.02 | #REF! | #REF! | 0.082896 | 0.95483 | 1.83 | 56.058 | 201.152 | 98.577 | 29/4/99
30/4/99 | 16:00:00pm | 1902 | 249.61 | 92.06 | 3.66 | 20.94 | 152.6 | 150.62 | 28.85 | 6.02 | 4.7 | 6.33 | 0.68 | 0.23 | 3.97 | 74.73% | 1.98 | 3.21 | 122.76 | #REF! | #REF! | 0.082896 | 0.96758 | 1.83 | 55.236 | 199.688 | 98.5643 | 30/4/99
1999-01-05 | 16:00:00pm | 1926 | 225.79 | 92.06 | 0.92 | 20.91 | 160.23 | 156.72 | 30.23 | 5.95 | 4.73 | 6.36 | 0.68 | 0.28 | 4.08 | 70.83% | 3.51 | 3.21 | 128.245 | #REF! | #REF! | 0.082896 | 0.96859 | 0.46 | 55.236 | 180.632 | 99.61 | 1999-01-05
1999-02-05 | 16:00:00pm | 1950 | 231.29 | 92.06 | 0.92 | 20.25 | 160.23 | 157.18 | 28.91 | 5.99 | 4.69 | 6.43 | 0.68 | 0.23 | 4.08 | 74.73% | 3.05 | 3.21 | 129.795 | #REF! | #REF! | 0.082896 | 0.99125 | 0.46 | 55.236 | 185.032 | 99.6171 | 1999-02-05
1999-03-05 | 16:00:00pm | 1974 | 232.66 | 95.72 | 1.37 | 19.52 | 161.3 | 156.41 | 28.06 | 6 | 4.69 | 6.43 | 0.68 | 0.23 | 4.18 | 74.73% | 4.89 | 3.21 | 130.795 | #REF! | #REF! | 0.082896 | 1.0171 | 0.685 | 57.432 | 186.128 | 99.4375 | 1999-03-05
1999-04-05 | 08:00:00am | 1990 | 232.66 | 90.23 | 2.29 | 19.2 | 161.3 | 158.7 | 27.54 | 6.06 | 4.7 | 6.42 | 0.68 | 0.23 | 4.18 | 74.73% | 2.6 | 3.21 | 132.46 | #REF! | #REF! | 0.082896 | 1.0286 | 1.145 | 54.138 | 186.128 | 99.0469 | 1999-04-05 |  | 4.7 | 51.4 |  |  | <10 |  | 600 |  |  |  | 10500 |  | 1750
|  | 12000 | [19 empty] | 0.082896

## LFC1. Weeks 1-10
FIELD-SET 1: LT-SEBST RESULTS: WEEKS 1-10 (FILE: ltsebst.xls)
Field 1-1: PWS And Treatment Plant Data |  |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  |  | Field 1-3: SEBST Design Parameters |  |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [47 empty] | Field 1-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [10 empty] | Field 1-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 6 | [9 empty] | Field 1-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 8 | [9 empty] | Field 1-11: Permeate, Feed, Concentrate And Blended Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 1-13: Membrane Cost Parameters
|  |  | General Information |  |  | Calculate Temperature Normalized MTCW |  |  | Parameters Evaluated Prior to Pretreatment |  | (see cell A47) | [49 empty] | Operating Parameters During Sample Collection | [10 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | City of Norfolk |  | Membrane manufacturer | Hydranautics |  | Average yearly temperature of feed water, TavgoC (oC) | 20 |  | PLANT FILTERED WATER: |  |  |  | Date | Time | Operation time | Permeate | PI | PC | PP | QR | Qp | QW | Cleaning | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.76 | [9 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.76 | [8 empty] | Recovery during sample collection (decimal) | 0.8 | [8 empty] | Recovery during sample collection (decimal) | NA | [8 empty] | Recovery during sample collection (decimal) | 0.71 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | VA37010100 |  | Membrane trade name | Low Fouling Composite |  | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.097757 |  | Alkalinity (mg/L as CaCO3) | 10.5 |  |  | MM/DD/YY | hh:mm | hh.hh | Temp.(oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Event | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.96 | [9 empty] | Feed flow rate during sample collection (gpm) | 0.91 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.96 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.85 | [8 empty] | Feed flow rate during sample collection (gpm) | NA | [8 empty] | Feed flow rate during sample collection (gpm) | 0.96 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA |  | Membrane element model number | LFC1 |  |  |  |  | pH (units) | 6.44 |  | 1 | 36405 | 16:00:00pm | 6 | 17.35 | 164.35 | 162.21 | 29.83 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.5869 | 2.3266 | 131.1234 | 0.10362 | 4.49 | 4.42 | 4.48 | 0.915 | 61.008 | 257.216 | 251.738 | 2.1297 | 98.5002 | 233.5732 | 99.6083 | [17 empty] | Influent flow rate during sample collection (gpm) | 4.83 | [9 empty] | Influent flow rate during sample collection (gpm) | 4.88 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.14 | [8 empty] | Influent flow rate during sample collection (gpm) | 4.82 | [8 empty] | Influent flow rate during sample collection (gpm) | NA | [8 empty] | Influent flow rate during sample collection (gpm) | 5.04 | [7 empty] | Capital Recovery Period (years) | 20
|  |  | Molecular weight cutoff (Daltons) | 200-300 |  | Calculate System Flow Rates1 |  |  | Total Dissolved Solids | 73 mg/L |  | 2 | 36435 | 16:00:00pm | 30 | 17.5 | 163.43 | 162.67 | 30.1 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 12.5885 | 2.1885 | 130.7615 | 0.096271 | 4.62 | 4.11 | 4.28 | 1.375 | 60.732 | 256.848 | 236.2223 | 8.0303 | 97.736 | 220.2206 | 99.3756 | [77 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide |  | Design recovery, R (decimal) | 0.75 |  | Conductivity | 129 umhos/cm |  | 3 | 36466 | 16:00:00pm | 54 | 17.26 | 163.43 | 163.13 | 30.38 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.6308 | 2.3459 | 130.5541 | 0.10441 | 4.64 | 4.11 | 4.23 | 0.685 | 61.278 | 268.208 | 253.5949 | 5.4484 | 98.8821 | 235.279 | 99.7089 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [10 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  |  | Membrane construction (e.g., thin-film composite) | Thin-film composite |  | Design flux, FW (gfd) | 11.8588 |  | SDI | 5.8 |  | 4 | 36496 | 16:00:00pm | 78 | 17.14 | 163.59 | 161.91 | 30.29 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.6896 | 2.2767 | 130.1833 | 0.10516 | 4.67 | 4.21 | 4.32 | 1.375 | 60.18 | 279.928 | 246.822 | 11.8266 | 97.7152 | 229.0465 | 99.3997 | [16 empty] | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-6 | CF-6 | CC-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-8 | CF-8 | CC-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-10 | CF-10 | CC-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 (dup) | CF-2 (dup) | CC-2 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 15
|  |  | Membrane hydrophobicity | Hydrophillic |  | Permeate flow rate, Qp (gpm) | 0.7 |  | Turbidity (ntu) | 0.26 |  | 5 | 1999-02-13 | 16:00:00pm | 102 | 17.4 | 162.82 | 161.3 | 29.95 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35769 | 0.81111 | 4.5333 | 12.3671 | 13.5626 | 2.8021 | 129.3079 | 0.10489 | 4.65 | 3.93 | 4 | 2.52 | 59.634 | 281.76 | 304.8882 | -8.2085 | 95.7742 | 282.7267 | 99.1087 | [16 empty] | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | 1999-02-16 | --- | --- | --- | --- | --- |  | Sampling date | MM/DD/YY | 1999-03-09 | 1999-03-09 | 1999-03-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-16 | 1999-03-16 | 1999-03-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-01 | 1999-04-01 | 1999-04-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | NA | NA | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 9
Phone Number |  |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Neutral |  | Feed flow rate, QF (gpm) | 0.93333 |  | Dissolved aluminum (mg/L) | <0.044 |  | 6 | 1999-02-14 | 16:00:00pm | 123 | 17.01 | 163.74 | 161.76 | 32.21 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.36427 | 0.70833 | 4.25 | 11.52 | 12.8116 | 2.2814 | 128.2586 | 0.099889 | 4.29 | 3.29 | 3.27 | 3.665 | 75.018 | 335.256 | 248.3039 | 25.936 | 95.1145 | 231.8004 | 98.4189 | [16 empty] | Sampling time (approx.) | hh:mm | 9:10 | 9:25 | 9:40 | --- | --- | --- | --- | --- |  | Sampling time | hh:mm | 9:50 | 10:05 | 9:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:10 | 9:20 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:25 | 9:40 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | NA | NA | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:10 | 9:25 | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | Concentrate-waste flow rate, QW (gpm) | 0.23333 |  | Total aluminum (mg/L) | 0.074 |  | 7 | 1999-02-15 | 15:00:00pm | 146 | 17.34 | 163.59 | 161.15 | 31.57 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35769 | 0.81111 | 4.5333 | 12.3671 | 13.5918 | 2.8379 | 127.9621 | 0.10622 | 4.68 | 4 | 4.12 | 2.06 | 59.904 | 279.2 | 308.2929 | -10.4201 | 96.5612 | 285.8482 | 99.2793 | [16 empty] | Operation time | hh.hh | 163 | 163 | 163 | --- | --- | --- | --- | --- |  | Operation time | hh.hh | 660 | 660 | 660 | --- | --- | --- | --- | --- | Operation time | hh.hh | 824 | 824 | 824 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1208 | 1208 | 1208 | --- | --- | --- | --- | --- | Operation time | hh.hh | NA | NA | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 163 | 163 | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 131.8
E-Mail Address (optional) |  |  | Design Parameters |  |  | Minimum influent flow rate, QI, min (gpm) | 12 |  | PILOT FILTERED: Sulfate (mg/L) | 43 |  | 8 | 1999-02-16 | 16:00:00pm | 170 | 17.52 | 162.98 | 159.01 | 32.06 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 12.5795 | 2.1867 | 126.7483 | 0.099248 | 4.67 | 3.89 | 3.99 | 2.52 | 61.83 | 279.928 | 237.1813 | 15.2706 | 95.9243 | 221.1924 | 98.8607 | [16 empty] | pH | --- | 5.35 | 5.69 | 3.99 | --- | --- | --- | --- | --- |  | pH | --- | 5.49 | 5.32 | 4.6 | --- | --- | --- | --- | --- | pH | --- | 5.63 | 4.97 | 4.68 | --- | --- | --- | --- | --- | pH | --- | 5.62 | 6.03 | 4.63 | --- | --- | --- | --- | --- | pH | --- | NA | NA | NA | --- | --- | --- | --- | --- | pH | --- | 5.32 | 5.64 | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.65
|  |  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" |  | Maximum influent flow rate, QI, max (gpm) | 20 |  | RAW WATER: |  |  | 9 | 1999-02-17 | 16:00:00pm | 194 | 17.12 | 163.43 | 161.6 | 32.27 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36621 | 0.72277 | 4.0396 | 12.3671 | 13.6994 | 1.9691 | 128.2759 | 0.1068 | 4.63 | 4 | 4.1 | 1.375 | 60.18 | 246.584 | 213.493 | 13.4198 | 97.7152 | 198.2822 | 99.3065 | [16 empty] | Temperature | oC | 16.8 | 13.6 | 16.2 | --- | --- | --- | --- | --- |  | Temperature | oC | 15.5 | 13.1 | 15.6 | --- | --- | --- | --- | --- | Temperature | oC | 14.8 | 12.5 | 15.1 | --- | --- | --- | --- | --- | Temperature | oC | 17.5 | 15.2 | 17.5 | --- | --- | --- | --- | --- | Temperature | oC | NA | NA | NA | --- | --- | --- | --- | --- | Temperature | oC | 16.5 | 13.3 | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 30
Technical ICR Contact Person |  |  | Active membrane area of membrane element used, A (ft2) | 85 |  | Design influent flow rate2, QI (gpm) | 4.93 |  | Dissolved iron (mg/L) | 0.2 |  | 10 | 1999-02-18 | 16:00:00pm | 218 | 16.82 | 163.43 | 161.76 | 31.84 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 12.8994 | 2.2272 | 128.5278 | 0.10036 | 4.69 | 3.99 | 4.09 | 2.52 | 62.928 | 260.512 | 241.5256 | 7.2881 | 95.9954 | 225.2406 | 98.8812 | [16 empty] | Alkalinity | mg/L as CaCO3 | 1 | 3 | BMRL | 9.3333 | #VALUE! | 66.6667 | 8.7039 | 88.5109 |  | Alkalinity | mg/L as CaCO3 | 1 | 1 | BMRL | 1 | #VALUE! | 0 | 1 | 0 | Alkalinity | mg/L as CaCO3 | 1 | 1 | BMRL | 1 | #VALUE! | 0 | 1 | 2.2204e-14 | Alkalinity | mg/L as CaCO3 | 3 | 4 | BMRL | 8 | #VALUE! | 25 | 7.6473 | 60.7705 | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 1 | 3 | NA | 7.8966 | #VALUE! | 66.6667 | 7.4302 | 86.5414 | Electric Rate ($/kW-h) | 0.049
Mailing Address |  |  | Design flux, FW (gfd) | 11.8588 |  | Design recycle flow rate, QR (gpm) | 3.9967 |  | Total iron (mg/L) | 0.6 |  | 11 | 1999-02-19 | 16:00:00pm | 238 | 17.08 | 164.96 | 164.81 | 30.38 | 3.97 | 0.78 | 0.23 |  | 1.01 | 4.98 | 0.35575 | 0.77228 | 3.9307 | 13.2141 | 14.6588 | 2.2485 | 132.2565 | 0.11084 | 4.6 | 4.05 | 4.16 | 2.975 | 58.53 | 260.512 | 246.9339 | 5.2121 | 94.9171 | 227.8287 | 98.6942 | [16 empty] | Total dissolved solids | mg/L | 3 | 75 | 246 | 303 | -23.1707 | -228 | 280.3416 | 12.2499 |  | Total dissolved solids | mg/L | 9 | 79 | 250 | 289 | -15.6 | 88.6076 | 269.4201 | 96.6595 | Total dissolved solids | mg/L | 16 | 63 | 154 | 211.8333 | -37.5541 | 74.6032 | 197.9345 | 91.9165 | Total dissolved solids | mg/L | 17 | 73 | 228 | 297 | -30.2632 | 76.7123 | 277.249 | 93.8683 | Total dissolved solids | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | NA
|  |  | Net driving pressure at the design flux, NDP (psi) | 131 |  | Recycle ratio, r | 4.2821 |  | Dissolved aluminum (mg/L) | 0.12 |  | 12 | 1999-02-20 | 16:00:00pm | 262 | 16.92 | 163.74 | 161.45 | 29.37 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.7982 | 2.3299 | 130.8951 | 0.10541 | 4.61 | 4.17 | 4.31 | 1.375 | 61.554 | 238.896 | 252.5569 | -5.7184 | 97.7662 | 234.3662 | 99.4133 | [16 empty] | Total hardness | mg/L as CaCO3 | 1 | 26 | 104 | 105.1667 | -1.1218 | 96.1538 | 97.2992 | 98.9722 |  | Total hardness | mg/L as CaCO3 | 1 | 27 | 94 | 105 | -11.7021 | 96.2963 | 97.7275 | 98.9767 | Total hardness | mg/L as CaCO3 | 1 | 27 | 91 | 109.3333 | -20.1465 | 96.2963 | 101.6446 | 99.0162 | Total hardness | mg/L as CaCO3 | 2 | 33 | 106 | 157 | -48.1132 | 93.9394 | 146.0664 | 98.6308 | Total hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 1 | 26 | NA | 87.2069 | #VALUE! | 96.1538 | 81.3777 | 98.7712 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.090525 |  | 1: Flow rates and pressures may need to be adjusted in order to obtain |  |  | Total aluminum (mg/L) | 0.38 |  | 13 | 1999-02-21 | 16:00:00pm | 285 | 16.77 | 163.89 | 161.76 | 28.88 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36621 | 0.72277 | 4.0396 | 12.3671 | 13.8728 | 1.9799 | 131.9651 | 0.10512 | 4.6 | 3.91 | 4.03 | 1.605 | 60.732 | 252.448 | 214.8845 | 14.8797 | 97.3572 | 199.5904 | 99.1959 | [16 empty] | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 59 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Calcium hardness | mg/L as CaCO3 | BMRL | 14 | 53 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 58 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | 67 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 15 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 0.49
FAX Number |  |  | Temperature at which the MTCW was determined, ToC (oC) | 17.4 |  | the desired operating conditions. |  |  | Fluoride (mg/L) | ND |  | 14 | 1999-02-22 | 16:00:00pm | 309 | 16.44 | 164.04 | 161.45 | 28.61 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 14.0386 | 2.266 | 131.869 | 0.10646 | 4.6 | 3.9 | 3.96 | 1.375 | 59.904 | 256.112 | 245.67 | 4.0771 | 97.7047 | 227.978 | 99.3969 | [16 empty] | Turbidity | ntu | 0.06 | 0.09 | 0.16 | 0.185 | -15.625 | 33.3333 | 0.17556 | 65.8235 |  | Turbidity | ntu | 0.08 | 0.1 | 0.23 | 0.16 | 30.4348 | 20 | 0.15441 | 48.1885 | Turbidity | ntu | 0.1 | 0.13 | 0.27 | 0.225 | 16.6667 | 23.0769 | 0.21613 | 53.7312 | Turbidity | ntu | 0.16 | 0.13 | 0.21 | 0.01 | 95.2381 | -23.0769 | 0.020581 | -677.4194 | Turbidity | ntu | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 0.11 | NA | 0.23241 | #VALUE! | 45.4545 | 0.22076 | 72.8206 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  |  | Maximum flow rate to the element, QI, max (gpm) | 20 |  | 2: The design influent flow rate must be within the range established by the |  |  | Sulfate (mg/L) | 13.2 |  | 15 | 1999-02-23 | 16:00:00pm | 333 | 15.58 | 164.5 | 162.82 | 30.65 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 13.4901 | 2.2354 | 130.7746 | 0.10316 | 4.65 | 3.89 | 4 | 2.75 | 63.48 | 255.016 | 243.0296 | 4.7003 | 95.6679 | 226.2888 | 98.7847 | [16 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | 0.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  | Minimum flow rate to the element, QI, min (gpm) | 12 |  | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  |  | Calcium (mg/L) | 8.4 |  | 16 | 1999-02-24 | 16:00:00pm | 357 | 15.05 | 164.96 | 162.67 | 29.58 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 13.7523 | 2.3332 | 131.9018 | 0.10426 | 4.64 | 4.03 | 4.15 | 0.915 | 64.302 | 256.112 | 251.707 | 1.7199 | 98.577 | 234.2338 | 99.6094 | [16 empty] | Total organic carbon | mg/L | BMRL | 2.44 | 9.46 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | Total organic carbon | mg/L | BMRL | 2.47 | 8.52 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.39 | 8.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.65 | 9.89 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | 37th Street WTP |  | Total width of all membrane envelopes in the element, w (ft) | 12.32 |  |  |  |  | Barium (mg/L) | 0.037 |  | 17 | 1999-02-25 | 16:00:00pm | 381 | 14.21 | 165.27 | 163.13 | 29.74 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35575 | 0.8 | 4.8 | 11.52 | 14.1806 | 2.8485 | 131.6115 | 0.10775 | 4.61 | 3.72 | 3.83 | 2.29 | 63.48 | 275.896 | 308.24 | -11.7233 | 96.3926 | 287.14 | 99.2025 | [16 empty] | UV254 | cm-1 | BMRL | 0.039 | 0.154 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | UV254 | cm-1 | BMRL | 0.036 | 0.136 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.033 | 0.129 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.034 | 0.155 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.039 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Treatment Plant Category | Conventional |  | Feed spacer thickness, T (ft) | 0.0023333 |  | Estimate the Osmotic Pressure Gradient |  |  | Strontium (mg/L) | 0.051 |  | 18 | 1999-02-26 | 16:00:00pm | 405 | 15.46 | 164.2 | 163.89 | 29.34 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 13.5489 | 2.2877 | 132.4173 | 0.10232 | 4.6 | 3.83 | 3.93 | 1.605 | 63.756 | 270.04 | 247.5068 | 8.3444 | 97.4826 | 230.3743 | 99.3033 | [16 empty] | SUVA | L/(mg*m) | NR | 1.5984 | 1.6279 | --- | --- | --- | --- | --- |  | SUVA | L/(mg*m) | NR | 1.4575 | 1.5962 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.3808 | 1.5674 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.283 | 1.5672 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NA | NA | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 1.56 | #VALUE! | --- | --- | --- | --- | ---
Process Train Name | West |  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 |  | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.7 |  | Reactive silica (mg/L as SiO2) | 3.7 |  | 19 | 1999-02-27 | 16:00:00pm | 429 | 15.55 | 164.35 | 162.06 | 29.71 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35575 | 0.8 | 4.8 | 11.52 | 13.5047 | 2.8571 | 130.6379 | 0.10338 | 4.62 | 3.73 | 3.79 | 1.83 | 63.204 | 282.864 | 308.7 | -9.1337 | 97.1046 | 287.5366 | 99.3636 | [16 empty] | Bromide | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | Bromide | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | 30 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 677 |  | Purchase price for an equivalent 8" x 40 " element ($) | 900 |  | Feed TDS, TDSF (mg/L) | 70 |  |  |  |  | 20 | 1999-02-28 | 16:00:00pm | 453 | 15.61 | 163.43 | 162.37 | 29.74 | 3.97 | 0.68 | 0.17 |  | 0.85 | 4.82 | 0.34722 | 0.8 | 4.6706 | 11.52 | 13.4754 | 2.7606 | 130.3994 | 0.10334 | 4.67 | 4.19 | 4.35 | 1.605 | 61.008 | 268.208 | 298.62 | -11.339 | 97.3692 | 277.6687 | 99.422 | [16 empty] | SDS-Cl2 dose | mg/L | 1.86 | 3.72 | --- | --- | --- | --- | --- | --- |  | SDS-Cl2 dose | mg/L | 1.6 | 3.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.67 | 3.33 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.73 | 3.45 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.86 | 3.72 | NA | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | VA3710150 |  |  |  |  | Waste TDS, TDSW (mg/L) | 154.99 |  |  |  |  | 21 | 36163 | 16:00:00pm | 477 | 15.81 | 163.28 | 160.99 | 30.1 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 13.3781 | 2.2001 | 129.8349 | 0.10304 | 4.65 | 4.08 | 4.2 | 1.605 | 61.278 | 245.488 | 237.7025 | 3.1714 | 97.3808 | 221.6157 | 99.2758 | [16 empty] | SDS-Free Cl2 residual | mg/L | 1.3 | 1.32 | --- | --- | --- | --- | --- | --- |  | SDS-Free Cl2 residual | mg/L | 1.32 | 1.52 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.26 | 1.37 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | 1.27 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.16 | 1.35 | NA | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 9 |  | Additional Information |  |  | Permeate TDS, TDSp (mg/L) | 41.67 |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  | 22 | 36194 | 16:00:00pm | 501 | 16.08 | 164.35 | 162.98 | 31.08 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 13.2481 | 2.2628 | 130.3222 | 0.10166 | 4.63 | 3.76 | 3.8 | 1.83 | 63.204 | 270.768 | 244.6576 | 9.6431 | 97.1046 | 228.1122 | 99.1978 | [16 empty] | SDS-Cl2 demand | mg/L | 0.56 | 2.4 | --- | 8.2267 | --- | 76.6667 | 7.6476 | 92.6775 |  | SDS-Cl2 demand | mg/L | 0.28 | 1.68 | --- | 5.88 | --- | 83.3333 | 5.4884 | 94.8983 | SDS-Cl2 demand | mg/L | 0.41 | 1.96 | --- | 6.8683 | --- | 79.0816 | 6.41 | 93.6037 | SDS-Cl2 demand | mg/L | 0.43 | 2.18 | --- | 9.18 | --- | 80.2752 | 8.5628 | 94.9783 | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 0.7 | 2.37 | NA | 6.4586 | --- | 70.4641 | 6.0692 | 88.4664
Historical Average Water Temperature (oC) | 32 |  | Design cross-flow velocity (fps) | 0.35497 |  | Influent TDS, TDSI (mg/L) | 138.9 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  | 23 | 36222 | 16:00:00pm | 525 | 16.59 | 163.74 | 161.45 | 31.45 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.9629 | 2.2767 | 128.8683 | 0.10835 | 4.62 | 4 | 4.07 | 1.375 | 60.18 | 270.4 | 246.822 | 8.7197 | 97.7152 | 229.0465 | 99.3997 | [16 empty] | SDS-Chlorination temp. | oC | 15.6 | 15.2 | --- | --- | --- | --- | --- | --- |  | SDS-Chlorination temp. | oC | 14.7 | 14.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 15.6 | 15.7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 17.8 | 17.7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 16 | 15.4 | NA | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 28 |  | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 |  | Osmotic pressure gradient, Dp (psi) | 1.0528 |  |  |  |  | 24 | 36253 | 16:00:00pm | 548 | 16.05 | 164.04 | 161.3 | 30.74 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 14.2376 | 2.4498 | 129.4802 | 0.10996 | 4.59 | 3.73 | 3.8 | 2.29 | 65.676 | 255.016 | 266.8577 | -4.6435 | 96.5132 | 247.27 | 99.0739 | [16 empty] | SDS-Chlorination pH | --- | 7.09 | 6.98 | --- | --- | --- | --- | --- | --- |  | SDS-Chlorination pH | --- | 6.91 | 6.95 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.01 | 6.94 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.06 | 6.99 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7 | 7.02 | NA | --- | --- | --- | --- | ---
|  |  | Maximum element recovery (%) | 15 | [7 empty] | 25 | 36283 | 16:00:00pm | 572 | 16.63 | 164.5 | 162.67 | 31.05 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.9428 | 2.3141 | 130.2209 | 0.10707 | 4.64 | 3.92 | 3.98 | 2.06 | 61.83 | 252.816 | 251.5348 | 0.50678 | 96.6683 | 233.4677 | 99.1177 | [16 empty] | SDS-Incubation time | hours | 23.6667 | 23.4167 | --- | --- | --- | --- | --- | --- |  | SDS-Incubation time | hours | 24.0833 | 23.8333 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.25 | 24.0833 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24.0833 | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 23.6667 | 23.4167 | NA | --- | --- | --- | --- | ---
|  |  | Variability of design flux (%) | 15 |  | Estimate the Required Influent Pressure | [5 empty] | 26 | 36314 | 16:00:00pm | 596 | 16.66 | 163.13 | 161.6 | 29.98 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36621 | 0.72277 | 4.0396 | 12.3671 | 13.9278 | 2.0259 | 130.3591 | 0.10684 | 4.69 | 4.61 | 4.81 | 1.605 | 62.106 | 211.776 | 219.8408 | -3.8082 | 97.4157 | 204.1912 | 99.214 | [16 empty] | SDS-TOX | mg Cl- /L | BMRL | 113.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-TOX | mg Cl- /L | BMRL | 121.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 139.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 150.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | 120.8 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Rejection of reference solute and conditions of test | 99% |  | Estimated system pressure losses, DPloss (psi) | 2 |  |  |  |  | 27 | 36344 | 16:00:00pm | 620 | 16.62 | 164.04 | 162.21 | 30.47 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.9479 | 2.4399 | 130.2151 | 0.10711 | 4.63 | 3.92 | 4 | 0.46 | 63.48 | 242.92 | 263.5 | -8.4719 | 99.2754 | 244.4505 | 99.8118 | [16 empty] | SDS-CHCl3 | mg/L | 1 | 27.2 | --- | 110.1667 | --- | 96.3235 | 101.9215 | 99.0189 |  | SDS-CHCl3 | mg/L | 1.1 | 26.2 | --- | 101.5 | --- | 95.8015 | 94.4792 | 98.8357 | SDS-CHCl3 | mg/L | 0.8 | 28.6 | --- | 116.6333 | --- | 97.2028 | 108.4123 | 99.2621 | SDS-CHCl3 | mg/L | 1 | 37.4 | --- | 183 | --- | 97.3262 | 170.1618 | 99.4123 | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 0.9 | 25.2 | NA | 84.6931 | --- | 96.4286 | 79.0271 | 98.8612
|  |  | (e.g., solute type and concentration) | (1500 ppm NaCl) |  | Design permeate pressure, Pp (psi) | 30 |  |  |  |  | 28 | 36375 | 16:00:00pm | 642 | 16.5 | 159.92 | 158.09 | 31.96 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 13.0488 | 2.0905 | 124.9545 | 0.10443 | 4.68 | 4.19 | 4.3 | 1.83 | 58.53 | 222.408 | 226.1648 | -1.6891 | 96.8734 | 210.8794 | 99.1322 | [16 empty] | SDS-BDCM | mg/L | BMRL | 7.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-BDCM | mg/L | 1.8 | 7 | --- | 22.6 | --- | 74.2857 | 21.1455 | 91.4875 | SDS-BDCM | mg/L | 1.8 | 6.9 | --- | 23.05 | --- | 73.913 | 21.5418 | 91.6442 | SDS-BDCM | mg/L | 1.9 | 5.6 | --- | 20.4 | --- | 66.0714 | 19.095 | 90.0498 | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | 7.6 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Variability of rejection of reference solute (%) | 6.7 |  | Required influent pressure, PI (psi) | 154.3622 |  |  |  |  | 29 | 36406 | 16:00:00pm | 666 | 15.9 | 159.01 | 156.72 | 30.84 | 3.97 | 0.63 | 0.23 |  | 0.86 | 4.83 | 0.34993 | 0.73256 | 4.6163 | 10.6729 | 12.3541 | 2.1898 | 124.8352 | 0.098963 | 4.66 | 3.93 | 4.06 | 1.375 | 64.026 | 240.728 | 235.6353 | 2.1156 | 97.8524 | 220.3574 | 99.376 | [16 empty] | SDS-DBCM | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-DBCM | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 2.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | 2.9 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing recovery (%) | 15 | [7 empty] | 30 | 36436 | 16:00:00pm | 690 | 16.1 | 159.77 | 158.4 | 30.84 | 4.08 | 0.68 | 0.17 |  | 0.85 | 4.93 | 0.35575 | 0.8 | 4.8 | 11.52 | 13.2385 | 2.8633 | 125.3817 | 0.10559 | 4.64 | 3.83 | 3.97 | 1.145 | 62.652 | 251.72 | 308.68 | -22.6283 | 98.1724 | 287.4707 | 99.6017 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | 0.5 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Standard testing pH | 6.5 - 7.0 | [7 empty] | 31 | 36467 | 16:00:00pm | 714 | 15.41 | 163.13 | 161.76 | 30.9 | 4.08 | 0.63 | 0.23 |  | 0.86 | 4.94 | 0.35846 | 0.73256 | 4.7442 | 10.6729 | 12.5755 | 2.1131 | 129.4319 | 0.097159 | 4.64 | 4.09 | 4.23 | 0.915 | 61.278 | 253.552 | 226.6201 | 10.6218 | 98.5068 | 212.228 | 99.5689 | [16 empty] | SDS-THM4 | mg/L | 1 | 37.8 | --- | 154.3333 | --- | 97.3545 | 142.7524 | 99.2995 |  | SDS-THM4 | mg/L | 2.9 | 36.4 | --- | 136.9 | --- | 92.033 | 127.5296 | 97.726 | SDS-THM4 | mg/L | 2.6 | 38.3 | --- | 151.35 | --- | 93.2115 | 140.7928 | 98.1533 | SDS-THM4 | mg/L | 2.9 | 46 | --- | 218.4 | --- | 93.6957 | 203.1988 | 98.5728 | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 0.9 | 36.2 | NA | 122.6241 | --- | 97.5138 | 114.3933 | 99.2132
|  |  | Acceptable range of operating pressures | 600 psig max. | [7 empty] | 32 | 36497 | 16:00:00pm | 738 | 15.89 | 162.67 | 161.3 | 31.02 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 13.3394 | 2.1495 | 128.8155 | 0.10355 | 4.63 | 4.25 | 4.38 | 2.06 | 60.456 | 253.552 | 233.105 | 8.0642 | 96.5926 | 217.0076 | 99.0507 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Acceptable range of operating pH values | 3.0 - 10.0 | [7 empty] | 33 | 1999-03-13 | 16:00:00pm | 762 | 15.95 | 165.11 | 163.59 | 31.57 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.36427 | 0.70833 | 4.25 | 11.52 | 13.3105 | 1.9037 | 130.8763 | 0.1017 | 4.61 | 4.04 | 4.17 | 2.29 | 61.83 | 222.768 | 206.4271 | 7.3354 | 96.2963 | 192.656 | 98.8114 | [16 empty] | SDS-DCAA* | mg/L | BMRL | 11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-DCAA* | mg/L | BMRL | 9.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 9.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NA | 12 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Typical pressure drop across a single element (psi) | [8 empty] | 34 | 1999-03-14 | 16:00:00pm | 783 | 15.61 | 169.23 | 168.01 | 32.45 | 4.18 | 0.68 | 0.34 |  | 1.02 | 5.2 | 0.37667 | 0.66667 | 4.098 | 11.52 | 13.4754 | 1.7863 | 134.3837 | 0.10028 | 4.64 | 4 | 4.13 | 1.145 | 64.854 | 213.608 | 192.272 | 9.9884 | 98.2345 | 179.7752 | 99.3631 | [16 empty] | SDS-TCAA* | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-TCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | 18 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible SDI | 5 | [7 empty] | 35 | 1999-03-15 | 16:00:00pm | 807 | 15.75 | 170 | 166.64 | 32.39 | 4.18 | 0.73 | 0.23 |  | 0.96 | 5.14 | 0.37009 | 0.76042 | 4.3542 | 12.3671 | 14.393 | 2.3442 | 133.5858 | 0.10774 | 4.59 | 3.85 | 3.96 | 1.375 | 61.83 | 243.656 | 253.7089 | -4.1259 | 97.7762 | 235.7903 | 99.4169 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | BMRL | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 36 | 1999-03-16 | 16:00:00pm | 831 | 15.49 | 170.15 | 168.01 | 32.82 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 13.5342 | 2.0449 | 134.2151 | 0.10084 | 4.62 | 4.06 | 4.18 | 2.52 | 57.984 | 255.016 | 221.9645 | 12.9606 | 95.654 | 207.0124 | 98.7827 | [16 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | BMRL | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <1.0 mg/L | [7 empty] | 37 | 1999-03-17 | 16:00:00pm | 855 | 17.01 | 169.69 | 169.39 | 34.07 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.7536 | 2.3956 | 133.0744 | 0.10335 | 4.63 | 3.75 | 3.82 | 1.605 | 63.48 | 275.168 | 259.8659 | 5.561 | 97.4716 | 241.1625 | 99.3345 | [16 empty] | SDS-BCAA* | mg/L | BMRL | 3.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-BCAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 2.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | 3.2 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 38 | 1999-03-18 | 16:00:00pm | 879 | 16.97 | 168.62 | 167.55 | 30.93 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.7734 | 2.4488 | 134.7062 | 0.10225 | 4.64 | 3.89 | 3.94 | 1.605 | 64.854 | 250.616 | 265.6008 | -5.9792 | 97.5252 | 246.4821 | 99.3488 | [16 empty] | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | BMRL | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 39 | 1999-03-19 | 16:00:00pm | 903 | 16.63 | 168.62 | 166.03 | 30.74 | 4.18 | 0.73 | 0.23 |  | 0.96 | 5.14 | 0.37009 | 0.76042 | 4.3542 | 12.3671 | 13.9428 | 2.2839 | 134.3011 | 0.10382 | 4.64 | 4.38 | 4.5 | 1.83 | 60.732 | 258.68 | 247.6818 | 4.2517 | 96.9868 | 230.2235 | 99.2051 | [16 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | 2.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | BMRL | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 40 | 1999-03-20 | 15:30:00pm | 926 | 17.32 | 167.86 | 165.88 | 30.8 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.6016 | 2.323 | 133.747 | 0.1017 | 4.65 | 4.25 | 4.36 | 1.83 | 61.83 | 261.608 | 252.2648 | 3.5715 | 97.0403 | 234.1281 | 99.2184 | [16 empty] | SDS-DCBAA | mg/L | BMRL | 5.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | 1 | SDS-DCBAA | mg/L | BMRL | 6.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 5.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | 6.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | 6.1 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Field 1-5: Pretreatment Used Prior To Membranes1 | [11 empty] | 41 | 1999-03-21 | 16:00:00pm | 951 | 16.94 | 163.89 | 163.74 | 29.8 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.7883 | 2.3673 | 131.6477 | 0.10474 | 4.61 | 3.94 | 4.05 | 2.06 | 63.204 | 256.848 | 257.2697 | -0.1642 | 96.7407 | 238.7873 | 99.1373 | [16 empty] | SDS-HAA5 | mg/L | 0 | 28 | --- | 116.6667 | --- | 100 | 107.8551 | 100 |  | SDS-HAA5 | mg/L | 0 | 25.3 | --- | 101.2 | --- | 100 | 94.1233 | 100 | SDS-HAA5 | mg/L | 0 | 25.4 | --- | 105.8333 | --- | 100 | 98.322 | 100 | SDS-HAA5 | mg/L | 0 | 31 | --- | 155 | --- | 100 | 144.0664 | 100 | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NA | 30 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[12 empty] | 42 | 1999-03-22 | 16:00:00pm | 975 | 17.12 | 164.66 | 161.6 | 29.86 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.6994 | 2.3938 | 130.8762 | 0.10467 | 4.59 | 4.01 | 4.12 | 1.375 | 63.204 | 268.936 | 259.4439 | 3.5295 | 97.8245 | 240.7544 | 99.4289 | [16 empty] | SDS-HAA6 | mg/L | 0 | 31.1 | --- | 129.5833 | --- | 100 | 119.7962 | 100 |  | SDS-HAA6 | mg/L | 0 | 28.3 | --- | 113.2 | --- | 100 | 105.2841 | 100 | SDS-HAA6 | mg/L | 0 | 28 | --- | 116.6667 | --- | 100 | 108.3865 | 100 | SDS-HAA6 | mg/L | 0 | 34.1 | --- | 170.5 | --- | 100 | 158.473 | 100 | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NA | 33.2 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Process | Description | [8 empty] | Scale |  | 43 | 1999-03-23 | 16:00:00pm | 999 | 17.59 | 163.59 | 161.91 | 30.04 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36621 | 0.72277 | 4.0396 | 12.3671 | 13.4707 | 1.9739 | 130.7361 | 0.10304 | 4.67 | 4.1 | 4.21 | 2.06 | 61.008 | 233.4 | 214.6939 | 8.0146 | 96.6234 | 199.446 | 98.9671 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [10 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Rapid Mix | Type: | Mechanical | [7 empty] | Full |  | 44 | 1999-03-24 | 16:00:00pm | 1023 | 18.33 | 162.82 | 161.45 | 29.95 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 13.1198 | 2.3012 | 129.8838 | 0.10101 | 4.66 | 4.16 | 4.27 | 0.915 | 60.456 | 246.224 | 249.434 | -1.3037 | 98.4865 | 231.0345 | 99.604 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [10 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
| Chemical Name: | Alum |  |  |  | Powdered Activated Carbon (PAC) | [5 empty] | 45 | 1999-03-25 | 16:00:00pm | 1047 | 17.85 | 162.98 | 161.91 | 31.75 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.3462 | 2.3281 | 128.3669 | 0.10397 | 4.65 | 3.86 | 3.97 | 2.52 | 62.652 | 253.552 | 253.5057 | 0.018245 | 95.9778 | 235.3292 | 98.9292 | [67 empty] | 1 HAA Permeate Data Collected on 2/17/99
| Chemical Formula: | Al2(SO4)3*14H2O | [9 empty] | 46 | 1999-03-26 | 16:00:00pm | 1071 | 17.84 | 163.89 | 161.6 | 32.09 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 12.4365 | 2.1444 | 128.5106 | 0.096774 | 4.63 | 3.94 | 4.04 | 1.375 | 59.634 | 263.072 | 231.878 | 11.8576 | 97.6943 | 215.8184 | 99.3629 | [27 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
| Dose: | AVG | MAX | MIN | STD DEV | AVG | MAX | MIN | STD DEV |  |  | 47 | 1999-03-27 | 16:00:00pm | 1095 | 17.26 | 163.89 | 163.13 | 30.84 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 13.6308 | 2.3083 | 130.3617 | 0.10456 | 4.66 | 4.17 | 4.35 | 1.83 | 61.554 | 235.592 | 251.1128 | -6.588 | 97.027 | 232.6568 | 99.2134 | [16 empty] | Blending Calculations For D-DBP MCLs | [11 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Blending Calculations For D-DBP MCLs
|  | 25.2 | 27.7 | 21.7 | 1.35 | 3.2 | 5.7 | 0.64 | 1.56 |  |  | 48 | 1999-03-28 | 16:00:00pm | 1119 | 18.3 | 163.74 | 161.45 | 32.94 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 13.1338 | 2.2569 | 127.3981 | 0.10309 | 4.62 | 3.86 | 3.96 | 2.06 | 60.456 | 264.544 | 245.7998 | 7.0855 | 96.5926 | 227.7542 | 99.0955 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [6 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | THM4 Controls |  |  |  | HAA5 Controls
Flocculation | Type: | Mechanical | [7 empty] | Full |  | 49 | 1999-03-29 | 16:00:00pm | 1143 | 17.78 | 164.04 | 163.13 | 32.06 | 3.97 | 0.73 | 0.17 |  | 0.9 | 4.87 | 0.34916 | 0.81111 | 4.4111 | 12.3671 | 13.3796 | 2.9384 | 128.5866 | 0.10405 | 4.58 | 3.74 | 3.81 | 1.83 | 61.83 | 303.744 | 319.4771 | -5.1797 | 97.0403 | 295.6698 | 99.3811 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Qp/QT (THM4), % | -106.2687 | 1.194 |  | Qp/QT (HAA5), % | -113.4387 | -6.7194 |  |  |  | Qp/QT (THM4), % | -94.3978 | 6.4426 |  | Qp/QT (HAA5), % | -112.5984 | -6.2992 |  |  |  | Qp/QT (THM4), % | -60.3248 | 23.2019 |  | Qp/QT (HAA5), % | -74.1935 | 12.9032 |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
Sedimentation | Type: | Conventional | [7 empty] | Full |  | 50 | 1999-03-30 | 16:00:00pm | 1167 | 17.64 | 163.43 | 160.08 | 31.72 | 3.97 | 0.73 | 0.28 |  | 1.01 | 4.98 | 0.35769 | 0.72277 | 3.9307 | 12.3671 | 13.4467 | 2.116 | 127.919 | 0.10512 | 4.63 | 3.8 | 3.89 | 1.83 | 65.13 | 272.6 | 230.1621 | 15.5678 | 97.1902 | 213.427 | 99.1426 | [16 empty] | Qp/QT (THM4), % | -92.9348 | 4.8913 |  | Qp/QT (HAA5), % | -92.8571 | 3.5714 |  |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 40.4387 |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | -101.4164 | 0.56657 |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
Filtration | Type: | Dual Media - Anthracite/Sand | [7 empty] | Pilot |  | 51 | 1999-03-31 | 16:00:00pm | 1191 | 17.52 | 162.82 | 160.08 | 31.75 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.5045 | 2.167 | 127.533 | 0.10589 | 4.62 | 3.98 | 4.09 | 2.29 | 58.26 | 260.144 | 235.9039 | 9.3179 | 96.0693 | 218.9854 | 98.9543 | [16 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 36.4857 |  |  |  |  | SDS-HAA5b, mg/L | NA | 24.9979 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 23.7636 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | NA | 23.8074 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[12 empty] | 52 | 36164 | 16:00:00pm | 1215 | 17.9 | 163.13 | 160.54 | 31.6 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 13.3224 | 2.252 | 127.983 | 0.10409 | 4.66 | 4.13 | 4.27 | 0.915 | 59.082 | 246.224 | 243.699 | 1.0255 | 98.4513 | 226.1164 | 99.5953 | [16 empty] | SDS-HAA5b, mg/L | NA | 26.6304 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | NA | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in | [11 empty] | 53 | 36195 | 16:00:00pm | 1239 | 18.39 | 164.04 | 161.76 | 32.09 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 13.0918 | 2.3614 | 128.4486 | 0.10192 | 4.59 | 3.9 | 4 | 1.83 | 62.928 | 264.904 | 256.8477 | 3.0412 | 97.0919 | 237.9671 | 99.231 | [16 empty] | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  |  | SDS-CDb, mg/L | NA | 1.6633 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.8601 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | NA | 1.774 |  | SDS-CDb, mg/L | NA | 1.9542 |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table | [11 empty] | 54 | 36223 | 16:00:00pm | 1263 | 17.98 | 164.5 | 161.3 | 31.54 | 3.97 | 0.73 | 0.28 |  | 1.01 | 4.98 | 0.35769 | 0.72277 | 3.9307 | 12.3671 | 13.2844 | 2.0637 | 129.2963 | 0.10274 | 4.64 | 4.08 | 4.24 | 2.29 | 64.026 | 243.656 | 224.9806 | 7.6647 | 96.4233 | 208.6589 | 98.9025 | [16 empty] | SDS-CDb, mg/L | NA | 2.31 |  | SDS-CDb, mg/L | NA | 2.3343 |  |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | NA | 2.3605 |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
is to list the pretreatment processes used in this particular Long-Term SEBST run. | [11 empty] | 55 | 36254 | 16:00:00pm | 1287 | 20.16 | 162.37 | 162.21 | 32.88 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 12.2977 | 2.2074 | 127.2026 | 0.096678 | 4.71 | 4.12 | 4.2 | 1.145 | 58.26 | 253.912 | 239.538 | 5.661 | 98.0347 | 221.8883 | 99.484 | [16 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[12 empty] | 56 | 36284 | 16:00:00pm | 1311 | 18.05 | 164.2 | 162.06 | 32.36 | 4.08 | 0.73 | 0.17 |  | 0.9 | 4.98 | 0.35769 | 0.81111 | 4.5333 | 12.3671 | 13.2513 | 2.9369 | 127.8331 | 0.10366 | 4.62 | 4.1 | 4.21 | 1.145 | 61.008 | 275.536 | 318.0668 | -15.4356 | 98.1232 | 294.8386 | 99.6117 | [16 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[12 empty] | 57 | 36315 | 9:00:00am | 1328 | 18.74 | 164.35 | 162.98 | 29.1 | 3.97 | 0.68 | 0.17 | X | 0.85 | 4.82 | 0.34722 | 0.8 | 4.6706 | 11.52 | 12.0444 | 2.5944 | 131.9706 | 0.091266 | 4.69 | 6.02 | 6.33 | 1.605 | 57.432 | 248.056 | 280.74 | -13.1761 | 97.2054 | 261.05 | 99.3852 | [16 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  |  | Alkb, mg/L CaCO3 | NA | 1 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 1 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | NA | 3.768 |  | Alkb, mg/L CaCO3 | NA | 3.871 |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[12 empty] | 58 | 36345 | 16:00:00pm | 1356 | 19.75 | 150.92 | 148.63 | 30.68 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 11.6218 | 2.1935 | 116.9015 | 0.099416 | 4.71 | 5.98 | 6.34 | 0.685 | 60.18 | 228.632 | 236.0783 | -3.2569 | 98.8617 | 220.0394 | 99.6887 | [16 empty] | Alkb, mg/L CaCO3 | NA | 2.9022 |  | Alkb, mg/L CaCO3 | NA | 2.9286 |  |  |  |  | T-Hdb, mg/L CaCO3 | NA | 26.6896 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 25.3249 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | NA | 25.8074 |  | T-Hdb, mg/L CaCO3 | NA | 29 |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | NA | 2.9887 |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[12 empty] | 59 | 36376 | 16:00:00pm | 1380 | 21.68 | 150.16 | 147.11 | 31.75 | 4.18 | 0.73 | 0.17 |  | 0.9 | 5.08 | 0.36544 | 0.81111 | 4.6444 | 12.3671 | 11.6613 | 2.6308 | 114.2542 | 0.10206 | 4.77 | 6.09 | 6.37 | 1.145 | 54.684 | 239.992 | 284.5868 | -18.5818 | 97.9062 | 264.2214 | 99.5667 | [16 empty] | T-Hdb, mg/L CaCO3 | NA | 24.7772 |  | T-Hdb, mg/L CaCO3 | NA | 25.1071 |  |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | NA | 25.8584 |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[12 empty] | 60 | 36407 | 16:00:00pm | 1404 | 21.81 | 150.46 | 149.85 | 32.76 | 4.08 | 0.78 | 0.23 |  | 1.01 | 5.09 | 0.36427 | 0.77228 | 4.0396 | 13.2141 | 12.4038 | 2.2805 | 115.1145 | 0.10775 | 4.81 | 6.04 | 6.34 | 0.915 | 57.156 | 224.6 | 247.8863 | -10.3679 | 98.3991 | 228.9632 | 99.6004 | [16 empty] | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  |  | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Ca-Hdb, mg/L CaCO3 | NA | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[12 empty] | 61 | 36437 | 16:00:00pm | 1428 | 19.81 | 150.16 | 147.72 | 30.8 | 4.08 | 0.73 | 0.4 |  | 1.13 | 5.21 | 0.37551 | 0.64602 | 3.6106 | 12.3671 | 12.45 | 1.4955 | 116.6445 | 0.10673 | 4.71 | 5.8 | 6.14 | 1.605 | 58.53 | 169.64 | 162.4181 | 4.2572 | 97.2578 | 151.1519 | 98.9382 | [27 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[12 empty] | 62 | 36468 | 16:00:00pm | 1450 | 19.07 | 151.68 | 150.01 | 30.8 | 4.08 | 0.73 | 0.28 |  | 1.01 | 5.09 | 0.36621 | 0.72277 | 4.0396 | 12.3671 | 12.7797 | 1.8742 | 118.1708 | 0.10815 | 4.7 | 5.94 | 6.31 | 0.915 | 56.886 | 212.144 | 202.8104 | 4.3997 | 98.3915 | 188.3326 | 99.5142 | [16 empty] | Notes: | [10 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | Notes:
[12 empty] | 63 | 36498 | 16:00:00pm | 1473 | 19.46 | 152.45 | 149.85 | 30.99 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 12.6047 | 2.1401 | 118.0199 | 0.1068 | 4.51 | 5.97 | 6.24 | 0.685 | 56.058 | 229.368 | 231.8071 | -1.0634 | 98.7781 | 214.6956 | 99.6809 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [10 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[12 empty] | 64 | 1999-04-13 | 16:00:00pm | 1497 | 19.15 | 151.84 | 150.16 | 30.71 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 12.7435 | 2.133 | 118.157 | 0.10785 | 4.71 | 6.1 | 6.4 | 1.145 | 56.334 | 204.088 | 231.4991 | -13.431 | 97.9675 | 214.4445 | 99.4661 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [10 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[12 empty] | 65 | 1999-04-14 | 16:00:00pm | 1521 | 19.79 | 152.29 | 150.16 | 30.9 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 12.4588 | 2.0939 | 118.2311 | 0.10538 | 4.77 | 6.15 | 6.5 | 1.605 | 55.782 | 213.248 | 227.7351 | -6.7935 | 97.1227 | 210.9932 | 99.2393 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [10 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[12 empty] | 66 | 1999-04-15 | 16:00:00pm | 1545 | 20.19 | 151.38 | 148.33 | 30.65 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 12.2847 | 2.0179 | 117.1871 | 0.10483 | 4.78 | 6.17 | 6.51 | 1.375 | 53.586 | 212.88 | 219.2992 | -3.0154 | 97.434 | 203.1648 | 99.3232 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [10 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[12 empty] | 67 | 1999-04-16 | 16:00:00pm | 1569 | 20.94 | 150.62 | 149.4 | 30.56 | 3.97 | 0.73 | 0.23 |  | 0.96 | 4.93 | 0.35381 | 0.76042 | 4.1354 | 12.3671 | 11.9661 | 2.0728 | 117.3772 | 0.10195 | 4.78 | 6.1 | 6.41 | 0.23 | 53.862 | 218.376 | 224.0853 | -2.6144 | 99.573 | 207.5118 | 99.8892 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [10 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[12 empty] | 68 | 1999-04-17 | 16:00:00pm | 1590 | 20.19 | 151.84 | 149.55 | 32.54 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 12.2847 | 2.1508 | 116.0042 | 0.1059 | 4.75 | 6.02 | 6.39 | 0.23 | 55.782 | 223.504 | 232.0992 | -3.8457 | 99.5877 | 215.3071 | 99.8932 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [10 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[12 empty] | 69 | 1999-04-18 | 16:00:00pm | 1614 | 20.28 | 151.23 | 149.7 | 31.66 | 3.97 | 0.68 | 0.28 |  | 0.96 | 4.93 | 0.35575 | 0.70833 | 4.1354 | 11.52 | 11.4072 | 1.7237 | 117.0813 | 0.09743 | 4.73 | 5.99 | 6.35 | 0.685 | 54.684 | 194.192 | 185.8244 | 4.3089 | 98.7473 | 173.0562 | 99.6042 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [10 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[12 empty] | 70 | 1999-04-19 | 16:00:00pm | 1638 | 20.65 | 151.99 | 150.01 | 32.06 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 12.0881 | 2.112 | 116.828 | 0.10347 | 4.69 | 5.86 | 6.2 | 2.06 | 56.61 | 207.384 | 229.747 | -10.7834 | 96.3611 | 213.2577 | 99.034 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [10 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[12 empty] | 71 | 1999-04-20 | 16:00:00pm | 1662 | 20.97 | 151.84 | 148.02 | 31.26 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 11.1348 | 2.0448 | 116.6252 | 0.095475 | 4.7 | 6.01 | 6.4 | 0.23 | 55.782 | 209.584 | 220.0227 | -4.9807 | 99.5877 | 204.7093 | 99.8876 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [50 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[12 empty] | 72 | 1999-04-21 | 16:00:00pm | 1686 | 20.25 | 151.53 | 149.4 | 30.99 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 11.4192 | 1.9858 | 117.4892 | 0.097194 | 4.67 | 5.9 | 6.25 | 1.375 | 55.236 | 207.016 | 214.4772 | -3.6042 | 97.5107 | 199.9572 | 99.3124 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [50 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[12 empty] | 73 | 1999-04-22 | 16:00:00pm | 1710 | 22.05 | 151.07 | 148.33 | 31.69 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 10.7239 | 1.8664 | 116.1436 | 0.092333 | 4.66 | 5.9 | 6.29 | 0.685 | 51.39 | 206.648 | 201.3004 | 2.5878 | 98.6671 | 187.3231 | 99.6343
[12 empty] | 74 | 1999-04-23 | 15:30:00pm | 1734 | 23.03 | 150.31 | 147.87 | 32.42 | 3.87 | 0.68 | 0.23 |  | 0.91 | 4.78 | 0.34412 | 0.74725 | 4.2527 | 11.52 | 10.3666 | 1.914 | 114.756 | 0.090336 | 4.78 | 5.96 | 6.31 | 0.685 | 52.764 | 209.216 | 206.7367 | 1.185 | 98.7018 | 192.0803 | 99.6434
[12 empty] | 75 | 1999-04-24 | 16:00:00pm | 1758 | 22.07 | 151.53 | 149.85 | 32.27 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 11.5044 | 2.0853 | 116.3347 | 0.09889 | 4.74 | 5.87 | 6.3 | 1.375 | 55.236 | 197.12 | 226.1861 | -14.7454 | 97.5107 | 209.9052 | 99.3449
[12 empty] | 76 | 1999-04-25 | 16:00:00pm | 1782 | 21.62 | 152.91 | 151.23 | 32.02 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 11.6856 | 2.112 | 117.938 | 0.099083 | 4.74 | 5.96 | 6.32 | 0.685 | 55.236 | 200.424 | 228.3761 | -13.9465 | 98.7599 | 211.8866 | 99.6767
[12 empty] | 77 | 1999-04-26 | 16:00:00pm | 1806 | 21.97 | 152.14 | 148.94 | 30.77 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 11.5444 | 2.0976 | 117.6724 | 0.098106 | 4.73 | 5.92 | 6.3 | 0.23 | 54.408 | 198.952 | 226.3643 | -13.7783 | 99.5773 | 209.9875 | 99.8905
[12 empty] | 78 | 1999-04-27 | 16:00:00pm | 1821 | 21 | 152.6 | 148.78 | 30.16 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 11.1231 | 1.9708 | 118.5592 | 0.093819 | 4.71 | 5.95 | 6.33 | 0.685 | 54.138 | 196.392 | 212.173 | -8.0354 | 98.7347 | 197.763 | 99.6536
[12 empty] | 79 | 1999-04-28 | 16:00:00pm | 1854 | 21.15 | 152.45 | 150.31 | 29.95 | 4.08 | 0.73 | 0.23 |  | 0.96 | 5.04 | 0.36234 | 0.76042 | 4.25 | 12.3671 | 11.8786 | 2.1774 | 119.2526 | 0.099609 | 4.75 | 5.96 | 6.33 | 0.915 | 57.156 | 201.888 | 235.66 | -16.7281 | 98.3991 | 218.6597 | 99.5815
[12 empty] | 80 | 1999-04-29 | 16:00:00pm | 1878 | 21.32 | 153.67 | 151.23 | 29.43 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 10.9996 | 1.9994 | 121.0206 | 0.09089 | 4.71 | 5.96 | 6.3 | 1.83 | 56.058 | 201.152 | 216.3843 | -7.5725 | 96.7355 | 201.7653 | 99.093
[12 empty] | 81 | 1999-04-30 | 16:00:00pm | 1902 | 20.94 | 152.6 | 150.62 | 28.85 | 3.97 | 0.68 | 0.23 |  | 0.91 | 4.88 | 0.35187 | 0.74725 | 4.3626 | 11.52 | 11.1465 | 1.9658 | 120.7942 | 0.092277 | 4.7 | 6.02 | 6.33 | 1.83 | 55.236 | 199.688 | 213.132 | -6.7325 | 96.6869 | 198.4101 | 99.0777
[12 empty] | 82 | 36165 | 16:00:00pm | 1926 | 20.91 | 160.23 | 156.72 | 30.23 | 4.08 | 0.68 | 0.28 |  | 0.96 | 5.04 | 0.36427 | 0.70833 | 4.25 | 11.52 | 11.1582 | 1.7513 | 126.4937 | 0.088211 | 4.73 | 5.95 | 6.36 | 0.46 | 55.236 | 180.632 | 188.2634 | -4.2248 | 99.1672 | 175.5941 | 99.738
[12 empty] | 83 | 36196 | 16:00:00pm | 1950 | 20.25 | 160.23 | 157.18 | 28.91 | 4.08 | 0.68 | 0.23 |  | 0.91 | 4.99 | 0.3604 | 0.74725 | 4.4835 | 11.52 | 11.4192 | 2.0196 | 127.7754 | 0.089369 | 4.69 | 5.99 | 6.43 | 0.46 | 55.236 | 185.032 | 217.1824 | -17.3756 | 99.1672 | 202.4158 | 99.7727
[12 empty] | 84 | 36224 | 16:00:00pm | 1974 | 19.52 | 161.3 | 156.41 | 28.06 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36815 | 0.74725 | 4.5934 | 11.52 | 11.7165 | 2.0952 | 128.6998 | 0.091037 | 4.69 | 6 | 6.43 | 0.685 | 57.432 | 186.128 | 225.2057 | -20.9951 | 98.8073 | 210.2083 | 99.6741
[12 empty] | 85 | 36255 | 08:00:00am | 1990 | 19.2 | 161.3 | 158.7 | 27.54 | 4.18 | 0.68 | 0.23 |  | 0.91 | 5.09 | 0.36815 | 0.74725 | 4.5934 | 11.52 | 11.8497 | 1.9566 | 130.5034 | 0.0908 | 4.7 | 6.06 | 6.42 | 1.145 | 54.138 | 186.128 | 210.813 | -13.2624 | 97.885 | 196.8076 | 99.4182
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
Note on H14: C. Rice: Manufacturer does not have a specific minimum flow rate recommendation -- the 12 gpm min. and 20 gpm max. represent the variability observed during their own testing. Their minimum flow rate will vary with application and is based on a maximum membrane polarization factor of 1.2.
Note on K13: C. Rice: Consultant verified aluminum values.
Note on K14: C. Rice: This value is higher than the raw water concentration because aluminum sulfate is added for coagulation.
Note on K19: C. Rice: Consultant verified aluminum values.
Note on AS5: TSC_ADM: Operational TDS data is based on an empirical factor applied to the on-line conductivity measurements (compared to the biweekly TDS data, which are based on lab measurements); therefore, there may be discrepancies between the operational and biweekly TDS data.
Note on BP19: TSC_ADM: Reviewer changed "0" value to BMRL
Note on BR16: TSC_ADM: Reviewer changed "0" value to BMRL
Note on BT17: C. Rice: Consultant verified the TDS data for weeks 2, 6 and 8; no explanation was given for the high MB closure errors.
Note on CA19: TSC_ADM: Reviewer changed "0" value to BMRL
Note on CC16: TSC_ADM: Reviewer changed "0" value to BMRL
Note on CL19: TSC_ADM: Reviewer changed "0" value to BMRL
Note on CN16: TSC_ADM: Reviewer changed "0" value to BMRL
Note on CP17: C. Rice: Consultant verified the TDS data for weeks 2, 6 and 8; no explanation was given for the high MB closure errors.
Note on CW19: TSC_ADM: Reviewer changed "0" value to BMRL
Note on CY16: TSC_ADM: Reviewer changed "0" value to BMRL
Note on DA17: C. Rice: Consultant verified the TDS data for weeks 2, 6 and 8; no explanation was given for the high MB closure errors.
Note on DA18: C. Rice: Consultant verified the total hardness data for week 8; no explanation was given for the high MB closure error.
Note on DS19: TSC_ADM: Reviewer changed "0" value to BMRL