## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: ICR452.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [13 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [11 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [9 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [13 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [12 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [8 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Raleigh | Carbon manufacturer | Calgon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | NC 0392010 | Carbon trade name | Filtasorb 820 | mesh size | (mm) | Coagulation | Ferric Sulfate Fe2(SO4)3.9H2O @ 40-50 mg/L | Full Scale | ID | duplicated? | date | time | time | volumes | volumes |  |  | mg/L as |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7.8
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 | Flocculation | Walking beam flocculators, 0.1-0.2mg/L polymer | Full Scale |  | Y/N | MM/DD/YY | hh:mm | hh:hh | ( 20 minute) | ( 10 minute) | --- | ntu | CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 2 | 6 | 3.35 | Sedimentation | 138 Minutes Conventional | Full Scale | START | --- | 1998-04-14 | 11:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 11:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 11:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 153.924 | 8 | 2.36 | Ozonation | Ozone residual 0.1 mg/L | Pilot Scale | A-1 | N | 1998-04-15 | 11:00 | 24 | 72 | 144 | 6.86 | 0.06 | BMRL | 20.3 | 16 | 9.7 | BMRL | NA | 2.1 | 0.026 | 1.2381 | 2.1 | 0.85 | 1.25 | 18.3 | 7.5 | 48 | 160 | 25 | 4.5 | BMRL | BMRL | 29.5 | 3.8 | 12 | 14 | BMRL | BMRL | 1.8 | NA | NA | NA | 29.8 | 31.6 | B-1 | N | 1998-04-15 | 11:00 | 24 | 144 | 9.24 | 0.08 | 20.3 | BMRL | BMRL | BMRL | BMRL | 1 | 0.67 | 0.33 | 18.3 | 7.5 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-1 | N | 1998-04-15 | 11:00 | 24 | 72 | 10.14 | 0.1 | 20.6 | BMRL | NA | BMRL | BMRL | 1 | 0.47 | 0.53 | 18.3 | 7.5 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 465 | 10 | 2 | Dual media filtration | sand / anthracite | Pilot Scale | A-2 | N | 1998-04-21 | 15:30 | 162.5 | 487.5 | 975 |  | 0.17 | BMRL | 20.4 | 16 | 9.5 | BMRL | BMRL | 1.7 | 0.026 | 1.5294 | 2.25 | 0.72 | 1.53 | 19.6 | 7.5 | 48 | 65 | 18 | 4.1 | BMRL | BMRL | 22.1 | 3.7 | 8.8 | 8.3 | BMRL | BMRL | 1.6 | NA | NA | NA | 20.8 | 22.4 | B-2 | N | 1998-04-21 | 15:30 | 162.5 | 975 | 6.71 | 0.07 | 20.4 | BMRL | BMRL | 0.005 | BMRL | 1.6 | 0.92 | 0.68 | 19.6 | 7.5 | 48 | BMRL | 1.9 | BMRL | BMRL | BMRL | 1.9 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-2 | N | 1998-04-21 | 15:30 | 162.5 | 487.5 | 7.56 | 0.07 | 20.6 | BMRL | BMRL | 0.006 | BMRL | 1.3 | 0.8 | 0.5 | 19.6 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A-3 | N | 1998-04-23 | 15:00 | 210 | 630 | 1260 | 6.06 | 0.05 | BMRL | 18.7 | 16 | 9.7 | BMRL | BMRL | 1.8 | 0.02 | 1.1111 | 2.25 | 0.69 | 1.56 | 19.1 | 7.5 | 48 | 150 | 18 | 4 | BMRL | BMRL | 22 | 3.7 | 8.8 | 8 | BMRL | BMRL | 1.6 | NA | NA | NA | 20.5 | 22.1 | B-3 | N | 1998-04-23 | 15:00 | 210 | 1260 | 6.34 | 0.05 | 19.1 | BMRL | BMRL | 0.005 | BMRL | 1.6 | 0.94 | 0.66 | 19.1 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-3 | N | 1998-04-23 | 15:00 | 210 | 630 | 6.8 | BMRL | 19.7 | BMRL | BMRL | 0.005 | BMRL | 1.3 | 0.88 | 0.42 | 19.1 | 7.5 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 20 | 16 | 1.18 |  |  |  | Avg-A-4 | Y | 1998-04-27 | 12:30 | 303.5 | 910.5 | 1821 | 5.73 | 0.09 | BMRL | 21.1 | 16.5 | BMRL | BMRL | BMRL | 1.8 | 0.022 | 1.2222 | 2.25 | 0.865 | 1.385 | 19.6 | 7.5 | 48 | NR | 20 | 4.65 | BMRL | BMRL | 24.65 | 2.55 | 11.5 | 6.95 | BMRL | BMRL | 1.45 | NA | NA | NA | 21 | 22.45 | Avg-B-4 | Y | 1998-04-27 | 12:30 | 303.5 | 1821 | 5.78 | 0.065 | 21.4 | BMRL | BMRL | 0.008 | BMRL | 1.6 | 1.04 | 0.56 | 19.6 | 7.5 | 48 | NR | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Avg-C-4 | Y | 1998-04-27 | 12:30 | 303.5 | 910.5 | 5.88 | BMRL | 21.3 | BMRL | BMRL | 0.006 | BMRL | 1.3 | 1.04 | 0.26 | 19.6 | 7.5 | 48 | NR | 1.7 | BMRL | BMRL | BMRL | 1.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 78.8
FAX Number |  | Flow rate, Q (L/hr) | 181.68 | 20 | 0.85 |  |  |  | A-5 | N | 1998-04-30 | 10:30 | 373.5 | 1120.5 | 2241 | 5.7 | 0.08 | BMRL | 20.4 | 17 | 9.7 | BMRL | BMRL | 2 | 0.027 | 1.35 | 1.7 | 0.49 | 1.21 | 20.7 | 7.5 | 48 | 130 | 23 | 5.1 | BMRL | BMRL | 28.1 | 3.4 | 10 | 7.6 | BMRL | BMRL | 1.7 | NA | NA | NA | 21 | 22.7 | B-5 | N | 1998-04-30 | 10:30 | 373.5 | 2241 | 5.72 | 0.11 | 20.2 | BMRL | BMRL | 0.006 | BMRL | 1.5 | 0.93 | 0.57 | 20.7 | 7.5 | 48 | NR | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-5 | N | 1998-04-30 | 10:30 | 373.5 | 1120.5 | 5.87 | 0.06 | 20.4 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.73 | 0.47 | 20.7 | 7.5 | 48 | NR | 1.3 | BMRL | BMRL | BMRL | 1.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1998 Producers Price Index (PPI base year 1982 = 100) | 131.3
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A-6 | N | 1998-05-04 | 12:00 | 471 | 1413 | 2826 | 5.7 | 0.08 | BMRL | 21.8 | 17 | 10 | BMRL | BMRL | 1.8 | 0.022 | 1.2222 | 2.5 | 0.72 | 1.78 | 21.5 | 7.5 | 48 | 130 | 22 | 4.8 | BMRL | BMRL | 26.8 | 4.6 | 11 | 10 | BMRL | BMRL | 1.7 | NA | NA | NA | 25.6 | 27.3 | B-6 | N | 1998-05-04 | 12:00 | 471 | 2826 | 5.7 | 0.07 | 22.6 | BMRL | BMRL | BMRL | BMRL | 1.65 | 1.01 | 0.64 | 21.5 | 7.5 | 48 | BMRL | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-6 | N | 1998-05-04 | 12:00 | 471 | 1413 | 5.65 | 0.06 | 22.6 | BMRL | BMRL | BMRL | BMRL | 1.6 | 0.99 | 0.61 | 21.5 | 7.5 | 48 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1.7 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.1 | 1.1 | Labor Rate + Fringe ($/work-hour) | 22
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A-7 | N | 1998-05-07 | 14:30 | 545.5 | 1636.5 | 3273 | 5.74 | 0.08 | BMRL | 22.9 | 17 | 10 | BMRL | NA | 2.2 | 0.029 | 1.3182 | 2.5 | 0.88 | 1.62 | 22.2 | 7.5 | 48 | 140 | 28 | 5.7 | BMRL | BMRL | 33.7 | 3.2 | 12 | 15 | BMRL | BMRL | 2 | NA | NA | NA | 30.2 | 32.2 | B-7 | N | 1998-05-07 | 14:30 | 545.5 | 3273 | 5.78 | 0.06 | 23.7 | BMRL | BMRL | BMRL | BMRL | 1.4 | 0.96 | 0.44 | 22.2 | 7.5 | 48 | BMRL | NR | NR | NR | NR | NR | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-7 | N | 1998-05-07 | 14:30 | 545.5 | 1636.5 | 5.7 | 0.05 | 23.8 | BMRL | BMRL | 0.005 | BMRL | 1.3 | 1.04 | 0.26 | 22.2 | 7.5 | 48 | BMRL | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Labor Overhead Factor (% of labor) | 6
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 8812.9385 | 50 | 0.3 |  |  |  | A-8 | N | 1998-05-18 | 10:00 | 793 | 2379 | 4758 | 5.68 | 0.09 | BMRL | 24.7 | 22 | 13 | BMRL | NA | 1.7 | 0.02 | 1.1765 | 2.5 | 0.9 | 1.6 | 23.3 | 7.5 | 48 | 120 | 29 | 6.8 | 1.2 | BMRL | 37 | 2.9 | 12 | 10 | BMRL | BMRL | 2.2 | NA | NA | NA | 24.9 | 27.1 | B-8 | N | 1998-05-18 | 10:00 | 793 | 4758 | 5.48 | 0.09 | 24.9 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.64 | 0.56 | 23.3 | 7.5 | 48 | BMRL | 1.6 | BMRL | BMRL | BMRL | 1.6 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-8 | N | 1998-05-18 | 10:00 | 793 | 2379 | 5.43 | 0.06 | 25 | BMRL | BMRL | BMRL | BMRL | 1 | 0.61 | 0.39 | 23.3 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Electric Rate ($/kW-h) | 0.08
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 17625.877 | 60 | 0.25 |  |  |  | A-9 | N | 1998-05-21 | 10:00 | 865 | 2595 | 5190 | 5.74 | 0.08 | BMRL | 26.8 | 22 | 13 | BMRL | NA | 2 | 0.022 | 1.1 | 2.5 | 0.83 | 1.67 | 25.1 | 7.5 | 48 | 130 | 25 | 6 | 1.1 | BMRL | 32.1 | 3.6 | 12 | 9 | BMRL | BMRL | 2.3 | NA | NA | NA | 24.6 | 26.9 | B-9 | N | 1998-05-21 | 10:00 | 865 | 5190 | 5.72 | 0.09 | 27.3 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.68 | 0.52 | 25.1 | 7.5 | 48 | BMRL | 1.5 | BMRL | BMRL | BMRL | 1.5 | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.2 | 1.2 | C-9 | N | 1998-05-21 | 10:00 | 865 | 2595 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Fuel Oil Rate ($/gal) | 0.55
|  |  |  | 70 | 0.21 |  |  |  | Avg-A-10 | Y | 1998-05-27 | 11:00 | 1005 | 3015 | 6030 | 5.75 | 0.065 | BMRL | 26.8 | 18 | 11 | BMRL | 21 | 1.9 | 0.024 | 1.2632 | 2.5 | 0.465 | 2.035 | 25.8 | 7.5 | 48 | 150 | 27.5 | 1.3 | 6.6 | BMRL | 35.4 | 3.35 | 12 | 9.75 | BMRL | BMRL | 2.25 | NA | NA | NA | 25.1 | 27.35 | Avg-B-10 | Y | 1998-05-27 | 11:00 | 1005 | 6030 | 5.73 | 0.055 | 26.9 | BMRL | BMRL | BMRL | BMRL | 1.3 | 0.49 | 0.81 | 25.8 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Avg-C-10 | Y | 1998-05-27 | 11:00 | 1005 | 3015 | 5.57 | 0.06 | 27.1 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.4 | 0.8 | 25.8 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A-11 | N | 1998-06-01 | 13:00 | 1122 | 3366 | 6732 | 5.6 | 0.07 | BMRL | 28 | 18 | 11 | BMRL | BMRL | 1.8 | 0.027 | 1.5 | 2.6 | 0.79 | 1.81 | 27 | 7.5 | 48 | 120 | 33 | 8 | 1.7 | BMRL | 42.7 | 3.5 | 11 | 8.5 | BMRL | BMRL | 2.1 | NA | NA | NA | 23 | 25.1 | B-11 | N | 1998-06-01 | 13:00 | 1122 | 6732 | 5.54 | 0.07 | 28.2 | BMRL | BMRL | 0.009 | BMRL | 1.5 | 0.6 | 0.9 | 27 | 7.5 | 48 | BMRL | 2.1 | 1.2 | BMRL | BMRL | 3.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-11 | N | 1998-06-01 | 13:00 | 1122 | 3366 | 5.38 | 0.05 | 28.2 | BMRL | BMRL | 0.006 | BMRL | 1.4 | 0.8 | 0.6 | 27 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Current Process Water Rate ($/1000 gal) | 0.4
FAX Number |  | Carbon particle diameter, d (mm) | 1.605 | [5 empty] | A-12 | N | 1998-06-04 | 13:15 | 1190.25 | 3570.75 | 7141.5 | 5.27 | 0.06 | BMRL | 28.4 | 19 | 12 | BMRL | BMRL | 1.4 | 0.02 | 1.4286 | 2.6 | 0.93 | 1.67 | 27.5 | 7.5 | 48 | 110 | 33 | 8.4 | 1.8 | BMRL | 43.2 | 3.3 | 9.9 | 6.7 | BMRL | BMRL | 2.3 | NA | NA | NA | 19.9 | 22.2 | B-12 | N | 1998-06-04 | 13:15 | 1190.25 | 7141.5 | 5.38 | 0.06 | 28.3 | BMRL | BMRL | BMRL | BMRL | 1.5 | 0.87 | 0.63 | 27.5 | 7.5 | 48 | BMRL | 1.8 | 1 | BMRL | BMRL | 2.8 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-12 | N | 1998-06-04 | 13:15 | 1190.25 | 3570.75 | 5.27 | 0.08 | 28.2 | BMRL | BMRL | BMRL | BMRL | 1.4 | 0.81 | 0.59 | 27.5 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.018608 | [5 empty] | A-13 | N | 1998-06-08 | 10:30 | 1283.5 | 3850.5 | 7701 | 5.34 | 0.07 | BMRL | 24 | 19 | 11 | BMRL | BMRL | 1.6 | 0.021 | 1.3125 | 2.5 | 1.11 | 1.39 | 25.1 | 7.5 | 48 | 110 | 26 | 7 | 1.5 | BMRL | 34.5 | 3.2 | 8.4 | 6.8 | BMRL | BMRL | 1.9 | NA | NA | NA | 18.4 | 20.3 | B-13 | N | 1998-06-08 | 10:30 | 1283.5 | 7701 | 5.6 | 0.07 | 23.2 | BMRL | BMRL | 0.006 | BMRL | 1.4 | 0.78 | 0.62 | 25.1 | 7.5 | 48 | BMRL | 1.3 | BMRL | BMRL | BMRL | 1.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-13 | N | 1998-06-08 | 10:30 | 1283.5 | 3850.5 | 5.58 | 0.1 | 22.8 | BMRL | BMRL | 0.005 | BMRL | 1.2 | 0.44 | 0.76 | 25.1 | 7.5 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
|  | Hydraulic loading rate1, v (m/hr) | 9.7635 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, |  |  | A-14 | N | 1998-06-11 | 11:00 | 1356 | 4068 | 8136 | 4.95 | 0.12 | BMRL | 25 | 20 | 12 | BMRL | 21 | 1.7 | 0.022 | 1.2941 | 2.5 | NR | NR | 25.4 | 7.5 | 48 | NA | 17 | 5 | 1.2 | BMRL | 23.2 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B-14 | N | 1998-06-11 | 11:00 | 1356 | 8136 | 5.11 | 0.07 | 24.8 | BMRL | BMRL | BMRL | BMRL | 1.4 | NR | NR | 25.4 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-14 | N | 1998-06-11 | 11:00 | 1356 | 4068 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
Plant Name | E.M. Johnson Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | must be included in the hard-copy Treatment Study Summary Report (see Section 10.0). |  |  | A-15 | N | 1998-06-15 | 13:00 | 1454 | 4362 | 8724 | 4.98 | 0.09 | BMRL | 28.8 | 20 | 12 | BMRL | 22 | 1.7 | 0.036 | 2.1176 | 2.5 | 0.88 | 1.62 | 27.5 | 7.5 | 48 | 120 | 28 | 7.5 | 1.7 | BMRL | 37.2 | 3.4 | 12 | 9.7 | BMRL | BMRL | 2.4 | NA | NA | NA | 25.1 | 27.5 | B-15 | N | 1998-06-15 | 13:00 | 1454 | 8724 | 4.93 | 0.1 | 29 | BMRL | BMRL | 0.011 | BMRL | 1.4 | NR | NR | 27.5 | 7.5 | 48 | BMRL | 1.3 | BMRL | BMRL | BMRL | 1.3 | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.4 | 1.4 | C-15 | N | 1998-06-15 | 13:00 | 1454 | 4362 | 5 | 0.08 | 28.6 | BMRL | BMRL | 0.007 | BMRL | 1.3 | 0.89 | 0.41 | 27.5 | 7.5 | 48 | BMRL | 1.5 | BMRL | BMRL | BMRL | 1.5 | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1 | 1
Treatment Plant Category | CONV |  |  |  |  | The purpose of this table is to list the pretreatment processes used in this |  |  | A-16 | N | 1998-06-22 | 11:15 | 1620.25 | 4860.75 | 9721.5 | 5.18 | 0.14 | BMRL | 29.3 | 23 | 13 | BMRL | 21 | 1.8 | 0.021 | 1.1667 | 2.4 | 0.99 | 1.41 | 29.2 | 7.5 | 48 | 180 | 20 | 6.2 | 1.3 | BMRL | 27.5 | 4.1 | 11 | 10 | BMRL | BMRL | 2.1 | NA | NA | NA | 25.1 | 27.2 | B-16 | N | 1998-06-22 | 11:15 | 1620.25 | 9721.5 | 5.08 | 0.08 | 29.5 | BMRL | BMRL | BMRL | BMRL | 1.4 | 0.96 | 0.44 | 29.2 | 7.5 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-16 | N | 1998-06-22 | 11:15 | 1620.25 | 4860.75 | 4.82 | 0.07 | 29.5 | BMRL | BMRL | 0.005 | BMRL | 1.1 | 0.7 | 0.4 | 29.2 | 7.5 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
Process Train Name | Conventional Train | 10-Minute EBCT Run |  |  |  | particular pilot GAC run. |  |  | A-17 | N | 1998-06-29 | 15:15 | 1792.25 | 5376.75 | 10753.5 | 4.86 | 0.25 | BMRL | 31.3 | 22 | 12 | BMRL | 23 | 1.7 | 0.025 | 1.4706 | 2.3 | 0.31 | 1.99 | 30.9 | 7.5 | 48 | 160 | 39 | 10 | 1.7 | 1.5 | 52.2 | 3.2 | 14 | 12 | BMRL | BMRL | 2.7 | NA | NA | NA | 29.2 | 31.9 | B-17 | N | 1998-06-29 | 15:15 | 1792.25 | 10753.5 | 4.98 | 0.14 | 31.4 | NA | BMRL | BMRL | BMRL | 1.3 | 0.72 | 0.58 | 30.9 | 7.5 | 48 | BMRL | 1.9 | 1.8 | 1.4 | 1.8 | 6.9 | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.2 | 1.2 | C-17 | N | 1998-06-29 | 15:15 | 1792.25 | 5376.75 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
ICR Treatment Plant Identification Number | 452 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A-18 | N | 1998-07-14 | 10:45 | 2147.75 | 6443.25 | 12886.5 | 5.31 | BMRL | BMRL | 28.3 | 22 | 13 | 0.11 | 24 | 1.7 | 0.019 | 1.1176 | 2.8 | 0.95 | 1.85 | 29.2 | 7.5 | 48 | 130 | 27 | 8.9 | 2.5 | BMRL | 38.4 | 4.8 | 13 | 7.8 | BMRL | BMRL | 2.7 | NA | NA | NA | 25.6 | 28.3 | B-18 | N | 1998-07-14 | 10:45 | 2147.75 | 12886.5 | 5.48 | BMRL | 27.5 | NA | BMRL | 0.008 | BMRL | 1.9 | 1.01 | 0.89 | 29.2 | 7.5 | 48 | 72 | 4.1 | 4 | 2.1 | BMRL | 10.2 | 3.1 | 3.2 | 1.2 | BMRL | BMRL | 1.4 | NA | NA | NA | 7.5 | 8.9 | C-18 | N | 1998-07-14 | 10:45 | 2147.75 | 6443.25 | 5.56 | BMRL | 27.7 | NA | BMRL | BMRL | BMRL | 1.5 | 0.94 | 0.56 | 29.2 | 7.5 | 48 | NR | 1.2 | 1 | BMRL | BMRL | 2.2 | 2.8 | 1.5 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 4.3 | 4.3
PWSID Number of Plant (if assigned) | NC 0392010 | Estimated run time, t (days) | 122.4019 | [5 empty] | A-19 | N | 1998-07-27 | 15:00 | 2464 | 7392 | 14784 | 5.71 | 0.06 | BMRL | 28.6 | 20 | 11 | BMRL | 23 | 1.6 | 0.023 | 1.4375 | 2.7 | 0.46 | 2.24 | 30.1 | 7.5 | 48 | NR | 46 | 11 | 2 | BMRL | 59 | 5 | 18 | 23 | BMRL | BMRL | 4.2 | NA | NA | NA | 46 | 50.2 | B-19 | N | 1998-07-27 | 15:00 | 2464 | 14784 | 5.58 | 0.06 | 28.1 | NA | BMRL | BMRL | BMRL | 1.9 | 0.98 | 0.92 | 30.1 | 7.5 | 48 | BMRL | 2.8 | 4.9 | 2 | BMRL | 9.7 | 8.1 | 1.8 | 2.6 | BMRL | BMRL | 1.1 | NA | NA | NA | 12.5 | 13.6 | C-19 | N | 1998-07-27 | 15:00 | 2464 | 7392 | 5.51 | BMRL | 27.7 | NA | BMRL | BMRL | BMRL | 1.4 | 0.46 | 0.94 | 30.1 | 7.5 | 48 | BMRL | 5.7 | 4.6 | 3.2 | BMRL | 13.5 | 4 | 3.4 | 4.3 | BMRL | BMRL | 1.7 | NA | NA | NA | 11.7 | 13.4
Historical Minimum Water Temperature (oC) | 6 | Pilot column bed length, l (m) | 1.6272 | [5 empty] | A-20 | N | 1998-08-06 | 14:00 | 2703 | 8109 | 16218 | 5.65 | BMRL | BMRL | 27.9 | 21 | 11 | BMRL | 28 | 1.6 | 0.022 | 1.375 | 2.8 | 0.66 | 2.14 | 28.5 | 7.5 | 48 | 130 | 33 | 11 | 2.7 | BMRL | 46.7 | 4.3 | 10 | 11 | BMRL | BMRL | 2.6 | NA | NA | NA | 25.3 | 27.9 | B-20 | N | 1998-08-06 | 14:00 | 2703 | 16218 | 5.4 | BMRL | 27.7 | NA | BMRL | 0.009 | BMRL | 1.9 | 0.98 | 0.92 | 28.5 | 7.5 | 48 | BMRL | 3.8 | 3.6 | 2.4 | BMRL | 9.8 | 1.8 | 1.9 | 1.8 | BMRL | BMRL | BMRL | NA | NA | NA | 5.5 | 5.5 | C-20 | N | 1998-08-06 | 14:00 | 2703 | 8109 | 5.32 | BMRL | 27.5 | NA | BMRL | BMRL | BMRL | 1.5 | 0.76 | 0.74 | 28.5 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | 1 | BMRL | 1 | BMRL | BMRL | BMRL | NA | NA | NA | 2 | 2
Historical Average Water Temperature (oC) | 21.1 | Mass GAC required, m (kg) | 14.0802 | [5 empty] | A-21 | N | 1998-08-18 | 9:45 | 2966.75 | 8900.25 | 17800.5 | 6.08 | 0.06 | BMRL | 28.4 | 21 | 12 | BMRL | 26 | 1.5 | 0.017 | 1.1333 | 3 | 0.91 | 2.09 | 29.5 | 7.5 | 48 | 150 | 31 | 11 | 3.2 | BMRL | 45.2 | 6.6 | 10 | 7.7 | BMRL | BMRL | 2.5 | NA | NA | NA | 24.3 | 26.8 | B-21 | N | 1998-08-18 | 9:45 | 2966.75 | 17800.5 | 5.92 | 0.05 | 28.1 | NA | 0.8 | 0.008 | 1 | 1.7 | 0.65 | 1.05 | 29.5 | 7.5 | 48 | BMRL | 1.3 | 1.1 | BMRL | BMRL | 2.4 | 3.2 | 1 | 1.4 | BMRL | BMRL | BMRL | NA | NA | NA | 5.6 | 5.6 | C-21 | N | 1998-08-18 | 9:45 | 2966.75 | 8900.25 | 5.75 | BMRL | 27.7 | NA | BMRL | 0.008 | BMRL | 1.5 | 0.3 | 1.2 | 29.5 | 7.5 | 48 | NR | 7.1 | 6.9 | 4 | BMRL | 18 | 2.9 | 2.6 | 2 | BMRL | BMRL | 1.4 | NA | NA | NA | 7.5 | 8.9
State Approved Plant Capacity (MGD) | 78 | [7 empty] | A-22 | N | 1998-08-25 | 10:00 | 3135 | 9405 | 18810 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | B-22 | N | 1998-08-25 | 10:00 | 3135 | 18810 | NR | NR | NR | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | C-22 | N | 1998-08-25 | 10:00 | 3135 | 9405 | NR | NR | NR | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
|  | 20-Minute EBCT Run | [6 empty] | A-23 | N | 1998-09-14 | 14:30 | 3599.5 | 10798.5 | 21597 | 5.84 | BMRL | BMRL | 28.5 | 24 | 14 | 0.14 | NA | 1.4 | 0.025 | 1.7857 | 2 | 0.93 | 1.07 | 27.9 | 7.5 | 48 | 170 | 15 | 7.4 | 3.4 | BMRL | 25.8 | 3.8 | 5.3 | 4.3 | BMRL | BMRL | 2.3 | NA | NA | NA | 13.4 | 15.7 | B-23 | N | 1998-09-14 | 14:30 | 3599.5 | 21597 | 5.74 | BMRL | 28.3 | NA | 1 | 0.015 | 1.5 | 2.3 | 1.35 | 0.95 | 27.9 | 7.5 | 48 | 81 | 6.4 | 5.3 | 3.1 | BMRL | 14.8 | 1.8 | BMRL | 2 | BMRL | BMRL | 1.7 | NA | NA | NA | 3.8 | 5.5 | C-23 | N | 1998-09-14 | 14:30 | 3599.5 | 10798.5 | 5.62 | 0.07 | 28 | NA | BMRL | 0.013 | BMRL | 2.3 | 0.9 | 1.4 | 27.9 | 7.5 | 48 | NR | 5.6 | 4.4 | 3.1 | BMRL | 13.1 | BMRL | 2.9 | 3.6 | BMRL | BMRL | 1.5 | NA | NA | NA | 6.5 | 8
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | Avg-A-24 | Y | 1998-09-22 | 9:00 | 3786 | 11358 | 22716 | 6.02 | 0.05 | 5 | 28.5 | 27 | 17 | 0.1 | 31.5 | 1.8 | 0.022 | 1.2222 | 3.275 | 1.35 | 1.925 | 27.9 | 7.5 | 48 | 202.5 | 28 | 11 | 4.15 | BMRL | 43.15 | 4.4 | 10.95 | 7.85 | BMRL | BMRL | 4.1 | NA | NA | NA | 23.2 | 27.3 | Avg-B-24 | Y | 1998-09-22 | 9:00 | 3786 | 22716 | 5.9 | 0.05 | 26.4 | NA | 1.07 | 0.014 | 1.3084 | 2.425 | 1.205 | 1.22 | 27.9 | 7.5 | 48 | 95.5 | 13 | 9.85 | 5.5 | BMRL | 28.35 | 2.05 | 4.85 | 3.25 | BMRL | BMRL | 3.25 | NA | NA | NA | 10.15 | 13.4 | Avg-C-24 | Y | 1998-09-22 | 9:00 | 3786 | 11358 | 5.84 | BMRL | 26 | NA | BMRL | 0.0075 | BMRL | 2.125 | 1.365 | 0.76 | 27.9 | 7.5 | 48 | BMRL | 2.7 | 3 | 2.15 | BMRL | 7.85 | BMRL | 2.1 | 1.2 | BMRL | BMRL | 1.25 | NA | NA | NA | 3.3 | 4.55
|  | Estimated run time, t (days) | 244.8038 | [5 empty] | A-25 | N | 1998-09-30 | 14:00 | 3983 | 11949 | 23898 | 5.72 | BMRL | BMRL | 28.3 | 26 | 15 | BMRL | 27 | 1.8 | 0.019 | 1.0556 | 2.8 | 1.35 | 1.45 | 27 | 7.5 | 48 | 150 | 17 | 7.8 | 3.2 | BMRL | 28 | 4.9 | 8.2 | 5.6 | BMRL | BMRL | 3.2 | NA | NA | NA | 18.7 | 21.9 | B-25 | N | 1998-09-30 | 14:00 | 3983 | 23898 | 5.68 | BMRL | 27.2 | NA | 1.2 | 0.01 | 0.83333 | 2.2 | 1.31 | 0.89 | 27 | 7.5 | 48 | 95 | 7.3 | 6 | 3.6 | BMRL | 16.9 | 2.1 | 3.3 | 2.2 | BMRL | BMRL | 2.3 | NA | NA | NA | 7.6 | 9.9 | C-25 | N | 1998-09-30 | 14:00 | 3983 | 11949 | 5.62 | BMRL | 25.8 | NA | BMRL | 0.008 | BMRL | 1.8 | 1.26 | 0.54 | 27 | 7.5 | 48 | BMRL | 1.5 | 2 | 1.8 | BMRL | 5.3 | 2.5 | 1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 3.5 | 3.5
|  | Pilot column bed length, l (m) | 3.2545 | [5 empty] | A-26 | N | 1998-10-07 | 10:00 | 4123 | 12369 | 24738 | 5.64 | 0.06 | BMRL | 22.8 | 27 | 16 | BMRL | 38 | 1.8 | NR | NR | 2.05 | 0.69 | 1.36 | 24.2 | 7.5 | 48 | NR | 14 | 7.2 | 3.2 | BMRL | 24.4 | 3.6 | 7.4 | 4.4 | BMRL | BMRL | 2.9 | NA | NA | NA | 15.4 | 18.3 | B-26 | N | 1998-10-07 | 10:00 | 4123 | 24738 | 5.58 | 0.22 | 22.4 | NA | 1.3 | 0.007 | 0.53846 | 2.4 | 1.11 | 1.29 | 24.2 | 7.5 | 48 | 100 | 10 | 7.1 | 3.9 | BMRL | 21 | 2.4 | 4.5 | 2.8 | BMRL | BMRL | 2.7 | NA | NA | NA | 9.7 | 12.4 | C-26 | N | 1998-10-07 | 10:00 | 4123 | 12369 | NA | NA | NA | NA | NA | NA | BMRL | NA | NA | NA | NA | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
|  | Mass GAC required, m (kg) | 28.1604 | [5 empty] | A-27 | N | 1998-10-20 | 13:30 | 4438.5 | 13315.5 | 26631 | 5.6 | BMRL | BMRL | 23.3 | 27 | 16 | BMRL | 34 | 2.1 | 0.021 | 1 | 2 | 0.33 | 1.67 | 22.8 | 7.5 | 48 | 140 | 13 | 6.9 | 3.4 | BMRL | 23.3 | 3.1 | 4.5 | 3.5 | BMRL | BMRL | 2.3 | NA | NA | NA | 11.1 | 13.4 | B-27 | N | 1998-10-20 | 13:30 | 4438.5 | 26631 | 5.66 | BMRL | 22.3 | NA | 1.4 | 0.012 | 0.85714 | 2 | 0.45 | 1.55 | 22.8 | 7.5 | 48 | 90 | 7.8 | 6 | 3.8 | BMRL | 17.6 | 2.1 | 3.4 | 2.5 | BMRL | BMRL | 2.3 | NA | NA | NA | 8 | 10.3 | C-27 | N | 1998-10-20 | 13:30 | 4438.5 | 13315.5 | NA | NA | NA | NA | NA | NA | BMRL | NA | NA | NA | NA | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[9 empty] | A-28 | N | 1998-10-28 | 13:30 | 4630.5 | 13891.5 | 27783 | 5.88 | 0.08 | BMRL | 21.3 | 28 | 17 | 0.1 | NA | 1.8 | 0.023 | 1.2778 | 3 | 0.65 | 2.35 | 20.6 | 7.5 | 48 | 170 | 14 | 7 | 3.3 | BMRL | 24.3 | 5.8 | 6.2 | 6.7 | BMRL | BMRL | 2.6 | NA | NA | NA | 18.7 | 21.3 | B-28 | N | 1998-10-28 | 13:30 | 4630.5 | 27783 | 6.06 | 0.06 | 21.2 | NA | 1.1 | 0.014 | 1.2727 | 3 | 0.46 | 2.54 | 20.6 | 7.5 | 48 | 110 | 9.6 | 6.4 | 3.7 | BMRL | 19.7 | 3.4 | 3.7 | 4.4 | BMRL | BMRL | 2.3 | NA | NA | NA | 11.5 | 13.8 | C-28 | N | 1998-10-28 | 13:30 | 4630.5 | 13891.5 | NA | NA | NA | NA | NA | NA | BMRL | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
[9 empty] | A-29 | N | 1998-11-09 | 10:30 | 4915.5 | 14746.5 | 29493 | 6.3 | 0.09 | 6.4 | 21.2 | 28 | 17 | 0.18 | 35 | 1.8 | 0.022 | 1.2222 | 5 | 1.2 | 3.8 | 17.3 | 7.5 | 48 | 280 | 14 | 6.7 | 3.1 | BMRL | 23.8 | 7.2 | 6.8 | 6.2 | BMRL | BMRL | 2 | NA | NA | NA | 20.2 | 22.2 | B-29 | N | 1998-11-09 | 10:30 | 4915.5 | 29493 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-29 | N | 1998-11-09 | 10:30 | 4915.5 | 14746.5 | 6.28 | BMRL | 20.9 | NA | 0.96 | 0.007 | 0.72917 | 4.8 | 1.3 | 3.5 | 17.3 | 7.5 | 48 | 290 | 5.2 | 4.8 | 3.3 | BMRL | 13.3 | 1.8 | 3.6 | 2.7 | BMRL | BMRL | 1.4 | NA | NA | NA | 8.1 | 9.5
[9 empty] | A-30 | N | 1998-11-16 | 13:00 | 5086 | 15258 | 30516 | 5.54 | 0.09 | BMRL | 19.4 | 27 | 16 | 0.25 | 37 | 1.9 | 0.019 | 1 | 4.5 | 1.28 | 3.22 | 17 | 7.5 | 48 | 220 | 12 | 6.8 | 3.4 | BMRL | 22.2 | 7.72 | 6.75 | 6.05 | BMRL | BMRL | 2.52 | NA | NA | NA | 20.52 | 23.04 | B-30 | N | 1998-11-16 | 13:00 | 5086 | 30516 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-30 | N | 1998-11-16 | 13:00 | 5086 | 15258 | 5.72 | BMRL | 19.8 | NA | BMRL | 0.006 | BMRL | 4.5 | 1.28 | 3.22 | 17 | 7.5 | 48 | NR | 4.2 | 2.9 | 1.8 | BMRL | 8.9 | 2.1 | 3.7 | 3.1 | BMRL | BMRL | 1.1 | NA | NA | NA | 8.9 | 10
[9 empty] | A-31 | N | 1998-12-01 | 12:00 | 5445 | 16335 | 32670 | 6.07 | 0.06 | BMRL | 22.9 | 27 | 16 | 0.14 | 40 | 1.6 | 0.023 | 1.1875 | 3.25 | 0.77 | 2.48 | 16.5 | 7.5 | 48 | 170 | 12 | 6.5 | 2.7 | BMRL | 21.2 | 2.6 | 8.8 | 5.4 | BMRL | BMRL | 2 | NA | NA | NA | 16.8 | 18.8 | B-31 | N | 1998-12-01 | 12:00 | 5445 | 32670 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-31 | N | 1998-12-01 | 12:00 | 5445 | 16335 | 5.67 | BMRL | 22.4 | NA | BMRL | BMRL | BMRL | 2.7 | 1.05 | 1.65 | 16.5 | 7.5 | 48 | 45 | 1.4 | 1.1 | BMRL | BMRL | 2.5 | 4 | 3.7 | 1.1 | BMRL | BMRL | 2 | NA | NA | NA | 8.8 | 10.8
[9 empty] | A-32 | N | 1998-12-16 | 10:30 | 5768.5 | 17305.5 | 34611 | 5.62 | 0.05 | BMRL | 15.7 | 27 | 16 | 0.11 | 43 | 1.6 | 0.019 | 1.1875 | 2.75 | 1.09 | 1.66 | 13.5 | 7.5 | 48 | 160 | 9.1 | 6 | 2.7 | BMRL | 17.8 | 2.3 | 4.2 | 3 | BMRL | BMRL | 1.9 | NA | NA | NA | 9.5 | 11.4 | B-32 | N | 1998-12-16 | 10:30 | 5803.5 | 34821 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-32 | N | 1998-12-16 | 10:30 | 5768.5 | 17305.5 | 5.75 | 0.06 | 16 | NA | 0.55 | 0.006 | 1.0909 | 2.5 | 1.24 | 1.26 | 13.5 | 7.5 | 48 | 69 | 2.9 | 2.5 | 1.6 | BMRL | 7 | BMRL | 1.5 | 1 | BMRL | BMRL | 1 | NA | NA | NA | 2.5 | 3.5
[9 empty] | A-33 | N | 1999-01-11 | 11:00 | 6386 | 19158 | 38316 | 6.09 | BMRL | 7.4 | 15.9 | 30 | 19.25 | 0.19 | 44 | 1.7 | 0.02 | 1.1765 | 4.4 | 1.2 | 3.2 | 11 | 7.5 | 48 | 130 | 10 | 7.8 | 4.4 | BMRL | 22.2 | BMRL | 6.2 | 4 | BMRL | 2 | 3.3 | NA | NA | NA | 12.2 | 15.5 | B-33 | N | 1999-01-11 | 11:00 | 6428 | 38568 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-33 | N | 1999-01-11 | 11:00 | 6386 | 19158 | 5.84 | BMRL | 14.9 | NA | 0.91 | 0.009 | 0.98901 | 3.7 | 0.7 | 3 | 11 | 7.5 | 48 | 41 | 2.8 | 3.1 | 2.2 | BMRL | 8.1 | BMRL | 1.8 | BMRL | BMRL | BMRL | 1.5 | NA | NA | NA | 1.8 | 3.3
[9 empty] | A-34 | N | 1999-01-25 | 12:00 | 6683 | 20049 | 40098 | 5.43 | BMRL | 3 | 14.2 | 31 | 19.5 | 0.13 | 50 | 1.7 | 0.022 | 1.2941 | 2.87 | 0.87 | 2 | 12 | 7.5 | 48 | 150 | 12 | 10 | 5.8 | BMRL | 27.8 | BMRL | 4.44 | 2.61 | BMRL | 1.61 | 1.89 | NA | NA | NA | 8.66 | 10.55 | B-34 | N | 1999-01-25 | 12:00 | 6765 | 40590 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-34 | N | 1999-01-25 | 12:00 | 6683 | 20049 | 5.49 | BMRL | 15.2 | 0.13 | 0.83 | 0.012 | 1.4458 | 2.09 | 0.59 | 1.5 | 12 | 7.5 | 48 | 71 | 4.3 | 5.6 | 5.4 | 1.7 | 17 | BMRL | 1.61 | 1.13 | BMRL | 1.3 | 1.1 | NA | NA | NA | 4.04 | 5.14
[9 empty] | A-35 | N | 1999-02-15 | 11:00 | 7092 | 21276 | 42552 | 6.8 | BMRL | BMRL | 12.7 | 29 | 18 | 0.09 |  | 2.1 | 0.031 | 1.4762 | 2.67 | 0.87 | 1.8 | 11.9 | 7.5 | 48 | 210 | 30 | 13 | 4.6 | BMRL | 47.6 | BMRL | 9.21 | 8.06 | BMRL | BMRL | 2.68 | NA | NA | NA | 17.27 | 19.95 | B-35 | N | 1999-02-15 | 11:00 | 7268 | 43608 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-35 | N | 1999-02-15 | 11:00 | 7092 | 21276 | 6.36 | BMRL | 14 | NA | 0.89 | 0.008 | 0.89888 | 1.62 | 0.62 | 1 | 11.9 | 7.5 | 48 | 98 | 16 | 12 | 5.7 | BMRL | 33.7 | 1.22 | 9.74 | 1.21 | BMRL | 1.53 | 6.74 | NA | NA | NA | 13.7 | 20.44
[9 empty] | A-36 | N | 1999-03-15 | 15:00 | 7753 | 23259 | 46518 | 5.2 | BMRL | 2 | 13.9 | 26 | 16 | NA | BMRL | 2.2 | 0.032 | 1.4545 | 3.8 | 1.2 | 2.6 | 11 | 7.5 | 48 | 210 | 27 | 8 | 2.8 | BMRL | 37.8 | BMRL | 9.9 | 8.7 | BMRL | BMRL | 2.58 | NA | NA | NA | 18.6 | 21.18 | B-36 | N | 1999-03-15 | 15:00 | 7753 | 46518 | 5.25 | BMRL | 14.7 | NA | 2 | 0.023 | 1.15 | 2.4 | 1 | 1.4 | 11 | 7.5 | 48 | 160 | 19 | 8.3 | 3.7 | BMRL | 31 | BMRL | 6.89 | 5.56 | BMRL | BMRL | 2.25 | NA | NA | NA | 12.45 | 14.7 | C-36 | N | 1999-03-15 | 15:00 | 7753 | 23259 | 5.14 | BMRL | 15.1 | NA | 1.4 | 0.016 | 1.1429 | 1.92 | 0.72 | 1.2 | 11 | 7.5 | 48 | 100 | 10 | 6.3 | 3.5 | BMRL | 19.8 | BMRL | 5.29 | 4.07 | BMRL | BMRL | 2.54 | NA | NA | NA | 9.36 | 11.9
[9 empty] | A-37 | N | 1999-03-22 | 11:00 | 7917 | 23751 | 47502 | 4.8 | BMRL | 2.4 | 14.5 | 25 | 15.4 | 0.08 | BMRL | 2.4 | 0.036 | 1.5 | 2.74 | 0.94 | 1.8 | 13 | 7.5 | 48 | 230 | 28 | 8.6 | 2.2 | BMRL | 2.2 | BMRL | 10.9 | 11.1 | BMRL | 2.61 | 2.61 | NA | NA | NA | 24.61 | 27.22 | B-37 | N | 1999-03-22 | 11:00 | 7917 | 47502 | 5.03 | BMRL | 14.6 | NA | 2.1 | 0.026 | 1.2381 | 1.54 | 0.14 | 1.4 | 13 | 7.5 | 48 | 140 | 26 | 8.9 | 2.8 | BMRL | 37.7 | BMRL | 5.29 | 4.07 | BMRL | BMRL | 2.54 | NA | NA | NA | 9.36 | 11.9 | C-37 | N | 1999-03-22 | 11:00 | 7917 | 23751 | 4.89 | 0.25 | 14.9 | NA | 1.6 | 0.02 | 1.25 | 1.95 | 0.75 | 1.2 | 13 | 7.5 | 48 | 120 | 12 | 6.9 | 3.3 | BMRL | 22.2 | BMRL | 4.93 | 3.61 | BMRL | BMRL | 2.19 | NA | NA | NA | 8.54 | 10.73
[9 empty] | A-38 | N | 1999-03-29 | 10:30 | 8084.5 | 24253.5 | 48507 | 4.93 | BMRL | BMRL | 14.9 | 24 | 14.6 | BMRL | BMRL | 2.5 | 0.031 | 1.24 | 1.74 | 0.24 | 1.5 | 14 | 7.5 | 48 | 250 | 29 | 8.9 | 2.2 | BMRL | 2.2 | 1.26 | 13.7 | 12.5 | BMRL | BMRL | 2.73 | NA | NA | NA | 27.46 | 30.19 | B-38 | N | 1999-03-29 | 10:30 | 8084.5 | 48507 | 5.05 | BMRL | 15.2 | NA | 1.8 | 0.021 | 1.1667 | 1.93 | 0.63 | 1.3 | 14 | 7.5 | 48 | 170 | 20 | 7.9 | 2.8 | BMRL | 30.7 | BMRL | 8.92 | 7.8 | BMRL | BMRL | 2.31 | NA | NA | NA | 16.72 | 19.03 | C-38 | N | 1999-03-29 | 10:30 | 8084.5 | 24253.5 | 5.1 | BMRL | 15.7 | NA | 1.8 | 0.013 | 0.72222 | 1.82 | 0.82 | 1 | 14 | 7.5 | 48 | 130 | 11 | 6.6 | 3.3 | BMRL | 20.9 | BMRL | 5.29 | 3.98 | BMRL | BMRL | 2.2 | NA | NA | NA | 9.27 | 11.47
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [21 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [12 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [21 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [12 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter
[9 empty] | enter the results for the primary and duplicate analyses below. | [40 empty] | the results for the primary and duplicate analyses below. | [35 empty] | the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [15 empty] | Group D, 3 duplicate influent samples per run (continued) | [10 empty] | Group D, 3 duplicate influent samples per run (continued) | [13 empty] | Group D, 3 duplicate effluent [10-minute] samples per run | [13 empty] | Group D, 3 duplicate effluent [10-minute] samples per run (continued) | [11 empty] | Group D, 3 duplicate effluent [10-minute] samples per run (continued) | [9 empty] | Group D, 3 duplicate effluent [20-minute] samples per run | [13 empty] | Group D, 3 duplicate effluent [20-minute] samples per run (continued) | [12 empty] | Group D, 3 duplicate effluent [20-minute] samples per run (continued)
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A4 | Primary | 1998-04-27 | 12:30 | 303.5 | 910.5 | 1821 | 5.73 | 0.09 | BMRL | 21.1 | 16 | BMRL | BMRL | BMRL | 1.8 | 0.022 | 1.2222 | 2.25 | 0.91 | 1.34 | 19.6 | 7.5 | 48 | NR | 20 | 4.9 | BMRL | BMRL | 0 | 1.9 | 11 | 6.9 | BMRL | BMRL | 1.5 | NA | NA | NA | 19.8 | 21.3 | B4 | Primary | 1998-04-27 | 12:30 | 303.5 | 1821 | 5.78 | 0.07 | 21.4 | BMRL | BMRL | 0.008 | BMRL | 1.6 | 1.03 | 0.57 | 19.6 | 7.5 | 48 | NR | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C4 | Primary | 1998-04-27 | 12:00 | 313 | 939 | 5.88 | BMRL | 21.3 | BMRL | BMRL | 0.005 | BMRL | 1.3 | 1.04 | 0.26 | 19.6 | 7.5 | 48 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | D-A4 | Duplicate | 1998-04-27 | 12:30 | 303.5 | 910.5 | 1821 | 5.73 | 0.09 | BMRL | 21.1 | 17 | BMRL | NR | BMRL | 1.8 | 0.022 | 1.2222 | 2.25 | 0.82 | 1.43 | 19.6 | 7.5 | 48 | NR | 20 | 4.4 | BMRL | BMRL | 0 | 3.2 | 12 | 7 | BMRL | BMRL | 1.4 | NA | NA | NA | 22.2 | 23.6 | D-B4 | Duplicate | 1998-04-27 | 12:30 | 303.5 | 1821 | 5.78 | 0.06 | 21.4 | BMRL | BMRL | BMRL | BMRL | 1.6 | 1.05 | 0.55 | 19.6 | 7.5 | 48 | NR | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | D-C4 | Duplicate | 1998-04-27 | 12:00 | 313 | 939 | 5.88 | BMRL | 21.3 | BMRL | BMRL | 0.007 | BMRL | 1.3 | 1.04 | 0.26 | 19.6 | 7.5 | 48 | NR | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | Avg-A4 | Average | --- | --- | --- | --- | --- | 5.73 | 0.09 | BMRL | 21.1 | 16.5 | BMRL | BMRL | BMRL | 1.8 | 0.022 | 1.2222 | 2.25 | 0.865 | 1.385 | 19.6 | 7.5 | 48 | NR | 20 | 4.65 | BMRL | BMRL | 0 | 2.55 | 11.5 | 6.95 | BMRL | BMRL | 1.45 | NA | NA | NA | 21 | 22.45 | Avg-B4 | Average | --- | --- | --- | --- | 5.78 | 0.065 | 21.4 | BMRL | BMRL | 0.008 | BMRL | 1.6 | 1.04 | 0.56 | 19.6 | 7.5 | 48 | NR | 1.2 | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Avg-C4 | Average | --- | --- | --- | --- | 5.88 | BMRL | 21.3 | BMRL | BMRL | 0.006 | BMRL | 1.3 | 1.04 | 0.26 | 19.6 | 7.5 | 48 | NR | 1.7 | BMRL | BMRL | BMRL | 1.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | RPD-A4 | RPD | --- | --- | --- | --- | --- | 0 | 0 | BMRL | 0 | 6.0606 | BMRL | BMRL | BMRL | 0 | 0 | 0 | 0 | 10.4046 | 6.4982 | 0 | 0 | 0 | NR | 0 | 10.7527 | BMRL | BMRL | 0 | 50.9804 | 8.6957 | 1.4388 | BMRL | BMRL | 6.8966 | NA | NA | NA | 11.4286 | 10.245 | RPD-B4 | RPD | --- | --- | --- | --- | 0 | 15.3846 | 0 | BMRL | BMRL | BMRL | BMRL | 0 | 1.9231 | 3.5714 | 0 | 0 | 0 | NR | 0 | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | RPD-C4 | RPD | --- | --- | --- | --- | 0 | BMRL | 0 | BMRL | BMRL | 33.3333 | BMRL | 0 | 0 | 0 | 0 | 0 | 0 | NR | BMRL | BMRL | BMRL | BMRL | 100 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | A10 | Primary | 1998-05-27 | 11:00 | 1005 | 3015 | 6030 | 5.75 | 0.06 | BMRL | 26.8 | 18 | 11 | BMRL | BMRL | 1.9 | 0.025 | 1.3158 | 2.5 | 0.72 | 1.78 | 25.8 | 7.5 | 48 | 145 | 27 | 1.3 | 6.6 | BMRL | 24.9 | 3.5 | 12 | 9.5 | BMRL | BMRL | 2.2 | NA | NA | NA | 25 | 27.2 | B10 | Primary | 1998-05-27 | 11:00 | 1005 | 6030 | 5.73 | 0.05 | 26.9 | BMRL | BMRL | BMRL | BMRL | 1.3 | 0.31 | 0.99 | 25.8 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C10 | Primary | 1998-05-27 | 11:00 | 1032 | 3096 | 5.57 | 0.06 | 27.1 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.56 | 0.64 | 25.8 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | D-A10 | Duplicate | 1998-05-27 | 11:00 | 1005 | 3015 | 6030 | 5.75 | 0.07 | BMRL | 26.8 | 18 | 11 | BMRL | 21 | 1.9 | 0.023 | 1.2105 | 2.5 | 0.21 | 2.29 | 25.8 | 7.5 | 48 | 130 | 28 | 1.3 | 6.6 | BMRL | 24.4 | 3.2 | 12 | 10 | BMRL | BMRL | 2.3 | NA | NA | NA | 25.2 | 27.5 | D-B10 | Duplicate | 1998-05-27 | 11:00 | 1005 | 6030 | 5.73 | 0.06 | 26.9 | BMRL | BMRL | BMRL | BMRL | 1.3 | 0.67 | 0.63 | 25.8 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | D-C10 | Duplicate | 1998-05-27 | 11:00 | 1032 | 3096 | 5.57 | 0.06 | 27.1 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.24 | 0.96 | 25.8 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | Avg-A10 | Average | --- | --- | --- | --- | --- | 5.75 | 0.065 | BMRL | 26.8 | 18 | 11 | BMRL | 21 | 1.9 | 0.024 | 1.2632 | 2.5 | 0.465 | 2.035 | 25.8 | 7.5 | 48 | 137.5 | 27.5 | 1.3 | 6.6 | BMRL | 24.65 | 3.35 | 12 | 9.75 | BMRL | BMRL | 2.25 | NA | NA | NA | 25.1 | 27.35 | Avg-B10 | Average | --- | --- | --- | --- | 5.73 | 0.055 | 26.9 | BMRL | BMRL | BMRL | BMRL | 1.3 | 0.49 | 0.81 | 25.8 | 7.5 | 48 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Avg-C10 | Average | --- | --- | --- | --- | 5.57 | 0.06 | 27.1 | BMRL | BMRL | BMRL | BMRL | 1.2 | 0.4 | 0.8 | 25.8 | 7.5 | 48 | BMRL | 1 | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | RPD-A10 | RPD | --- | --- | --- | --- | --- | 0 | 15.3846 | BMRL | 0 | 0 | 0 | BMRL | BMRL | 0 | 8.3333 | 8.3333 | 0 | 109.6774 | 25.0614 | 0 | 0 | 0 | 10.9091 | 3.6364 | 0 | 0 | BMRL | 2.0284 | 8.9552 | 0 | 5.1282 | BMRL | BMRL | 4.4444 | NA | NA | NA | 0.79681 | 1.0969 | RPD-B10 | RPD | --- | --- | --- | --- | 0 | 18.1818 | 0 | BMRL | BMRL | BMRL | BMRL | 0 | 73.4694 | 44.4444 | 0 | 0 | 0 | BMRL | 0 | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | RPD-C10 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | BMRL | BMRL | BMRL | BMRL | 0 | 80 | 40 | 0 | 0 | 0 | BMRL | 0 | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | A24 | Primary | 1998-09-22 | 9:00 | 3786 | 11358 | 22716 | 6.02 | 0.05 | 5 | 28.5 | 29 | 19 | 0.1 | 32 | 1.8 | 0.021 | 1.1667 | 3.65 | 1.63 | 2.02 | 27.9 | 7.5 | 48 | 195 | 29 | 11 | 4.2 | BMRL | 34.9 | 4.9 | 12 | 8.4 | BMRL | BMRL | 4.1 | NA | NA | NA | 25.3 | 29.4 | B24 | Primary | 1998-09-22 | 9:00 | 3786 | 22716 | 5.9 | 0.05 | 26.4 | NA | 1.2 | 0.014 | 1.1667 | 2.45 | 1.2 | 1.25 | 27.9 | 7.5 | 48 | 110 | 12 | 8.7 | 4.8 | BMRL | 25.5 | 2.2 | 4.6 | 3.5 | BMRL | BMRL | 3.4 | NA | NA | NA | 10.3 | 13.7 | C24 | Primary | 1998-09-22 | 9:00 | 3862 | 11586 | 5.84 | BMRL | 26 | NA | BMRL | 0.006 | BMRL | 2.25 | 1.51 | 0.74 | 27.9 | 7.5 | 48 | 30 | 2.7 | 2.9 | 2 | BMRL | 7.6 | BMRL | 2.2 | 1.1 | BMRL | BMRL | 1.2 | NA | NA | NA | 3.3 | 4.5
[9 empty] | D-A24 | Duplicate | 1998-09-22 | 9:00 | 3786 | 11358 | 22716 | 6.02 | 0.05 | 5 | 28.5 | 25 | 15 | 0.1 | 31 | 1.8 | 0.023 | 1.2778 | 2.9 | 1.07 | 1.83 | 27.9 | 7.5 | 48 | 210 | 27 | 11 | 4.1 | BMRL | 35.9 | 3.9 | 9.9 | 7.3 | BMRL | BMRL | 4.1 | NA | NA | NA | 21.1 | 25.2 | D-B24 | Duplicate | 1998-09-22 | 9:00 | 3786 | 22716 | 5.9 | 0.05 | 26.4 | NA | 0.94 | 0.014 | 1.4894 | 2.4 | 1.21 | 1.19 | 27.9 | 7.5 | 48 | 99.5 | 14 | 11 | 6.2 | BMRL | 31.2 | 1.9 | 5.1 | 3 | BMRL | BMRL | 3.1 | NA | NA | NA | 10 | 13.1 | D-C24 | Duplicate | 1998-09-22 | 9:00 | 3862 | 11586 | 5.84 | BMRL | 26 | NA | BMRL | 0.009 | BMRL | 2 | 1.22 | 0.78 | 27.9 | 7.5 | 48 | 25 | 2.7 | 3.1 | 2.3 | BMRL | 8.1 | BMRL | 2 | 1.3 | BMRL | BMRL | 1.3 | NA | NA | NA | 3.3 | 4.6
[9 empty] | Avg-A24 | Average | --- | --- | --- | --- | --- | 6.02 | 0.05 | 5 | 28.5 | 27 | 17 | 0.1 | 31.5 | 1.8 | 0.022 | 1.2222 | 3.275 | 1.35 | 1.925 | 27.9 | 7.5 | 48 | 202.5 | 28 | 11 | 4.15 | BMRL | 35.4 | 4.4 | 10.95 | 7.85 | BMRL | BMRL | 4.1 | NA | NA | NA | 23.2 | 27.3 | Avg-B24 | Average | --- | --- | --- | --- | 5.9 | 0.05 | 26.4 | NA | 1.07 | 0.014 | 1.3084 | 2.425 | 1.205 | 1.22 | 27.9 | 7.5 | 48 | 104.75 | 13 | 9.85 | 5.5 | BMRL | 28.35 | 2.05 | 4.85 | 3.25 | BMRL | BMRL | 3.25 | NA | NA | NA | 10.15 | 13.4 | Avg-C24 | Average | --- | --- | --- | --- | 5.84 | BMRL | 26 | NA | BMRL | 0.0075 | BMRL | 2.125 | 1.365 | 0.76 | 27.9 | 7.5 | 48 | 27.5 | 2.7 | 3 | 2.15 | BMRL | 7.85 | BMRL | 2.1 | 1.2 | BMRL | BMRL | 1.25 | NA | NA | NA | 3.3 | 4.55
[9 empty] | RPD-A24 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 14.8148 | 23.5294 | 0 | 3.1746 | 0 | 9.0909 | 9.0909 | 22.9008 | 41.4815 | 9.8701 | 0 | 0 | 0 | 7.4074 | 7.1429 | 0 | 2.4096 | BMRL | 2.8249 | 22.7273 | 19.1781 | 14.0127 | BMRL | BMRL | 0 | NA | NA | NA | 18.1034 | 15.3846 | RPD-B24 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | NA | 24.2991 | 0 | 24.6631 | 2.0619 | 0.82988 | 4.918 | 0 | 0 | 0 | 10.0239 | 15.3846 | 23.3503 | 25.4545 | BMRL | 20.1058 | 14.6341 | 10.3093 | 15.3846 | BMRL | BMRL | 9.2308 | NA | NA | NA | 2.9557 | 4.4776 | RPD-C24 | RPD | --- | --- | --- | --- | 0 | BMRL | 0 | NA | BMRL | 40 | BMRL | 11.7647 | 21.2454 | 5.2632 | 0 | 0 | 0 | 18.1818 | 0 | 6.6667 | 13.9535 | BMRL | 6.3694 | BMRL | 9.5238 | 16.6667 | BMRL | BMRL | 8 | NA | NA | NA | 0 | 2.1978
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [21 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [12 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [21 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [12 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
THIS PAGE INTENTIONALLY LEFT BLANK
Note on N30: CDM: Analytical error
Note on R5: CDM: Formula for calculation of operation times was modified to account for downtime. The modifications were double checked for accuracy.
Note on R10: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R16: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R18: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R19: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R20: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R29: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R31: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R34: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R40: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R41: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R42: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R43: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R44: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R57: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R58: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R61: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R62: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R65: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on R66: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on Z41: R Bharati: Total Calcium was reported to us instead of Ca hardness. Ca hardness = total Ca * 2.5
Note on Z42: R Bharati: Total Calcium was reported to us instead of Ca hardness. Ca hardness = total Ca * 2.5
Note on Z43: R Bharati: Total Calcium was reported to us instead of Ca hardness. Ca hardness = total Ca * 2.5
Note on Z44: R Bharati: Total Calcium was reported to us instead of Ca hardness. Ca hardness = total Ca * 2.5
Note on AA44: R Bharati: Not analyzed because sample bottle was broken
Note on AB5: CDM: No explanation for increasing bromide concentration.
Note on AB42: R Bharati: Alpha Analytical did this one themselves rather than sub to EHL. Their MRL is 50 ug/L
Note on AB43: R Bharati: Alpha Analytical did this one themselves rather than sub to EHL. Their MRL is 50 ug/L
Note on AB44: R Bharati: Alpha Analytical did this one themselves rather than sub to EHL. Their MRL is 50 ug/L
Note on AB45: R Bharati: Alpha Analytical did this one themselves rather than sub to EHL. Their MRL is 50 ug/L
Note on AB46: R Bharati: Alpha Analytical did this one themselves rather than sub to EHL. Their MRL is 50 ug/L
Note on AF68: CDM: Cl2 doses are listed correct as reported. There is no explanation for the large variation in applied Cl2 doses.
Note on AG22: R Bharati: Bottle cracked by Lab
Note on AJ5: Reviewer M.H. (11/8/99): Per consultant, pH was measured to 2 significant figures and rounded.
Note on AK5: Reviewer M.H. (11/8/99): Per consultant, time was measured to within 10 minutes.
Note on AL22: R Bharati: Never sent to EHL (subsontractor) by Alpha.
Note on AL27: Parameswarc: SAMPLE DID NOT MEET RPD < 20% ON ANALYTICAL DUPS
Note on AL29: CDM: EHL changed the MRL from 50ug/L to 25 ug/L for the remaninder of the study.
Note on AL57: Parameswarc: SAMPLE DID NOT MEET RPD < 20% ON ANALYTICAL DUPS
Note on AR60: CDM: No explanation for RPD>20%. Analyses meet QA/QC checks.
Note on BH5: CDM: Formula for calculation of operation times was modified to account for downtime. The modifications were double checked for accuracy.
Note on BH10: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH16: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH18: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH19: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH20: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH29: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH31: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH34: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH40: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH41: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH42: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH43: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH44: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH57: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH58: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH61: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH62: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH65: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BH66: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on BN68: CDM: No explanation for RPD>20%. Analyses meet QA/QC checks.
Note on BU5: Reviewer M.H. (11/8/99): Per consultant, pH was measured to 2 significant figures and rounded.
Note on BU6: R Bharati: Measured values sent to us by Labs
Note on BV5: Reviewer M.H. (11/8/99): Per consultant, time was measured to within 10 minutes.
Note on BV6: R Bharati: Measured values sent to us by Labs
Note on BW57: Parameswarc: B4a = BMRL, B4b = 92, therefore, reject both
Note on BY68: CDM: No explanation for RPD>20%. Analyses meet QA/QC checks.
Note on BZ68: CDM: No explanation for RPD>20%. Analyses meet QA/QC checks.
Note on CC25: R Bharati: Confirmed 06.16.99
Note on CC26: R Bharati: Confirmed 06.16.99
Note on CC27: R Bharati: Confirmed 06.16.99
Note on CS5: CDM: Formula for calculation of operation times was modified to account for downtime. The modifications were double checked for accuracy.
Note on CS10: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS16: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS18: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS19: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS20: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS29: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS31: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS34: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS40: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS41: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS42: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS43: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CS44: R Bharati: Downtime from previous sampling date to this one has been subtracted in formula
Note on CZ60: CDM: No explanation for RPD>20%. Analyses meet QA/QC checks.
Note on CZ68: CDM: No explanation for RPD>20%. Analyses meet QA/QC checks.
Note on DF5: Reviewer M.H. (11/8/99): Per consultant, pH was measured to 2 significant figures and rounded.
Note on DG5: Reviewer M.H. (11/8/99): Per consultant, time was measured to within 10 minutes.
Note on DH29: CDM: Sample did not meet EHL RPD requirements. Also, EHL's MRL changed from 50ug/L to 25 ug/L for the remainder of the study.
Note on DH31: CDM: Unexplained outlier. TOC reported asBMRL. TOX reported as 90 ug/L.
Note on DH57: Parameswarc: c4a+BMRL, C4b = NR due to lab QC failure, therefore reject due to QC
Note on DI43: R Bharati: Confirmed 06.16.99
Note on DJ43: R Bharati: Confirmed 06.16.99
Note on DK43: R Bharati: Confirmed 06.16.99
Note on DL43: R Bharati: Confirmed 06.16.99