## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 |  |  |  | NOTE: HI-4 (10-8-97) MOVED TO WEEK 12 | [5 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 |  |  |  | NOTE: HI-5 (10-22-97) MOVED TO WEEK 14 | [5 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | Stage 1 and 2 -- General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment (from Performance sampling & MDWASD) |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection |  |  |  | NOTE: HI-4 (10-8-97) MOVED TO WEEK 12 |  |  |  | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection |  |  |  | NOTE: HI-5 DUPLICATE (10-22-97) MOVED TO WEEK 20 DUPLICATE | [5 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Miami-Dade Water and Sewer Dept. | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 26 | Alkalinity (mg/L as CaCO3) | 176 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.84 | HI-1 | [7 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.49 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [7 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL 4130871 | Membrane trade name | TFC-S | Temperature normalized MTCW (gfd/psi) | 0.30179 | Calcium Hardness (mg/L as CaCO3) | NA | Antiscalant Addition | King Lee Pre-treat 100 (2 mg/L dose) | Pilot Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 18.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.4 |  | HI-1 |  |  |  |  | System feed flow rate during sample collection (gpm) | 20.6 | HI-2 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 11 |  | HI-2 |  |  |  |  | System feed flow rate during sample collection (gpm) | 17.9 | HI-3 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.7 |  | HI-3 |  |  |  |  | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [7 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | 1029 | Membrane element model number | TFC 4921S |  |  | LSI | 0.14 | Sulfuric Acid Addition | pH ~ 6.75 (85 mg/L dose) | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 18.3 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 20.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.9 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [7 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | NA | Cartridge Filtration | 5 um exclusion size | Pilot Scale | 1997-07-07 | 11:20 | 10.14 | 25.5556 | 85 | 52 | 8.5667 | 0 | 14.8 | 3 |  | 17.8 | 17.8 | 0.83146 | 0 | 13.5573 | 13.7365 | 15.3603 | 44.5731 | 0.30818 | 7.29 | 6.69 | 79.395 | 512.11 | 522.48 | 2831.4 | 2708.366 | 4.3453 | 84.8042 | 1615.423 | 95.0852 | 85 | 70 | 8.2 | 9.7 | 8.1 | 17.8 | 17.8 | 0.42361 | 0.54494 | 14.9231 | 15.1204 | 7.5571 | 61.7429 | 0.24489 | 6.69 | NA | 49.796 | 522.48 | 1065.24 | 1088.5337 | -2.1867 | 90.4693 | 805.5068 | 93.8181 | 70 | 40 | 8 | 2.8 | 6.9 | 9.7 | 9.7 | 0.543 | 0.28866 | 8.6154 | 8.7293 | 10.835 | 36.165 | 0.24137 | NA | NA | 164.5 | 1065.24 | 1687.64 | 1430.7577 | 15.2214 | 68.5155 | 1247.9988 | 86.8189 | 110 | 52 | 9.5 | 2.3 | 3 | 5.3 | 5.3 | 0.55997 | 0.43396 | 19.7143 | 19.975 | 21.5594 | 49.9406 | 0.39997 | NA | 7.34 | 129.129 | 1687.64 | 2831.4 | 2882.4984 | -1.8047 | 75.2854 | 2285.0692 | 94.349 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.67 |  |  |  | 1997-07-07 | 15:50 | 14.79 | 23.3333 | 100 | 60 | 9 | 0 | 16.8 | 3.1 |  | 19.9 | 19.9 | 0.84422 | 0 | 15.3893 | 16.6514 | 16.2728 | 54.7272 | 0.30426 | 7.2 | 6.76 | 71.221 | 506.3 | 509.88 | 2988.7 | 2887.1288 | 3.3985 | 86.0318 | 1698.5044 | 95.8068 | 100 | 80 | 9 | 11.1 | 8.8 | 19.9 | 19.9 | 0.4694 | 0.55779 | 17.0769 | 18.4775 | 7.5468 | 73.4532 | 0.25155 | 6.76 | NA | 47.082 | 509.88 | 1094.94 | 1093.6366 | 0.11904 | 90.7661 | 801.7583 | 94.1277 | 80 | 50 | 8.5 | 3.4 | 7.2 | 10.6 | 10.6 | 0.58226 | 0.32075 | 10.4615 | 11.3195 | 11.8041 | 44.6959 | 0.25326 | NA | NA | 140 | 1094.94 | 1786.84 | 1545.8839 | 13.485 | 72.5426 | 1320.4119 | 89.3972 | 110 | 60 | 9.5 | 2.3 | 3.1 | 5.4 | 5.4 | 0.57346 | 0.42593 | 19.7143 | 21.3311 | 23.0001 | 52.4999 | 0.40631 | NA | 7.35 | 109.186 | 1786.84 | 2988.7 | 3031.551 | -1.4338 | 78.5859 | 2409.1955 | 95.4679 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1997-07-08 | 15:08 | 37.78 | 24.4444 | 100 | 60 | 9.2 | 0 | 16.8 | 3.1 |  | 19.9 | 19.9 | 0.84422 | 0 | 15.3893 | 16.1134 | 15.5858 | 55.2142 | 0.29183 | 7.25 | 6.65 | 68.742 | 472.27 | 488.88 | 3003 | 2765.7569 | 7.9002 | 85.9389 | 1627.3185 | 95.7757 | 100 | 80 | 9 | 11.1 | 8.8 | 19.9 | 19.9 | 0.4694 | 0.55779 | 17.0769 | 17.8805 | 7.2803 | 73.7197 | 0.24255 | 6.65 | NA | 42.421 | 488.88 | 1057.32 | 1052.0271 | 0.50059 | 91.3228 | 770.4536 | 94.494 | 80 | 50 | 8.6 | 3.4 | 7.2 | 10.6 | 10.6 | 0.58226 | 0.32075 | 10.4615 | 10.9538 | 11.3304 | 45.0696 | 0.24304 | NA | NA | 140.7 | 1057.32 | 1769.48 | 1490.1683 | 15.785 | 71.2199 | 1273.7442 | 88.9538 | 110 | 60 | 10 | 2.3 | 3.1 | 5.4 | 5.4 | 0.57346 | 0.42593 | 19.7143 | 20.6419 | 22.8033 | 52.1967 | 0.39546 | NA | 7.31 | 106.183 | 1769.48 | 3003 | 3003.5391 | -0.017951 | 78.2804 | 2386.5095 | 95.5507 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | BDL |  |  |  | 1997-07-09 | 14:10 | 60.7 | 24.4444 | 100 | 60 | 9.2 | 0 | 16.8 | 3.1 |  | 19.9 | 19.9 | 0.84422 | 0 | 15.3893 | 16.1134 | 15.7079 | 55.0921 | 0.29248 | 7.27 | 6.8 | 68.809 | 484.72 | 492.24 | 2845.7 | 2786.9628 | 2.0641 | 86.0212 | 1639.6014 | 95.8033 | 100 | 80 | 9 | 11.1 | 8.8 | 19.9 | 19.9 | 0.4694 | 0.55779 | 17.0769 | 17.8805 | 7.4082 | 73.5918 | 0.24297 | 6.8 | NA | 37.937 | 492.24 | 1092.96 | 1065.2813 | 2.5325 | 92.293 | 778.7606 | 95.1285 | 80 | 50 | 8.8 | 3.4 | 7.2 | 10.6 | 10.6 | 0.58226 | 0.32075 | 10.4615 | 10.9538 | 11.7831 | 44.4169 | 0.24661 | NA | NA | 139.72 | 1092.96 | 1734.76 | 1543.1011 | 11.0482 | 71.6155 | 1318.0306 | 89.3993 | 110 | 60 | 9.8 | 2.3 | 3.1 | 5.4 | 5.4 | 0.57346 | 0.42593 | 19.7143 | 20.6419 | 22.2755 | 52.9245 | 0.39003 | NA | 7.41 | 109.956 | 1734.76 | 2845.7 | 2940.2597 | -3.3229 | 77.6621 | 2337.5099 | 95.296 | Sampling date | MM/DD/YY | 1997-07-30 | 1997-07-30 | 1997-07-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-07-30 | 1997-07-30 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-08-13 | 1997-08-13 | 1997-08-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-08-13 | 1997-08-13 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-08-27 | 1997-08-27 | 1997-08-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-08-27 | 1997-08-27 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1997-07-10 | 0:45 | 70.91 | 24.4444 | 100 | 60 | 9.4 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 16.0175 | 15.4906 | 55.1094 | 0.29065 | 7.26 | 6.97 | 68.943 | 488.87 | 498.12 | 2802.8 | 2737.8875 | 2.316 | 86.1594 | 1618.0037 | 95.739 | 100 | 80 | 9.2 | 11.1 | 8.8 | 19.9 | 19.9 | 0.4694 | 0.55779 | 17.0769 | 17.8805 | 7.4137 | 73.3863 | 0.24365 | 6.97 | NA | 43.483 | 498.12 | 1111.77 | 1071.5826 | 3.6147 | 91.2706 | 784.8513 | 94.4597 | 80 | 50 | 9 | 3.4 | 7.2 | 10.6 | 10.6 | 0.58226 | 0.32075 | 10.4615 | 10.9538 | 12.007 | 43.993 | 0.24899 | NA | NA | 140.42 | 1111.77 | 1708.72 | 1570.4631 | 8.0913 | 71.81 | 1341.1165 | 89.5296 | 110 | 60 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.4741 | 53.5259 | 0.36888 | NA | 7.43 | 110.649 | 1708.72 | 2802.8 | 2807.3938 | -0.1639 | 77.7867 | 2258.0569 | 95.0998 | Sampling time | hh:mm | 12:00 | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:15 | 11:15 | 11:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:15 | 11:15 | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881 (May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.08 |  |  |  | 1997-07-12 | 22:21 | 140.81 | 24.4444 | 100 | 60 | 9.4667 | 0 | 16.45 | 3.2 |  | 19.65 | 19.65 | 0.83715 | 0 | 15.0687 | 15.7777 | 15.5785 | 54.9548 | 0.2871 | 7.44 | 6.85 | 69.345 | 520.41 | 505.68 | 2888.6 | 2748.7146 | 4.8427 | 86.2868 | 1627.1973 | 95.7384 | 100 | 80 | 9.2 | 10.95 | 8.7 | 19.65 | 19.65 | 0.46368 | 0.55725 | 16.8462 | 17.6388 | 7.5614 | 73.2386 | 0.24084 | 6.85 | NA | 41.595 | 505.68 | 1109.79 | 1089.787 | 1.8024 | 91.7744 | 797.7335 | 94.7859 | 80 | 50 | 9.2 | 3.3 | 7.2 | 10.5 | 10.5 | 0.57898 | 0.31429 | 10.1538 | 10.6316 | 11.9031 | 43.8969 | 0.2422 | NA | NA | 141.4 | 1109.79 | 1671.52 | 1553.6354 | 7.0525 | 72.0377 | 1331.7127 | 89.3821 | 110 | 60 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 20.9939 | 54.0061 | 0.3656 | NA | 7.55 | 109.186 | 1671.52 | 2888.6 | 2745.6246 | 4.9496 | 78.4081 | 2208.5723 | 95.0563 | Operation time | hh.hh | 480.1 | 480.1 | 480.1 | --- | --- | --- | --- | --- | Operation time | hh.hh | 480.1 | 480.1 | --- | --- | --- | --- | Operation time | hh.hh | 814.8 | 814.8 | 814.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 814.8 | 814.8 | --- | --- | --- | --- | Operation time | hh.hh | 1147.8 | 1147.8 | 1147.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1147.8 | 1147.8 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 130
E-Mail Address (optional) |  | Stage 1 and 2 -- Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 9.16 |  |  |  | 1997-07-14 | 22:10 | 188.43 | 23.3333 | 100 | 60 | 9.2667 | 0 | 15.8 | 3.2 |  | 19 | 19 | 0.83158 | 0 | 14.4733 | 15.6603 | 15.6942 | 55.0391 | 0.28453 | 7.38 | 6.85 | 63.315 | 516.26 | 515.76 | 2831.4 | 2749.7072 | 2.8852 | 87.7239 | 1632.7336 | 96.1221 | 100 | 80 | 9 | 10.4 | 8.6 | 19 | 19 | 0.45141 | 0.54737 | 16 | 17.3122 | 7.6333 | 73.3667 | 0.23597 | 6.85 | NA | 40.061 | 515.76 | 1040.49 | 1091.0239 | -4.8567 | 92.2326 | 803.392 | 95.0135 | 80 | 49 | 9 | 3.2 | 7 | 10.2 | 10.2 | 0.56263 | 0.31373 | 9.8462 | 10.6537 | 11.4072 | 44.0928 | 0.24162 | NA | NA | 112 | 1040.49 | 1726.08 | 1464.9426 | 15.1289 | 78.2845 | 1252.7163 | 91.0594 | 112 | 60 | 9.8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 20.4037 | 21.6763 | 54.5237 | 0.37422 | NA | 7.55 | 112.959 | 1726.08 | 2831.4 | 2835.1007 | -0.1307 | 78.0985 | 2280.5903 | 95.0469 | pH | --- | 6.19 | 7.04 | 7.37 | --- | --- | --- | --- | --- | pH | --- | 6.22 | 7.04 | --- | --- | --- | --- | pH | --- | 6.15 | 6.95 | 7.45 | --- | --- | --- | --- | --- | pH | --- | 6.13 | 6.95 | --- | --- | --- | --- | pH | --- | 6.41 | 7.22 | 7.66 | --- | --- | --- | --- | --- | pH | --- | 6.35 | 7.22 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | ~20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.8125 | Calcium (mg/L) | 56 |  |  |  | 1997-07-16 | 8:15 | 222.75 | 24.4444 | 98 | 60 | 9.2333 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 16.1358 | 53.6309 | 0.27899 | 7.32 | 6.89 | 71.556 | 527.88 | 540.96 | 3003 | 2829.3045 | 5.7841 | 86.7724 | 1685.1323 | 95.7537 | 98 | 75 | 9 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 8.1165 | 69.3835 | 0.24145 | 6.89 | NA | 39.648 | 540.96 | 1176.12 | 1161.632 | 1.2318 | 92.6708 | 851.296 | 95.3426 | 75 | 46 | 8.9 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 12.6042 | 38.9958 | 0.25611 | NA | NA | 144.2 | 1176.12 | 1860 | 1633.1131 | 12.1982 | 73.3437 | 1404.6166 | 89.7339 | 112 | 60 | 9.8 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 23.1385 | 53.0615 | 0.35519 | NA | 7.58 | 117.81 | 1860 | 3003 | 3003.3122 | -0.010396 | 78.222 | 2431.6561 | 95.1552 | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | NA | --- | --- | --- | --- | Temperature | oC | NA | 25.5 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 25.5 | --- | --- | --- | --- | Temperature | oC | NA | 25 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 25 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 67%
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.875 | Barium (mg/L) | < 0.05 |  |  |  | 1997-07-16 | 14:15 | 228.64 | 24.4444 | 100 | 60 | 9.0667 | 0 | 16.2 | 3.4 |  | 19.6 | 19.6 | 0.82653 | 0 | 14.8397 | 15.538 | 14.9482 | 55.9851 | 0.27754 | 7.36 | 6.79 | 69.613 | 493.85 | 511.56 | 2960.1 | 2617.3075 | 11.5804 | 86.392 | 1564.4337 | 95.5503 | 100 | 79 | 8.9 | 10.8 | 8.8 | 19.6 | 19.6 | 0.4645 | 0.55102 | 16.6154 | 17.3972 | 7.5854 | 73.0146 | 0.23827 | 6.79 | NA | 41.477 | 511.56 | 1106.82 | 1088.48 | 1.657 | 91.8921 | 800.02 | 94.8155 | 79 | 50 | 8.8 | 3.2 | 7.1 | 10.3 | 10.3 | 0.56917 | 0.31068 | 9.8462 | 10.3095 | 11.9739 | 43.7261 | 0.23577 | NA | NA | 129.64 | 1106.82 | 1779.4 | 1547.2392 | 13.0471 | 74.6579 | 1327.0296 | 90.2308 | 110 | 60 | 9.5 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.7444 | 22.0273 | 53.4727 | 0.36924 | NA | 7.56 | 115.115 | 1779.4 | 2960.1 | 2856.2903 | 3.507 | 77.4973 | 2317.8451 | 95.0335 | Alkalinity | mg/L as CaCO3 | 26 | 198 | 764 | 1101 | -44.1099 | 86.8687 | 649.5 | 95.9969 | Alkalinity | mg/L as CaCO3 | 21 | 198 | 431.0127 | 89.3939 | 314.5063 | 93.3229 | Alkalinity | mg/L as CaCO3 | 27 | 203 | 937 | 1062.2941 | -13.3718 | 86.6995 | 632.6471 | 95.7322 | Alkalinity | mg/L as CaCO3 | 19 | 203 | 413.8333 | 90.6404 | 308.4167 | 93.8395 | Alkalinity | mg/L as CaCO3 | 31 | 221 | 988 | 981 | 0.7085 | 85.9729 | 601 | 94.8419 | Alkalinity | mg/L as CaCO3 | 22 | 221 | 409.1848 | 90.0452 | 315.0924 | 93.0179 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | Strontium (mg/L) | 0.49 |  |  |  | 1997-07-16 | 22:35 | 236.94 | 25.5556 | 100 | 60 | 9.2333 | 0 | 15.9 | 3.2 |  | 19.1 | 19.1 | 0.83246 | 0 | 14.5649 | 14.7575 | 15.7169 | 55.0497 | 0.26808 | 7.24 | 6.9 | 63.851 | 473.93 | 514.92 | 2902.9 | 2756.1691 | 5.0546 | 87.5998 | 1635.5445 | 96.096 | 100 | 78 | 8.9 | 10.7 | 8.4 | 19.1 | 19.1 | 0.44978 | 0.56021 | 16.4615 | 16.6792 | 7.7392 | 72.3608 | 0.2305 | 6.9 | NA | 42.126 | 514.92 | 1051.38 | 1117.1695 | -6.2574 | 91.8189 | 816.0448 | 94.8378 | 78 | 48 | 9 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.6646 | 11.2003 | 42.7997 | 0.22581 | NA | NA | 134.4 | 1051.38 | 1506.6 | 1457.4711 | 3.2609 | 73.8989 | 1254.4256 | 89.2859 | 114 | 60 | 9.8 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 18.4663 | 58.7337 | 0.31052 | NA | 7.89 | 116.193 | 1506.6 | 2902.9 | 2419.0546 | 16.6677 | 77.4347 | 1962.8273 | 94.0803 | Total dissolved solids | mg/L | 67 | 379 | 1266 | 2017 | -59.3207 | 82.3219 | 1198 | 94.4073 | Total dissolved solids | mg/L | 71 | 379 | 784.4684 | 81.2665 | 581.7342 | 87.7951 | Total dissolved solids | mg/L | 67 | 380 | 1477 | 1908.1765 | -29.1927 | 82.3684 | 1144.0882 | 94.1438 | Total dissolved solids | mg/L | 51 | 380 | 756.9792 | 86.5789 | 568.4896 | 91.0289 | Total dissolved solids | mg/L | 73 | 386 | 1464 | 1638 | -11.8852 | 81.0881 | 1012 | 92.7866 | Total dissolved solids | mg/L | 53 | 386 | 700.9022 | 86.2694 | 543.4511 | 90.2475 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | Reactive silica (mg/L as SiO2) | 8.41 |  |  |  | 1997-07-17 | 9:15 | 247.65 | 24.4444 | 100 | 60 | 9.1 | 0 | 15.9 | 3.2 |  | 19.1 | 19.1 | 0.83246 | 0 | 14.5649 | 15.2502 | 15.4249 | 55.4751 | 0.2749 | 7.25 | 6.69 | 70.551 | 480.57 | 513.24 | 3017.3 | 2712.851 | 10.0901 | 86.2538 | 1613.0455 | 95.6262 | 100 | 75 | 9 | 10.6 | 8.5 | 19.1 | 19.1 | 0.45141 | 0.55497 | 16.3077 | 17.075 | 7.7004 | 70.7996 | 0.24117 | 6.69 | NA | 38.94 | 513.24 | 1121.67 | 1104.72 | 1.5111 | 92.4129 | 808.98 | 95.1865 | 75 | 46 | 8.8 | 3.2 | 7 | 10.2 | 10.2 | 0.56263 | 0.31373 | 9.8462 | 10.3095 | 12.1035 | 39.5965 | 0.26036 | NA | NA | 136.5 | 1121.67 | 1815.36 | 1572.0334 | 13.4038 | 73.4043 | 1346.8517 | 89.8653 | 110 | 60 | 9.5 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 22.4883 | 53.0117 | 0.35552 | NA | 7.39 | 122.122 | 1815.36 | 3017.3 | 2926.5474 | 3.0077 | 76.2057 | 2370.9537 | 94.8492 | Total hardness | mg/L as CaCO3 | 18 | 221 | 926 | 1286.75 | -38.9579 | 91.8552 | 753.875 | 97.6123 | Total hardness | mg/L as CaCO3 | 12 | 221 | 496.1392 | 94.5701 | 358.5696 | 96.6534 | Total hardness | mg/L as CaCO3 | 18 | 226 | 1100 | 1241.5294 | -12.8663 | 92.0354 | 733.7647 | 97.5469 | Total hardness | mg/L as CaCO3 | 12 | 226 | 471.2083 | 94.6903 | 348.6042 | 96.5577 | Total hardness | mg/L as CaCO3 | 23 | 233 | 1077 | 1073 | 0.3714 | 90.1288 | 653 | 96.4778 | Total hardness | mg/L as CaCO3 | 16 | 233 | 438.2065 | 93.133 | 335.6033 | 95.2325 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | 0.2714¢/therm
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.293 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | Turbidity (ntu) | 0.5 |  |  |  | 1997-07-18 | 8:20 | 271.01 | 24.4444 | 100 | 61 | 9.1667 | 0 | 16 | 3.2 |  | 19.2 | 19.2 | 0.83333 | 0 | 14.6565 | 15.3461 | 16.1005 | 55.2328 | 0.27784 | 7.35 | 6.67 | 66.665 | 507.13 | 526.68 | 3024.45 | 2826.755 | 6.5366 | 87.3424 | 1676.7175 | 96.0241 | 100 | 79 | 9 | 10.8 | 8.4 | 19.2 | 19.2 | 0.45141 | 0.5625 | 16.6154 | 17.3972 | 7.9673 | 72.5327 | 0.23985 | 6.67 | NA | 41.713 | 526.68 | 1162.26 | 1150.209 | 1.0369 | 92.08 | 838.4445 | 95.025 | 79 | 48 | 9 | 3.2 | 7 | 10.2 | 10.2 | 0.56263 | 0.31373 | 9.8462 | 10.3095 | 12.6108 | 41.8892 | 0.24611 | NA | NA | 135.8 | 1162.26 | 1876.12 | 1631.4989 | 13.0387 | 74.2158 | 1396.8794 | 90.2783 | 115 | 61 | 9.5 | 2 | 3.2 | 5.2 | 5.2 | 0.56672 | 0.38462 | 17.1429 | 17.9495 | 23.0475 | 55.4525 | 0.32369 | NA | 7.47 | 120.12 | 1876.12 | 3024.45 | 2973.62 | 1.6806 | 77.193 | 2424.87 | 95.0463 | Calcium hardness | mg/L as CaCO3 | 17 | 187 | 801 | 1079.5 | -34.769 | 90.9091 | 633.25 | 97.3154 | Calcium hardness | mg/L as CaCO3 | 12 | 187 | 417.3797 | 93.5829 | 302.1899 | 96.029 | Calcium hardness | mg/L as CaCO3 | 17 | 199 | 972 | 1087.5882 | -11.8918 | 91.4573 | 643.2941 | 97.3574 | Calcium hardness | mg/L as CaCO3 | 12 | 199 | 413.2708 | 93.9698 | 306.1354 | 96.0802 | Calcium hardness | mg/L as CaCO3 | 19 | 201 | 948 | 929 | 2.0042 | 90.5473 | 565 | 96.6372 | Calcium hardness | mg/L as CaCO3 | 12 | 201 | 379.7283 | 94.0299 | 290.3641 | 95.8673 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 0.21*
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 16.375 | SDI | 4.67 |  |  |  | 1997-07-22 | 15:44 | 292.12 | 24.4444 | 95 | 60 | 9.3 | 0 | 15.1 | 3.1 |  | 18.2 | 18.2 | 0.82967 | 0 | 13.8321 | 14.4829 | 14.5489 | 53.6511 | 0.26995 | 7.25 | 6.79 | 65.392 | 460.65 | 488.88 | 2789.93 | 2551.6764 | 8.5398 | 86.6241 | 1520.2782 | 95.6987 | 95 | 70 | 9 | 9.9 | 8.3 | 18.2 | 18.2 | 0.43342 | 0.54396 | 15.2308 | 15.9474 | 7.1489 | 66.3511 | 0.24035 | 6.79 | NA | 41.064 | 488.88 | 1066.23 | 1023.022 | 4.0524 | 91.6004 | 755.951 | 94.5679 | 70 | 41 | 9 | 3.1 | 6.8 | 9.9 | 9.9 | 0.54627 | 0.31313 | 9.5385 | 9.9873 | 11.3822 | 35.1178 | 0.28439 | NA | NA | 139.3 | 1066.23 | 1700.04 | 1488.801 | 12.4255 | 71.5063 | 1277.5155 | 89.096 | 110 | 60 | 9.9 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 21.2134 | 53.8866 | 0.34975 | NA | 7.35 | 115.423 | 1700.04 | 2789.93 | 2773.4902 | 0.58925 | 76.3903 | 2236.7651 | 94.8397 | Turbidity | ntu | BMRL | 0.12 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.15 | 0.12 | 0.080506 | -25 | 0.10025 | -49.6212 | Turbidity | ntu | 0.02 | 0.09 | 31 | 0.43176 | 98.6072 | 77.7778 | 0.26088 | 92.3337 | Turbidity | ntu | 0.02 | 0.09 | 0.17021 | 77.7778 | 0.1301 | 84.6277 | Turbidity | ntu | 0.01 | 0.11 | 19 | 0.51 | 97.3158 | 90.9091 | 0.31 | 96.7742 | Turbidity | ntu | 0.04 | 0.11 | 0.1762 | 63.6364 | 0.1431 | 72.0471 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | Feed flow rate to system, QF-sys (gpm) | 19.2647 | MFI | NA |  |  |  | 1997-07-22 | 23:00 | 296.82 | 24.4444 | 100 | 60 | 9.3333 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 15.0722 | 55.5945 | 0.26914 | 7.3 | 6.85 | 62.176 | 486.38 | 500.64 | 2931.5 | 2638.152 | 10.0068 | 87.5807 | 1569.396 | 96.0382 | 100 | 78 | 9 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 7.4551 | 72.5449 | 0.23093 | 6.85 | NA | 40.179 | 500.64 | 1109.79 | 1070.7346 | 3.5192 | 91.9745 | 785.6873 | 94.8861 | 78 | 48 | 9 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.9821 | 42.0179 | 0.23769 | NA | NA | 128.8 | 1109.79 | 1769.48 | 1544.2284 | 12.7298 | 74.2729 | 1327.0092 | 90.294 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 21.9434 | 53.0566 | 0.35522 | NA | 7.56 | 117.271 | 1769.48 | 2931.5 | 2853.7422 | 2.6525 | 76.5758 | 2311.6111 | 94.9269 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.41 | 19.8 | 45.3261 | 97.9293 | 32.563 | 98.7409 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.1 | 14.96 | 31.9871 | 99.3316 | 23.4735 | 99.574 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.29 | 23.8 | 45.0866 | 94.5798 | 34.4433 | 96.2547 | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 6.5 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.8897 | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1997-07-23 | 6:40 | 306.67 | 25.5556 | 98 | 60 | 9.8667 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.479 | 15.0056 | 54.1278 | 0.2675 | 7.38 | 6.89 | 65.794 | 492.19 | 502.32 | 2827.11 | 2630.3843 | 6.9585 | 86.902 | 1566.3521 | 95.7995 | 98 | 75 | 9.8 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.2116 | 7.4498 | 69.2502 | 0.2341 | 6.89 | NA | 42.185 | 502.32 | 1056.33 | 1072.011 | -1.4845 | 91.602 | 787.1655 | 94.6409 | 75 | 48 | 9.8 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.6646 | 11.2949 | 40.4051 | 0.23919 | NA | NA | 131.6 | 1056.33 | 1732.28 | 1465.8533 | 15.3801 | 73.8016 | 1261.0916 | 89.5646 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.4524 | 53.5476 | 0.34059 | NA | 7.59 | 117.04 | 1732.28 | 2827.11 | 2792.2812 | 1.232 | 76.7001 | 2262.2806 | 94.8265 | Total organic carbon | mg/L | 1.04 | 19.8 | 77.9 | 118.29 | -51.8485 | 94.7475 | 69.045 | 98.4937 | UV254 | cm-1 | 0.016 | 0.669 | 1.5286 | 97.6084 | 1.0988 | 98.5439 | Total organic carbon | mg/L | 0.26 | 14.96 | 74.4 | 86.7306 | -16.5734 | 98.262 | 50.8453 | 99.4886 | UV254 | cm-1 | 0.017 | 0.489 | 1.0298 | 96.5235 | 0.75942 | 97.7614 | Total organic carbon | mg/L | 1.48 | 23.8 | 60.7 | 113.08 | -86.2932 | 93.7815 | 68.44 | 97.8375 | UV254 | cm-1 | 0.014 | 0.458 | 0.87787 | 96.9432 | 0.66793 | 97.904 | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | *Treatment plant operations only consisting of staffing, power,
Plant Name | Hialeah Water Treatment | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  | TOC (mg/L) | 11.35 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1997-07-23 | 15:20 | 315.74 | 24.4444 | 97 | 60 | 9.3333 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 14.7277 | 54.439 | 0.27485 | 7.27 | 6.83 | 58.759 | 473.93 | 487.2 | 2789.93 | 2575.8499 | 7.6733 | 87.9394 | 1531.5249 | 96.1634 | 97 | 73 | 9.1 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 7.2862 | 68.6138 | 0.24416 | 6.83 | NA | 37.17 | 487.2 | 1049.4 | 1044.38 | 0.47837 | 92.3707 | 765.79 | 95.1462 | 73 | 44 | 9.1 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.3573 | 38.0427 | 0.26253 | NA | NA | 119.56 | 1049.4 | 1678.96 | 1461.1863 | 12.9708 | 75.4598 | 1255.2931 | 90.4755 | 110 | 60 | 9.8 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 20.7954 | 54.4046 | 0.34642 | NA | 7.5 | 113.19 | 1678.96 | 2789.93 | 2706.4966 | 2.9905 | 76.7672 | 2192.7283 | 94.8379 | UV254 | cm-1 | 0.013 | 0.669 | 0.943 | 4.113 | -336.1612 | 98.0568 | 2.391 | 99.4563 | SUVA | L/(mg*m) | 3.9024 | 3.3788 | --- | --- | --- | --- | UV254 | cm-1 | 0.011 | 0.489 | 0.93 | 2.8228 | -203.5231 | 97.7505 | 1.6559 | 99.3357 | SUVA | L/(mg*m) | 17 | 3.2687 | --- | --- | --- | --- | UV254 | cm-1 | 0.013 | 0.458 | 0.9 | 2.238 | -148.6667 | 97.1616 | 1.348 | 99.0356 | SUVA | L/(mg*m) | 1.0853 | 1.9244 | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | chemicals, and miscellaneous
Treatment Plant Category | Softening | Feed spacer thickness, T (ft) | 0.00258 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1997-07-23 | 23:20 | 324.48 | 24.4444 | 100 | 60 | 9.8667 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 14.886 | 55.2473 | 0.27083 | 7.36 | 6.87 | 60.032 | 480.57 | 493.08 | 2902.9 | 2604.189 | 10.2901 | 87.8251 | 1548.6345 | 96.1236 | 100 | 74 | 9.9 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 7.3585 | 69.7415 | 0.24021 | 6.87 | NA | 38.586 | 493.08 | 1078.11 | 1055.7869 | 2.0706 | 92.1745 | 774.4334 | 95.0175 | 74 | 44 | 9.8 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.7499 | 37.4501 | 0.26668 | NA | NA | 116.13 | 1078.11 | 1758.32 | 1504.1297 | 14.4564 | 76.448 | 1291.1199 | 91.0055 | 110 | 60 | 9.9 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 21.8668 | 53.2332 | 0.35405 | NA | 7.59 | 111.881 | 1758.32 | 2902.9 | 2838.7956 | 2.2083 | 77.3098 | 2298.5578 | 95.1326 | SUVA | L/(mg*m) | 1.25 | 3.3788 | 1.2105 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 4.2308 | 3.2687 | 1.25 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.87838 | 1.9244 | 1.4827 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | Hialeah WTP | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 11.1397 | [5 empty] | 1997-07-24 | 4:40 | 342.99 | 24.4444 | 98 | 60 | 9.3 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 14.8782 | 54.8218 | 0.27293 | 7.3 | 6.74 | 62.779 | 478.08 | 495.6 | 2875.73 | 2605.6024 | 9.3934 | 87.3327 | 1550.6012 | 95.9513 | 98 | 72 | 9 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 7.3792 | 68.6208 | 0.24414 | 6.74 | NA | 39.825 | 495.6 | 1061.28 | 1059.8929 | 0.1307 | 91.9643 | 777.7464 | 94.8794 | 72 | 44 | 9.1 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.5212 | 37.3788 | 0.26719 | NA | NA | 118.02 | 1061.28 | 1724.84 | 1479.0094 | 14.2524 | 76.1864 | 1270.1447 | 90.7081 | 110 | 60 | 9.8 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 21.3986 | 53.8014 | 0.35031 | NA | 7.54 | 113.652 | 1724.84 | 2875.73 | 2782.1821 | 3.253 | 77.0678 | 2253.5111 | 94.9567 | Bromide | mg/L | 38 | 159 | --- | 794.25 | --- | 76.1006 | 476.625 | 92.0273 | [8 empty] | Bromide | mg/L | 34.05 | 169.9 | --- | 833.1676 | --- | 79.9588 | 501.5338 | 93.2108 | [8 empty] | Bromide | mg/L | 41.21 | 179.87 | --- | 734.51 | --- | 77.089 | 457.19 | 90.9862 | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 302 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4522 | [5 empty] | 1997-07-25 | 7:00 | 354.82 | 25.5556 | 100 | 60 | 9.8667 | 0 | 15.7 | 3.2 |  | 18.9 | 18.9 | 0.83069 | 0 | 14.3817 | 14.5719 | 15.0272 | 55.1062 | 0.26443 | 7.41 | 6.89 | 63.784 | 496.34 | 498.96 | 2688.4 | 2634.0422 | 2.0219 | 87.2166 | 1566.5011 | 95.9283 | 100 | 75 | 9.8 | 10.5 | 8.4 | 18.9 | 18.9 | 0.4465 | 0.55556 | 16.1538 | 16.3675 | 7.4763 | 70.2237 | 0.23308 | 6.89 | NA | 38.881 | 498.96 | 1082.07 | 1074.0587 | 0.74036 | 92.2076 | 786.5094 | 95.0565 | 75 | 48 | 9.8 | 3.1 | 7.1 | 10.2 | 10.2 | 0.5659 | 0.30392 | 9.5385 | 9.6646 | 11.6667 | 40.0333 | 0.24141 | NA | NA | 124.46 | 1082.07 | 1732.28 | 1500.1814 | 13.3984 | 75.0561 | 1291.1257 | 90.3603 | 112 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.4862 | 54.5138 | 0.33456 | NA | 7.62 | 114.499 | 1732.28 | 2688.4 | 2793.9488 | -3.9261 | 77.0525 | 2263.1144 | 94.9406 | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 2.5 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4130871 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 0.57721 | [5 empty] | 1997-07-25 | 17:30 | 365.38 | 24.4444 | 98 | 60 | 9.3667 | 0 | 15.7 | 3.2 |  | 18.9 | 18.9 | 0.83069 | 0 | 14.3817 | 15.0584 | 14.8553 | 54.7781 | 0.2749 | 7.36 | 6.79 | 62.042 | 473.1 | 492.24 | 2778.49 | 2602.8989 | 6.3197 | 87.396 | 1547.5695 | 95.991 | 98 | 74 | 9 | 10.5 | 8.4 | 18.9 | 18.9 | 0.4465 | 0.55556 | 16.1538 | 16.9139 | 7.3987 | 69.6013 | 0.24301 | 6.79 | NA | 36.934 | 492.24 | 1086.03 | 1061.3725 | 2.2704 | 92.4967 | 776.8062 | 95.2454 | 74 | 46 | 9.2 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.7723 | 39.0277 | 0.2559 | NA | NA | 122.22 | 1086.03 | 1733.52 | 1512.8601 | 12.729 | 75.1706 | 1299.4451 | 90.5944 | 110 | 60 | 9.9 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 21.5118 | 53.5882 | 0.3517 | NA | 7.58 | 113.806 | 1733.52 | 2778.49 | 2796.4573 | -0.64666 | 76.88 | 2264.9887 | 94.9754 | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.41 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.36 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.64 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.36 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | [5 empty] | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 23 | Stage 1 and 2 -- Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1997-07-26 | 7:00 | 379.12 | 25.5556 | 100 | 60 | 9.8667 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.479 | 14.8164 | 55.317 | 0.26175 | 7.33 | 6.91 | 67.938 | 496.34 | 498.96 | 2808.52 | 2600.1923 | 7.4177 | 86.3841 | 1549.5761 | 95.6157 | 100 | 78 | 9.8 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.2116 | 7.4518 | 71.7482 | 0.22595 | 6.91 | NA | 38.704 | 498.96 | 1065.24 | 1068.8008 | -0.33427 | 92.2431 | 783.8804 | 95.0625 | 78 | 48 | 9.8 | 3.1 | 7.1 | 10.2 | 10.2 | 0.5659 | 0.30392 | 9.5385 | 9.6646 | 11.3874 | 41.8126 | 0.23114 | NA | NA | 130.55 | 1065.24 | 1758.32 | 1473.3441 | 16.2073 | 73.8356 | 1269.292 | 89.7147 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.83 | 53.17 | 0.34301 | NA | 7.62 | 114.653 | 1758.32 | 2808.52 | 2836.9765 | -1.0132 | 77.0216 | 2297.6482 | 95.01 | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.2 |  |  |  |  | SDS-Cl2 demand | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.86 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.3 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | [5 empty] | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 26 | Design cross-flow velocity (fps) | 0.75 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1997-07-26 | 23:15 | 395.48 | 25.5556 | 100 | 60 | 9.8667 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.479 | 14.7558 | 55.3775 | 0.26146 | 7.37 | 6.91 | 62.98 | 480.57 | 492.24 | 2874.3 | 2584.8825 | 10.0691 | 87.2054 | 1538.5612 | 95.9066 | 100 | 78 | 9.8 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.2116 | 7.3219 | 71.8781 | 0.22554 | 6.91 | NA | 40.002 | 492.24 | 1080.09 | 1052.1537 | 2.5865 | 91.8735 | 772.1969 | 94.8197 | 78 | 48 | 9.8 | 3.1 | 7.1 | 10.2 | 10.2 | 0.5659 | 0.30392 | 9.5385 | 9.6646 | 11.6144 | 41.5856 | 0.2324 | NA | NA | 126.77 | 1080.09 | 1740.96 | 1496.3283 | 14.0515 | 74.2463 | 1288.2092 | 90.1592 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.6096 | 53.3904 | 0.3416 | NA | 7.53 | 113.883 | 1740.96 | 2874.3 | 2808.7293 | 2.2813 | 76.8643 | 2274.8446 | 94.9938 | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.9 |  |  |  |  | SDS-Chlorination temp. | oC | NA | NA | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.6 |  |  |  |  | SDS-Chlorination temp. | oC | 23 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.2 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | [5 empty] | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 60 | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1.8603 | [5 empty] | 1997-07-27 | 7:15 | 403.18 | 25.5556 | 100 | 60 | 9.8667 | 0 | 15.7 | 3.2 |  | 18.9 | 18.9 | 0.83069 | 0 | 14.3817 | 14.5719 | 14.2977 | 55.8357 | 0.26098 | 7.38 | 6.91 | 89.11 | 506.3 | 503.16 | 2788.5 | 2534.5928 | 9.1055 | 82.2899 | 1518.8764 | 94.1332 | 100 | 76 | 9.8 | 10.5 | 8.4 | 18.9 | 18.9 | 0.4465 | 0.55556 | 16.1538 | 16.3675 | 7.486 | 70.7139 | 0.23146 | 6.91 | NA | 42.48 | 503.16 | 1075.14 | 1079.01 | -0.35995 | 91.5574 | 791.085 | 94.6302 | 76 | 49 | 9.8 | 3.1 | 7.1 | 10.2 | 10.2 | 0.5659 | 0.30392 | 9.5385 | 9.6646 | 11.5464 | 41.1536 | 0.23484 | NA | NA | 127.4 | 1075.14 | 1754.6 | 1488.942 | 15.1407 | 74.68 | 1282.041 | 90.0627 | 112 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.8092 | 54.1908 | 0.33655 | NA | 7.62 | 112.497 | 1754.6 | 2788.5 | 2832.2301 | -1.5682 | 77.6419 | 2293.415 | 95.0948 | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NA | NA | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.45 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 17 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.0478 | [5 empty] | 1997-07-27 | 20:00 | 416.27 | 24.4444 | 100 | 60 | 9.8 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 14.6741 | 55.5259 | 0.26947 | 7.36 | 6.88 | 66.196 | 493.02 | 493.08 | 2835.69 | 2574.1395 | 9.2235 | 86.575 | 1533.6098 | 95.6836 | 100 | 72 | 9.6 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 7.3088 | 69.0912 | 0.24247 | 6.88 | NA | 41.654 | 493.08 | 1078.11 | 1051.9884 | 2.4229 | 91.5523 | 772.5342 | 94.6081 | 72 | 48 | 9.8 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.5661 | 38.6339 | 0.25851 | NA | NA | 131.18 | 1078.11 | 1763.28 | 1497.4647 | 15.075 | 73.3958 | 1287.7874 | 89.8135 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 21.9204 | 53.0796 | 0.35507 | NA | 7.59 | 112.805 | 1763.28 | 2835.69 | 2846.4042 | -0.37783 | 77.1224 | 2304.8421 | 95.1057 | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NA | NA | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 5 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -0.077206 | [5 empty] | 1997-07-27 | 23:05 | 419.2 | 25.5556 | 100 | 60 | 9.9 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.479 | 14.8989 | 55.2011 | 0.2623 | 7.4 | 6.88 | 62.176 | 486.38 | 495.6 | 3008.72 | 2608.542 | 13.3006 | 87.4544 | 1552.071 | 95.994 | 100 | 75 | 9.9 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.2116 | 7.406 | 70.194 | 0.23095 | 6.88 | NA | 38.173 | 495.6 | 1085.04 | 1061.9382 | 2.1291 | 92.2976 | 778.7691 | 95.0983 | 75 | 48 | 9.8 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.6646 | 11.7063 | 39.9937 | 0.24165 | NA | NA | 126.63 | 1085.04 | 1758.32 | 1509.4787 | 14.1522 | 74.4492 | 1297.2594 | 90.2387 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.8698 | 53.1302 | 0.34327 | NA | 7.57 | 111.65 | 1758.32 | 3008.72 | 2838.9472 | 5.6427 | 77.4718 | 2298.6336 | 95.1428 | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | Chloride ion rejection = 85 % | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1997-07-28 | 6:40 | 426.6 | 25.5556 | 100 | 60 | 9.9 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.479 | 15.0077 | 55.0923 | 0.26281 | 7.37 | 6.9 | 64.052 | 498.83 | 500.64 | 2781.35 | 2629.0065 | 5.4773 | 87.206 | 1564.8232 | 95.9068 | 100 | 75 | 9.8 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.2116 | 7.4828 | 70.2172 | 0.23088 | 6.9 | NA | 38.468 | 500.64 | 1055.34 | 1072.853 | -1.6595 | 92.3162 | 786.7465 | 95.1105 | 75 | 48 | 9.8 | 3.1 | 7.1 | 10.2 | 10.2 | 0.5659 | 0.30392 | 9.5385 | 9.6646 | 11.341 | 40.359 | 0.23947 | NA | NA | 124.46 | 1055.34 | 1729.8 | 1461.7806 | 15.4942 | 75.1398 | 1258.5603 | 90.1109 | 111 | 60 | 10.1 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.238 | 21.488 | 53.912 | 0.33829 | NA | 7.63 | 111.881 | 1729.8 | 2781.35 | 2791.5593 | -0.36706 | 77.6524 | 2260.6797 | 95.051 | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1997-07-30 | 1997-07-30 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1997-08-13 | 1997-08-13 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 2.71 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1997-08-27 | 1997-08-27 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | at 500 mg/L NaCL solution | meet the manufacturer's minimum flow requirement. | [6 empty] | 1997-07-28 | 14:15 | 434.15 | 24.4444 | 98 | 60 | 9.4667 | 0 | 15.6 | 3.2 |  | 18.8 | 18.8 | 0.82979 | 0 | 14.2901 | 14.9625 | 14.1656 | 55.3678 | 0.27024 | 7.39 | 6.86 | 62.511 | 443.22 | 474.6 | 2874.3 | 2483.5339 | 13.5952 | 86.8287 | 1479.0669 | 95.7736 | 98 | 74 | 9.2 | 10.4 | 8.4 | 18.8 | 18.8 | 0.44487 | 0.55319 | 16 | 16.7529 | 7.0469 | 69.7531 | 0.24017 | 6.86 | NA | 39.353 | 474.6 | 1061.28 | 1013.4772 | 4.5043 | 91.7082 | 744.0386 | 94.7109 | 74 | 46 | 9.2 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.4255 | 39.3745 | 0.25365 | NA | NA | 125.86 | 1061.28 | 1693.84 | 1475.5374 | 12.888 | 73.4808 | 1268.4087 | 90.0773 | 110 | 60 | 10 | 2.1 | 3.2 | 5.3 | 5.3 | 0.57346 | 0.39623 | 18 | 18.847 | 21.0053 | 53.9947 | 0.34905 | NA | 7.6 | 112.266 | 1693.84 | 2874.3 | 2731.7479 | 4.9595 | 76.3451 | 2212.794 | 94.9265 | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:15 | 11:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.88 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1997-07-28 | 20:30 | 440.69 | 24.4444 | 100 | 60 | 9.6667 | 0 | 15.7 | 3.2 |  | 18.9 | 18.9 | 0.83069 | 0 | 14.3817 | 15.0584 | 15.222 | 55.1113 | 0.27324 | 7.33 | 6.83 | 63.181 | 483.06 | 504 | 2960.1 | 2666.7682 | 9.9095 | 87.4641 | 1585.3841 | 96.0148 | 100 | 78 | 9.5 | 10.4 | 8.5 | 18.9 | 18.9 | 0.44814 | 0.55026 | 16 | 16.7529 | 7.489 | 72.011 | 0.23264 | 6.83 | NA | 39.353 | 504 | 1096.92 | 1072.5093 | 2.2254 | 92.1919 | 788.2546 | 95.0076 | 78 | 48 | 9.5 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.8471 | 41.6529 | 0.23977 | NA | NA | 126.98 | 1096.92 | 1771.96 | 1526.4649 | 13.8544 | 74.8056 | 1311.6924 | 90.3194 | 110 | 60 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 22.357 | 52.643 | 0.37506 | NA | 7.63 | 108.185 | 1771.96 | 2960.1 | 2915.8053 | 1.4964 | 78.5347 | 2343.8827 | 95.3844 | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 480.1 | 480.1 | --- | --- | --- | --- | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 814.8 | 814.8 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1147.8 | 1147.8 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1997-07-29 | 14:30 | 458.53 | 24.4444 | 98 | 60 | 9.3667 | 0 | 15.6 | 3.15 |  | 18.75 | 18.75 | 0.832 | 0 | 14.2901 | 14.9625 | 14.3098 | 55.3236 | 0.27045 | 7.25 | 6.83 | 62.109 | 460.65 | 473.76 | 2812.81 | 2512.4126 | 10.6796 | 86.8902 | 1493.0863 | 95.8402 | 98 | 74 | 9 | 10.4 | 8.35 | 18.75 | 18.75 | 0.44323 | 0.55467 | 16 | 16.7529 | 7.0991 | 69.9009 | 0.23967 | 6.83 | NA | 36.285 | 473.76 | 1075.14 | 1018.639 | 5.2552 | 92.3411 | 746.1995 | 95.1374 | 74 | 46 | 9.1 | 3.1 | 7 | 10.1 | 10.1 | 0.55936 | 0.30693 | 9.5385 | 9.9873 | 11.6392 | 39.2608 | 0.25438 | NA | NA | 122.22 | 1075.14 | 1682.68 | 1497.1474 | 11.026 | 74.2021 | 1286.1437 | 90.4972 | 110 | 60 | 10 | 2.1 | 3.15 | 5.25 | 5.25 | 0.56672 | 0.4 | 18 | 18.847 | 20.9235 | 54.0765 | 0.34852 | NA | 7.59 | 113.421 | 1682.68 | 2812.81 | 2728.8527 | 2.9848 | 76.0594 | 2205.7663 | 94.858 | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.48 | 7.2 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.42 | 7.2 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.25 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.67 | 7.45 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 8 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 0.73529 | [5 empty] | 1997-07-29 | 23:30 | 468.29 | 25.5556 | 100 | 51 | 9.7 | 0 | 15.3 | 3 |  | 18.3 | 18.3 | 0.83607 | 0 | 14.0153 | 14.2006 | 14.5779 | 51.2221 | 0.27724 | 7.3 | 6.9 | 63.114 | 461.48 | 473.76 | 2811.38 | 2568.0546 | 8.655 | 86.6781 | 1520.9073 | 95.8502 | 100 | 79 | 9.8 | 10.4 | 7.9 | 18.3 | 18.3 | 0.42851 | 0.56831 | 16 | 16.2116 | 7.2494 | 72.4506 | 0.22376 | 6.9 | NA | 36.58 | 473.76 | 1074.15 | 1049.2881 | 2.3146 | 92.2788 | 761.5241 | 95.1965 | 79 | 50 | 9.8 | 3.1 | 6.8 | 9.9 | 9.9 | 0.54627 | 0.31313 | 9.5385 | 9.6646 | 11.69 | 43.01 | 0.22471 | NA | NA | 122.15 | 1074.15 | 1683.92 | 1508.15 | 10.4381 | 74.2169 | 1291.15 | 90.5394 | 99 | 51 | 9.5 | 1.8 | 3 | 4.8 | 4.8 | 0.52624 | 0.375 | 15.4286 | 15.6326 | 20.4195 | 45.0805 | 0.34677 | NA | 7.55 | 113.19 | 1683.92 | 2811.38 | 2626.358 | 6.5812 | 76.1082 | 2155.139 | 94.7479 | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.84 | 0 | --- | -23.36 | --- | #DIV/0! | -11.68 | 150 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 to 350 psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 0.48529 | [5 empty] | 1997-07-30 | 8:10 | 476.4 | 24.4444 | 100 | 50 | 9.7333 | 0 | 15.3 | 2.95 |  | 18.25 | 18.25 | 0.83836 | 0 | 14.0153 | 14.6747 | 16.3659 | 48.9008 | 0.30009 | 7.42 | 6.9 | 61.975 | 493.85 | 517.44 | 3031.6 | 2879.6822 | 5.0111 | 88.0228 | 1698.5611 | 96.3513 | 100 | 78 | 9.8 | 10.3 | 7.95 | 18.25 | 18.25 | 0.42851 | 0.56438 | 15.8462 | 16.5918 | 7.7894 | 71.4106 | 0.23234 | 6.9 | NA | 44.722 | 517.44 | 1141.47 | 1129.8923 | 1.0143 | 91.3571 | 823.6661 | 94.5704 | 78 | 45 | 9.9 | 3.2 | 6.7 | 9.9 | 9.9 | 0.543 | 0.32323 | 9.8462 | 10.3095 | 12.4618 | 39.1382 | 0.26341 | NA | NA | 135.52 | 1141.47 | 1881.08 | 1621.9237 | 13.777 | 73.8095 | 1381.6969 | 90.1918 | 100 | 50 | 9.5 | 1.8 | 2.95 | 4.75 | 4.75 | 0.51949 | 0.37895 | 15.4286 | 16.1545 | 22.6916 | 42.8084 | 0.37737 | NA | 7.65 | 142.373 | 1881.08 | 3031.6 | 2941.986 | 2.956 | 72.4851 | 2411.533 | 94.0962 | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 54 | 387 | 613.7234 | 72.7273 | 500.3617 | 89.2078 | SDS-MCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 54 | 414 | 620.5574 | 73.399 | 517.2787 | 89.5608 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 62 | 444 | 657.661 | 71.9457 | 550.8305 | 88.7443 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 4 to 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | -2.1397 | [5 empty] | 1997-07-30 | 14:30 | 482.11 | 24.4444 | 98 | 50 | 9.0333 | 0 | 15.4 | 2.9 |  | 18.3 | 18.3 | 0.84153 | 0 | 14.1069 | 14.7707 | 15.5271 | 49.4396 | 0.29876 | 7.39 | 6.73 | 64.923 | 476.42 | 489.72 | 2984.41 | 2745.5386 | 8.004 | 86.7428 | 1617.6293 | 95.9865 | 98 | 75 | 9.1 | 10.4 | 7.9 | 18.3 | 18.3 | 0.42851 | 0.56831 | 16 | 16.7529 | 7.3781 | 70.0219 | 0.23925 | 6.73 | NA | 44.781 | 489.72 | 1128.6 | 1075.4625 | 4.7083 | 90.8558 | 782.5912 | 94.2779 | 75 | 45 | 9 | 3.2 | 6.6 | 9.8 | 9.8 | 0.53646 | 0.32653 | 9.8462 | 10.3095 | 12.3983 | 38.6017 | 0.26707 | NA | NA | 130.69 | 1128.6 | 1842.64 | 1612.4352 | 12.4932 | 73.3133 | 1370.5176 | 90.4642 | 95 | 50 | 9 | 1.8 | 2.9 | 4.7 | 4.7 | 0.51274 | 0.38298 | 15.4286 | 16.1545 | 22.3016 | 41.1984 | 0.39212 | NA | 7.53 | 140.679 | 1842.64 | 2984.41 | 2899.0296 | 2.8609 | 71.2736 | 2370.8348 | 94.0663 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 126 | 697 | 1085.766 | 66.7546 | 891.383 | 85.8647 | SDS-DCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 123 | 722 | 1065.6885 | 67.6316 | 893.8443 | 86.2392 | SDS-DCAA* | mg/L | 1.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 136 | 719 | 1045.0847 | 64.7668 | 882.0424 | 84.5812 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1997-07-30 | 20:45 | 488.32 | 24.4444 | 95 | 50 | 9.4 | 0 | 15.4 | 2.9 |  | 18.3 | 18.3 | 0.84153 | 0 | 14.1069 | 14.7707 | 15.2102 | 47.8898 | 0.30843 | 7.37 | 6.86 | 65.191 | 481.4 | 481.32 | 2911.48 | 2691.1085 | 7.5691 | 86.4558 | 1586.2142 | 95.8902 | 95 | 70 | 9.5 | 10.4 | 7.9 | 18.3 | 18.3 | 0.42851 | 0.56831 | 16 | 16.7529 | 7.2486 | 65.7514 | 0.25479 | 6.86 | NA | 44.191 | 481.32 | 1126.62 | 1056.781 | 6.199 | 90.8188 | 769.0505 | 94.2538 | 70 | 45 | 9.5 | 3.2 | 6.6 | 9.8 | 9.8 | 0.53646 | 0.32653 | 9.8462 | 10.3095 | 12.3563 | 35.6437 | 0.28924 | NA | NA | 132.09 | 1126.62 | 1783.12 | 1608.8164 | 9.7752 | 72.5567 | 1367.7182 | 90.3423 | 97 | 50 | 9.2 | 1.8 | 2.9 | 4.7 | 4.7 | 0.51274 | 0.38298 | 15.4286 | 16.1545 | 21.5459 | 42.7541 | 0.37785 | NA | 7.67 | 138.831 | 1783.12 | 2911.48 | 2803.7132 | 3.7014 | 71.1562 | 2293.4166 | 93.9465 | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 42 | 448 | 724.4255 | 80.9955 | 586.2128 | 92.8354 | SDS-TCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 42 | 468 | 712.4262 | 81.4159 | 590.2131 | 92.8839 | SDS-TCAA* | mg/L | 2.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 52 | 476 | 713.1525 | 77.6824 | 594.5763 | 91.2543 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1997-07-31 | 8:00 | 499.5 | 24.4444 | 98 | 30 | 9.1667 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 14.0993 | 13.3648 | 41.4686 | 0.34 | 7.44 | 6.92 | 64.052 | 503.81 | 511.56 | 2556.84 | 2289.4972 | 10.456 | 87.4791 | 1400.5286 | 95.4266 | 98 | 78 | 9.2 | 10.3 | 8.1 | 18.4 | 18.4 | 0.43342 | 0.55978 | 15.8462 | 16.5918 | 7.6964 | 71.1036 | 0.23335 | 6.92 | NA | 41.064 | 511.56 | 1114.74 | 1109.845 | 0.43911 | 91.9728 | 810.7025 | 94.9348 | 78 | 48 | 9.2 | 3.2 | 6.8 | 10 | 10 | 0.54954 | 0.32 | 9.8462 | 10.3095 | 12.1101 | 41.6899 | 0.24729 | NA | NA | 134.4 | 1114.74 | 1819.08 | 1576.0765 | 13.3586 | 73.7274 | 1345.4082 | 90.0105 | 80 | 30 | 9.1 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.7697 | 18.9482 | 26.9518 | 0.39959 | NA | 7.62 | 188.65 | 1819.08 | 2556.84 | 2347.8681 | 8.1731 | 63.1226 | 2083.4741 | 90.9454 | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 37 | 387 | 625.2979 | 80.2139 | 506.1489 | 92.6899 | SDS-MBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 39 | 415 | 630.7377 | 80.402 | 522.8689 | 92.5412 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 44 | 412 | 617.8305 | 78.1095 | 514.9153 | 91.4549 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1.8603 | [5 empty] | 1997-07-31 | 20:00 | 511.78 | 24.4444 | 98 | 28 | 8.8667 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 14.0993 | 12.588 | 41.5454 | 0.33937 | 7.33 | 6.76 | 74.102 | 468.95 | 495.6 | 2330.9 | 2170.2002 | 6.8943 | 85.048 | 1332.9001 | 94.4405 | 98 | 78 | 9.2 | 10.3 | 8.1 | 18.4 | 18.4 | 0.43342 | 0.55978 | 15.8462 | 16.5918 | 7.445 | 71.355 | 0.23252 | 6.76 | NA | 40.474 | 495.6 | 1061.28 | 1074.3405 | -1.2306 | 91.8333 | 784.9702 | 94.8439 | 78 | 46 | 9.2 | 3.2 | 6.8 | 10 | 10 | 0.54954 | 0.32 | 9.8462 | 10.3095 | 11.5621 | 41.2379 | 0.25 | NA | NA | 125.3 | 1061.28 | 1738.48 | 1501.7412 | 13.6176 | 74.7175 | 1281.5106 | 90.2225 | 80 | 28 | 8.2 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.7697 | 18.0563 | 27.7437 | 0.38819 | NA | 7.52 | 184.8 | 1738.48 | 2330.9 | 2242.3762 | 3.7978 | 62.7119 | 1990.4281 | 90.7156 | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.78 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 2.4 | 3.7656 | 77.7778 | 3.0828 | 99.3512 | SDS-DBAA* | mg/L | 1.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 4.1 | 6.3876 | 90.9091 | 5.2438 | 99.8093 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | Zero for extended use | Maximum system recycle flow rate, (QR-sys)max (gpm) | -2.1397 | [5 empty] | 1997-07-31 | 23:50 | 515.34 | 24.4444 | 99 | 28 | 8.7667 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 14.0993 | 12.7154 | 42.0179 | 0.33555 | 7.22 | 6.75 | 74.035 | 471.44 | 499.8 | 2328.04 | 2191.3528 | 5.8713 | 85.1871 | 1345.5764 | 94.4979 | 99 | 78 | 9.2 | 10.3 | 8.1 | 18.4 | 18.4 | 0.43342 | 0.55978 | 15.8462 | 16.5918 | 7.505 | 71.795 | 0.2311 | 6.75 | NA | 41.005 | 499.8 | 1064.25 | 1083.206 | -1.7812 | 91.7957 | 791.503 | 94.8193 | 78 | 45 | 9.1 | 3.2 | 6.8 | 10 | 10 | 0.54954 | 0.32 | 9.8462 | 10.3095 | 11.6057 | 40.7943 | 0.25272 | NA | NA | 124.74 | 1064.25 | 1739.72 | 1506.3724 | 13.4129 | 75.042 | 1285.3112 | 90.295 | 80 | 28 | 8 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.7697 | 18.0528 | 27.9472 | 0.38536 | NA | 7.54 | 186.34 | 1739.72 | 2328.04 | 2243.5189 | 3.6306 | 62.7171 | 1991.6195 | 90.6438 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.7 | 19.8 | 32.8043 | 96.4646 | 26.3021 | 97.3386 | SDS-BCAA* | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.74 | 32.4 | 49.9918 | 88.369 | 41.1959 | 95.7763 | SDS-BCAA* | mg/L | 2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 2.25 | 26.7 | 40.3754 | 90.5462 | 33.5377 | 93.2911 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1997-08-01 | 8:25 | 524.15 | 24.4444 | 100 | 30 | 8.8 | 0 | 14.7 | 3.65 |  | 18.35 | 18.35 | 0.80109 | 0 | 13.4656 | 14.0993 | 13.2143 | 42.9857 | 0.328 | 7.37 | 6.84 | 65.526 | 491.36 | 504 | 2523.95 | 2269.909 | 10.0652 | 86.9988 | 1386.9545 | 95.2755 | 100 | 78 | 9.2 | 10.3 | 8.05 | 18.35 | 18.35 | 0.43178 | 0.56131 | 15.8462 | 16.5918 | 7.5929 | 72.2071 | 0.22978 | 6.84 | NA | 40.946 | 504 | 1091.97 | 1096.479 | -0.41293 | 91.8758 | 800.2395 | 94.8833 | 78 | 45 | 9.2 | 3.2 | 6.8 | 10 | 10 | 0.54954 | 0.32 | 9.8462 | 10.3095 | 11.8608 | 40.4392 | 0.25494 | NA | NA | 131.81 | 1091.97 | 1788.08 | 1543.81 | 13.661 | 73.8472 | 1317.89 | 89.9984 | 80 | 30 | 8 | 1.2 | 3.65 | 4.85 | 4.85 | 0.57346 | 0.24742 | 10.2857 | 10.7697 | 18.6235 | 28.3765 | 0.37953 | NA | 7.54 | 188.65 | 1788.08 | 2523.95 | 2313.92 | 8.3215 | 62.5694 | 2051 | 90.802 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.019 | 0.669 | 1.1116 | 97.1599 | 0.89028 | 97.8658 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.024 | 0.85 | 1.3239 | 95.092 | 1.087 | 97.792 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.037 | 0.845 | 1.2969 | 91.9214 | 1.071 | 96.5452 | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 19.2647 | [5 empty] | 1997-08-01 | 16:30 | 532.29 | 24.4444 | 98 | 28 | 8.8 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 14.0993 | 12.4298 | 41.7702 | 0.33754 | 7.37 | 6.79 | 77.72 | 492.19 | 493.92 | 2413.84 | 2147.4714 | 11.0351 | 84.2647 | 1320.6957 | 94.1152 | 98 | 75 | 9.2 | 10.3 | 8.1 | 18.4 | 18.4 | 0.43342 | 0.55978 | 15.8462 | 16.5918 | 7.4136 | 69.8864 | 0.23741 | 6.79 | NA | 40.71 | 493.92 | 1055.34 | 1070.2241 | -1.4104 | 91.7578 | 782.072 | 94.7946 | 75 | 45 | 9.2 | 3.2 | 6.8 | 10 | 10 | 0.54954 | 0.32 | 9.8462 | 10.3095 | 11.4611 | 39.3389 | 0.26207 | NA | NA | 127.54 | 1055.34 | 1762.04 | 1491.9518 | 15.3282 | 74.178 | 1273.6459 | 89.9862 | 80 | 28 | 8 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.7697 | 18.3211 | 27.6789 | 0.38909 | NA | 7.52 | 185.57 | 1762.04 | 2413.84 | 2273.3276 | 5.8211 | 62.4291 | 2017.6838 | 90.8028 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 2.7143 | 3.3788 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.3793 | 2.6235 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.6444 | 3.1648 | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1997-08-01 | 21:36 | 536.78 | 25 | 98 | 30 | 8.8 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 13.8696 | 13.112 | 42.088 | 0.32954 | 7.39 | 6.82 | 65.794 | 481.4 | 504.84 | 2328.04 | 2249.1579 | 3.3883 | 86.9674 | 1376.9989 | 95.2219 | 98 | 78 | 9.2 | 10.4 | 8 | 18.4 | 18.4 | 0.43178 | 0.56522 | 16 | 16.48 | 7.6562 | 71.1438 | 0.23164 | 6.82 | NA | 40.828 | 504.84 | 1109.79 | 1108.0556 | 0.15628 | 91.9127 | 806.4478 | 94.9373 | 78 | 48 | 9.2 | 3.1 | 6.8 | 9.9 | 9.9 | 0.54627 | 0.31313 | 9.5385 | 9.8246 | 12.009 | 41.791 | 0.23509 | NA | NA | 131.81 | 1109.79 | 1789.32 | 1555.6338 | 13.0601 | 73.8907 | 1332.7119 | 90.1096 | 80 | 30 | 8 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.5943 | 18.8708 | 28.1292 | 0.37663 | NA | 7.59 | 165.55 | 1789.32 | 2328.04 | 2315.9481 | 0.5194 | 67.2074 | 2052.6341 | 91.9348 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 4.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1997-08-02 | 9:15 | 548.9 | 24.4444 | 99 | 30 | 8.7667 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 14.0993 | 13.2464 | 42.4869 | 0.33185 | 7.38 | 6.73 | 64.655 | 489.7 | 508.2 | 2528.24 | 2270.3923 | 10.1987 | 87.2776 | 1389.2961 | 95.3462 | 99 | 78 | 9.2 | 10.4 | 8 | 18.4 | 18.4 | 0.43178 | 0.56522 | 16 | 16.7529 | 7.6785 | 71.6215 | 0.23391 | 6.73 | NA | 42.834 | 508.2 | 1131.57 | 1113.1758 | 1.6255 | 91.5714 | 810.6879 | 94.7163 | 78 | 46 | 9.1 | 3.1 | 6.8 | 9.9 | 9.9 | 0.54627 | 0.31313 | 9.5385 | 9.9873 | 12.2687 | 40.6313 | 0.2458 | NA | NA | 132.44 | 1131.57 | 1807.92 | 1587.0557 | 12.2165 | 73.9394 | 1359.3129 | 90.2568 | 80 | 30 | 8 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.7697 | 18.8633 | 28.1367 | 0.38276 | NA | 7.56 | 184.8 | 1807.92 | 2528.24 | 2334.3373 | 7.6695 | 63.6364 | 2071.1286 | 91.0773 | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 5.5 | 0 | --- | -22 | --- | #DIV/0! | -11 | 150 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Stage 3 -- General Information |  | maximum system recycle flow rates. | [6 empty] | 1997-08-04 | 8:35 | 596.28 | 24.4444 | 100 | 30 | 8.8 | 0 | 14.7 | 3.7 |  | 18.4 | 18.4 | 0.79891 | 0 | 13.4656 | 14.0993 | 13.1822 | 43.0178 | 0.32775 | 7.36 | 6.8 | 65.124 | 491.36 | 506.52 | 2516.8 | 2260.1744 | 10.1965 | 87.1429 | 1383.3472 | 95.2923 | 100 | 75 | 9.2 | 10.4 | 8 | 18.4 | 18.4 | 0.43178 | 0.56522 | 16 | 16.7529 | 7.6781 | 70.6219 | 0.23722 | 6.8 | NA | 41.182 | 506.52 | 1141.47 | 1111.4594 | 2.6291 | 91.8696 | 808.9897 | 94.9095 | 75 | 48 | 9.2 | 3.1 | 6.7 | 9.8 | 9.8 | 0.53973 | 0.31633 | 9.5385 | 9.9873 | 12.4332 | 39.8668 | 0.25052 | NA | NA | 131.74 | 1141.47 | 1795.52 | 1608.6585 | 10.4071 | 73.9912 | 1375.0643 | 90.4194 | 80 | 30 | 8 | 1.2 | 3.7 | 4.9 | 4.9 | 0.58021 | 0.2449 | 10.2857 | 10.7697 | 18.6744 | 28.3256 | 0.38021 | NA | 7.62 | 188.65 | 1795.52 | 2516.8 | 2316.667 | 7.9519 | 62.7557 | 2056.0935 | 90.8248 | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 7.5 | 0 | --- | -30 | --- | #DIV/0! | -15 | 150 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Stage 3 Operating Parameters During Sample Collection
|  | Membrane manufacturer | Fluid Systems | [7 empty] | 1997-08-05 | 10:30 | 622.51 | 25.5556 | 100 | 88 | 11.5 | 0 | 18.1 | 3.3 |  | 21.4 | 21.4 | 0.84579 | 0 | 16.5802 | 16.7994 | 14.9808 | 67.5192 | 0.24881 | 7.25 | 6.62 | 63.382 | 459.82 | 463.68 | 3446.3 | 2659.2539 | 22.8374 | 86.3307 | 1561.4669 | 95.9409 | 100 | 80 | 10 | 11.4 | 10 | 21.4 | 21.4 | 0.51356 | 0.53271 | 17.5385 | 17.7704 | 6.6925 | 73.3075 | 0.24241 | 6.62 | NA | 37.406 | 463.68 | 1099.89 | 949.6324 | 13.6612 | 91.9328 | 706.6562 | 94.7066 | 80 | 60 | 10 | 3.6 | 6 | 9.6 | 9.6 | 0.51029 | 0.375 | 11.0769 | 11.2234 | 12.5486 | 47.4514 | 0.23652 | NA | NA | 134.61 | 1099.89 | 1913.32 | 1679.058 | 12.2437 | 70.9692 | 1389.474 | 90.3122 | 150 | 88 | 14.5 | 3.1 | 3.3 | 6.4 | 6.4 | 0.65442 | 0.48438 | 26.5714 | 26.9228 | 26.4791 | 78.0209 | 0.34507 | NA | 7.39 | 111.65 | 1913.32 | 3446.3 | 3605.7979 | -4.6281 | 75.9209 | 2759.5589 | 95.9541 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.38 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal)
|  | Membrane trade name | TFC-S | Summary of the Stage and System Flow Rates | [6 empty] | 1997-08-05 | 15:00 | 626.64 | 25 | 102 | 90 | 11.1667 | 0 | 18.1 | 3.3 |  | 21.4 | 21.4 | 0.84579 | 0 | 16.5802 | 17.0776 | 15.3621 | 69.4712 | 0.24582 | 7.32 | 6.65 | 65.794 | 441.56 | 476.28 | 3703.7 | 2727.7335 | 26.3511 | 86.1859 | 1602.0068 | 95.893 | 102 | 80 | 10 | 11.4 | 10 | 21.4 | 21.4 | 0.51356 | 0.53271 | 17.5385 | 18.0646 | 6.857 | 74.143 | 0.24365 | 6.65 | NA | 39.53 | 476.28 | 1119.69 | 974.175 | 12.996 | 91.7003 | 725.2275 | 94.5493 | 80 | 58 | 10 | 3.6 | 5.9 | 9.5 | 9.5 | 0.50375 | 0.37895 | 11.0769 | 11.4092 | 12.9776 | 46.0224 | 0.24791 | NA | NA | 125.3 | 1119.69 | 1929.44 | 1726.4364 | 10.5214 | 73.6919 | 1423.0632 | 91.1951 | 150 | 90 | 13.5 | 3.1 | 3.3 | 6.4 | 6.4 | 0.65442 | 0.48438 | 26.5714 | 27.3686 | 26.8088 | 79.6912 | 0.34343 | NA | 7.5 | 105.336 | 1929.44 | 3703.7 | 3642.9922 | 1.6391 | 77.8836 | 2786.2161 | 96.2194 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.8 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.7 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.4 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm)
|  | Membrane element model number | SC 2540S | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.2647 | [5 empty] | 1997-08-06 | 15:30 | 651.03 | 25 | 103 | 90 | 11.3 | 0 | 18 | 3.3 |  | 21.3 | 21.3 | 0.84507 | 0 | 16.4885 | 16.9832 | 16.114 | 69.086 | 0.24583 | 7.44 | 6.64 | 65.794 | 489.7 | 498.12 | 3689.4 | 2856.2618 | 22.5819 | 86.7915 | 1677.1909 | 96.0771 | 103 | 82 | 10.2 | 11.4 | 9.9 | 21.3 | 21.3 | 0.51029 | 0.53521 | 17.5385 | 18.0646 | 7.2198 | 75.0802 | 0.2406 | 6.64 | NA | 39.943 | 498.12 | 1143.45 | 1025.7178 | 10.2962 | 91.9812 | 761.9189 | 94.7576 | 82 | 58 | 10.2 | 3.6 | 5.9 | 9.5 | 9.5 | 0.50375 | 0.37895 | 11.0769 | 11.4092 | 13.0685 | 46.7315 | 0.24414 | NA | NA | 142.1 | 1143.45 | 1900.92 | 1754.4432 | 7.7056 | 71.4727 | 1448.9466 | 90.1929 | 152 | 90 | 13.5 | 3 | 3.3 | 6.3 | 6.3 | 0.64768 | 0.47619 | 25.7143 | 26.4857 | 26.1579 | 81.3421 | 0.32561 | NA | 7.58 | 102.564 | 1900.92 | 3689.4 | 3535.7891 | 4.1636 | 79.4098 | 2718.3545 | 96.227 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.7 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 6.1 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.9 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | [17 empty] | Stage 3 influent flow rate during sample collection (gpm) | [17 empty] | Stage 3 influent flow rate during sample collection (gpm)
|  | Molecular weight cutoff (Daltons) | 300 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | [5 empty] | 1997-08-07 | 7:30 | 666.93 | 24.4444 | 102 | 90 | 11.3 | 0 | 18 | 3.3 |  | 21.3 | 21.3 | 0.84507 | 0 | 16.4885 | 17.2644 | 16.2208 | 68.4792 | 0.25211 | 7.62 | 6.89 | 68.809 | 493.85 | 504 | NA | 2877.7691 | #VALUE! | 86.3474 | 1690.8845 | 95.9306 | 102 | 82 | 10.2 | 11.4 | 9.9 | 21.3 | 21.3 | 0.51029 | 0.53521 | 17.5385 | 18.3637 | 7.3115 | 74.4885 | 0.24653 | 6.89 | NA | 40.002 | 504 | 1172.16 | 1038.3007 | 11.4199 | 92.0631 | 771.1504 | 94.8127 | 82 | 58 | 10.2 | 3.6 | 5.8 | 9.4 | 9.4 | 0.49721 | 0.38298 | 11.0769 | 11.5981 | 13.4331 | 46.3669 | 0.25014 | NA | NA | 147 | 1172.16 | 2021.2 | 1808.4662 | 10.5251 | 70.8333 | 1490.3131 | 90.1363 | 152 | 90 | 13.5 | 3 | 3.3 | 6.3 | 6.3 | 0.64768 | 0.47619 | 25.7143 | 26.9242 | 27.8436 | 79.6564 | 0.338 | NA | 7.72 | 106.953 | 2021.2 | NA | 3761.4245 | #VALUE! | 78.7792 | 2891.3123 | 96.3009 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.5147 | [5 empty] | 1997-08-07 | 15:20 | 677 | 24.4444 | 102 | 90 | 11.1667 | 0 | 17.5 | 3.3 |  | 20.8 | 20.8 | 0.84135 | 0 | 16.0305 | 16.7848 | 15.7116 | 69.1218 | 0.24283 | 7.52 | 6.79 | 65.325 | 493.02 | 495.6 | 3655.08 | 2777.3614 | 24.0137 | 86.819 | 1636.4807 | 96.0082 | 102 | 81 | 10 | 10.9 | 9.9 | 20.8 | 20.8 | 0.50211 | 0.52404 | 16.7692 | 17.5583 | 7.0677 | 74.4323 | 0.2359 | 6.79 | NA | 39.766 | 495.6 | 1126.62 | 997.4778 | 11.4628 | 91.9762 | 746.5389 | 94.6733 | 81 | 59 | 10 | 3.6 | 5.9 | 9.5 | 9.5 | 0.50375 | 0.37895 | 11.0769 | 11.5981 | 12.8762 | 47.1238 | 0.24612 | NA | NA | 140 | 1126.62 | 1981.52 | 1728.6254 | 12.7627 | 71.7514 | 1427.6227 | 90.1935 | 152 | 90 | 13.5 | 3 | 3.3 | 6.3 | 6.3 | 0.64768 | 0.47619 | 25.7143 | 26.9242 | 27.2832 | 80.2168 | 0.33564 | NA | 7.6 | 105.798 | 1981.52 | 3655.08 | 3686.7218 | -0.86569 | 78.6525 | 2834.1209 | 96.267 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.5147 | [5 empty] | 1997-08-11 | 9:30 | 772.19 | 25 | 100 | 91 | 10.6667 | 0 | 18.1 | 3.3 |  | 21.4 | 21.4 | 0.84579 | 0 | 16.5802 | 17.0776 | 14.9079 | 69.9254 | 0.24423 | 7.4 | 6.6 | 63.65 | 448.2 | 462 | 3432 | 2646.8894 | 22.8762 | 86.2229 | 1554.4447 | 95.9053 | 100 | 82 | 10 | 11.4 | 10 | 21.4 | 21.4 | 0.51356 | 0.53271 | 17.5385 | 18.0646 | 6.6328 | 74.3672 | 0.24291 | 6.6 | NA | 39.53 | 462 | 1110.78 | 943.6158 | 15.0493 | 91.4437 | 702.8079 | 94.3754 | 82 | 58 | 10 | 3.6 | 6 | 9.6 | 9.6 | 0.51029 | 0.375 | 11.0769 | 11.4092 | 12.8021 | 47.1979 | 0.24173 | NA | NA | 126 | 1110.78 | 1897.2 | 1701.648 | 10.3074 | 72.7273 | 1406.214 | 91.0398 | 156 | 91 | 12 | 3.1 | 3.3 | 6.4 | 6.4 | 0.65442 | 0.48438 | 26.5714 | 27.3686 | 26.4685 | 85.0315 | 0.32186 | NA | 7.5 | 96.25 | 1897.2 | 3432 | 3589.0015 | -4.5746 | 79.1667 | 2743.1008 | 96.4912 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-2 | CI-s3-2 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-4 | CI-s3-4 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-6 | CI-s3-6 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-8 | CI-s3-8 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-10 | CI-s3-10 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-10 (dup) | CI-s3-10 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | [5 empty] | 1997-08-11 | 17:50 | 774.01 | 25 | 100 | 91 | 10.6667 | 0 | 17.2 | 3.4 |  | 20.6 | 20.6 | 0.83495 | 0 | 15.7557 | 16.2284 | 14.2064 | 70.627 | 0.22978 | 7.31 | 6.65 | 62.846 | 427.45 | 465.36 | 3474.9 | 2501.6073 | 28.0092 | 86.4952 | 1483.4836 | 95.7636 | 100 | 80 | 10 | 10.9 | 9.7 | 20.6 | 20.6 | 0.49557 | 0.52913 | 16.7692 | 17.2723 | 6.6647 | 73.3353 | 0.23553 | 6.65 | NA | 38.645 | 465.36 | 1090.98 | 944.8645 | 13.3931 | 91.6957 | 705.1122 | 94.5193 | 80 | 59 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.4092 | 12.7552 | 46.7448 | 0.24407 | NA | NA | 125.72 | 1090.98 | 1886.04 | 1711.5043 | 9.2541 | 72.9844 | 1401.2421 | 91.028 | 153 | 91 | 12 | 2.7 | 3.4 | 6.1 | 6.1 | 0.64093 | 0.44262 | 23.1429 | 23.8371 | 25.0152 | 84.9848 | 0.28049 | NA | 7.39 | 95.48 | 1886.04 | 3474.9 | 3307.9553 | 4.8043 | 79.4826 | 2596.9976 | 96.3234 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1997-07-30 | 1997-07-30 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1997-08-13 | 1997-08-13 | --- | --- | --- | --- | Qp/QT (THM4), % | 1232.8767 | 616.4384 |  | Qp/QT (HAA5), % | 981.8182 | 490.9091 |  |  |  | Sampling date | MM/DD/YY | 1997-08-27 | 1997-08-27 | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.6397 | [5 empty] | 1997-08-11 | 23:00 | 778.4 | 24.4444 | 100 | 92 | 10.9 | 0 | 17.3 | 3.4 |  | 20.7 | 20.7 | 0.83575 | 0 | 15.8473 | 16.593 | 14.9897 | 70.1103 | 0.23667 | 7.6 | 6.82 | 64.253 | 453.18 | 487.2 | 3417.7 | 2639.2539 | 22.7769 | 86.8118 | 1563.2269 | 95.8897 | 100 | 80 | 10.1 | 10.9 | 9.8 | 20.7 | 20.7 | 0.49884 | 0.52657 | 16.7692 | 17.5583 | 6.9553 | 72.9447 | 0.24071 | 6.82 | NA | 40.238 | 487.2 | 1086.03 | 984.3312 | 9.3643 | 91.741 | 735.7656 | 94.5311 | 80 | 60 | 10.1 | 3.6 | 5.8 | 9.4 | 9.4 | 0.49721 | 0.38298 | 11.0769 | 11.5981 | 12.4329 | 47.4671 | 0.24434 | NA | NA | 137.2 | 1086.03 | 1928.2 | 1674.959 | 13.1335 | 71.8391 | 1380.4945 | 90.0615 | 158 | 92 | 12.5 | 2.8 | 3.4 | 6.2 | 6.2 | 0.64768 | 0.45161 | 24 | 25.1293 | 25.7976 | 86.7024 | 0.28983 | NA | 7.37 | 100.87 | 1928.2 | 3417.7 | 3433.06 | -0.44943 | 79.296 | 2680.63 | 96.2371 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 11:15 | 11:15 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm |  |  | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 4.6397 | [5 empty] | 1997-08-12 | 11:30 | 790.04 | 24.4444 | 101 | 90 | 10.7333 | 0 | 17.1 | 3.1 |  | 20.2 | 20.2 | 0.84653 | 0 | 15.6641 | 16.4012 | 15.6407 | 69.1259 | 0.23727 | 7.57 | 6.69 | 63.449 | 437.41 | 479.64 | 3459.17 | 2775.4033 | 19.7668 | 86.7715 | 1627.5216 | 96.1015 | 101 | 81 | 10.2 | 10.6 | 9.6 | 20.2 | 20.2 | 0.48739 | 0.52475 | 16.3077 | 17.075 | 6.83 | 73.97 | 0.23084 | 6.69 | NA | 39.589 | 479.64 | 1078.11 | 965.5296 | 10.4424 | 91.7461 | 722.5848 | 94.5212 | 81 | 58 | 10.2 | 3.6 | 5.7 | 9.3 | 9.3 | 0.49066 | 0.3871 | 11.0769 | 11.5981 | 12.4476 | 46.8524 | 0.24755 | NA | NA | 132.09 | 1078.11 | 1918.28 | 1675.5963 | 12.6511 | 72.4606 | 1376.8532 | 90.4064 | 154 | 90 | 11.8 | 2.9 | 3.1 | 6 | 6 | 0.61394 | 0.48333 | 24.8571 | 26.0268 | 26.6817 | 83.5183 | 0.31163 | NA | 7.33 | 100.408 | 1918.28 | 3459.17 | 3618.8699 | -4.6167 | 79.066 | 2768.575 | 96.3733 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 480.1 | 480.1 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 814.8 | 814.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 1147.8 | 1147.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh |  |  | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Stage 3 -- Design Parameters |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | [5 empty] | 1997-08-12 | 14:20 | 794.04 | 25 | 100 | 91 | 10.6 | 0 | 17.3 | 3.4 |  | 20.7 | 20.7 | 0.83575 | 0 | 15.8473 | 16.3227 | 14.5883 | 70.3117 | 0.23215 | 7.42 | 6.66 | 62.98 | 441.56 | 474.6 | 3469.18 | 2569.0194 | 25.9474 | 86.7299 | 1521.8097 | 95.8615 | 100 | 80 | 9.9 | 10.9 | 9.8 | 20.7 | 20.7 | 0.49884 | 0.52657 | 16.7692 | 17.2723 | 6.7757 | 73.3243 | 0.23556 | 6.66 | NA | 39.176 | 474.6 | 1096.92 | 958.8981 | 12.5827 | 91.7455 | 716.7491 | 94.5342 | 80 | 58 | 9.9 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.4092 | 12.8078 | 46.2922 | 0.24646 | NA | NA | 127.68 | 1096.92 | 1894.72 | 1720.0029 | 9.2213 | 73.0973 | 1408.4614 | 90.9348 | 159 | 91 | 12 | 2.8 | 3.4 | 6.2 | 6.2 | 0.64768 | 0.45161 | 24 | 24.72 | 25.3771 | 87.6229 | 0.28212 | NA | 7.56 | 97.174 | 1894.72 | 3469.18 | 3375.052 | 2.7133 | 79.5251 | 2634.886 | 96.312 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.41 | 7.29 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.26 | 7.34 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 6.68 | 7.53 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- |  |  | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- |  |  | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- |  |  | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 2.8897 | [5 empty] | 1997-08-12 | 23:10 | 803.15 | 24.4444 | 100 | 90 | 10.6667 | 0 | 17.2 | 3.4 |  | 20.6 | 20.6 | 0.83495 | 0 | 15.7557 | 16.4971 | 14.8006 | 69.5327 | 0.23726 | 7.38 | 6.78 | 63.65 | 446.54 | 483 | 3389.1 | 2604.4176 | 23.1531 | 86.8219 | 1543.7088 | 95.8768 | 100 | 82 | 10 | 11 | 9.6 | 20.6 | 20.6 | 0.49394 | 0.53398 | 16.9231 | 17.7194 | 6.9652 | 74.0348 | 0.23934 | 6.78 | NA | 40.179 | 483 | 1089 | 990.3991 | 9.0543 | 91.6814 | 736.6995 | 94.5461 | 82 | 59 | 10 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 11.276 | 12.5622 | 47.9378 | 0.23522 | NA | NA | 131.88 | 1089 | 1904.64 | 1687.2 | 11.4163 | 72.6957 | 1388.1 | 90.4992 | 156 | 90 | 12 | 2.7 | 3.4 | 6.1 | 6.1 | 0.64093 | 0.44262 | 23.1429 | 24.2318 | 25.2449 | 85.7551 | 0.28257 | NA | 7.41 | 97.636 | 1904.64 | 3389.1 | 3339.6138 | 1.4602 | 79.7855 | 2622.1269 | 96.2765 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | NA | 26 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | NA | 25.4 | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC |  |  | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC |  |  | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC |  |  | --- | --- | --- | ---
|  | Active membrane area of membrane element used, A (ft2) | 28 | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1997-08-13 | 7:10 | 810.77 | 24.4444 | 100 | 92 | 10.7333 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.4012 | 14.6302 | 70.6364 | 0.23219 | 7.36 | 6.87 | 63.382 | 445.71 | 479.64 | 3462.03 | 2573.1729 | 25.6744 | 86.7855 | 1526.4064 | 95.8476 | 100 | 80 | 10.1 | 11 | 9.5 | 20.5 | 20.5 | 0.49066 | 0.53659 | 16.9231 | 17.7194 | 6.9444 | 72.9556 | 0.24288 | 6.87 | NA | 39.825 | 479.64 | 1086.03 | 988.8995 | 8.9436 | 91.6969 | 734.2697 | 94.5762 | 80 | 60 | 10.1 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 11.276 | 12.5324 | 47.3676 | 0.23805 | NA | NA | 131.18 | 1086.03 | 1910.84 | 1682.8112 | 11.9334 | 72.6503 | 1384.4206 | 90.5246 | 158 | 92 | 12 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 25.0457 | 87.9543 | 0.2653 | NA | 7.43 | 99.022 | 1910.84 | 3462.03 | 3296.3479 | 4.7857 | 79.3549 | 2603.5939 | 96.1967 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 44 | 515 | 807.3448 | 77.7778 | 661.1724 | 93.3452 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 34 | 591 | 1033.3235 | 83.2512 | 812.1618 | 95.8136 | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 36 | 618 | 1017.0857 | 83.7104 | 817.5429 | 95.5966 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Design flux, FW (gfd) | 41.43 | System concentrate waste flow rate, QW-sys (gpm) | 2.8897 | [5 empty] | 1997-08-13 | 14:05 | 818.17 | 25.5556 | 101 | 92 | 10.4667 | 0 | 17.2 | 3.4 |  | 20.6 | 20.6 | 0.83495 | 0 | 15.7557 | 15.9641 | 14.9488 | 71.0845 | 0.22458 | 7.38 | 6.66 | 63.65 | 474.76 | 487.2 | 3374.8 | 2629.8647 | 22.0735 | 86.9356 | 1558.5324 | 95.916 | 101 | 80 | 9.8 | 11 | 9.6 | 20.6 | 20.6 | 0.49394 | 0.53398 | 16.9231 | 17.1469 | 7.0712 | 73.6288 | 0.23288 | 6.66 | NA | 37.642 | 487.2 | 1132.56 | 1002.3185 | 11.4997 | 92.2738 | 744.7593 | 94.9457 | 80 | 59 | 9.8 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 10.9116 | 13.19 | 46.51 | 0.23461 | NA | NA | 127.61 | 1132.56 | 1992.68 | 1760.6537 | 11.6439 | 73.8075 | 1446.6069 | 91.1787 | 155 | 92 | 11.8 | 2.7 | 3.4 | 6.1 | 6.1 | 0.64093 | 0.44262 | 23.1429 | 23.4489 | 26.4351 | 85.2649 | 0.27501 | NA | 7.55 | 100.485 | 1992.68 | 3374.8 | 3495.3054 | -3.5707 | 79.375 | 2743.9927 | 96.338 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 114 | 887 | 1366.7931 | 69.9208 | 1126.8966 | 89.8837 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 89 | 986 | 1698.3235 | 76.5789 | 1342.1618 | 93.3689 | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 93 | 965 | 1562.9429 | 75.9067 | 1263.9714 | 92.6422 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Net driving pressure at the design flux, NDP (psi) | 97 | System permeate flow rate, Qp-sys (gpm) | 16.375 | [5 empty] | 1997-08-13 | 23:20 | 826.84 | 24.4444 | 102 | 98 | 11.1333 | 0 | 17.3 | 3.4 |  | 20.7 | 20.7 | 0.83575 | 0 | 15.8473 | 16.593 | 14.7348 | 74.1319 | 0.22383 | 7.4 | 6.69 | 63.047 | 453.18 | 478.8 | 3403.4 | 2594.2491 | 23.7748 | 86.8323 | 1536.5245 | 95.8968 | 102 | 81 | 10.5 | 11 | 9.7 | 20.7 | 20.7 | 0.49721 | 0.5314 | 16.9231 | 17.7194 | 6.8908 | 74.1092 | 0.2391 | 6.69 | NA | 39.058 | 478.8 | 1100.88 | 977.4765 | 11.2095 | 91.8425 | 728.1382 | 94.6359 | 81 | 60 | 10.5 | 3.6 | 5.8 | 9.4 | 9.4 | 0.49721 | 0.38298 | 11.0769 | 11.5981 | 12.6881 | 47.3119 | 0.24514 | NA | NA | 132.58 | 1100.88 | 1961.68 | 1701.8938 | 13.243 | 72.3099 | 1401.3869 | 90.5394 | 158 | 98 | 12.4 | 2.7 | 3.4 | 6.1 | 6.1 | 0.64093 | 0.44262 | 23.1429 | 24.2318 | 26.0278 | 89.5722 | 0.27053 | NA | 7.51 | 98.637 | 1961.68 | 3403.4 | 3441.1553 | -1.1093 | 79.3991 | 2701.4177 | 96.3487 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 32 | 592 | 939.5862 | 85.5204 | 765.7931 | 95.8213 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 19 | 678 | 1201.3235 | 91.5929 | 939.6618 | 97.978 | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 23 | 669 | 1111.9714 | 90.1288 | 890.4857 | 97.4171 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.427 | System feed flow rate, QF-sys (gpm) | 19.2647 | [5 empty] | 1997-08-14 | 7:15 | 834.86 | 25 | 102 | 95 | 10.9667 | 0 | 17.3 | 3.4 |  | 20.7 | 20.7 | 0.83575 | 0 | 15.8473 | 16.3227 | 14.8444 | 72.689 | 0.22456 | 7.43 | 6.81 | 63.315 | 458.99 | 482.16 | 3427.71 | 2613.3419 | 23.7584 | 86.8685 | 1547.751 | 95.9092 | 102 | 80 | 10.3 | 11.1 | 9.6 | 20.7 | 20.7 | 0.49557 | 0.53623 | 17.0769 | 17.5892 | 7.0002 | 73.6998 | 0.23866 | 6.81 | NA | 38.586 | 482.16 | 1114.74 | 995.0424 | 10.7377 | 91.9973 | 738.6012 | 94.7758 | 80 | 60 | 10.4 | 3.6 | 5.7 | 9.3 | 9.3 | 0.49066 | 0.3871 | 11.0769 | 11.4092 | 12.9296 | 46.6704 | 0.24446 | NA | NA | 132.09 | 1114.74 | 1943.08 | 1735.3611 | 10.6902 | 72.6045 | 1425.0505 | 90.7309 | 156 | 95 | 12.2 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 22.9543 | 25.4797 | 87.8203 | 0.26138 | NA | 7.56 | 99.869 | 1943.08 | 3427.71 | 3352.5943 | 2.1914 | 79.2872 | 2647.8371 | 96.2283 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 28 | 518 | 822.1379 | 85.0267 | 670.069 | 95.8213 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 18 | 603 | 1067.5588 | 90.9548 | 835.2794 | 97.845 | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 19 | 580 | 964.6857 | 90.5473 | 772.3429 | 97.54 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Temperature at which the MTCW was determined, ToC (oC) | 25 | [7 empty] | 1997-08-14 | 14:35 | 842.19 | 26.1111 | 100 | 92 | 10.6667 | 0 | 17.6 | 3.3 |  | 20.9 | 20.9 | 0.84211 | 0 | 16.1221 | 16.0693 | 15.4427 | 69.8907 | 0.22992 | 7.41 | 6.65 | 63.516 | 455.67 | 484.68 | 3434.86 | 2730.888 | 20.4949 | 86.8953 | 1607.784 | 96.0495 | 100 | 82 | 9.9 | 11.3 | 9.6 | 20.9 | 20.9 | 0.49884 | 0.54067 | 17.3846 | 17.3276 | 7.078 | 74.022 | 0.23409 | 6.65 | NA | 39.117 | 484.68 | 1119.69 | 1009.1448 | 9.8728 | 91.9293 | 746.9124 | 94.7628 | 82 | 58 | 10.1 | 3.6 | 5.5 | 9.1 | 9.1 | 0.47758 | 0.3956 | 11.0769 | 11.0406 | 13.1323 | 46.7677 | 0.23607 | NA | NA | 130.27 | 1119.69 | 1956.72 | 1767.3104 | 9.68 | 73.1225 | 1443.5002 | 90.9754 | 159 | 92 | 12 | 2.7 | 3.3 | 6 | 6 | 0.62744 | 0.45 | 23.1429 | 23.067 | 26.1593 | 87.3407 | 0.2641 | NA | 7.52 | 100.254 | 1956.72 | 3434.86 | 3475.6467 | -1.1874 | 79.3154 | 2716.1834 | 96.309 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | BMRL | 8.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.02 | 13.7 | 24.5635 | 77.7778 | 19.1318 | 99.8955 | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.01 | 9.9 | 16.6817 | 90.9091 | 13.2909 | 99.9248 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum flow rate to the element, QI, max (gpm) | 2.5 | Calculate the Required System Influent Pressure | [6 empty] | 1997-08-15 | 12:10 | 851.38 | 24.4444 | 101 | 93 | 10.8 | 0 | 17.4 | 3.4 |  | 20.8 | 20.8 | 0.83654 | 0 | 15.9389 | 16.6889 | 14.9335 | 71.2665 | 0.23418 | 7.37 | 6.72 | 63.382 | 457.33 | 483 | 3429.14 | 2630.4568 | 23.2911 | 86.8774 | 1556.7284 | 95.9285 | 101 | 80 | 10.2 | 10.9 | 9.9 | 20.8 | 20.8 | 0.50211 | 0.52404 | 16.7692 | 17.5583 | 6.887 | 73.413 | 0.23917 | 6.72 | NA | 38.822 | 483 | 1109.79 | 972.0445 | 12.4119 | 91.9623 | 727.5222 | 94.6638 | 80 | 60 | 10 | 3.6 | 5.9 | 9.5 | 9.5 | 0.50375 | 0.37895 | 11.0769 | 11.5981 | 12.7689 | 47.2311 | 0.24556 | NA | NA | 131.39 | 1109.79 | 1913.32 | 1706.7798 | 10.7949 | 72.7971 | 1408.2849 | 90.6702 | 155 | 93 | 12.2 | 2.9 | 3.4 | 6.3 | 6.3 | 0.65442 | 0.46032 | 24.8571 | 26.0268 | 25.8716 | 85.9284 | 0.30289 | NA | 7.57 | 99.638 | 1913.32 | 3429.14 | 3460.2841 | -0.90822 | 79.371 | 2686.802 | 96.2916 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | 0.7 | 51.8 | 83.5172 | 96.4646 | 67.6586 | 98.9654 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | 0.14 | 45.9 | 82.2388 | 99.0642 | 64.0694 | 99.7815 | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 1.19 | 37.2 | 61.8926 | 95 | 49.5463 | 97.5982 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 0.5 | Osmotic pressure for stage 13, Dp1 (psi) | 8.9 | [5 empty] | 1997-08-15 | 10:40 | 862.31 | 24.4444 | 100 | 95 | 10.7 | 0 | 17.2 | 3.4 |  | 20.6 | 20.6 | 0.83495 | 0 | 15.7557 | 16.4971 | 14.0601 | 72.7399 | 0.2268 | 7.45 | 6.74 | 70.35 | 448.2 | 468.72 | 3474.9 | 2484.0035 | 28.5158 | 84.991 | 1476.3618 | 95.2349 | 100 | 80 | 10.1 | 11 | 9.6 | 20.6 | 20.6 | 0.49394 | 0.53398 | 16.9231 | 17.7194 | 6.7267 | 73.1733 | 0.24216 | 6.74 | NA | 41.064 | 468.72 | 1097.91 | 958.7425 | 12.6757 | 91.2391 | 713.7313 | 94.2466 | 80 | 58 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.5378 | 46.4622 | 0.24963 | NA | NA | 149.1 | 1097.91 | 1882.32 | 1707.8593 | 9.2684 | 68.19 | 1402.8846 | 89.3719 | 158 | 95 | 12 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 24.6728 | 89.8272 | 0.25977 | NA | 7.62 | 97.482 | 1882.32 | 3474.9 | 3247.1961 | 6.5528 | 79.2025 | 2564.7581 | 96.1992 | Notes: | [9 empty] | UV254 | cm-1 | 0.013 | 0.975 | 1.5721 | 98.0568 | 1.2736 | 98.9792 | Notes: | [9 empty] | UV254 | cm-1 | 0.006 | 0.872 | 1.5597 | 98.773 | 1.2159 | 99.5065 | Notes: | [9 empty] | UV254 | cm-1 | 0.005 | 0.928 | 1.5609 | 98.9083 | 1.2445 | 99.5982 | Notes: | [9 empty] | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Notes: | [9 empty] | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Notes: | [9 empty] | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Total width of all membrane envelopes in the element, w (ft) | 6.4 | Osmotic pressure for stage 23, Dp2 (psi) | 13.4 | [5 empty] | 1997-08-15 | 16:30 | 867.9 | 24.4444 | 100 | 98 | 10.6667 | 0 | 17.4 | 3.4 |  | 20.8 | 20.8 | 0.83654 | 0 | 15.9389 | 16.6889 | 14.2331 | 74.1003 | 0.22522 | 7.44 | 6.64 | 66.263 | 449.86 | 466.2 | 3489.2 | 2512.9364 | 27.9796 | 85.7866 | 1489.5682 | 95.5515 | 100 | 80 | 10 | 11.2 | 9.6 | 20.8 | 20.8 | 0.49721 | 0.53846 | 17.2308 | 18.0415 | 6.7762 | 73.2238 | 0.24639 | 6.64 | NA | 38.232 | 466.2 | 1098.9 | 965.496 | 12.1398 | 91.7992 | 715.848 | 94.6592 | 80 | 58 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.7221 | 46.2779 | 0.25062 | NA | NA | 136.15 | 1098.9 | 1879.84 | 1717.8107 | 8.6193 | 70.7958 | 1408.3554 | 90.3327 | 158 | 98 | 12 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 24.6214 | 91.3786 | 0.25536 | NA | 7.58 | 98.714 | 1879.84 | 3489.2 | 3241.8775 | 7.0882 | 78.8258 | 2560.8588 | 96.1453 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.8571 | 1.8822 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 4.2857 | 1.8998 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.42017 | 2.4946 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  | Feed spacer thickness, T (ft) | 0.00258 | Osmotic pressure for stage 33, Dp3 (psi) | 18.6 | [5 empty] | 1997-08-16 | 12:30 | 875.2 | 25.5556 | 100 | 98 | 10.7667 | 0 | 17.5 | 3.1 |  | 20.6 | 20.6 | 0.84951 | 0 | 16.0305 | 16.2425 | 15.2915 | 72.9419 | 0.22268 | 7.62 | 6.69 | 63.65 | 462.31 | 463.68 | 3420.56 | 2721.9139 | 20.4249 | 86.2729 | 1592.7969 | 96.0039 | 100 | 82 | 10.1 | 11.3 | 9.3 | 20.6 | 20.6 | 0.48903 | 0.54854 | 17.3846 | 17.6145 | 6.8354 | 74.0646 | 0.23783 | 6.69 | NA | 38.468 | 463.68 | 1090.98 | 980.3354 | 10.1418 | 91.7038 | 722.0077 | 94.6721 | 82 | 56 | 10.1 | 3.4 | 5.4 | 8.8 | 8.8 | 0.4645 | 0.38636 | 10.4615 | 10.5999 | 12.5966 | 46.3034 | 0.22892 | NA | NA | 132.93 | 1090.98 | 1949.28 | 1694.1967 | 13.086 | 71.3315 | 1392.5883 | 90.4545 | 157 | 98 | 12.1 | 2.8 | 3.1 | 5.9 | 5.9 | 0.6072 | 0.47458 | 24 | 24.3174 | 26.8653 | 88.5347 | 0.27466 | NA | 7.42 | 98.56 | 1949.28 | 3420.56 | 3620.8981 | -5.8569 | 78.744 | 2785.089 | 96.4612 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses due to stage hardware, DPs (psi) | 4 | [5 empty] | 1997-08-16 | 9:00 | 887.36 | 23.8889 | 102 | 93 | 10.5 | 0 | 17.9 | 3.3 |  | 21.2 | 21.2 | 0.84434 | 0 | 16.3969 | 17.4527 | 15.2129 | 71.7871 | 0.24312 | 7.57 | 6.81 | 66.464 | 464.8 | 476.28 | 3432 | 2699.2213 | 21.3514 | 86.0452 | 1587.7507 | 95.814 | 102 | 81 | 10 | 11.4 | 9.8 | 21.2 | 21.2 | 0.50702 | 0.53774 | 17.5385 | 18.6678 | 6.9022 | 74.5978 | 0.25025 | 6.81 | NA | 39.884 | 476.28 | 1112.76 | 983.9243 | 11.578 | 91.6259 | 730.1022 | 94.5372 | 81 | 59 | 9.8 | 3.6 | 5.9 | 9.5 | 9.5 | 0.50375 | 0.37895 | 11.0769 | 11.7902 | 12.7648 | 47.4352 | 0.24855 | NA | NA | 134.68 | 1112.76 | 1918.28 | 1709.5546 | 10.8809 | 71.7225 | 1411.1573 | 90.4561 | 154 | 93 | 11.7 | 2.9 | 3.3 | 6.2 | 6.2 | 0.64093 | 0.46774 | 24.8571 | 26.4577 | 26.1741 | 85.6259 | 0.30899 | NA | 7.49 | 99.869 | 1918.28 | 3432 | 3516.2775 | -2.4556 | 79.0315 | 2717.2788 | 96.3247 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1997-08-16 | 15:20 | 890.83 | 24.4444 | 102 | 98 | 10.6 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.4012 | 14.2986 | 75.1014 | 0.21839 | 7.48 | 6.73 | 65.258 | 459.82 | 472.08 | 3463.46 | 2518.1554 | 27.2936 | 86.1765 | 1495.1177 | 95.6353 | 102 | 80 | 10 | 10.9 | 9.6 | 20.5 | 20.5 | 0.4923 | 0.53171 | 16.7692 | 17.5583 | 6.7959 | 74.2041 | 0.23662 | 6.73 | NA | 38.586 | 472.08 | 1100.88 | 964.2763 | 12.4086 | 91.8264 | 718.1782 | 94.6272 | 80 | 59 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.8028 | 46.6972 | 0.24837 | NA | NA | 132.02 | 1100.88 | 1915.8 | 1723.7186 | 10.0262 | 72.0344 | 1412.2993 | 90.6521 | 158 | 98 | 11.8 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 25.1207 | 91.0793 | 0.2562 | NA | 7.46 | 98.56 | 1915.8 | 3463.46 | 3305.4541 | 4.5621 | 79.1222 | 2610.6271 | 96.2247 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1997-08-17 | 12:00 | 898.84 | 24.4444 | 102 | 98 | 10.6667 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.4012 | 14.9345 | 74.3988 | 0.22045 | 7.52 | 6.83 | 70.685 | 490.53 | 495.6 | 3460.6 | 2632.6725 | 23.9244 | 85.7375 | 1564.1363 | 95.4809 | 102 | 80 | 10 | 10.9 | 9.6 | 20.5 | 20.5 | 0.4923 | 0.53171 | 16.7692 | 17.5583 | 7.1406 | 73.8594 | 0.23773 | 6.83 | NA | 40.12 | 495.6 | 1112.76 | 1012.7596 | 8.9867 | 91.9048 | 754.1798 | 94.6803 | 80 | 58 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.6508 | 46.3492 | 0.25023 | NA | NA | 155.4 | 1112.76 | 1938.12 | 1728.2057 | 10.8308 | 68.6441 | 1420.4829 | 89.0601 | 158 | 98 | 12 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 25.343 | 90.657 | 0.25739 | NA | 7.72 | 104.797 | 1938.12 | 3460.6 | 3340.0729 | 3.4828 | 78.8545 | 2639.0964 | 96.0291 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  | Stage 3 -- Additional Information |  | Mechanical pressure losses per stage, Ls (psi) | 22 | [5 empty] | 1997-08-17 | 9:15 | 911.09 | 23.8889 | 100 | 99 | 10.8667 | 0 | 17.2 | 3.3 |  | 20.5 | 20.5 | 0.83902 | 0 | 15.7557 | 16.7702 | 15.1477 | 73.4857 | 0.22821 | 7.49 | 6.89 | 65.459 | 494.68 | 485.52 | 3456.31 | 2674.9288 | 22.6074 | 86.5178 | 1580.2244 | 95.8576 | 100 | 80 | 10.3 | 10.7 | 9.8 | 20.5 | 20.5 | 0.49557 | 0.52195 | 16.4615 | 17.5215 | 6.8892 | 72.8108 | 0.24064 | 6.89 | NA | 39.884 | 485.52 | 1085.04 | 972.0818 | 10.4105 | 91.7853 | 728.8009 | 94.5274 | 80 | 60 | 10.2 | 3.6 | 6 | 9.6 | 9.6 | 0.51029 | 0.375 | 11.0769 | 11.7902 | 12.2646 | 47.5354 | 0.24803 | NA | NA | 141.61 | 1085.04 | 1971.6 | 1651.098 | 16.2559 | 70.8333 | 1368.069 | 89.6489 | 154 | 99 | 12.1 | 2.9 | 3.3 | 6.2 | 6.2 | 0.64093 | 0.46774 | 24.8571 | 26.4577 | 26.9083 | 87.4917 | 0.3024 | NA | 7.66 | 102.179 | 1971.6 | 3456.31 | 3614.4245 | -4.5747 | 78.9547 | 2793.0123 | 96.3416 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 0.75 | Net driving pressure required for permeation, NDP (psi) | 49.7034 | [5 empty] | 1997-08-17 | 16:00 | 916.71 | 23.8889 | 101 | 95 | 10.5333 | 0 | 17.5 | 3.2 |  | 20.7 | 20.7 | 0.84541 | 0 | 16.0305 | 17.0627 | 15.2579 | 72.2088 | 0.2363 | 7.55 | 6.77 | 68.541 | 480.57 | 477.12 | 3416.27 | 2711.5364 | 20.6287 | 85.6344 | 1594.3282 | 95.7009 | 101 | 82 | 10.1 | 11.5 | 9.2 | 20.7 | 20.7 | 0.48903 | 0.55556 | 17.6923 | 18.8315 | 7.1128 | 74.2872 | 0.2535 | 6.77 | NA | 39.412 | 477.12 | 1100.88 | 1024.255 | 6.9603 | 91.7396 | 750.6875 | 94.7499 | 82 | 59 | 9.9 | 3.3 | 5.8 | 9.1 | 9.1 | 0.48739 | 0.36264 | 10.1538 | 10.8077 | 12.3351 | 48.2649 | 0.22392 | NA | NA | 140.56 | 1100.88 | 1948.04 | 1647.269 | 15.4397 | 70.5399 | 1374.0745 | 89.7706 | 157 | 95 | 11.6 | 2.7 | 3.2 | 5.9 | 5.9 | 0.61394 | 0.45763 | 23.1429 | 24.633 | 26.2524 | 88.1476 | 0.27945 | NA | 7.79 | 101.717 | 1948.04 | 3416.27 | 3505.875 | -2.6229 | 78.681 | 2726.9575 | 96.2699 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Flow weighted system pressure losses, Lsys (psi) | 33.5282 | [5 empty] | 1997-08-18 | 0:00 | 922.08 | 25 | 100 | 98 | 10.7 | 0 | 17.4 | 3.4 |  | 20.8 | 20.8 | 0.83654 | 0 | 15.9389 | 16.4171 | 15.1499 | 73.1501 | 0.22443 | 7.48 | 6.69 | 63.181 | 461.48 | 488.88 | 3446.3 | 2667.4572 | 22.5994 | 87.0764 | 1578.1686 | 95.9966 | 100 | 80 | 10 | 11.2 | 9.6 | 20.8 | 20.8 | 0.49721 | 0.53846 | 17.2308 | 17.7477 | 7.1222 | 72.8778 | 0.24353 | 6.69 | NA | 39.058 | 488.88 | 1112.76 | 1013.6723 | 8.9047 | 92.0107 | 751.2762 | 94.8011 | 80 | 60 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.4092 | 12.9875 | 47.0125 | 0.24269 | NA | NA | 129.92 | 1112.76 | 1940.6 | 1744.5857 | 10.1007 | 73.425 | 1428.6729 | 90.9062 | 158 | 98 | 12.1 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 22.9543 | 25.4805 | 90.4195 | 0.25386 | NA | 7.49 | 97.328 | 1940.6 | 3446.3 | 3350.1609 | 2.7896 | 80.0916 | 2645.3805 | 96.3208 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Maximum element recovery (%) | 17 | Required influent pressure to the system, PI (psi) | 83.2317 | [5 empty] | 1997-08-18 | 11:20 | 934.84 | 23.8889 | 101 | 95 | 10.8333 | 0 | 17.6 | 3.3 |  | 20.9 | 20.9 | 0.84211 | 0 | 16.1221 | 17.1602 | 15.4036 | 71.7631 | 0.23912 | 7.47 | 6.63 | 66.263 | 473.1 | 486.36 | 3419.13 | 2726.8773 | 20.2465 | 86.3757 | 1606.6187 | 95.8756 | 101 | 80 | 10 | 11.2 | 9.7 | 20.9 | 20.9 | 0.50048 | 0.53589 | 17.2308 | 18.3403 | 7.0442 | 73.4558 | 0.24968 | 6.63 | NA | 39.766 | 486.36 | 1140.48 | 1002.0149 | 12.1409 | 91.8238 | 744.1875 | 94.6565 | 80 | 60 | 10.3 | 3.6 | 5.4 | 9 | 9 | 0.47104 | 0.4 | 11.0769 | 11.7902 | 13.3883 | 46.3117 | 0.25458 | NA | NA | 136.36 | 1140.48 | 1887.28 | 1809.8933 | 4.1004 | 71.9632 | 1475.1867 | 90.7564 | 160 | 95 | 12.2 | 2.8 | 3.3 | 6.1 | 6.1 | 0.63418 | 0.45902 | 24 | 25.5454 | 25.4483 | 89.8517 | 0.28431 | NA | 7.61 | 100.485 | 1887.28 | 3419.13 | 3403.3485 | 0.46157 | 79.3394 | 2645.3142 | 96.2014 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Variability of design flux (%) | 5 | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1997-08-18 | 19:00 | 942.62 | 24.4444 | 100 | 99 | 10.6 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.4012 | 14.1761 | 74.7239 | 0.21949 | 7.58 | 6.67 | 68.742 | 454.01 | 472.08 | 3403.4 | 2500.6329 | 26.5254 | 85.4385 | 1486.3564 | 95.3751 | 100 | 80 | 10 | 10.9 | 9.6 | 20.5 | 20.5 | 0.4923 | 0.53171 | 16.7692 | 17.5583 | 6.7737 | 73.2263 | 0.23978 | 6.67 | NA | 40.002 | 472.08 | 1097.91 | 962.6686 | 12.3181 | 91.5264 | 717.3743 | 94.4238 | 80 | 60 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.5378 | 47.4622 | 0.24437 | NA | NA | 149.1 | 1097.91 | 1877.36 | 1707.8593 | 9.0287 | 68.4164 | 1402.8846 | 89.3719 | 158 | 99 | 11.8 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 24.5339 | 92.1661 | 0.25318 | NA | 7.58 | 102.564 | 1877.36 | 3403.4 | 3234.5569 | 4.961 | 78.274 | 2555.9585 | 95.9873 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Rejection of reference solute and conditions of test | Magnesium Sulfate = 98 % Rejection | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1997-08-18 | 23:58 | 947 | 24.4444 | 100 | 100 | 10.6667 | 0 | 17.4 | 3.4 |  | 20.8 | 20.8 | 0.83654 | 0 | 15.9389 | 16.6889 | 14.6743 | 74.659 | 0.22354 | 7.49 | 6.75 | 66.464 | 453.18 | 478.8 | 3420.56 | 2588.9901 | 24.3109 | 86.1186 | 1533.8951 | 95.667 | 100 | 80 | 10 | 11.2 | 9.6 | 20.8 | 20.8 | 0.49721 | 0.53846 | 17.2308 | 18.0415 | 6.9495 | 73.0505 | 0.24697 | 6.75 | NA | 39.884 | 478.8 | 1112.76 | 990.8687 | 10.954 | 91.67 | 734.8343 | 94.5724 | 80 | 60 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.9052 | 47.0948 | 0.24627 | NA | NA | 136.15 | 1112.76 | 1894.72 | 1740.5807 | 8.1352 | 71.5643 | 1426.6704 | 90.4568 | 160 | 100 | 12 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 24.8271 | 93.1729 | 0.25044 | NA | 7.42 | 98.714 | 1894.72 | 3420.56 | 3268.1364 | 4.4561 | 79.383 | 2581.4282 | 96.176
|  | (e.g., solute type and concentration) | San Diego Tap = 75 % Rejection | [7 empty] | 1997-08-19 | 10:30 | 958.03 | 24.4444 | 100 | 97 | 10.6667 | 0 | 17.5 | 3.3 |  | 20.8 | 20.8 | 0.84135 | 0 | 16.0305 | 16.7848 | 15.1203 | 72.713 | 0.23084 | 7.51 | 6.71 | 66.397 | 456.5 | 480.48 | 3442.01 | 2676.3747 | 22.2438 | 86.1811 | 1578.4273 | 95.7935 | 100 | 78 | 10.2 | 11.2 | 9.6 | 20.8 | 20.8 | 0.49721 | 0.53846 | 17.2308 | 18.0415 | 6.9836 | 71.8164 | 0.25122 | 6.71 | NA | 39.412 | 480.48 | 1165.23 | 995.0593 | 14.604 | 91.7974 | 737.7697 | 94.658 | 78 | 58 | 10.1 | 3.4 | 5.5 | 8.9 | 8.9 | 0.47104 | 0.38202 | 10.4615 | 10.9538 | 13.2654 | 44.6346 | 0.24541 | NA | NA | 151.9 | 1165.23 | 1862.48 | 1791.6522 | 3.8029 | 68.3858 | 1478.4411 | 89.7257 | 157 | 97 | 11.7 | 2.9 | 3.3 | 6.2 | 6.2 | 0.64093 | 0.46774 | 24.8571 | 26.0268 | 25.3399 | 89.9601 | 0.28931 | NA | 7.58 | 102.025 | 1862.48 | 3442.01 | 3409.5465 | 0.94315 | 78.766 | 2636.0133 | 96.1296
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1997-08-19 | 19:00 | 966.41 | 24.4444 | 100 | 98 | 10.6 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.4012 | 14.272 | 74.128 | 0.22125 | 7.75 | 6.64 | 70.216 | 455.67 | 476.28 | 3374.8 | 2518.5431 | 25.3721 | 85.2574 | 1497.4115 | 95.3108 | 100 | 80 | 10 | 10.9 | 9.6 | 20.5 | 20.5 | 0.4923 | 0.53171 | 16.7692 | 17.5583 | 6.8386 | 73.1614 | 0.23999 | 6.64 | NA | 40.061 | 476.28 | 1099.89 | 971.5703 | 11.6666 | 91.5888 | 723.9252 | 94.4661 | 80 | 58 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.5085 | 46.4915 | 0.24947 | NA | NA | 153.3 | 1099.89 | 1866.2 | 1708.4121 | 8.455 | 67.8131 | 1404.1511 | 89.0824 | 158 | 98 | 11.8 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 24.3744 | 91.8256 | 0.25412 | NA | 7.72 | 102.949 | 1866.2 | 3374.8 | 3214.5684 | 4.7479 | 78.3848 | 2540.3842 | 95.9475
|  | Standard testing recovery (%) | 15 | [7 empty] | 1997-08-20 | 0:01 | 971.07 | 24.4444 | 100 | 99 | 10.6667 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.4012 | 14.4466 | 74.3868 | 0.22049 | 7.64 | 6.76 | 68.608 | 458.16 | 479.64 | 3371.94 | 2546.8892 | 24.4681 | 85.6959 | 1513.2646 | 95.4662 | 100 | 80 | 10 | 10.9 | 9.6 | 20.5 | 20.5 | 0.4923 | 0.53171 | 16.7692 | 17.5583 | 6.9043 | 73.0957 | 0.24021 | 6.76 | NA | 39.235 | 479.64 | 1120.68 | 979.6832 | 12.5814 | 91.8199 | 729.6616 | 94.6228 | 80 | 58 | 10 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 12.8406 | 46.1594 | 0.25126 | NA | NA | 148.96 | 1120.68 | 1882.32 | 1745.3571 | 7.2763 | 68.9434 | 1433.0186 | 89.6052 | 158 | 99 | 12 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 23.3343 | 24.6323 | 91.8677 | 0.254 | NA | 7.5 | 100.408 | 1882.32 | 3371.94 | 3244.9586 | 3.7658 | 79.066 | 2563.6393 | 96.0834
|  | Standard testing pH | 7 | [7 empty] | 1997-08-20 | 7:30 | 979.18 | 24.4444 | 104 | 98 | 10.7667 | 0 | 17.1 | 3.5 |  | 20.6 | 20.6 | 0.8301 | 0 | 15.6641 | 16.4012 | 14.0783 | 76.155 | 0.21537 | 7.53 | 6.84 | 68.206 | 471.44 | 477.12 | 3188.9 | 2474.957 | 22.3884 | 85.7046 | 1476.0385 | 95.3791 | 104 | 80 | 10.2 | 10.9 | 9.7 | 20.6 | 20.6 | 0.49557 | 0.52913 | 16.7692 | 17.5583 | 6.8216 | 74.9784 | 0.23418 | 6.84 | NA | 40.356 | 477.12 | 1038.51 | 967.9167 | 6.7976 | 91.5418 | 722.5183 | 94.4145 | 80 | 58 | 10.2 | 3.6 | 5.6 | 9.2 | 9.2 | 0.48412 | 0.3913 | 11.0769 | 11.5981 | 11.7622 | 47.0378 | 0.24657 | NA | NA | 148.4 | 1038.51 | 1842.64 | 1610.7236 | 12.5861 | 68.8967 | 1324.6168 | 88.7968 | 158 | 98 | 11.9 | 2.6 | 3.5 | 6.1 | 6.1 | 0.64768 | 0.42623 | 22.2857 | 23.3343 | 23.904 | 92.196 | 0.2531 | NA | 7.69 | 99.638 | 1842.64 | 3188.9 | 3137.4415 | 1.6137 | 79.1168 | 2490.0407 | 95.9985
|  | Acceptable range of operating pressures | 0 to 350 psi | [7 empty] | 1997-08-20 | 15:40 | 987.74 | 25 | 100 | 95 | 10.5333 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.134 | 14.4029 | 72.5638 | 0.22234 | 7.47 | 6.63 | 69.01 | 434.92 | 478.8 | 3289 | 2539.8026 | 22.7789 | 85.5869 | 1509.3013 | 95.4277 | 100 | 80 | 10 | 11 | 9.5 | 20.5 | 20.5 | 0.49066 | 0.53659 | 16.9231 | 17.4308 | 6.9303 | 73.0697 | 0.23855 | 6.63 | NA | 39.884 | 478.8 | 1083.06 | 987.0185 | 8.8676 | 91.67 | 732.9093 | 94.5581 | 80 | 58 | 10 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 11.0923 | 12.1939 | 46.8061 | 0.23698 | NA | NA | 154 | 1083.06 | 1863.72 | 1663.7225 | 10.7311 | 67.8363 | 1373.3912 | 88.7869 | 155 | 95 | 11.6 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 22.9543 | 24.3326 | 89.0674 | 0.25772 | NA | 7.61 | 103.488 | 1863.72 | 3289 | 3209.7798 | 2.4086 | 78.386 | 2536.7499 | 95.9204
|  | Acceptable range of operating pH values | 4 to 11 | [7 empty] | 1997-08-21 | 0:06 | 995.29 | 25 | 100 | 99 | 10.6 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.134 | 14.2861 | 74.6139 | 0.21623 | 7.53 | 6.79 | 69.814 | 444.05 | 476.28 | 3346.2 | 2520.5649 | 24.6738 | 85.3418 | 1498.4224 | 95.3408 | 100 | 80 | 10 | 11 | 9.5 | 20.5 | 20.5 | 0.49066 | 0.53659 | 16.9231 | 17.4308 | 6.8923 | 73.1077 | 0.23843 | 6.79 | NA | 39.766 | 476.28 | 1108.8 | 981.7173 | 11.4613 | 91.6507 | 728.9986 | 94.5451 | 80 | 58 | 10 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 11.0923 | 12.5465 | 46.4535 | 0.23878 | NA | NA | 152.88 | 1108.8 | 1874.88 | 1706.25 | 8.9942 | 67.9012 | 1407.525 | 89.1384 | 158 | 99 | 11.8 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 22.9543 | 24.5039 | 92.1961 | 0.24897 | NA | 7.68 | 102.256 | 1874.88 | 3346.2 | 3230.416 | 3.4602 | 78.5303 | 2552.648 | 95.9941
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1997-08-21 | 6:30 | 1002.28 | 24.4444 | 102 | 98 | 10.7333 | 0 | 17.1 | 3.5 |  | 20.6 | 20.6 | 0.8301 | 0 | 15.6641 | 16.4012 | 13.9788 | 75.2879 | 0.21785 | 7.43 | 6.83 | 67.737 | 456.5 | 473.76 | 3103.1 | 2457.4724 | 20.8059 | 85.7023 | 1465.6162 | 95.3783 | 102 | 80 | 10.2 | 11 | 9.6 | 20.6 | 20.6 | 0.49394 | 0.53398 | 16.9231 | 17.7194 | 6.8189 | 73.9811 | 0.23951 | 6.83 | NA | 40.238 | 473.76 | 1041.48 | 970.504 | 6.8149 | 91.5067 | 722.132 | 94.4279 | 80 | 58 | 10.2 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 11.276 | 11.6849 | 47.1151 | 0.23933 | NA | NA | 151.2 | 1041.48 | 1821.56 | 1597.905 | 12.2782 | 68.0851 | 1319.6925 | 88.5428 | 158 | 98 | 11.8 | 2.6 | 3.5 | 6.1 | 6.1 | 0.64768 | 0.42623 | 22.2857 | 23.3343 | 23.6044 | 92.5956 | 0.252 | NA | 7.73 | 100.408 | 1821.56 | 3103.1 | 3100.1301 | 0.095709 | 78.8061 | 2460.845 | 95.9198
|  | Maximum permissible SDI | 5 | [7 empty] | 1997-08-22 | 0:10 | 1019.03 | 25 | 100 | 98 | 10.6667 | 0 | 17.1 | 3.4 |  | 20.5 | 20.5 | 0.83415 | 0 | 15.6641 | 16.134 | 14.3297 | 74.0036 | 0.21802 | 7.63 | 6.79 | 69.412 | 439.9 | 477.12 | 3309.02 | 2527.6514 | 23.6133 | 85.4519 | 1502.3857 | 95.3799 | 100 | 80 | 10.2 | 11 | 9.5 | 20.5 | 20.5 | 0.49066 | 0.53659 | 16.9231 | 17.4308 | 6.9019 | 72.8981 | 0.23911 | 6.79 | NA | 40.002 | 477.12 | 1116.72 | 983.2566 | 11.9514 | 91.6159 | 730.1883 | 94.5217 | 80 | 58 | 10 | 3.5 | 5.6 | 9.1 | 9.1 | 0.48085 | 0.38462 | 10.7692 | 11.0923 | 12.6136 | 46.3864 | 0.23913 | NA | NA | 155.68 | 1116.72 | 1852.56 | 1717.37 | 7.2975 | 67.3709 | 1417.045 | 89.0138 | 158 | 98 | 11.8 | 2.6 | 3.4 | 6 | 6 | 0.63418 | 0.43333 | 22.2857 | 22.9543 | 24.1837 | 92.0163 | 0.24946 | NA | 7.68 | 103.103 | 1852.56 | 3309.02 | 3190.3801 | 3.5853 | 78.3906 | 2521.47 | 95.911
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 1997-08-22 | 6:30 | 1026.12 | 24.4444 | 105 | 88 | 9.4333 | 0 | 13 | 3.3 |  | 16.3 | 16.3 | 0.79755 | 0 | 11.9084 | 12.4687 | 12.1844 | 74.8823 | 0.16651 | 7.5 | 6.75 | 67.67 | 481.4 | 477.96 | 2203.63 | 2094.2539 | 4.9634 | 85.8419 | 1286.107 | 94.7384 | 105 | 60 | 8.5 | 8.1 | 8.2 | 16.3 | 16.3 | 0.40071 | 0.49693 | 12.4615 | 13.0479 | 5.8931 | 68.1069 | 0.19158 | 6.75 | NA | 83.485 | 477.96 | 905.85 | 867.6243 | 4.2199 | 82.5331 | 672.7922 | 87.5913 | 60 | 40 | 8.8 | 2.4 | 5.4 | 7.8 | 7.8 | 0.43178 | 0.30769 | 7.3846 | 7.7321 | 9.2663 | 31.9337 | 0.24213 | NA | NA | 147.7 | 905.85 | 1945.56 | 1242.8056 | 36.1209 | 69.0978 | 1074.3278 | 86.2519 | 145 | 88 | 11 | 2.5 | 3.3 | 5.8 | 5.8 | 0.61394 | 0.43103 | 21.4286 | 22.4369 | 23.4278 | 82.0722 | 0.27338 | NA | 7.71 | 246.4 | 1945.56 | 2203.63 | 3232.8024 | -46.7035 | 48.4476 | 2589.1812 | 90.4835
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1997-08-23 | 0:00 | 1041.84 | 25.5556 | 120 | 90 | 9.9 | 0 | 14.4 | 3.8 |  | 18.2 | 18.2 | 0.79121 | 0 | 13.1908 | 13.3653 | 11.8817 | 83.2183 | 0.16061 | 7.57 | 6.78 | 68.34 | 448.2 | 478.8 | 3360.5 | 2034.2274 | 39.4665 | 85.7268 | 1256.5137 | 94.5611 | 120 | 70 | 9.2 | 9 | 9.2 | 18.2 | 18.2 | 0.44814 | 0.49451 | 13.8462 | 14.0293 | 6.5343 | 79.2657 | 0.17699 | 6.78 | NA | 40.002 | 478.8 | 1098.9 | 908.0589 | 17.3666 | 91.6454 | 693.4295 | 94.2313 | 70 | 50 | 9.5 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.3528 | 12.1524 | 38.3476 | 0.2439 | NA | NA | 147.84 | 1098.9 | 1874.88 | 1627.2667 | 13.2069 | 69.1228 | 1363.0833 | 89.154 | 152 | 90 | 11 | 2.4 | 3.8 | 6.2 | 6.2 | 0.67466 | 0.3871 | 20.5714 | 20.8435 | 23.3321 | 86.6679 | 0.2405 | NA | 7.58 | 101.64 | 1874.88 | 3360.5 | 2994.8211 | 10.8817 | 78.7719 | 2434.8505 | 95.8256
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1997-08-23 | 7:20 | 1049.86 | 25.5556 | 120 | 95 | 10.0667 | 0 | 14.5 | 3.4 |  | 17.9 | 17.9 | 0.81006 | 0 | 13.2824 | 13.4581 | 12.6033 | 84.8301 | 0.15865 | 7.36 | 6.78 | 78.122 | 475.59 | 480.48 | 2676.96 | 2196.4185 | 17.951 | 83.7408 | 1338.4493 | 94.1632 | 120 | 72 | 9.5 | 9 | 8.9 | 17.9 | 17.9 | 0.43833 | 0.50279 | 13.8462 | 14.0293 | 6.5457 | 79.9543 | 0.17547 | 6.78 | NA | 45.725 | 480.48 | 1031.58 | 920.1199 | 10.8048 | 90.4835 | 700.2999 | 93.4707 | 72 | 50 | 9.5 | 3 | 5.5 | 8.5 | 8.5 | 0.45795 | 0.35294 | 9.2308 | 9.3528 | 11.3652 | 40.1348 | 0.23304 | NA | NA | 138.6 | 1031.58 | 1702.52 | 1518.66 | 10.7993 | 71.1538 | 1275.12 | 89.1304 | 152 | 95 | 11.2 | 2.5 | 3.4 | 5.9 | 5.9 | 0.62744 | 0.42373 | 21.4286 | 21.7119 | 22.0987 | 90.2013 | 0.24071 | NA | 7.59 | 86.702 | 1702.52 | 2676.96 | 2890.6215 | -7.9815 | 81.9551 | 2296.5707 | 96.2247
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1997-08-23 | 14:20 | 1056.93 | 25 | 119 | 92 | 9.7333 | 0 | 14.3 | 3.4 |  | 17.7 | 17.7 | 0.80791 | 0 | 13.0992 | 13.4922 | 12.6236 | 83.1431 | 0.16228 | 7.43 | 6.76 | 77.854 | 473.93 | 484.68 | 2818.53 | 2195.7423 | 22.0962 | 83.937 | 1340.2111 | 94.1909 | 119 | 70 | 9 | 8.8 | 8.9 | 17.7 | 17.7 | 0.43506 | 0.49718 | 13.5385 | 13.9446 | 6.4794 | 79.0206 | 0.17647 | 6.76 | NA | 51.094 | 484.68 | 1032.57 | 913.3942 | 11.5417 | 89.4582 | 699.0371 | 92.6908 | 70 | 50 | 9.1 | 3 | 5.5 | 8.5 | 8.5 | 0.45795 | 0.35294 | 9.2308 | 9.5077 | 11.3333 | 39.5667 | 0.2403 | NA | NA | 142.1 | 1032.57 | 1729.8 | 1518.2809 | 12.228 | 70.6817 | 1275.4255 | 88.8586 | 151 | 92 | 11.1 | 2.5 | 3.4 | 5.9 | 5.9 | 0.62744 | 0.42373 | 21.4286 | 22.0714 | 22.477 | 87.923 | 0.25103 | NA | 7.55 | 86.317 | 1729.8 | 2818.53 | 2938.2434 | -4.2474 | 82.1909 | 2334.0217 | 96.3018
[11 empty] | 1997-08-24 | 1:30 | 1068.25 | 25.5556 | 105 | 98 | 9.7333 | 0 | 14.4 | 3.4 |  | 17.8 | 17.8 | 0.80899 | 0 | 13.1908 | 13.3653 | 12.7757 | 78.991 | 0.1692 | 7.48 | 6.8 | 67.335 | 456.5 | 477.12 | 3203.2 | 2212.68 | 30.9228 | 85.8872 | 1344.9 | 94.9933 | 105 | 85 | 9 | 9 | 8.8 | 17.8 | 17.8 | 0.43506 | 0.50562 | 13.8462 | 14.0293 | 6.5993 | 79.4007 | 0.17669 | 6.8 | NA | 40.474 | 477.12 | 1011.78 | 923.6898 | 8.7065 | 91.517 | 700.4049 | 94.2213 | 85 | 70 | 9.2 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.3528 | 11.0929 | 57.2071 | 0.16349 | NA | NA | 143.64 | 1011.78 | 1872.4 | 1494.08 | 20.2051 | 69.8944 | 1252.93 | 88.5357 | 152 | 98 | 11 | 2.4 | 3.4 | 5.8 | 5.8 | 0.62069 | 0.41379 | 20.5714 | 20.8435 | 24.0824 | 89.9176 | 0.23181 | NA | 7.54 | 92.4 | 1872.4 | 3203.2 | 3128.8706 | 2.3205 | 80.6338 | 2500.6353 | 96.3049
[11 empty] | 1997-08-24 | 8:20 | 1075.14 | 25 | 120 | 95 | 10.1 | 0 | 14.7 | 3.4 |  | 18.1 | 18.1 | 0.81215 | 0 | 13.4656 | 13.8696 | 13.1502 | 84.2498 | 0.16462 | 7.57 | 6.81 | 71.288 | 483.06 | 487.2 | 2715.57 | 2285.4078 | 15.8406 | 85.3678 | 1386.3039 | 94.8577 | 120 | 72 | 9.5 | 9.1 | 9 | 18.1 | 18.1 | 0.44323 | 0.50276 | 14 | 14.42 | 6.6449 | 79.8551 | 0.18058 | 6.81 | NA | 45.843 | 487.2 | 1025.64 | 933.461 | 8.9875 | 90.5905 | 710.3305 | 93.5462 | 72 | 50 | 9.5 | 3.1 | 5.5 | 8.6 | 8.6 | 0.46122 | 0.36047 | 9.5385 | 9.8246 | 11.3747 | 40.1253 | 0.24485 | NA | NA | 138.25 | 1025.64 | 1717.4 | 1525.8053 | 11.1561 | 71.6236 | 1275.7226 | 89.163 | 154 | 95 | 11.3 | 2.5 | 3.4 | 5.9 | 5.9 | 0.62744 | 0.42373 | 21.4286 | 22.0714 | 22.2064 | 90.9936 | 0.24256 | NA | 7.71 | 93.709 | 1717.4 | 2715.57 | 2911.2904 | -7.2073 | 80.7658 | 2314.3452 | 95.9509
[11 empty] | 1997-08-24 | 14:50 | 1081.63 | 25 | 116 | 92 | 9.6667 | 0 | 14.9 | 3.4 |  | 18.3 | 18.3 | 0.81421 | 0 | 13.6489 | 14.0583 | 12.6657 | 81.6677 | 0.17214 | 7.52 | 6.73 | 71.824 | 447.37 | 468.72 | 2814.24 | 2208.0584 | 21.5398 | 84.6766 | 1338.3892 | 94.6335 | 116 | 71 | 9 | 9.3 | 9 | 18.3 | 18.3 | 0.4465 | 0.5082 | 14.3077 | 14.7369 | 6.3993 | 78.1007 | 0.18869 | 6.73 | NA | 46.787 | 468.72 | 1042.47 | 904.7174 | 13.2141 | 90.0181 | 686.7187 | 93.1869 | 71 | 50 | 9 | 3.1 | 5.5 | 8.6 | 8.6 | 0.46122 | 0.36047 | 9.5385 | 9.8246 | 11.5052 | 39.9948 | 0.24565 | NA | NA | 144.9 | 1042.47 | 1731.04 | 1548.3731 | 10.5524 | 69.086 | 1295.4215 | 88.8145 | 154 | 92 | 11 | 2.5 | 3.4 | 5.9 | 5.9 | 0.62744 | 0.42373 | 21.4286 | 22.0714 | 22.4614 | 89.5386 | 0.2465 | NA | 7.67 | 88.704 | 1731.04 | 2814.24 | 2938.64 | -4.4204 | 81.0753 | 2334.84 | 96.2009
[11 empty] | 1997-08-25 | 1:00 | 1091.46 | 25.5556 | 118 | 99 | 10.2667 | 0 | 14.9 | 3.4 |  | 18.3 | 18.3 | 0.81421 | 0 | 13.6489 | 13.8293 | 14.2977 | 83.9357 | 0.16476 | 7.72 | 6.8 | 72.762 | 509.62 | 520.8 | 3231.8 | 2484.2606 | 23.1307 | 86.0288 | 1502.5303 | 95.1574 | 118 | 74 | 9.8 | 9.3 | 9 | 18.3 | 18.3 | 0.4465 | 0.5082 | 14.3077 | 14.4969 | 7.1874 | 79.0126 | 0.18348 | 6.8 | NA | 46.905 | 520.8 | 1106.82 | 1010.4915 | 8.7032 | 90.9937 | 765.6458 | 93.8738 | 74 | 50 | 9.8 | 3.2 | 5.4 | 8.6 | 8.6 | 0.45795 | 0.37209 | 9.8462 | 9.9764 | 12.3514 | 39.8486 | 0.25036 | NA | NA | 154 | 1106.82 | 1799.24 | 1671.4541 | 7.1022 | 70.4301 | 1389.137 | 88.914 | 155 | 99 | 11.2 | 2.4 | 3.4 | 5.8 | 5.8 | 0.62069 | 0.41379 | 20.5714 | 20.8435 | 22.9654 | 92.8346 | 0.22452 | NA | 7.79 | 101.794 | 1799.24 | 3231.8 | 2997.4372 | 7.2518 | 80.4543 | 2398.3386 | 95.7556
[11 empty] | 1997-08-25 | 7:10 | 1097.95 | 25 | 118 | 98 | 10.3 | 0 | 15 | 3.5 |  | 18.5 | 18.5 | 0.81081 | 0 | 13.7405 | 14.1527 | 13.1548 | 84.5452 | 0.1674 | 7.44 | 6.81 | 69.479 | 472.27 | 488.04 | 2787.07 | 2281.8729 | 18.1265 | 85.7637 | 1384.9564 | 94.9833 | 118 | 75 | 9.8 | 9.3 | 9.2 | 18.5 | 18.5 | 0.45305 | 0.5027 | 14.3077 | 14.7369 | 6.7165 | 79.9835 | 0.18425 | 6.81 | NA | 41.89 | 488.04 | 1039.5 | 939.0395 | 9.6643 | 91.4167 | 713.5397 | 94.1293 | 75 | 52 | 9.8 | 3.2 | 5.6 | 8.8 | 8.8 | 0.47104 | 0.36364 | 9.8462 | 10.1415 | 11.6028 | 42.0972 | 0.24091 | NA | NA | 137.06 | 1039.5 | 1758.32 | 1555.18 | 11.5531 | 71.9162 | 1297.34 | 89.4353 | 158 | 98 | 11.3 | 2.5 | 3.5 | 6 | 6 | 0.64093 | 0.41667 | 21.4286 | 22.0714 | 22.5702 | 94.1298 | 0.23448 | NA | 7.73 | 95.249 | 1758.32 | 2787.07 | 2946.2279 | -5.7106 | 80.4834 | 2352.2739 | 95.9508
[11 empty] | 1997-08-25 | 16:10 | 1107 | 25 | 118 | 95 | 9.6333 | 0 | 16 | 3.4 |  | 19.4 | 19.4 | 0.82474 | 0 | 14.6565 | 15.0962 | 13.0407 | 83.8259 | 0.18009 | 7.69 | 6.66 | 72.226 | 442.39 | 461.16 | 3088.8 | 2291.4376 | 25.8146 | 84.3382 | 1376.2988 | 94.7522 | 118 | 70 | 9 | 10.4 | 9 | 19.4 | 19.4 | 0.4645 | 0.53608 | 16 | 16.48 | 6.5621 | 78.4379 | 0.2101 | 6.66 | NA | 45.253 | 461.16 | 1036.53 | 941.7636 | 9.1427 | 90.1871 | 701.4618 | 93.5488 | 70 | 50 | 9 | 3.1 | 5.4 | 8.5 | 8.5 | 0.45468 | 0.36471 | 9.5385 | 9.8246 | 11.545 | 39.455 | 0.24901 | NA | NA | 139.51 | 1036.53 | 1698.8 | 1551.4859 | 8.6717 | 69.748 | 1294.008 | 89.2188 | 152 | 95 | 10.9 | 2.5 | 3.4 | 5.9 | 5.9 | 0.62744 | 0.42373 | 21.4286 | 22.0714 | 21.9235 | 90.6765 | 0.24341 | NA | 7.76 | 95.788 | 1698.8 | 3088.8 | 2877.4853 | 6.8413 | 79.2289 | 2288.1426 | 95.8137
[11 empty] | 1997-08-26 | 7:00 | 1121.63 | 25 | 116 | 98 | 10.5 | 0 | 16 | 3.5 |  | 19.5 | 19.5 | 0.82051 | 0 | 14.6565 | 15.0962 | 13.8 | 82.7 | 0.18254 | 7.5 | 6.79 | 67.201 | 483.06 | 487.2 | 2724.15 | 2407.1954 | 11.635 | 86.2067 | 1447.1977 | 95.3565 | 116 | 80 | 10 | 10.1 | 9.4 | 19.5 | 19.5 | 0.47267 | 0.51795 | 15.5385 | 16.0046 | 6.8609 | 81.1391 | 0.19725 | 6.79 | NA | 40.887 | 487.2 | 1052.37 | 966.7491 | 8.136 | 91.6078 | 726.9745 | 94.3757 | 80 | 58 | 10 | 3.4 | 5.6 | 9 | 9 | 0.47758 | 0.37778 | 10.4615 | 10.7754 | 11.8113 | 47.1887 | 0.22835 | NA | NA | 146.3 | 1052.37 | 1798 | 1602.4839 | 10.8741 | 69.9713 | 1327.427 | 88.9787 | 160 | 98 | 11.5 | 2.5 | 3.5 | 6 | 6 | 0.64093 | 0.41667 | 21.4286 | 22.0714 | 23.0534 | 94.4466 | 0.23369 | NA | 7.69 | 99.33 | 1798 | 2724.15 | 3011.3357 | -10.5422 | 79.6121 | 2404.6679 | 95.8693
[11 empty] | 1997-08-26 | 16:48 | 1131.48 | 25.5556 | 114 | 98 | 10.2667 | 0 | 15.4 | 3.5 |  | 18.9 | 18.9 | 0.81481 | 0 | 14.1069 | 14.2934 | 12.9469 | 82.7865 | 0.17265 | 7.61 | 6.67 | 71.69 | 458.99 | 476.28 | 3088.8 | 2256.476 | 26.9465 | 84.9479 | 1366.378 | 94.7533 | 114 | 78 | 9.8 | 9.7 | 9.2 | 18.9 | 18.9 | 0.45959 | 0.51323 | 14.9231 | 15.1204 | 6.6267 | 79.5733 | 0.19002 | 6.67 | NA | 42.362 | 476.28 | 1071.18 | 933.7805 | 12.8269 | 91.1057 | 705.0303 | 93.9915 | 78 | 55 | 9.8 | 3.3 | 5.5 | 8.8 | 8.8 | 0.46777 | 0.375 | 10.1538 | 10.2881 | 12.0598 | 44.6402 | 0.23047 | NA | NA | 143.5 | 1071.18 | 1810.4 | 1627.788 | 10.0868 | 69.8707 | 1349.484 | 89.3663 | 156 | 98 | 11.2 | 2.4 | 3.5 | 5.9 | 5.9 | 0.63418 | 0.40678 | 20.5714 | 20.8435 | 22.9421 | 92.8579 | 0.22447 | NA | 7.74 | 101.948 | 1810.4 | 3088.8 | 2981.9099 | 3.4606 | 78.5949 | 2396.155 | 95.7454
[11 empty] | 1997-08-27 | 5:00 | 1143.54 | 24.4444 | 112 | 98 | 10.4 | 0 | 15.9 | 3.5 |  | 19.4 | 19.4 | 0.81959 | 0 | 14.5649 | 15.2502 | 13.7137 | 80.8863 | 0.18854 | 7.48 | 6.81 | 68.005 | 474.76 | 487.2 | 2751.32 | 2391.543 | 13.0765 | 86.0417 | 1439.3715 | 95.2754 | 112 | 80 | 10 | 10.1 | 9.3 | 19.4 | 19.4 | 0.4694 | 0.52062 | 15.5385 | 16.2696 | 6.8785 | 79.1215 | 0.20563 | 6.81 | NA | 41.418 | 487.2 | 1044.45 | 971.3288 | 7.0009 | 91.4988 | 729.2644 | 94.3206 | 80 | 55 | 10 | 3.4 | 5.4 | 8.8 | 8.8 | 0.4645 | 0.38636 | 10.4615 | 10.9538 | 11.9222 | 45.5778 | 0.24033 | NA | NA | 137.69 | 1044.45 | 1791.8 | 1615.373 | 9.8464 | 71.7385 | 1329.9115 | 89.6467 | 160 | 98 | 11.2 | 2.4 | 3.5 | 5.9 | 5.9 | 0.63418 | 0.40678 | 20.5714 | 21.5394 | 22.775 | 95.025 | 0.22667 | NA | 7.7 | 95.788 | 1791.8 | 2751.32 | 2954.7797 | -7.395 | 80.3391 | 2373.2898 | 95.9639
[11 empty] | 1997-08-27 | 8:05 | 1146.79 | 25 | 118 | 99 | 10.4 | 0 | 15.4 | 3.5 |  | 18.9 | 18.9 | 0.81481 | 0 | 14.1069 | 14.5301 | 13.2831 | 84.8169 | 0.17131 | 7.56 | 6.76 | 68.742 | 481.4 | 483.84 | 3074.5 | 2310.2712 | 24.857 | 85.7924 | 1397.0556 | 95.0795 | 118 | 80 | 10 | 9.7 | 9.2 | 18.9 | 18.9 | 0.45959 | 0.51323 | 14.9231 | 15.3708 | 6.7728 | 82.2272 | 0.18693 | 6.76 | NA | 40.356 | 483.84 | 1067.22 | 951.4264 | 10.85 | 91.6592 | 717.6332 | 94.3765 | 80 | 55 | 10 | 3.3 | 5.4 | 8.7 | 8.7 | 0.46122 | 0.37931 | 10.1538 | 10.4585 | 12.0844 | 45.4156 | 0.23028 | NA | NA | 141.61 | 1067.22 | 1765.76 | 1632.8706 | 7.5259 | 70.7321 | 1350.0453 | 89.5107 | 158 | 99 | 11.2 | 2.4 | 3.5 | 5.9 | 5.9 | 0.63418 | 0.40678 | 20.5714 | 21.1886 | 22.4005 | 94.8995 | 0.22327 | NA | 7.72 | 97.636 | 1765.76 | 3074.5 | 2909.6165 | 5.3629 | 79.8206 | 2337.6882 | 95.8234
[11 empty] | 1997-08-27 | 15:50 | 1154.61 | 25 | 112 | 96 | 10.2667 | 0 | 14.4 | 3.5 |  | 17.9 | 17.9 | 0.80447 | 0 | 13.1908 | 13.5866 | 12.6756 | 81.0577 | 0.16762 | 7.56 | 6.67 | 67.536 | 457.33 | 482.16 | 2789.93 | 2188.0416 | 21.5736 | 85.993 | 1335.1008 | 94.9415 | 112 | 76 | 9.8 | 8.7 | 9.2 | 17.9 | 17.9 | 0.44323 | 0.48603 | 13.3846 | 13.7862 | 6.5053 | 77.6947 | 0.17744 | 6.67 | NA | 40.474 | 482.16 | 1035.54 | 899.8413 | 13.1041 | 91.6057 | 691.0007 | 94.1427 | 76 | 52 | 9.8 | 3.3 | 5.4 | 8.7 | 8.7 | 0.46122 | 0.37931 | 10.1538 | 10.4585 | 11.6735 | 42.5265 | 0.24593 | NA | NA | 141.4 | 1035.54 | 1780.64 | 1581.9589 | 11.1578 | 70.6736 | 1308.7494 | 89.1958 | 158 | 96 | 11.2 | 2.4 | 3.5 | 5.9 | 5.9 | 0.63418 | 0.40678 | 20.5714 | 21.1886 | 22.5569 | 93.2431 | 0.22724 | NA | 7.71 | 100.87 | 1780.64 | 2789.93 | 2932.4823 | -5.1095 | 79.0796 | 2356.5611 | 95.7196
[11 empty] | 1997-08-28 | 2:30 | 1164.99 | 24.4444 | 110 | 98 | 9.9 | 0 | 13.9 | 3.4 |  | 17.3 | 17.3 | 0.80347 | 0 | 12.7328 | 13.332 | 12.9418 | 81.1582 | 0.16427 | 7.64 | 6.73 | 78.859 | 486.38 | 504 | 3131.7 | 2242.0764 | 28.407 | 84.3534 | 1373.0382 | 94.2566 | 110 | 72 | 9.2 | 8.5 | 8.8 | 17.3 | 17.3 | 0.42688 | 0.49133 | 13.0769 | 13.6922 | 6.705 | 75.095 | 0.18233 | 6.73 | NA | 51.861 | 504 | 1071.18 | 940.7252 | 12.1786 | 89.7101 | 722.3626 | 92.8206 | 72 | 50 | 9.5 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.6651 | 11.7195 | 39.7805 | 0.24296 | NA | NA | 154 | 1071.18 | 1771.96 | 1580.7244 | 10.7923 | 69.4444 | 1325.9522 | 88.3857 | 155 | 98 | 11 | 2.4 | 3.4 | 5.8 | 5.8 | 0.62069 | 0.41379 | 20.5714 | 21.5394 | 22.6516 | 92.8484 | 0.23198 | NA | 7.75 | 97.713 | 1771.96 | 3131.7 | 2953.7814 | 5.6812 | 80.6125 | 2362.8707 | 95.8646
[11 empty] | 1997-08-28 | 8:45 | 1171.47 | 25 | 111 | 98 | 9.7 | 0 | 13.9 | 3.4 |  | 17.3 | 17.3 | 0.80347 | 0 | 12.7328 | 13.1148 | 12.8516 | 81.9484 | 0.16004 | 7.58 | 6.71 | 76.782 | 479.74 | 498.96 | 3134.56 | 2224.923 | 29.0196 | 84.6116 | 1361.9415 | 94.3623 | 111 | 70 | 9.2 | 8.5 | 8.8 | 17.3 | 17.3 | 0.42688 | 0.49133 | 13.0769 | 13.4692 | 6.7125 | 74.5875 | 0.18058 | 6.71 | NA | 46.315 | 498.96 | 1043.46 | 936.1739 | 10.2818 | 90.7177 | 717.567 | 93.5456 | 70 | 50 | 9 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.5077 | 11.47 | 39.53 | 0.24052 | NA | NA | 145.81 | 1043.46 | 1773.2 | 1542.1544 | 13.0299 | 70.7772 | 1292.8072 | 88.7214 | 155 | 98 | 10.9 | 2.4 | 3.4 | 5.8 | 5.8 | 0.62069 | 0.41379 | 20.5714 | 21.1886 | 22.6819 | 92.9181 | 0.22803 | NA | 7.72 | 96.712 | 1773.2 | 3134.56 | 2956.6033 | 5.6772 | 80.6173 | 2364.9016 | 95.9105
[11 empty] | 1997-08-28 | 15:50 | 1178.47 | 25 | 112 | 98 | 9.6 | 0 | 13.8 | 3.4 |  | 17.2 | 17.2 | 0.80233 | 0 | 12.6412 | 13.0205 | 12.3029 | 83.0971 | 0.15669 | 7.56 | 6.68 | 76.045 | 478.91 | 482.16 | 2562.56 | 2130.5091 | 16.8601 | 84.2283 | 1306.3346 | 94.1788 | 112 | 70 | 9 | 8.5 | 8.7 | 17.2 | 17.2 | 0.42361 | 0.49419 | 13.0769 | 13.4692 | 6.564 | 75.436 | 0.17855 | 6.68 | NA | 41.182 | 482.16 | 1001.88 | 913.0006 | 8.8713 | 91.4589 | 697.5803 | 94.0965 | 70 | 50 | 9 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.5077 | 10.902 | 40.098 | 0.23711 | NA | NA | 148.68 | 1001.88 | 1645.48 | 1475.88 | 10.307 | 69.1638 | 1238.88 | 87.9988 | 155 | 98 | 10.8 | 2.3 | 3.4 | 5.7 | 5.7 | 0.61394 | 0.40351 | 19.7143 | 20.3057 | 20.6788 | 95.0212 | 0.2137 | NA | 7.67 | 100.254 | 1645.48 | 2562.56 | 2690.7799 | -5.0036 | 79.2073 | 2168.13 | 95.376
[11 empty] | 1997-08-29 | 0:00 | 1185.91 | 25.5556 | 110 | 98 | 9.6 | 0 | 13.7 | 3.8 |  | 17.5 | 17.5 | 0.78286 | 0 | 12.5496 | 12.7156 | 11.4772 | 82.9228 | 0.15334 | 7.62 | 6.67 | 78.524 | 482.23 | 488.04 | 2751.32 | 1964.4529 | 28.5996 | 83.9103 | 1226.2465 | 93.5964 | 110 | 70 | 9 | 8.5 | 9 | 17.5 | 17.5 | 0.43342 | 0.48571 | 13.0769 | 13.2499 | 6.0124 | 74.9876 | 0.17669 | 6.67 | NA | 79.65 | 488.04 | 1032.57 | 873.7417 | 15.3818 | 83.6796 | 680.8908 | 88.3021 | 70 | 48 | 9 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.3528 | 11.4444 | 38.5556 | 0.24258 | NA | NA | 136.92 | 1032.57 | 1686.4 | 1530.1533 | 9.2651 | 71.9449 | 1281.3617 | 89.3145 | 152 | 98 | 10.8 | 2.2 | 3.8 | 6 | 6 | 0.66117 | 0.36667 | 18.8571 | 19.1065 | 20.5244 | 93.6756 | 0.20396 | NA | 7.65 | 94.71 | 1686.4 | 2751.32 | 2607.9047 | 5.2126 | 80.5938 | 2147.1524 | 95.589
[11 empty] | 1997-08-29 | 8:20 | 1195 | 25.5556 | 110 | 98 | 9.6333 | 0 | 13.8 | 3.8 |  | 17.6 | 17.6 | 0.78409 | 0 | 12.6412 | 12.8084 | 11.6209 | 82.7457 | 0.15479 | 7.58 | 6.71 | 77.854 | 489.7 | 490.56 | 2888.6 | 1989.3344 | 31.1315 | 84.1296 | 1239.9472 | 93.7212 | 110 | 70 | 9 | 8.5 | 9.1 | 17.6 | 17.6 | 0.43669 | 0.48295 | 13.0769 | 13.2499 | 6.5683 | 74.4317 | 0.17801 | 6.71 | NA | 42.834 | 490.56 | 1028.61 | 908.7656 | 11.6511 | 91.2683 | 699.6628 | 93.8779 | 70 | 50 | 9 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.3528 | 11.341 | 39.659 | 0.23583 | NA | NA | 141.05 | 1028.61 | 1671.52 | 1521.6989 | 8.9632 | 71.2471 | 1275.1544 | 88.9386 | 155 | 98 | 10.9 | 2.3 | 3.8 | 6.1 | 6.1 | 0.66792 | 0.37705 | 19.7143 | 19.975 | 20.523 | 95.077 | 0.21009 | NA | 7.63 | 96.019 | 1671.52 | 2888.6 | 2625.1127 | 9.1216 | 80.4267 | 2148.3164 | 95.5305
[11 empty] | 1997-08-29 | 14:40 | 1201.11 | 25 | 112 | 98 | 9.1333 | 0 | 13.7 | 3.4 |  | 17.1 | 17.1 | 0.80117 | 0 | 12.5496 | 12.9261 | 12.0658 | 83.8009 | 0.15425 | 7.46 | 6.63 | 74.37 | 447.37 | 474.6 | 2638.35 | 2087.2915 | 20.8865 | 84.33 | 1280.9457 | 94.1941 | 112 | 70 | 8.6 | 8.6 | 8.5 | 17.1 | 17.1 | 0.4187 | 0.50292 | 13.2308 | 13.6277 | 6.326 | 76.074 | 0.17914 | 6.63 | NA | 54.516 | 474.6 | 987.03 | 899.6262 | 8.8552 | 88.5133 | 687.1131 | 92.0659 | 70 | 49 | 8.6 | 2.9 | 5.4 | 8.3 | 8.3 | 0.44814 | 0.3494 | 8.9231 | 9.1908 | 10.8433 | 40.0567 | 0.22944 | NA | NA | 132.23 | 987.03 | 1626.88 | 1446.0893 | 11.1127 | 72.1386 | 1216.5596 | 89.1308 | 152 | 98 | 10.2 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.4229 | 20.3195 | 94.4805 | 0.20558 | NA | 7.59 | 91.63 | 1626.88 | 2638.35 | 2620.2771 | 0.68501 | 80.6932 | 2123.5785 | 95.6851
[11 empty] | 1997-08-30 | 20:00 | 1206.46 | 25 | 112 | 98 | 9.3333 | 0 | 13.8 | 3.4 |  | 17.2 | 17.2 | 0.80233 | 0 | 12.6412 | 13.0205 | 12.6479 | 83.0188 | 0.15684 | 7.44 | 6.66 | 75.576 | 463.14 | 493.08 | 2781.35 | 2187.6551 | 21.3456 | 84.6727 | 1340.3675 | 94.3615 | 112 | 70 | 8.9 | 8.6 | 8.6 | 17.2 | 17.2 | 0.42197 | 0.5 | 13.2308 | 13.6277 | 6.6147 | 75.4853 | 0.18053 | 6.66 | NA | 52.097 | 493.08 | 1020.69 | 934.063 | 8.4871 | 89.4344 | 713.5715 | 92.6991 | 70 | 49 | 8.9 | 2.9 | 5.4 | 8.3 | 8.3 | 0.44814 | 0.3494 | 8.9231 | 9.1908 | 11.2188 | 39.3812 | 0.23338 | NA | NA | 136.29 | 1020.69 | 1706.24 | 1495.6456 | 12.3426 | 72.3595 | 1258.1678 | 89.1676 | 156 | 98 | 10.2 | 2.3 | 3.4 | 5.7 | 5.7 | 0.61394 | 0.40351 | 19.7143 | 20.3057 | 21.6753 | 95.1247 | 0.21346 | NA | 7.72 | 86.548 | 1706.24 | 2781.35 | 2801.914 | -0.73935 | 82.4475 | 2254.077 | 96.1604
[11 empty] | 1997-08-30 | 8:45 | 1219.52 | 25 | 112 | 98 | 9.5 | 0 | 13.7 | 3.4 |  | 17.1 | 17.1 | 0.80117 | 0 | 12.5496 | 12.9261 | 12.4012 | 83.0988 | 0.15555 | 7.48 | 6.69 | 75.844 | 466.46 | 487.2 | 2809.95 | 2144.7227 | 23.674 | 84.4327 | 1315.9614 | 94.2366 | 112 | 70 | 9 | 8.5 | 8.6 | 17.1 | 17.1 | 0.42034 | 0.49708 | 13.0769 | 13.4692 | 6.5365 | 75.4635 | 0.17849 | 6.69 | NA | 49.737 | 487.2 | 1025.64 | 919.5762 | 10.3412 | 89.7913 | 703.3881 | 92.9289 | 70 | 50 | 9 | 3 | 5.4 | 8.4 | 8.4 | 0.45141 | 0.35714 | 9.2308 | 9.5077 | 11.3281 | 39.6719 | 0.23966 | NA | NA | 139.09 | 1025.64 | 1683.92 | 1518.1678 | 9.8432 | 71.4511 | 1271.9039 | 89.0644 | 155 | 98 | 10.5 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.4229 | 21.0785 | 94.9215 | 0.20462 | NA | 7.68 | 91.322 | 1683.92 | 2809.95 | 2714.4246 | 3.3995 | 81.2557 | 2199.1723 | 95.8474
[11 empty] | 1997-08-30 | 15:30 | 1226.22 | 25 | 112 | 98 | 9.2667 | 0 | 13.8 | 3.4 |  | 17.2 | 17.2 | 0.80233 | 0 | 12.6412 | 13.0205 | 12.2242 | 83.5091 | 0.15592 | 7.51 | 6.74 | 72.762 | 468.12 | 476.28 | 2615.47 | 2114.0884 | 19.1698 | 84.7229 | 1295.1842 | 94.3821 | 112 | 70 | 8.8 | 8.6 | 8.6 | 17.2 | 17.2 | 0.42197 | 0.5 | 13.2308 | 13.6277 | 6.3583 | 75.8417 | 0.17969 | 6.74 | NA | 52.392 | 476.28 | 1001.88 | 900.168 | 10.1521 | 88.9997 | 688.224 | 92.3874 | 70 | 50 | 8.8 | 2.9 | 5.4 | 8.3 | 8.3 | 0.44814 | 0.3494 | 8.9231 | 9.1908 | 10.9748 | 40.2252 | 0.22848 | NA | NA | 136.71 | 1001.88 | 1636.8 | 1466.5083 | 10.4039 | 71.2963 | 1234.1942 | 88.9231 | 155 | 98 | 10.2 | 2.3 | 3.4 | 5.7 | 5.7 | 0.61394 | 0.40351 | 19.7143 | 20.3057 | 20.6358 | 95.6642 | 0.21226 | NA | 7.68 | 94.787 | 1636.8 | 2615.47 | 2679.9264 | -2.4644 | 80.0985 | 2158.3632 | 95.6084
[11 empty] | 1997-08-30 | 23:15 | 1233.98 | 25 | 112 | 98 | 9.5 | 0 | 13.7 | 3.4 |  | 17.1 | 17.1 | 0.80117 | 0 | 12.5496 | 12.9261 | 12.7504 | 82.7496 | 0.15621 | 7.49 | 6.69 | 73.499 | 463.14 | 496.44 | 2676.96 | 2200.6434 | 17.7932 | 85.1948 | 1348.5417 | 94.5497 | 112 | 70 | 9 | 8.6 | 8.5 | 17.1 | 17.1 | 0.4187 | 0.50292 | 13.2308 | 13.6277 | 6.7055 | 75.2945 | 0.18099 | 6.69 | NA | 51.153 | 496.44 | 1011.78 | 946.9657 | 6.406 | 89.696 | 721.7028 | 92.9122 | 70 | 50 | 9 | 2.9 | 5.3 | 8.2 | 8.2 | 0.4416 | 0.35366 | 8.9231 | 9.1908 | 11.135 | 39.865 | 0.23055 | NA | NA | 137.48 | 1011.78 | 1670.28 | 1490.1706 | 10.7832 | 72.3068 | 1250.9753 | 89.0102 | 155 | 98 | 10.5 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.4229 | 20.8705 | 95.1295 | 0.20417 | NA | 7.67 | 93.401 | 1670.28 | 2676.96 | 2690.6135 | -0.51004 | 81.1858 | 2180.4467 | 95.7164
[11 empty] | 1997-08-31 | 8:10 | 1242.86 | 25 | 115 | 98 | 9.5 | 0 | 13.7 | 3.4 |  | 17.1 | 17.1 | 0.80117 | 0 | 12.5496 | 12.9261 | 12.3858 | 84.6142 | 0.15277 | 7.46 | 6.69 | 73.834 | 464.8 | 484.68 | 2728.44 | 2140.1477 | 21.5615 | 84.7664 | 1312.4139 | 94.3742 | 115 | 70 | 9 | 8.6 | 8.5 | 17.1 | 17.1 | 0.4187 | 0.50292 | 13.2308 | 13.6277 | 6.524 | 76.976 | 0.17704 | 6.69 | NA | 51.448 | 484.68 | 1017.72 | 923.0088 | 9.3062 | 89.3852 | 703.8444 | 92.6904 | 70 | 50 | 9 | 2.9 | 5.2 | 8.1 | 8.1 | 0.43506 | 0.35802 | 8.9231 | 9.1908 | 11.2533 | 39.7467 | 0.23123 | NA | NA | 137.76 | 1017.72 | 1654.16 | 1508.4669 | 8.8077 | 71.5771 | 1263.0935 | 89.0934 | 155 | 98 | 10.5 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.4229 | 20.6734 | 95.3266 | 0.20375 | NA | 7.69 | 92.169 | 1654.16 | 2728.44 | 2664.8601 | 2.3303 | 80.9835 | 2159.51 | 95.7319
[11 empty] | 1997-08-31 | 16:45 | 1251.31 | 24.4444 | 117 | 98 | 9.4 | 0 | 13.8 | 3.5 |  | 17.3 | 17.3 | 0.79769 | 0 | 12.6412 | 13.236 | 12.051 | 86.049 | 0.15382 | 7.47 | 6.66 | 71.556 | 455.67 | 477.12 | 2671.24 | 2076.2009 | 22.2758 | 85.0025 | 1276.6605 | 94.3951 | 117 | 70 | 9 | 8.6 | 8.7 | 17.3 | 17.3 | 0.42524 | 0.49711 | 13.2308 | 13.8533 | 6.3641 | 78.1359 | 0.1773 | 6.66 | NA | 51.212 | 477.12 | 953.37 | 898.1325 | 5.7939 | 89.2664 | 687.6263 | 92.5523 | 70 | 50 | 9 | 2.9 | 5.4 | 8.3 | 8.3 | 0.44814 | 0.3494 | 8.9231 | 9.3429 | 10.3426 | 40.6574 | 0.2298 | NA | NA | 138.04 | 953.37 | 1644.24 | 1391.2324 | 15.3875 | 71.0681 | 1172.3012 | 88.2249 | 155 | 98 | 10.2 | 2.3 | 3.5 | 5.8 | 5.8 | 0.62744 | 0.39655 | 19.7143 | 20.6419 | 20.603 | 95.697 | 0.2157 | NA | 7.62 | 93.478 | 1644.24 | 2671.24 | 2663.3122 | 0.29678 | 80.4079 | 2153.7761 | 95.6598
[11 empty] | 1997-09-01 | 7:40 | 1266.34 | 25 | 112 | 98 | 9.4 | 0 | 13.7 | 3.5 |  | 17.2 | 17.2 | 0.79651 | 0 | 12.5496 | 12.9261 | 12.1303 | 83.4697 | 0.15486 | 7.45 | 6.69 | 71.958 | 458.16 | 482.16 | 2706.99 | 2087.8078 | 22.8735 | 85.0759 | 1284.9839 | 94.4001 | 112 | 70 | 9 | 8.6 | 8.6 | 17.2 | 17.2 | 0.42197 | 0.5 | 13.2308 | 13.6277 | 6.4589 | 75.5411 | 0.1804 | 6.69 | NA | 51.566 | 482.16 | 1001.88 | 912.754 | 8.8959 | 89.3052 | 697.457 | 92.6066 | 70 | 50 | 9 | 2.9 | 5.4 | 8.3 | 8.3 | 0.44814 | 0.3494 | 8.9231 | 9.1908 | 10.9633 | 40.0367 | 0.22956 | NA | NA | 137.62 | 1001.88 | 1656.64 | 1466.0196 | 11.5064 | 71.4576 | 1233.9498 | 88.8472 | 155 | 98 | 10.2 | 2.2 | 3.5 | 5.7 | 5.7 | 0.62069 | 0.38596 | 18.8571 | 19.4229 | 20.5535 | 95.7465 | 0.20286 | NA | 7.66 | 92.785 | 1656.64 | 2706.99 | 2639.6346 | 2.4882 | 80.7564 | 2148.1373 | 95.6807
[11 empty] | 1997-09-02 | 16:30 | 1298.6 | 23.8889 | 116 | 97 | 9.3667 | 0 | 14.3 | 3.3 |  | 17.6 | 17.6 | 0.8125 | 0 | 13.0992 | 13.9427 | 13.923 | 83.2103 | 0.16756 | 7.52 | 6.72 | 73.566 | 487.21 | 513.24 | 3156.01 | 2418.494 | 23.3686 | 85.6664 | 1465.867 | 94.9814 | 116 | 77 | 8.8 | 8.7 | 8.9 | 17.6 | 17.6 | 0.43342 | 0.49432 | 13.3846 | 14.2465 | 6.8293 | 80.8707 | 0.17616 | 6.72 | NA | 54.516 | 513.24 | 1035.54 | 961.6556 | 7.1349 | 89.3781 | 737.4478 | 92.6075 | 77 | 52 | 9.3 | 3.1 | 5.5 | 8.6 | 8.6 | 0.46122 | 0.36047 | 9.5385 | 10.1526 | 11.4909 | 43.7091 | 0.23228 | NA | NA | 139.09 | 1035.54 | 1790.56 | 1540.8118 | 13.948 | 72.8996 | 1288.1759 | 89.2026 | 154 | 97 | 10 | 2.5 | 3.3 | 5.8 | 5.8 | 0.61394 | 0.43103 | 21.4286 | 22.8084 | 23.4225 | 92.0775 | 0.24771 | NA | 7.61 | 91.784 | 1790.56 | 3156.01 | 3077.5115 | 2.4873 | 82.1167 | 2434.0358 | 96.2291
[11 empty] | 1997-09-02 | 23:00 | 1305.5 | 25.5556 | 115 | 98 | 9.2667 | 0 | 14 | 3.3 |  | 17.3 | 17.3 | 0.80925 | 0 | 12.8244 | 12.994 | 14.0608 | 83.1726 | 0.15623 | 7.54 | 6.68 | 72.829 | 491.36 | 523.32 | 3094.52 | 2434.4939 | 21.3289 | 86.0833 | 1478.907 | 95.0755 | 115 | 78 | 8.6 | 8.5 | 8.8 | 17.3 | 17.3 | 0.42688 | 0.49133 | 13.0769 | 13.2499 | 6.9548 | 80.9452 | 0.16369 | 6.68 | NA | 54.339 | 523.32 | 1028.61 | 976.313 | 5.0842 | 89.6165 | 749.8165 | 92.753 | 78 | 50 | 9.2 | 3 | 5.5 | 8.5 | 8.5 | 0.45795 | 0.35294 | 9.2308 | 9.3528 | 11.3158 | 43.4842 | 0.21509 | NA | NA | 139.51 | 1028.61 | 1769.48 | 1513.5736 | 14.4622 | 73.3414 | 1271.0918 | 89.0244 | 155 | 98 | 10 | 2.5 | 3.3 | 5.8 | 5.8 | 0.61394 | 0.43103 | 21.4286 | 21.7119 | 23.1382 | 93.3618 | 0.23256 | NA | 7.65 | 91.322 | 1769.48 | 3094.52 | 3040.8118 | 1.7356 | 82.5495 | 2405.1459 | 96.2031
[11 empty] | 1997-09-03 | 7:00 | 1313.51 | 25.5556 | 118 | 98 | 9.4667 | 0 | 13.8 | 3.5 |  | 17.3 | 17.3 | 0.79769 | 0 | 12.6412 | 12.8084 | 12.5723 | 85.961 | 0.149 | 7.51 | 6.69 | 72.494 | 488.87 | 495.6 | 2708.42 | 2163.8465 | 20.1067 | 85.3725 | 1329.7233 | 94.5482 | 118 | 72 | 9.2 | 8.6 | 8.7 | 17.3 | 17.3 | 0.42524 | 0.49711 | 13.2308 | 13.4057 | 6.6473 | 79.1527 | 0.16937 | 6.69 | NA | 50.74 | 495.6 | 1053.36 | 935.3467 | 11.2035 | 89.7619 | 715.4733 | 92.9082 | 72 | 50 | 9.2 | 3 | 5.3 | 8.3 | 8.3 | 0.44487 | 0.36145 | 9.2308 | 9.3528 | 11.7689 | 40.0311 | 0.23364 | NA | NA | 136.08 | 1053.36 | 1674 | 1572.5751 | 6.0588 | 72.5424 | 1312.9675 | 89.6357 | 157 | 98 | 10 | 2.2 | 3.5 | 5.7 | 5.7 | 0.62069 | 0.38596 | 18.8571 | 19.1065 | 20.6501 | 96.8499 | 0.19728 | NA | 7.62 | 102.795 | 1674 | 2708.42 | 2661.6146 | 1.7281 | 79.2585 | 2167.8073 | 95.2581
[11 empty] | 1997-09-03 | 16:15 | 1322.92 | 25.5556 | 115 | 98 | 9.0667 | 0 | 13.7 | 3.5 |  | 17.2 | 17.2 | 0.79651 | 0 | 12.5496 | 12.7156 | 11.6266 | 85.8067 | 0.14819 | 7.51 | 6.52 | 73.03 | 463.14 | 466.2 | 2605.46 | 2005.1797 | 23.0393 | 84.335 | 1235.6899 | 94.0899 | 115 | 70 | 8.6 | 8.6 | 8.6 | 17.2 | 17.2 | 0.42197 | 0.5 | 13.2308 | 13.4057 | 6.2673 | 77.6327 | 0.17268 | 6.52 | NA | 48.38 | 466.2 | 995.94 | 884.02 | 11.2376 | 89.6225 | 675.11 | 92.8338 | 70 | 48 | 8.6 | 2.9 | 5.3 | 8.2 | 8.2 | 0.4416 | 0.35366 | 8.9231 | 9.0411 | 11.099 | 39.301 | 0.23005 | NA | NA | 124.46 | 995.94 | 1675.24 | 1472.7875 | 12.085 | 73.3033 | 1234.3638 | 89.9171 | 157 | 98 | 10 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.1065 | 20.9218 | 96.5782 | 0.19783 | NA | 7.57 | 94.479 | 1675.24 | 2605.46 | 2698.0854 | -3.555 | 79.7342 | 2186.6627 | 95.6793
[11 empty] | 1997-09-04 | 9:15 | 1339.75 | 25.5556 | 112 | 98 | 8.9333 | 0 | 12.6 | 3.4 |  | 16 | 16 | 0.7875 | 0 | 11.542 | 11.6946 | 11.3685 | 84.6982 | 0.13807 | 7.64 | 6.6 | 74.437 | 458.16 | 472.92 | 2486.77 | 1949.6511 | 21.5991 | 84.2601 | 1211.2856 | 93.8547 | 112 | 65 | 8.4 | 7.8 | 8.2 | 16 | 16 | 0.3958 | 0.4875 | 12 | 12.1587 | 6.2297 | 73.8703 | 0.1646 | 6.6 | NA | 50.74 | 472.92 | 973.17 | 874.5059 | 10.1384 | 89.2709 | 673.7129 | 92.4686 | 65 | 45 | 8.4 | 2.6 | 5.21 | 7.81 | 7.81 | 0.4259 | 0.33291 | 8 | 8.1058 | 10.5681 | 36.0319 | 0.22496 | NA | NA | 127.4 | 973.17 | 1569.84 | 1395.2433 | 11.1219 | 73.061 | 1184.2067 | 89.2417 | 152 | 98 | 10 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.1065 | 19.5819 | 95.4181 | 0.20024 | NA | 7.71 | 90.321 | 1569.84 | 2486.77 | 2527.1758 | -1.6248 | 80.9014 | 2048.5079 | 95.5909
[11 empty] | 1997-09-04 | 16:00 | 1346.6 | 25.5556 | 110 | 92 | 8.9667 | 0 | 12.2 | 3.4 |  | 15.6 | 15.6 | 0.78205 | 0 | 11.1756 | 11.3234 | 11.5734 | 80.4599 | 0.14073 | 7.6 | 6.58 | 73.834 | 464.8 | 488.04 | 2511.08 | 1974.3086 | 21.3761 | 84.8713 | 1231.1743 | 94.003 | 110 | 60 | 8.5 | 8 | 7.6 | 15.6 | 15.6 | 0.37945 | 0.51282 | 12.3077 | 12.4704 | 6.6908 | 69.8092 | 0.17864 | 6.58 | NA | 49.678 | 488.04 | 984.06 | 949.4737 | 3.5147 | 89.8209 | 718.7568 | 93.0883 | 60 | 40 | 8.5 | 2 | 5.1 | 7.1 | 7.1 | 0.39907 | 0.28169 | 6.1538 | 6.2352 | 10.2673 | 31.2327 | 0.19964 | NA | NA | 125.65 | 984.06 | 1590.92 | 1320.6914 | 16.9857 | 74.2542 | 1152.3757 | 89.0964 | 148 | 92 | 9.9 | 2.2 | 3.4 | 5.6 | 5.6 | 0.6072 | 0.39286 | 18.8571 | 19.1065 | 19.7681 | 90.3319 | 0.21151 | NA | 7.54 | 97.328 | 1590.92 | 2511.08 | 2557.3619 | -1.8431 | 80.0574 | 2074.1409 | 95.3076
[11 empty] | 1997-09-04 | 22:45 | 1352.91 | 25.5556 | 100 | 95 | 11 | 0 | 16.5 | 3.3 |  | 19.8 | 19.8 | 0.83333 | 0 | 15.1145 | 15.3144 | 13.7988 | 72.7012 | 0.21065 | 7.54 | 6.55 | 75.308 | 454.01 | 469.56 | 2496.78 | 2440.82 | 2.2413 | 83.962 | 1455.19 | 94.8249 | 100 | 55 | 11.5 | 13.2 | 6.6 | 19.8 | 19.8 | 0.43178 | 0.66667 | 20.3077 | 20.5762 | 8.3835 | 57.6165 | 0.35712 | 6.55 | NA | 50.386 | 469.56 | 969.21 | 1307.908 | -34.9458 | 89.2695 | 888.734 | 94.3306 | 55 | 30 | 11.5 | 1.3 | 5 | 6.3 | 6.3 | 0.36963 | 0.20635 | 4 | 4.0529 | 9.5235 | 21.4765 | 0.18871 | NA | NA | 126.42 | 969.21 | 1577.28 | 1188.3354 | 24.6592 | 73.0769 | 1078.7727 | 88.2811 | 140 | 95 | 10 | 2 | 3.3 | 5.3 | 5.3 | 0.58021 | 0.37736 | 17.1429 | 17.3696 | 19.3113 | 88.1887 | 0.19696 | NA | 7.61 | 95.249 | 1577.28 | 2496.78 | 2475.4806 | 0.85307 | 79.7153 | 2026.3803 | 95.2995
[11 empty] | 1997-09-05 | 9:40 | 1359.19 | 25.5556 | 98 | 88 | 11.3667 | 0 | 17.6 | 3.3 | X | 20.9 | 20.9 | 0.84211 | 0 | 16.1221 | 16.3353 | 6.9058 | 74.7275 | 0.2186 | 7.58 | 6.63 | 285.42 | 461.48 | 473.76 | 1703.13 | 1478.24 | 13.2045 | 39.7543 | 976 | 70.7561 | 98 | 45 | 11.8 | 14.2 | 6.7 | 20.9 | 20.9 | 0.45141 | 0.67943 | 21.8462 | 22.135 | 6.5012 | 53.1988 | 0.41608 | 6.63 | NA | 158.12 | 473.76 | 797.94 | 1142.7284 | -43.2098 | 66.6245 | 808.2442 | 80.4366 | 45 | 30 | 11.8 | 1.3 | 5 | 6.3 | 6.3 | 0.36963 | 0.20635 | 4 | 4.0529 | 6.9364 | 18.7636 | 0.216 | NA | NA | 184.1 | 797.94 | 1093.68 | 957.5384 | 12.448 | 61.1407 | 877.7392 | 79.0257 | 140 | 88 | 10.5 | 2.1 | 3.3 | 5.4 | 5.4 | 0.58696 | 0.38889 | 18 | 18.238 | 13.5154 | 89.9846 | 0.20268 | NA | 7.71 | 68.376 | 1093.68 | 1703.13 | 1746.1462 | -2.5257 | 85.5674 | 1419.9131 | 95.1845
[11 empty] | 1997-09-05 | 1:30 | 1364 | 25.5556 | 102 | 88 | 11.9333 | 0 | 20.1 | 3.3 | X | 23.4 | 23.4 | 0.85897 | 0 | 18.4122 | 18.6557 | 7.4562 | 75.6105 | 0.24673 | 7.46 | 6.69 | 286.09 | 455.67 | 470.4 | 1886.17 | 1593.0155 | 15.5423 | 39.1815 | 1031.7077 | 72.2702 | 102 | 50 | 12.5 | 16.3 | 7.1 | 23.4 | 23.4 | 0.49884 | 0.69658 | 25.0769 | 25.4085 | 7.0242 | 56.4758 | 0.4499 | 6.69 | NA | 143.37 | 470.4 | 820.71 | 1221.1872 | -48.7964 | 69.5217 | 845.7936 | 83.0491 | 50 | 31 | 12.5 | 1.7 | 5.1 | 6.8 | 6.8 | 0.38926 | 0.25 | 5.2308 | 5.2999 | 7.1331 | 20.8669 | 0.25399 | NA | NA | 209.3 | 820.71 | 1210.24 | 1024.5133 | 15.3463 | 55.506 | 922.6117 | 77.3144 | 140 | 88 | 10.8 | 2.1 | 3.3 | 5.4 | 5.4 | 0.58696 | 0.38889 | 18 | 18.238 | 15.0163 | 88.1837 | 0.20682 | NA | 7.63 | 71.071 | 1210.24 | 1886.17 | 1935.1657 | -2.5976 | 84.8914 | 1572.7029 | 95.481
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A1: Alison Gusses: Please refer to comment in column AJ prior to Base Analyses
Note on W6: S Allgeier (11/17/99): Reviewer entered formula to calculate average system permeate pressure.
Note on AJ6: Alison Gusses: MTCw may be incorrect due to third stage booster pump
Note on DU17: CDM: verified with lab data sheets
Note on DU22: CDM: verified w/ lab data sheets
Note on DU23: CDM: verified w/ lab data sheets
Note on DV17: CDM: verified w/ lab data sheets
Note on DV22: CDM: verified w/ lab data sheets
Note on DV23: CDM: verified w/ lab data sheets
Note on DW17: CDM: verified w/ lab data sheets
Note on DW22: CDM: verified w/ lab data sheets
Note on DW23: CDM: value changed-originally entered incorrectly as 0.443
Note on EO17: CDM: verified w/ lab data sheets
Note on EO22: CDM: verified w/ lab data sheets
Note on EO23: CDM: verified w/ lab data sheets
Note on EP17: CDM: verified w/ lab data sheets
Note on EP22: CDM: verified w/ lab data sheets
Note on EP23: CDM: verified w/ lab data sheets
Note on EQ17: CDM: verified w/ lab data sheets
Note on EQ22: CDM: verified w/ lab data sheets
Note on EQ23: CDM: verified w/ lab data sheets
Note on FI17: CDM: verified w/ lab data sheets
Note on FI22: CDM: verified w/ lab data sheets
Note on FI23: CDM: verified w/ lab data sheets
Note on FJ17: CDM: verified w/ lab data sheets
Note on FJ22: CDM: verified w/ lab data sheets
Note on FJ23: CDM: verified w/ lab data sheets
Note on FJ32: S Allgeier (11/17/99): Reviewer changed value of 145 to NR since residual was BMRL.
Note on FK17: CDM: verified w/ lab data sheets
Note on FK22: CDM: verified w/ lab data sheets
Note on FK23: CDM: verified w/ lab data sheets

## Sheet2. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Week 12 | [9 empty] | Field 2-7: System And Stage Water Quality For Week 12 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | Stage 1 and 2 -- General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment (from Performance sampling & MDWASD) |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Miami-Dade Water and Sewer Dept. | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 26 | Alkalinity (mg/L as CaCO3) | 176 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.81 | [6 empty] | System recovery during sample collection (decimal) | 0.78 | HI-6 | [7 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 |  | HI-6 |  |  |  |  | System recovery during sample collection (decimal) | 0.84 | HI-7 | [7 empty] | Stage 1 recovery during sample collection (decimal) | 0.55 |  | HI-7 |  |  |  |  | System recovery during sample collection (decimal) | 0.86 | HI-8 | [7 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 |  | HI-8 |  |  |  |  | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL 4130871 | Membrane trade name | TFC-S | Temperature normalized MTCW (gfd/psi) | 0.30179 | Calcium Hardness (mg/L as CaCO3) | NA | Antiscalant Addition | King Lee Pre-treat 100 (2 mg/L dose) | Pilot Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 18.3 | HI-4 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.2 |  | HI-4 |  |  |  |  | System feed flow rate during sample collection (gpm) | 18.4 | HI-5 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 18.4 |  | HI-5 |  |  |  |  | System feed flow rate during sample collection (gpm) | 17.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.75 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.7 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.8 | [6 empty] | System feed flow rate during sample collection (gpm) | 20.95 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.95 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | 1029 | Membrane element model number | TFC 4921S |  |  | LSI | 0.14 | Sulfuric Acid Addition | pH ~ 6.75 (85 mg/L dose) | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 18.3 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.7 | [6 empty] | System influent flow rate during sample collection (gpm) | 20.95 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20.95 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | NA | Cartridge Filtration | 5 um exclusion size | Pilot Scale | 1997-10-03 | 3:45 | 1396.98 | 25.5556 | 90 | 90 | 10.2 | 0 | 15.1 | 3.45 |  | 18.55 | 18.55 | 0.81402 | 0 | 13.8321 | 14.015 | 11.5905 | 68.2095 | 0.20547 | 7.49 | 6.59 | 101.84 | 424.13 | 465.36 | 2452.45 | 2056.4186 | 16.1484 | 78.1159 | 1260.8893 | 91.9232 | 90 | 65 | 9 | 9.4 | 9.15 | 18.55 | 18.55 | 0.45305 | 0.50674 | 14.4615 | 14.6528 | 5.9276 | 62.5724 | 0.23417 | 6.59 | NA | 73.75 | 465.36 | 950.4 | 867.6697 | 8.7048 | 84.1521 | 666.5149 | 88.935 | 65 | 40 | 8.8 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.7293 | 9.6841 | 34.0159 | 0.25662 | NA | NA | 165.2 | 950.4 | 1478.08 | 1316.8267 | 10.9096 | 64.5006 | 1133.6133 | 85.4271 | 150 | 90 | 12.8 | 2.9 | 3.45 | 6.35 | 6.35 | 0.66117 | 0.45669 | 24.8571 | 25.1859 | 19.5527 | 87.6473 | 0.28735 | NA | 7.53 | 101.409 | 1478.08 | 2452.45 | 2635.2817 | -7.4551 | 78.2085 | 2056.6809 | 95.0693 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.67 |  |  |  | 1997-10-03 | 11:30 | 1404.78 | 24.4444 | 90 | 86 | 10.6667 | 0 | 15.2 | 3.5 |  | 18.7 | 18.7 | 0.81283 | 0 | 13.9237 | 14.5788 | 11.1672 | 66.1661 | 0.22034 | 7.38 | 6.59 | 109.88 | 441.56 | 462 | 2579.72 | 1991.2069 | 22.8131 | 76.2165 | 1226.6034 | 91.0419 | 90 | 70 | 9.8 | 9.5 | 9.2 | 18.7 | 18.7 | 0.45632 | 0.50802 | 14.6154 | 15.3031 | 5.7708 | 64.4292 | 0.23752 | 6.37 | NA | 81.42 | 462 | 851.4 | 854.9902 | -0.42168 | 82.3766 | 658.4951 | 87.6354 | 70 | 48 | 9.2 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 8.3508 | 41.4492 | 0.21763 | NA | NA | 172.2 | 851.4 | 1346.64 | 1163.1639 | 13.6247 | 62.7273 | 1007.282 | 82.9045 | 155 | 86 | 13 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 17.6449 | 89.8551 | 0.28965 | NA | 7.5 | 99.022 | 1346.64 | 2579.72 | 2380.3806 | 7.7272 | 78.5667 | 1863.5103 | 94.6863 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1997-10-04 | 7:00 | 1411.98 | 25.5556 | 90 | 88 | 10.6667 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 13.7365 | 11.9513 | 66.382 | 0.20693 | 7.55 | 6.37 | 94.202 | 465.63 | 477.96 | 2445.3 | 2100.7081 | 14.092 | 80.2908 | 1289.3341 | 92.6937 | 90 | 70 | 9.8 | 9 | 9.3 | 18.3 | 18.3 | 0.45141 | 0.4918 | 13.8462 | 14.0293 | 6.0767 | 64.1233 | 0.21879 | 6.38 | NA | 68.44 | 477.96 | 863.28 | 874.2697 | -1.273 | 85.6808 | 676.1148 | 89.8775 | 70 | 48 | 9.2 | 3 | 6 | 9 | 9 | 0.49066 | 0.33333 | 9.2308 | 9.3528 | 8.7785 | 41.0215 | 0.228 | NA | NA | 161 | 863.28 | 1476.84 | 1214.42 | 17.769 | 66.3152 | 1038.85 | 84.5021 | 155 | 88 | 13 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 24.3174 | 19.5395 | 88.9605 | 0.27335 | NA | 7.6 | 81.158 | 1476.84 | 2445.3 | 2593.3856 | -6.0559 | 83.0199 | 2035.1128 | 96.0121 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | BDL |  |  |  | 1997-10-04 | 16:00 | 1420.63 | 25.5556 | 90 | 88 | 10.6 | 0 | 15.1 | 3.5 |  | 18.6 | 18.6 | 0.81183 | 0 | 13.8321 | 14.015 | 11.509 | 66.891 | 0.20952 | 7.42 | 6.38 | 105.86 | 454.84 | 470.4 | 2453.88 | 2043.1297 | 16.7388 | 77.4957 | 1256.7649 | 91.5768 | 90 | 68 | 9.8 | 9.4 | 9.2 | 18.6 | 18.6 | 0.45468 | 0.50538 | 14.4615 | 14.6528 | 6.0196 | 63.1804 | 0.23192 | 6.21 | NA | 71.98 | 470.4 | 954.36 | 877.4813 | 8.0555 | 84.6981 | 673.9407 | 89.3195 | 68 | 48 | 9 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.7293 | 9.6984 | 39.3016 | 0.22211 | NA | NA | 168 | 954.36 | 1468.16 | 1321.328 | 10.0011 | 64.2857 | 1137.844 | 85.2352 | 155 | 88 | 13 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 25.1859 | 19.6064 | 88.8936 | 0.28333 | NA | 7.58 | 81.851 | 1468.16 | 2453.88 | 2616.816 | -6.6399 | 82.5997 | 2042.488 | 95.9926 | Sampling date | MM/DD/YY | 1997-10-08 | 1997-10-08 | 1997-10-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-10-08 | 1997-10-08 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-10-22 | 1997-10-22 | 1997-10-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-10-22 | 1997-10-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-11-05 | 1997-11-05 | 1997-11-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-11-05 | 1997-11-05 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-11-19 | 1997-11-19 | 1997-11-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1997-11-19 | 1997-11-19 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-01-14 | 1998-01-14 | 1998-01-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-01-14 | 1998-01-14 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1997-10-04 | 168:00 | 1428.17 | 24.4444 | 90 | 88 | 10.6 | 0 | 15.1 | 3.55 |  | 18.65 | 18.65 | 0.80965 | 0 | 13.8321 | 14.4829 | 11.6413 | 66.7587 | 0.21694 | 7.46 | 6.21 | 98.088 | 476.42 | 470.4 | 2522.52 | 2054.037 | 18.572 | 79.148 | 1262.2185 | 92.2289 | 90 | 70 | 9.8 | 9.3 | 9.35 | 18.65 | 18.65 | 0.45795 | 0.49866 | 14.3077 | 14.9809 | 5.8773 | 64.3227 | 0.2329 | 6.35 | NA | 77.88 | 470.4 | 938.52 | 860.821 | 8.2789 | 83.4439 | 665.6105 | 88.2995 | 70 | 48 | 9 | 2.9 | 6 | 8.9 | 8.9 | 0.48739 | 0.32584 | 8.9231 | 9.3429 | 9.6021 | 40.3979 | 0.23127 | NA | NA | 165.2 | 938.52 | 1378.88 | 1312.2913 | 4.8292 | 64.881 | 1125.4057 | 85.3208 | 155 | 88 | 13 | 2.9 | 3.55 | 6.45 | 6.45 | 0.67466 | 0.44961 | 24.8571 | 26.0268 | 18.1606 | 90.3394 | 0.2881 | NA | 7.54 | 89.474 | 1378.88 | 2522.52 | 2432.1976 | 3.5806 | 80.9792 | 1905.5388 | 95.3045 | Sampling time | hh:mm | 7:30 | 7:30 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:30 | 7:30 | --- | --- | --- | --- | Sampling time | hh:mm | 7:00 | 7:00 | 7:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:00 | 7:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 7:30 | 7:30 | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 7:30 | 7:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881 (May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.08 |  |  |  | 1997-10-05 | 7:40 | 1436.41 | 24.4444 | 90 | 88 | 10.5333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.7253 | 66.7413 | 0.21269 | 7.54 | 6.35 | 94.738 | 468.12 | 471.24 | 2502.5 | 2063.3056 | 17.5502 | 79.896 | 1267.2728 | 92.5243 | 90 | 70 | 9.8 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 5.9931 | 64.2069 | 0.23081 | 6.39 | NA | 73.16 | 471.24 | 945.45 | 873.6945 | 7.5896 | 84.475 | 672.4673 | 89.1207 | 70 | 48 | 9 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.6317 | 40.3683 | 0.22346 | NA | NA | 164.5 | 945.45 | 1382.6 | 1309.8933 | 5.2587 | 65.0921 | 1127.6717 | 85.4124 | 158 | 88 | 12.8 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 18.1652 | 92.0348 | 0.27304 | NA | 7.55 | 85.085 | 1382.6 | 2502.5 | 2420.612 | 3.2722 | 81.9444 | 1901.606 | 95.5256 | Operation time | hh.hh | 1508 | 1508 | 1508 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1508 | 1508 | --- | --- | --- | --- | Operation time | hh.hh | 1770.8 | 1770.8 | 1770.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1770.8 | 1770.8 | --- | --- | --- | --- | Operation time | hh.hh | 2094 | 2094 | 2094 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2094 | 2094 | --- | --- | --- | --- | Operation time | hh.hh | 2340 | 2340 | 2340 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2340 | 2340 | --- | --- | --- | --- | Operation time | hh.hh | 2405 | 2405 | 2405 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2405 | 2405 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 130
E-Mail Address (optional) |  | Stage 1 and 2 -- Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 9.16 |  |  |  | 1997-10-05 | 5:20 | 1446.43 | 24.4444 | 90 | 88 | 10.5 | 0 | 15.1 | 3.5 |  | 18.6 | 18.6 | 0.81183 | 0 | 13.8321 | 14.4829 | 11.9674 | 66.5326 | 0.21768 | 7.48 | 6.39 | 95.542 | 473.1 | 474.6 | 2516.8 | 2109.9645 | 16.1648 | 79.8689 | 1292.2823 | 92.6067 | 90 | 70 | 9.8 | 9.4 | 9.2 | 18.6 | 18.6 | 0.45468 | 0.50538 | 14.4615 | 15.142 | 6.0296 | 64.1704 | 0.23597 | 6.2 | NA | 75.52 | 474.6 | 942.48 | 882.3557 | 6.3794 | 84.0877 | 678.4778 | 88.8692 | 70 | 48 | 9.2 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.5692 | 40.2308 | 0.22423 | NA | NA | 166.6 | 942.48 | 1393.76 | 1304.5573 | 6.4001 | 64.8968 | 1123.5187 | 85.1716 | 155 | 88 | 12.5 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 18.4877 | 90.5123 | 0.28755 | NA | 7.6 | 86.548 | 1393.76 | 2516.8 | 2476.8785 | 1.5862 | 81.764 | 1935.3193 | 95.528 | pH | --- | 5.91 | 6.49 | 6.98 | --- | --- | --- | --- | --- | pH | --- | 5.86 | 6.49 | --- | --- | --- | --- | pH | --- | 7.27 | 6.47 | 6.94 | --- | --- | --- | --- | --- | pH | --- | 5.96 | 6.47 | --- | --- | --- | --- | pH | --- | 6.07 | 6.73 | 7.1 | --- | --- | --- | --- | --- | pH | --- | 6.1 | 6.73 | --- | --- | --- | --- | pH | --- | 6.51 | 7.14 | 7.61 | --- | --- | --- | --- | --- | pH | --- | 6.73 | 7.14 | --- | --- | --- | --- | pH | --- | 5.75 | 6.47 | 7.06 | --- | --- | --- | --- | --- | pH | --- | 5.92 | 6.47 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | ~20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.8125 | Calcium (mg/L) | 56 |  |  |  | 1997-10-05 | 11:45 | 1452.6 | 24.4444 | 90 | 88 | 10.6 | 0 | 15.1 | 3.55 |  | 18.65 | 18.65 | 0.80965 | 0 | 13.8321 | 14.4829 | 11.8603 | 66.5397 | 0.21766 | 7.42 | 6.2 | 91.924 | 446.54 | 471.24 | 2459.6 | 2084.6686 | 15.2436 | 80.4932 | 1277.9543 | 92.8069 | 90 | 70 | 9.8 | 9.4 | 9.25 | 18.65 | 18.65 | 0.45632 | 0.50402 | 14.4615 | 15.142 | 6.0569 | 64.1431 | 0.23607 | 6.31 | NA | 69.62 | 471.24 | 944.46 | 879.3728 | 6.8915 | 85.2262 | 675.3064 | 89.6906 | 70 | 48 | 9 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.6155 | 40.3845 | 0.22337 | NA | NA | 162.4 | 944.46 | 1445.84 | 1303.4384 | 9.8491 | 65.5377 | 1123.9492 | 85.5509 | 157 | 88 | 13 | 2.9 | 3.55 | 6.45 | 6.45 | 0.67466 | 0.44961 | 24.8571 | 26.0268 | 19.1645 | 90.3355 | 0.28811 | NA | 7.54 | 85.162 | 1445.84 | 2459.6 | 2557.3798 | -3.9754 | 81.9281 | 2001.6099 | 95.7453 | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | --- | --- | --- | --- | Temperature | oC | NA | 25.5 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 25.5 | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | --- | --- | --- | --- | Temperature | oC | NA | 23.8 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 23.8 | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 67%
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.875 | Barium (mg/L) | < 0.05 |  |  |  | 1997-10-06 | 9:30 | 1462.31 | 24.4444 | 90 | 88 | 10.4333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.6109 | 66.9557 | 0.21201 | 7.59 | 6.31 | 90.852 | 449.86 | 463.68 | 2483.91 | 2040.2098 | 17.863 | 80.4063 | 1251.9449 | 92.7431 | 90 | 70 | 9.5 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 5.9787 | 64.5213 | 0.22969 | 6.28 | NA | 66.552 | 463.68 | 951.39 | 865.172 | 9.0623 | 85.647 | 664.426 | 89.9835 | 70 | 48 | 9 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.8431 | 40.1569 | 0.22464 | NA | NA | 153.3 | 951.39 | 1488 | 1323.832 | 11.0328 | 66.9384 | 1137.611 | 86.5244 | 155 | 88 | 12.8 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.7562 | 88.9438 | 0.28253 | NA | 7.55 | 76.846 | 1488 | 2483.91 | 2616.9232 | -5.355 | 83.4269 | 2052.4616 | 96.2559 | Alkalinity | mg/L as CaCO3 | 35.94 | 146.12 | 604.91 | 615.8347 | -1.806 | 75.4038 | 380.9774 | 90.5664 | Alkalinity | mg/L as CaCO3 | 30.34 | 146.12 | 263.1723 | 79.2362 | 204.6462 | 85.1744 | Alkalinity | mg/L as CaCO3 | NA | 132.57 | 491.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 29.26 | 132.57 | #DIV/0! | 77.9286 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 | 37 | 162 | 593 | 605.1818 | -2.0543 | 77.1605 | 383.5909 | 90.3543 | Alkalinity | mg/L as CaCO3 | 31 | 162 | 294.5145 | 80.8642 | 228.2572 | 86.4188 | Alkalinity | mg/L as CaCO3 | 45 | 224 | 996 | 1163.75 | -16.8424 | 79.9107 | 693.875 | 93.5147 | Alkalinity | mg/L as CaCO3 | 46 | 224 | 444.8101 | 79.4643 | 334.4051 | 86.2442 | Alkalinity | mg/L as CaCO3 | 21 | 116 | 577 | 699.5714 | -21.2429 | 81.8966 | 407.7857 | 94.8502 | Alkalinity | mg/L as CaCO3 | 21 | 116 | 220.025 | 81.8966 | 168.0125 | 87.5009 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | Strontium (mg/L) | 0.49 |  |  |  | 1997-10-06 | 16:00 | 1468.82 | 24.4444 | 90 | 88 | 10.5333 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 14.2911 | 11.8157 | 66.6509 | 0.21442 | 7.54 | 6.28 | 92.728 | 454.84 | 470.4 | 2479.62 | 2078.2037 | 16.1886 | 80.2874 | 1274.3018 | 92.7232 | 90 | 70 | 9.8 | 9.2 | 9.2 | 18.4 | 18.4 | 0.45141 | 0.5 | 14.1538 | 14.8198 | 5.994 | 64.206 | 0.23082 | 6.27 | NA | 70.8 | 470.4 | 946.44 | 870 | 8.0766 | 84.949 | 670.2 | 89.436 | 70 | 48 | 9 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.6353 | 40.3647 | 0.22348 | NA | NA | 165.2 | 946.44 | 1465.68 | 1311.0187 | 10.5522 | 64.881 | 1128.7293 | 85.3641 | 155 | 88 | 12.8 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 19.5179 | 89.1821 | 0.29184 | NA | 7.58 | 85.624 | 1465.68 | 2479.62 | 2609.155 | -5.224 | 81.7976 | 2037.4175 | 95.7974 | Total dissolved solids | mg/L | 98 | 398 | 1334 | 1676.9474 | -25.7082 | 75.3769 | 1037.4737 | 90.554 | Total dissolved solids | mg/L | 86 | 398 | 713.4286 | 78.392 | 555.7143 | 84.5244 | Total dissolved solids | mg/L | 371 | 385 | 1259 | 444.6842 | 64.6796 | 3.6364 | 414.8421 | 10.5684 | Total dissolved solids | mg/L | 88 | 385 | #DIV/0! | 77.1429 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L | 96 | 388 | 1224 | 1423.2727 | -16.2805 | 75.2577 | 905.6364 | 89.3997 | Total dissolved solids | mg/L | 82 | 388 | 697.5376 | 78.866 | 542.7688 | 84.8923 | Total dissolved solids | mg/L | 67 | 380 | 1266 | 2023.25 | -59.8144 | 82.3684 | 1201.625 | 94.4242 | Total dissolved solids | mg/L | 71 | 380 | 763.3165 | 81.3158 | 571.6582 | 87.58 | Total dissolved solids | mg/L | 63.7 | 322 | 1353 | 1908.7 | -41.0717 | 80.2174 | 1115.35 | 94.2888 | Total dissolved solids | mg/L | 61.8 | 322 | 606.919 | 80.8075 | 464.4595 | 86.6942 | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | Reactive silica (mg/L as SiO2) | 8.41 |  |  |  | 1997-10-06 | 0:00 | 1476.92 | 24.4444 | 90 | 88 | 10.5333 | 0 | 14.6 | 3.2 |  | 17.8 | 17.8 | 0.82022 | 0 | 13.374 | 14.0033 | 12.2402 | 66.2265 | 0.21145 | 7.46 | 6.27 | 92.326 | 449.86 | 465.36 | 2516.8 | 2167.3276 | 13.8856 | 80.1603 | 1316.3438 | 92.9862 | 90 | 70 | 9.8 | 9.2 | 8.6 | 17.8 | 17.8 | 0.43178 | 0.51685 | 14.1538 | 14.8198 | 6.0723 | 64.1277 | 0.2311 | 6.08 | NA | 69.738 | 465.36 | 942.48 | 888.5835 | 5.7186 | 85.0142 | 676.9718 | 89.6985 | 70 | 48 | 9 | 2.8 | 6.3 | 9.1 | 9.1 | 0.50375 | 0.30769 | 8.6154 | 9.0208 | 9.6712 | 40.3288 | 0.22368 | NA | NA | 151.2 | 942.48 | 1520.24 | 1294.16 | 14.8713 | 67.509 | 1118.32 | 86.4797 | 156 | 88 | 12.8 | 2.6 | 3.2 | 5.8 | 5.8 | 0.6072 | 0.44828 | 22.2857 | 23.3343 | 20.2912 | 88.9088 | 0.26245 | NA | 7.1 | 77.308 | 1520.24 | 2516.8 | 2692.6222 | -6.9859 | 83.3875 | 2106.4311 | 96.3299 | Total hardness | mg/L as CaCO3 | 35 | 235 | 1130 | 1087.6316 | 3.7494 | 85.1064 | 661.3158 | 94.7075 | Total hardness | mg/L as CaCO3 | 29.4 | 235 | 442.8593 | 87.4894 | 338.9297 | 91.3256 | Total hardness | mg/L as CaCO3 | 221.6 | 223.6 | 933 | 232.1263 | 75.1204 | 0.89445 | 227.8632 | 2.7486 | Total hardness | mg/L as CaCO3 | 28 | 223.6 | #DIV/0! | 87.4776 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 | 35 | 234 | 923 | 939.5455 | -1.7926 | 85.0427 | 586.7727 | 94.0352 | Total hardness | mg/L as CaCO3 | 28 | 234 | 442.3815 | 88.0342 | 338.1908 | 91.7206 | Total hardness | mg/L as CaCO3 | 36 | 229 | 1062 | 1242.25 | -16.9727 | 84.2795 | 735.625 | 95.1062 | Total hardness | mg/L as CaCO3 | 39 | 229 | 464.6962 | 82.9694 | 346.8481 | 88.7559 | Total hardness | mg/L as CaCO3 | 19 | 188 | 1100 | 1226.1429 | -11.4675 | 89.8936 | 707.0714 | 97.3129 | Total hardness | mg/L as CaCO3 | 19 | 188 | 373.055 | 89.8936 | 280.5275 | 93.227 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | 0.2714¢/therm
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.293 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | Turbidity (ntu) | 0.5 |  |  |  | 1997-10-07 | 10:40 | 1493.67 | 24.4444 | 90 | 88 | 10.5333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.8558 | 66.6108 | 0.21311 | 7.48 | 6.08 | 91.388 | 444.88 | 472.08 | 2488.2 | 2081.8633 | 16.3305 | 80.6414 | 1276.9717 | 92.8434 | 90 | 70 | 9.8 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 6.059 | 64.141 | 0.23105 | 6.8 | NA | 69.62 | 472.08 | 948.42 | 878.9626 | 7.3235 | 85.2525 | 675.5213 | 89.6939 | 70 | 48 | 9 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.7633 | 40.2367 | 0.22419 | NA | NA | 156.8 | 948.42 | 1483.04 | 1317.8427 | 11.1391 | 66.7853 | 1133.1313 | 86.1622 | 158 | 88 | 12.8 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.5487 | 90.6513 | 0.27721 | NA | 7.32 | 86.702 | 1483.04 | 2488.2 | 2600.1104 | -4.4976 | 81.634 | 2041.5752 | 95.7532 | Calcium hardness | mg/L as CaCO3 | 30.2 | 204 | 961 | 944.9368 | 1.6715 | 85.1961 | 574.4684 | 94.743 | Calcium hardness | mg/L as CaCO3 | 25 | 204 | 384.967 | 87.7451 | 294.4835 | 91.5106 | Calcium hardness | mg/L as CaCO3 | 170 | 198.2 | 818 | 318.4211 | 61.0732 | 14.2281 | 258.3105 | 34.1877 | Calcium hardness | mg/L as CaCO3 | 24 | 198.2 | #DIV/0! | 87.891 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | 29 | 203 | 812 | 819.9091 | -0.97403 | 85.7143 | 511.4545 | 94.3299 | Calcium hardness | mg/L as CaCO3 | 24 | 203 | 384.0694 | 88.1773 | 293.5347 | 91.8238 | Calcium hardness | mg/L as CaCO3 | 62 | 199 | 938 | 918.25 | 2.1055 | 68.8442 | 558.625 | 88.9013 | Calcium hardness | mg/L as CaCO3 | 35 | 199 | 402.443 | 82.4121 | 300.7215 | 88.3613 | Calcium hardness | mg/L as CaCO3 | 18 | 180 | 1024 | 1175.1429 | -14.76 | 90 | 677.5714 | 97.3435 | Calcium hardness | mg/L as CaCO3 | 18 | 180 | 357.39 | 90 | 268.695 | 93.301 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 0.21*
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 16.375 | SDI | 4.67 |  |  |  | 1997-10-07 | 11:45 | 1500.56 | 24.4444 | 90 | 90 | 10.4 | 0 | 14.8 | 3.6 |  | 18.4 | 18.4 | 0.80435 | 0 | 13.5573 | 14.1952 | 10.904 | 68.696 | 0.20664 | 7.42 | 6.8 | 98.423 | 458.16 | 455.28 | 2425.28 | 1922.3588 | 20.7366 | 78.3819 | 1188.8194 | 91.7209 | 90 | 70 | 9.8 | 9.2 | 9.2 | 18.4 | 18.4 | 0.45141 | 0.5 | 14.1538 | 14.8198 | 5.7584 | 64.4416 | 0.22997 | 6.8 | NA | 71.39 | 455.28 | 950.4 | 839.17 | 11.7035 | 84.3195 | 647.225 | 88.9698 | 70 | 48 | 8.8 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.7187 | 40.4813 | 0.22284 | NA | NA | 162.4 | 950.4 | 1497.92 | 1318.1333 | 12.0024 | 64.3296 | 1134.2667 | 85.6824 | 158 | 90 | 12.6 | 2.8 | 3.6 | 6.4 | 6.4 | 0.67466 | 0.4375 | 24 | 25.1293 | 19.6452 | 91.7548 | 0.27387 | NA | 7.5 | 83.468 | 1497.92 | 2425.28 | 2598.0493 | -7.1237 | 81.6667 | 2047.9847 | 95.9244 | Turbidity | ntu | 0.04 | 0.06 | 20 | 0.14526 | 99.2737 | 33.3333 | 0.10263 | 61.0256 | Turbidity | ntu | BMRL | 0.06 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.94 | 0.19 | 20.03 | -3.0074 | 115.0143 | -394.7368 | -1.4087 | 166.7289 | Turbidity | ntu | 0.02 | 0.19 | #DIV/0! | 89.4737 | #DIV/0! | #DIV/0! | Turbidity | ntu | 0.02 | 0.15 | 23 | 0.61091 | 97.3439 | 86.6667 | 0.38045 | 94.7431 | Turbidity | ntu | 0.02 | 0.15 | 0.2815 | 86.6667 | 0.21575 | 90.7301 | Turbidity | ntu | BMRL | 0.38 | 0.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.47 | 0.38 | 0.26835 | -23.6842 | 0.32418 | -44.9824 | Turbidity | ntu | 0.03 | 0.06 | 31.8 | 0.24429 | 99.2318 | 50 | 0.15214 | 80.2817 | Turbidity | ntu | 0.04 | 0.06 | 0.0819 | 33.3333 | 0.07095 | 43.6223 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | Feed flow rate to system, QF-sys (gpm) | 19.2647 | MFI | NA |  |  |  | 1997-10-08 | 15:50 | 1516.51 | 24.4444 | 90 | 88 | 10.4667 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.6762 | 66.8571 | 0.21232 | 7.46 | 5.85 | 95.475 | 454.84 | 470.4 | 2482.48 | 2055.7971 | 17.1878 | 79.7034 | 1263.0986 | 92.4412 | 90 | 70 | 9.8 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 6.016 | 64.184 | 0.2309 | 5.86 | NA | 70.8 | 470.4 | 946.44 | 874.3912 | 7.6126 | 84.949 | 672.3956 | 89.4705 | 70 | 48 | 9 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.6353 | 40.3647 | 0.22348 | NA | NA | 165.2 | 946.44 | 1512.8 | 1311.0187 | 13.3383 | 64.881 | 1128.7293 | 85.3641 | 156 | 88 | 12.6 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.974 | 89.426 | 0.28101 | NA | 7.35 | 86.086 | 1512.8 | 2482.48 | 2654.1712 | -6.9161 | 81.6994 | 2083.4856 | 95.8682 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.66 | 10.72 | 20.8905 | 93.8433 | 15.8053 | 95.8242 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.86 | 15.25 | #DIV/0! | 94.3607 | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.64 | 11.25 | 21.9827 | 94.3111 | 16.6163 | 96.1484 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.78 | 11.85 | 25.5824 | 93.4177 | 18.7162 | 95.8325 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.43 | 6.53 | 13.2095 | 93.415 | 9.8697 | 95.6433 | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 6.5 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.8897 | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1997-10-08 | 10:30 | 1522.92 | 24.4444 | 90 | 89 | 10.3 | 0 | 14.9 | 3.6 |  | 18.5 | 18.5 | 0.80541 | 0 | 13.6489 | 14.2911 | 11.7407 | 67.4593 | 0.21185 | 7.33 | 5.96 | 89.579 | 464.8 | 472.08 | 2412.41 | 2055.2091 | 14.8068 | 81.0246 | 1263.6446 | 92.9111 | 90 | 69 | 9.5 | 9.2 | 9.3 | 18.5 | 18.5 | 0.45468 | 0.4973 | 14.1538 | 14.8198 | 6.0329 | 63.9671 | 0.23168 | 5.96 | NA | 68.44 | 472.08 | 925.65 | 871.3798 | 5.8629 | 85.5025 | 671.7299 | 89.8114 | 69 | 42 | 8.6 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.4703 | 37.4297 | 0.24101 | NA | NA | 155.4 | 925.65 | 1484.28 | 1279.2074 | 13.8163 | 67.0819 | 1102.4287 | 85.9039 | 155 | 89 | 12.8 | 2.9 | 3.6 | 6.5 | 6.5 | 0.68141 | 0.44615 | 24.8571 | 26.0268 | 19.4321 | 89.7679 | 0.28993 | NA | 7.01 | 99.022 | 1484.28 | 2412.41 | 2600.1823 | -7.7836 | 79.0243 | 2042.2311 | 95.1513 | Total organic carbon | mg/L | 0.77 | 10.72 | 46.95 | 53.1384 | -13.1809 | 92.8172 | 31.9292 | 97.5884 | UV254 | cm-1 | 0.015 | 0.343 | 0.6746 | 95.6268 | 0.5088 | 97.0519 | Total organic carbon | mg/L | 1.11 | 15.25 | 68.3 | 75.5311 | -10.5872 | 92.7213 | 45.3905 | 97.5546 | UV254 | cm-1 | 0.031 | 0.573 | #DIV/0! | 94.5899 | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 0.73 | 11.25 | 43.1 | 48.5482 | -12.6408 | 93.5111 | 29.8991 | 97.5585 | UV254 | cm-1 | 0.016 | 0.396 | 0.78039 | 95.9596 | 0.5882 | 97.2798 | Total organic carbon | mg/L | 0.76 | 11.85 | 61.7 | 70.0725 | -13.5697 | 93.5865 | 40.9612 | 98.1446 | UV254 | cm-1 | 0.019 | 0.395 | 0.86143 | 95.1899 | 0.62822 | 96.9756 | Total organic carbon | mg/L | 0.31 | 6.53 | 31.3 | 44.7386 | -42.9347 | 95.2527 | 25.6343 | 98.7907 | UV254 | cm-1 | 0.008 | 0.214 | 0.43957 | 96.2617 | 0.32678 | 97.5519 | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Hialeah Water Treatment | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  | TOC (mg/L) | 11.35 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1997-10-09 | 15:00 | 1539.17 | 24.4444 | 90 | 88 | 9.8333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.8014 | 67.3652 | 0.21072 | 7.46 | 5.87 | 91.455 | 457.33 | 470.4 | 2416.7 | 2072.796 | 14.2303 | 80.558 | 1271.598 | 92.8079 | 90 | 68 | 9 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 6.0337 | 63.9663 | 0.23168 | 5.87 | NA | 69.62 | 470.4 | 932.58 | 875.5842 | 6.1116 | 85.1998 | 672.9921 | 89.6552 | 68 | 42 | 8 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.6025 | 37.3975 | 0.24121 | NA | NA | 154 | 932.58 | 1506.6 | 1295.9173 | 13.984 | 67.2619 | 1114.2487 | 86.179 | 152 | 88 | 12.5 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.6781 | 87.8219 | 0.28614 | NA | 7.68 | 101.024 | 1506.6 | 2416.7 | 2631.0608 | -8.87 | 78.5238 | 2068.8304 | 95.1169 | UV254 | cm-1 | 0.019 | 0.343 | 0.912 | 1.7243 | -89.0639 | 94.4606 | 1.0336 | 98.1618 | SUVA | L/(mg*m) | 2.2727 | 3.1996 | --- | --- | --- | --- | UV254 | cm-1 | 0.038 | 0.573 | 0.855 | 2.8538 | -233.7765 | 93.3682 | 1.7134 | 97.7822 | SUVA | L/(mg*m) | 3.6047 | 3.7574 | --- | --- | --- | --- | UV254 | cm-1 | 0.036 | 0.396 | 0.688 | 1.6724 | -143.0761 | 90.9091 | 1.0342 | 96.519 | SUVA | L/(mg*m) | 2.5 | 3.52 | --- | --- | --- | --- | UV254 | cm-1 | 0.02 | 0.395 | 1.962 | 2.3638 | -20.4766 | 94.9367 | 1.3794 | 98.5501 | SUVA | L/(mg*m) | 2.4359 | 3.3333 | --- | --- | --- | --- | UV254 | cm-1 | 0.006 | 0.214 | 1.26 | 1.4917 | -18.39 | 97.1963 | 0.85286 | 99.2965 | SUVA | L/(mg*m) | 1.8605 | 3.2772 | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | Softening | Feed spacer thickness, T (ft) | 0.00258 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1997-10-09 | 11:10 | 1547.38 | 25.5556 | 90 | 88 | 10.4 | 0 | 14.9 | 3.55 |  | 18.45 | 18.45 | 0.80759 | 0 | 13.6489 | 13.8293 | 11.7108 | 66.8892 | 0.20675 | 7.38 | 6 | 92.46 | 463.14 | 470.4 | 2445.3 | 2056.6834 | 15.8924 | 80.3444 | 1263.5417 | 92.6825 | 90 | 69 | 9.8 | 9.2 | 9.25 | 18.45 | 18.45 | 0.45305 | 0.49864 | 14.1538 | 14.341 | 5.992 | 63.708 | 0.22511 | 6 | NA | 70.21 | 470.4 | 928.62 | 868.4268 | 6.482 | 85.0744 | 669.4134 | 89.5117 | 69 | 42 | 8.5 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 8.7293 | 9.4552 | 37.5448 | 0.2325 | NA | NA | 159.6 | 928.62 | 1478.08 | 1281.6128 | 13.2921 | 66.0714 | 1105.1164 | 85.5581 | 152 | 88 | 12.9 | 2.9 | 3.55 | 6.45 | 6.45 | 0.67466 | 0.44961 | 24.8571 | 25.1859 | 19.4082 | 87.6918 | 0.28721 | NA | 7.12 | 100.1 | 1478.08 | 2445.3 | 2603.7538 | -6.4799 | 78.7202 | 2040.9169 | 95.0953 | SUVA | L/(mg*m) | 2.4675 | 3.1996 | 1.9425 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 3.4234 | 3.7574 | 1.2518 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 4.9315 | 3.52 | 1.5963 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 2.6316 | 3.3333 | 3.1799 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.9355 | 3.2772 | 4.0256 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | Hialeah WTP | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 11.1397 | [5 empty] | 1997-10-13 | 18:45 | 1639.29 | 24.4444 | 90 | 88 | 9.6333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.8297 | 67.537 | 0.21018 | 7.54 | 5.84 | 91.388 | 458.16 | 471.24 | 2453.88 | 2077.4713 | 15.3393 | 80.6069 | 1274.3557 | 92.8287 | 90 | 68 | 9.2 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 5.922 | 63.878 | 0.232 | 5.84 | NA | 77.88 | 471.24 | 948.42 | 868.9226 | 8.3821 | 83.4734 | 670.0813 | 88.3775 | 68 | 42 | 7.2 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.8324 | 37.9676 | 0.23759 | NA | NA | 151.2 | 948.42 | 1476.84 | 1320.456 | 10.5891 | 67.9144 | 1134.438 | 86.6718 | 152 | 88 | 12.5 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.5395 | 87.9605 | 0.28569 | NA | 7.6 | 81.158 | 1476.84 | 2453.88 | 2593.3856 | -5.6851 | 82.7778 | 2035.1128 | 96.0121 | Bromide | mg/L | 53.05 | 170.18 | --- | 669.5237 | --- | 68.8271 | 419.8518 | 87.3646 | [8 empty] | Bromide | mg/L | 52 | 154 | --- | 588.8421 | --- | 66.2338 | 371.4211 | 85.9997 | [8 empty] | Bromide | mg/L | 50.748 | 165.612 | --- | 572.8571 | --- | 69.3573 | 369.2345 | 86.2559 | [8 empty] | Bromide | mg/L | 97.4 | 142.91 | --- | 381.8375 | --- | 31.8452 | 262.3737 | 62.8774 | [8 empty] | Bromide | mg/L | 17 | 78 | --- | 452.7143 | --- | 78.2051 | 265.3571 | 93.5935 | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 302 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4522 | [5 empty] | 1997-10-14 | 1:00 | 1645.81 | 24.4444 | 90 | 88 | 10.1333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.7618 | 67.1049 | 0.21154 | 7.46 | 5.86 | 92.728 | 454.84 | 470.4 | 2482.48 | 2067.413 | 16.7199 | 80.2874 | 1268.9065 | 92.6923 | 90 | 69 | 9.8 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 6.016 | 63.684 | 0.23271 | 5.86 | NA | 70.8 | 470.4 | 932.58 | 874.3912 | 6.2395 | 84.949 | 672.3956 | 89.4705 | 69 | 42 | 8 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.435 | 38.065 | 0.23698 | NA | NA | 165.2 | 932.58 | 1497.92 | 1284.82 | 14.2264 | 64.881 | 1108.7 | 85.0997 | 156 | 88 | 12.6 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.825 | 89.575 | 0.28054 | NA | 7.68 | 81.851 | 1497.92 | 2482.48 | 2630.7752 | -5.9737 | 82.5997 | 2064.3476 | 96.035 | SDS-Cl2 dose | mg/L | 3 | 7.7 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 12 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 12 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4130871 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 0.57721 | [5 empty] | 1997-10-14 | 7:50 | 1652.41 | 24.4444 | 90 | 88 | 9.7333 | 0 | 14.3 | 3.5 |  | 17.8 | 17.8 | 0.80337 | 0 | 13.0992 | 13.7156 | 11.8467 | 67.4199 | 0.20344 | 7.22 | 5.89 | 91.991 | 467.29 | 481.32 | 2448.16 | 2072.0071 | 15.3647 | 80.8878 | 1276.6635 | 92.7944 | 90 | 68 | 9.5 | 8.7 | 9.1 | 17.8 | 17.8 | 0.43996 | 0.48876 | 13.3846 | 14.0144 | 6.024 | 63.476 | 0.22078 | 5.89 | NA | 73.75 | 481.32 | 970.2 | 870.9748 | 10.2273 | 84.6776 | 676.1474 | 89.0926 | 68 | 42 | 7.2 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.8765 | 37.9235 | 0.23787 | NA | NA | 169.4 | 970.2 | 1463.2 | 1343.9067 | 8.1529 | 64.8051 | 1157.0533 | 85.3594 | 152 | 88 | 12.5 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.3583 | 88.1417 | 0.2851 | NA | 6.83 | 80.465 | 1463.2 | 2448.16 | 2569.388 | -4.9518 | 83.2824 | 2016.294 | 96.0093 | SDS-Free Cl2 residual | mg/L | 1.01 | 1.12 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.31 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.9 | 0.55 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.3 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.25 | 0.65 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.29 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.91 | 1.07 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.41 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.18 | 1.91 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 23 | Stage 1 and 2 -- Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1997-10-14 | 18:00 | 1668.01 | 24.4444 | 90 | 88 | 9.9667 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.8801 | 67.1533 | 0.21138 | 7.3 | 5.88 | 93.13 | 464.8 | 474.6 | 2473.9 | 2087.6731 | 15.6121 | 80.3772 | 1281.1366 | 92.7307 | 90 | 69 | 9.6 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 6.0614 | 63.8386 | 0.23215 | 5.88 | NA | 71.98 | 474.6 | 960.3 | 881.6444 | 8.1907 | 84.8335 | 678.1222 | 89.3854 | 69 | 42 | 7.9 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.7328 | 37.8672 | 0.23822 | NA | NA | 168.7 | 960.3 | 1469.4 | 1323.6574 | 9.9185 | 64.4543 | 1141.9787 | 85.2274 | 154 | 88 | 12.4 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.4397 | 89.1603 | 0.28184 | NA | 6.9 | 80.85 | 1469.4 | 2473.9 | 2580.24 | -4.2985 | 82.9646 | 2024.82 | 96.0071 | SDS-Cl2 demand | mg/L | 1.99 | 6.58 | --- | 26.1479 | --- | 69.7568 | 16.3639 | 87.8391 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.1 | 11.45 | --- | 51.3105 | --- | 81.6594 | 31.3803 | 93.3079 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.75 | 11.85 | --- | 44.1136 | --- | 76.7932 | 27.9818 | 90.1722 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.09 | 11.43 | --- | 60.465 | --- | 81.7148 | 35.9475 | 94.186 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 3.2 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.32 | 10.09 | --- | 57.82 | --- | 77.0069 | 33.955 | 93.1674 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 26 | Design cross-flow velocity (fps) | 0.75 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1997-10-15 | 7:00 | 1675.75 | 24.4444 | 90 | 90 | 9.9333 | 0 | 14.8 | 3.45 |  | 18.25 | 18.25 | 0.81096 | 0 | 13.5573 | 14.1952 | 12.1618 | 67.9049 | 0.20904 | 7.38 | 5.85 | 92.929 | 459.82 | 479.64 | 2502.5 | 2138.5741 | 14.5425 | 80.6253 | 1309.1071 | 92.9013 | 90 | 68 | 9.8 | 9.2 | 9.05 | 18.25 | 18.25 | 0.4465 | 0.50411 | 14.1538 | 14.8198 | 6.1487 | 63.0513 | 0.23504 | 5.85 | NA | 71.98 | 479.64 | 949.41 | 894.0568 | 5.8303 | 84.9929 | 686.8484 | 89.5202 | 68 | 44 | 7.5 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.8141 | 38.6859 | 0.23318 | NA | NA | 151.2 | 949.41 | 1470.64 | 1315.8015 | 10.5286 | 68.4764 | 1132.6057 | 86.6503 | 154 | 90 | 12.5 | 2.8 | 3.45 | 6.25 | 6.25 | 0.65442 | 0.448 | 24 | 25.1293 | 19.6145 | 89.8855 | 0.27957 | NA | 7.12 | 75.383 | 1470.64 | 2502.5 | 2603.0225 | -4.0169 | 84.2834 | 2036.8312 | 96.299 | SDS-Chlorination temp. | oC | 23 | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.1 |  |  |  |  | SDS-Chlorination temp. | oC | 23 | 23.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.2 |  |  |  |  | SDS-Chlorination temp. | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.65 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.9 |  |  |  |  | SDS-Chlorination temp. | oC | 26 | 26 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 10 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 60 | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1.8603 | [5 empty] | 1997-10-15 | 20:00 | 1688.55 | 24.4444 | 90 | 88 | 9.5667 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.9322 | 67.5011 | 0.2103 | 7.46 | 5.71 | 91.455 | 458.16 | 474.6 | 2448.16 | 2094.756 | 14.4355 | 80.7301 | 1284.678 | 92.8811 | 90 | 68 | 9.5 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 6.0383 | 63.4617 | 0.23352 | 5.71 | NA | 73.514 | 474.6 | 968.22 | 880.0935 | 9.1019 | 84.5103 | 677.3468 | 89.1468 | 68 | 42 | 7 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 10.0248 | 37.9752 | 0.23754 | NA | NA | 155.4 | 968.22 | 1480.56 | 1347.536 | 8.9847 | 67.2566 | 1157.878 | 86.5789 | 155 | 88 | 12.2 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.6671 | 89.6329 | 0.28036 | NA | 7.24 | 75.768 | 1480.56 | 2448.16 | 2604.3936 | -6.3817 | 84.0354 | 2042.4768 | 96.2904 | SDS-Chlorination pH | --- | 6.15 | 8.24 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.03 | 6.63 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.3 | 6.84 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.65 | 7.16 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.91 | 6.52 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 17 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.0478 | [5 empty] | 1997-10-15 | 2:00 | 1690 | 24.4444 | 90 | 88 | 9.7 | 0 | 14.8 | 3.4 |  | 18.2 | 18.2 | 0.81319 | 0 | 13.5573 | 14.1952 | 12.1598 | 67.1402 | 0.21143 | 7.3 | 5.75 | 91.79 | 460.65 | 474.6 | 2473.9 | 2140.9494 | 13.4585 | 80.6595 | 1307.7747 | 92.9812 | 90 | 68 | 9.6 | 9.2 | 9 | 18.2 | 18.2 | 0.44487 | 0.50549 | 14.1538 | 14.8198 | 6.084 | 63.316 | 0.23406 | 5.75 | NA | 71.98 | 474.6 | 959.31 | 886.1671 | 7.6245 | 84.8335 | 680.3836 | 89.4207 | 68 | 43 | 7.2 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.9014 | 38.3986 | 0.23492 | NA | NA | 154 | 959.31 | 1463.2 | 1328.9605 | 9.1744 | 67.5516 | 1144.1352 | 86.5401 | 155 | 88 | 12.3 | 2.8 | 3.4 | 6.2 | 6.2 | 0.64768 | 0.45161 | 24 | 25.1293 | 19.5916 | 89.6084 | 0.28043 | NA | 7.2 | 75.46 | 1463.2 | 2473.9 | 2606.0447 | -5.3416 | 84.1003 | 2034.6224 | 96.2912 | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 5 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -0.077206 | [5 empty] | 1997-10-16 | 12:10 | 1691.96 | 24.4444 | 90 | 88 | 9.8333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | 11.7952 | 67.3715 | 0.2107 | 7.32 | 5.75 | 91.656 | 468.12 | 470.4 | 2499.64 | 2071.9461 | 17.1102 | 80.5153 | 1271.173 | 92.7897 | 90 | 68 | 9.5 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | 5.9804 | 63.5196 | 0.23331 | 5.75 | NA | 73.16 | 470.4 | 972.18 | 872.0053 | 10.3041 | 84.4473 | 671.2026 | 89.1002 | 68 | 42 | 7.5 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.9528 | 37.5472 | 0.24025 | NA | NA | 165.2 | 972.18 | 1460.72 | 1348.7707 | 7.664 | 64.881 | 1160.4753 | 85.7645 | 154 | 88 | 12.5 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.3807 | 89.1193 | 0.28197 | NA | 6.96 | 76.384 | 1460.72 | 2499.64 | 2568.1888 | -2.7423 | 83.7619 | 2014.4544 | 96.2082 | SDS-TOX | mg Cl- /L | BMRL | 700 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 66 | 1160 | --- | 5823.8947 | --- | 94.3103 | 3491.9474 | 98.1099 | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 40 | 730 | --- | 3176.3636 | --- | 94.5205 | 1953.1818 | 97.9521 | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 64 | 790 | --- | 4601.5 | --- | 91.8987 | 2695.75 | 97.6259 | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 335 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | Chloride ion rejection = 85 % | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1997-10-16 | 7:35 | 1700.36 | 24.4444 | 90 | 90 | 9.5333 | 0 | 14.65 | 3.55 |  | 18.2 | 18.2 | 0.80495 | 0 | 13.4198 | 14.0513 | 11.4459 | 69.0207 | 0.20358 | 7.48 | 6.49 | 91.723 | 453.18 | 465.36 | 2355.21 | 2007.2704 | 14.7732 | 80.2899 | 1236.3152 | 92.5809 | 90 | 70 | 9.6 | 8.95 | 9.25 | 18.2 | 18.2 | 0.44896 | 0.49176 | 13.7692 | 14.4171 | 6.0339 | 64.3661 | 0.22399 | 6.49 | NA | 58.705 | 465.36 | 917.73 | 858.8262 | 6.4184 | 87.385 | 662.0931 | 91.1334 | 70 | 45 | 7 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.4245 | 41.0755 | 0.21961 | NA | NA | 151.2 | 917.73 | 1443.36 | 1269.5798 | 12.04 | 67.509 | 1093.6549 | 86.1748 | 156 | 90 | 12 | 2.9 | 3.55 | 6.45 | 6.45 | 0.67466 | 0.44961 | 24.8571 | 26.0268 | 19.2619 | 91.7381 | 0.28371 | NA | 7.69 | 75.768 | 1443.36 | 2355.21 | 2560.5478 | -8.7185 | 83.7184 | 2001.9539 | 96.2153 | SDS-CHCl3 | mg/L | 2.7 | 71.5 | --- | 364.8053 | --- | 96.2238 | 218.1526 | 98.7623 | Sampling date | MM/DD/YY | 1997-10-08 | 1997-10-08 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.04 | 145 | --- | 750.1979 | --- | 97.9034 | 447.5989 | 99.3208 | Sampling date | MM/DD/YY | 1997-10-22 | 1997-10-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1.31 | 56.7 | --- | 253.0827 | --- | 97.6896 | 154.8914 | 99.1542 | Sampling date | MM/DD/YY | 1997-11-05 | 1997-11-05 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.31 | 97 | --- | 588.8725 | --- | 96.5876 | 342.9362 | 99.0348 | Sampling date | MM/DD/YY | 1997-11-19 | 1997-11-19 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.82 | 35.8 | --- | 250.6771 | --- | 97.7095 | 143.2386 | 99.4275 | Sampling date | MM/DD/YY | 1998-01-14 | 1998-01-14 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | at 500 mg/L NaCL solution | meet the manufacturer's minimum flow requirement. | [6 empty] | 1997-10-16 | 15:27 | 1708.09 | 25 | 90 | 85 | 9.4 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 14.0583 | 11.5076 | 66.5924 | 0.21111 | 7.42 | 5.59 | 91.656 | 458.99 | 459.48 | 2468.18 | 2025.3593 | 17.9412 | 80.0522 | 1242.4197 | 92.6228 | 90 | 65 | 9.2 | 9.2 | 9.2 | 18.4 | 18.4 | 0.45141 | 0.5 | 14.1538 | 14.5785 | 5.8886 | 62.4114 | 0.23359 | 5.59 | NA | 66.906 | 459.48 | 954.36 | 852.054 | 10.7199 | 85.4388 | 655.767 | 89.7973 | 65 | 40 | 7 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.8738 | 9.8452 | 35.6548 | 0.24888 | NA | NA | 156.1 | 954.36 | 1465.68 | 1326.8813 | 9.4699 | 66.0268 | 1140.6207 | 86.3145 | 152 | 85 | 12 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 25.6029 | 19.6508 | 86.8492 | 0.2948 | NA | 7.37 | 76.23 | 1465.68 | 2468.18 | 2616.9386 | -6.0271 | 83.4095 | 2041.3093 | 96.2656 | SDS-BDCM | mg/L | 2.57 | 31.2 | --- | 153.2542 | --- | 91.7628 | 92.2271 | 97.2134 | Sampling time | hh:mm | 7:30 | 7:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | 3.01 | 27.1 | --- | 129.7995 | --- | 88.893 | 78.4497 | 96.1631 | Sampling time | hh:mm | 7:00 | 7:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.07 | 30 | --- | 132.57 | --- | 96.4333 | 81.285 | 98.6836 | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | 3.93 | 31.5 | --- | 176.2425 | --- | 87.5238 | 103.8713 | 96.2165 | Sampling time | hh:mm | 7:30 | 7:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.44 | 19 | --- | 133.0114 | --- | 97.6842 | 76.0057 | 99.4211 | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1997-10-17 | 12:05 | 1716.34 | 25 | 90 | 88 | 9.6 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 13.964 | 11.5262 | 67.8738 | 0.20573 | 7.36 | 5.58 | 91.053 | 463.14 | 461.16 | 2473.9 | 2026.1839 | 18.0976 | 80.2557 | 1243.6719 | 92.6787 | 90 | 69 | 9.6 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.5785 | 5.8458 | 64.0542 | 0.2276 | 5.58 | NA | 72.865 | 461.16 | 966.24 | 853.722 | 11.6449 | 84.1996 | 657.441 | 88.9169 | 69 | 43 | 7.2 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.8738 | 9.7759 | 39.0241 | 0.22739 | NA | NA | 173.6 | 966.24 | 1453.28 | 1336.1387 | 8.0605 | 62.3558 | 1151.1893 | 84.9199 | 158 | 88 | 12 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 24.72 | 19.2916 | 91.7084 | 0.26955 | NA | 7.52 | 75.306 | 1453.28 | 2473.9 | 2555.6592 | -3.3049 | 83.6703 | 2004.4696 | 96.2431 | SDS-DBCM | mg/L | 1.96 | 6.16 | --- | 24.0653 | --- | 68.1818 | 15.1126 | 87.0307 | Operation time | hh.hh | 1508 | 1508 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.53 | 3.51 | --- | 11.9511 | --- | 56.4103 | 7.7305 | 80.2083 | Operation time | hh.hh | 1770.8 | 1770.8 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.17 | 0.481 | --- | -1.9618 | --- | -143.2432 | -0.74041 | 258.0208 | Operation time | hh.hh | 2094 | 2094 | --- | --- | --- | --- | SDS-DBCM | mg/L | 3.07 | 7.52 | --- | 30.8825 | --- | 59.1755 | 19.2013 | 84.0115 | Operation time | hh.hh | 1962.6 | 1962.6 | --- | --- | --- | --- | SDS-DBCM | mg/L | 0.18 | 3.12 | --- | 21.18 | --- | 94.2308 | 12.15 | 98.5185 | Operation time | hh.hh | 2405 | 2405 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1997-10-17 | 7:00 | 1723.63 | 24.4444 | 90 | 88 | 9.7333 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 14.2911 | 11.5139 | 67.7528 | 0.21093 | 7.34 | 5.49 | 102.376 | 463.97 | 470.4 | 2372.37 | 2037.1307 | 14.131 | 78.2364 | 1253.7654 | 91.8345 | 90 | 69 | 9.8 | 9.2 | 9.2 | 18.4 | 18.4 | 0.45141 | 0.5 | 14.1538 | 14.8198 | 5.825 | 63.875 | 0.23201 | 5.49 | NA | 82.069 | 470.4 | 922.68 | 858.731 | 6.9308 | 82.5534 | 664.5655 | 87.6507 | 69 | 43 | 7.2 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 10.4089 | 38.3911 | 0.23497 | NA | NA | 76.09 | 922.68 | 1448.32 | 1311.2787 | 9.4621 | 83.8244 | 1116.9793 | 93.1879 | 154 | 88 | 12.2 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 18.8031 | 89.9969 | 0.2892 | NA | 6.97 | 118.811 | 1448.32 | 2372.37 | 2549.9132 | -7.4838 | 74.7426 | 1999.1166 | 94.0568 | SDS-CHBr3 | mg/L | 0.23 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.07 | 6.68 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.12 | 6.67 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.45 | 6.86 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.31 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.72 | 7.4 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.8 | 6.69 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 8 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 0.73529 | [5 empty] | 1997-10-17 | 15:45 | 1732.38 | 25 | 90 | 88 | 9.5333 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 13.964 | 11.9154 | 67.5513 | 0.20672 | 7.38 | 5.43 | 90.316 | 447.37 | 472.92 | 2366.65 | 2090.7883 | 11.6562 | 80.9025 | 1281.8542 | 92.9543 | 90 | 66 | 9.6 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.5785 | 6.0104 | 62.3896 | 0.23367 | 5.43 | NA | 73.691 | 472.92 | 924.66 | 876.5361 | 5.2045 | 84.4179 | 674.7281 | 89.0784 | 66 | 42 | 7 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.8738 | 9.5393 | 37.4607 | 0.23688 | NA | NA | 151.2 | 924.66 | 1488 | 1285.608 | 13.6016 | 68.0284 | 1105.134 | 86.3184 | 152 | 88 | 12 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 24.72 | 19.8025 | 88.1975 | 0.28028 | NA | 6.98 | 73.535 | 1488 | 2366.65 | 2619.572 | -10.6869 | 84.4509 | 2053.786 | 96.4195 | SDS-THM4 | mg/L | 7.46 | 108.86 | --- | 541.1442 | --- | 93.1472 | 325.0021 | 97.7046 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 7.58 | 175.61 | --- | 891.9484 | --- | 95.6836 | 533.7792 | 98.5799 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.55 | 87.181 | --- | 383.6909 | --- | 95.928 | 235.436 | 98.4922 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 10.62 | 136.02 | --- | 794.37 | --- | 92.1923 | 465.195 | 97.7171 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.44 | 57.92 | --- | 404.8686 | --- | 97.5138 | 231.3943 | 99.3777 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 to 350 psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 0.48529 | [5 empty] | 1997-10-18 | 1:00 | 1741.69 | 24.4444 | 90 | 88 | 9.6667 | 0 | 14.8 | 3.8 |  | 18.6 | 18.6 | 0.7957 | 0 | 13.5573 | 14.1952 | 11.0125 | 68.3209 | 0.20777 | 6.12 | 5.42 | 91.723 | 488.87 | 465.36 | 2452.45 | 1920.5778 | 21.6874 | 80.2899 | 1192.9689 | 92.3114 | 90 | 68 | 9.8 | 9.2 | 9.4 | 18.6 | 18.6 | 0.45795 | 0.49462 | 14.1538 | 14.8198 | 5.8536 | 63.3464 | 0.23395 | 5.42 | NA | 72.334 | 465.36 | 930.6 | 850.0237 | 8.6585 | 84.4563 | 657.6919 | 89.0018 | 68 | 42 | 7 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.5953 | 38.4047 | 0.23489 | NA | NA | 152.6 | 930.6 | 1473.12 | 1293.6667 | 12.1819 | 67.2082 | 1112.1333 | 86.2786 | 154 | 88 | 12.2 | 2.8 | 3.8 | 6.6 | 6.6 | 0.70165 | 0.42424 | 24 | 25.1293 | 19.1417 | 89.6583 | 0.28028 | NA | NA | 74.305 | 1473.12 | 2452.45 | 2503.8258 | -2.0949 | 84.0328 | 1988.4729 | 96.2632 | SDS-MCAA* | mg/L | BMRL | 5.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 52.64 | 257.28 | 348.2311 | 63.9748 | 302.7556 | 82.613 | SDS-MCAA* | mg/L | BMRL | 6.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 50.47 | 231.25 | 310.3413 | 61.9295 | 270.7956 | 81.3623 | SDS-MCAA* | mg/L | BMRL | 5.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 59 | 290 | 383.9024 | 63.5802 | 336.9512 | 82.49 | SDS-MCAA* | mg/L | BMRL | 5.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 67 | 444 | 700.6809 | 70.0893 | 572.3404 | 88.2937 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 213 | 392.0769 | 83.6207 | 302.5385 | 93.7198 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 4 to 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | -2.1397 | [5 empty] | 1997-10-18 | 8:00 | 1748.96 | 24.4444 | 90 | 90 | 9.5333 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 14.2911 | #VALUE! | #VALUE! | #VALUE! | 7.36 | NA | NA | 440.73 | 451.08 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 90 | 68 | 9.8 | 9.2 | 9.2 | 18.4 | 18.4 | 0.45141 | 0.5 | 14.1538 | 14.8198 | #VALUE! | #VALUE! | #VALUE! | 5.18 | NA | NAA | 451.08 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 68 | 42 | 7 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | 1409.88 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 154 | 90 | 11.8 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | #VALUE! | #VALUE! | #VALUE! | NA | N/A | NA | 1409.88 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 2.3 | 39 | --- | 195.4579 | --- | 94.1026 | 117.2289 | 98.038 | Total dissolved solids | mg/L | 148 | 679 | 915 | 62.8141 | 797 | 81.4304 | SDS-DCAA* | mg/L | 4.7 | 62 | --- | 306.2789 | --- | 92.4194 | 184.1395 | 97.4476 | Total dissolved solids | mg/L | 181 | 667 | 879.625 | 52.987 | 773.3125 | 76.5942 | SDS-DCAA* | mg/L | 2 | 39 | --- | 170.1818 | --- | 94.8718 | 104.5909 | 98.0878 | Total dissolved solids | mg/L | 150 | 666 | 875.7561 | 61.3402 | 770.878 | 80.5417 | SDS-DCAA* | mg/L | 2.5 | 48 | --- | 286.875 | --- | 94.7917 | 167.4375 | 98.5069 | Total dissolved solids | mg/L | 126 | 697 | 1085.766 | 66.8421 | 891.383 | 85.8647 | SDS-DCAA* | mg/L | BMRL | 22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 54.7 | 573 | 1051.4308 | 83.0124 | 812.2154 | 93.2653 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1997-10-21 | 9:15 | 1749.33 | 25.5556 | 88 | 88 | 9.5 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 13.8293 | 11.8143 | 66.6857 | 0.20738 | 7.37 | 5.26 | 88.574 | 442.39 | 466.2 | 2306.59 | 2073.8078 | 10.092 | 81.0009 | 1270.0039 | 93.0257 | 88 | 65 | 9.5 | 9.3 | 9.1 | 18.4 | 18.4 | 0.44978 | 0.50543 | 14.3077 | 14.4969 | 6.0636 | 60.9364 | 0.2379 | 5.26 | NA | 64.9 | 466.2 | 888.03 | 876.3198 | 1.3187 | 86.0789 | 671.2599 | 90.3316 | 65 | 40 | 7 | 2.7 | 6.1 | 8.8 | 8.8 | 0.48739 | 0.30682 | 8.3077 | 8.4176 | 9.17 | 36.33 | 0.2317 | NA | NA | 137.2 | 888.03 | 1356.56 | 1220.3646 | 10.0398 | 70.5706 | 1054.1973 | 86.9854 | 150 | 88 | 12 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 25.1859 | 18.1838 | 88.8162 | 0.28357 | NA | 7.17 | 70.84 | 1356.56 | 2306.59 | 2421.8709 | -4.9979 | 84.8048 | 1889.2154 | 96.2503 | SDS-TCAA* | mg/L | 2.4 | 100 | --- | 516.0842 | --- | 97.6 | 308.0421 | 99.2209 | Total hardness | mg/L as CaCO3 | 35.4 | 505 | 713.7111 | 84.9362 | 609.3556 | 94.1906 | SDS-TCAA* | mg/L | 5.7 | 120 | --- | 607.2789 | --- | 95.25 | 363.6395 | 98.4325 | Total hardness | mg/L as CaCO3 | 55.4 | 430 | 593.8875 | 75.2236 | 511.9438 | 89.1785 | SDS-TCAA* | mg/L | 1.7 | 77 | --- | 343.9727 | --- | 97.7922 | 210.4864 | 99.1923 | Total hardness | mg/L as CaCO3 | 58 | 473 | 641.6992 | 75.2137 | 557.3496 | 89.5936 | SDS-TCAA* | mg/L | 2.7 | 120 | --- | 735.825 | --- | 97.75 | 427.9125 | 99.369 | Total hardness | mg/L as CaCO3 | 53 | 467 | 748.8723 | 76.8559 | 607.9362 | 91.282 | SDS-TCAA* | mg/L | 1.1 | 39 | --- | 271.8143 | --- | 97.1795 | 155.4071 | 99.2922 | Total hardness | mg/L as CaCO3 | 11 | 384 | 728.3077 | 94.1489 | 556.1538 | 98.0221 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1997-10-22 | 9:00 | 1772.81 | 25.5556 | 90 | 90 | 9.1667 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 13.8293 | 11.7346 | 69.0987 | 0.20014 | 7.38 | 5.77 | 91.12 | 444.05 | 466.2 | 2349.49 | 2062.9691 | 12.195 | 80.4547 | 1264.5846 | 92.7945 | 90 | 68 | 9.5 | 9.2 | 9.2 | 18.4 | 18.4 | 0.45141 | 0.5 | 14.1538 | 14.341 | 6.0018 | 63.4982 | 0.22585 | 5.77 | NA | 66.08 | 466.2 | 921.69 | 866.32 | 6.0074 | 85.8258 | 666.26 | 90.0819 | 68 | 40 | 7 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.7293 | 9.7444 | 37.2556 | 0.23431 | NA | NA | 131.6 | 921.69 | 1409.88 | 1290.3987 | 8.4746 | 71.7718 | 1106.0443 | 88.1017 | 160 | 90 | 11 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 25.1859 | 18.9161 | 95.0839 | 0.26488 | NA | 7.01 | 72.38 | 1409.88 | 2349.49 | 2518.0943 | -7.1762 | 84.4745 | 1963.9871 | 96.3146 | SDS-MBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 47 | 425 | 593 | 76.9608 | 509 | 90.7662 | SDS-MBAA* | mg/L | BMRL | 1.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 48 | 370 | 510.875 | 75.782 | 440.4375 | 89.1017 | SDS-MBAA* | mg/L | BMRL | 1.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 52 | 390 | 527.3984 | 74.3842 | 458.6992 | 88.6636 | SDS-MBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 46 | 408 | 654.4681 | 76.8844 | 531.234 | 91.3409 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 11 | 359 | 680.2308 | 93.8889 | 519.6154 | 97.883 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1.8603 | [5 empty] | 1997-10-22 | 17:00 | 1780.65 | 25 | 92 | 90 | 9.2 | 0 | 14.9 | 3.5 |  | 18.4 | 18.4 | 0.80978 | 0 | 13.6489 | 14.0583 | 11.9249 | 69.8751 | 0.20119 | 7.41 | 5.74 | 90.919 | 449.03 | 472.08 | 2283.71 | 2094.7368 | 8.2748 | 80.7408 | 1283.4084 | 92.9158 | 92 | 70 | 9.6 | 9.3 | 9.1 | 18.4 | 18.4 | 0.44978 | 0.50543 | 14.3077 | 14.7369 | 6.1524 | 65.2476 | 0.22586 | 5.74 | NA | 64.9 | 472.08 | 929.61 | 888.209 | 4.4536 | 86.2523 | 680.1445 | 90.4579 | 70 | 40 | 7 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 8.8738 | 9.8076 | 38.1924 | 0.23235 | NA | NA | 134.4 | 929.61 | 1435.92 | 1300.708 | 9.4164 | 71.5302 | 1115.159 | 87.9479 | 155 | 90 | 11 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 24.72 | 19.0842 | 92.4158 | 0.26749 | NA | 7.06 | 72.765 | 1435.92 | 2283.71 | 2526.444 | -10.6289 | 84.5863 | 1981.182 | 96.3272 | SDS-DBAA* | mg/L | 1 | 2 | --- | 6.2632 | --- | 50 | 4.1316 | 75.7962 | Turbidity | ntu | 0.09 | 0.12 | 0.13333 | -50 | 0.12667 | 28.9474 | SDS-DBAA* | mg/L | 1.1 | 1.5 | --- | 3.2053 | --- | 26.6667 | 2.3526 | 53.2438 | Turbidity | ntu | 0.22 | 0.33 | 0.37812 | -15.7895 | 0.35406 | 37.8641 | SDS-DBAA* | mg/L | 1.4 | 2.2 | --- | 5.0364 | --- | 36.3636 | 3.6182 | 61.3065 | Turbidity | ntu | 0.02 | 1.24 | 1.7359 | 86.6667 | 1.488 | 98.6559 | SDS-DBAA* | mg/L | 1.3 | 1.8 | --- | 4.425 | --- | 27.7778 | 3.1125 | 58.2329 | Turbidity | ntu | BMRL | 0.43 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.15 | 0.27 | 66.6667 | 0.21 | 90.4762 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | Zero for extended use | Maximum system recycle flow rate, (QR-sys)max (gpm) | -2.1397 | [5 empty] | 1997-10-23 | 12:20 | 1788.06 | 24.4444 | 88 | 90 | 8.9333 | 0 | 14.3 | 3.5 |  | 17.8 | 17.8 | 0.80337 | 0 | 13.0992 | 13.7156 | 11.5491 | 68.5176 | 0.20018 | 7.4 | 6.51 | 90.852 | 460.65 | 470.4 | 2259.4 | 2021.1247 | 10.546 | 80.6862 | 1245.7623 | 92.7071 | 88 | 68 | 9.5 | 8.7 | 9.1 | 17.8 | 17.8 | 0.43996 | 0.48876 | 13.3846 | 14.0144 | 5.9672 | 62.5328 | 0.22411 | 6.51 | NA | 66.67 | 470.4 | 932.58 | 856.3836 | 8.1705 | 85.827 | 663.3918 | 89.9501 | 68 | 42 | 6.5 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.8788 | 38.6212 | 0.23357 | NA | NA | 131.6 | 932.58 | 1440.88 | 1306.3707 | 9.3352 | 72.0238 | 1119.4753 | 88.2445 | 152 | 90 | 10.8 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.1525 | 91.0475 | 0.276 | NA | 7.28 | 72.842 | 1440.88 | 2259.4 | 2535.3104 | -12.2117 | 84.5149 | 1988.0952 | 96.3361 | SDS-BCAA* | mg/L | 1.7 | 13 | --- | 61.1737 | --- | 86.9231 | 37.0868 | 95.4162 | Total organic carbon | mg/L | 1.21 | 21.55 | 30.59 | 88.7127 | 26.07 | 95.3586 | SDS-BCAA* | mg/L | 3.1 | 13 | --- | 55.2053 | --- | 76.1538 | 34.1026 | 90.9098 | Total organic carbon | mg/L | 1.51 | 30.98 | 43.8731 | 90.0984 | 37.4266 | 95.9654 | SDS-BCAA* | mg/L | 1.6 | 12 | --- | 48.8727 | --- | 86.6667 | 30.4364 | 94.7431 | Total organic carbon | mg/L | 1.18 | 22.45 | 31.0963 | 89.5111 | 26.7732 | 95.5926 | SDS-BCAA* | mg/L | 2.4 | 13 | --- | 68.65 | --- | 81.5385 | 40.825 | 94.1212 | Total organic carbon | mg/L | 0.52 | 23.35 | 38.8938 | 95.6118 | 31.1219 | 98.3292 | SDS-BCAA* | mg/L | BMRL | 6.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.29 | 12.13 | 23.0592 | 95.559 | 17.5946 | 98.3518 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1997-10-23 | 8:50 | 1796.7 | 24.4444 | 89 | 90 | 9.1 | 0 | 14.4 | 3.5 |  | 17.9 | 17.9 | 0.80447 | 0 | 13.1908 | 13.8115 | 11.1181 | 69.2819 | 0.19935 | 7.42 | 6.49 | 86.564 | 454.01 | 450.24 | 2197.91 | 1946.507 | 11.4383 | 80.7738 | 1198.3735 | 92.7765 | 89 | 68 | 9.8 | 8.7 | 9.2 | 17.9 | 17.9 | 0.44323 | 0.48603 | 13.3846 | 14.0144 | 5.7041 | 62.9959 | 0.22247 | 6.49 | NA | 62.953 | 450.24 | 884.07 | 816.4788 | 7.6455 | 86.0179 | 633.3594 | 90.0605 | 68 | 42 | 6.9 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 8.9677 | 39.1323 | 0.23052 | NA | NA | 154.7 | 884.07 | 1388.8 | 1218.8628 | 12.2363 | 65.6405 | 1051.4664 | 85.2872 | 154 | 90 | 10.6 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 18.5776 | 92.8224 | 0.28039 | NA | 7.74 | 75.229 | 1388.8 | 2197.91 | 2477.1874 | -12.7065 | 83.2914 | 1932.9937 | 96.1082 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.032 | 0.65 | 0.92467 | 90.6706 | 0.78733 | 95.9356 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.058 | 0.857 | 1.2066 | 89.8778 | 1.0318 | 94.3787 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.036 | 0.705 | 0.97695 | 90.9091 | 0.84098 | 95.7193 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.839 | 1.4021 | 96.962 | 1.1205 | 98.9291 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.002 | 0.456 | 0.87508 | 99.0654 | 0.66554 | 99.6995 | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 19.2647 | [5 empty] | 1997-10-23 | 18:00 | 1805.94 | 24.4444 | 88 | 90 | 9 | 0 | 14.2 | 3.5 |  | 17.7 | 17.7 | 0.80226 | 0 | 13.0076 | 13.6197 | 11.2136 | 68.7864 | 0.198 | 7.42 | 6.42 | 86.698 | 453.18 | 456.96 | 2183.61 | 1959.1658 | 10.2786 | 81.0272 | 1208.0629 | 92.8234 | 88 | 67 | 9.7 | 8.5 | 9.2 | 17.7 | 17.7 | 0.43996 | 0.48023 | 13.0769 | 13.6922 | 5.7386 | 62.0614 | 0.22062 | 6.42 | NA | 64.428 | 456.96 | 890.01 | 819.6254 | 7.9083 | 85.9007 | 638.2927 | 89.9062 | 67 | 42 | 6.7 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.0235 | 38.7765 | 0.23263 | NA | NA | 156.1 | 890.01 | 1392.52 | 1226.8867 | 11.8945 | 65.8395 | 1058.4484 | 85.252 | 154 | 90 | 10.6 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 18.6368 | 92.7632 | 0.28057 | NA | 7.66 | 74.767 | 1392.52 | 2183.61 | 2484.3725 | -13.7736 | 83.6382 | 1938.4462 | 96.1429 | SDS-CDBAA | mg/L | BMRL | 5.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 2.6446 | 3.0162 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.5 | 3.9 | --- | 9.8684 | --- | 35.8974 | 6.8842 | 63.685 | SUVA | L/(mg*m) | 3.8411 | 2.7663 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 3.0508 | 3.1403 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.1 | 4.2 | --- | 15.225 | --- | 50 | 9.7125 | 78.3784 | SUVA | L/(mg*m) | 2.3077 | 3.5931 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.68966 | 3.7593 | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1997-10-24 | 12:20 | 1812.04 | 24.4444 | 88 | 90 | 8.8667 | 0 | 14.1 | 3.5 |  | 17.6 | 17.6 | 0.80114 | 0 | 12.916 | 13.5238 | 10.9531 | 69.1803 | 0.19549 | 7.4 | 6.4 | 86.028 | 448.2 | 449.4 | 2230.8 | 1913.2701 | 14.2339 | 80.8571 | 1181.335 | 92.7177 | 88 | 68 | 9.5 | 8.5 | 9.1 | 17.6 | 17.6 | 0.43669 | 0.48295 | 13.0769 | 13.6922 | 5.6909 | 62.8091 | 0.218 | 6.4 | NA | 61.478 | 449.4 | 881.1 | 811.7447 | 7.8714 | 86.32 | 630.5724 | 90.2504 | 68 | 42 | 6.5 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 8.9053 | 39.5947 | 0.22783 | NA | NA | 156.8 | 881.1 | 1378.88 | 1213.5656 | 11.989 | 65.109 | 1047.3328 | 85.0286 | 152 | 90 | 10.6 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 18.2382 | 92.1618 | 0.27266 | NA | 7.62 | 76.153 | 1378.88 | 2230.8 | 2421.0616 | -8.5289 | 83.0545 | 1899.9708 | 95.9919 | SDS-DCBAA | mg/L | 2.5 | 36 | --- | 178.8158 | --- | 93.0556 | 107.4079 | 97.6724 | [8 empty] | SDS-DCBAA | mg/L | 4.5 | 30 | --- | 138.7105 | --- | 85 | 84.3553 | 94.6654 | [8 empty] | SDS-DCBAA | mg/L | 2.4 | 28 | --- | 118.7636 | --- | 91.4286 | 73.3818 | 96.7294 | [8 empty] | SDS-DCBAA | mg/L | 3.8 | 34 | --- | 192.55 | --- | 88.8235 | 113.275 | 96.6453 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1997-10-24 | 8:40 | 1820.55 | 24.4444 | 88 | 88 | 8.9667 | 0 | 14.6 | 3.5 |  | 18.1 | 18.1 | 0.80663 | 0 | 13.374 | 14.0033 | 11.5812 | 67.4521 | 0.2076 | 7.47 | 5.72 | 91.723 | 449.03 | 467.04 | 2333.76 | 2032.6481 | 12.9024 | 80.3608 | 1249.844 | 92.6612 | 88 | 68 | 9.5 | 8.9 | 9.2 | 18.1 | 18.1 | 0.4465 | 0.49171 | 13.6923 | 14.3366 | 5.9079 | 62.5921 | 0.22905 | 5.72 | NA | 68.853 | 467.04 | 906.84 | 852.2426 | 6.0206 | 85.2576 | 659.6413 | 89.5621 | 68 | 42 | 6.8 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.2304 | 38.9696 | 0.23148 | NA | NA | 156.1 | 906.84 | 1438.4 | 1251.442 | 12.9976 | 66.5767 | 1079.141 | 85.5348 | 152 | 88 | 10.6 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 19.278 | 90.122 | 0.28879 | NA | 6.86 | 75.306 | 1438.4 | 2333.76 | 2567.8207 | -10.0293 | 83.8759 | 2003.1104 | 96.2405 | SDS-HAA5 | mg/L | 5.7 | 147.5 | --- | 752.0158 | --- | 96.1356 | 449.7579 | 98.7327 | [8 empty] | SDS-HAA5 | mg/L | 11.5 | 191.6 | --- | 959.3947 | --- | 93.9979 | 575.4974 | 98.0017 | [8 empty] | SDS-HAA5 | mg/L | 5.1 | 124.5 | --- | 547.8273 | --- | 95.9036 | 336.1636 | 98.4829 | [8 empty] | SDS-HAA5 | mg/L | 6.5 | 176.4 | --- | 1068.375 | --- | 96.3152 | 622.3875 | 98.9556 | [8 empty] | SDS-HAA5 | mg/L | 1.1 | 62.2 | --- | 437.5286 | --- | 98.2315 | 249.8643 | 99.5598 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Stage 3 -- General Information |  | maximum system recycle flow rates. | [6 empty] | 1998-10-24 | 23:35 | 1835.35 | 24.4444 | 88 | 88 | 8.8667 | 0 | 14.65 | 3.5 |  | 18.15 | 18.15 | 0.80716 | 0 | 13.4198 | 14.0513 | 11.9808 | 67.1525 | 0.20924 | 7.51 | 5.76 | 88.909 | 450.69 | 476.28 | 2277.99 | 2097.7043 | 7.9142 | 81.3326 | 1286.9922 | 93.0917 | 88 | 66 | 9.5 | 8.95 | 9.2 | 18.15 | 18.15 | 0.44732 | 0.49311 | 13.7692 | 14.4171 | 6.1192 | 61.3808 | 0.23488 | 5.76 | NA | 64.605 | 476.28 | 924.66 | 876.7682 | 5.1794 | 86.4355 | 676.5241 | 90.4505 | 66 | 40 | 6.5 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.4185 | 37.0815 | 0.24327 | NA | NA | 161 | 924.66 | 1421.04 | 1281.0347 | 9.8523 | 66.1964 | 1102.8473 | 85.4014 | 152 | 88 | 10.6 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 19.0423 | 90.3577 | 0.28804 | NA | 7.43 | 74.613 | 1421.04 | 2277.99 | 2536.6509 | -11.3548 | 84.3342 | 1978.8455 | 96.2295 | SDS-HAA6 | mg/L | 7.4 | 160.5 | --- | 813.1895 | --- | 95.3894 | 486.8447 | 98.48 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 14.6 | 204.6 | --- | 1014.6 | --- | 92.8641 | 609.6 | 97.605 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 6.7 | 136.5 | --- | 596.7 | --- | 95.0916 | 366.6 | 98.1724 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.9 | 189.4 | --- | 1137.025 | --- | 95.301 | 663.2125 | 98.658 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 1.1 | 68.9 | --- | 485.3857 | --- | 98.4035 | 277.1429 | 99.6031 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Stage 3 Operating Parameters During Sample Collection
|  | Membrane manufacturer | Fluid Systems | [7 empty] | 1998-10-25 | 8:05 | 1843.83 | 24.4444 | 88 | 90 | 8.8667 | 0 | 14.6 | 3.5 |  | 18.1 | 18.1 | 0.80663 | 0 | 13.374 | 14.0033 | 11.5 | 68.6334 | 0.20403 | 7.38 | 5.8 | 87.636 | 444.88 | 460.32 | 2346.63 | 2014.9447 | 14.1345 | 80.9619 | 1237.6323 | 92.9191 | 88 | 68 | 9.5 | 8.9 | 9.2 | 18.1 | 18.1 | 0.4465 | 0.49171 | 13.6923 | 14.3366 | 5.8441 | 62.6559 | 0.22881 | 5.8 | NA | 66.434 | 460.32 | 912.78 | 841.3619 | 7.8242 | 85.5679 | 650.8409 | 89.7926 | 68 | 40 | 6.5 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.2604 | 38.2396 | 0.2359 | NA | NA | 159.6 | 912.78 | 1433.44 | 1258.502 | 12.2041 | 65.3285 | 1085.641 | 85.299 | 152 | 90 | 10.6 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 19.1992 | 91.2008 | 0.28538 | NA | 7 | 75.922 | 1433.44 | 2346.63 | 2558.2406 | -9.0176 | 83.5067 | 1995.8403 | 96.196 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.44 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.45 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.37 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.38 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal)
|  | Membrane trade name | TFC-S | Summary of the Stage and System Flow Rates | [6 empty] | 1997-10-25 | 16:40 | 1852.4 | 24.4444 | 88 | 88 | 8.5667 | 0 | 14.4 | 3.5 |  | 17.9 | 17.9 | 0.80447 | 0 | 13.1908 | 13.8115 | 11.0856 | 68.3477 | 0.20208 | 7.42 | 6.69 | 90.986 | 454.84 | 453.6 | 2285.14 | 1945.4976 | 14.8631 | 79.9414 | 1199.5488 | 92.415 | 88 | 66 | 9.5 | 8.7 | 9.2 | 17.9 | 17.9 | 0.44323 | 0.48603 | 13.3846 | 14.0144 | 5.7214 | 61.7786 | 0.22685 | 6.69 | NA | 65.136 | 453.6 | 896.94 | 820.9518 | 8.4719 | 85.6402 | 637.2759 | 89.779 | 66 | 42 | 6.2 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | 9.1173 | 38.6827 | 0.2332 | NA | NA | 155.4 | 896.94 | 1440.88 | 1237.319 | 14.1275 | 65.7407 | 1067.1295 | 85.4376 | 154 | 88 | 10 | 2.9 | 3.5 | 6.4 | 6.4 | 0.66792 | 0.45312 | 24.8571 | 26.0268 | 19.3131 | 91.6869 | 0.28387 | NA | 7.02 | 75.306 | 1440.88 | 2285.14 | 2572.3556 | -12.5688 | 83.3981 | 2006.6178 | 96.2471 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.8 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.9 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.3 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.8 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm)
|  | Membrane element model number | SC 2540S | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.2647 | [5 empty] | 1997-10-25 | 23:30 | 1859.54 | 24.4444 | 88 | 88 | 8.5667 | 0 | 14.3 | 3.5 |  | 17.8 | 17.8 | 0.80337 | 0 | 13.0992 | 13.7156 | 11.0839 | 68.3495 | 0.20067 | 7.39 | 6.62 | 90.182 | 447.37 | 454.44 | 2318.03 | 1942.6941 | 16.192 | 80.1554 | 1198.5671 | 92.4758 | 88 | 66 | 9.3 | 8.8 | 9 | 17.8 | 17.8 | 0.43833 | 0.49438 | 13.5385 | 14.1755 | 5.7682 | 61.9318 | 0.22889 | 6.62 | NA | 67.024 | 454.44 | 908.82 | 833.2468 | 8.3155 | 85.2513 | 643.8434 | 89.59 | 66 | 40 | 6.4 | 2.7 | 6 | 8.7 | 8.7 | 0.48085 | 0.31034 | 8.3077 | 8.6986 | 9.2637 | 37.3363 | 0.23298 | NA | NA | 152.6 | 908.82 | 1435.92 | 1249.119 | 13.0092 | 66.4202 | 1078.9695 | 85.8569 | 152 | 88 | 10 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.054 | 90.946 | 0.27631 | NA | 7.16 | 74.921 | 1435.92 | 2318.03 | 2524.7192 | -8.9166 | 83.5136 | 1980.3196 | 96.2167 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 6.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 6.4 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 6.15 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.7 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.2 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm)
|  | Molecular weight cutoff (Daltons) | 300 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | [5 empty] | 1998-10-26 | 7:50 | 1867.54 | 24.4444 | 90 | 89 | 8.4667 | 0 | 14.3 | 3.5 |  | 17.8 | 17.8 | 0.80337 | 0 | 13.0992 | 13.7156 | 11.508 | 69.5253 | 0.19728 | 7.28 | 5.76 | 88.842 | 449.86 | 467.04 | 2330.9 | 2012.249 | 13.6707 | 80.9776 | 1239.6445 | 92.8333 | 90 | 68 | 9.2 | 8.7 | 9.1 | 17.8 | 17.8 | 0.43996 | 0.48876 | 13.3846 | 14.0144 | 5.9071 | 63.8929 | 0.21934 | 5.76 | NA | 67.378 | 467.04 | 910.8 | 849.1344 | 6.7705 | 85.5734 | 658.0872 | 89.7615 | 68 | 40 | 6.2 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.2475 | 38.5525 | 0.23399 | NA | NA | 161 | 910.8 | 1443.36 | 1260.7067 | 12.6547 | 65.5276 | 1085.7533 | 85.1716 | 152 | 89 | 10 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 19.1678 | 91.3322 | 0.27514 | NA | 7.21 | 74.228 | 1443.36 | 2330.9 | 2538.6656 | -8.9135 | 84.1067 | 1991.0128 | 96.2718 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.5147 | [5 empty] | 1997-10-26 | 22:00 | 1882.86 | 24.4444 | 88 | 88 | 8.6333 | 0 | 14.55 | 3.5 |  | 18.05 | 18.05 | 0.80609 | 0 | 13.3282 | 13.9554 | 12.1423 | 67.2243 | 0.20759 | 7.52 | 5.8 | 96.145 | 470.61 | 490.56 | 2333.76 | 2130.1995 | 8.7224 | 80.401 | 1310.3798 | 92.6628 | 88 | 65 | 9.5 | 8.95 | 9.1 | 18.05 | 18.05 | 0.44405 | 0.49584 | 13.7692 | 14.4171 | 6.2512 | 60.7488 | 0.23732 | 5.8 | NA | 71.508 | 490.56 | 936.54 | 902.7045 | 3.6128 | 85.4232 | 696.6323 | 89.7352 | 65 | 40 | 6.4 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.6427 | 36.4573 | 0.24743 | NA | NA | 154.7 | 936.54 | 1423.52 | 1301.3987 | 8.5788 | 68.4646 | 1118.9693 | 86.1748 | 152 | 88 | 10 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 18.9052 | 91.0948 | 0.27586 | NA | 7.07 | 73.15 | 1423.52 | 2333.76 | 2503.816 | -7.2868 | 85.0885 | 1963.668 | 96.2748 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.5147 | [5 empty] | 1997-10-27 | 9:25 | 1893.16 | 24.4444 | 88 | 88 | 8.5667 | 0 | 14.3 | 3.5 |  | 17.8 | 17.8 | 0.80337 | 0 | 13.0992 | 13.7156 | 11.6342 | 67.7991 | 0.2023 | 7.46 | 6.67 | 93.934 | 455.67 | 476.28 | 2316.6 | 2038.4365 | 12.0074 | 80.2776 | 1257.3583 | 92.5293 | 88 | 66 | 9.5 | 8.7 | 9.1 | 17.8 | 17.8 | 0.43996 | 0.48876 | 13.3846 | 14.0144 | 6.0053 | 61.4947 | 0.2279 | 6.67 | NA | 69.974 | 476.28 | 914.76 | 864.7264 | 5.4696 | 85.3082 | 670.5032 | 89.564 | 66 | 40 | 6.2 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.0208 | 9.4172 | 37.3828 | 0.24131 | NA | NA | 151.2 | 914.76 | 1428.48 | 1271.088 | 11.0181 | 68.254 | 1092.924 | 86.1656 | 154 | 88 | 10 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | 18.9617 | 92.0383 | 0.27303 | NA | 7.14 | 74.074 | 1428.48 | 2316.6 | 2512.0048 | -8.435 | 84.4474 | 1970.2424 | 96.2404 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-12 | CI-s3-12 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-14 | CI-s3-14 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-16 | CI-s3-16 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-18 | CI-s3-18 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-20 | CI-s3-20 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-20 (dup) | CI-s3-20 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | [5 empty] | 1997-10-27 | 14:40 | 1898.35 | 24.4444 | 88 | 90 | 8.4667 | 0 | 14.8 | 3.5 |  | 18.3 | 18.3 | 0.80874 | 0 | 13.5573 | 14.1952 | #VALUE! | #VALUE! | #VALUE! | 7.4 | 5.74 | NA | 430.77 | 463.68 | 2370.94 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 88 | 65 | 9 | 9.2 | 9.1 | 18.3 | 18.3 | 0.44814 | 0.50273 | 14.1538 | 14.8198 | #VALUE! | #VALUE! | #VALUE! | 5.74 | NA | NA | 463.68 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 65 | 40 | 6.4 | 2.8 | 6.1 | 8.9 | 8.9 | 0.49066 | 0.31461 | 8.6154 | 9.0208 | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | 1423.52 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 152 | 90 | 10 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.1293 | #VALUE! | #VALUE! | #VALUE! | NA | 6.91 | NA | 1423.52 | 2370.94 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Qp/QT (THM4), % | 36.3511 | 71.854 |  | Qp/QT (HAA5), % | 65.9379 | 84.9788 |  |  |  | Sampling date | MM/DD/YY | 1997-10-08 | 1997-10-08 | --- | --- | --- | --- | Qp/QT (THM4), % | 61.6616 | 83.0864 |  | Qp/QT (HAA5), % | 76.402 | 91.3937 |  |  |  | Sampling date | MM/DD/YY | 1997-10-22 | 1997-10-22 | --- | --- | --- | --- | Qp/QT (THM4), % | 18.1524 | 61.1986 |  | Qp/QT (HAA5), % | 59.0452 | 81.6583 |  |  |  | Sampling date | MM/DD/YY | 1997-11-05 | 1997-11-05 | --- | --- | --- | --- | Qp/QT (THM4), % | 51.0526 | 79.7608 |  | Qp/QT (HAA5), % | 72.0424 | 87.9341 |  |  |  | Sampling date | MM/DD/YY | 1997-11-19 | 1997-11-19 | --- | --- | --- | --- | Qp/QT (THM4), % | -24.9292 | 38.8102 |  | Qp/QT (HAA5), % | 13.4206 | 57.6105 |  |  |  | Sampling date | MM/DD/YY | 1998-01-14 | 1998-01-14 | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.6397 | [5 empty] | 1997-10-28 | 14:25 | 1921.64 | 24.4444 | 88 | 90 | 8.5333 | 0 | 14.65 | 3.55 |  | 18.2 | 18.2 | 0.80495 | 0 | 13.4198 | 14.0513 | 11.3594 | 69.1073 | 0.20333 | 7.39 | 5.74 | 91.187 | 400.06 | 462 | 2236.52 | 1992.2565 | 10.9216 | 80.2626 | 1227.1282 | 92.5691 | 88 | 65 | 9.2 | 9.05 | 9.15 | 18.2 | 18.2 | 0.44732 | 0.49725 | 13.9231 | 14.5782 | 5.8422 | 61.4578 | 0.23721 | 5.74 | NA | 71.095 | 462 | 903.87 | 848.6328 | 6.1112 | 84.6115 | 655.3164 | 89.151 | 65 | 40 | 6.4 | 2.7 | 6.1 | 8.8 | 8.8 | 0.48739 | 0.30682 | 8.3077 | 8.6986 | 9.5797 | 36.5203 | 0.23819 | NA | NA | 119.49 | 903.87 | 1364 | 1251.0546 | 8.2805 | 74.1364 | 1077.4623 | 88.9101 | 154 | 90 | 10 | 2.9 | 3.55 | 6.45 | 6.45 | 0.67466 | 0.44961 | 24.8571 | 26.0268 | 18.1203 | 93.8797 | 0.27724 | NA | 6.97 | 77.462 | 1364 | 2236.52 | 2414.9747 | -7.9791 | 83.2333 | 1889.4874 | 95.9004 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 41.9989 | 22.6915 |  |  |  | Sampling time | hh:mm | 7:30 | 7:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 47.2317 | 22.0412 |  |  |  | Sampling time | hh:mm | 7:00 | 7:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 37.8009 | 18.8894 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 45.6789 | 25.7507 |  |  |  | Sampling time | hh:mm | 7:30 | 7:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 50.34 | 25.3816 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 4.6397 | [5 empty] | 1997-10-28 | 23:15 | 1930.32 | 23.8889 | 88 | 88 | 8.8667 | 0 | 14.55 | 3.5 |  | 18.05 | 18.05 | 0.80609 | 0 | 13.3282 | 14.1865 | 11.0783 | 68.0551 | 0.20846 | 7.43 | 5.79 | 99.629 | 411.68 | 459.48 | 2282.28 | 1955.432 | 14.3211 | 78.317 | 1207.456 | 91.7489 | 88 | 66 | 9.8 | 8.95 | 9.1 | 18.05 | 18.05 | 0.44405 | 0.49584 | 13.7692 | 14.6558 | 5.8052 | 61.3948 | 0.23871 | 5.79 | NA | 70.328 | 459.48 | 888.03 | 842.2174 | 5.1589 | 84.694 | 650.8487 | 89.1944 | 66 | 40 | 6.8 | 2.8 | 6 | 8.8 | 8.8 | 0.48412 | 0.31818 | 8.6154 | 9.1701 | 9.2827 | 36.9173 | 0.2484 | NA | NA | 135.38 | 888.03 | 1396.24 | 1239.2667 | 11.2426 | 70.5363 | 1063.6483 | 87.2721 | 152 | 88 | 10 | 2.8 | 3.5 | 6.3 | 6.3 | 0.66117 | 0.44444 | 24 | 25.5454 | 18.4866 | 91.5134 | 0.27914 | NA | 7.04 | 75.768 | 1396.24 | 2282.28 | 2452.6176 | -7.4635 | 83.5101 | 1924.4288 | 96.0628 | SDS-HAA5b, mg/L | 95.9542 | 45.611 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 1508 | 1508 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 80.5474 | 41.9615 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 1770.8 | 1770.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 102.8261 | 51.4289 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 2094 | 2094 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 89.6616 | 40.8865 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 1962.6 | 1962.6 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 38.487 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 2405 | 2405 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Stage 3 -- Design Parameters |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | [5 empty] | 1997-10-29 | 15:30 | 1946.8 | 24.4444 | 88 | 78 | 8.5333 | 0 | 14.7 | 3.9 |  | 18.6 | 18.6 | 0.79032 | 0 | 13.4656 | 14.0993 | 11.2461 | 63.2206 | 0.22302 | 7.37 | 5.82 | 91.455 | 461.48 | 481.32 | 2368.08 | 1950.8112 | 17.6206 | 80.9991 | 1216.0656 | 92.4794 | 88 | 66 | 9.4 | 9.2 | 9.4 | 18.6 | 18.6 | 0.45795 | 0.49462 | 14.1538 | 14.8198 | 6.1581 | 61.4419 | 0.2412 | 5.82 | NA | 67.85 | 481.32 | 943.47 | 885.9928 | 6.0921 | 85.9033 | 683.6564 | 90.0754 | 66 | 40 | 6.4 | 2.8 | 6.3 | 9.1 | 9.1 | 0.50375 | 0.30769 | 8.6154 | 9.0208 | 9.6833 | 36.9167 | 0.24435 | NA | NA | 151.2 | 943.47 | 1490.48 | 1295.59 | 13.0757 | 68.5864 | 1119.53 | 86.4943 | 150 | 78 | 9.8 | 2.7 | 3.9 | 6.6 | 6.6 | 0.7084 | 0.40909 | 23.1429 | 24.2318 | 19.0629 | 85.1371 | 0.28462 | NA | 7.1 | 74.382 | 1490.48 | 2368.08 | 2470.8555 | -4.34 | 84.5462 | 1980.6678 | 96.2446 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.76 | 6.78 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 485.422 | 251.0353 |  | SDS-TOXb, mg Cl- /L | 324.1621 | 160.1532 |  |  |  | pH | --- | 5.78 | 6.75 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 604.7487 | 307.7297 |  | SDS-TOXb, mg Cl- /L | 322.5879 | 166.5578 |  |  |  | pH | --- | 5.94 | 6.96 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 419.3579 | 210.9368 |  | SDS-TOXb, mg Cl- /L | 266.9723 | 151.5986 |  |  |  | pH | --- | 6.49 | 7.53 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.98 | 6.93 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- |  |  | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 2.8897 | [5 empty] | 1997-10-29 | 23:20 | 1954.47 | 23.8889 | 88 | 78 | 8.8667 | 0 | 14.45 | 3.9 |  | 18.35 | 18.35 | 0.78747 | 0 | 13.2366 | 14.0889 | 10.7658 | 63.3675 | 0.22234 | 7.38 | 5.84 | 94.671 | 446.54 | 472.08 | 2320.89 | 1870.4287 | 19.409 | 79.946 | 1171.2544 | 91.9171 | 88 | 66 | 9.6 | 8.95 | 9.4 | 18.35 | 18.35 | 0.45386 | 0.48774 | 13.7692 | 14.6558 | 5.9458 | 61.4542 | 0.23848 | 5.84 | NA | 69.266 | 472.08 | 916.74 | 855.6104 | 6.6682 | 85.3275 | 663.8452 | 89.5659 | 66 | 40 | 7 | 2.8 | 6.2 | 9 | 9 | 0.49721 | 0.31111 | 8.6154 | 9.1701 | 9.4475 | 36.5525 | 0.25088 | NA | NA | 146.02 | 916.74 | 1480.56 | 1264.8071 | 14.5724 | 69.0688 | 1090.7735 | 86.6132 | 150 | 78 | 10 | 2.7 | 3.9 | 6.6 | 6.6 | 0.7084 | 0.40909 | 23.1429 | 24.633 | 18.9158 | 85.0842 | 0.28951 | NA | 7.09 | 75.383 | 1480.56 | 2320.89 | 2453.3748 | -5.7084 | 84.0317 | 1966.9674 | 96.1676 | SDS-CDb, mg/L | 4.9115 | 3.2819 |  | SDS-CDb, mg/L | 3.5534 | 2.6795 |  |  |  | Temperature | oC | NA | 26 | --- | --- | --- | --- | SDS-CDb, mg/L | 5.6846 | 3.6814 |  | SDS-CDb, mg/L | 4.3064 | 2.9047 |  |  |  | Temperature | oC | NA | 22.6 | --- | --- | --- | --- | SDS-CDb, mg/L | 10.1981 | 6.2809 |  | SDS-CDb, mg/L | 6.4769 | 4.4191 |  |  |  | Temperature | oC | NA | 25 | --- | --- | --- | --- | SDS-CDb, mg/L | 6.6617 | 3.9803 |  | SDS-CDb, mg/L | 4.7012 | 3.217 |  |  |  | Temperature | oC | NA | 24.5 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 7.0744 |  | SDS-CDb, mg/L | 9.0472 | 5.6137 |  |  |  | Temperature | oC | NA | 25.8 | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC |  |  | --- | --- | --- | ---
|  | Active membrane area of membrane element used, A (ft2) | 28 | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1997-10-30 | 10:00 | 1965.07 | 24.4444 | 90 | 80 | 8.4 | 0 | 14.1 | 3.8 |  | 17.9 | 17.9 | 0.78771 | 0 | 12.916 | 13.5238 | 10.8652 | 65.7348 | 0.20573 | 7.34 | 6.59 | 94.068 | 448.2 | 474.6 | 2348.06 | 1886.574 | 19.6539 | 80.1795 | 1180.587 | 92.0321 | 90 | 68 | 9.2 | 8.7 | 9.2 | 17.9 | 17.9 | 0.44323 | 0.48603 | 13.3846 | 14.0144 | 5.9603 | 63.8397 | 0.21953 | 6.59 | NA | 69.915 | 474.6 | 923.67 | 857.2912 | 7.1864 | 85.2686 | 665.9456 | 89.5014 | 68 | 40 | 6.2 | 2.8 | 6.2 | 9 | 9 | 0.49721 | 0.31111 | 8.6154 | 9.0208 | 9.5127 | 38.2873 | 0.23561 | NA | NA | 147.63 | 923.67 | 1473.12 | 1274.1397 | 13.5074 | 68.8938 | 1098.9048 | 86.5657 | 150 | 80 | 9.8 | 2.6 | 3.8 | 6.4 | 6.4 | 0.68816 | 0.40625 | 22.2857 | 23.3343 | 18.7488 | 86.4512 | 0.26991 | NA | 7.25 | 76.153 | 1473.12 | 2348.06 | 2428.9395 | -3.4445 | 83.9543 | 1951.0298 | 96.0968 | TOCb, mg/L | 7.1031 | 3.5705 |  | TOCb, mg/L | 4.1592 | 2.2646 |  |  |  | Alkalinity | mg/L as CaCO3 | 23.37 | 322.9 | 562.524 | 84.0063 | 442.712 | 94.7212 | TOCb, mg/L | 6.531 | 3.5016 |  | TOCb, mg/L | 4.4468 | 2.3269 |  |  |  | Alkalinity | mg/L as CaCO3 | 20.82 | 298.55 | 528.6691 | 84.2951 | 413.6096 | 94.9663 | TOCb, mg/L | 9.3404 | 4.8119 |  | TOCb, mg/L | 5.0384 | 2.6595 |  |  |  | Alkalinity | mg/L as CaCO3 | 23 | 378 | 590.0779 | 85.8025 | 484.039 | 95.2483 | TOCb, mg/L | 6.1883 | 3.0045 |  | TOCb, mg/L | 3.8605 | 2.0981 |  |  |  | Alkalinity | mg/L as CaCO3 | 47 | 639 | 1006.4483 | 79.0179 | 822.7241 | 94.2873 | TOCb, mg/L | NA | 4.116 |  | TOCb, mg/L | 5.6952 | 2.9466 |  |  |  | Alkalinity | mg/L as CaCO3 | 30 | 383 | 641.8667 | 74.1379 | 512.4333 | 94.1456 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Design flux, FW (gfd) | 41.43 | System concentrate waste flow rate, QW-sys (gpm) | 2.8897 | [5 empty] | 1997-10-30 | 17:45 | 1972.9 | 24.4444 | 88 | 78 | 8.5333 | 0 | 14.8 | 3.8 |  | 18.6 | 18.6 | 0.7957 | 0 | 13.5573 | 14.1952 | 11.375 | 63.0917 | 0.22499 | 7.42 | 5.84 | 92.862 | 444.88 | 478.8 | 2365.22 | 1981.9269 | 16.2054 | 80.6053 | 1230.3635 | 92.4525 | 88 | 68 | 9.2 | 9.2 | 9.4 | 18.6 | 18.6 | 0.45795 | 0.49462 | 14.1538 | 14.8198 | 6.11 | 62.69 | 0.2364 | 5.84 | NA | 68.558 | 478.8 | 904.86 | 880.3134 | 2.7127 | 85.6813 | 679.5567 | 89.9114 | 68 | 40 | 6.4 | 2.8 | 6.2 | 9 | 9 | 0.49721 | 0.31111 | 8.6154 | 9.0208 | 9.2693 | 38.3307 | 0.23534 | NA | NA | 148.68 | 904.86 | 1478.08 | 1246.3606 | 15.6771 | 68.9474 | 1075.6103 | 86.1772 | 150 | 78 | 10 | 2.8 | 3.8 | 6.6 | 6.6 | 0.70165 | 0.42424 | 24 | 25.1293 | 19.2001 | 84.7999 | 0.29634 | NA | 7.18 | 74.998 | 1478.08 | 2365.22 | 2511.9299 | -6.2028 | 84.3363 | 1995.0049 | 96.2407 | UV254 b, cm-1 | 0.22522 | 0.11019 |  | UV254 b, cm-1 | 0.12936 | 0.067669 |  |  |  | Total dissolved solids | mg/L | 73 | 844 | 1460.8 | 81.6583 | 1152.4 | 93.6654 | UV254 b, cm-1 | 0.24311 | 0.12849 |  | UV254 b, cm-1 | 0.16425 | 0.084044 |  |  |  | Total dissolved solids | mg/L | 75 | 835 | 1464.7143 | 80.5195 | 1149.8571 | 93.4775 | UV254 b, cm-1 | 0.33065 | 0.17569 |  | UV254 b, cm-1 | 0.18344 | 0.10203 |  |  |  | Total dissolved solids | mg/L | 71 | 837 | 1294.6104 | 81.701 | 1065.8052 | 93.3384 | UV254 b, cm-1 | 0.20355 | 0.095897 |  | UV254 b, cm-1 | 0.12484 | 0.065247 |  |  |  | Total dissolved solids | mg/L | 114 | 887 | 1366.7931 | 70 | 1126.8966 | 89.8837 | UV254 b, cm-1 | NA | 0.13327 |  | UV254 b, cm-1 | 0.18609 | 0.09417 |  |  |  | Total dissolved solids | mg/L | 90.5 | 950 | 1580.3 | 71.8944 | 1265.15 | 92.8467 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Net driving pressure at the design flux, NDP (psi) | 97 | System permeate flow rate, Qp-sys (gpm) | 16.375 | [5 empty] | 1997-10-31 | 8:45 | 1987.82 | 24.4444 | 90 | 80 | 8.5 | 0 | 14.1 | 3.6 |  | 17.7 | 17.7 | 0.79661 | 0 | 12.916 | 13.5238 | 10.9999 | 65.5001 | 0.20647 | 7.4 | 6.6 | 93.532 | 447.37 | 465.36 | 2270.84 | 1921.6863 | 15.3755 | 79.9012 | 1193.5232 | 92.1634 | 90 | 68 | 9.2 | 8.9 | 8.8 | 17.7 | 17.7 | 0.43342 | 0.50282 | 13.6923 | 14.3366 | 5.9835 | 63.8165 | 0.22465 | 6.6 | NA | 67.968 | 465.36 | 914.76 | 867.2678 | 5.1918 | 85.3945 | 666.3139 | 89.7994 | 68 | 40 | 6.8 | 2.6 | 6.2 | 8.8 | 8.8 | 0.49066 | 0.29545 | 8 | 8.3764 | 9.2408 | 37.9592 | 0.22067 | NA | NA | 150.85 | 914.76 | 1494.2 | 1235.1094 | 17.3398 | 67.5842 | 1074.9347 | 85.9666 | 150 | 80 | 9.5 | 2.6 | 3.6 | 6.2 | 6.2 | 0.66117 | 0.41935 | 22.2857 | 23.3343 | 19.3274 | 86.1726 | 0.27079 | NA | 7.01 | 74.228 | 1494.2 | 2270.84 | 2519.7353 | -10.9605 | 84.0493 | 2006.9677 | 96.3015 | Bromideb, mg/L | 127.602 | 86.0174 |  | Bromideb, mg/L | 92.9469 | 70.6443 |  |  |  | Total hardness | mg/L as CaCO3 | 15.2 | 647 | 1152.44 | 93.5319 | 899.72 | 98.3106 | Bromideb, mg/L | 91.1052 | 69.2519 |  | Bromideb, mg/L | 76.07 | 60.7785 |  |  |  | Total hardness | mg/L as CaCO3 | 13.6 | 568 | 1027.36 | 93.9177 | 797.68 | 98.2951 | Bromideb, mg/L | 144.7615 | 95.3168 |  | Bromideb, mg/L | 97.7903 | 71.816 |  |  |  | Total hardness | mg/L as CaCO3 | 16 | 608 | 961.6623 | 93.1624 | 784.8312 | 97.9613 | Bromideb, mg/L | 119.6759 | 106.6109 |  | Bromideb, mg/L | 110.1235 | 102.8912 |  |  |  | Total hardness | mg/L as CaCO3 | 32 | 665 | 1057.8966 | 86.0262 | 861.4483 | 96.2853 | Bromideb, mg/L | NA | 54.3258 |  | Bromideb, mg/L | 69.8134 | 42.8576 |  |  |  | Total hardness | mg/L as CaCO3 | 23 | 700 | 1196.4667 | 87.766 | 948.2333 | 97.5744 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.427 | System feed flow rate, QF-sys (gpm) | 19.2647 | [5 empty] | 1997-10-31 | 23:05 | 2002.19 | 24.4444 | 90 | 78 | 8.8 | 0 | 14.55 | 3.8 |  | 18.35 | 18.35 | 0.79292 | 0 | 13.3282 | 13.9554 | 11.0462 | 64.1538 | 0.21753 | 7.42 | 5.83 | 91.388 | 449.86 | 470.4 | 2336.62 | 1921.617 | 17.7608 | 80.5723 | 1196.0085 | 92.3589 | 90 | 68 | 9.6 | 8.95 | 9.4 | 18.35 | 18.35 | 0.45386 | 0.48774 | 13.7692 | 14.4171 | 5.9419 | 63.4581 | 0.22719 | 5.83 | NA | 67.85 | 470.4 | 936.54 | 853.679 | 8.8476 | 85.5761 | 662.0395 | 89.7514 | 68 | 40 | 7 | 2.8 | 6.3 | 9.1 | 9.1 | 0.50375 | 0.30769 | 8.6154 | 9.0208 | 9.5729 | 37.4271 | 0.24102 | NA | NA | 153.3 | 936.54 | 1507.84 | 1284.6467 | 14.8022 | 67.4107 | 1110.5933 | 86.1966 | 150 | 78 | 9.8 | 2.8 | 3.8 | 6.6 | 6.6 | 0.70165 | 0.42424 | 24 | 25.1293 | 19.6094 | 84.5906 | 0.29707 | NA | 7.08 | 74.844 | 1507.84 | 2336.62 | 2563.7318 | -9.7197 | 84.0893 | 2035.7859 | 96.3236 | Alkb, mg/L CaCO3 | 106.0684 | 66.9512 |  | Alkb, mg/L CaCO3 | 73.4696 | 52.4903 |  |  |  | Calcium hardness | mg/L as CaCO3 | 14 | 535 | 951.8 | 93.1373 | 743.4 | 98.1168 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 12 | 500 | 904.3429 | 93.9455 | 702.1714 | 98.291 | Alkb, mg/L CaCO3 | 139.3096 | 85.5018 |  | Alkb, mg/L CaCO3 | 88.1935 | 59.9271 |  |  |  | Calcium hardness | mg/L as CaCO3 | 13 | 520 | 822.8831 | 93.5961 | 671.4416 | 98.0639 | Alkb, mg/L CaCO3 | 132.6158 | 81.2282 |  | Alkb, mg/L CaCO3 | 95.0441 | 66.598 |  |  |  | Calcium hardness | mg/L as CaCO3 | 24 | 587 | 936.4483 | 87.9397 | 761.7241 | 96.8493 | Alkb, mg/L CaCO3 | NA | 79.1303 |  | Alkb, mg/L CaCO3 | 103.2504 | 61.27 |  |  |  | Calcium hardness | mg/L as CaCO3 | 22 | 668 | 1141.7333 | 87.7778 | 904.8667 | 97.5687 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Temperature at which the MTCW was determined, ToC (oC) | 25 | [7 empty] | 1997-11-01 | 23:30 | 2026.72 | 24.4444 | 90 | 78 | 8.7667 | 0 | 14.8 | 3.9 |  | 18.7 | 18.7 | 0.79144 | 0 | 13.5573 | 14.1952 | 10.7323 | 64.5011 | 0.22008 | 7.38 | 5.8 | 89.914 | 446.54 | 460.32 | 2339.48 | 1865.9633 | 20.2403 | 80.4671 | 1163.1416 | 92.2697 | 90 | 68 | 9.5 | 9.2 | 9.5 | 18.7 | 18.7 | 0.46122 | 0.49198 | 14.1538 | 14.8198 | 5.7988 | 63.7012 | 0.23265 | 5.8 | NA | 69.62 | 460.32 | 898.92 | 838.6821 | 6.7011 | 84.8757 | 649.5011 | 89.281 | 68 | 40 | 7 | 2.8 | 6.2 | 9 | 9 | 0.49721 | 0.31111 | 8.6154 | 9.0208 | 9.1982 | 37.8018 | 0.23863 | NA | NA | 148.54 | 898.92 | 1483.04 | 1237.8013 | 16.5362 | 67.7311 | 1068.3606 | 86.0965 | 150 | 78 | 9.8 | 2.8 | 3.9 | 6.7 | 6.7 | 0.71514 | 0.41791 | 24 | 25.1293 | 19.1161 | 85.0839 | 0.29535 | NA | 7 | 76.384 | 1483.04 | 2339.48 | 2492.9469 | -6.5599 | 83.4063 | 1987.9934 | 96.1577 | T-Hdb, mg/L CaCO3 | 162.2978 | 91.2919 |  | T-Hdb, mg/L CaCO3 | 103.1241 | 65.0423 |  |  |  | Turbidity | ntu | 0.01 | 0.45 | 0.802 | 83.3333 | 0.626 | 98.4026 | T-Hdb, mg/L CaCO3 | 222.3668 | 221.9383 |  | T-Hdb, mg/L CaCO3 | 222.072 | 221.7721 |  |  |  | Turbidity | ntu | BMRL | 0.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 197.8768 | 112.2148 |  | T-Hdb, mg/L CaCO3 | 116.5 | 71.5 |  |  |  | Turbidity | ntu | 0.01 | 4.94 | 7.8852 | 93.3333 | 6.4126 | 99.8441 | T-Hdb, mg/L CaCO3 | 130.4684 | 75.0617 |  | T-Hdb, mg/L CaCO3 | 89.9582 | 59.2872 |  |  |  | Turbidity | ntu | BMRL | 0.51 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | 122.4108 |  | T-Hdb, mg/L CaCO3 | 165.3191 | 90.6383 |  |  |  | Turbidity | ntu | 0.01 | 14.03 | 24.3113 | 83.3333 | 19.1707 | 99.9478 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum flow rate to the element, QI, max (gpm) | 2.5 | Calculate the Required System Influent Pressure | [6 empty] | 1997-11-01 | 8:30 | 2011.58 | 24.4444 | 90 | 80 | 8.6 | 0 | 14.3 | 3.8 |  | 18.1 | 18.1 | 0.79006 | 0 | 13.0992 | 13.7156 | 10.5283 | 65.8717 | 0.20822 | 7.41 | 5.86 | 89.914 | 444.05 | 455.28 | 2273.7 | 1830.2099 | 19.5052 | 80.2508 | 1142.745 | 92.1318 | 90 | 68 | 9.2 | 8.9 | 9.2 | 18.1 | 18.1 | 0.4465 | 0.49171 | 13.6923 | 14.3366 | 5.7719 | 64.0281 | 0.22391 | 5.86 | NA | 66.257 | 455.28 | 930.6 | 831.6175 | 10.6364 | 85.447 | 643.4487 | 89.7028 | 68 | 40 | 6.8 | 2.6 | 6.2 | 8.8 | 8.8 | 0.49066 | 0.29545 | 8 | 8.3764 | 9.4096 | 37.7904 | 0.22165 | NA | NA | 152.74 | 930.6 | 1510.32 | 1256.7994 | 16.7859 | 66.4514 | 1093.6997 | 86.0346 | 150 | 80 | 9.8 | 2.8 | 3.8 | 6.6 | 6.6 | 0.70165 | 0.42424 | 24 | 25.1293 | 19.6202 | 85.5798 | 0.29364 | NA | 7.2 | 76.538 | 1510.32 | 2273.7 | 2566.7909 | -12.8905 | 83.1888 | 2038.5555 | 96.2455 | Ca-Hdb, mg/L CaCO3 | 140.8218 | 79.1177 |  | Ca-Hdb, mg/L CaCO3 | 89.3999 | 56.3068 |  |  |  | Total organic carbon | mg/L | 0.24 | 28.15 | 50.478 | 97.7612 | 39.314 | 99.3895 | Ca-Hdb, mg/L CaCO3 | 180.8114 | 174.7696 |  | Ca-Hdb, mg/L CaCO3 | 176.6546 | 172.427 |  |  |  | Total organic carbon | mg/L | 0.42 | 41.25 | 75.0806 | 97.2459 | 58.1653 | 99.2779 | Ca-Hdb, mg/L CaCO3 | 171.4149 | 96.5144 |  | Ca-Hdb, mg/L CaCO3 | 100.2613 | 60.9146 |  |  |  | Total organic carbon | mg/L | 0.37 | 26.95 | 42.829 | 96.7111 | 34.8895 | 98.9395 | Ca-Hdb, mg/L CaCO3 | 129.0579 | 89.7278 |  | Ca-Hdb, mg/L CaCO3 | 100.3019 | 78.5303 |  |  |  | Total organic carbon | mg/L | 0.32 | 36.33 | 58.681 | 97.2996 | 47.5055 | 99.3264 | Ca-Hdb, mg/L CaCO3 | NA | 117.1275 |  | Ca-Hdb, mg/L CaCO3 | 158.2586 | 86.671 |  |  |  | Total organic carbon | mg/L | 0.47 | 20.9 | 35.882 | 92.8025 | 28.391 | 98.3445 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 0.5 | Osmotic pressure for stage 13, Dp1 (psi) | 8.9 | [5 empty] | 1997-11-01 | 16:00 | 2019.17 | 24.4444 | 90 | 80 | 8.6 | 0 | 14.3 | 3.8 |  | 18.1 | 18.1 | 0.79006 | 0 | 13.0992 | 13.7156 | 10.999 | 65.401 | 0.20972 | 7.38 | 6.82 | 92.058 | 448.2 | 473.76 | 2325.18 | 1910.1649 | 17.8487 | 80.5686 | 1191.9624 | 92.2768 | 90 | 68 | 9.2 | 8.7 | 9.4 | 18.1 | 18.1 | 0.44978 | 0.48066 | 13.3846 | 14.0144 | 5.9392 | 63.8608 | 0.21945 | 6.82 | NA | 67.732 | 473.76 | 924.66 | 849.5519 | 8.1228 | 85.7033 | 661.6559 | 89.7633 | 68 | 40 | 6.8 | 2.8 | 6.2 | 9 | 9 | 0.49721 | 0.31111 | 8.6154 | 9.0208 | 9.4777 | 37.7223 | 0.23914 | NA | NA | 151.48 | 924.66 | 1505.36 | 1273.8381 | 15.3798 | 68.026 | 1099.249 | 86.2197 | 150 | 80 | 9.8 | 2.8 | 3.8 | 6.6 | 6.6 | 0.70165 | 0.42424 | 24 | 25.1293 | 19.5639 | 85.6361 | 0.29344 | NA | 7.16 | 75.691 | 1505.36 | 2325.18 | 2558.8003 | -10.0474 | 84.0233 | 2032.0802 | 96.2752 | Notes: | [9 empty] | UV254 | cm-1 | 0.003 | 0.832 | 1.4952 | 99.1254 | 1.1636 | 99.7422 | Notes: | [9 empty] | UV254 | cm-1 | 0.008 | 0.858 | 1.5623 | 98.6038 | 1.2101 | 99.3389 | Notes: | [9 empty] | UV254 | cm-1 | 0.005 | 1.04 | 1.6583 | 98.7374 | 1.3492 | 99.6294 | Notes: | [9 empty] | UV254 | cm-1 | 0.008 | 1.209 | 1.9544 | 97.9747 | 1.5817 | 99.4942 | Notes: | [9 empty] | UV254 | cm-1 | 0.005 | 0.709 | 1.2253 | 97.6636 | 0.96713 | 99.483 | Notes: | [9 empty] | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Total width of all membrane envelopes in the element, w (ft) | 6.4 | Osmotic pressure for stage 23, Dp2 (psi) | 13.4 | [5 empty] | 1997-11-07 | 14:10 | 2147.77 | 24.4444 | 86 | 75 | 9.3333 | 0 | 13.55 | 3.85 |  | 17.4 | 17.4 | 0.77874 | 0 | 12.4122 | 12.9963 | 10.0596 | 61.1071 | 0.21268 | 7.58 | 6.77 | 84.889 | 423.3 | 449.4 | 2053.48 | 1732.2894 | 15.6413 | 81.1106 | 1090.8447 | 92.218 | 86 | 65 | 9 | 8.75 | 8.7 | 17.45 | 17.45 | 0.4277 | 0.50143 | 13.4615 | 14.095 | 5.689 | 60.811 | 0.23178 | 6.77 | NA | 70.859 | 449.4 | 911.79 | 830.1165 | 8.9575 | 84.2325 | 639.7583 | 88.9241 | 65 | 39 | 8.5 | 2.5 | 6 | 8.5 | 8.5 | 0.47431 | 0.29412 | 7.6923 | 8.0543 | 9.5863 | 33.9137 | 0.23749 | NA | NA | 118.44 | 911.79 | 1360.28 | 1242.3525 | 8.6694 | 73.6449 | 1077.0712 | 89.0035 | 149 | 75 | 10.5 | 2.3 | 3.85 | 6.15 | 6.15 | 0.67466 | 0.37398 | 19.7143 | 20.6419 | 16.78 | 84.72 | 0.24365 | NA | 6.9 | 68.222 | 1360.28 | 2053.48 | 2132.1588 | -3.8315 | 84.8193 | 1746.2194 | 96.0932 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.25 | 2.9556 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.9048 | 2.08 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.3514 | 3.859 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 2.5 | 3.3278 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.0638 | 3.3923 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  | Feed spacer thickness, T (ft) | 0.00258 | Osmotic pressure for stage 33, Dp3 (psi) | 18.6 | [5 empty] | 1997-11-09 | 24:30 | 2182.12 | 24.4444 | 89 | 80 | 8.6667 | 0 | 13.8 | 3.9 |  | 17.7 | 17.7 | 0.77966 | 0 | 12.6412 | 13.236 | 9.6967 | 66.1366 | 0.20013 | 7.4 | 6.95 | 83.281 | 501.32 | 433.44 | 1993.42 | 1672.4642 | 16.1008 | 80.786 | 1052.9521 | 92.0907 | 89 | 65 | 9 | 9 | 8.7 | 17.7 | 17.7 | 0.43178 | 0.50847 | 13.8462 | 14.4977 | 5.5344 | 62.4656 | 0.23209 | 6.95 | NA | 68.676 | 433.44 | 887.04 | 810.7821 | 8.5969 | 84.1556 | 622.111 | 88.9608 | 65 | 40 | 8 | 2.5 | 6 | 8.5 | 8.5 | 0.47431 | 0.29412 | 7.6923 | 8.0543 | 9.3921 | 35.1079 | 0.22941 | NA | NA | 109.76 | 887.04 | 1388.8 | 1210.9067 | 12.8091 | 74.677 | 1048.9733 | 89.5364 | 150 | 80 | 9 | 2.3 | 3.9 | 6.2 | 6.2 | 0.68141 | 0.37097 | 19.7143 | 20.6419 | 17.0629 | 88.9371 | 0.2321 | NA | 6.86 | 71.071 | 1388.8 | 1993.42 | 2165.9222 | -8.6536 | 83.603 | 1777.3611 | 96.0013 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses due to stage hardware, DPs (psi) | 4 | [5 empty] | 1997-11-09 | 13:30 | 2195.37 | 24.4444 | 86 | 78 | 8.0667 | 0 | 13.4 | 3.9 |  | 17.3 | 17.3 | 0.77457 | 0 | 12.2748 | 12.8524 | 9.8798 | 64.0536 | 0.20065 | 7.46 | 6.64 | 84.219 | 507.96 | 447.72 | 2019.16 | 1696.6722 | 15.9714 | 81.1894 | 1072.1961 | 92.1452 | 86 | 64 | 8.8 | 8.5 | 8.8 | 17.3 | 17.3 | 0.42688 | 0.49133 | 13.0769 | 13.6922 | 5.5931 | 60.6069 | 0.22592 | 6.64 | NA | 70.564 | 447.72 | 922.68 | 812.0184 | 11.9935 | 84.2393 | 629.8692 | 88.797 | 64 | 40 | 7 | 2.5 | 6 | 8.5 | 8.5 | 0.47431 | 0.29412 | 7.6923 | 8.0543 | 9.8101 | 35.1899 | 0.22888 | NA | NA | 110.81 | 922.68 | 1434.68 | 1260.9592 | 12.1087 | 75.2502 | 1091.8196 | 89.8509 | 150 | 78 | 8.4 | 2.4 | 3.9 | 6.3 | 6.3 | 0.68816 | 0.38095 | 20.5714 | 21.5394 | 17.8439 | 87.7561 | 0.24545 | NA | 6.98 | 70.147 | 1434.68 | 2019.16 | 2274.3926 | -12.6405 | 84.3324 | 1854.5363 | 96.2175 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1997-11-09 | 17:45 | 2199.3 | 24.4444 | 86 | 80 | 8.6667 | 0 | 13.5 | 3.9 |  | 17.4 | 17.4 | 0.77586 | 0 | 12.3664 | 12.9483 | 9.9694 | 64.3639 | 0.20117 | 7.44 | 6.88 | 83.482 | 506.3 | 448.56 | 1973.4 | 1712.2915 | 13.2314 | 81.3889 | 1080.4258 | 92.2732 | 86 | 65 | 9 | 8.5 | 8.9 | 17.4 | 17.4 | 0.43015 | 0.48851 | 13.0769 | 13.6922 | 5.5946 | 60.9054 | 0.22481 | 6.88 | NA | 69.915 | 448.56 | 912.78 | 810.1872 | 11.2396 | 84.4135 | 629.3736 | 88.8913 | 65 | 40 | 8 | 2.5 | 6 | 8.5 | 8.5 | 0.47431 | 0.29412 | 7.6923 | 8.0543 | 9.6829 | 34.8171 | 0.23133 | NA | NA | 111.44 | 912.78 | 1432.2 | 1246.6717 | 12.9541 | 75.1561 | 1079.7258 | 89.6789 | 150 | 80 | 9 | 2.5 | 3.9 | 6.4 | 6.4 | 0.6949 | 0.39062 | 21.4286 | 22.4369 | 17.9973 | 88.0027 | 0.25496 | NA | 6.88 | 69.3 | 1432.2 | 1973.4 | 2305.8538 | -16.8468 | 84.5506 | 1869.0269 | 96.2922 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1997-11-10 | 9:55 | 2215.48 | 24.4444 | 88 | 78 | 8.2667 | 0 | 13.75 | 3.9 |  | 17.65 | 17.65 | 0.77904 | 0 | 12.5954 | 13.1881 | 9.9147 | 64.8186 | 0.20346 | 7.47 | 6.64 | 83.817 | 504.64 | 442.68 | 1997.71 | 1707.9021 | 14.507 | 81.066 | 1075.2911 | 92.2052 | 88 | 65 | 9 | 8.65 | 9 | 17.65 | 17.65 | 0.43587 | 0.49008 | 13.3077 | 13.9339 | 5.5216 | 61.9784 | 0.22482 | 6.64 | NA | 69.738 | 442.68 | 924.66 | 801.1187 | 13.3607 | 84.2464 | 621.8994 | 88.7863 | 65 | 40 | 7 | 2.6 | 6 | 8.6 | 8.6 | 0.47758 | 0.30233 | 8 | 8.3764 | 9.9052 | 35.5948 | 0.23533 | NA | NA | 110.53 | 924.66 | 1421.04 | 1277.4497 | 10.1046 | 75.0316 | 1101.0548 | 89.9614 | 150 | 78 | 8.8 | 2.5 | 3.9 | 6.4 | 6.4 | 0.6949 | 0.39062 | 21.4286 | 22.4369 | 17.8367 | 87.3633 | 0.25682 | NA | 6.91 | 70.301 | 1421.04 | 1997.71 | 2286.8983 | -14.476 | 84.1192 | 1853.9692 | 96.2081 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  | Stage 3 -- Additional Information |  | Mechanical pressure losses per stage, Ls (psi) | 22 | [5 empty] | 1997-11-10 | 16:02 | 2221.86 | 24.4444 | 88 | 80 | 8.2 | 0 | 13.5 | 3.8 |  | 17.3 | 17.3 | 0.78035 | 0 | 12.3664 | 12.9483 | 10.1087 | 65.6913 | 0.19711 | 7.55 | 6.65 | 83.616 | 505.47 | 447.72 | 2016.3 | 1741.2474 | 13.6415 | 81.324 | 1094.4837 | 92.3602 | 88 | 65 | 8.8 | 8.4 | 8.9 | 17.3 | 17.3 | 0.42851 | 0.48555 | 12.9231 | 13.5312 | 5.5531 | 62.1469 | 0.21773 | 6.65 | NA | 70.446 | 447.72 | 931.59 | 803.7988 | 13.7175 | 84.2656 | 625.7594 | 88.7423 | 65 | 40 | 7 | 2.6 | 6 | 8.6 | 8.6 | 0.47758 | 0.30233 | 8 | 8.3764 | 9.97 | 35.53 | 0.23576 | NA | NA | 112.14 | 931.59 | 1426 | 1286.685 | 9.7696 | 74.9531 | 1109.1375 | 89.8894 | 150 | 80 | 8.8 | 2.5 | 3.8 | 6.3 | 6.3 | 0.68141 | 0.39683 | 21.4286 | 22.4369 | 18.0247 | 88.1753 | 0.25446 | NA | 6.82 | 69.685 | 1426 | 2016.3 | 2318.3125 | -14.9785 | 84.4356 | 1872.1562 | 96.2778 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 0.75 | Net driving pressure required for permeation, NDP (psi) | 49.7034 | [5 empty] | 1997-11-11 | 12:15 | 2229.76 | 24.4444 | 88 | 80 | 8.2667 | 0 | 13.5 | 3.9 |  | 17.4 | 17.4 | 0.77586 | 0 | 12.3664 | 12.9483 | 9.8208 | 65.9125 | 0.19645 | 7.48 | 5.9 | 83.884 | 507.96 | 443.52 | 1986.27 | 1688.4138 | 14.9958 | 81.0868 | 1065.9669 | 92.1307 | 88 | 64 | 9 | 8.5 | 8.9 | 17.4 | 17.4 | 0.43015 | 0.48851 | 13.0769 | 13.6922 | 5.5262 | 61.4738 | 0.22273 | 5.9 | NA | 69.502 | 443.52 | 918.72 | 800.7282 | 12.8431 | 84.3295 | 622.1241 | 88.8283 | 64 | 40 | 7 | 2.5 | 6 | 8.5 | 8.5 | 0.47431 | 0.29412 | 7.6923 | 8.0543 | 9.7614 | 35.2386 | 0.22856 | NA | NA | 110.88 | 918.72 | 1423.52 | 1255.32 | 11.8158 | 75 | 1087.02 | 89.7996 | 150 | 80 | 8.8 | 2.5 | 3.9 | 6.4 | 6.4 | 0.6949 | 0.39062 | 21.4286 | 22.4369 | 17.8572 | 88.3428 | 0.25398 | NA | 6.92 | 71.225 | 1423.52 | 1986.27 | 2290.3758 | -15.3104 | 83.941 | 1856.9479 | 96.1644 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Flow weighted system pressure losses, Lsys (psi) | 33.5282 | [5 empty] | 1997-11-11 | 14:05 | 2243.6 | 24.4444 | 88 | 80 | 8.2667 | 0 | 13.5 | 3.8 |  | 17.3 | 17.3 | 0.78035 | 0 | 12.3664 | 12.9483 | 10.0164 | 65.7169 | 0.19703 | 7.44 | 5.72 | 84.42 | 506.3 | 445.2 | 2002 | 1726.9184 | 13.7403 | 81.0377 | 1086.0592 | 92.2269 | 88 | 65 | 9 | 8.5 | 8.8 | 17.3 | 17.3 | 0.42688 | 0.49133 | 13.0769 | 13.6922 | 5.5644 | 61.9356 | 0.22107 | 5.72 | NA | 69.974 | 445.2 | 930.6 | 807.6342 | 13.2136 | 84.2826 | 626.4171 | 88.8295 | 65 | 40 | 7 | 2.5 | 6 | 8.5 | 8.5 | 0.47431 | 0.29412 | 7.6923 | 8.0543 | 9.8897 | 35.6103 | 0.22618 | NA | NA | 112.14 | 930.6 | 1426 | 1271.625 | 10.8257 | 74.8113 | 1101.1125 | 89.8158 | 150 | 80 | 8.8 | 2.5 | 3.8 | 6.3 | 6.3 | 0.68141 | 0.39683 | 21.4286 | 22.4369 | 18.0278 | 88.1722 | 0.25447 | NA | 6.86 | 69.454 | 1426 | 2002 | 2318.4645 | -15.8074 | 84.3994 | 1872.2322 | 96.2903 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Maximum element recovery (%) | 17 | Required influent pressure to the system, PI (psi) | 83.2317 | [5 empty] | 1997-11-12 | 12:05 | 2253.68 | 24.4444 | 88 | 80 | 8.2 | 0 | 13.5 | 3.8 |  | 17.3 | 17.3 | 0.78035 | 0 | 12.3664 | 12.9483 | 10.1134 | 65.6866 | 0.19712 | 7.52 | 5.91 | 84.286 | 502.98 | 448.56 | 1990.56 | 1742.6913 | 12.4522 | 81.2096 | 1095.6257 | 92.307 | 88 | 65 | 8.8 | 8.5 | 8.8 | 17.3 | 17.3 | 0.42688 | 0.49133 | 13.0769 | 13.6922 | 5.616 | 62.084 | 0.22054 | 5.91 | NA | 69.856 | 448.56 | 926.64 | 814.3536 | 12.1176 | 84.4266 | 631.4568 | 88.9373 | 65 | 40 | 7 | 2.5 | 6.2 | 8.7 | 8.7 | 0.48739 | 0.28736 | 7.6923 | 8.0543 | 9.7947 | 35.7053 | 0.22558 | NA | NA | 111.51 | 926.64 | 1417.32 | 1255.3215 | 11.4299 | 75.1404 | 1090.9807 | 89.7789 | 150 | 80 | 8.8 | 2.5 | 3.8 | 6.3 | 6.3 | 0.68141 | 0.39683 | 21.4286 | 22.4369 | 17.8961 | 88.3039 | 0.25409 | NA | 6.8 | 70.686 | 1417.32 | 1990.56 | 2303.2634 | -15.7093 | 84.2416 | 1860.2917 | 96.2003 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Variability of design flux (%) | 5 | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1997-11-12 | 6:03 | 2259.99 | 24.4444 | 88 | 78 | 8.5333 | 0 | 14.1 | 3.8 |  | 17.9 | 17.9 | 0.78771 | 0 | 12.916 | 13.5238 | 11.0394 | 63.4272 | 0.21322 | 7.53 | 5.92 | 89.646 | 556.93 | 476.28 | 2202.2 | 1910.8956 | 13.2279 | 81.1779 | 1193.5878 | 92.4894 | 88 | 65 | 9.2 | 8.9 | 9 | 17.9 | 17.9 | 0.43996 | 0.49721 | 13.6923 | 14.3366 | 6.08 | 61.22 | 0.23418 | 5.92 | NA | 69.443 | 476.28 | 925.65 | 878.5966 | 5.0833 | 85.4197 | 677.4383 | 89.7492 | 65 | 40 | 7.2 | 2.6 | 6.2 | 8.8 | 8.8 | 0.49066 | 0.29545 | 8 | 8.3764 | 9.4192 | 35.8808 | 0.23345 | NA | NA | 147 | 925.65 | 1397.48 | 1252.1806 | 10.3972 | 69.1358 | 1088.9153 | 86.5003 | 150 | 78 | 9.2 | 2.6 | 3.8 | 6.4 | 6.4 | 0.68816 | 0.40625 | 22.2857 | 23.3343 | 17.7336 | 87.0664 | 0.26801 | NA | 6.84 | 76.153 | 1397.48 | 2202.2 | 2301.5458 | -4.5112 | 84.0109 | 1849.5129 | 95.8825 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Rejection of reference solute and conditions of test | Magnesium Sulfate = 98 % Rejection | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1997-11-12 | 13:05 | 2266.59 | 24.4444 | 88 | 78 | 8.4 | 0 | 14.1 | 3.8 |  | 17.9 | 17.9 | 0.78771 | 0 | 12.916 | 13.5238 | 10.4801 | 64.1199 | 0.21091 | N/A | 5.87 | 100.835 | 522.9 | 467.88 | 2230.8 | 1829.8101 | 17.9752 | 78.4485 | 1148.8451 | 91.2229 | 88 | 65 | 9 | 8.9 | 9 | 17.9 | 17.9 | 0.43996 | 0.49721 | 13.6923 | 14.3366 | 5.95 | 61.55 | 0.23293 | 5.87 | NA | 69.738 | 467.88 | 926.64 | 861.5982 | 7.0191 | 85.0949 | 664.7391 | 89.509 | 65 | 40 | 7.2 | 2.6 | 6.2 | 8.8 | 8.8 | 0.49066 | 0.29545 | 8 | 8.3764 | 9.5378 | 35.7622 | 0.23423 | NA | NA | 138.18 | 926.64 | 1385.08 | 1257.2845 | 9.2266 | 70.4668 | 1091.9623 | 87.3457 | 150 | 78 | 9 | 2.6 | 3.8 | 6.4 | 6.4 | 0.68816 | 0.40625 | 22.2857 | 23.3343 | 17.5651 | 87.4349 | 0.26688 | NA | N/A | 76.307 | 1385.08 | 2230.8 | 2280.5563 | -2.2304 | 83.6909 | 1832.8181 | 95.8366
|  | (e.g., solute type and concentration) | San Diego Tap = 75 % Rejection | [7 empty] | 1997-11-13 | 7:02 | 2284.92 | 24.4444 | 88 | 78 | 8.4667 | 0 | 14.1 | 3.8 |  | 17.9 | 17.9 | 0.78771 | 0 | 12.916 | 13.5238 | 10.519 | 64.0144 | 0.21126 | N/A | 5.89 | 95.274 | 571.87 | 463.68 | 2049.19 | 1830.6602 | 10.6642 | 79.4526 | 1147.1701 | 91.6949 | 88 | 64 | 9 | 8.8 | 9.1 | 17.9 | 17.9 | 0.4416 | 0.49162 | 13.5385 | 14.1755 | 5.8573 | 61.1427 | 0.23184 | 5.89 | NA | 68.853 | 463.68 | 889.02 | 845.4907 | 4.8963 | 85.1508 | 654.5854 | 89.4814 | 64 | 40 | 7 | 2.6 | 6.2 | 8.8 | 8.8 | 0.49066 | 0.29545 | 8 | 8.3764 | 8.976 | 36.024 | 0.23252 | NA | NA | 147 | 889.02 | 1321.84 | 1200.1897 | 9.2031 | 68.2971 | 1044.6048 | 85.9277 | 150 | 78 | 9.4 | 2.7 | 3.8 | 6.5 | 6.5 | 0.6949 | 0.41538 | 23.1429 | 24.2318 | 16.9585 | 87.6415 | 0.27649 | NA | N/A | 70.532 | 1321.84 | 2049.19 | 2210.9273 | -7.8927 | 84.7886 | 1766.3836 | 96.007
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1997-11-14 | 6:45 | 2308.45 | 24.4444 | 88 | 70 | 8.1333 | 0 | 13.9 | 3.7 |  | 17.6 | 17.6 | 0.78977 | 0 | 12.7328 | 13.332 | 10.4791 | 60.3876 | 0.22077 | N/A | 5.9 | 92.058 | 428.28 | 456.12 | 2022.02 | 1823.8124 | 9.8025 | 79.8172 | 1139.9662 | 91.9245 | 88 | 65 | 9 | 8.8 | 8.8 | 17.6 | 17.6 | 0.43178 | 0.5 | 13.5385 | 14.1755 | 5.8214 | 61.6786 | 0.22983 | 5.9 | NA | 68.027 | 456.12 | 874.17 | 844.213 | 3.4269 | 85.0857 | 650.1665 | 89.537 | 65 | 40 | 7 | 2.7 | 5.8 | 8.5 | 8.5 | 0.46777 | 0.31765 | 8.3077 | 8.6986 | 8.9038 | 36.5962 | 0.23769 | NA | NA | 151.9 | 874.17 | 1339.2 | 1210.3991 | 9.6177 | 66.6974 | 1042.2846 | 85.4262 | 140 | 70 | 8.4 | 2.4 | 3.7 | 6.1 | 6.1 | 0.66117 | 0.39344 | 20.5714 | 21.5394 | 16.6493 | 79.9507 | 0.26941 | NA | N/A | 82.005 | 1339.2 | 2022.02 | 2154.6778 | -6.5607 | 82.0212 | 1746.9389 | 95.3058
|  | Standard testing recovery (%) | 15 | [7 empty] | 1997-11-19 | 12:00 | 2338.67 | 24.4444 | 110 | 70 | 8.9667 | 0 | 14.8 | 2.9 |  | 17.7 | 17.7 | 0.83616 | 0 | 13.5573 | 14.1952 | 14.2874 | 66.746 | 0.21267 | 7.48 | 6.66 | 69.814 | 448.2 | 472.08 | 2814.24 | 2525.0237 | 10.2769 | 85.2114 | 1498.5519 | 95.3412 | 110 | 80 | 10 | 9.8 | 7.9 | 17.7 | 17.7 | 0.4187 | 0.55367 | 15.0769 | 15.7864 | 6.7082 | 78.2918 | 0.20163 | 6.66 | NA | 58.056 | 472.08 | 1035.54 | 985.6794 | 4.8149 | 87.7021 | 728.8797 | 92.0349 | 80 | 60 | 9 | 3.2 | 4.5 | 7.7 | 7.7 | 0.39907 | 0.41558 | 9.8462 | 10.3095 | 12.2724 | 48.7276 | 0.21157 | NA | NA | 130.2 | 1035.54 | 1760.8 | 1679.3373 | 4.6265 | 72.4199 | 1357.4387 | 90.4084 | 110 | 70 | 7.9 | 1.8 | 2.9 | 4.7 | 4.7 | 0.51274 | 0.38298 | 15.4286 | 16.1545 | 21.8376 | 60.2624 | 0.26807 | NA | 7.62 | 94.248 | 1760.8 | 2814.24 | 2795.2116 | 0.67615 | 80.0356 | 2278.0058 | 95.8627
|  | Standard testing pH | 7 | [7 empty] | 1997-11-19 | 15:20 | 2341.73 | 23.89 | 110 | 68 | 8.4 | 0 | 14.8 | 2.9 |  | 17.7 | 17.7 | 0.83616 | 0 | 13.5573 | 14.4297 | 11.9518 | 68.6482 | 0.2102 | 7.53 | 6.66 | 80.132 | 395.91 | 416.64 | 1960.53 | 2133.9912 | -8.8477 | 80.7671 | 1275.3156 | 93.7167 | 110 | 75 | 9.8 | 9.8 | 7.9 | 17.7 | 17.7 | 0.4187 | 0.55367 | 15.0769 | 16.0472 | 5.8291 | 76.8709 | 0.20876 | 6.66 | NA | 56.876 | 416.64 | 891 | 862.9295 | 3.1504 | 86.3489 | 639.7848 | 91.1101 | 75 | 60 | 8.4 | 3.2 | 4.5 | 7.7 | 7.7 | 0.39907 | 0.41558 | 9.8462 | 10.4798 | 10.4915 | 48.6085 | 0.2156 | NA | NA | 117.04 | 891 | 1391.28 | 1441.3716 | -3.6004 | 71.9086 | 1166.1858 | 89.9639 | 110 | 68 | 7 | 1.8 | 2.9 | 4.7 | 4.7 | 0.51274 | 0.38298 | 15.4286 | 16.4215 | 16.6727 | 65.3273 | 0.25137 | NA | 7.92 | 118.888 | 1391.28 | 1960.53 | 2181.0406 | -11.2475 | 71.4651 | 1786.1603 | 93.3439
|  | Acceptable range of operating pressures | 0 to 350 psi | [7 empty] | 1997-11-20 | 1:50 | 2352.13 | 24.4 | 110 | 68 | 8.4 | 0 | 14.8 | 2.9 |  | 17.7 | 17.7 | 0.83616 | 0 | 13.5573 | 14.2138 | 11.799 | 68.801 | 0.20659 | 7.54 | 6.59 | 79.395 | 396.74 | 411.6 | 1973.4 | 2106.991 | -6.7696 | 80.7106 | 1259.2955 | 93.6953 | 110 | 78 | 9.8 | 9.8 | 7.9 | 17.7 | 17.7 | 0.4187 | 0.55367 | 15.0769 | 15.8071 | 5.7589 | 78.4411 | 0.20152 | 6.59 | NA | 56.168 | 411.6 | 1013.76 | 852.5156 | 15.9056 | 86.3537 | 632.0578 | 91.1135 | 78 | 60 | 8.4 | 3.2 | 4.5 | 7.7 | 7.7 | 0.39907 | 0.41558 | 9.8462 | 10.323 | 12.1062 | 48.4938 | 0.21287 | NA | NA | 120.68 | 1013.76 | 1388.8 | 1648.8391 | -18.724 | 70.6803 | 1331.2996 | 90.9352 | 110 | 68 | 7 | 1.8 | 2.9 | 4.7 | 4.7 | 0.51274 | 0.38298 | 15.4286 | 16.1758 | 16.5827 | 65.4173 | 0.24727 | NA | 7.68 | 123.277 | 1388.8 | 1973.4 | 2174.297 | -10.1802 | 70.0493 | 1781.5485 | 93.0803
|  | Acceptable range of operating pH values | 4 to 11 | [7 empty] | 1997-11-20 | 9:00 | 2359.45 | 24.4 | 110 | 68 | 8.4667 | 0 | 14.8 | 2.9 |  | 17.7 | 17.7 | 0.83616 | 0 | 13.5573 | 14.2138 | 12.3311 | 68.2022 | 0.20841 | 7.5 | 6.63 | 77.854 | 400.06 | 425.04 | 1950.52 | 2196.8858 | -12.6308 | 81.6831 | 1310.9629 | 94.0613 | 110 | 75 | 10 | 9.8 | 7.9 | 17.7 | 17.7 | 0.4187 | 0.55367 | 15.0769 | 15.8071 | 5.9537 | 76.5463 | 0.2065 | 6.63 | NA | 57.584 | 425.04 | 1019.7 | 880.8715 | 13.6146 | 86.4521 | 652.9557 | 91.181 | 75 | 60 | 8.4 | 3.2 | 4.5 | 7.7 | 7.7 | 0.39907 | 0.41558 | 9.8462 | 10.323 | 12.1488 | 46.9512 | 0.21987 | NA | NA | 123.48 | 1019.7 | 1398.72 | 1657.012 | -18.4663 | 70.9486 | 1338.356 | 90.7738 | 110 | 68 | 7 | 1.8 | 2.9 | 4.7 | 4.7 | 0.51274 | 0.38298 | 15.4286 | 16.1758 | 16.7521 | 65.2479 | 0.24791 | NA | 7.66 | 120.274 | 1398.72 | 1950.52 | 2192.2382 | -12.3925 | 71.7029 | 1795.4791 | 93.3013
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1997-11-20 | 15:30 | 2366.26 | 24.4 | 110 | 48 | 7.0333 | 0 | 12.1 | 2.9 | X | 15 | 15 | 0.80667 | 0 | 11.084 | 11.6208 | 10.6101 | 61.3566 | 0.1894 | 7.12 | 5.74 | 133.33 | 405.04 | 477.12 | 2425.28 | 1911.5541 | 21.1821 | 72.0552 | 1194.3371 | 88.8365 | 110 | 62 | 8.3 | 8.1 | 6.9 | 15 | 15 | 0.35819 | 0.54 | 12.4615 | 13.0651 | 6.4331 | 71.2669 | 0.18333 | 5.74 | NA | 71.744 | 477.12 | 984.06 | 952.9962 | 3.1567 | 84.9631 | 715.0581 | 89.9667 | 62 | 44 | 6.8 | 2.4 | 4.4 | 6.8 | 6.8 | 0.36636 | 0.35294 | 7.3846 | 7.7423 | 10.8343 | 35.3657 | 0.21892 | NA | NA | 132.79 | 984.06 | 1614.48 | 1448.3891 | 10.2876 | 72.1684 | 1216.2245 | 89.0818 | 105 | 48 | 6 | 1.6 | 2.9 | 4.5 | 4.5 | 0.49925 | 0.35556 | 13.7143 | 14.3785 | 19.1288 | 51.3712 | 0.27989 | NA | 6.76 | 115.192 | 1614.48 | 2425.28 | 2441.6734 | -0.67594 | 75.8568 | 2028.0767 | 94.3201
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-01-09 | 14:20 | 2385.23 | 25 | 100 | 70 | 10.6 | 0 | 21.2 | 3.05 |  | 24.25 | 24.25 | 0.87423 | 0 | 19.4198 | 20.0024 | 15.3183 | 59.0817 | 0.33856 | 7.43 | 6.53 | 65.124 | 379.31 | 407.4 | 2402.4 | 2786.4988 | -15.9881 | 84.0147 | 1596.9494 | 95.922 | 100 | 78 | 11 | 11 | 10.2 | 21.2 | 21.2 | 0.51356 | 0.51887 | 16.9231 | 17.4308 | 5.5097 | 72.4903 | 0.24046 | 6.53 | NA | 49.442 | 407.4 | 841.5 | 793.4331 | 5.712 | 87.864 | 600.4166 | 91.7654 | 78 | 61 | 10.3 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 15.8462 | 11.8087 | 47.3912 | 0.33437 | NA | NA | 54.25 | 841.5 | 1599.6 | 1628.75 | -1.8223 | 86.6838 | 1235.125 | 95.6077 | 119 | 70 | 10.5 | 2.15 | 3.05 | 5.2 | 5.2 | 0.5566 | 0.41346 | 18.4286 | 18.9814 | #VALUE! | #VALUE! | #VALUE! | NA | 7.19 | NA | 1599.6 | 2402.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 1998-01-09 | 20:10 | 2392.54 | 25.5556 | 100 | 70 | 10.2333 | 0 | 21.2 | 3 |  | 24.2 | 24.2 | 0.87603 | 0 | 19.4198 | 19.6767 | 15.6065 | 59.1602 | 0.3326 | 7.44 | 6.71 | 65.66 | 381.8 | 409.92 | 2245.1 | 2842.6907 | -26.6176 | 83.9822 | 1626.3053 | 95.9626 | 100 | 80 | 10.2 | 11 | 10.2 | 21.2 | 21.2 | 0.51356 | 0.51887 | 16.9231 | 17.1469 | 5.5331 | 74.2669 | 0.23088 | 6.71 | NA | 50.445 | 409.92 | 840.51 | 797.5891 | 5.1065 | 87.6939 | 603.7546 | 91.6448 | 80 | 62 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 15.5881 | 11.7887 | 48.7114 | 0.32001 | NA | NA | 54.6 | 840.51 | 1595.88 | 1626.42 | -1.9137 | 86.6803 | 1233.465 | 95.5734 | 120 | 70 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | #VALUE! | #VALUE! | #VALUE! | NA | 7.29 | NA | 1595.88 | 2245.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-01-10 | 6:15 | 2400.78 | 24.4444 | 102 | 70 | 9.9667 | 0 | 21.3 | 3.1 |  | 24.4 | 24.4 | 0.87295 | 0 | 19.5115 | 20.4295 | 15.3853 | 60.6481 | 0.33685 | 7.47 | 6.74 | 61.372 | 393.42 | 408.24 | 2220.79 | 2791.5588 | -25.7012 | 84.9667 | 1599.8994 | 96.164 | 102 | 80 | 9.5 | 11 | 10.3 | 21.3 | 21.3 | 0.51683 | 0.51643 | 16.9231 | 17.7194 | 5.4967 | 76.0033 | 0.23314 | 6.74 | NA | 49.914 | 408.24 | 814.77 | 790.9183 | 2.9274 | 87.7734 | 599.5791 | 91.6752 | 80 | 64 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.4498 | 50.3502 | 0.31993 | NA | NA | 51.45 | 814.77 | 1533.88 | 1578.09 | -2.8822 | 87.3971 | 1196.43 | 95.6997 | 120 | 70 | 10.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.3305 | 65.4695 | 0.30158 | NA | 7.32 | 107.107 | 1533.88 | 2220.79 | 2546.4286 | -14.6632 | 73.7637 | 2040.1543 | 94.7501
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-01-14 | 13:30 | 2410.26 | 24.4444 | 100 | 70 | 10.0667 | 0 | 20.95 | 3 |  | 23.95 | 23.95 | 0.87474 | 0 | 19.1908 | 20.0938 | 15.1181 | 59.8152 | 0.33593 | 7.57 | 6.5 | 59.898 | 374.33 | 396.48 | 2102.1 | 2746.9443 | -30.6762 | 84.8926 | 1571.7122 | 96.189 | 100 | 72 | 10 | 10.95 | 10 | 20.95 | 20.95 | 0.5062 | 0.52267 | 16.8462 | 17.6388 | 5.4088 | 70.5912 | 0.24987 | 6.5 | NA | 46.964 | 396.48 | 813.78 | 779.2 | 4.2493 | 88.1548 | 587.84 | 92.0108 | 72 | 62 | 10.1 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2711 | 45.6289 | 0.33891 | NA | NA | 52.22 | 813.78 | 1486.76 | 1544.8776 | -3.909 | 86.8291 | 1179.3288 | 95.5721 | 115 | 70 | 10.1 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 18.8521 | 63.5479 | 0.3107 | NA | 7.3 | 107.338 | 1486.76 | 2102.1 | 2498.3361 | -18.8495 | 72.9273 | 1992.5481 | 94.613
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-01-14 | 14:30 | 2412.05 | 24.4444 | 100 | 68 | 9.9667 | 0 | 20.95 | 3 |  | 23.95 | 23.95 | 0.87474 | 0 | 19.1908 | 20.0938 | 16.0132 | 58.0201 | 0.34633 | 7.53 | 6.45 | 60.97 | 396.74 | 417.48 | 2576.86 | 2907.1082 | -12.8159 | 85.3957 | 1662.2941 | 96.3322 | 100 | 75 | 9.8 | 10.95 | 10 | 20.95 | 20.95 | 0.5062 | 0.52267 | 16.8462 | 17.6388 | 5.6689 | 72.0311 | 0.24488 | 6.45 | NA | 51.153 | 417.48 | 843.48 | 818.6081 | 2.9487 | 87.7472 | 618.044 | 91.7234 | 75 | 62 | 10.1 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 11.7892 | 46.6108 | 0.33177 | NA | NA | 52.15 | 843.48 | 1661.6 | 1618.6604 | 2.5842 | 87.5084 | 1231.0702 | 95.7638 | 115 | 68 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 21.2763 | 60.2237 | 0.32785 | NA | 7.23 | 104.797 | 1661.6 | 2576.86 | 2803.2555 | -8.7857 | 74.8977 | 2232.4278 | 95.3057
[11 empty] | 1998-01-15 | 7:20 | 2428.81 | 24.4444 | 98 | 70 | 10.0333 | 0 | 20.2 | 3 |  | 23.2 | 23.2 | 0.87069 | 0 | 18.5038 | 19.3745 | 14.8515 | 59.1152 | 0.32774 | 7.6 | 6.54 | 71.489 | 400.89 | 411.6 | 2478.19 | 2701.6807 | -9.0183 | 82.6314 | 1556.6404 | 95.4075 | 98 | 78 | 10 | 10.2 | 10 | 20.2 | 20.2 | 0.49394 | 0.50495 | 15.6923 | 16.4307 | 5.5247 | 72.4753 | 0.22671 | 6.54 | NA | 45.725 | 411.6 | 826.65 | 784.7925 | 5.0635 | 88.8909 | 598.1962 | 92.3562 | 78 | 60 | 10.1 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.5393 | 47.3607 | 0.32652 | NA | NA | 46.97 | 826.65 | 1631.84 | 1575.1428 | 3.4744 | 88.5884 | 1200.8964 | 96.0888 | 120 | 70 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 20.8422 | 64.1578 | 0.30775 | NA | 7.31 | 106.799 | 1631.84 | 2478.19 | 2750.2034 | -10.9763 | 74.0527 | 2191.0217 | 95.1256
[11 empty] | 1998-01-15 | 14:40 | 2435.7 | 24.4444 | 100 | 70 | 10.4 | 0 | 20.3 | 3 |  | 23.3 | 23.3 | 0.87124 | 0 | 18.5954 | 19.4704 | 15.5001 | 59.0999 | 0.32945 | 7.52 | 6.51 | 58.826 | 392.59 | 412.44 | 2425.28 | 2805.2281 | -15.6662 | 85.7371 | 1608.834 | 96.3436 | 100 | 78 | 10.2 | 10.7 | 9.6 | 20.3 | 20.3 | 0.48903 | 0.52709 | 16.4615 | 17.2361 | 5.6621 | 73.1379 | 0.23567 | 6.51 | NA | 48.852 | 412.44 | 852.39 | 817.6891 | 4.071 | 88.1554 | 615.0646 | 92.0574 | 78 | 60 | 10.2 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 11.9365 | 46.8635 | 0.32998 | NA | NA | 51.17 | 852.39 | 1692.6 | 1637.2586 | 3.2696 | 87.5933 | 1244.8243 | 95.8894 | 118 | 70 | 10.8 | 1.8 | 3 | 4.8 | 4.8 | 0.52624 | 0.375 | 15.4286 | 16.1545 | 20.6484 | 62.5516 | 0.25826 | NA | 7.2 | 104.258 | 1692.6 | 2425.28 | 2645.6052 | -9.0845 | 74.7217 | 2169.1026 | 95.1935
[11 empty] | 1998-01-16 | 2:00 | 2436.82 | 24.4444 | 100 | 70 | 10.1333 | 0 | 20.2 | 3 |  | 23.2 | 23.2 | 0.87069 | 0 | 18.5038 | 19.3745 | 15.3986 | 59.4681 | 0.3258 | 7.6 | 6.5 | 58.96 | 392.59 | 411.6 | 2365.22 | 2786.0427 | -17.7921 | 85.6754 | 1598.8213 | 96.3123 | 100 | 78 | 10.2 | 10.2 | 10 | 20.2 | 20.2 | 0.49394 | 0.50495 | 15.6923 | 16.4307 | 5.5149 | 73.2851 | 0.2242 | 6.5 | NA | 46.374 | 411.6 | 833.58 | 784.1305 | 5.9322 | 88.7332 | 597.8653 | 92.2434 | 78 | 60 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.6304 | 47.1696 | 0.32784 | NA | NA | 47.74 | 833.58 | 1612 | 1587.9864 | 1.4897 | 88.4014 | 1210.7832 | 96.0571 | 118 | 70 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 20.6153 | 63.3847 | 0.3115 | NA | 7.31 | 103.565 | 1612 | 2365.22 | 2718.1857 | -14.9232 | 74.8384 | 2165.0928 | 95.2166
[11 empty] | 1998-01-16 | 12:40 | 2445.38 | 24.4444 | 98 | 70 | 10.0333 | 0 | 20 | 3 |  | 23 | 23 | 0.86957 | 0 | 18.3206 | 19.1827 | 15.223 | 58.7437 | 0.32655 | 7.54 | 6.52 | 60.3 | 396.74 | 411.6 | 2459.6 | 2753.6 | -11.9532 | 85.3499 | 1582.6 | 96.1898 | 98 | 78 | 10 | 10.2 | 9.8 | 20 | 20 | 0.48739 | 0.51 | 15.6923 | 16.4307 | 5.5583 | 72.4417 | 0.22681 | 6.52 | NA | 46.02 | 411.6 | 841.5 | 792.1016 | 5.8703 | 88.8192 | 601.8508 | 92.3536 | 78 | 60 | 10.1 | 4.8 | 5.1 | 9.9 | 9.9 | 0.49066 | 0.48485 | 14.7692 | 15.4642 | 11.7049 | 47.1951 | 0.32766 | NA | NA | 45.57 | 841.5 | 1641.76 | 1590.6106 | 3.1155 | 88.9286 | 1216.0553 | 96.2526 | 115 | 70 | 10 | 2 | 3 | 5 | 5 | 0.53973 | 0.4 | 17.1429 | 17.9495 | 20.4682 | 62.0318 | 0.28936 | NA | 7.3 | 106.645 | 1641.76 | 2459.6 | 2665.17 | -8.3579 | 74.0901 | 2153.465 | 95.0477
[11 empty] | 1998-01-16 | 19:10 | 2452.34 | 24.4444 | 100 | 70 | 9.7 | 0 | 20.2 | 3 |  | 23.2 | 23.2 | 0.87069 | 0 | 18.5038 | 19.3745 | 16.1273 | 59.1727 | 0.32742 | 7.59 | 6.59 | 54.873 | 406.7 | 424.2 | 2622.62 | 2911.0018 | -10.9959 | 87.0644 | 1667.6009 | 96.7095 | 100 | 78 | 9 | 10.2 | 10 | 20.2 | 20.2 | 0.49394 | 0.50495 | 15.6923 | 16.4307 | 5.7052 | 74.2948 | 0.22116 | 6.59 | NA | 46.374 | 424.2 | 865.26 | 809.5825 | 6.4348 | 89.0679 | 616.8913 | 92.4826 | 78 | 60 | 10.1 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 12.1014 | 46.7986 | 0.33044 | NA | NA | 47.6 | 865.26 | 1701.28 | 1650.2136 | 3.0016 | 88.7789 | 1257.7368 | 96.2154 | 118 | 70 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 21.9007 | 62.0993 | 0.31795 | NA | 7.32 | 98.791 | 1701.28 | 2622.62 | 2876.4386 | -9.6781 | 76.7112 | 2288.8593 | 95.6838
[11 empty] | 1998-01-16 | 18:00 | 2463.3 | 24.4444 | 102 | 70 | 10.4 | 0 | 20.85 | 3.05 |  | 23.9 | 23.9 | 0.87238 | 0 | 19.0992 | 19.9979 | 16.1077 | 59.4923 | 0.33614 | 7.56 | 6.56 | 55.409 | 384.29 | 420 | 2501.07 | 2912.368 | -16.4449 | 86.8074 | 1666.184 | 96.6745 | 102 | 80 | 9.8 | 10.8 | 10.05 | 20.85 | 20.85 | 0.50538 | 0.51799 | 16.6154 | 17.3972 | 5.7665 | 75.4335 | 0.23063 | 6.56 | NA | 44.899 | 420 | 844.47 | 823.0936 | 2.5313 | 89.3098 | 621.5468 | 92.7762 | 80 | 65 | 10.6 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 11.8707 | 50.0293 | 0.3091 | NA | NA | 47.67 | 844.47 | 1678.96 | 1625.0088 | 3.2134 | 88.65 | 1234.7394 | 96.1393 | 120 | 70 | 10.8 | 2.2 | 3.05 | 5.25 | 5.25 | 0.55997 | 0.41905 | 18.8571 | 19.7444 | 21.6892 | 62.5108 | 0.31586 | NA | 7.26 | 84.931 | 1678.96 | 2501.07 | 2828.7514 | -13.1016 | 79.7783 | 2253.8557 | 96.2317
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A1: Alison Gusses: Please refer to comment in column AJ prior to Base Analyses
Note on W6: S Allgeier (11/17/99): Reviewer entered formula to calculate average system permeate pressure.
Note on AJ6: Alison Gusses: MTCw may be incorrect due to third stage booster pump
Note on DU16: CDM: verified w/ lab data sheets
Note on DU23: CDM: verified w/ lab data sheets
Note on DV16: CDM: verified w/ lab data sheets
Note on DV22: Alison Gusses: Drop in TOC due to change in raw water source (wells)
Note on DV23: CDM: verified w/ lab data sheets; drop in UV due to change in raw water source (wells)
Note on DV26: Alison Gusses: SDS dose verified by consultant
Note on DW16: CDM: verified w/ lab data sheets
Note on DW23: CDM: verified w/ lab data sheets
Note on EO10: Alison Gusses: Consultant suspects some of the feed water entered the permeate stream through damaged membrane leaves and o-rings, explaining the high TDS and hardness concentrations
Note on EO16: CDM: this value was orig. entered and verified with lab data sheets as 214.37, but the average alkalinity of stage 1,2 & 3 is approx. 30, so must be in error.
Note on EO23: CDM: verified w/ lab data sheets
Note on EP16: CDM: verified w/ lab data sheets
Note on EP23: CDM: verified w/ lab data sheets
Note on EQ16: CDM: verified w/ lab data sheets
Note on EQ23: CDM: verified w/ lab data sheets
Note on FI16: CDM: verified w/ lab data sheets
Note on FI23: CDM: verified w/ lab data sheets
Note on FJ16: CDM: verified w/ lab data sheets
Note on FJ23: CDM: verified w/ lab data sheets
Note on FK16: CDM: verified w/ lab data sheets
Note on FK23: CDM: verified w/ lab data sheets
Note on GC16: CDM: verified w/ lab data sheets
Note on GC23: CDM: verified w/ lab data sheets
Note on GD16: CDM: verified w/ lab data sheets
Note on GD23: CDM: verified w/ lab data sheets
Note on GE16: CDM: value changed-originally entered as 96
Note on GE23: CDM: verified w/ lab data sheets
Note on GW16: CDM: verified w/ lab data sheets
Note on GW23: CDM: verified w/ lab data sheets
Note on GX16: CDM: verified w/ lab data sheets
Note on GX23: CDM: verified w/ lab data sheets
Note on GY16: CDM: verified w/ lab data sheets
Note on GY23: CDM: verified w/ lab data sheets

## Sheet3. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 24 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | Stage 1 and 2 -- General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment (from Performance sampling & MDWASD) |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Miami-Dade Water and Sewer Dept. | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 26 | Alkalinity (mg/L as CaCO3) | 176 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51 | [6 empty] | System recovery during sample collection (decimal) | 0.84518 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50254 | [6 empty] | System recovery during sample collection (decimal) | 0.84694 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5051 | [6 empty] | System recovery during sample collection (decimal) | 0.85 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 4130871 | Membrane trade name | TFC-S | Temperature normalized MTCW (gfd/psi) | 0.30179 | Calcium Hardness (mg/L as CaCO3) | NA | Antiscalant Addition | King Lee Pre-treat 100 (2 mg/L dose) | Pilot Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 20.8 | HI-9 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.5 | HI-9 | [5 empty] | System feed flow rate during sample collection (gpm) | 20.8 | HI-10 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.7 | HI-10 | [5 empty] | System feed flow rate during sample collection (gpm) | 20.45 | HI-11 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.4 | HI-11 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.7 | HI-12 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.9 | HI-12 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.6 | HI-13 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.9 | HI-13 | [5 empty] | System feed flow rate during sample collection (gpm) | 20.8 | HI-10 DUP | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.7 | HI - 10 DUP |  |  |  | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | 1029 | Membrane element model number | TFC 4921S |  |  | LSI | 0.14 | Sulfuric Acid Addition | pH ~ 6.75 (85 mg/L dose) | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 20.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 20.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 20.45 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20.45 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.7 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 20.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20.8 |  |  |  |  | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | NA | Cartridge Filtration | 5 um exclusion size | Pilot Scale | 1998-01-17 | 0:00 | 2469.13 | 23.8889 | 102 | 70 | 10.3 | 0 | 17.4 | 3 |  | 20.4 | 20.4 | 0.85294 | 0 | 15.9389 | 16.9652 | 14.4245 | 61.2755 | 0.27687 | 7.51 | 6.62 | 52.662 | 274.73 | 422.52 | 2628.34 | 2567.6964 | 2.3073 | 87.5362 | 1495.1082 | 96.4777 | 102 | 80 | 9.6 | 10.4 | 10 | 20.4 | 20.4 | 0.49721 | 0.5098 | 16 | 17.0302 | 5.7632 | 75.6368 | 0.22516 | 6.62 | NA | 43.365 | 422.52 | 856.35 | 816.8412 | 4.6136 | 89.7366 | 619.6806 | 93.002 | 80 | 68 | 10.5 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.7202 | 11.9975 | 51.5025 | 0.30523 | NA | NA | 45.71 | 856.35 | 1655.4 | 1634.5644 | 1.2586 | 89.1816 | 1245.4572 | 96.3299 | 120 | 70 | 10.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 20.0714 | 21.3168 | 62.8832 | 0.31918 | NA | 7.31 | 95.634 | 1655.4 | 2628.34 | 2799.2284 | -6.5018 | 77.3658 | 2227.3142 | 95.7063 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.67 |  |  |  | 1998-01-17 | 7:52 | 2476.88 | 24.4444 | 102 | 70 | 10.3333 | 0 | 17.6 | 3 |  | 20.6 | 20.6 | 0.85437 | 0 | 18.0513 | 18.9007 | 14.4922 | 61.1745 | 0.30896 | 7.48 | 6.64 | 52.394 | 310.42 | 420.84 | 2571.14 | 2582.3899 | -0.43754 | 87.5501 | 1501.6149 | 96.5108 | 102 | 80 | 9.6 | 10.6 | 10 | 20.6 | 20.6 | 0.50048 | 0.51456 | 16.3077 | 17.075 | 5.76 | 75.64 | 0.22574 | 6.64 | NA | 44.368 | 420.84 | 856.35 | 819.9003 | 4.2564 | 89.4573 | 620.3702 | 92.8481 | 80 | 68 | 10.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.9809 | 51.4191 | 0.30075 | NA | NA | 46.83 | 856.35 | 1664.08 | 1633.4892 | 1.8383 | 88.8723 | 1244.9196 | 96.2383 | 120 | 70 | 10.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 21.4975 | 62.7025 | 0.31489 | NA | 7.24 | 91.091 | 1664.08 | 2571.14 | 2817.6053 | -9.5858 | 78.355 | 2240.8426 | 95.935 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1998-01-17 | 16:30 | 2485.92 | 24.4444 | 102 | 70 | 10.3333 | 0 | 17.7 | 3.05 |  | 20.75 | 20.75 | 0.85301 | 0 | 18.1538 | 19.0081 | 14.0702 | 61.5965 | 0.30859 | 7.55 | 6.56 | 54.337 | 398.4 | 414.96 | 2516.8 | 2507.7558 | 0.35935 | 86.9055 | 1461.3579 | 96.2817 | 102 | 80 | 9.6 | 10.7 | 10.05 | 20.75 | 20.75 | 0.50375 | 0.51566 | 16.4615 | 17.2361 | 5.6887 | 75.7113 | 0.22766 | 6.56 | NA | 43.719 | 414.96 | 861.3 | 810.2116 | 5.9315 | 89.4643 | 612.5858 | 92.8632 | 80 | 66 | 10.6 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 12.1079 | 50.2921 | 0.30749 | NA | NA | 48.58 | 861.3 | 1681.44 | 1657.4339 | 1.4277 | 88.2928 | 1259.3669 | 96.1425 | 120 | 70 | 10.8 | 2.2 | 3.05 | 5.25 | 5.25 | 0.55997 | 0.41905 | 18.8571 | 19.7444 | 21.4904 | 62.7096 | 0.31486 | NA | 7.32 | 102.025 | 1681.44 | 2516.8 | 2820.6902 | -12.0745 | 75.4133 | 2251.0651 | 95.4677 | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 (dup) | CF-sys-30 (dup) | CC-sys-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 (dup) | CI-s1-30 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | BDL |  |  |  | 1998-01-18 | 22:30 | 2490.72 | 24.4444 | 102 | 70 | 10.3333 | 0 | 17.6 | 3 |  | 20.6 | 20.6 | 0.85437 | 0 | 18.0513 | 18.9007 | 14.1699 | 61.4968 | 0.30734 | 7.49 | 6.63 | 53.868 | 329.51 | 414.12 | 2553.98 | 2527.5984 | 1.033 | 86.9922 | 1470.8592 | 96.3377 | 102 | 80 | 9.6 | 10.6 | 10 | 20.6 | 20.6 | 0.50048 | 0.51456 | 16.3077 | 17.075 | 5.6626 | 75.7374 | 0.22545 | 6.63 | NA | 44.014 | 414.12 | 864.27 | 806.4324 | 6.6921 | 89.3717 | 610.2762 | 92.7879 | 80 | 68 | 10.6 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 12.1594 | 51.2406 | 0.3018 | NA | NA | 48.09 | 864.27 | 1671.52 | 1663.7933 | 0.46226 | 88.3874 | 1264.0316 | 96.1955 | 120 | 70 | 10.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 21.474 | 62.726 | 0.31477 | NA | 7.34 | 100.254 | 1671.52 | 2553.98 | 2823.7817 | -10.564 | 75.7911 | 2247.6509 | 95.5396 | Sampling date | MM/DD/YY | 1998-01-28 | 1998-01-28 | 1998-01-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-01-28 | 1998-01-28 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | 1998-02-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-25 | 1998-02-25 | 1998-02-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-25 | 1998-02-25 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-11 | 1998-03-11 | 1998-03-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-11 | 1998-03-11 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-25 | 1998-03-25 | 1998-03-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-25 | 1998-03-25 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | 1998-02-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1998-01-18 | 8:00 | 2501.01 | 24.4444 | 102 | 70 | 10.3333 | 0 | 17.5 | 3 |  | 20.5 | 20.5 | 0.85366 | 0 | 17.9487 | 18.7933 | 13.8531 | 61.8135 | 0.30403 | 7.46 | 6.66 | 52.863 | 345.28 | 406.56 | 2542.54 | 2469.7925 | 2.8612 | 86.9975 | 1438.1762 | 96.3243 | 102 | 80 | 9.6 | 10.5 | 10 | 20.5 | 20.5 | 0.49884 | 0.5122 | 16.1538 | 16.9139 | 5.5261 | 75.8739 | 0.22292 | 6.66 | NA | 44.191 | 406.56 | 859.32 | 787.0475 | 8.4104 | 89.1305 | 596.8037 | 92.5954 | 80 | 68 | 10.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 12.001 | 51.399 | 0.30087 | NA | NA | 48.44 | 859.32 | 1676.48 | 1637.7648 | 2.3093 | 88.0854 | 1248.5424 | 96.1203 | 120 | 70 | 10.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 21.5565 | 62.6435 | 0.31519 | NA | 7.28 | 99.176 | 1676.48 | 2542.54 | 2833.1696 | -11.4307 | 75.6061 | 2254.8248 | 95.6016 | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:15 | 8:15 | 8:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881 (May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.08 |  |  |  | 1998-01-18 | 17:00 | 2509.88 | 24.4444 | 102 | 70 | 10.0667 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.4332 | 62.5001 | 0.29726 | 7.59 | 6.34 | 54.672 | 393.42 | 409.08 | 2339.48 | 2386.9053 | -2.0272 | 86.6354 | 1397.9926 | 96.0892 | 102 | 80 | 9.2 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.5918 | 5.4881 | 76.3119 | 0.21742 | 6.34 | NA | 45.607 | 409.08 | 813.78 | 779.7505 | 4.1817 | 88.8513 | 594.4152 | 92.3274 | 80 | 67 | 10.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.3405 | 51.7595 | 0.29877 | NA | NA | 47.53 | 813.78 | 1595.88 | 1549.38 | 2.9138 | 88.3812 | 1181.58 | 95.9774 | 120 | 70 | 10.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.2644 | 64.1356 | 0.30785 | NA | 7.27 | 100.177 | 1595.88 | 2339.48 | 2657.3466 | -13.5871 | 75.5116 | 2126.6133 | 95.2894 | Operation time | hh.hh | 2740 | 2740 | 2740 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2740 | 2740 | --- | --- | --- | --- | Operation time | hh.hh | 3070.7 | 3070.7 | 3070.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3070.7 | 3070.7 | --- | --- | --- | --- | Operation time | hh.hh | 3401.8 | 3401.8 | 3401.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3401.8 | 3401.8 | --- | --- | --- | --- | Operation time | hh.hh | 3711.4 | 3711.4 | 3711.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3711.4 | 3711.4 | --- | --- | --- | --- | Operation time | hh.hh | 3953.8 | 3953.8 | 3953.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3953.8 | 3953.8 | --- | --- | --- | --- | Operation time | hh.hh | 3070.7 | 3070.7 | 3070.7 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3070.7 | 3070.7 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 130
E-Mail Address (optional) |  | Stage 1 and 2 -- Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 9.16 |  |  |  | 1998-01-18 | 23:00 | 2515.79 | 24.4444 | 102 | 70 | 10.1667 | 0 | 17.4 | 3 |  | 20.4 | 20.4 | 0.85294 | 0 | 17.8462 | 18.6859 | 13.6161 | 62.2172 | 0.30033 | 7.52 | 6.64 | 54.069 | 383.46 | 403.2 | 2462.46 | 2428.1598 | 1.3929 | 86.59 | 1415.6799 | 96.1807 | 102 | 80 | 9.4 | 10.4 | 10 | 20.4 | 20.4 | 0.49721 | 0.5098 | 16 | 16.7529 | 5.4453 | 76.1547 | 0.21998 | 6.64 | NA | 44.958 | 403.2 | 845.46 | 775.7717 | 8.2427 | 88.8497 | 589.4858 | 92.3734 | 80 | 68 | 10.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8011 | 51.7989 | 0.29854 | NA | NA | 48.09 | 845.46 | 1626.88 | 1610.9352 | 0.98008 | 88.0729 | 1228.1976 | 96.0845 | 120 | 70 | 10.7 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 20.8702 | 63.4298 | 0.31128 | NA | 7.34 | 99.792 | 1626.88 | 2462.46 | 2746.7445 | -11.5447 | 75.25 | 2186.8123 | 95.4366 | pH | --- | 5.69 | 6.55 | 7.1 | --- | --- | --- | --- | --- | pH | --- | 5.85 | 6.55 | --- | --- | --- | --- | pH | --- | 5.69 | 6.57 | 7.1 | --- | --- | --- | --- | --- | pH | --- | 5.83 | 6.57 | --- | --- | --- | --- | pH | --- | 5.74 | 6.6 | 7.15 | --- | --- | --- | --- | --- | pH | --- | 5.86 | 6.6 | --- | --- | --- | --- | pH | --- | 5.64 | 6.45 | 7.01 | --- | --- | --- | --- | --- | pH | --- | 5.79 | 6.45 | --- | --- | --- | --- | pH | --- | 5.66 | 6.45 | 6.97 | --- | --- | --- | --- | --- | pH | --- | 5.76 | 6.45 | --- | --- | --- | --- | pH | --- | 5.67 | 6.55 | 7.11 | --- | --- | --- | --- | --- | pH | --- | 5.82 | 6.55 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | ~20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.8125 | Calcium (mg/L) | 56 |  |  |  | 1998-01-19 | 8:05 | 2524.94 | 24.4444 | 102 | 70 | 10.2667 | 0 | 17.6 | 3 |  | 20.6 | 20.6 | 0.85437 | 0 | 18.0513 | 18.9007 | 14.0311 | 61.7023 | 0.30632 | 7.5 | 6.67 | 53.198 | 390.1 | 409.92 | 2528.24 | 2502.6891 | 1.0106 | 87.0223 | 1456.3045 | 96.3471 | 102 | 80 | 9.6 | 10.6 | 10 | 20.6 | 20.6 | 0.50048 | 0.51456 | 16.3077 | 17.075 | 5.5875 | 75.8125 | 0.22523 | 6.67 | NA | 44.722 | 409.92 | 860.31 | 797.0299 | 7.3555 | 89.0901 | 603.4749 | 92.5893 | 80 | 68 | 10.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 12.0177 | 51.5823 | 0.2998 | NA | NA | 48.3 | 860.31 | 1676.48 | 1639.8396 | 2.1856 | 88.2172 | 1250.0748 | 96.1362 | 120 | 70 | 10.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 21.5397 | 62.6603 | 0.3151 | NA | 7.26 | 100.408 | 1676.48 | 2528.24 | 2832.2661 | -12.0252 | 75.5055 | 2254.3731 | 95.5461 | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | --- | --- | --- | --- | Temperature | oC | 21.1 | 24 | 25.3 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24 | --- | --- | --- | --- | Temperature | oC | 23.4 | 24.3 | 23.8 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24.3 | --- | --- | --- | --- | Temperature | oC | 23.5 | 23.2 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 23.5 | 23.2 | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | 24.4 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 67%
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.875 | Barium (mg/L) | < 0.05 |  |  |  | 1998-01-19 | 16:15 | 2533.28 | 24.4444 | 102 | 70 | 10.0333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 11.7157 | 64.251 | 0.28916 | 7.56 | 6.56 | 47.905 | 330.34 | 357 | 2150.72 | 2081.9495 | 3.1976 | 86.5812 | 1219.4748 | 96.0717 | 102 | 80 | 9.6 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.5918 | 4.7187 | 76.6813 | 0.21637 | 6.56 | NA | 44.486 | 357 | 736.56 | 675.7024 | 8.2624 | 87.5389 | 516.3512 | 91.3845 | 80 | 66 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.2256 | 52.5744 | 0.29414 | NA | NA | 45.64 | 736.56 | 1391.28 | 1399.8432 | -0.61549 | 87.2157 | 1068.2016 | 95.7274 | 120 | 70 | 10.3 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.5205 | 67.1795 | 0.29391 | NA | 7.34 | 98.098 | 1391.28 | 2150.72 | 2309.0221 | -7.3604 | 72.5216 | 1850.151 | 94.6978 | Alkalinity | mg/L as CaCO3 | 16 | 126 | 610 | 749.3333 | -22.8415 | 87.3016 | 437.6667 | 96.3442 | Alkalinity | mg/L as CaCO3 | 16 | 126 | 238.1359 | 87.3016 | 182.068 | 91.2121 | Alkalinity | mg/L as CaCO3 | 16 | 117 | 615 | 689.3333 | -12.0867 | 86.3248 | 403.1667 | 96.0314 | Alkalinity | mg/L as CaCO3 | 16 | 117 | 224 | 86.3248 | 170.5 | 90.6158 | Alkalinity | mg/L as CaCO3 | 15 | 124 | 674 | 741.6667 | -10.0396 | 87.9032 | 432.8333 | 96.5345 | Alkalinity | mg/L as CaCO3 | 15 | 124 | 236.796 | 87.9032 | 180.398 | 91.6851 | Alkalinity | mg/L as CaCO3 | 16 | 107 | 533 | 603.7705 | -13.2778 | 85.0467 | 355.3852 | 95.4978 | Alkalinity | mg/L as CaCO3 | 15 | 107 | 199.9388 | 85.9813 | 153.4694 | 90.2261 | Alkalinity | mg/L as CaCO3 | 16 | 109 | 556 | 623.6 | -12.1583 | 85.3211 | 366.3 | 95.632 | Alkalinity | mg/L as CaCO3 | 10 | 109 | 210.0412 | 90.8257 | 159.5206 | 93.7312 | Alkalinity | mg/L as CaCO3 | 16 | 117 | 598 | 689.3333 | -15.2731 | 86.3248 | 403.1667 | 96.0314 | Alkalinity | mg/L as CaCO3 | 16 | 117 | 224 | 86.3248 | 170.5 | 90.6158 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | Strontium (mg/L) | 0.49 |  |  |  | 1998-01-20 | 0:15 | 2541.17 | 24.4444 | 100 | 70 | 10.1 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 18.1538 | 19.0081 | 13.6283 | 61.2717 | 0.31023 | 7.58 | 6.66 | 49.781 | 364.37 | 394.8 | 2300.87 | 2430.4121 | -5.6301 | 87.3908 | 1412.6061 | 96.4759 | 100 | 80 | 9.6 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | 5.3764 | 75.0236 | 0.22974 | 6.66 | NA | 44.545 | 394.8 | 778.14 | 769.5729 | 1.101 | 88.7171 | 582.1864 | 92.3487 | 80 | 65 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.8244 | 51.4756 | 0.30042 | NA | NA | 46.76 | 778.14 | 1557.44 | 1480.2648 | 4.9553 | 88.156 | 1129.2024 | 95.859 | 120 | 70 | 10.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 19.9349 | 64.5651 | 0.30581 | NA | 7.33 | 98.791 | 1557.44 | 2300.87 | 2627.1159 | -14.1792 | 74.977 | 2092.278 | 95.2783 | Total dissolved solids | mg/L | 36.6 | 347 | 1390 | 2105.9333 | -51.506 | 89.4524 | 1226.4667 | 97.0158 | Total dissolved solids | mg/L | 34 | 347 | 666.0777 | 90.2017 | 506.5388 | 93.2878 | Total dissolved solids | mg/L | 34 | 330 | 1400 | 2007.3333 | -43.381 | 89.697 | 1168.6667 | 97.0907 | Total dissolved solids | mg/L | 33 | 330 | 644.6436 | 90 | 487.3218 | 93.2283 | Total dissolved solids | mg/L | 34 | 334 | 1434 | 2034 | -41.841 | 89.8204 | 1184 | 97.1284 | Total dissolved solids | mg/L | 31 | 334 | 647.5522 | 90.7186 | 490.7761 | 93.6835 | Total dissolved solids | mg/L | 38 | 346 | 1346 | 2027.377 | -50.6224 | 89.0173 | 1186.6885 | 96.7978 | Total dissolved solids | mg/L | 37 | 346 | 658.1531 | 89.3064 | 502.0765 | 92.6306 | Total dissolved solids | mg/L | 36 | 336 | 1365 | 1996 | -46.2271 | 89.2857 | 1166 | 96.9125 | Total dissolved solids | mg/L | 34 | 336 | 644.2268 | 89.881 | 490.1134 | 93.0628 | Total dissolved solids | mg/L | 34 | 327 | 1379 | 1987.3333 | -44.1141 | 89.6024 | 1157.1667 | 97.0618 | Total dissolved solids | mg/L | 32 | 327 | 639.5248 | 90.2141 | 483.2624 | 93.3783 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | Reactive silica (mg/L as SiO2) | 8.41 |  |  |  | 1998-01-20 | 8:00 | 2548.95 | 24.4444 | 102 | 72 | 10.2333 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.7784 | 62.9883 | 0.29495 | 7.59 | 6.65 | 52.126 | 418.32 | 424.2 | 2579.72 | 2435.7251 | 5.5818 | 87.7119 | 1429.9625 | 96.3547 | 102 | 80 | 9.7 | 10.3 | 10.2 | 20.5 | 20.5 | 0.50211 | 0.50244 | 15.8462 | 16.5918 | 5.7232 | 75.5768 | 0.21954 | 6.65 | NA | 43.896 | 424.2 | 868.23 | 808.2325 | 6.9103 | 89.6521 | 616.2162 | 92.8765 | 80 | 68 | 10.5 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 12.1692 | 51.3308 | 0.30126 | NA | NA | 45.99 | 868.23 | 1678.96 | 1657.5804 | 1.2734 | 89.1584 | 1262.9052 | 96.3584 | 120 | 72 | 10.5 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.1683 | 64.3317 | 0.30692 | NA | 7.46 | 103.642 | 1678.96 | 2579.72 | 2761.9911 | -7.0655 | 75.5677 | 2220.4756 | 95.3324 | Total hardness | mg/L as CaCO3 | 11 | 205 | 1058 | 1304.3333 | -23.2829 | 94.6341 | 754.6667 | 98.5424 | Total hardness | mg/L as CaCO3 | 12 | 205 | 401.7476 | 94.1463 | 303.3738 | 96.0445 | Total hardness | mg/L as CaCO3 | 11 | 192 | 1160 | 1217.6667 | -4.9713 | 94.2708 | 704.8333 | 98.4393 | Total hardness | mg/L as CaCO3 | 12 | 192 | 382.6931 | 93.75 | 287.3465 | 95.8239 | Total hardness | mg/L as CaCO3 | 10 | 194 | 1146 | 1236.6667 | -7.9116 | 94.8454 | 715.3333 | 98.6021 | Total hardness | mg/L as CaCO3 | 11 | 194 | 383.3731 | 94.3299 | 288.6866 | 96.1896 | Total hardness | mg/L as CaCO3 | 10 | 194 | 1079 | 1198.459 | -11.0713 | 94.8454 | 696.2295 | 98.5637 | Total hardness | mg/L as CaCO3 | 14 | 194 | 375.8367 | 92.7835 | 284.9184 | 95.0863 | Total hardness | mg/L as CaCO3 | 11 | 196 | 1120 | 1219.6667 | -8.8988 | 94.3878 | 707.8333 | 98.446 | Total hardness | mg/L as CaCO3 | 10 | 196 | 385.8351 | 94.898 | 290.9175 | 96.5626 | Total hardness | mg/L as CaCO3 | 11 | 191 | 1120 | 1211 | -8.125 | 94.2408 | 701 | 98.4308 | Total hardness | mg/L as CaCO3 | 11 | 191 | 381.6931 | 94.2408 | 286.3465 | 96.1585 | Natural Gas Rate ($/ft3) | 0.2714¢/therm
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.293 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | Turbidity (ntu) | 0.5 |  |  |  | 1998-01-20 | 19:00 | 2559.98 | 24.4444 | 102 | 70 | 10.2 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.1675 | 62.6325 | 0.29663 | 7.57 | 6.65 | 52.662 | 395.08 | 408.24 | 2328.04 | 2330.5836 | -0.10926 | 87.1002 | 1369.4118 | 96.1544 | 102 | 80 | 9.8 | 10.3 | 10.2 | 20.5 | 20.5 | 0.50211 | 0.50244 | 15.8462 | 16.5918 | 5.4759 | 75.7241 | 0.21911 | 6.65 | NA | 44.368 | 408.24 | 819.72 | 775.6794 | 5.3726 | 89.1319 | 591.9597 | 92.5049 | 80 | 68 | 10.3 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 11.503 | 52.197 | 0.29627 | NA | NA | 47.6 | 819.72 | 1568.6 | 1576.0824 | -0.47701 | 88.3402 | 1197.9012 | 96.0264 | 120 | 70 | 10.5 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 19.7702 | 64.7298 | 0.30503 | NA | 7.39 | 97.328 | 1568.6 | 2328.04 | 2580.0995 | -10.8271 | 76.1591 | 2074.3497 | 95.308 | Calcium hardness | mg/L as CaCO3 | 10 | 184 | 1008 | 1170 | -16.0714 | 94.5652 | 677 | 98.5229 | Calcium hardness | mg/L as CaCO3 | 11 | 184 | 360.3592 | 94.0217 | 272.1796 | 95.9586 | Calcium hardness | mg/L as CaCO3 | 11 | 180 | 1052 | 1137.6667 | -8.1432 | 93.8889 | 658.8333 | 98.3304 | Calcium hardness | mg/L as CaCO3 | 11 | 180 | 359.0396 | 93.8889 | 269.5198 | 95.9187 | Calcium hardness | mg/L as CaCO3 | 10 | 181 | 1105 | 1150 | -4.0724 | 94.4751 | 665.5 | 98.4974 | Calcium hardness | mg/L as CaCO3 | 8 | 181 | 360.0249 | 95.5801 | 270.5124 | 97.0426 | Calcium hardness | mg/L as CaCO3 | 9 | 180 | 1018 | 1113.4918 | -9.3803 | 95 | 646.7459 | 98.6084 | Calcium hardness | mg/L as CaCO3 | 12 | 180 | 349.7143 | 93.3333 | 264.8571 | 95.4693 | Calcium hardness | mg/L as CaCO3 | 9 | 183 | 1003 | 1145.8 | -14.2373 | 95.082 | 664.4 | 98.6454 | Calcium hardness | mg/L as CaCO3 | 10 | 183 | 359.567 | 94.5355 | 271.2835 | 96.3138 | Calcium hardness | mg/L as CaCO3 | 9 | 180 | 1034 | 1149 | -11.1219 | 95 | 664.5 | 98.6456 | Calcium hardness | mg/L as CaCO3 | 11 | 180 | 359.0396 | 93.8889 | 269.5198 | 95.9187 | Current Process Water Rate ($/1000 gal) | 0.21*
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 16.375 | SDI | 4.67 |  |  |  | 1998-01-20 | 22:00 | 2562.84 | 24.4444 | 102 | 70 | 10.2333 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 17.641 | 18.4711 | 13.5939 | 62.1728 | 0.29709 | 7.58 | 6.65 | 52.193 | 409.19 | 420.84 | 2496.78 | 2402.3176 | 3.7834 | 87.5979 | 1411.5788 | 96.3025 | 102 | 80 | 9.8 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 16.4307 | 5.6497 | 75.5503 | 0.21748 | 6.65 | NA | 44.191 | 420.84 | 837.54 | 797.489 | 4.782 | 89.4993 | 609.1645 | 92.7456 | 80 | 68 | 10.4 | 4.8 | 4.8 | 9.6 | 9.6 | 0.47104 | 0.5 | 14.7692 | 15.4642 | 11.8617 | 51.7383 | 0.29889 | NA | NA | 46.76 | 837.54 | 1608.28 | 1628.32 | -1.2461 | 88.8889 | 1232.93 | 96.2074 | 120 | 70 | 10.5 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 20.2734 | 64.2266 | 0.30742 | NA | 7.43 | 99.561 | 1608.28 | 2496.78 | 2645.5243 | -5.9574 | 76.3423 | 2126.9022 | 95.319 | Turbidity | ntu | 0.01 | 0.06 | 37 | 0.34333 | 99.0721 | 83.3333 | 0.20167 | 95.0413 | Turbidity | ntu | 0.03 | 0.06 | 0.090583 | 50 | 0.075291 | 60.1547 | Turbidity | ntu | BMRL | 0.03 | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.03 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.03 | 38 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.03 | 0.040348 | 33.3333 | 0.035174 | 43.14 | Turbidity | ntu | BMRL | 0.04 | 29 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.03 | 0.04 | 0.050102 | 25 | 0.045051 | 33.4088 | Turbidity | ntu | BMRL | 0.04 | 27 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 0.04 | 0.070619 | 75 | 0.055309 | 81.9199 | Turbidity | ntu | 0.01 | 0.03 | 28 | 0.14333 | 99.4881 | 66.6667 | 0.086667 | 88.4615 | Turbidity | ntu | BMRL | 0.03 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | Feed flow rate to system, QF-sys (gpm) | 19.2647 | MFI | NA |  |  |  | 1998-01-21 | 8:00 | 2573.81 | 25.5556 | 102 | 70 | 10 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 17.9782 | 14.3435 | 61.6565 | 0.29159 | 7.66 | 6.67 | 51.657 | 409.19 | 430.08 | 2548.26 | 2541.9245 | 0.24862 | 87.989 | 1486.0022 | 96.5238 | 102 | 80 | 9.8 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.0557 | 5.8257 | 75.3743 | 0.21301 | 6.67 | NA | 44.25 | 430.08 | 860.31 | 823.5502 | 4.2729 | 89.7112 | 626.8151 | 92.9405 | 80 | 68 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 12.055 | 51.745 | 0.2892 | NA | NA | 45.78 | 860.31 | 1674 | 1642.2588 | 1.8961 | 89.3555 | 1251.2844 | 96.3414 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 21.3123 | 63.6877 | 0.3 | NA | 7.45 | 100.947 | 1674 | 2548.26 | 2790.3602 | -9.5006 | 76.5283 | 2232.1801 | 95.4776 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.16 | 5.85 | 11.6505 | 97.265 | 8.7502 | 98.1715 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.36 | 6 | 11.975 | 94 | 8.9875 | 95.9944 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.25 | 6.65 | 13.2729 | 96.2406 | 9.9614 | 97.4903 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.25 | 5.31 | 10.4216 | 95.2919 | 7.8658 | 96.8217 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.29 | 5.05 | 9.9081 | 94.2574 | 7.4791 | 96.1225 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.32 | 5.7 | 11.3996 | 94.386 | 8.5498 | 96.2572
|  | Minimum flow rate to the element, QI, min (gpm) | 6.5 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.8897 | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-01-21 | 15:00 | 2579.95 | 24.4444 | 102 | 70 | 10.1333 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 17.641 | 18.4711 | 14.0919 | 61.7747 | 0.29901 | 7.59 | 6.58 | 52.126 | 403.38 | 434.28 | 2536.82 | 2488.3578 | 1.9104 | 87.9971 | 1461.3189 | 96.4329 | 102 | 80 | 9.8 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 16.4307 | 5.8469 | 75.3531 | 0.21805 | 6.58 | NA | 44.486 | 434.28 | 886.05 | 824.074 | 6.9946 | 89.7564 | 629.177 | 92.9295 | 80 | 68 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 12.4101 | 51.3899 | 0.30092 | NA | NA | 47.53 | 886.05 | 1645.48 | 1691.0292 | -2.7681 | 89.0554 | 1288.5396 | 96.3113 | 120 | 70 | 10.4 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 20.7309 | 63.8691 | 0.30914 | NA | 7.47 | 102.718 | 1645.48 | 2536.82 | 2706.1289 | -6.6741 | 76.3475 | 2175.8044 | 95.2791 | Total organic carbon | mg/L | 0.21 | 5.85 | 31.43 | 37.81 | -20.2991 | 96.4103 | 21.83 | 99.038 | UV254 | cm-1 | 0.003 | 0.223 | 0.44727 | 98.6547 | 0.33514 | 99.1048 | Total organic carbon | mg/L | 0.11 | 6 | 34.7 | 39.3767 | -13.4774 | 98.1667 | 22.6883 | 99.5152 | UV254 | cm-1 | BMRL | 0.213 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.49 | 6.65 | 31.45 | 41.5567 | -32.1357 | 92.6316 | 24.1033 | 97.9671 | UV254 | cm-1 | 0.002 | 0.22 | 0.44559 | 99.0909 | 0.3328 | 99.399 | Total organic carbon | mg/L | 0.18 | 5.31 | 30.75 | 33.3148 | -8.3407 | 96.6102 | 19.3124 | 99.068 | UV254 | cm-1 | 0.004 | 0.213 | 0.42413 | 98.1221 | 0.31857 | 98.7444 | Total organic carbon | mg/L | 0.16 | 5.05 | 30.8 | 32.108 | -4.2468 | 96.8317 | 18.579 | 99.1388 | UV254 | cm-1 | 0.001 | 0.209 | 0.42129 | 99.5215 | 0.31514 | 99.6827 | Total organic carbon | mg/L | 0.09 | 5.7 | 35.1 | 37.49 | -6.8091 | 98.4211 | 21.595 | 99.5832 | UV254 | cm-1 | BMRL | 0.211 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Hialeah Water Treatment | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  | TOC (mg/L) | 11.35 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-01-21 | 22:00 | 2586.99 | 24.4444 | 100 | 70 | 10.2333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.5006 | 61.2661 | 0.30324 | 7.64 | 6.65 | 53.734 | 395.91 | 409.92 | 2360.93 | 2397.6677 | -1.5561 | 86.8916 | 1403.7938 | 96.1722 | 100 | 80 | 9.9 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.5918 | 5.4607 | 74.6393 | 0.22229 | 6.65 | NA | 48.262 | 409.92 | 820.71 | 778.7395 | 5.1139 | 88.2265 | 594.3298 | 91.8796 | 80 | 66 | 10.3 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4524 | 51.2476 | 0.30175 | NA | NA | 46.9 | 820.71 | 1566.12 | 1563.5676 | 0.16298 | 88.5587 | 1192.1388 | 96.0659 | 120 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.9363 | 64.5637 | 0.30581 | NA | 7.42 | 94.633 | 1566.12 | 2360.93 | 2610.4011 | -10.5666 | 76.9143 | 2088.2605 | 95.4683 | UV254 | cm-1 | 0.001 | 0.223 | 1.128 | 1.481 | -31.2943 | 99.5516 | 0.852 | 99.8826 | SUVA | L/(mg*m) | 1.875 | 3.812 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.213 | 1.179 | 1.4143 | -19.9604 | 99.5305 | 0.81367 | 99.8771 | SUVA | L/(mg*m) | #VALUE! | 3.55 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.22 | 1.21 | 1.461 | -20.7438 | 99.5455 | 0.8405 | 99.881 | SUVA | L/(mg*m) | 0.8 | 3.3083 | --- | --- | --- | --- | UV254 | cm-1 | 0.003 | 0.213 | 1.174 | 1.3594 | -15.7916 | 98.5915 | 0.7862 | 99.6184 | SUVA | L/(mg*m) | 1.6 | 4.0113 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.209 | 1.073 | 1.3599 | -26.7412 | 99.5215 | 0.78447 | 99.8725 | SUVA | L/(mg*m) | 0.34483 | 4.1386 | --- | --- | --- | --- | UV254 | cm-1 | 0.002 | 0.211 | 1.196 | 1.3953 | -16.6667 | 99.0521 | 0.80317 | 99.751 | SUVA | L/(mg*m) | #VALUE! | 3.7018 | --- | --- | --- | ---
Treatment Plant Category | Softening | Feed spacer thickness, T (ft) | 0.00258 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-01-22 | 8:50 | 2597.77 | 24.4444 | 100 | 70 | 10.3333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.9038 | 60.7628 | 0.31282 | 7.66 | 6.64 | 52.595 | 396.74 | 413.28 | 2350.92 | 2472.675 | -5.179 | 87.2738 | 1442.9775 | 96.3551 | 100 | 80 | 10 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.5054 | 74.4946 | 0.22705 | 6.64 | NA | 48.616 | 413.28 | 824.67 | 785.0249 | 4.8074 | 88.2365 | 599.1524 | 91.8859 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.6518 | 52.1482 | 0.3089 | NA | NA | 47.88 | 824.67 | 1562.4 | 1601.46 | -2.5 | 88.4146 | 1213.065 | 96.053 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.9057 | 64.2943 | 0.30709 | NA | 7.45 | 93.17 | 1562.4 | 2350.92 | 2605.0794 | -10.8111 | 77.456 | 2083.7397 | 95.5287 | SUVA | L/(mg*m) | 0.47619 | 3.812 | 3.5889 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.90909 | 3.55 | 3.3977 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.20408 | 3.3083 | 3.8474 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.6667 | 4.0113 | 3.8179 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.625 | 4.1386 | 3.4838 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 2.2222 | 3.7018 | 3.4074 | --- | --- | --- | --- | ---
Process Train Name | Hialeah WTP | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 11.1397 | [5 empty] | 1998-01-22 | 16:00 | 2605.51 | 24.4444 | 102 | 70 | 9.9667 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 12.164 | 63.8694 | 0.29088 | 7.62 | 6.57 | 47.838 | 359.39 | 368.76 | 2350.92 | 2159.7118 | 8.1333 | 87.0273 | 1264.2359 | 96.2161 | 102 | 80 | 9.5 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.5918 | 4.8347 | 76.6653 | 0.21642 | 6.57 | NA | 48.557 | 368.76 | 828.63 | 695.3037 | 16.09 | 86.8324 | 532.0318 | 90.8733 | 80 | 68 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.5965 | 52.2035 | 0.29623 | NA | NA | 45.08 | 828.63 | 1469.4 | 1580.838 | -7.5839 | 87.7752 | 1204.734 | 96.2581 | 120 | 70 | 10.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.5737 | 66.2263 | 0.29814 | NA | 7.36 | 98.483 | 1469.4 | 2350.92 | 2442.3088 | -3.8874 | 73.2935 | 1955.8544 | 94.9647 | Bromide | mg/L | 13 | 84 | --- | 486.3333 | --- | 84.5238 | 285.1667 | 95.4413 | [8 empty] | Bromide | mg/L | 14 | 68 | --- | 374 | --- | 79.4118 | 221 | 93.6652 | [8 empty] | Bromide | mg/L | 6 | 98 | --- | 619.3333 | --- | 93.8776 | 358.6667 | 98.3271 | [8 empty] | Bromide | mg/L | 10 | 72 | --- | 410.459 | --- | 86.1111 | 241.2295 | 95.8546 | [8 empty] | Bromide | mg/L | 12 | 67 | --- | 371.3333 | --- | 82.0896 | 219.1667 | 94.5247 | [8 empty] | Bromide | mg/L | 13 | 65 | --- | 359.6667 | --- | 80 | 212.3333 | 93.8776
ICR Treatment Plant Identification Number | 302 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4522 | [5 empty] | 1998-01-22 | 22:00 | 2610.78 | 24.4444 | 100 | 70 | 10.2 | 0 | 17.5 | 3.1 |  | 20.6 | 20.6 | 0.84951 | 0 | 17.9487 | 18.7933 | 13.5521 | 61.2479 | 0.30684 | 7.63 | 6.65 | 49.513 | 379.31 | 404.04 | 2355.21 | 2405.4021 | -2.1311 | 87.7455 | 1404.721 | 96.4752 | 100 | 80 | 9.8 | 10.3 | 10.3 | 20.6 | 20.6 | 0.50538 | 0.5 | 15.8462 | 16.5918 | 5.4429 | 74.7571 | 0.22194 | 6.65 | NA | 41.182 | 404.04 | 738.54 | 766.898 | -3.8397 | 89.8074 | 585.469 | 92.966 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 10.3714 | 53.4286 | 0.3015 | NA | NA | 47.11 | 738.54 | 1511.56 | 1429.97 | 5.3977 | 88.3403 | 1084.255 | 95.6551 | 120 | 70 | 10.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.1773 | 65.2227 | 0.30272 | NA | 7.41 | 96.096 | 1511.56 | 2355.21 | 2516.0828 | -6.8305 | 76.2162 | 2013.8214 | 95.2282 | SDS-Cl2 dose | mg/L | 2.8 | 11.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 2.7 | 11 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 2.7 | 11 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.3 | 11.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 2.7 | 11 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4130871 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 0.57721 | [5 empty] | 1998-01-23 | 8:00 | 2621.05 | 24.4444 | 102 | 70 | 10.1 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.5417 | 62.3583 | 0.29793 | 7.68 | 6.6 | 50.116 | 366.86 | 415.8 | 2350.92 | 2392.7791 | -1.7805 | 87.9471 | 1404.2896 | 96.4312 | 102 | 80 | 9.7 | 10.3 | 10.2 | 20.5 | 20.5 | 0.50211 | 0.50244 | 15.8462 | 16.5918 | 5.5995 | 75.7005 | 0.21918 | 6.6 | NA | 43.719 | 415.8 | 834.57 | 791.5289 | 5.1573 | 89.4856 | 603.6644 | 92.7577 | 80 | 68 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.6047 | 52.1953 | 0.29628 | NA | NA | 50.47 | 834.57 | 1620.68 | 1587.306 | 2.0593 | 87.862 | 1210.938 | 95.8322 | 120 | 70 | 10.4 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 20.5032 | 64.0968 | 0.30804 | NA | 7.42 | 94.864 | 1620.68 | 2350.92 | 2669.6785 | -13.5589 | 77.1852 | 2145.1793 | 95.5778 | SDS-Free Cl2 residual | mg/L | 0.96 | 1.67 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.66 | 0.65 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | NR | 0.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.73 | 0.22 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46939 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 0.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47423 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.64 | 0.7 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48
Historical Minimum Water Temperature (oC) | 23 | Stage 1 and 2 -- Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-01-23 | 15:45 | 2627.42 | 24.4444 | 102 | 70 | 10 | 0 | 17.5 | 3.1 |  | 20.6 | 20.6 | 0.84951 | 0 | 17.9487 | 18.7933 | 13.7692 | 62.2308 | 0.30199 | 7.62 | 6.42 | 49.714 | 373.5 | 409.92 | 2342.34 | 2443.341 | -4.312 | 87.8723 | 1426.6305 | 96.5153 | 102 | 80 | 9.6 | 10.3 | 10.3 | 20.6 | 20.6 | 0.50538 | 0.5 | 15.8462 | 16.5918 | 5.5063 | 75.8937 | 0.21862 | 6.42 | NA | 42.834 | 409.92 | 790.02 | 777.006 | 1.6473 | 89.5506 | 593.463 | 92.7824 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.1321 | 52.6679 | 0.30585 | NA | NA | 47.88 | 790.02 | 1607.04 | 1532.16 | 4.6595 | 88.3197 | 1161.09 | 95.8763 | 120 | 70 | 10.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.4667 | 64.3333 | 0.30691 | NA | 7.4 | 96.404 | 1607.04 | 2342.34 | 2679.1043 | -14.3773 | 76.4822 | 2143.0721 | 95.5016 | SDS-Cl2 demand | mg/L | 1.84 | 9.83 | --- | 55.1067 | --- | 81.2818 | 32.4683 | 94.3329 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 5 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.04 | 10.35 | --- | 57.44 | --- | 80.2899 | 33.895 | 93.9814 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.8 |  |  |  |  | SDS-Cl2 demand | mg/L | NR | 10.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.57 | 11.28 | --- | 58.828 | --- | 77.2163 | 35.054 | 92.6685 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.5 | 11.8 | --- | 63.26 | --- | 78.8136 | 37.53 | 93.3387 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.06 | 10.3 | --- | 56.9933 | --- | 80 | 33.6467 | 93.8776 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.8
Historical Average Water Temperature (oC) | 26 | Design cross-flow velocity (fps) | 0.75 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-01-23 | 22:25 | 2634.11 | 24.4444 | 100 | 70 | 10.7333 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.5954 | 60.6713 | 0.30622 | 7.59 | 6.47 | 51.188 | 398.4 | 418.32 | 2558.27 | 2403.1274 | 6.0644 | 87.7634 | 1410.7237 | 96.3715 | 100 | 80 | 11 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 5.7096 | 73.2904 | 0.22199 | 6.47 | NA | 33.984 | 418.32 | 846.45 | 791.5694 | 6.4836 | 91.8761 | 604.9447 | 94.3823 | 80 | 68 | 10.6 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.9786 | 51.4215 | 0.31326 | NA | NA | 47.88 | 846.45 | 1678.96 | 1645.02 | 2.0215 | 88.5542 | 1245.735 | 96.1565 | 120 | 70 | 10.6 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.2822 | 63.1178 | 0.31282 | NA | 7.34 | 95.172 | 1678.96 | 2558.27 | 2767.8142 | -8.1909 | 77.249 | 2223.3871 | 95.7195 | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 10.3 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 10.1 |  |  |  |  | SDS-Chlorination temp. | oC | NR | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 10.05 |  |  |  |  | SDS-Chlorination temp. | oC | 23 | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.8 |  |  |  |  | SDS-Chlorination temp. | oC | 25.5 | 26 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.7 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 10.1
State Approved Plant Capacity (MGD) | 60 | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1.8603 | [5 empty] | 1998-01-24 | 9:00 | 2645.38 | 24.4444 | 100 | 72 | 10.5 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.2931 | 62.2069 | 0.29866 | 7.56 | 6.49 | 51.791 | 395.91 | 410.76 | 2486.77 | 2351.4362 | 5.4422 | 87.3914 | 1381.0981 | 96.25 | 100 | 80 | 10.4 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 5.5508 | 74.0492 | 0.21971 | 6.49 | NA | 37.111 | 410.76 | 834.57 | 773.6307 | 7.3019 | 90.9653 | 592.1953 | 93.7333 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8287 | 51.6713 | 0.31175 | NA | NA | 45.99 | 834.57 | 1693.84 | 1623.15 | 4.1734 | 88.8037 | 1228.86 | 96.2575 | 120 | 72 | 10.6 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.4148 | 63.9852 | 0.30858 | NA | 7.42 | 100.177 | 1693.84 | 2486.77 | 2789.4833 | -12.173 | 75.6118 | 2241.6617 | 95.5311 | SDS-Chlorination pH | --- | 5.91 | 6.52 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.88 | 6.68 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | 6.68 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.67 | 6.28 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.69 | 6.68 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.61 | 6.75 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 17 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.0478 | [5 empty] | 1998-01-24 | 15:00 | 2651.9 | 25 | 100 | 72 | 10.2667 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.2759 | 13.0534 | 62.68 | 0.29157 | 7.54 | 6.47 | 55.744 | 390.93 | 408.24 | 2461.03 | 2313.9215 | 5.9775 | 86.3453 | 1361.0808 | 95.9044 | 100 | 80 | 10.2 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.0046 | 5.4941 | 74.3059 | 0.21539 | 6.47 | NA | 38.409 | 408.24 | 851.4 | 767.4028 | 9.8658 | 90.5916 | 587.8214 | 93.4659 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 15.8462 | 12.0528 | 51.7472 | 0.30622 | NA | NA | 47.88 | 851.4 | 1643 | 1654.92 | -0.7255 | 88.2716 | 1253.16 | 96.1793 | 120 | 72 | 10.4 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.4229 | 20.7617 | 64.8383 | 0.29956 | NA | 7.34 | 97.944 | 1643 | 2461.03 | 2705.226 | -9.9225 | 76.0082 | 2174.113 | 95.495 | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NR | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 5 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -0.077206 | [5 empty] | 1998-01-25 | 0:00 | 2659.54 | 24.4444 | 102 | 70 | 10.4333 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.8135 | 61.7532 | 0.30085 | 7.59 | 6.56 | 43.617 | 402.55 | 416.64 | 2432.43 | 2433.2956 | -0.035586 | 89.5312 | 1424.9678 | 96.9391 | 102 | 80 | 10.2 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 5.6145 | 75.1855 | 0.21639 | 6.56 | NA | 38.704 | 416.64 | 846.45 | 783.674 | 7.4164 | 90.7104 | 600.157 | 93.551 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.9911 | 51.5089 | 0.31273 | NA | NA | 47.04 | 846.45 | 1671.52 | 1645.86 | 1.5351 | 88.7097 | 1246.155 | 96.2252 | 120 | 70 | 10.6 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.0849 | 63.3151 | 0.31184 | NA | 7.4 | 102.41 | 1671.52 | 2432.43 | 2750.2831 | -13.0673 | 75.42 | 2210.9016 | 95.368 | SDS-TOX | mg Cl- /L | BMRL | 390 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 330 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | 315 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 280 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 385 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 385 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | Chloride ion rejection = 85 % | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-01-25 | 8:00 | 2668.58 | 24.4444 | 100 | 70 | 10.3 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.6393 | 61.0607 | 0.30426 | 7.44 | 6.56 | 43.282 | 405.04 | 411.6 | 2431 | 2402.8192 | 1.1592 | 89.4845 | 1407.2096 | 96.9243 | 100 | 80 | 10.2 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 5.5432 | 74.2568 | 0.2191 | 6.56 | NA | 38.468 | 411.6 | 840.51 | 773.9686 | 7.9168 | 90.654 | 592.7843 | 93.5106 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8895 | 51.9106 | 0.31031 | NA | NA | 47.88 | 840.51 | 1643 | 1633.14 | 0.60012 | 88.3673 | 1236.825 | 96.1288 | 120 | 70 | 10.5 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 20.7006 | 63.7994 | 0.30948 | NA | 7.41 | 102.487 | 1643 | 2431 | 2702.1027 | -11.1519 | 75.1003 | 2172.5513 | 95.2826 | SDS-CHCl3 | mg/L | BMRL | 40.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-01-28 | 1998-01-28 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 33.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | 27.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-02-25 | 1998-02-25 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 27.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-03-11 | 1998-03-11 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 28.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-03-25 | 1998-03-25 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 29.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | at 500 mg/L NaCL solution | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-01-25 | 15:20 | 2675.1 | 24.4444 | 100 | 70 | 10.3333 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.6669 | 60.9997 | 0.30457 | 7.62 | 6.59 | 45.895 | 396.74 | 414.96 | 2519.66 | 2410.2177 | 4.3435 | 88.9399 | 1412.5888 | 96.751 | 100 | 80 | 10.4 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 5.6053 | 73.9947 | 0.21988 | 6.59 | NA | 37.642 | 414.96 | 833.58 | 781.3938 | 6.2605 | 90.9288 | 598.1769 | 93.7072 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8065 | 51.9935 | 0.30982 | NA | NA | 46.48 | 833.58 | 1681.44 | 1620.68 | 3.6136 | 88.7989 | 1227.13 | 96.2123 | 120 | 70 | 10.4 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.2234 | 63.3766 | 0.31154 | NA | 7.36 | 102.025 | 1681.44 | 2519.66 | 2767.2878 | -9.8278 | 75.4133 | 2224.3639 | 95.4133 | SDS-BDCM | mg/L | BMRL | 16.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 14.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | NR | 9.95 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 7.67 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 11.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 13.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1998-01-25 | 22:30 | 2682.13 | 24.4444 | 100 | 70 | 10.6333 | 0 | 16.9 | 3.1 |  | 20 | 20 | 0.845 | 0 | 17.3333 | 18.1489 | 13.968 | 60.3987 | 0.30049 | 7.65 | 6.64 | 41.741 | 398.4 | 416.64 | 2445.3 | 2460.4442 | -0.61932 | 89.9815 | 1438.5421 | 97.0984 | 100 | 80 | 10.6 | 10.1 | 9.9 | 20 | 20 | 0.48903 | 0.505 | 15.5385 | 16.2696 | 5.7705 | 73.6295 | 0.22097 | 6.64 | NA | 34.515 | 416.64 | 826.65 | 806.4847 | 2.4394 | 91.7159 | 611.5623 | 94.3563 | 80 | 66 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.669 | 50.831 | 0.3169 | NA | NA | 48.72 | 826.65 | 1656.64 | 1604.58 | 3.1425 | 88.3065 | 1215.615 | 95.9922 | 120 | 70 | 10.8 | 1.8 | 3.1 | 4.9 | 4.9 | 0.53973 | 0.36735 | 15.4286 | 16.1545 | 20.0526 | 64.1474 | 0.25183 | NA | 7.43 | 102.564 | 1656.64 | 2445.3 | 2559.0067 | -4.65 | 75.3831 | 2107.8234 | 95.1341 | SDS-DBCM | mg/L | BMRL | 3.19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2740 | 2740 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3070.7 | 3070.7 | --- | --- | --- | --- | SDS-DBCM | mg/L | NR | 2.61 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3401.8 | 3401.8 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3711.4 | 3711.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3953.8 | 3953.8 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 2.81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3070.7 | 3070.7 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-01-26 | 8:00 | 2692.91 | 25 | 100 | 72 | 10.7 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.1703 | 14.3398 | 60.9602 | 0.29807 | 7.69 | 6.5 | 43.416 | 406.7 | 423.36 | 2629.77 | 2531.4364 | 3.7392 | 89.7449 | 1477.3982 | 97.0613 | 100 | 80 | 10.8 | 10.1 | 10.2 | 20.3 | 20.3 | 0.49884 | 0.49754 | 15.5385 | 16.0046 | 5.8357 | 73.3643 | 0.21815 | 6.5 | NA | 33.04 | 423.36 | 862.29 | 809.8533 | 6.0811 | 92.1958 | 616.6067 | 94.6416 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 15.8462 | 12.2141 | 51.2859 | 0.30898 | NA | NA | 48.02 | 862.29 | 1713.68 | 1676.56 | 2.1661 | 88.6574 | 1269.425 | 96.2172 | 120 | 72 | 10.8 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.54 | 21.5259 | 63.6741 | 0.29117 | NA | 7.41 | 105.721 | 1713.68 | 2629.77 | 2802.9425 | -6.5851 | 75.0281 | 2258.3113 | 95.3186 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.83 | 6.86 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.81 | 6.76 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.88 | 6.82 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.91 | 6.67 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.77 | 6.64 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.83 | 6.77 | --- | --- | --- | ---
|  | Standard testing pH | 8 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 0.73529 | [5 empty] | 1998-01-26 | 14:20 | 2698.01 | 24.4444 | 100 | 70 | 10.6333 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 13.9179 | 60.4488 | 0.30734 | 7.52 | 6.47 | 42.478 | 403.38 | 418.32 | 2491.06 | 2450.2158 | 1.6396 | 89.8456 | 1434.2679 | 97.0383 | 100 | 80 | 10.8 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 5.7131 | 73.4869 | 0.22139 | 6.47 | NA | 33.748 | 418.32 | 854.37 | 791.7986 | 7.3237 | 91.9325 | 605.0593 | 94.4224 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 12.1078 | 51.3922 | 0.31344 | NA | NA | 47.18 | 854.37 | 1696.32 | 1661.56 | 2.0491 | 88.7216 | 1257.965 | 96.2495 | 120 | 70 | 10.6 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 21.3788 | 63.0212 | 0.3133 | NA | 7.39 | 105.336 | 1696.32 | 2491.06 | 2790.1215 | -12.0054 | 74.8193 | 2243.2207 | 95.3043 | SDS-THM4 | mg/L | 0 | 60.39 | --- | 402.6 | --- | 100 | 231.495 | 100 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 51.1 | --- | 340.6667 | --- | 100 | 195.8833 | 100 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | NR | 39.86 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24 | 24.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 38.11 | --- | 246.1531 | --- | 100 | 142.1316 | 100 | Temperature | oC | 23.8 | 24.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 43.48 | --- | 284.0693 | --- | 100 | 163.7747 | 100 | Temperature | oC | 23.1 | 24 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 45.61 | --- | 304.0667 | --- | 100 | 174.8383 | 100 | Temperature | oC | NA | NA | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 to 350 psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 0.48529 | [5 empty] | 1998-01-26 | 23:45 | 2707.53 | 24.4444 | 102 | 70 | 10.7333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.6245 | 61.6422 | 0.30139 | 7.61 | 6.54 | 45.426 | 413.34 | 404.88 | 2272.27 | 2410.8652 | -6.0994 | 88.7804 | 1407.8726 | 96.7734 | 102 | 80 | 10.8 | 10.1 | 10.3 | 20.4 | 20.4 | 0.50211 | 0.4951 | 15.5385 | 16.2696 | 5.5222 | 74.6778 | 0.21786 | 6.54 | NA | 34.338 | 404.88 | 713.79 | 768.227 | -7.6265 | 91.519 | 586.5535 | 94.1458 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 10.0244 | 53.4757 | 0.30123 | NA | NA | 45.5 | 713.79 | 1556.2 | 1382.08 | 11.1888 | 88.7621 | 1047.935 | 95.6581 | 120 | 70 | 10.9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7424 | 64.3576 | 0.30679 | NA | 7.39 | 99.022 | 1556.2 | 2272.27 | 2590.3263 | -13.9973 | 75.5429 | 2073.2632 | 95.2239 | SDS-MCAA* | mg/L | BMRL | 2.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 245 | 459.1509 | 85.7143 | 352.0755 | 94.8875 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 225 | 411.566 | 83.7607 | 318.283 | 94.0305 | SDS-MCAA* | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 236 | 435.3143 | 85.4839 | 335.6571 | 94.6374 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 208 | 370.7692 | 77.5701 | 289.3846 | 91.7065 | SDS-MCAA* | mg/L | BMRL | 2.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 201 | 366.0588 | 83.4862 | 283.5294 | 93.6515 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 17 | 226 | 415.283 | 85.4701 | 320.6415 | 94.6981
|  | Acceptable range of operating pH values | 4 to 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | -2.1397 | [5 empty] | 1998-01-27 | 8:00 | 2616.17 | 24.4444 | 102 | 72 | 10.7333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 14.3027 | 61.964 | 0.29983 | 7.68 | 6.54 | 40.133 | 372.67 | 417.48 | 2413.84 | 2523.3197 | -4.5355 | 90.3868 | 1470.3999 | 97.2706 | 102 | 80 | 10.8 | 10.1 | 10.3 | 20.4 | 20.4 | 0.50211 | 0.4951 | 15.5385 | 16.2696 | 5.7469 | 74.4531 | 0.21852 | 6.54 | NA | 31.86 | 417.48 | 823.68 | 795.6122 | 3.4076 | 92.3685 | 606.5461 | 94.7473 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.6654 | 51.8347 | 0.31077 | NA | NA | 45.99 | 823.68 | 1418.56 | 1601.37 | -12.887 | 88.9839 | 1212.525 | 96.2071 | 120 | 72 | 10.9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.7493 | 67.3507 | 0.29316 | NA | 7.44 | 108.493 | 1418.56 | 2413.84 | 2348.285 | 2.7158 | 74.0124 | 1883.4225 | 94.2396 | SDS-DCAA* | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 41.2 | 656 | 1236 | 88.1268 | 946 | 95.6448 | SDS-DCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 38 | 611 | 1129.9434 | 88.4848 | 870.4717 | 95.6346 | SDS-DCAA* | mg/L | NR | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 38 | 616 | 1144.4571 | 88.6228 | 880.2286 | 95.6829 | SDS-DCAA* | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 48 | 612 | 1110.9231 | 86.1272 | 861.4615 | 94.4281 | SDS-DCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 44 | 614 | 1128.1176 | 86.9048 | 871.0588 | 94.9487 | SDS-DCAA* | mg/L | BMRL | 21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 39 | 601 | 1109.9811 | 88.0734 | 855.4906 | 95.4412
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1998-01-27 | 14:25 | 2722.18 | 24.4444 | 100 | 70 | 10.7333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.9526 | 60.314 | 0.30803 | 7.64 | 6.5 | 41.808 | 390.1 | 409.92 | 2316.6 | 2464.2225 | -6.3724 | 89.8009 | 1437.0712 | 97.0907 | 100 | 80 | 10.8 | 10.1 | 10.3 | 20.4 | 20.4 | 0.50211 | 0.4951 | 15.5385 | 16.2696 | 5.6219 | 73.5781 | 0.22112 | 6.5 | NA | 32.686 | 409.92 | 780.12 | 779.8291 | 0.037293 | 92.0262 | 594.8745 | 94.5054 | 80 | 68 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.0172 | 52.4828 | 0.30693 | NA | NA | 45.64 | 780.12 | 1478.08 | 1514.6 | -2.4708 | 88.8661 | 1147.36 | 96.0222 | 120 | 70 | 10.9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.6444 | 65.4556 | 0.30165 | NA | 7.4 | 101.948 | 1478.08 | 2316.6 | 2454.6898 | -5.9609 | 75.1298 | 1966.3849 | 94.8155 | SDS-TCAA* | mg/L | BMRL | 42 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 10 | 422 | 810.6792 | 95.122 | 616.3396 | 98.3775 | SDS-TCAA* | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 11 | 393 | 738.9623 | 94.2708 | 565.9811 | 98.0565 | SDS-TCAA* | mg/L | NR | 21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 9 | 393 | 744.0857 | 95.3608 | 568.5429 | 98.417 | SDS-TCAA* | mg/L | BMRL | 24 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 18 | 393 | 724.7308 | 90.7216 | 558.8654 | 96.7792 | SDS-TCAA* | mg/L | BMRL | 25 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 11 | 380 | 712.8235 | 94.3878 | 546.4118 | 97.9869 | SDS-TCAA* | mg/L | BMRL | 35 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 12 | 393 | 738.0566 | 93.7173 | 565.5283 | 97.8781
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-01-27 | 22:20 | 2730.09 | 24.4444 | 102 | 70 | 10.7333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 14.1235 | 61.1431 | 0.30385 | 7.59 | 6.55 | 44.019 | 402.55 | 416.64 | 2488.2 | 2496.1056 | -0.31772 | 89.4348 | 1456.3728 | 96.9775 | 102 | 80 | 10.8 | 10.1 | 10.3 | 20.4 | 20.4 | 0.50211 | 0.4951 | 15.5385 | 16.2696 | 5.7291 | 74.4709 | 0.21847 | 6.55 | NA | 32.214 | 416.64 | 842.49 | 793.6014 | 5.8029 | 92.2681 | 605.1207 | 94.6764 | 80 | 69 | 10.5 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.9506 | 52.0493 | 0.30949 | NA | NA | 45.78 | 842.49 | 1670.28 | 1639.2 | 1.8608 | 89.0121 | 1240.845 | 96.3106 | 120 | 70 | 10.9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 21.3005 | 62.7995 | 0.3144 | NA | 7.44 | 98.098 | 1670.28 | 2488.2 | 2786.0221 | -11.9694 | 76.455 | 2228.151 | 95.5973 | SDS-MBAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 404 | 776.6415 | 95.1087 | 590.3208 | 98.4754 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 10 | 355 | 667.4528 | 94.4444 | 511.2264 | 98.0439 | SDS-MBAA* | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 8 | 370 | 700.9714 | 95.5801 | 535.4857 | 98.506 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 385 | 711.4231 | 91.1111 | 548.2115 | 97.0814 | SDS-MBAA* | mg/L | BMRL | 1.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 11 | 375 | 703.3137 | 93.9891 | 539.1569 | 97.9598 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 365 | 687.4151 | 95 | 526.2075 | 98.2896
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1.8603 | [5 empty] | 1998-01-28 | 11:00 | 2742.87 | 24.4444 | 100 | 70 | 10.4667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.7241 | 59.8092 | 0.31781 | 7.46 | 6.54 | 44.756 | 405.04 | 426.72 | 2348.06 | 2607.6112 | -11.0539 | 89.5116 | 1517.1656 | 97.05 | 100 | 80 | 10.5 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.939 | 73.561 | 0.22993 | 6.54 | NA | 33.335 | 426.72 | 851.4 | 827.7435 | 2.7785 | 92.1881 | 627.2318 | 94.6854 | 80 | 68 | 10.1 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 12.0496 | 51.8503 | 0.31067 | NA | NA | 48.09 | 851.4 | 1680.2 | 1654.71 | 1.5171 | 88.7303 | 1253.055 | 96.1622 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 21.4015 | 62.7985 | 0.31441 | NA | 7.38 | 100.562 | 1680.2 | 2348.06 | 2801.2334 | -19.2999 | 76.4337 | 2240.7167 | 95.5121 | SDS-DBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 0.31 | 0.59302 | 83.3333 | 0.45151 | 97.7852 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.09 | 0.09 | 0.09 | -200 | 0.09 | 0 | SDS-DBAA* | mg/L | NR | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.13 | 0.23057 | 33.3333 | 0.18029 | 88.9065 | SDS-DBAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.05 | 0.1 | 0.14423 | -25 | 0.12212 | 59.0551 | SDS-DBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 0.09 | 0.11706 | -50 | 0.10353 | 42.0455 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 0.08 | 0.1434 | 66.6667 | 0.1117 | 91.0473
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | Zero for extended use | Maximum system recycle flow rate, (QR-sys)max (gpm) | -2.1397 | [5 empty] | 1998-01-28 | 14:20 | 2746.79 | 25 | 90 | 70 | 10.3333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 18.6985 | 15.0249 | 54.6418 | 0.3422 | 7.32 | 6.4 | 47.034 | 391.76 | 436.8 | 2282.28 | 2662.2381 | -16.6482 | 89.2321 | 1549.5191 | 96.9646 | 90 | 79 | 10.5 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.6385 | 6.1116 | 67.8884 | 0.24509 | 6.4 | NA | 31.978 | 436.8 | 786.06 | 849.4826 | -8.0684 | 92.679 | 643.1413 | 95.0278 | 79 | 70 | 10 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 15.8462 | 11.0927 | 53.4074 | 0.2967 | NA | NA | 46.55 | 786.06 | 1607.04 | 1525.57 | 5.0696 | 89.3429 | 1155.815 | 95.9725 | 120 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 20.439 | 64.061 | 0.30319 | NA | 7.46 | 98.4445 | 1607.04 | 2282.28 | 2677.6562 | -17.3237 | 77.4623 | 2142.3481 | 95.4048 | SDS-BCAA* | mg/L | BMRL | 7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.23 | 12 | 23.1038 | 96.0684 | 17.5519 | 98.6896 | SDS-BCAA* | mg/L | BMRL | 5.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.12 | 12.4 | 23.5215 | 98 | 17.9608 | 99.3319 | SDS-BCAA* | mg/L | NR | 5.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.24 | 10.1 | 19.1149 | 96.391 | 14.6074 | 98.357 | SDS-BCAA* | mg/L | BMRL | 5.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.18 | 10.2 | 19.0638 | 96.6102 | 14.6319 | 98.7698 | SDS-BCAA* | mg/L | BMRL | 6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.18 | 12.85 | 24.2778 | 96.4356 | 18.5639 | 99.0304 | SDS-BCAA* | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.33 | 12.25 | 23.0455 | 94.2105 | 17.6477 | 98.1301
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-01-28 | 23:00 | 2754.71 | 24.4444 | 100 | 70 | 10.5667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0868 | 60.3465 | 0.31498 | 7.6 | 6.57 | 44.488 | 369.35 | 409.92 | 2295.15 | 2496.4188 | -8.7693 | 89.1472 | 1453.1694 | 96.9386 | 100 | 80 | 10.6 | 10.6 | 10.2 | 20.8 | 20.8 | 0.50702 | 0.50962 | 16.3077 | 17.075 | 5.7486 | 73.6514 | 0.23184 | 6.57 | NA | 31.624 | 409.92 | 819.72 | 803.0511 | 2.0335 | 92.2853 | 606.4856 | 94.7857 | 80 | 67 | 10.3 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.5296 | 51.6704 | 0.30552 | NA | NA | 45.92 | 819.72 | 1573.56 | 1578.044 | -0.28496 | 88.7978 | 1198.882 | 96.1698 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.9599 | 64.2401 | 0.30735 | NA | 7.41 | 100.331 | 1573.56 | 2295.15 | 2619.0774 | -14.1136 | 75.5242 | 2096.3187 | 95.2139 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.473 | 0.91828 | 99.5516 | 0.69564 | 99.8562 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.453 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.456 | 0.872 | 99.5455 | 0.664 | 99.8494 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.466 | 0.87558 | 98.5915 | 0.67079 | 99.5528 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.457 | 0.86829 | 99.5215 | 0.66265 | 99.8491 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.45 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 19.2647 | [5 empty] | 1998-01-29 | 7:15 | 2762.93 | 24.4444 | 100 | 70 | 10.4667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.4911 | 60.0423 | 0.31658 | 7.42 | 6.59 | 45.761 | 378.48 | 421.68 | 2235.09 | 2568.0562 | -14.8972 | 89.1479 | 1494.8681 | 96.9388 | 100 | 80 | 10.6 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.8745 | 73.5255 | 0.23004 | 6.59 | NA | 32.568 | 421.68 | 838.53 | 818.3476 | 2.4069 | 92.2766 | 620.0138 | 94.7472 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8808 | 51.9192 | 0.31026 | NA | NA | 46.48 | 838.53 | 1551.24 | 1630.58 | -5.1146 | 88.9774 | 1234.555 | 96.2351 | 120 | 70 | 10.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6721 | 64.7279 | 0.30504 | NA | 7.463 | 99.253 | 1551.24 | 2235.09 | 2581.6824 | -15.5069 | 76.4625 | 2066.4612 | 95.197 | SDS-CDBAA | mg/L | BMRL | 3.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.43478 | 3.9417 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.6532 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.41667 | 4.5149 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.6667 | 4.5686 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.55556 | 3.5564 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.6735 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-01-29 | 15:45 | 2771.36 | 24.4444 | 100 | 70 | 10.4667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.4289 | 60.1044 | 0.31625 | 7.44 | 6.45 | 45.694 | 373.5 | 420 | 2232.23 | 2557.1665 | -14.5566 | 89.1205 | 1488.5833 | 96.9304 | 100 | 80 | 10.6 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.8544 | 73.5456 | 0.22998 | 6.45 | NA | 32.214 | 420 | 836.55 | 815.3158 | 2.5383 | 92.33 | 617.6579 | 94.7845 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8531 | 51.9468 | 0.3101 | NA | NA | 46.34 | 836.55 | 1552.48 | 1626.76 | -4.7846 | 88.9667 | 1231.655 | 96.2376 | 120 | 70 | 10.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6983 | 64.7017 | 0.30516 | NA | 7.42 | 98.56 | 1552.48 | 2232.23 | 2584.2942 | -15.7719 | 76.5333 | 2068.3871 | 95.2349 | SDS-DCBAA | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 9.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NR | 7.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1 | 9.5 | --- | 56.5333 | --- | 89.4737 | 33.0167 | 96.9712 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-01-29 | 23:00 | 2778.85 | 24.4444 | 102 | 70 | 10.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.3595 | 61.9071 | 0.30704 | 7.63 | 6.52 | 49.915 | 369.35 | 396.48 | 2260.83 | 2375.2544 | -5.0612 | 87.4105 | 1385.8672 | 96.3983 | 102 | 80 | 10.8 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.4842 | 74.7158 | 0.22638 | 6.52 | NA | 33.217 | 396.48 | 809.82 | 766.7967 | 5.3127 | 91.622 | 581.6383 | 94.2891 | 80 | 68 | 10.4 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.4459 | 52.1541 | 0.30886 | NA | NA | 46.76 | 809.82 | 1522.72 | 1572.88 | -3.2941 | 88.2062 | 1191.35 | 96.075 | 120 | 70 | 11 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.2617 | 64.7383 | 0.30499 | NA | 7.41 | 101.024 | 1522.72 | 2260.83 | 2531.6655 | -11.9795 | 74.5198 | 2027.1928 | 95.0166 | SDS-HAA5 | mg/L | 0 | 69.7 | --- | 464.6667 | --- | 100 | 267.1833 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 48 | --- | 320 | --- | 100 | 184 | 100 | [8 empty] | SDS-HAA5 | mg/L | NR | 38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | 42 | --- | 271.2787 | --- | 100 | 156.6393 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 47.8 | --- | 312.2933 | --- | 100 | 180.0467 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 56 | --- | 373.3333 | --- | 100 | 214.6667 | 100
|  | Stage 3 -- General Information |  | maximum system recycle flow rates. | [6 empty] | 1998-01-30 | 9:30 | 2789.24 | 24.4444 | 100 | 71 | 10.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.9201 | 60.9799 | 0.31171 | 7.59 | 6.55 | 47.972 | 364.37 | 409.08 | 2206.49 | 2470.8902 | -11.9828 | 88.2732 | 1439.9851 | 96.6686 | 100 | 80 | 10.8 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.6825 | 73.5175 | 0.23007 | 6.55 | NA | 32.686 | 409.08 | 817.74 | 792.7826 | 3.052 | 92.0099 | 600.9313 | 94.5608 | 80 | 65 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.5721 | 50.7279 | 0.31755 | NA | NA | 46.27 | 817.74 | 1579.76 | 1589.21 | -0.59819 | 88.6893 | 1203.475 | 96.1553 | 120 | 71 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.0428 | 64.6572 | 0.30537 | NA | 7.33 | 100.408 | 1579.76 | 2206.49 | 2629.6227 | -19.1767 | 75.4552 | 2104.6914 | 95.2293 | SDS-HAA6 | mg/L | 0 | 76.7 | --- | 511.3333 | --- | 100 | 294.0167 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 53.5 | --- | 356.6667 | --- | 100 | 205.0833 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | NR | 43.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 47.4 | --- | 306.1574 | --- | 100 | 176.7787 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 53.8 | --- | 351.4933 | --- | 100 | 202.6467 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 62.5 | --- | 416.6667 | --- | 100 | 239.5833 | 100 | Stage 3 Operating Parameters During Sample Collection
|  | Membrane manufacturer | Fluid Systems | [7 empty] | 1998-01-30 | 15:15 | 2794.84 | 24.4444 | 100 | 70 | 10.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0717 | 60.3283 | 0.31508 | 7.56 | 6.42 | 48.24 | 365.2 | 413.28 | 2209.35 | 2497.5406 | -13.0441 | 88.3275 | 1455.4103 | 96.6855 | 100 | 80 | 10.8 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.7476 | 73.4524 | 0.23027 | 6.42 | NA | 32.568 | 413.28 | 816.75 | 801.3845 | 1.8813 | 92.1196 | 607.3322 | 94.6375 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.5793 | 52.2208 | 0.30847 | NA | NA | 44.8 | 816.75 | 1587.2 | 1588.7 | -0.094506 | 89.1599 | 1202.725 | 96.2751 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.1562 | 64.0438 | 0.3083 | NA | 7.44 | 99.484 | 1587.2 | 2209.35 | 2642.9985 | -19.6279 | 75.9282 | 2115.0992 | 95.2965 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41346 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41176 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42
|  | Membrane trade name | TFC-S | Summary of the Stage and System Flow Rates | [6 empty] | 1998-01-31 | 12:30 | 2804.21 | 24.4444 | 102 | 71 | 10.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.5771 | 62.3229 | 0.30499 | 7.489 | 6.53 | 49.312 | 381.8 | 401.52 | 2233.66 | 2412.5141 | -8.0072 | 87.7187 | 1407.017 | 96.4953 | 102 | 80 | 10.8 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.5612 | 74.6388 | 0.22661 | 6.53 | NA | 33.158 | 401.52 | 811.8 | 777.0347 | 4.2825 | 91.7419 | 589.2773 | 94.3731 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.4756 | 52.3244 | 0.30786 | NA | NA | 46.76 | 811.8 | 1554.96 | 1576.84 | -1.4071 | 88.3543 | 1194.32 | 96.0848 | 120 | 71 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7089 | 64.9911 | 0.3038 | NA | 7.32 | 100.254 | 1554.96 | 2233.66 | 2587.332 | -15.8337 | 75.0314 | 2071.146 | 95.1595 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.15 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.1 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2
|  | Membrane element model number | SC 2540S | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.2647 | [5 empty] | 1998-01-31 | 13:30 | 2817.24 | 24.4444 | 102 | 70 | 10.6 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 18.1538 | 19.0081 | 14.025 | 61.375 | 0.3097 | 7.53 | 6.49 | 48.977 | 353.58 | 404.04 | 2212.21 | 2498.9117 | -12.96 | 87.8782 | 1451.4759 | 96.6257 | 102 | 80 | 10.6 | 9.9 | 10.8 | 20.7 | 20.7 | 0.5152 | 0.47826 | 15.2308 | 15.9474 | 5.425 | 74.975 | 0.2127 | 6.49 | NA | 32.037 | 404.04 | 809.82 | 745.0427 | 7.999 | 92.0708 | 574.5414 | 94.4239 | 80 | 68 | 10.4 | 5.6 | 5 | 10.6 | 10.6 | 0.51029 | 0.5283 | 17.2308 | 18.0415 | 11.9157 | 51.6843 | 0.34907 | NA | NA | 45.99 | 809.82 | 1541.32 | 1665.3096 | -8.0444 | 88.6175 | 1237.5648 | 96.2838 | 120 | 70 | 10.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 19.7114 | 64.4886 | 0.30617 | NA | 7.41 | 99.022 | 1541.32 | 2212.21 | 2599.0052 | -17.4846 | 75.492 | 2070.1626 | 95.2167 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.25 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.2 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.1 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3
|  | Molecular weight cutoff (Daltons) | 300 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | [5 empty] | 1998-01-31 | 19:25 | 2827.09 | 24.4444 | 100 | 70 | 10.6 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 13.3943 | #VALUE! | #VALUE! | 7.44 | 6.52 | 48.307 | 348.6 | 403.2 | 2233.66 | 2372.2837 | -6.2061 | 88.0191 | 1387.7419 | 96.519 | 100 | 80 | 10.8 | 9.5 | 10.8 | 20.3 | 20.3 | 0.50866 | 0.46798 | 14.6154 | 15.3031 | 5.3339 | 73.8661 | 0.20717 | 6.52 | NA | 32.745 | 403.2 | 810.81 | 729.0632 | 10.0821 | 91.8787 | 566.1316 | 94.216 | 80 | 68 | 10.2 | 5.5 | 5 | 10.5 | 10.5 | 0.50702 | 0.52381 | 16.9231 | 17.7194 | 11.871 | 51.929 | 0.34122 | NA | NA | 44.94 | 810.81 | 1550 | 1653.267 | -6.6624 | 88.8542 | 1232.0385 | 96.3524 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6772 | 64.5228 | 0.30601 | NA | 7.46 | 97.636 | 1550 | 2233.66 | 2580.7099 | -15.5373 | 75.7847 | 2065.355 | 95.2727 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.5147 | [5 empty] | 1998-01-31 | 22:40 | 2826.34 | 24.4444 | 102 | 70 | 10.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.5977 | #VALUE! | #VALUE! | 7.48 | 6.57 | 48.776 | 375.16 | 401.52 | 2219.36 | 2415.5745 | -8.841 | 87.8522 | 1408.5472 | 96.5371 | 102 | 80 | 10.6 | 9.9 | 10.9 | 20.8 | 20.8 | 0.51847 | 0.47596 | 15.2308 | 15.9474 | 5.3547 | 75.0453 | 0.2125 | 6.57 | NA | 33.276 | 401.52 | 819.72 | 735.9801 | 10.2157 | 91.7125 | 568.7501 | 94.1493 | 80 | 68 | 10.4 | 5.6 | 5 | 10.6 | 10.6 | 0.51029 | 0.5283 | 17.2308 | 18.0415 | 12.0795 | 51.5205 | 0.35018 | NA | NA | 45.395 | 819.72 | 1547.52 | 1686.964 | -9.0108 | 88.6942 | 1253.342 | 96.3781 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6373 | 64.5627 | 0.30582 | NA | 7.36 | 98.098 | 1547.52 | 2219.36 | 2576.1421 | -16.0759 | 75.5683 | 2061.831 | 95.2422 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.5147 | [5 empty] | 1998-02-01 | 12:00 | 2839.94 | 24.4444 | 100 | 70 | 10.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.4461 | #VALUE! | #VALUE! | 7.43 | 6.52 | 48.508 | 371.01 | 397.32 | 2232.23 | 2388.924 | -7.0196 | 87.7912 | 1393.122 | 96.518 | 100 | 80 | 10.8 | 10 | 10.8 | 20.8 | 20.8 | 0.51683 | 0.48077 | 15.3846 | 16.1085 | 5.331 | 73.869 | 0.21807 | 6.52 | NA | 32.922 | 397.32 | 807.84 | 734.7256 | 9.0506 | 91.714 | 566.0228 | 94.1836 | 80 | 68 | 10.2 | 5.5 | 5 | 10.5 | 10.5 | 0.50702 | 0.52381 | 16.9231 | 17.7194 | 11.8282 | 51.9718 | 0.34094 | NA | NA | 44.73 | 807.84 | 1551.24 | 1647.261 | -6.19 | 88.7421 | 1227.5505 | 96.3562 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6804 | 64.5196 | 0.30602 | NA | 7.38 | 98.637 | 1551.24 | 2232.23 | 2582.1195 | -15.6744 | 75.1744 | 2066.6798 | 95.2273 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-22 | CI-s3-22 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-24 | CI-s3-24 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-26 | CI-s3-26 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-28 | CI-s3-28 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-30 | CI-s3-30 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-30 (dup) | CI-s3-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | [5 empty] | 1998-02-01 | 16:30 | 2844.28 | 24.4444 | 100 | 70 | 10.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.2922 | #VALUE! | #VALUE! | 7.44 | 6.5 | 49.982 | 374.33 | 394.8 | 2252.25 | 2363.5995 | -4.9439 | 87.3399 | 1379.1998 | 96.376 | 100 | 80 | 10.8 | 10 | 10.8 | 20.8 | 20.8 | 0.51683 | 0.48077 | 15.3846 | 16.1085 | 5.308 | 73.892 | 0.218 | 6.5 | NA | 31.978 | 394.8 | 806.85 | 730.7463 | 9.4322 | 91.9002 | 562.7731 | 94.3178 | 80 | 68 | 10.2 | 5.5 | 5 | 10.5 | 10.5 | 0.50702 | 0.52381 | 16.9231 | 17.7194 | 11.7922 | 52.0078 | 0.34071 | NA | NA | 46.06 | 806.85 | 1548.76 | 1643.719 | -6.1313 | 88.3333 | 1225.2845 | 96.2409 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6771 | 64.5229 | 0.30601 | NA | 7.36 | 96.404 | 1548.76 | 2252.25 | 2579.4643 | -14.5283 | 75.5816 | 2064.1121 | 95.3295 | Qp/QT (THM4), % | -19.225 | 40.3875 |  | Qp/QT (HAA5), % | 22.5251 | 61.2626 |  |  |  | Sampling date | MM/DD/YY | 1998-01-28 | 1998-01-28 | --- | --- | --- | --- | Qp/QT (THM4), % | -40.9002 | 29.5499 |  | Qp/QT (HAA5), % | -12.5 | 43.75 |  |  |  | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Sampling date | MM/DD/YY | 1998-02-25 | 1998-02-25 | --- | --- | --- | --- | Qp/QT (THM4), % | -88.9268 | 5.5366 |  | Qp/QT (HAA5), % | -28.5714 | 35.7143 |  |  |  | Sampling date | MM/DD/YY | 1998-03-11 | 1998-03-11 | --- | --- | --- | --- | Qp/QT (THM4), % | -65.5934 | 17.2033 |  | Qp/QT (HAA5), % | -12.9707 | 43.5146 |  |  |  | Sampling date | MM/DD/YY | 1998-03-25 | 1998-03-25 | --- | --- | --- | --- | Qp/QT (THM4), % | -57.8601 | 21.0699 |  | Qp/QT (HAA5), % | 3.5714 | 51.7857 |  |  |  | Sampling date | MM/DD/YY | 1998-02-11 | 1998-02-11 | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.6397 | [5 empty] | 1998-02-02 | 0:15 | 2852.05 | 24.4444 | 100 | 72 | 10.4667 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 14.146 | 60.254 | 0.30834 | 7.64 | 6.58 | 40.066 | 400.89 | 413.28 | 2333.76 | 2496.0549 | -6.9542 | 90.3054 | 1454.6675 | 97.2457 | 100 | 80 | 10.4 | 10.1 | 10.3 | 20.4 | 20.4 | 0.50211 | 0.4951 | 15.5385 | 16.2696 | 5.6816 | 73.9184 | 0.2201 | 6.58 | NA | 32.037 | 413.28 | 870.21 | 787.1202 | 9.5482 | 92.2481 | 600.2001 | 94.6623 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 12.3517 | 51.4483 | 0.3131 | NA | NA | 46.76 | 870.21 | 1569.84 | 1693.66 | -7.8874 | 88.6856 | 1281.935 | 96.3524 | 120 | 72 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.8907 | 65.3093 | 0.30232 | NA | 7.45 | 101.717 | 1569.84 | 2333.76 | 2611.7337 | -11.911 | 75.3879 | 2090.7869 | 95.135 | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 46.7871 | 23.3935 |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 28.7437 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 24.4993 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 24.5598 |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 43.9811 | 21.9905 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 4.6397 | [5 empty] | 1998-02-02 | 9:30 | 2861.11 | 24.4444 | 100 | 71 | 10.4333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.1257 | 61.2743 | 0.31021 | 7.56 | 6.56 | 45.158 | 391.76 | 411.6 | 2285.14 | 2503.8656 | -9.5717 | 89.0287 | 1457.7328 | 96.9022 | 100 | 80 | 10.4 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.7267 | 73.8733 | 0.22896 | 6.56 | NA | 32.273 | 411.6 | 827.64 | 798.2926 | 3.5459 | 92.1591 | 604.9463 | 94.6651 | 80 | 68 | 10.1 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.7205 | 52.1795 | 0.30871 | NA | NA | 46.27 | 827.64 | 1553.72 | 1609.01 | -3.5586 | 88.7585 | 1218.325 | 96.2022 | 120 | 71 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6911 | 65.0089 | 0.30372 | NA | 7.39 | 100.331 | 1553.72 | 2285.14 | 2585.1574 | -13.1291 | 75.6241 | 2069.4387 | 95.1518 | SDS-HAA5b, mg/L | NA | 41.5499 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 2740 | 2740 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 33.816 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 3070.7 | 3070.7 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | Operation time | hh.hh | 3401.8 | 3401.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 39.6746 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 3711.4 | 3711.4 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 39.5768 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 3953.8 | 3953.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 44.2008 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 3070.7 | 3070.7 | --- | --- | --- | ---
|  | Stage 3 -- Design Parameters |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | [5 empty] | 1998-02-02 | 15:30 | 2867.91 | 24.4444 | 100 | 71 | 10.4667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.1375 | 60.2625 | 0.31542 | 7.55 | 6.51 | 45.694 | 394.25 | 412.44 | 2230.8 | 2506.4414 | -12.3562 | 88.9211 | 1459.4407 | 96.8691 | 100 | 80 | 10.4 | 10.5 | 10.3 | 20.8 | 20.8 | 0.50866 | 0.50481 | 16.1538 | 16.9139 | 5.7314 | 73.8686 | 0.22897 | 6.51 | NA | 32.804 | 412.44 | 831.6 | 799.4476 | 3.8663 | 92.0464 | 605.9438 | 94.5863 | 80 | 68 | 10.2 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.7999 | 52.0001 | 0.30978 | NA | NA | 44.94 | 831.6 | 1550 | 1618.26 | -4.4039 | 89.1039 | 1224.93 | 96.3312 | 120 | 71 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6302 | 65.0698 | 0.30344 | NA | 7.42 | 101.101 | 1550 | 2230.8 | 2578.2509 | -15.5752 | 75.4871 | 2064.1255 | 95.102 | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.03 | 7.03 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.98 | 6.98 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.05 | 7.04 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.86 | 6.98 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.85 | 6.88 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.99 | 6.99 | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 2.8897 | [5 empty] | 1998-02-03 | 9:00 | 2880.27 | 24.4444 | 100 | 72 | 9.7333 | 0 | 17.3 | 3.2 |  | 20.5 | 20.5 | 0.8439 | 0 | 17.7436 | 18.5785 | 11.0529 | 63.3471 | 0.29328 | N/A | 6.51 | 35.845 | 344.45 | 334.32 | 2175.03 | 1947.9505 | 10.4403 | 89.2782 | 1141.1352 | 96.8588 | 100 | 80 | 9.2 | 10.1 | 10.4 | 20.5 | 20.5 | 0.50538 | 0.49268 | 15.5385 | 16.2696 | 4.488 | 76.312 | 0.2132 | 6.51 | NA | 32.214 | 334.32 | 832.59 | 627.7114 | 24.6074 | 90.3643 | 481.0157 | 93.3029 | 80 | 68 | 10 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8148 | 52.1853 | 0.30868 | NA | NA | 44.94 | 832.59 | 1414.84 | 1620.24 | -14.5175 | 86.5578 | 1226.415 | 96.3357 | 120 | 72 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 17.8324 | 68.1676 | 0.28965 | NA | NA | 87.78 | 1414.84 | 2175.03 | 2327.1937 | -6.9959 | 73.7437 | 1871.0169 | 95.3084 | SDS-CDb, mg/L | NA | 6.603 |  | SDS-CDb, mg/L | 8.0302 | 4.9351 |  |  |  | Temperature | oC | NA | 24.8 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 7.8944 |  | SDS-CDb, mg/L | NA | 6.7144 |  |  |  | Temperature | oC | NA | 24.2 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 24.5 | 24.8 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 10.7978 |  | SDS-CDb, mg/L | NA | 8.1693 |  |  |  | Temperature | oC | 24 | 24.5 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 10.2001 |  | SDS-CDb, mg/L | NA | 7.7531 |  |  |  | Temperature | oC | 24.4 | 24.5 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 8.5638 |  | SDS-CDb, mg/L | 10.0057 | 6.0329 |  |  |  | Temperature | oC | NA | 24.2 | --- | --- | --- | ---
|  | Active membrane area of membrane element used, A (ft2) | 28 | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-02-03 | 18:00 | 2889.02 | 24.4444 | 100 | 72 | 9.7333 | 0 | 17.4 | 3.2 |  | 20.6 | 20.6 | 0.84466 | 0 | 17.8462 | 18.6859 | 10.8222 | 64.7111 | 0.28876 | N/A | 6.53 | 36.582 | 348.6 | 327.6 | 2205.06 | 1910.0104 | 13.3806 | 88.8333 | 1118.8052 | 96.7303 | 100 | 80 | 9.2 | 10.2 | 10.4 | 20.6 | 20.6 | 0.50702 | 0.49515 | 15.6923 | 16.4307 | 4.398 | 76.402 | 0.21506 | 6.53 | NA | 32.509 | 327.6 | 836.55 | 617.0162 | 26.2428 | 90.0766 | 472.3081 | 93.117 | 80 | 68 | 10 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.8731 | 52.1269 | 0.30903 | NA | NA | 45.01 | 836.55 | 1412.36 | 1628.09 | -15.2744 | 86.2607 | 1232.32 | 96.3475 | 120 | 72 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 17.7804 | 68.2196 | 0.28942 | NA | NA | 89.166 | 1412.36 | 2205.06 | 2322.0559 | -5.3058 | 72.7821 | 1867.2079 | 95.2246 | TOCb, mg/L | NA | 3.5721 |  | TOCb, mg/L | 4.5796 | 2.3948 |  |  |  | Alkalinity | mg/L as CaCO3 | 30 | 437 | 725.8387 | 76.1905 | 581.4194 | 94.8402 | TOCb, mg/L | NA | 4.2595 |  | TOCb, mg/L | NA | 3.4231 |  |  |  | Alkalinity | mg/L as CaCO3 | 30 | 395 | 654.0323 | 74.359 | 524.5161 | 94.2804 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 27 | 445 | 746.5082 | 78.2258 | 595.7541 | 95.4679 | TOCb, mg/L | NA | 5.026 |  | TOCb, mg/L | NA | 3.4779 |  |  |  | Alkalinity | mg/L as CaCO3 | 24 | 355 | 588.3279 | 77.5701 | 471.6639 | 94.9116 | TOCb, mg/L | NA | 4.2088 |  | TOCb, mg/L | NA | 2.9221 |  |  |  | Alkalinity | mg/L as CaCO3 | 23 | 366 | 606.1 | 78.8991 | 486.05 | 95.268 | TOCb, mg/L | NA | 4.518 |  | TOCb, mg/L | 5.4996 | 2.7948 |  |  |  | Alkalinity | mg/L as CaCO3 | 29 | 377 | 623.9677 | 75.2137 | 500.4839 | 94.2056
|  | Design flux, FW (gfd) | 41.43 | System concentrate waste flow rate, QW-sys (gpm) | 2.8897 | [5 empty] | 1998-02-04 | 1:40 | 2896.48 | 24.4444 | 100 | 72 | 9.7333 | 0 | 17.6 | 3.2 |  | 20.8 | 20.8 | 0.84615 | 0 | 18.0513 | 18.9007 | 10.7597 | 64.3069 | 0.29391 | 7.54 | 6.59 | 38.994 | 341.96 | 325.92 | 2199.34 | 1904.013 | 13.428 | 88.0357 | 1114.9665 | 96.5027 | 100 | 80 | 9.2 | 10.4 | 10.4 | 20.8 | 20.8 | 0.51029 | 0.5 | 16 | 16.7529 | 4.3914 | 76.4086 | 0.21925 | 6.59 | NA | 33.158 | 325.92 | 842.49 | 618.682 | 26.5651 | 89.8263 | 472.301 | 92.9795 | 80 | 68 | 10 | 5 | 5 | 10 | 10 | 0.49066 | 0.5 | 15.3846 | 16.1085 | 11.9433 | 52.0567 | 0.30944 | NA | NA | 46.27 | 842.49 | 1416.08 | 1638.71 | -15.7216 | 85.8033 | 1240.6 | 96.2704 | 120 | 72 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 17.847 | 68.153 | 0.28971 | NA | 7.48 | 87.934 | 1416.08 | 2199.34 | 2329.1804 | -5.9036 | 73.0198 | 1872.6302 | 95.3043 | UV254 b, cm-1 | NA | 0.13334 |  | UV254 b, cm-1 | 0.17299 | 0.086997 |  |  |  | Total dissolved solids | mg/L | 82 | 1109 | 1837.8387 | 76.3689 | 1473.4194 | 94.4347 | UV254 b, cm-1 | NA | 0.15035 |  | UV254 b, cm-1 | NA | 0.12025 |  |  |  | Total dissolved solids | mg/L | 78 | 989 | 1635.5161 | 76.3636 | 1312.2581 | 94.056 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 68 | 1054 | 1765.2131 | 79.6407 | 1409.6066 | 95.176 | UV254 b, cm-1 | NA | 0.20137 |  | UV254 b, cm-1 | NA | 0.138 |  |  |  | Total dissolved solids | mg/L | 67 | 996 | 1650.8689 | 80.6358 | 1323.4344 | 94.9374 | UV254 b, cm-1 | NA | 0.17322 |  | UV254 b, cm-1 | NA | 0.11849 |  |  |  | Total dissolved solids | mg/L | 66 | 1017 | 1682.7 | 80.3571 | 1349.85 | 95.1106 | UV254 b, cm-1 | NA | 0.16696 |  | UV254 b, cm-1 | 0.20354 | 0.10277 |  |  |  | Total dissolved solids | mg/L | 76 | 970 | 1604.4516 | 76.7584 | 1287.2258 | 94.0958
|  | Net driving pressure at the design flux, NDP (psi) | 97 | System permeate flow rate, Qp-sys (gpm) | 16.375 | [5 empty] | 1998-02-04 | 6:30 | 2901.65 | 24.4444 | 100 | 70 | 9.9333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.5235 | 61.5098 | 0.30204 | 7.17 | 6.59 | 42.21 | 386.78 | 399 | 2316.6 | 2390.1184 | -3.1735 | 89.4211 | 1394.5592 | 96.9732 | 100 | 80 | 9.8 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 16.4307 | 5.5133 | 74.6867 | 0.21999 | 6.59 | NA | 31.447 | 399 | 807.84 | 766.553 | 5.1108 | 92.1185 | 582.7765 | 94.6039 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.3484 | 51.1516 | 0.30862 | NA | NA | 46.2 | 807.84 | 1557.44 | 1554.2472 | 0.205 | 88.4211 | 1181.0436 | 96.0882 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.8416 | 65.1584 | 0.30302 | NA | 7.05 | 92.939 | 1557.44 | 2316.6 | 2596.7633 | -12.0937 | 76.707 | 2077.1016 | 95.5255 | Bromideb, mg/L | NA | 55.3249 |  | Bromideb, mg/L | 68.0072 | 40.5036 |  |  |  | Total hardness | mg/L as CaCO3 | 23 | 757 | 1277.9032 | 88.7805 | 1017.4516 | 97.7395 | Bromideb, mg/L | NA | 52.0431 |  | Bromideb, mg/L | NA | 44.375 |  |  |  | Total hardness | mg/L as CaCO3 | 25 | 697 | 1173.9032 | 86.9792 | 935.4516 | 97.3275 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 751 | 1280.4426 | 91.2371 | 1015.7213 | 98.3263 | Bromideb, mg/L | NA | 68.5673 |  | Bromideb, mg/L | NA | 49.8571 |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 711 | 1200.2131 | 91.2371 | 955.6066 | 98.221 | Bromideb, mg/L | NA | 57.5382 |  | Bromideb, mg/L | NA | 43.0669 |  |  |  | Total hardness | mg/L as CaCO3 | 16 | 727 | 1224.7 | 91.8367 | 975.85 | 98.3604 | Bromideb, mg/L | NA | 54.0436 |  | Bromideb, mg/L | 63.1429 | 38.0714 |  |  |  | Total hardness | mg/L as CaCO3 | 21 | 684 | 1154.5161 | 89.0052 | 919.2581 | 97.7155
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.427 | System feed flow rate, QF-sys (gpm) | 19.2647 | [5 empty] | 1998-02-04 | 15:15 | 2910.25 | 24.4444 | 100 | 70 | 9.9333 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 17.641 | 18.4711 | 13.1914 | 63.0753 | 0.29284 | 7.27 | 6.48 | 42.947 | 385.95 | 400.68 | 2345.2 | 2323.4949 | 0.92551 | 89.2815 | 1362.0874 | 96.847 | 100 | 80 | 9.8 | 10.1 | 10.3 | 20.4 | 20.4 | 0.50211 | 0.4951 | 15.5385 | 16.2696 | 5.493 | 74.707 | 0.21778 | 6.48 | NA | 32.096 | 400.68 | 806.85 | 762.107 | 5.5454 | 91.9896 | 581.3935 | 94.4795 | 80 | 68 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.3253 | 52.6747 | 0.2997 | NA | NA | 46.76 | 806.85 | 1562.4 | 1551.7382 | 0.6824 | 88.3298 | 1179.2941 | 96.0349 | 120 | 70 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 19.7407 | 65.2593 | 0.30255 | NA | 7.15 | 93.324 | 1562.4 | 2345.2 | 2572.3897 | -9.6874 | 76.7086 | 2067.3949 | 95.4859 | Alkb, mg/L CaCO3 | NA | 81.5738 |  | Alkb, mg/L CaCO3 | 101.2224 | 58.6112 |  |  |  | Calcium hardness | mg/L as CaCO3 | 20 | 730 | 1233.871 | 89.1304 | 981.9355 | 97.9632 | Alkb, mg/L CaCO3 | NA | 87.1546 |  | Alkb, mg/L CaCO3 | NA | 72.8125 |  |  |  | Calcium hardness | mg/L as CaCO3 | 22 | 661 | 1114.4839 | 87.7778 | 887.7419 | 97.5218 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Calcium hardness | mg/L as CaCO3 | 15 | 704 | 1200.9836 | 91.7127 | 952.4918 | 98.4252 | Alkb, mg/L CaCO3 | NA | 101.9617 |  | Alkb, mg/L CaCO3 | NA | 74.5 |  |  |  | Calcium hardness | mg/L as CaCO3 | 15 | 669 | 1130.0164 | 91.6667 | 899.5082 | 98.3324 | Alkb, mg/L CaCO3 | NA | 93.0009 |  | Alkb, mg/L CaCO3 | NA | 68.5314 |  |  |  | Calcium hardness | mg/L as CaCO3 | 15 | 697 | 1174.4 | 91.8033 | 935.7 | 98.3969 | Alkb, mg/L CaCO3 | NA | 95.7194 |  | Alkb, mg/L CaCO3 | 113.3929 | 64.6964 |  |  |  | Calcium hardness | mg/L as CaCO3 | 20 | 656 | 1107.3548 | 88.8889 | 881.6774 | 97.7316
|  | Temperature at which the MTCW was determined, ToC (oC) | 25 | [7 empty] | 1998-02-04 | 23:30 | 2918.66 | 24.4444 | 100 | 70 | 9.9333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 13.3469 | 62.9198 | 0.29357 | 7.48 | 6.56 | 43.684 | 374.33 | 397.32 | 2285.14 | 2359.4294 | -3.251 | 89.0053 | 1378.3747 | 96.8308 | 100 | 80 | 9.8 | 10.1 | 10.2 | 20.3 | 20.3 | 0.49884 | 0.49754 | 15.5385 | 16.2696 | 5.4481 | 74.7519 | 0.21765 | 6.56 | NA | 32.922 | 397.32 | 861.3 | 758.1455 | 11.9766 | 91.714 | 577.7327 | 94.3015 | 80 | 68 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 12.1669 | 51.8331 | 0.30456 | NA | NA | 44.73 | 861.3 | 1551.24 | 1661.5386 | -7.1104 | 88.7421 | 1261.4193 | 96.454 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7023 | 65.2977 | 0.30238 | NA | 7.32 | 97.02 | 1551.24 | 2285.14 | 2583.2671 | -13.0463 | 75.5814 | 2067.2535 | 95.3068 | T-Hdb, mg/L CaCO3 | NA | 126.6483 |  | T-Hdb, mg/L CaCO3 | 161.3013 | 86.1506 |  |  |  | Turbidity | ntu | 0.02 | 0.22 | 0.36194 | 66.6667 | 0.29097 | 93.1264 | T-Hdb, mg/L CaCO3 | NA | 138.5147 |  | T-Hdb, mg/L CaCO3 | NA | 112.8125 |  |  |  | Turbidity | ntu | 0.01 | 10.9 | 18.6284 | 66.6667 | 14.7642 | 99.9323 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.02 | 19.02 | 32.7249 | 33.3333 | 25.8725 | 99.9227 | T-Hdb, mg/L CaCO3 | NA | 183.8126 |  | T-Hdb, mg/L CaCO3 | NA | 128.2857 |  |  |  | Turbidity | ntu | 0.01 | 10.03 | 17.0933 | 75 | 13.5616 | 99.9263 | T-Hdb, mg/L CaCO3 | NA | 164.1739 |  | T-Hdb, mg/L CaCO3 | NA | 115.4979 |  |  |  | Turbidity | ntu | BMRL | 4.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | 153.0741 |  | T-Hdb, mg/L CaCO3 | 184.5714 | 97.7857 |  |  |  | Turbidity | ntu | BMRL | 10.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Maximum flow rate to the element, QI, max (gpm) | 2.5 | Calculate the Required System Influent Pressure | [6 empty] | 1998-02-04 | 6:10 | 2925.36 | 24.4444 | 100 | 70 | 10.0333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.0834 | 63.1833 | 0.29404 | 7.27 | 6.58 | 47.101 | 366.03 | 392.28 | 2172.17 | 2318.6015 | -6.7413 | 87.993 | 1355.4408 | 96.525 | 100 | 80 | 10 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 16.4307 | 5.4284 | 74.5716 | 0.22033 | 6.58 | NA | 30.385 | 392.28 | 776.16 | 754.175 | 2.8325 | 92.2543 | 573.2275 | 94.6993 | 80 | 64 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 10.9265 | 51.0735 | 0.30909 | NA | NA | 42.84 | 776.16 | 1474.36 | 1494.8136 | -1.3873 | 89.0792 | 1135.4868 | 96.2272 | 120 | 70 | 10.1 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.6753 | 66.2247 | 0.29814 | NA | 7.13 | 95.942 | 1474.36 | 2172.17 | 2452.5921 | -12.9098 | 75.5425 | 1963.4761 | 95.1137 | Ca-Hdb, mg/L CaCO3 | NA | 113.7258 |  | Ca-Hdb, mg/L CaCO3 | 144.8063 | 77.4032 |  |  |  | Total organic carbon | mg/L | 0.23 | 19.7 | 33.5174 | 96.0684 | 26.6087 | 99.1356 | Ca-Hdb, mg/L CaCO3 | NA | 130.0607 |  | Ca-Hdb, mg/L CaCO3 | NA | 106.0625 |  |  |  | Total organic carbon | mg/L | 0.19 | 21.7 | 36.9652 | 96.8333 | 29.3326 | 99.3523 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Total organic carbon | mg/L | 0.24 | 17.85 | 30.5523 | 96.391 | 24.2011 | 99.0083 | Ca-Hdb, mg/L CaCO3 | NA | 170.5324 |  | Ca-Hdb, mg/L CaCO3 | NA | 118.9286 |  |  |  | Total organic carbon | mg/L | 0.26 | 17.55 | 29.738 | 95.1036 | 23.644 | 98.9004 | Ca-Hdb, mg/L CaCO3 | NA | 153.0662 |  | Ca-Hdb, mg/L CaCO3 | NA | 107.2845 |  |  |  | Total organic carbon | mg/L | 0.13 | 18.5 | 31.359 | 97.4257 | 24.9295 | 99.4785 | Ca-Hdb, mg/L CaCO3 | NA | 143.9704 |  | Ca-Hdb, mg/L CaCO3 | 173.8929 | 91.4464 |  |  |  | Total organic carbon | mg/L | 0.13 | 20.15 | 34.3577 | 97.7193 | 27.2539 | 99.523
|  | Minimum flow rate to the element, QI, min (gpm) | 0.5 | Osmotic pressure for stage 13, Dp1 (psi) | 8.9 | [5 empty] | 1998-02-05 | 17:45 | 2936.82 | 24.4444 | 100 | 70 | 10 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 12.854 | 62.2126 | 0.2969 | N/A | 6.51 | 47.503 | 375.99 | 388.08 | 2240.81 | 2277.733 | -1.6478 | 87.7595 | 1332.9065 | 96.4361 | 100 | 80 | 10 | 10.1 | 10.2 | 20.3 | 20.3 | 0.49884 | 0.49754 | 15.5385 | 16.2696 | 5.3294 | 74.6706 | 0.21788 | 6.51 | NA | 31.624 | 388.08 | 805.86 | 741.0413 | 8.0434 | 91.8512 | 564.5607 | 94.3985 | 80 | 64 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.3534 | 50.6466 | 0.3117 | NA | NA | 43.89 | 805.86 | 1530.16 | 1552.5906 | -1.4659 | 88.6905 | 1179.2253 | 96.2781 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.4261 | 65.5739 | 0.3011 | NA | N/A | 96.327 | 1530.16 | 2240.81 | 2547.7189 | -13.6963 | 75.1786 | 2038.9395 | 95.2756 | Notes: | [9 empty] | UV254 | cm-1 | 0.018 | 0.747 | 1.2644 | 91.9283 | 1.0057 | 98.2102 | Notes: | [9 empty] | UV254 | cm-1 | 0.002 | 0.704 | 1.2022 | 99.061 | 0.9531 | 99.7902 | Notes: | [9 empty] | UV254 | cm-1 | 0.002 | 0.705 | 1.2121 | 99.0909 | 0.95854 | 99.7913 | Notes: | [9 empty] | UV254 | cm-1 | 0.004 | 0.713 | 1.2128 | 98.1221 | 0.96289 | 99.5846 | Notes: | [9 empty] | UV254 | cm-1 | 0.001 | 0.709 | 1.2046 | 99.5215 | 0.9568 | 99.8955 | Notes: | [9 empty] | UV254 | cm-1 | 0.002 | 0.718 | 1.2261 | 99.0521 | 0.97206 | 99.7943
|  | Total width of all membrane envelopes in the element, w (ft) | 6.4 | Osmotic pressure for stage 23, Dp2 (psi) | 13.4 | [5 empty] | 1998-02-06 | 0:15 | 2943.28 | 24.4444 | 100 | 70 | 10 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 13.2421 | 61.8246 | 0.29877 | N/A | 6.55 | 47.302 | 381.8 | 398.16 | 2185.04 | 2344.856 | -7.3141 | 88.1199 | 1371.508 | 96.5511 | 100 | 80 | 10 | 10.1 | 10.2 | 20.3 | 20.3 | 0.49884 | 0.49754 | 15.5385 | 16.2696 | 5.4871 | 74.5129 | 0.21835 | 6.55 | NA | 31.152 | 398.16 | 788.04 | 761.5699 | 3.359 | 92.176 | 579.8649 | 94.6277 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.0857 | 51.4143 | 0.30704 | NA | NA | 44.03 | 788.04 | 1510.32 | 1517.1698 | -0.45353 | 88.9416 | 1152.6049 | 96.18 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.15 | 65.85 | 0.29984 | NA | N/A | 96.866 | 1510.32 | 2185.04 | 2513.4164 | -15.0284 | 75.6716 | 2011.8682 | 95.1853 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 7.8261 | 3.7919 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.0526 | 3.2442 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.83333 | 3.9496 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.5385 | 4.0627 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.76923 | 3.8324 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.5385 | 3.5633 | --- | --- | --- | ---
|  | Feed spacer thickness, T (ft) | 0.00258 | Osmotic pressure for stage 33, Dp3 (psi) | 18.6 | [5 empty] | 1998-02-06 | 7:00 | 2950.25 | 24.4444 | 100 | 70 | 10.0333 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 13.4485 | 61.6182 | 0.30151 | N/A | 6.57 | 43.349 | 385.12 | 398.16 | 2236.52 | 2378.2343 | -6.3364 | 89.1127 | 1388.1971 | 96.8773 | 100 | 80 | 10 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 16.4307 | 5.5042 | 74.4958 | 0.22056 | 6.57 | NA | 31.211 | 398.16 | 791.01 | 765.109 | 3.2744 | 92.1612 | 581.6345 | 94.6339 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.0831 | 51.4169 | 0.30703 | NA | NA | 47.18 | 791.01 | 1527.68 | 1519.9634 | 0.50512 | 88.1505 | 1155.4867 | 95.9169 | 120 | 70 | 10.1 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.4489 | 65.4511 | 0.30167 | NA | N/A | 92.169 | 1527.68 | 2236.52 | 2546.4297 | -13.8568 | 76.8513 | 2037.0549 | 95.4754 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses due to stage hardware, DPs (psi) | 4 | [5 empty] | 1998-02-06 | 19:40 | 2962.73 | 24.4444 | 100 | 70 | 10 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 13.1318 | 61.8349 | 0.29872 | 7.34 | 6.54 | 47.704 | 380.97 | 395.64 | 2215.07 | 2326.1236 | -5.0135 | 87.9426 | 1360.8818 | 96.4946 | 100 | 80 | 10 | 10.1 | 10.2 | 20.3 | 20.3 | 0.49884 | 0.49754 | 15.5385 | 16.2696 | 5.453 | 74.547 | 0.21825 | 6.54 | NA | 30.916 | 395.64 | 785.07 | 756.7883 | 3.6024 | 92.1858 | 576.2141 | 94.6346 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.0133 | 51.4867 | 0.30661 | NA | NA | 45.92 | 785.07 | 1520.24 | 1509.437 | 0.71061 | 88.3935 | 1147.2535 | 95.9974 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.3168 | 65.6832 | 0.3006 | NA | 7.26 | 94.479 | 1520.24 | 2215.07 | 2532.0704 | -14.3111 | 76.12 | 2026.1552 | 95.337 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-02-06 | 23:00 | 2965.9 | 24.4444 | 100 | 70 | 10 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 13.1584 | 61.8416 | 0.29868 | 7.38 | 6.55 | 47.838 | 377.65 | 396.48 | 2216.5 | 2330.8808 | -5.1604 | 87.9343 | 1363.6804 | 96.492 | 100 | 80 | 10 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 16.4307 | 5.4856 | 74.5144 | 0.2205 | 6.55 | NA | 31.978 | 396.48 | 782.1 | 764.5909 | 2.2387 | 91.9345 | 580.5355 | 94.4916 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 10.9597 | 51.5403 | 0.30629 | NA | NA | 46.55 | 782.1 | 1519 | 1502.939 | 1.0573 | 88.2592 | 1142.5195 | 95.9257 | 120 | 70 | 10 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 19.065 | 65.935 | 0.28584 | NA | 7.24 | 94.864 | 1519 | 2216.5 | 2483.7373 | -12.0567 | 76.0734 | 2001.3686 | 95.26 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-02-07 | 20:30 | 2987.65 | 24.4444 | 100 | 70 | 10 | 0 | 17.35 | 3.1 |  | 20.45 | 20.45 | 0.84841 | 0 | 17.7949 | 18.6322 | 12.9249 | 62.0751 | 0.30016 | 7.36 | 6.57 | 46.967 | 370.18 | 387.24 | 2206.49 | 2291.6711 | -3.8605 | 87.8713 | 1339.4556 | 96.4936 | 100 | 80 | 10 | 10.35 | 10.1 | 20.45 | 20.45 | 0.49966 | 0.50611 | 15.9231 | 16.6723 | 5.3783 | 74.6217 | 0.22342 | 6.57 | NA | 31.624 | 387.24 | 775.17 | 751.6584 | 3.0331 | 91.8335 | 569.4492 | 94.4466 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 10.8596 | 51.6404 | 0.3057 | NA | NA | 46.34 | 775.17 | 1541.32 | 1489.4234 | 3.367 | 88.0333 | 1132.2967 | 95.9074 | 120 | 70 | 10 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 19.3669 | 65.6331 | 0.28716 | NA | 7.27 | 94.633 | 1541.32 | 2206.49 | 2521.3338 | -14.269 | 75.5622 | 2031.3269 | 95.3413 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  | Stage 3 -- Additional Information |  | Mechanical pressure losses per stage, Ls (psi) | 22 | [5 empty] | 1998-02-08 | 0:00 | 2990.89 | 24.4444 | 100 | 70 | 10 | 0 | 17.4 | 3.1 |  | 20.5 | 20.5 | 0.84878 | 0 | 17.8462 | 18.6859 | 12.9178 | 62.0489 | 0.30115 | 7.4 | 6.6 | 47.034 | 369.35 | 386.4 | 2209.35 | 2291.2285 | -3.706 | 87.8276 | 1338.8143 | 96.4869 | 100 | 80 | 10 | 10.3 | 10.2 | 20.5 | 20.5 | 0.50211 | 0.50244 | 15.8462 | 16.5918 | 5.3266 | 74.6734 | 0.22219 | 6.6 | NA | 32.45 | 386.4 | 780.12 | 743.8201 | 4.6531 | 91.602 | 565.11 | 94.2578 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 10.9542 | 51.5458 | 0.30626 | NA | NA | 44.94 | 780.12 | 1540.08 | 1500.5964 | 2.5637 | 88.3696 | 1140.3582 | 96.0591 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.5991 | 65.4009 | 0.3019 | NA | 7.38 | 93.478 | 1540.08 | 2209.35 | 2566.7008 | -16.1745 | 75.808 | 2053.3904 | 95.4476 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 0.75 | Net driving pressure required for permeation, NDP (psi) | 49.7034 | [5 empty] | 1998-02-08 | 8:40 | 2999.98 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 12.8795 | 62.1205 | 0.29907 | N/A | 6.58 | 45.761 | 370.18 | 385.56 | 2123.55 | 2281.8576 | -7.4549 | 88.1313 | 1333.7088 | 96.5689 | 100 | 80 | 9.8 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.5918 | 5.3726 | 74.8274 | 0.22173 | 6.58 | NA | 29.736 | 385.56 | 769.23 | 748.43 | 2.704 | 92.2876 | 566.995 | 94.7555 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.7651 | 51.4349 | 0.30066 | NA | NA | 41.86 | 769.23 | 1428.48 | 1467.5052 | -2.7319 | 89.1431 | 1118.3676 | 96.257 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.1445 | 66.8555 | 0.29533 | NA | N/A | 89.243 | 1428.48 | 2123.55 | 2378.9063 | -12.025 | 76.8537 | 1903.6931 | 95.3121 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Flow weighted system pressure losses, Lsys (psi) | 33.5282 | [5 empty] | 1998-02-08 | 18:30 | 3009.66 | 24.4444 | 100 | 70 | 9.9333 | 0 | 17.45 | 3.1 |  | 20.55 | 20.55 | 0.84915 | 0 | 17.8974 | 18.7396 | 13.0541 | 61.9459 | 0.30252 | 7.37 | 6.54 | 46.699 | 375.99 | 388.92 | 2169.31 | 2315.293 | -6.7295 | 87.9926 | 1352.1065 | 96.5462 | 100 | 80 | 9.8 | 10.45 | 10.1 | 20.55 | 20.55 | 0.5013 | 0.50852 | 16.0769 | 16.8334 | 5.4213 | 74.7787 | 0.22511 | 6.54 | NA | 31.624 | 388.92 | 774.18 | 758.5975 | 2.0128 | 91.8688 | 573.7588 | 94.4883 | 80 | 65 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.8839 | 51.6161 | 0.2996 | NA | NA | 38.78 | 774.18 | 1480.56 | 1480.164 | 0.026747 | 90.0288 | 1127.172 | 96.5595 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.8814 | 66.1186 | 0.29862 | NA | 7.29 | 86.933 | 1480.56 | 2169.31 | 2469.5856 | -13.842 | 77.6476 | 1975.0728 | 95.5985 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Maximum element recovery (%) | 17 | Required influent pressure to the system, PI (psi) | 83.2317 | [5 empty] | 1998-02-08 | 23:40 | 3014.68 | 24.4444 | 100 | 70 | 9.9333 | 0 | 17.2 | 3.21 |  | 20.41 | 20.41 | 0.84272 | 0 | 17.641 | 18.4711 | 12.5251 | 62.4749 | 0.29566 | 7.36 | 6 | 45.962 | 373.5 | 386.4 | 2170.74 | 2210.5538 | -1.8341 | 88.1051 | 1298.4769 | 96.4603 | 100 | 80 | 9.8 | 10.1 | 10.31 | 20.41 | 20.41 | 0.50244 | 0.49486 | 15.5385 | 16.2696 | 5.2802 | 74.9198 | 0.21716 | 6 | NA | 31.978 | 386.4 | 783.09 | 733.6029 | 6.3195 | 91.7241 | 560.0015 | 94.2897 | 80 | 65 | 10 | 4.9 | 5 | 9.9 | 9.9 | 0.48739 | 0.49495 | 15.0769 | 15.7864 | 11.0881 | 51.4119 | 0.30706 | NA | NA | 38.92 | 783.09 | 1552.48 | 1512.3766 | 2.5832 | 89.9275 | 1147.7333 | 96.609 | 120 | 70 | 10 | 2.2 | 3.21 | 5.41 | 5.41 | 0.58156 | 0.40665 | 18.8571 | 19.7444 | 19.6755 | 65.3245 | 0.30225 | NA | 7.27 | 87.087 | 1552.48 | 2170.74 | 2556.7992 | -17.7847 | 77.462 | 2054.6396 | 95.7614 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Variability of design flux (%) | 5 | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-02-09 | 6:30 | 3021.63 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.3 | 3.1 |  | 20.4 | 20.4 | 0.84804 | 0 | 17.7436 | 18.5785 | 12.8894 | #VALUE! | #VALUE! | N/A | 6.64 | 43.818 | 371.01 | 383.88 | 2117.83 | 2281.6454 | -7.7351 | 88.5855 | 1332.7627 | 96.7122 | 100 | 80 | 9.8 | 10.3 | 10.1 | 20.4 | 20.4 | 0.49884 | 0.5049 | 15.8462 | 16.5918 | #VALUE! | #VALUE! | #VALUE! | 6.64 | NA | NA | 383.88 | 758.34 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 80 | 64 | 9.8 | 4.8 | 4.9 | 9.7 | 9.7 | 0.47758 | 0.49485 | 14.7692 | 15.4642 | 10.6584 | 51.5416 | 0.30003 | NA | NA | 42.91 | 758.34 | 1412.36 | 1459.1694 | -3.3143 | 88.822 | 1108.7547 | 96.1299 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.9668 | 67.0332 | 0.29455 | NA | N/A | 86.24 | 1412.36 | 2117.83 | 2353.4774 | -11.1268 | 77.5346 | 1882.9187 | 95.4199 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Rejection of reference solute and conditions of test | Magnesium Sulfate = 98 % Rejection | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-02-09 | 14:30 | 3029.85 | 24.4444 | 100 | 70 | 9.6333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 12.4611 | #VALUE! | #VALUE! | N/A | 6.48 | 87.502 | 392.59 | 410.76 | 2436.72 | 2256.4589 | 7.3977 | 78.6975 | 1333.6095 | 93.4387 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7608 | 74.6392 | 0.23093 | 6.48 | NA | 34.161 | 410.76 | 819.72 | 809.7312 | 1.2186 | 91.6835 | 610.2456 | 94.4021 | 80 | 64 | 9.5 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4616 | 51.0384 | 0.30299 | NA | NA | 45.29 | 819.72 | 1662.84 | 1563.1728 | 5.9938 | 88.9741 | 1191.4464 | 96.1987 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 21.3218 | 63.8782 | 0.3091 | NA | N/A | 89.089 | 1662.84 | 2436.72 | 2779.6955 | -14.0753 | 78.3112 | 2221.2678 | 95.9893
|  | (e.g., solute type and concentration) | San Diego Tap = 75 % Rejection | [7 empty] | 1998-02-10 | 8:15 | 3047.46 | 24.4444 | 100 | 72 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.3195 | #VALUE! | #VALUE! | N/A | 6.62 | 40.133 | 379.31 | 411.6 | 2449.59 | 2532.5567 | -3.387 | 90.2495 | 1472.0784 | 97.2737 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.8324 | 74.3676 | 0.23177 | 6.62 | NA | 30.326 | 411.6 | 801.9 | 815.5239 | -1.699 | 92.6322 | 613.562 | 95.0574 | 80 | 65 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2113 | 51.4887 | 0.30034 | NA | NA | 44.38 | 801.9 | 1597.12 | 1529.1192 | 4.2577 | 89.2177 | 1165.5096 | 96.1922 | 120 | 72 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.4429 | 65.5571 | 0.30118 | NA | N/A | 88.242 | 1597.12 | 2449.59 | 2667.9366 | -8.9136 | 78.5612 | 2132.5283 | 95.8621
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1998-02-10 | 16:00 | 3055.1 | 24.4444 | 100 | 70 | 9.7 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.3137 | #VALUE! | #VALUE! | N/A | 6.43 | 46.163 | 385.12 | 417.48 | 2456.74 | 2537.5803 | -3.2906 | 88.9425 | 1477.5301 | 96.8757 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.879 | 74.521 | 0.23129 | 6.43 | NA | 33.158 | 417.48 | 820.71 | 824.633 | -0.478 | 92.0576 | 621.0565 | 94.661 | 80 | 64 | 9.5 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4845 | 51.0155 | 0.30313 | NA | NA | 44.73 | 820.71 | 1634.32 | 1565.6508 | 4.2017 | 89.2857 | 1193.1804 | 96.2512 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.9302 | 64.0698 | 0.30817 | NA | N/A | 89.474 | 1634.32 | 2456.74 | 2730.6623 | -11.1498 | 78.5681 | 2182.4912 | 95.9004
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-02-11 | 7:50 | 3070.95 | 24.4444 | 100 | 70 | 9.5667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0221 | 60.9779 | 0.31172 | N/A | 6.58 | 44.488 | 380.14 | 408.24 | 2453.88 | 2485.1466 | -1.2742 | 89.1025 | 1446.6933 | 96.9248 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7503 | 74.6497 | 0.23089 | 6.58 | NA | 32.332 | 408.24 | 825.66 | 806.4792 | 2.3231 | 92.0801 | 607.3596 | 94.6766 | 80 | 65 | 9.5 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.5567 | 51.4433 | 0.30061 | NA | NA | 44.8 | 825.66 | 1602.08 | 1575.2856 | 1.6725 | 89.0261 | 1200.4728 | 96.2681 | 118 | 70 | 9.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.4819 | 63.9181 | 0.3089 | NA | N/A | 90.321 | 1602.08 | 2453.88 | 2674.9412 | -9.0086 | 77.8755 | 2138.5106 | 95.7765
|  | Standard testing pH | 7 | [7 empty] | 1998-02-11 | 15:40 | 3078.8 | 24.4444 | 100 | 70 | 8.8667 | 0 | 17.4 | 3.1 |  | 20.5 | 20.5 | 0.84878 | 0 | 17.8462 | 18.6859 | 14.0316 | 61.1017 | 0.30582 | N/A | 6.47 | 45.493 | 394.25 | 414.12 | 2498.21 | 2483.1877 | 0.60132 | 89.0145 | 1448.6538 | 96.8596 | 100 | 78 | 8.8 | 10.5 | 10 | 20.5 | 20.5 | 0.49884 | 0.5122 | 16.1538 | 16.9139 | 5.8151 | 74.3849 | 0.22738 | 6.47 | NA | 32.804 | 414.12 | 842.49 | 814.5018 | 3.3221 | 92.0786 | 614.3109 | 94.66 | 78 | 64 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.7882 | 50.2118 | 0.30798 | NA | NA | 45.99 | 842.49 | 1635.56 | 1607.13 | 1.7382 | 88.8945 | 1224.81 | 96.2451 | 118 | 70 | 8.8 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 20.6605 | 64.5395 | 0.29202 | NA | N/A | 92.246 | 1635.56 | 2498.21 | 2681.0308 | -7.3181 | 77.7248 | 2158.2954 | 95.726
|  | Acceptable range of operating pressures | 0 to 350 psi | [7 empty] | 1998-02-11 | 23:00 | 3086.22 | 24.4444 | 100 | 70 | 9.6667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.8498 | 61.2168 | 0.3105 | N/A | 6.51 | 44.756 | 364.37 | 404.04 | 2328.04 | 2455.4357 | -5.4722 | 88.9229 | 1429.7379 | 96.8696 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6734 | 74.5266 | 0.23127 | 6.51 | NA | 33.158 | 404.04 | 807.84 | 796.9546 | 1.3475 | 91.7934 | 600.4973 | 94.4782 | 80 | 64 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2909 | 51.1091 | 0.30257 | NA | NA | 44.94 | 807.84 | 1569.84 | 1540.224 | 1.8866 | 88.8773 | 1174.032 | 96.1722 | 120 | 70 | 9.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.0472 | 65.3528 | 0.30212 | NA | N/A | 90.167 | 1569.84 | 2328.04 | 2619.9305 | -12.538 | 77.6836 | 2094.8853 | 95.6959
|  | Acceptable range of operating pH values | 4 to 11 | [7 empty] | 1998-02-12 | 7:05 | 3094.17 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.2695 | 61.7971 | 0.30759 | N/A | 6.5 | 44.689 | 351.92 | 388.92 | 2275.13 | 2354.368 | -3.4828 | 88.5095 | 1371.644 | 96.7419 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4033 | 74.5967 | 0.23106 | 6.5 | NA | 35.695 | 388.92 | 782.1 | 763.1287 | 2.4257 | 90.822 | 576.0243 | 93.8032 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.939 | 51.261 | 0.30168 | NA | NA | 42.98 | 782.1 | 1526.44 | 1491.6552 | 2.2788 | 88.9489 | 1136.8776 | 96.2195 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.5061 | 65.6939 | 0.30055 | NA | N/A | 86.702 | 1526.44 | 2275.13 | 2548.1895 | -12.0019 | 77.707 | 2037.3148 | 95.7443
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1998-02-13 | 5:30 | 3116.48 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.1233 | 62.01 | 0.30653 | N/A | 6.62 | 45.962 | 352.75 | 386.4 | 2270.84 | 2330.1912 | -2.6136 | 88.1051 | 1358.2956 | 96.6162 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.3675 | 74.6325 | 0.23095 | 6.62 | NA | 35.518 | 386.4 | 781.11 | 758.1265 | 2.9424 | 90.808 | 572.2632 | 93.7934 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.914 | 51.286 | 0.30153 | NA | NA | 43.68 | 781.11 | 1537.6 | 1489.0428 | 3.158 | 88.6957 | 1135.0764 | 96.1518 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6521 | 65.5479 | 0.30122 | NA | N/A | 87.087 | 1537.6 | 2270.84 | 2566.9963 | -13.0417 | 77.462 | 2052.2982 | 95.7566
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-02-13 | 14:00 | 3122.16 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.3875 | 61.9791 | 0.30668 | N/A | 6.52 | 45.828 | 375.16 | 393.12 | 2290.86 | 2376.0453 | -3.7185 | 88.3425 | 1384.5826 | 96.6901 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4829 | 74.5171 | 0.2313 | 6.52 | NA | 34.692 | 393.12 | 803.88 | 772.8408 | 3.8612 | 91.1752 | 582.9804 | 94.0492 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2489 | 50.9511 | 0.30351 | NA | NA | 43.82 | 803.88 | 1594.64 | 1533.5376 | 3.8317 | 88.8533 | 1168.7088 | 96.2506 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.3519 | 64.8481 | 0.30447 | NA | N/A | 92.477 | 1594.64 | 2290.86 | 2660.6912 | -16.1438 | 76.4761 | 2127.6656 | 95.6536
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 1998-02-13 | 22:45 | 3133.92 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.5377 | 62.5956 | 0.30366 | N/A | 6.54 | 45.292 | 359.39 | 396.48 | 2285.14 | 2401.6502 | -5.0986 | 88.5765 | 1399.0651 | 96.7627 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5126 | 74.4874 | 0.2314 | 6.54 | NA | 36.108 | 396.48 | 786.06 | 778.2602 | 0.99226 | 90.8929 | 587.3701 | 93.8526 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.9738 | 51.2262 | 0.30188 | NA | NA | 44.59 | 786.06 | 1554.96 | 1497.8712 | 3.6714 | 88.7535 | 1141.9656 | 96.0953 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.8717 | 65.3283 | 0.30223 | NA | N/A | 88.242 | 1554.96 | 2285.14 | 2595.8566 | -13.5973 | 77.7436 | 2075.4083 | 95.7482
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-02-14 | 9:45 | 3144.9 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6194 | 61.6806 | 0.30817 | N/A | 6.57 | 45.694 | 355.24 | 399 | 2276.56 | 2416.2633 | -6.1366 | 88.5479 | 1407.6316 | 96.7538 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5548 | 74.4452 | 0.23153 | 6.57 | NA | 35.872 | 399 | 784.08 | 783.7 | 0.048469 | 91.0095 | 591.35 | 93.9339 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.9558 | 51.2442 | 0.30177 | NA | NA | 43.82 | 784.08 | 1562.4 | 1494.7296 | 4.3312 | 89.0175 | 1139.4048 | 96.1541 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.9808 | 65.2192 | 0.30274 | NA | N/A | 87.626 | 1562.4 | 2276.56 | 2609.0138 | -14.6033 | 78.0386 | 2085.7069 | 95.7987
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-02-14 | 14:30 | 3149.8 | 24.4444 | 100 | 70 | 9.2667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.4785 | 61.9548 | 0.30681 | N/A | 6.49 | 48.508 | 395.08 | 398.16 | 2473.9 | 2394.5601 | 3.2071 | 87.817 | 1396.3601 | 96.5261 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.588 | 75.012 | 0.22978 | 6.49 | NA | 32.863 | 398.16 | 834.57 | 785.1578 | 5.9207 | 91.7463 | 591.6589 | 94.4456 | 80 | 64 | 9.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.6762 | 50.9238 | 0.30367 | NA | NA | 45.64 | 834.57 | 1604.56 | 1591.9428 | 0.78633 | 88.5373 | 1213.2564 | 96.2382 | 120 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.4331 | 65.5669 | 0.30113 | NA | N/A | 96.404 | 1604.56 | 2473.9 | 2674.8643 | -8.1234 | 75.7876 | 2139.7121 | 95.4945
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-02-14 | 22:15 | 3157.71 | 24.4444 | 100 | 70 | 9.5 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.2606 | 61.8727 | 0.30721 | N/A | 6.52 | 46.699 | 371.84 | 416.64 | 2322.32 | 2528.8838 | -8.8947 | 88.7915 | 1472.7619 | 96.8292 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.8463 | 74.5537 | 0.23119 | 6.52 | NA | 34.456 | 416.64 | 803.88 | 821.528 | -2.1954 | 91.73 | 619.084 | 94.4344 | 80 | 64 | 9.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2375 | 51.3625 | 0.30108 | NA | NA | 44.59 | 803.88 | 1581 | 1532.7984 | 3.0488 | 89.2977 | 1168.3392 | 96.1835 | 120 | 70 | 9.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.1535 | 65.3465 | 0.30215 | NA | N/A | 93.478 | 1581 | 2322.32 | 2636.6608 | -13.5356 | 77.5638 | 2108.8304 | 95.5673
[11 empty] | 1998-02-15 | 9:30 | 3168.68 | 24.4444 | 100 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.8216 | 61.5117 | 0.30902 | N/A | 6.11 | 47.168 | 381.8 | 405.72 | 2428.14 | 2452.9363 | -1.0212 | 88.3742 | 1429.3281 | 96.7 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7135 | 74.4865 | 0.2314 | 6.11 | NA | 32.214 | 405.72 | 827.64 | 801.4145 | 3.1687 | 92.06 | 603.5672 | 94.6627 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.5777 | 50.6223 | 0.30548 | NA | NA | 45.36 | 827.64 | 1594.64 | 1578.6288 | 1.0041 | 88.8199 | 1203.1344 | 96.2298 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.3164 | 64.8836 | 0.30431 | NA | N/A | 95.095 | 1594.64 | 2428.14 | 2658.8332 | -9.5008 | 76.5614 | 2126.7366 | 95.5286
[11 empty] | 1998-02-15 | 14:40 | 3173.84 | 24.4444 | 100 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6243 | 61.509 | 0.30903 | N/A | 6.52 | 43.885 | 375.16 | 397.32 | 2405.26 | 2415.3198 | -0.41824 | 88.9547 | 1406.3199 | 96.8794 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5562 | 74.8438 | 0.23029 | 6.52 | NA | 34.102 | 397.32 | 822.69 | 782.1153 | 4.932 | 91.417 | 589.7177 | 94.2172 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4879 | 50.7121 | 0.30494 | NA | NA | 46.48 | 822.69 | 1554.96 | 1567.8516 | -0.82906 | 88.3016 | 1195.2708 | 96.1113 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7986 | 65.2014 | 0.30282 | NA | N/A | 93.632 | 1554.96 | 2405.26 | 2592.0315 | -7.7651 | 76.4341 | 2073.4957 | 95.4843
[11 empty] | 1998-02-15 | 22:00 | 3181.08 | 24.4444 | 100 | 70 | 9.9 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.7696 | 61.3638 | 0.30976 | N/A | 6.53 | 45.158 | 385.12 | 402.36 | 2372.37 | 2441.8682 | -2.9295 | 88.7767 | 1422.1141 | 96.8246 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6432 | 74.5568 | 0.23118 | 6.53 | NA | 33.453 | 402.36 | 834.57 | 793.1823 | 4.9592 | 91.6858 | 597.7711 | 94.4037 | 80 | 64 | 9.9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.6762 | 50.4238 | 0.30668 | NA | NA | 45.64 | 834.57 | 1571.08 | 1591.9428 | -1.3279 | 88.6569 | 1213.2564 | 96.2382 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.0087 | 64.9913 | 0.3038 | NA | N/A | 94.248 | 1571.08 | 2372.37 | 2619.1543 | -10.4024 | 76.5762 | 2095.1172 | 95.5015
[11 empty] | 1998-02-16 | 7:30 | 3190.58 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.8822 | 61.2511 | 0.31033 | N/A | 6.54 | 44.756 | 380.14 | 404.88 | 2419.56 | 2461.0719 | -1.7157 | 88.9459 | 1432.9759 | 96.8767 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6772 | 74.5228 | 0.23129 | 6.54 | NA | 33.748 | 404.88 | 829.62 | 798.0594 | 3.8042 | 91.6647 | 601.4697 | 94.3891 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.5988 | 50.6012 | 0.30561 | NA | NA | 45.92 | 829.62 | 1559.92 | 1581.972 | -1.4137 | 88.6584 | 1205.796 | 96.1917 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.8627 | 65.1373 | 0.30312 | NA | N/A | 93.863 | 1559.92 | 2419.56 | 2600.3475 | -7.4719 | 76.8171 | 2080.1338 | 95.4876
[11 empty] | 1998-02-16 | 16:30 | 3199.42 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6283 | 61.505 | 0.30905 | N/A | 6.52 | 44.622 | 378.48 | 398.16 | 2399.54 | 2416.7479 | -0.71713 | 88.7929 | 1407.454 | 96.8296 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5744 | 74.6256 | 0.23097 | 6.52 | NA | 33.748 | 398.16 | 825.66 | 784.2202 | 5.019 | 91.524 | 591.1901 | 94.2915 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.5484 | 50.6516 | 0.30531 | NA | NA | 45.36 | 825.66 | 1569.84 | 1574.748 | -0.31264 | 88.6076 | 1200.204 | 96.2206 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.0044 | 64.9956 | 0.30378 | NA | N/A | 93.324 | 1569.84 | 2399.54 | 2617.6901 | -9.0913 | 76.5612 | 2093.765 | 95.5428
[11 empty] | 1998-02-16 | 22:30 | 3205.55 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.5518 | 61.5815 | 0.30867 | N/A | 6.5 | 44.086 | 372.67 | 395.64 | 2355.21 | 2402.8999 | -2.0249 | 88.857 | 1399.27 | 96.8494 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5431 | 74.6569 | 0.23087 | 6.5 | NA | 33.276 | 395.64 | 812.79 | 779.5306 | 4.092 | 91.5893 | 587.5853 | 94.3368 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.3631 | 50.8369 | 0.30419 | NA | NA | 45.01 | 812.79 | 1552.48 | 1549.8588 | 0.16884 | 88.6235 | 1181.3244 | 96.1899 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7744 | 65.2256 | 0.30271 | NA | N/A | 92.939 | 1552.48 | 2355.21 | 2588.2833 | -9.8961 | 76.5092 | 2070.3816 | 95.511
[11 empty] | 1998-02-17 | 14:40 | 3221.83 | 24.4444 | 100 | 70 | 9.1333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6168 | 62.1165 | 0.30601 | N/A | 6.47 | 45.761 | 377.65 | 399 | 2366.65 | 2415.8807 | -2.0802 | 88.5311 | 1407.4404 | 96.7486 | 100 | 80 | 9.3 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.618 | 75.082 | 0.22956 | 6.47 | NA | 31.742 | 399 | 797.94 | 788.0753 | 1.2363 | 92.0446 | 593.5377 | 94.6521 | 80 | 62 | 9.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.1403 | 50.6597 | 0.30526 | NA | NA | 45.22 | 797.94 | 1588.44 | 1520.5512 | 4.2739 | 88.6667 | 1159.2456 | 96.0992 | 120 | 70 | 8.9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.2867 | 65.8133 | 0.30001 | NA | N/A | 91.091 | 1588.44 | 2366.65 | 2651.0748 | -12.018 | 77.1702 | 2119.7574 | 95.7028
[11 empty] | 1998-02-17 | 22:00 | 3228.9 | 24.4444 | 100 | 70 | 9.4 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0417 | 61.4583 | 0.30928 | N/A | 6.5 | 46.498 | 380.97 | 410.76 | 2360.93 | 2490.5785 | -5.4914 | 88.68 | 1450.6693 | 96.7947 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.8042 | 74.5958 | 0.23106 | 6.5 | NA | 31.329 | 410.76 | 784.08 | 812.7315 | -3.6541 | 92.3729 | 611.7457 | 94.8788 | 80 | 64 | 9.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.9424 | 51.6576 | 0.29936 | NA | NA | 44.73 | 784.08 | 1619.44 | 1493.856 | 7.7548 | 89.1104 | 1138.968 | 96.0728 | 120 | 70 | 9.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.6921 | 65.1079 | 0.30326 | NA | N/A | 92.169 | 1619.44 | 2360.93 | 2703.3097 | -14.5019 | 77.5613 | 2161.3749 | 95.7356
[11 empty] | 1998-02-18 | 8:45 | 3240.08 | 24.4444 | 100 | 70 | 9.5667 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.9007 | 14.3011 | 60.8989 | 0.31036 | N/A | 6.56 | 42.411 | 398.4 | 414.96 | 2438.15 | 2530.0769 | -3.7704 | 89.7795 | 1472.5185 | 97.1198 | 100 | 79 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | 5.8896 | 73.8104 | 0.23352 | 6.56 | NA | 31.27 | 414.96 | 844.47 | 825.5083 | 2.2454 | 92.4643 | 620.2341 | 94.9584 | 79 | 62 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.831 | 49.069 | 0.31515 | NA | NA | 45.08 | 844.47 | 1609.52 | 1611.8844 | -0.1469 | 89.1363 | 1228.1772 | 96.3295 | 119 | 70 | 9.3 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 20.2892 | 64.9108 | 0.29035 | NA | N/A | 93.94 | 1609.52 | 2438.15 | 2636.2032 | -8.1231 | 77.3617 | 2122.8616 | 95.5748
[11 empty] | 1998-02-19 | 5:30 | 3260.67 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.9007 | #VALUE! | #VALUE! | #VALUE! | N/A | 6.49 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 100 | 80 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | #VALUE! | #VALUE! | #VALUE! | 6.49 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 80 | 62 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 120 | 70 | 9.2 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | #VALUE! | #VALUE! | #VALUE! | NA | N/A | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-02-19 | 16:00 | 3265.66 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.9007 | 13.5806 | 61.5194 | 0.30723 | N/A | 6.46 | 46.9 | 378.48 | 400.68 | 2516.8 | 2409.2374 | 4.2738 | 88.2949 | 1404.9587 | 96.6618 | 100 | 80 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | 5.6596 | 74.5404 | 0.23123 | 6.46 | NA | 31.978 | 400.68 | 830.61 | 795.1911 | 4.2642 | 92.0191 | 597.9356 | 94.6519 | 80 | 62 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.6321 | 49.7679 | 0.31073 | NA | NA | 44.66 | 830.61 | 1641.76 | 1585.122 | 3.4498 | 88.8539 | 1207.866 | 96.3026 | 120 | 70 | 9.2 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 20.727 | 65.073 | 0.28963 | NA | N/A | 93.478 | 1641.76 | 2516.8 | 2690.5962 | -6.9054 | 76.6702 | 2166.1781 | 95.6847
[11 empty] | 1998-02-20 | 5:00 | 3278.48 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.9007 | 13.8348 | #VALUE! | #VALUE! | N/A | 6.57 | 47.838 | 381.8 | 408.24 | 2536.82 | 2454.3933 | 3.2492 | 88.2819 | 1431.3166 | 96.6578 | 100 | 80 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | 5.7801 | 74.4199 | 0.23161 | 6.57 | NA | 31.683 | 408.24 | 844.47 | 811.156 | 3.945 | 92.2391 | 609.698 | 94.8035 | 80 | 62 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8299 | 49.5701 | 0.31197 | NA | NA | 45.15 | 844.47 | 1672.76 | 1611.8172 | 3.6432 | 88.9403 | 1228.1436 | 96.3237 | 120 | 70 | 9.2 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 21.1296 | 64.6704 | 0.29143 | NA | N/A | 94.402 | 1672.76 | 2536.82 | 2741.9703 | -8.0869 | 76.8759 | 2207.3651 | 95.7233
[11 empty] | 1998-02-20 | 17:00 | 3290.85 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.9007 | 13.7315 | #VALUE! | #VALUE! | N/A | 6.55 | 47.168 | 393.42 | 404.88 | 2499.64 | 2435.761 | 2.5555 | 88.3501 | 1420.3205 | 96.6791 | 100 | 80 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | 5.7268 | 74.4732 | 0.23144 | 6.55 | NA | 31.801 | 404.88 | 836.55 | 804.0745 | 3.8821 | 92.1456 | 604.4773 | 94.7391 | 80 | 62 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.7158 | 49.6842 | 0.31125 | NA | NA | 44.94 | 836.55 | 1656.64 | 1596.4956 | 3.6305 | 88.9004 | 1216.5228 | 96.3059 | 120 | 70 | 9.2 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 20.9231 | 64.8769 | 0.2905 | NA | N/A | 93.709 | 1656.64 | 2499.64 | 2715.3997 | -8.6316 | 76.8551 | 2186.0199 | 95.7133
[11 empty] | 1998-02-21 | 8:00 | 3307.82 | 25.5556 | 100 | 70 | 10.1333 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.29 | 13.9705 | #VALUE! | #VALUE! | N/A | 6.66 | 39.262 | 399.23 | 403.2 | 2542.54 | 2469.4286 | 2.8755 | 90.2624 | 1436.3143 | 97.2665 | 100 | 80 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 5.7372 | 74.4628 | 0.22399 | 6.66 | NA | 29.441 | 403.2 | 831.6 | 803.1221 | 3.4245 | 92.6982 | 603.1611 | 95.1189 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 11.7047 | 49.4953 | 0.30234 | NA | NA | 40.74 | 831.6 | 1613.24 | 1590.8256 | 1.3894 | 89.8958 | 1211.2128 | 96.6364 | 120 | 70 | 10.8 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.238 | 20.5349 | 63.6651 | 0.28647 | NA | N/A | 79.31 | 1613.24 | 2542.54 | 2652.3539 | -4.3191 | 80.3299 | 2132.7969 | 96.2814
[11 empty] | 1998-02-21 | 15:30 | 3313.19 | 24.4444 | 100 | 70 | 9.7333 | 0 | 17.6 | 3.1 |  | 20.7 | 20.7 | 0.85024 | 0 | 18.0513 | 18.9007 | 13.8495 | #VALUE! | #VALUE! | N/A | 6.57 | 40.736 | 389.27 | 401.52 | 2519.66 | 2449.8421 | 2.7709 | 89.8546 | 1425.681 | 97.1427 | 100 | 80 | 9.8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 17.2361 | 5.6888 | 74.5112 | 0.23132 | 6.57 | NA | 30.916 | 401.52 | 841.5 | 798.0663 | 5.1615 | 92.3003 | 599.7931 | 94.8456 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8285 | 49.3715 | 0.31322 | NA | NA | 42.28 | 841.5 | 1646.72 | 1608.7512 | 2.3057 | 89.47 | 1225.1256 | 96.5489 | 120 | 70 | 9.6 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.847 | 20.748 | 64.652 | 0.29151 | NA | N/A | 96.866 | 1646.72 | 2519.66 | 2696.6211 | -7.0232 | 75.8752 | 2171.6705 | 95.5396
[11 empty] | 1998-02-21 | 22:40 | 3320.3 | 24.4444 | 100 | 70 | 10.1333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.5207 | 61.6127 | 0.30851 | N/A | 6.64 | 43.215 | 378.48 | 393.96 | 2276.56 | 2396.6008 | -5.2729 | 89.0306 | 1395.2804 | 96.9028 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5345 | 74.6655 | 0.23084 | 6.64 | NA | 32.155 | 393.96 | 802.89 | 777.2584 | 3.1924 | 91.838 | 585.6092 | 94.5091 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2954 | 50.9046 | 0.30379 | NA | NA | 39.69 | 802.89 | 1521.48 | 1535.562 | -0.92555 | 89.9254 | 1169.226 | 96.6054 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.5568 | 64.6432 | 0.30544 | NA | N/A | 78.001 | 1521.48 | 2276.56 | 2545.8845 | -11.8303 | 80.2008 | 2033.6822 | 96.1645
[11 empty] | 1998-02-22 | 0:00 | 3330.62 | 25.5556 | 100 | 70 | 10.0333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 18.3939 | 12.2376 | 62.8958 | 0.29245 | N/A | 6.65 | 36.18 | 379.31 | 353.64 | 2349.49 | 2166.2342 | 7.7998 | 89.7693 | 1259.9371 | 97.1284 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 16.6792 | 4.971 | 75.229 | 0.22171 | 6.65 | NA | 28.674 | 353.64 | 781.11 | 697.9109 | 10.6514 | 91.8918 | 525.7755 | 94.5463 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 10.9254 | 51.2746 | 0.29185 | NA | NA | 42.91 | 781.11 | 1520.24 | 1489.782 | 2.0035 | 87.8662 | 1135.446 | 96.2209 | 120 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 19.5776 | 64.9224 | 0.2943 | NA | N/A | 75.229 | 1520.24 | 2349.49 | 2545.7317 | -8.3525 | 78.7272 | 2032.9858 | 96.2996
[11 empty] | 1998-02-22 | 16:00 | 3337.65 | 24.4444 | 100 | 70 | 10.0333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.0918 | 62.0416 | 0.30638 | N/A | 6.57 | 41.741 | 381.8 | 381.36 | 2325.18 | 2320.4749 | 0.20235 | 89.0547 | 1350.9175 | 96.9102 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.3842 | 74.8158 | 0.23038 | 6.57 | NA | 29.382 | 381.36 | 788.04 | 754.2476 | 4.2882 | 92.2955 | 567.8038 | 94.8253 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.0476 | 51.1524 | 0.30232 | NA | NA | 41.58 | 788.04 | 1589.68 | 1504.6416 | 5.3494 | 89.0969 | 1146.3408 | 96.3728 | 120 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.5027 | 63.9973 | 0.30852 | NA | N/A | 76.384 | 1589.68 | 2325.18 | 2663.632 | -14.5559 | 79.9706 | 2126.656 | 96.4083
[11 empty] | 1998-02-22 | 23:10 | 3344.71 | 24.4444 | 100 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6252 | 62.2415 | 0.30539 | N/A | 6.58 | 39.664 | 383.46 | 393.12 | 2339.48 | 2411.2397 | -3.0673 | 89.9105 | 1402.1799 | 97.1713 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5569 | 74.6431 | 0.23091 | 6.58 | NA | 29.854 | 393.12 | 804.87 | 777.9662 | 3.3426 | 92.4059 | 585.5431 | 94.9015 | 80 | 64 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2988 | 51.1012 | 0.30262 | NA | NA | 41.44 | 804.87 | 1567.36 | 1537.7628 | 1.8883 | 89.4587 | 1171.3164 | 96.4621 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.1857 | 64.8143 | 0.30463 | NA | N/A | 77.462 | 1567.36 | 2339.48 | 2624.707 | -12.1919 | 80.2956 | 2096.0335 | 96.3044
[11 empty] | 1998-02-23 | 15:45 | 3361.31 | 24.4444 | 100 | 70 | 10.0333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.3246 | 62.2754 | 0.30523 | N/A | 6.48 | 39.061 | 393.42 | 384.72 | 2433.86 | 2358.3214 | 3.1037 | 89.8469 | 1371.5207 | 97.152 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.414 | 74.786 | 0.23047 | 6.48 | NA | 30.798 | 384.72 | 837.54 | 759.6671 | 9.2978 | 91.9947 | 572.1935 | 94.6176 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.7688 | 50.4312 | 0.30664 | NA | NA | 42.35 | 837.54 | 1552.48 | 1600.9224 | -3.1203 | 88.992 | 1219.2312 | 96.5265 | 120 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.9685 | 64.5315 | 0.30597 | NA | N/A | 78.617 | 1552.48 | 2433.86 | 2598.4473 | -6.7624 | 79.5651 | 2075.4636 | 96.2121
[11 empty] | 1998-02-23 | 22:25 | 3368.02 | 24.4444 | 100 | 70 | 10.1667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 12.3929 | 63.0405 | 0.30152 | 7.4 | 6.54 | 46.431 | 371.84 | 367.92 | 2159.3 | 2203.5185 | -2.0478 | 87.3801 | 1285.7192 | 96.3887 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.2102 | 74.7898 | 0.23046 | 6.54 | NA | 27.317 | 367.92 | 760.32 | 728.7568 | 4.1513 | 92.5753 | 548.3384 | 95.0182 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.6695 | 51.5305 | 0.3001 | NA | NA | 39.41 | 760.32 | 1433.44 | 1452.3936 | -1.3222 | 89.2884 | 1106.3568 | 96.4379 | 120 | 70 | 10.7 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.4057 | 65.8943 | 0.29964 | NA | 7.2 | 74.921 | 1433.44 | 2159.3 | 2397.5503 | -11.0337 | 79.6366 | 1915.4951 | 96.0887
[11 empty] | 1998-02-24 | 7:45 | 3377.37 | 24.4444 | 100 | 70 | 10.0333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.2783 | 62.1884 | 0.30565 | 7.6 | 6.57 | 41.942 | 380.14 | 386.4 | 2328.04 | 2353.1441 | -1.0783 | 89.1454 | 1369.772 | 96.938 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4469 | 74.7531 | 0.23057 | 6.57 | NA | 30.326 | 386.4 | 811.8 | 763.6269 | 5.9341 | 92.1517 | 575.0135 | 94.726 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4117 | 50.7883 | 0.30448 | NA | NA | 40.74 | 811.8 | 1531.4 | 1552.0176 | -1.3463 | 89.4565 | 1181.9088 | 96.553 | 120 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7121 | 64.7879 | 0.30476 | NA | 7.3 | 76.461 | 1531.4 | 2328.04 | 2563.9374 | -10.1329 | 80.212 | 2047.6687 | 96.2659
[11 empty] | 1998-02-24 | 16:00 | 3386.11 | 25.5556 | 100 | 70 | 9.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 18.3939 | 13.6617 | 61.805 | 0.29761 | 7.6 | 6.45 | 42.076 | 391.76 | 396.48 | 2256.54 | 2420.0125 | -7.2444 | 89.3876 | 1408.2463 | 97.0122 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 16.6792 | 5.5902 | 75.0098 | 0.22236 | 6.45 | NA | 31.034 | 396.48 | 804.87 | 783.6357 | 2.6382 | 92.1726 | 590.0578 | 94.7405 | 80 | 62 | 9.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 11.3288 | 50.2712 | 0.29768 | NA | NA | 39.41 | 804.87 | 1538.84 | 1539.7116 | -0.05664 | 90.06 | 1172.2908 | 96.6382 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 19.8223 | 65.1777 | 0.29314 | NA | 7.1 | 75.768 | 1538.84 | 2256.54 | 2577.1492 | -14.208 | 80.8898 | 2057.9946 | 96.3184
[11 empty] | 1998-02-24 | 23:40 | 3393.43 | 24.4444 | 100 | 70 | 10.0667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 12.5715 | 62.8952 | 0.30222 | 7.42 | 6.57 | 45.158 | 378.48 | 371.28 | 2290.86 | 2233.3314 | 2.5112 | 87.8372 | 1302.3057 | 96.5325 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.2246 | 74.9754 | 0.22989 | 6.57 | NA | 29.736 | 371.28 | 774.18 | 733.1137 | 5.3045 | 91.991 | 552.1969 | 94.615 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.8663 | 51.3337 | 0.30125 | NA | NA | 39.97 | 774.18 | 1470.64 | 1479.0216 | -0.56993 | 89.2345 | 1126.6008 | 96.4522 | 120 | 70 | 10.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.9004 | 65.4996 | 0.30144 | NA | 7.2 | 75.614 | 1470.64 | 2290.86 | 2460.6585 | -7.412 | 79.6342 | 1965.6492 | 96.1532
[11 empty] | 1998-02-25 | 7:00 | 3400.98 | 25.5556 | 100 | 70 | 10.2667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 17.8743 | 13.2001 | 62.2666 | 0.28706 | 7.7 | 6.58 | 34.974 | 373.5 | 384.72 | 2299.44 | 2325.2462 | -1.1223 | 90.9092 | 1354.9831 | 97.4189 | 100 | 80 | 10 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 15.8998 | 5.3228 | 74.6772 | 0.21291 | 6.58 | NA | 31.034 | 384.72 | 833.58 | 741.9078 | 10.9974 | 91.9334 | 563.3139 | 94.4908 | 80 | 62 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 11.7102 | 49.2898 | 0.3036 | NA | NA | 42.35 | 833.58 | 1148.24 | 1593.1608 | -38.7481 | 88.992 | 1213.3704 | 96.5097 | 120 | 70 | 10.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 14.5157 | 69.6843 | 0.27419 | NA | 7.4 | 76.846 | 1148.24 | 2299.44 | 1908.5841 | 16.9979 | 80.0255 | 1528.4121 | 94.9722
[11 empty] | 1998-02-25 | 21:00 | 3413.33 | 24.4444 | 100 | 70 | 10 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 17.641 | 18.4711 | 13.3232 | 61.5435 | 0.30013 | 7.6 | 6.45 | 35.912 | 371.01 | 388.92 | 2318.03 | 2347.545 | -1.2733 | 90.7662 | 1368.2325 | 97.3753 | 100 | 80 | 9.8 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 16.4307 | 5.3807 | 74.8193 | 0.2196 | 6.45 | NA | 31.388 | 388.92 | 840.51 | 749.9919 | 10.7694 | 91.9294 | 569.456 | 94.4881 | 80 | 62 | 10.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8003 | 48.9997 | 0.3156 | NA | NA | 43.19 | 840.51 | 1168.08 | 1605.9372 | -37.4852 | 88.8949 | 1223.2236 | 96.4692 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 14.797 | 70.203 | 0.28125 | NA | 7.4 | 75.922 | 1168.08 | 2318.03 | 1943.1599 | 16.1719 | 80.4788 | 1555.6199 | 95.1195
[11 empty] | 1998-02-25 | 23:00 | 3415.56 | 24.4444 | 100 | 70 | 9.4333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6629 | 61.6038 | 0.30855 | 7.2 | 6.47 | 41.205 | 380.14 | 395.64 | 2203.63 | 2419.3495 | -9.7893 | 89.5852 | 1407.4948 | 97.0725 | 100 | 80 | 9 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5864 | 75.4136 | 0.22855 | 6.47 | NA | 30.444 | 395.64 | 792 | 782.5308 | 1.1956 | 92.3051 | 589.0854 | 94.832 | 80 | 64 | 9.5 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.0254 | 51.4746 | 0.30042 | NA | NA | 47.04 | 792 | 1526.44 | 1507.1616 | 1.263 | 88.1104 | 1149.5808 | 95.9081 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.6574 | 65.5426 | 0.30125 | NA | 7 | 75.537 | 1526.44 | 2203.63 | 2556.1131 | -15.9956 | 80.9076 | 2041.2765 | 96.2995
[11 empty] | 1998-02-26 | 9:45 | 3426.14 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.12 | 60.7467 | 0.31291 | 7.2 | 6.5 | 40.267 | 384.29 | 406.56 | 2277.99 | 2497.9749 | -9.657 | 90.0957 | 1452.2674 | 97.2273 | 100 | 80 | 9.2 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7462 | 75.0538 | 0.22965 | 6.5 | NA | 30.916 | 406.56 | 818.73 | 804.5195 | 1.7357 | 92.3957 | 605.5397 | 94.8945 | 80 | 64 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4479 | 50.9521 | 0.3035 | NA | NA | 45.22 | 818.73 | 1310.68 | 1561.2996 | -19.1213 | 88.8774 | 1190.0148 | 96.2 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 16.7321 | 68.4679 | 0.28838 | NA | 7.3 | 75.691 | 1310.68 | 2277.99 | 2187.1238 | 3.9889 | 81.3826 | 1748.9019 | 95.6721
[11 empty] | 1998-02-26 | 14:15 | 3430.62 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.1498 | 60.8169 | 0.31255 | 7.2 | 6.5 | 40.334 | 381.8 | 407.4 | 2279.42 | 2503.2285 | -9.8187 | 90.0997 | 1455.3142 | 97.2285 | 100 | 80 | 9.2 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7618 | 75.0382 | 0.2297 | 6.5 | NA | 30.739 | 407.4 | 816.75 | 806.4369 | 1.2627 | 92.4548 | 606.9185 | 94.9352 | 80 | 64 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4145 | 50.9855 | 0.30331 | NA | NA | 45.5 | 816.75 | 1309.44 | 1557.15 | -18.9172 | 88.8316 | 1186.95 | 96.1666 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 16.7164 | 68.4836 | 0.28831 | NA | 7.4 | 75.614 | 1309.44 | 2279.42 | 2185.0585 | 4.1397 | 81.4399 | 1747.2492 | 95.6724
[11 empty] | 1998-02-26 | 22:45 | 3439.26 | 24.4444 | 100 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.6881 | 61.2786 | 0.31019 | 7.3 | 6.45 | 46.431 | 382.63 | 401.52 | 2403.83 | 2428.9636 | -1.0456 | 88.4362 | 1415.2418 | 96.7192 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6664 | 74.7336 | 0.23063 | 6.45 | NA | 31.093 | 401.52 | 835.56 | 793.9526 | 4.9796 | 92.2562 | 597.7363 | 94.7982 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.754 | 50.446 | 0.30655 | NA | NA | 41.37 | 835.56 | 1587.2 | 1597.9824 | -0.67933 | 89.6967 | 1216.7712 | 96.6 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.443 | 64.557 | 0.30585 | NA | 6.9 | 78.309 | 1587.2 | 2403.83 | 2658.0259 | -10.5746 | 80.4969 | 2122.6129 | 96.3107
[11 empty] | 1998-02-27 | 8:00 | 3448.47 | 24.4444 | 100 | 70 | 9.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0598 | 61.1402 | 0.31089 | 7.3 | 6.42 | 46.029 | 391.76 | 410.76 | 2336.62 | 2493.2564 | -6.7035 | 88.7942 | 1452.0082 | 96.83 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7997 | 74.8003 | 0.23043 | 6.42 | NA | 31.624 | 410.76 | 844.47 | 812.4189 | 3.7954 | 92.3011 | 611.5895 | 94.8292 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8382 | 50.3618 | 0.30706 | NA | NA | 44.59 | 844.47 | 1434.68 | 1612.3548 | -12.3843 | 89.1445 | 1228.4124 | 96.3701 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.3923 | 66.6077 | 0.29643 | NA | 7.2 | 77.154 | 1434.68 | 2336.62 | 2398.0855 | -2.6305 | 81.2168 | 1916.3828 | 95.974
[11 empty] | 1998-02-27 | 15:45 | 3455.77 | 24.4444 | 100 | 70 | 9.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0222 | 60.9444 | 0.31189 | 7.2 | 6.44 | 46.163 | 390.1 | 409.92 | 2338.05 | 2486.8551 | -6.3645 | 88.7385 | 1448.3876 | 96.8128 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7886 | 74.8114 | 0.23039 | 6.44 | NA | 31.506 | 409.92 | 843.48 | 810.814 | 3.8728 | 92.3141 | 610.367 | 94.8382 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8153 | 50.3847 | 0.30692 | NA | NA | 45.15 | 843.48 | 1433.44 | 1609.8768 | -12.3086 | 88.9857 | 1226.6784 | 96.3193 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.3651 | 66.6349 | 0.29631 | NA | 7.2 | 77.924 | 1433.44 | 2338.05 | 2395.4191 | -2.4537 | 80.9904 | 1914.4295 | 95.9296
[11 empty] | 1998-02-28 | 0:15 | 3463.78 | 24.4444 | 100 | 70 | 9.6667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.561 | 61.2724 | 0.31022 | 7.4 | 6.42 | 44.689 | 386.78 | 396.48 | 2328.04 | 2405.0931 | -3.3098 | 88.7286 | 1400.7866 | 96.8097 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5993 | 75.0007 | 0.22981 | 6.42 | NA | 30.444 | 396.48 | 837.54 | 784.2607 | 6.3614 | 92.3214 | 590.3704 | 94.8432 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.7408 | 49.4592 | 0.31267 | NA | NA | 44.24 | 837.54 | 1423.52 | 1599.108 | -12.3348 | 88.8418 | 1218.324 | 96.3688 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.2244 | 66.9756 | 0.2948 | NA | 7.1 | 78.386 | 1423.52 | 2328.04 | 2378.1312 | -2.1516 | 80.2295 | 1900.8256 | 95.8762
[11 empty] | 1998-02-28 | 9:00 | 3473.2 | 24.4444 | 100 | 70 | 9.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.7825 | 61.1842 | 0.31067 | 7.4 | 6.43 | 44.823 | 375.99 | 402.36 | 2313.74 | 2443.7809 | -5.6204 | 88.86 | 1423.0705 | 96.8503 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.682 | 74.718 | 0.23068 | 6.43 | NA | 30.916 | 402.36 | 848.43 | 795.87 | 6.195 | 92.3163 | 599.115 | 94.8397 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.8948 | 49.3052 | 0.31364 | NA | NA | 44.73 | 848.43 | 1427.24 | 1619.982 | -13.5045 | 88.8831 | 1234.206 | 96.3758 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.2842 | 66.9158 | 0.29506 | NA | 7.2 | 77.693 | 1427.24 | 2313.74 | 2384.983 | -3.0791 | 80.6907 | 1906.1115 | 95.924
[11 empty] | 1998-02-28 | 14:40 | 3478.68 | 24.4444 | 100 | 70 | 9.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 12.0127 | 63.3873 | 0.29987 | 7.4 | 6.42 | 40.334 | 377.65 | 351.96 | 2315.17 | 2131.2439 | 7.9444 | 88.5402 | 1241.602 | 96.7515 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 4.8848 | 75.5152 | 0.22825 | 6.42 | NA | 32.627 | 351.96 | 855.36 | 690.2633 | 19.3014 | 90.7299 | 521.1116 | 93.739 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 12.0367 | 49.1633 | 0.31455 | NA | NA | 42.07 | 855.36 | 1426 | 1636.1184 | -14.7348 | 88.0469 | 1245.7392 | 96.6229 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.2643 | 66.9357 | 0.29498 | NA | 7.2 | 77.924 | 1426 | 2315.17 | 2382.6991 | -2.9168 | 77.86 | 1904.3495 | 95.9081
[11 empty] | 1998-03-01 | 0:15 | 3486.84 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.88 | 61.0533 | 0.31134 | 7.4 | 6.4 | 37.252 | 380.97 | 397.32 | 2237.95 | 2453.1921 | -9.6178 | 90.6242 | 1425.2561 | 97.3863 | 100 | 80 | 9.2 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6247 | 75.1753 | 0.22928 | 6.4 | NA | 29.618 | 397.32 | 789.03 | 786.8657 | 0.2743 | 92.5456 | 592.0928 | 94.9977 | 80 | 62 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.0602 | 50.3398 | 0.3072 | NA | NA | 41.72 | 789.03 | 1483.04 | 1506.4476 | -1.5784 | 89.4996 | 1147.7388 | 96.365 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.0694 | 66.1306 | 0.29857 | NA | 6.9 | 75.537 | 1483.04 | 2237.95 | 2481.9131 | -10.9012 | 80.9884 | 1982.4765 | 96.1898
[11 empty] | 1998-03-01 | 10:00 | 3498.81 | 24.4444 | 100 | 70 | 9.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.1005 | 61.6328 | 0.30841 | 7.4 | 6.45 | 38.994 | 384.29 | 378.84 | 2257.97 | 2319.251 | -2.714 | 89.707 | 1349.0455 | 97.1095 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.3195 | 75.2805 | 0.22896 | 6.45 | NA | 31.093 | 378.84 | 814.77 | 747.2452 | 8.2876 | 91.7926 | 563.0426 | 94.4777 | 80 | 60 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4442 | 48.9558 | 0.31588 | NA | NA | 41.51 | 814.77 | 1465.68 | 1557.0996 | -6.2374 | 89.0429 | 1185.9348 | 96.4998 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.8185 | 66.3815 | 0.29744 | NA | 7.1 | 76.692 | 1465.68 | 2257.97 | 2451.4134 | -8.5671 | 79.7561 | 1958.5467 | 96.0842
[11 empty] | 1998-03-01 | 17:45 | 3505.75 | 24.4444 | 100 | 70 | 9.6 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.2817 | 61.7183 | 0.30798 | 7.4 | 6.44 | 37.654 | 381.8 | 382.2 | 2259.4 | 2349.4465 | -3.9854 | 90.1481 | 1365.8233 | 97.2431 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.3592 | 75.2408 | 0.22908 | 6.44 | NA | 31.86 | 382.2 | 816.75 | 753.3523 | 7.7622 | 91.6641 | 567.7761 | 94.3886 | 80 | 60 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4849 | 48.9151 | 0.31614 | NA | NA | 40.74 | 816.75 | 1473.12 | 1561.7196 | -6.0144 | 89.3407 | 1189.2348 | 96.5743 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.9266 | 66.2734 | 0.29792 | NA | 7.1 | 76.153 | 1473.12 | 2259.4 | 2464.5159 | -9.0783 | 80.0751 | 1968.818 | 96.132
[11 empty] | 1998-03-02 | 0:15 | 3512.26 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.4953 | 62.0714 | 0.30623 | 7.4 | 6.45 | 36.314 | 376.82 | 386.4 | 2237.95 | 2385.2781 | -6.5832 | 90.602 | 1385.8391 | 97.3796 | 100 | 80 | 9.4 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4378 | 75.1622 | 0.22932 | 6.45 | NA | 30.916 | 386.4 | 804.87 | 763.0019 | 5.2019 | 91.999 | 574.7009 | 94.6205 | 80 | 60 | 9.6 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.3257 | 49.0743 | 0.31512 | NA | NA | 39.62 | 804.87 | 1452.04 | 1539.51 | -6.0239 | 89.7464 | 1172.19 | 96.62 | 120 | 70 | 9.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.6275 | 66.7725 | 0.2957 | NA | 7.1 | 77.154 | 1452.04 | 2237.95 | 2427.7655 | -8.4817 | 80.0326 | 1939.9028 | 96.0228
[11 empty] | 1998-03-02 | 11:00 | 3523.28 | 24.4444 | 100 | 70 | 8.9333 | 0 | 17.5 | 3.5 |  | 21 | 21 | 0.83333 | 0 | 17.9487 | 18.7933 | 12.4188 | 63.0479 | 0.29808 | 7.6 | 6.42 | 35.778 | 362.71 | 390.6 | 2219.36 | 2164.71 | 2.4624 | 90.8402 | 1277.655 | 97.1997 | 100 | 80 | 9 | 10.5 | 10.5 | 21 | 21 | 0.5152 | 0.5 | 16.1538 | 16.9139 | 5.3864 | 75.6136 | 0.22369 | 6.42 | NA | 31.506 | 390.6 | 816.75 | 749.694 | 8.2101 | 91.9339 | 570.147 | 94.4741 | 80 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4539 | 50.5461 | 0.30594 | NA | NA | 42.84 | 816.75 | 1458.24 | 1559.7036 | -6.9579 | 89.0323 | 1188.2268 | 96.3946 | 118 | 70 | 8.8 | 2.2 | 3.5 | 5.7 | 5.7 | 0.62069 | 0.38596 | 18.8571 | 19.7444 | 18.1342 | 67.0658 | 0.2944 | NA | 7 | 78.463 | 1458.24 | 2219.36 | 2325.5284 | -4.7837 | 79.9122 | 1891.8842 | 95.8527
[11 empty] | 1998-03-02 | 18:00 | 3529.92 | 24.4444 | 100 | 70 | 8.9333 | 0 | 17.5 | 3.1 |  | 20.6 | 20.6 | 0.84951 | 0 | 17.9487 | 18.7933 | 13.6341 | 61.8326 | 0.30394 | 7.6 | 6.44 | 36.448 | 368.52 | 393.12 | 2216.5 | 2406.591 | -8.5762 | 90.7285 | 1399.8555 | 97.3963 | 100 | 80 | 9 | 10.5 | 10.1 | 20.6 | 20.6 | 0.50211 | 0.50971 | 16.1538 | 16.9139 | 5.5075 | 75.4925 | 0.22405 | 6.44 | NA | 30.739 | 393.12 | 817.74 | 769.8527 | 5.8561 | 92.1808 | 581.4864 | 94.7137 | 80 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4561 | 50.5439 | 0.30596 | NA | NA | 43.68 | 817.74 | 1457 | 1560.8376 | -7.1268 | 88.8889 | 1189.2888 | 96.3272 | 118 | 70 | 8.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.6843 | 66.5157 | 0.29684 | NA | 7 | 77.924 | 1457 | 2216.5 | 2435.6991 | -9.8894 | 80.1781 | 1946.3495 | 95.9964
[11 empty] | 1998-03-03 | 0:15 | 3535.62 | 24.4444 | 100 | 72 | 10 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | #VALUE! | #VALUE! | #VALUE! | 7.6 | 6.52 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | #VALUE! | #VALUE! | #VALUE! | 6.52 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 80 | 64 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 120 | 72 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | #VALUE! | #VALUE! | #VALUE! | NA | 7.1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-03-03 | 8:00 | 3543.45 | 24.4444 | 100 | 70 | 10 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | #VALUE! | #VALUE! | #VALUE! | 7.5 | 6.47 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | #VALUE! | #VALUE! | #VALUE! | 6.47 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 80 | 64 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | #VALUE! | #VALUE! | #VALUE! | NA | 7.1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-03-03 | 20:00 | 3555.98 | 24.4444 | 100 | 70 | 10 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.5819 | 61.6848 | 0.30815 | 7.5 | 6.39 | 34.907 | 375.16 | 387.24 | 2152.15 | 2398.9478 | -11.4675 | 90.9857 | 1393.0939 | 97.4943 | 100 | 80 | 10 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4615 | 74.5385 | 0.23124 | 6.39 | NA | 30.208 | 387.24 | 816.75 | 765.4818 | 6.2771 | 92.1992 | 576.3609 | 94.7588 | 80 | 64 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4228 | 50.5772 | 0.30575 | NA | NA | 44.94 | 816.75 | 1416.08 | 1557.6876 | -10 | 88.3948 | 1187.2188 | 96.2147 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.1413 | 66.8587 | 0.29532 | NA | 7.2 | 77.077 | 1416.08 | 2152.15 | 2366.3402 | -9.9524 | 80.0958 | 1891.2101 | 95.9245
[11 empty] | 1998-03-04 | 8:20 | 3568.5 | 24.4444 | 102 | 70 | 10 | 0 | 17.7 | 3.2 |  | 20.9 | 20.9 | 0.84689 | 0 | 18.1538 | 19.0081 | 12.8509 | 62.4825 | 0.30421 | 7.2 | 6.46 | 42.612 | 367.69 | 383.88 | 2142.14 | 2271.5186 | -6.0397 | 88.8997 | 1327.6993 | 96.7905 | 102 | 80 | 10 | 10.7 | 10.2 | 20.9 | 20.9 | 0.50866 | 0.51196 | 16.4615 | 17.2361 | 5.399 | 75.601 | 0.22799 | 6.46 | NA | 29.736 | 383.88 | 778.14 | 755.384 | 2.9244 | 92.2538 | 569.632 | 94.7798 | 80 | 64 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.9073 | 51.0927 | 0.30267 | NA | NA | 41.16 | 778.14 | 1455.76 | 1485.6408 | -2.0526 | 89.2779 | 1131.8904 | 96.3636 | 120 | 70 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 18.5302 | 66.4698 | 0.29704 | NA | 7 | 76.769 | 1455.76 | 2142.14 | 2403.8163 | -12.2156 | 80.0018 | 1929.7882 | 96.0219
[11 empty] | 1998-03-04 | 18:40 | 3578.63 | 24.4444 | 102 | 70 | 10 | 0 | 17.7 | 3.2 |  | 20.9 | 20.9 | 0.84689 | 0 | 18.1538 | 19.0081 | 12.9508 | 62.3159 | 0.30503 | 7.2 | 6.46 | 42.478 | 369.35 | 386.4 | 2130.7 | 2288.7186 | -7.4163 | 89.0067 | 1337.5593 | 96.8242 | 102 | 80 | 10 | 10.7 | 10.2 | 20.9 | 20.9 | 0.50866 | 0.51196 | 16.4615 | 17.2361 | 5.4401 | 75.5599 | 0.22811 | 6.46 | NA | 29.559 | 386.4 | 780.12 | 760.7332 | 2.4851 | 92.3502 | 573.5666 | 94.8465 | 80 | 64 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.9594 | 51.0406 | 0.30298 | NA | NA | 39.62 | 780.12 | 1457 | 1491 | -2.3336 | 89.7464 | 1135.56 | 96.511 | 120 | 70 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 18.5624 | 66.4376 | 0.29719 | NA | 7 | 75.614 | 1457 | 2130.7 | 2406.7029 | -12.9536 | 80.4312 | 1931.8514 | 96.0859
[11 empty] | 1998-03-05 | 0:15 | 3583.94 | 24.4444 | 102 | 70 | 10 | 0 | 17.7 | 3.2 |  | 20.9 | 20.9 | 0.84689 | 0 | 18.1538 | 19.0081 | 13.4288 | 61.8379 | 0.30739 | 7.1 | 6.46 | 39.865 | 366.03 | 396.48 | 1996.28 | 2369.0067 | -18.6711 | 89.9453 | 1382.7434 | 97.117 | 102 | 80 | 10 | 10.7 | 10.2 | 20.9 | 20.9 | 0.50866 | 0.51196 | 16.4615 | 17.2361 | 5.6018 | 75.3982 | 0.2286 | 6.46 | NA | 29.028 | 396.48 | 753.39 | 781.9444 | -3.7901 | 92.6786 | 589.2122 | 95.0734 | 80 | 64 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.5752 | 51.4248 | 0.30071 | NA | NA | 38.85 | 753.39 | 1469.4 | 1439.3484 | 2.0452 | 90.2013 | 1096.3692 | 96.4565 | 120 | 70 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 18.7093 | 66.2907 | 0.29785 | NA | 7 | 77.077 | 1469.4 | 1996.28 | 2426.6221 | -21.5572 | 80.5597 | 1948.011 | 96.0433
[11 empty] | 1998-03-05 | 8:30 | 3592.57 | 24.4444 | 102 | 70 | 9.6667 | 0 | 17.7 | 3.2 |  | 20.9 | 20.9 | 0.84689 | 0 | 18.1538 | 19.0081 | 11.5901 | 63.8766 | 0.29757 | 7.3 | 6.44 | 37.453 | 380.97 | 345.24 | 1899.04 | 2047.6868 | -7.8275 | 89.1516 | 1196.4634 | 96.8697 | 102 | 80 | 9.8 | 10.7 | 10.2 | 20.9 | 20.9 | 0.50866 | 0.51196 | 16.4615 | 17.2361 | 4.8297 | 76.3703 | 0.22569 | 6.44 | NA | 28.438 | 345.24 | 687.06 | 677.5715 | 1.381 | 91.7628 | 511.4058 | 94.4392 | 80 | 65 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 9.5821 | 53.1179 | 0.29113 | NA | NA | 39.62 | 687.06 | 1607.04 | 1308.6024 | 18.5706 | 88.5239 | 997.8312 | 96.0294 | 120 | 70 | 9.4 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 20.7089 | 64.8911 | 0.30427 | NA | 6.9 | 65.912 | 1607.04 | 1899.04 | 2666.5655 | -40.4165 | 80.9084 | 2136.8027 | 96.9154
[11 empty] | 1998-03-05 | 18:30 | 3602.82 | 24.4444 | 102 | 70 | 9.6333 | 0 | 17.7 | 3.2 |  | 20.9 | 20.9 | 0.84689 | 0 | 18.1538 | 19.0081 | 12.1368 | 63.2632 | 0.30046 | 7.2 | 6.38 | 38.056 | 384.29 | 360.36 | 1954.81 | 2143.104 | -9.6323 | 89.4394 | 1251.732 | 96.9597 | 102 | 80 | 9.6 | 10.7 | 10.2 | 20.9 | 20.9 | 0.50866 | 0.51196 | 16.4615 | 17.2361 | 5.0566 | 76.3434 | 0.22577 | 6.38 | NA | 28.674 | 360.36 | 704.88 | 708.3051 | -0.48591 | 92.043 | 534.3326 | 94.6337 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 9.851 | 52.349 | 0.29541 | NA | NA | 39.27 | 704.88 | 1553.72 | 1343.8656 | 13.5066 | 89.1026 | 1024.3728 | 96.1664 | 120 | 70 | 9.5 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 19.9086 | 65.5914 | 0.30102 | NA | 7 | 72.149 | 1553.72 | 1954.81 | 2572.3001 | -31.5882 | 79.9786 | 2063.01 | 96.5027
[11 empty] | 1998-03-06 | 0:15 | 3608.04 | 25.5556 | 102 | 70 | 9.7333 | 0 | 17.7 | 3.2 |  | 20.9 | 20.9 | 0.84689 | 0 | 18.1538 | 18.3939 | 13.8154 | 61.5846 | 0.29868 | 7.2 | 6.46 | 34.639 | 380.14 | 401.52 | 1856.14 | 2430.8305 | -30.9616 | 91.373 | 1416.1753 | 97.554 | 102 | 80 | 9.6 | 10.7 | 10.2 | 20.9 | 20.9 | 0.50866 | 0.51196 | 16.4615 | 16.6792 | 5.6517 | 75.7483 | 0.22019 | 6.46 | NA | 30.798 | 401.52 | 686.07 | 790.4146 | -15.209 | 92.3296 | 595.9673 | 94.8323 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.5467 | 52.6533 | 0.28421 | NA | NA | 41.02 | 686.07 | 1550 | 1305.318 | 15.7859 | 89.7838 | 995.694 | 95.8803 | 120 | 70 | 9.8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 19.7924 | 65.4076 | 0.29211 | NA | 6.9 | 77.077 | 1550 | 1856.14 | 2562.6346 | -38.0626 | 80.8037 | 2056.3173 | 96.2517
[11 empty] | 1998-03-06 | 6:45 | 3614.82 | 24.4444 | 102 | 70 | 9.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.2578 | 62.2088 | 0.30555 | 7.3 | 6.46 | 44.153 | 371.01 | 388.08 | 2250.82 | 2351.7922 | -4.486 | 88.6227 | 1369.9361 | 96.777 | 102 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4672 | 75.9328 | 0.22699 | 6.46 | NA | 30.68 | 388.08 | 846.45 | 766.7117 | 9.4203 | 92.0944 | 577.3958 | 94.6865 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.9162 | 50.2838 | 0.30754 | NA | NA | 41.3 | 846.45 | 1507.84 | 1619.394 | -7.3983 | 89.3579 | 1232.922 | 96.6502 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.4221 | 65.7779 | 0.30017 | NA | 6.9 | 74.305 | 1507.84 | 2250.82 | 2525.1874 | -12.1897 | 80.8532 | 2016.5137 | 96.3152
[11 empty] | 1998-03-06 | 19:15 | 3627.31 | 24.4444 | 100 | 70 | 9.6667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.4458 | 62.6209 | 0.30354 | 7.2 | 6.25 | 45.158 | 373.5 | 393.96 | 2039.18 | 2385.5069 | -16.9836 | 88.5374 | 1389.7335 | 96.7506 | 100 | 80 | 9.6 | 11.4 | 9.4 | 20.8 | 20.8 | 0.49394 | 0.54808 | 17.5385 | 18.3637 | 5.8252 | 74.5748 | 0.24625 | 6.25 | NA | 31.329 | 393.96 | 804.87 | 833.7465 | -3.5877 | 92.0477 | 613.8533 | 94.8963 | 80 | 64 | 9.8 | 4.1 | 5 | 9.1 | 9.1 | 0.46122 | 0.45055 | 12.6154 | 13.209 | 10.7742 | 51.4258 | 0.25686 | NA | NA | 40.74 | 804.87 | 1558.68 | 1431.4566 | 8.1623 | 89.6588 | 1118.1633 | 96.3565 | 120 | 70 | 9.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 20.0817 | 65.3183 | 0.30228 | NA | 6.9 | 76.461 | 1558.68 | 2039.18 | 2610.5774 | -28.0209 | 80.5917 | 2084.6287 | 96.3322
[11 empty] | 1998-03-07 | 8:00 | 3640.11 | 24.4444 | 100 | 70 | 9.8667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.4527 | 62.6139 | 0.30358 | 7.4 | 6.45 | 38.257 | 367.69 | 387.24 | 2245.1 | 2379.8204 | -6.0006 | 90.1206 | 1383.5302 | 97.2348 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.4561 | 74.7439 | 0.2306 | 6.45 | NA | 30.562 | 387.24 | 791.01 | 765.1068 | 3.2747 | 92.1077 | 576.1734 | 94.6957 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.0916 | 51.1084 | 0.30258 | NA | NA | 41.58 | 791.01 | 1488 | 1510.4628 | -1.5096 | 89.2625 | 1150.7364 | 96.3867 | 120 | 70 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.1053 | 65.8947 | 0.29964 | NA | 6.9 | 77.847 | 1488 | 2245.1 | 2488.7537 | -10.8527 | 79.897 | 1988.3769 | 96.0849
[11 empty] | 1998-03-07 | 19:45 | 3651.71 | 24.4444 | 100 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.063 | 61.937 | 0.30689 | 7.3 | 6.37 | 40.066 | 382.63 | 404.88 | 2176.46 | 2487.8503 | -14.3072 | 90.1042 | 1446.3651 | 97.2299 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.7187 | 74.4813 | 0.23142 | 6.37 | NA | 31.034 | 404.88 | 800.91 | 800.9347 | -0.0030807 | 92.335 | 602.9073 | 94.8526 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2339 | 50.9661 | 0.30342 | NA | NA | 41.86 | 800.91 | 1533.88 | 1529.598 | 0.27916 | 89.6611 | 1165.254 | 96.4077 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7311 | 65.4689 | 0.30158 | NA | 6.8 | 77.539 | 1533.88 | 2176.46 | 2567.4123 | -17.9628 | 80.8489 | 2050.6462 | 96.2188
[11 empty] | 1998-03-07 | 23:30 | 3655.74 | 24.4444 | 100 | 70 | 9.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 14.0292 | 60.9708 | 0.31176 | 7.3 | 6.39 | 39.262 | 381.8 | 403.2 | 2173.6 | 2481.1686 | -14.1502 | 90.2624 | 1442.1843 | 97.2776 | 100 | 80 | 9.6 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6768 | 74.7232 | 0.23067 | 6.39 | NA | 32.096 | 403.2 | 792.99 | 796.3498 | -0.42369 | 92.0397 | 599.7749 | 94.6487 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.1333 | 51.0667 | 0.30282 | NA | NA | 40.74 | 792.99 | 1537.6 | 1515.15 | 1.4601 | 89.8958 | 1154.07 | 96.4699 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 19.7763 | 65.4237 | 0.30179 | NA | 6.8 | 77.924 | 1537.6 | 2173.6 | 2573.4991 | -18.398 | 80.6736 | 2055.5495 | 96.2091
[11 empty] | 1998-03-08 | 4:00 | 3660.04 | 24.4444 | 100 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.8518 | 61.1482 | 0.31085 | 7.3 | 6.39 | 39.664 | 378.48 | 399 | 2176.46 | 2450.6926 | -12.5999 | 90.0591 | 1424.8463 | 97.2163 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6053 | 74.5947 | 0.23106 | 6.39 | NA | 32.568 | 399 | 801.9 | 787.2002 | 1.8331 | 91.8376 | 593.1001 | 94.5089 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2465 | 50.9535 | 0.3035 | NA | NA | 42 | 801.9 | 1649.2 | 1531.404 | 7.1426 | 89.4737 | 1166.652 | 96.4 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 21.2737 | 63.9263 | 0.30886 | NA | 6.8 | 79.002 | 1649.2 | 2176.46 | 2763.5341 | -26.9738 | 80.2 | 2206.367 | 96.4194
[11 empty] | 1998-03-08 | 6:25 | 3662.61 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 12.8013 | 63.1987 | 0.30077 | 7.3 | 6.4 | 39.195 | 346.94 | 371.28 | 1987.7 | 2267.3782 | -14.0704 | 89.4433 | 1319.3291 | 97.0292 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.2156 | 74.9844 | 0.22986 | 6.4 | NA | 30.326 | 371.28 | 758.34 | 732.4887 | 3.4089 | 91.832 | 551.8843 | 94.505 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.6174 | 51.5826 | 0.29979 | NA | NA | 40.95 | 758.34 | 1458.24 | 1447.0344 | 0.76843 | 88.9706 | 1102.6872 | 96.2863 | 120 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.7584 | 67.2416 | 0.29363 | NA | 6.9 | 73.689 | 1458.24 | 1987.7 | 2440.8246 | -22.7964 | 80.1527 | 1949.5323 | 96.2202
[11 empty] | 1998-03-08 | 18:00 | 3675.89 | 24.4444 | 102 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.792 | 62.208 | 0.30556 | 7.4 | 6.37 | 37.855 | 358.56 | 395.64 | 1856.14 | 2438.4769 | -31.3735 | 90.432 | 1417.0585 | 97.3286 | 102 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.5684 | 75.6316 | 0.2279 | 6.37 | NA | 31.624 | 395.64 | 801.9 | 781.2807 | 2.5713 | 92.0069 | 588.4604 | 94.626 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.2548 | 50.9452 | 0.30355 | NA | NA | 41.44 | 801.9 | 1461.96 | 1531.9416 | -4.7868 | 89.5258 | 1166.9208 | 96.4488 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.7629 | 66.4371 | 0.29719 | NA | 6.9 | 77.077 | 1461.96 | 1856.14 | 2444.7802 | -31.7131 | 80.5184 | 1953.3701 | 96.0542
[11 empty] | 1998-03-08 | 22:40 | 3678.58 | 24.4444 | 102 | 70 | 9.8 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 13.95 | 62.05 | 0.30633 | 7.4 | 6.37 | 37.118 | 356.9 | 399 | 1830.4 | 2465.2295 | -34.6826 | 90.6972 | 1432.1147 | 97.4082 | 102 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.6333 | 75.5667 | 0.22809 | 6.37 | NA | 30.739 | 399 | 813.78 | 789.1379 | 3.0281 | 92.296 | 594.0689 | 94.8257 | 80 | 64 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 11.4368 | 50.7632 | 0.30463 | NA | NA | 41.02 | 813.78 | 1469.4 | 1555.6296 | -5.8684 | 89.7193 | 1184.7048 | 96.5375 | 120 | 70 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.8502 | 66.3498 | 0.29758 | NA | 6.9 | 78.078 | 1469.4 | 1830.4 | 2456.7898 | -34.2215 | 80.4316 | 1963.0949 | 96.0227
[11 empty] | 1998-03-09 | 8:30 | 3688.68 | 24.4444 | 102 | 70 | 9.2 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 18.1538 | 19.0081 | 12.7453 | 63.588 | 0.29892 | 7.3 | 6.45 | 47.369 | 351.09 | 378 | 2082.08 | 2265.7964 | -8.8237 | 87.4685 | 1321.8982 | 96.4166 | 102 | 80 | 9.2 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 5.3048 | 76.4952 | 0.22532 | 6.45 | NA | 31.211 | 378 | 771.21 | 745.3903 | 3.3479 | 91.7431 | 561.6952 | 94.4434 | 80 | 64 | 9.4 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 10.7851 | 51.8149 | 0.29845 | NA | NA | 42.49 | 771.21 | 1381.36 | 1470.7812 | -6.4734 | 88.7593 | 1120.9956 | 96.2096 | 120 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.6584 | 68.3416 | 0.28891 | NA | 6.9 | 78.001 | 1381.36 | 2082.08 | 2306.3245 | -10.7702 | 79.3648 | 1843.8422 | 95.7696
[11 empty] | 1998-03-10 | 18:30 | 3697.08 | 24.4444 | 100 | 70 | 10.0667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 17.0256 | 17.8268 | 11.8922 | 64.4745 | 0.27649 | 7.2 | 6.4 | 50.518 | 346.11 | 366.24 | 2047.76 | 2113.2351 | -3.1974 | 86.2063 | 1239.7375 | 95.9251 | 100 | 74 | 10.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 5.0528 | 71.7472 | 0.22227 | 6.4 | NA | 31.683 | 366.24 | 807.84 | 707.6951 | 12.3966 | 91.3491 | 536.9675 | 94.0996 | 74 | 60 | 10 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.8198 | 11.2285 | 45.7715 | 0.32378 | NA | NA | 43.68 | 807.84 | 1347.88 | 1525.2147 | -13.1566 | 88.0734 | 1166.5273 | 96.2556 | 120 | 70 | 10 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 17.1288 | 67.8712 | 0.27769 | NA | 6.8 | 79.079 | 1347.88 | 2047.76 | 2236.0407 | -9.1945 | 78.4079 | 1791.9604 | 95.587
[11 empty] | 1998-03-11 | 2:00 | 3704.59 | 24.4444 | 102 | 70 | 10.3333 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 17.0256 | 17.8268 | 11.8706 | 64.396 | 0.27683 | 7.2 | 6.4 | 50.25 | 346.94 | 365.4 | 2062.06 | 2109.23 | -2.2875 | 86.2479 | 1237.315 | 95.9388 | 102 | 74 | 10.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 5.0357 | 72.7643 | 0.21917 | 6.4 | NA | 31.978 | 365.4 | 806.85 | 705.6967 | 12.5368 | 91.2485 | 535.5483 | 94.0289 | 74 | 60 | 10 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.8198 | 11.216 | 45.784 | 0.32369 | NA | NA | 43.54 | 806.85 | 1339.2 | 1523.4267 | -13.7565 | 88.0843 | 1165.1384 | 96.2631 | 120 | 70 | 10.8 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 17.0137 | 67.1863 | 0.28052 | NA | 6.8 | 78.925 | 1339.2 | 2062.06 | 2221.3925 | -7.7269 | 78.4004 | 1780.2963 | 95.5667
[11 empty] | 1998-03-11 | 18:45 | 3721.37 | 24.4444 | 98 | 70 | 9.0667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 17.0256 | 17.8268 | 13.7464 | 62.5203 | 0.28514 | 7.1 | 6.34 | 39.932 | 396.74 | 404.88 | 2415.27 | 2424.2589 | -0.37217 | 90.1373 | 1414.5695 | 97.1771 | 98 | 70 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 5.6364 | 69.3636 | 0.22991 | 6.34 | NA | 31.683 | 404.88 | 821.7 | 785.7718 | 4.3724 | 92.1747 | 595.3259 | 94.678 | 70 | 60 | 9.2 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.8198 | 11.5298 | 44.2702 | 0.33476 | NA | NA | 37.03 | 821.7 | 1554.96 | 1558.329 | -0.21666 | 90.8541 | 1190.0145 | 96.8883 | 114 | 70 | 9 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 20.0949 | 62.9051 | 0.29961 | NA | 6.9 | 66.451 | 1554.96 | 2415.27 | 2596.9163 | -7.5207 | 83.5875 | 2075.9381 | 96.799
[11 empty] | 1998-03-12 | 0:15 | 3726.7 | 24.4444 | 98 | 70 | 9.4 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 17.0256 | 17.8268 | 13.7134 | 61.62 | 0.2893 | 7.1 | 6.34 | 39.128 | 394.25 | 403.2 | 2405.26 | 2417.7317 | -0.51852 | 90.2956 | 1410.4659 | 97.2259 | 98 | 70 | 9.5 | 9.8 | 9.8 | 19.6 | 19.6 | 0.48085 | 0.5 | 15.0769 | 15.7864 | 5.5683 | 68.9317 | 0.22901 | 6.34 | NA | 31.978 | 403.2 | 826.65 | 774.422 | 6.318 | 92.0689 | 588.811 | 94.5691 | 70 | 60 | 9.2 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.8198 | 11.6129 | 44.1871 | 0.33539 | NA | NA | 36.33 | 826.65 | 1550 | 1568.5831 | -1.1989 | 90.9896 | 1197.6165 | 96.9665 | 114 | 70 | 9.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 20.2762 | 62.2238 | 0.31731 | NA | 6.9 | 66.374 | 1550 | 2405.26 | 2637.9924 | -9.676 | 83.5382 | 2093.9962 | 96.8303
[11 empty] | 1998-03-17 | 8:00 | 3761.67 | 24.4444 | 100 | 70 | 9.4 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 13.2328 | 61.9005 | 0.28973 | 7.4 | 6.49 | 41.674 | 375.99 | 391.44 | 2089.23 | 2338.4707 | -11.9298 | 89.3537 | 1364.9554 | 96.9469 | 100 | 75 | 9.5 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.4502 | 72.5498 | 0.21981 | 6.49 | NA | 29.323 | 391.44 | 735.57 | 757.2521 | -2.9477 | 92.5089 | 574.346 | 94.8945 | 75 | 60 | 9.5 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.8198 | 10.2221 | 47.7779 | 0.31018 | NA | NA | 39.9 | 735.57 | 1398.72 | 1388.648 | 0.72009 | 89.8069 | 1062.109 | 96.2433 | 118 | 70 | 9.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 18.2098 | 66.5902 | 0.29651 | NA | 7 | 66.297 | 1398.72 | 2089.23 | 2375.8302 | -13.718 | 83.0633 | 1887.2751 | 96.4872
[11 empty] | 1998-03-17 | 28:15 | 3776.89 | 24.4444 | 100 | 70 | 9.3 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.8259 | 62.3741 | 0.28753 | 7.2 | 6.46 | 40.669 | 371.01 | 379.68 | 2047.76 | 2266.8412 | -10.6986 | 89.2886 | 1323.2606 | 96.9266 | 100 | 75 | 9.5 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.2679 | 72.7321 | 0.21926 | 6.46 | NA | 29.677 | 379.68 | 778.14 | 733.2545 | 5.7683 | 92.1837 | 556.4672 | 94.6669 | 75 | 60 | 9.4 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.8198 | 10.8692 | 47.2308 | 0.31377 | NA | NA | 38.43 | 778.14 | 1433.44 | 1472.5616 | -2.7292 | 89.8783 | 1125.3508 | 96.5851 | 116 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 18.6895 | 65.3105 | 0.30232 | NA | 7 | 65.912 | 1433.44 | 2047.76 | 2436.2939 | -18.9736 | 82.6401 | 1934.8669 | 96.5935
[11 empty] | 1998-03-18 | 11:00 | 3788.68 | 24.4444 | 100 | 70 | 9.2333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.9657 | 62.301 | 0.28786 | 7.2 | 6.41 | 40.334 | 369.35 | 383.04 | 2044.9 | 2290.7701 | -12.0236 | 89.47 | 1336.905 | 96.983 | 100 | 75 | 9.5 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.3194 | 72.6806 | 0.21942 | 6.41 | NA | 29.618 | 383.04 | 737.55 | 740.0683 | -0.34145 | 92.2676 | 561.5542 | 94.7257 | 75 | 60 | 9.2 | 4.6 | 4.8 | 9.4 | 9.4 | 0.4645 | 0.48936 | 14.1538 | 14.8198 | 10.3401 | 47.9599 | 0.309 | NA | NA | 38.5 | 737.55 | 1438.4 | 1407.4729 | 2.1501 | 89.9488 | 1072.5115 | 96.4103 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 18.751 | 66.249 | 0.29803 | NA | 7 | 66.374 | 1438.4 | 2044.9 | 2444.5524 | -19.5439 | 82.6718 | 1941.4762 | 96.5813
[11 empty] | 1998-03-18 | 16:01 | 3793.88 | 24.4444 | 100 | 70 | 8.8333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 11.9862 | 63.2138 | 0.28371 | 7.3 | 6.36 | 45.225 | 346.94 | 362.04 | 1816.1 | 2125.6435 | -17.0444 | 87.5083 | 1243.8418 | 96.3641 | 100 | 74 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.0113 | 72.9887 | 0.21849 | 6.36 | NA | 29.087 | 362.04 | 703.89 | 698.3905 | 0.7813 | 91.9658 | 530.2152 | 94.5141 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.6922 | 48.3078 | 0.30678 | NA | NA | 40.04 | 703.89 | 1244.96 | 1314.632 | -5.5963 | 88.9404 | 1009.261 | 96.0327 | 118 | 70 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 16.0537 | 69.4463 | 0.28431 | NA | 6.8 | 70.301 | 1244.96 | 1816.1 | 2106.3766 | -15.9835 | 80.582 | 1675.6683 | 95.8046
[11 empty] | 1998-03-18 | 28:20 | 3800.96 | 24.4444 | 100 | 70 | 8.9333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.5682 | 62.8985 | 0.28513 | 7.2 | 6.39 | 43.282 | 336.98 | 375.48 | 1936.22 | 2224.7155 | -14.8999 | 88.4729 | 1300.0978 | 96.6709 | 100 | 74 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.2002 | 72.5998 | 0.21966 | 6.39 | NA | 29.972 | 375.48 | 724.68 | 724.5136 | 0.022963 | 92.0177 | 549.9968 | 94.5505 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 10.0039 | 47.9961 | 0.30877 | NA | NA | 39.48 | 724.68 | 1347.88 | 1355.064 | -0.53299 | 89.4855 | 1039.872 | 96.2034 | 118 | 70 | 8.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 17.4729 | 67.9271 | 0.29067 | NA | 6.9 | 69.377 | 1347.88 | 1936.22 | 2285.4489 | -18.0366 | 81.5231 | 1816.6644 | 96.1811
[11 empty] | 1998-03-19 | 8:00 | 3810.03 | 24.4444 | 100 | 70 | 9 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.6266 | 63.5734 | 0.2821 | 7.4 | 6.39 | 43.416 | 342.79 | 377.16 | 1841.84 | 2235.0016 | -21.3461 | 88.4887 | 1306.0808 | 96.6759 | 100 | 74 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.2362 | 72.5638 | 0.21977 | 6.39 | NA | 29.264 | 377.16 | 706.86 | 728.606 | -3.0764 | 92.241 | 552.883 | 94.707 | 74 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.7693 | 48.0307 | 0.30855 | NA | NA | 37.73 | 706.86 | 1368.96 | 1322.4596 | 3.3968 | 89.9963 | 1014.6598 | 96.2815 | 116 | 70 | 8.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 17.7399 | 66.6601 | 0.2962 | NA | 6.9 | 70.917 | 1368.96 | 1841.84 | 2320.8582 | -26.0076 | 81.1971 | 1844.9091 | 96.1561
[11 empty] | 1998-03-19 | 23:20 | 3824.99 | 24.4444 | 100 | 70 | 9 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.2732 | 63.9268 | 0.28054 | 7.3 | 6.46 | 42.679 | 350.26 | 367.08 | 1798.94 | 2172.9122 | -20.7885 | 88.3734 | 1269.9961 | 96.6394 | 100 | 74 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.0925 | 72.7075 | 0.21934 | 6.46 | NA | 28.733 | 367.08 | 720.72 | 708.8795 | 1.6429 | 92.1726 | 537.9798 | 94.6591 | 74 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.9522 | 47.8478 | 0.30973 | NA | NA | 39.06 | 720.72 | 1396.24 | 1347.8472 | 3.4659 | 89.3593 | 1034.2836 | 96.2235 | 116 | 70 | 8.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 18.1064 | 66.2936 | 0.29783 | NA | 6.9 | 71.379 | 1396.24 | 1798.94 | 2367.8047 | -31.6222 | 80.5549 | 1882.0224 | 96.2073
[11 empty] | 1998-03-20 | 8:00 | 3833.43 | 24.4444 | 100 | 70 | 8.8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.5362 | 64.2638 | 0.27907 | 7.4 | 6.45 | 41.607 | 356.07 | 372.96 | 1721.72 | 2217.4917 | -28.7951 | 88.8441 | 1295.2259 | 96.7877 | 100 | 75 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.1641 | 73.3359 | 0.21746 | 6.45 | NA | 29.854 | 372.96 | 705.87 | 719.5671 | -1.9405 | 91.9954 | 546.2635 | 94.5349 | 75 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.7712 | 48.5288 | 0.30538 | NA | NA | 36.61 | 705.87 | 1135.84 | 1321.5892 | -16.3535 | 90.1839 | 1013.7296 | 96.3886 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.5592 | 71.2408 | 0.27715 | NA | 6.9 | 70.532 | 1135.84 | 1721.72 | 1917.0659 | -11.346 | 81.0886 | 1526.4529 | 95.3794
[11 empty] | 1998-03-20 | 18:00 | 3843.43 | 24.4444 | 100 | 70 | 9 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.3176 | 62.6157 | 0.28642 | 7.4 | 6.36 | 42.344 | 341.96 | 367.92 | 1776.06 | 2180.2931 | -22.7601 | 88.491 | 1274.1065 | 96.6766 | 100 | 75 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.0989 | 73.2011 | 0.21786 | 6.36 | NA | 29.146 | 367.92 | 712.8 | 710.1509 | 0.37165 | 92.0782 | 539.0354 | 94.5929 | 75 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.857 | 48.443 | 0.30592 | NA | NA | 37.66 | 712.8 | 1378.88 | 1333.9288 | 3.26 | 89.7641 | 1023.3644 | 96.32 | 116 | 70 | 8.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 17.8787 | 66.5213 | 0.29681 | NA | 6.9 | 70.686 | 1378.88 | 1776.06 | 2338.2223 | -31.6522 | 80.7877 | 1858.5511 | 96.1967
[11 empty] | 1998-03-20 | 22:35 | 3848.74 | 24.4444 | 100 | 70 | 8.8 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 11.7573 | 63.9094 | 0.28062 | 7.3 | 6.41 | 42.88 | 343.62 | 361.2 | 1813.24 | 2076.0206 | -14.4923 | 88.1285 | 1218.6103 | 96.4812 | 100 | 74 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 4.9746 | 73.0254 | 0.21838 | 6.41 | NA | 29.559 | 361.2 | 710.82 | 692.841 | 2.5293 | 91.8164 | 527.0205 | 94.3913 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.8169 | 48.1831 | 0.30757 | NA | NA | 38.43 | 710.82 | 1316.88 | 1329.4188 | -0.95216 | 89.3605 | 1020.1194 | 96.2328 | 118 | 70 | 8.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 16.8902 | 68.7098 | 0.28736 | NA | 6.9 | 70.224 | 1316.88 | 1813.24 | 2201.6036 | -21.4182 | 80.5581 | 1759.2418 | 96.0083
[11 empty] | 1998-03-21 | 8:05 | 3857.66 | 24.4444 | 100 | 70 | 8.8 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 11.9124 | 63.0209 | 0.28457 | 7.4 | 6.43 | 42.88 | 344.45 | 365.4 | 1807.52 | 2102.8465 | -16.3388 | 88.2649 | 1234.1232 | 96.5255 | 100 | 75 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 5.0279 | 73.4721 | 0.21705 | 6.43 | NA | 30.208 | 365.4 | 707.85 | 700.592 | 1.0254 | 91.7329 | 532.996 | 94.3324 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.7664 | 48.7336 | 0.3041 | NA | NA | 38.92 | 707.85 | 1314.4 | 1323.2656 | -0.6745 | 89.3487 | 1015.5578 | 96.1676 | 118 | 70 | 8.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 16.8545 | 68.7455 | 0.28721 | NA | 6.8 | 70.378 | 1314.4 | 1807.52 | 2197.2543 | -21.5618 | 80.7395 | 1755.8272 | 95.9917
[11 empty] | 1998-03-21 | 18:00 | 3868.21 | 24.4444 | 100 | 70 | 8.8 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 11.7672 | 62.8328 | 0.28543 | 7.4 | 6.4 | 42.612 | 342.79 | 361.2 | 1803.23 | 2077.4644 | -15.208 | 88.2027 | 1219.3322 | 96.5053 | 100 | 74 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 4.9728 | 73.0272 | 0.21838 | 6.4 | NA | 29.677 | 361.2 | 704.88 | 692.723 | 1.7247 | 91.7838 | 526.9615 | 94.3683 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.7567 | 48.2433 | 0.30719 | NA | NA | 36.61 | 704.88 | 1349.12 | 1319.6884 | 2.1815 | 89.8643 | 1012.2842 | 96.3834 | 116 | 70 | 8.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.327 | 67.273 | 0.2935 | NA | 6.9 | 70.224 | 1349.12 | 1803.23 | 2256.7236 | -25.149 | 80.5581 | 1802.9218 | 96.105
[11 empty] | 1998-03-22 | 12:10 | 3885.74 | 24.4444 | 100 | 70 | 8.8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.3558 | 63.2442 | 0.28357 | 7.4 | 6.4 | 43.014 | 345.28 | 369.6 | 1790.36 | 2187.5954 | -22.1875 | 88.362 | 1278.5977 | 96.6358 | 100 | 74 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.1002 | 72.8998 | 0.21876 | 6.4 | NA | 30.739 | 369.6 | 707.85 | 711.9188 | -0.57481 | 91.6832 | 540.7594 | 94.3156 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.7889 | 48.2111 | 0.30739 | NA | NA | 37.38 | 707.85 | 1357.8 | 1324.6824 | 2.4391 | 89.8864 | 1016.2662 | 96.3218 | 118 | 70 | 8.4 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 17.5937 | 68.0063 | 0.29033 | NA | 6.8 | 70.455 | 1357.8 | 1790.36 | 2301.853 | -28.5693 | 80.9375 | 1829.8265 | 96.1496
[11 empty] | 1998-03-22 | 22:10 | 3895.79 | 24.4444 | 100 | 70 | 8.9333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 11.941 | 63.759 | 0.28128 | 7.4 | 6.45 | 42.947 | 340.3 | 366.24 | 1796.08 | 2107.8507 | -17.3584 | 88.2735 | 1237.0453 | 96.5283 | 100 | 75 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 5.0458 | 73.4542 | 0.21711 | 6.45 | NA | 29.854 | 366.24 | 714.78 | 702.626 | 1.7004 | 91.8485 | 534.433 | 94.4139 | 75 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.8849 | 48.4151 | 0.3061 | NA | NA | 37.73 | 714.78 | 1373.92 | 1337.666 | 2.6387 | 89.698 | 1026.223 | 96.3234 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.6672 | 67.7328 | 0.2915 | NA | 6.9 | 69.916 | 1373.92 | 1796.08 | 2299.3422 | -28.02 | 80.9098 | 1836.6311 | 96.1932
[11 empty] | 1998-03-23 | 8:00 | 3906.45 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.6043 | 63.1624 | 0.28394 | 7.4 | 6.47 | 36.448 | 365.2 | 369.6 | 1570.14 | 2224.1461 | -41.6527 | 90.1385 | 1296.8731 | 97.1895 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.1473 | 74.6527 | 0.21362 | 6.47 | NA | 27.612 | 369.6 | 666.27 | 715.0777 | -7.3255 | 92.5292 | 542.3388 | 94.9087 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.1532 | 50.6468 | 0.29261 | NA | NA | 39.34 | 666.27 | 1117.24 | 1243.0456 | -11.2604 | 89.3561 | 954.6578 | 95.8792 | 120 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.3934 | 72.8066 | 0.27119 | NA | 7 | 64.064 | 1117.24 | 1570.14 | 1889.5691 | -20.344 | 82.6667 | 1503.4045 | 95.7387
[11 empty] | 1998-03-23 | 22:00 | 3916.24 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 12.5562 | 63.6105 | 0.28194 | 7.3 | 6.48 | 39.731 | 361.88 | 379.68 | 1595.88 | 2211.0182 | -38.5454 | 89.5357 | 1295.3491 | 96.9328 | 100 | 78 | 9.2 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 5.2518 | 74.5482 | 0.21392 | 6.48 | NA | 29.559 | 379.68 | 691.02 | 729.801 | -5.6121 | 92.2148 | 554.7405 | 94.6716 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.5309 | 50.0691 | 0.29599 | NA | NA | 38.22 | 691.02 | 1081.28 | 1291.596 | -19.4507 | 89.9336 | 991.308 | 96.1445 | 120 | 70 | 7.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.6867 | 73.7133 | 0.26785 | NA | 6.9 | 71.071 | 1081.28 | 1595.88 | 1798.2025 | -12.6778 | 81.2813 | 1439.7413 | 95.0636
[11 empty] | 1998-03-24 | 22:30 | 3944.33 | 24.4444 | 100 | 70 | 9 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 11.7094 | 64.3573 | 0.27867 | 7.3 | 6.42 | 35.778 | 335.32 | 352.8 | 1495.78 | 2060.6282 | -37.7628 | 89.8588 | 1206.7141 | 97.0351 | 100 | 75 | 9.2 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 4.8114 | 73.4886 | 0.21701 | 6.42 | NA | 32.037 | 352.8 | 683.1 | 673.563 | 1.3961 | 90.9192 | 513.1815 | 93.7572 | 75 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.4786 | 48.8214 | 0.30355 | NA | NA | 33.88 | 683.1 | 1082.52 | 1280.3824 | -18.2779 | 90.3968 | 981.7412 | 96.549 | 120 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.6847 | 72.7153 | 0.27153 | NA | 6.9 | 72.457 | 1082.52 | 1495.78 | 1799.3389 | -20.2944 | 79.4623 | 1440.9295 | 94.9715
[11 empty] | 1998-03-24 | 11:00 | 3932.18 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.429 | 63.571 | 0.28211 | 7.4 | 6.39 | 37.721 | 363.54 | 366.24 | 1603.03 | 2194.9958 | -36.9279 | 89.7005 | 1280.6179 | 97.0545 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.0496 | 74.7504 | 0.21334 | 6.39 | NA | 30.739 | 366.24 | 639.54 | 705.1645 | -10.2612 | 91.6069 | 535.7022 | 94.2619 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.7813 | 51.0187 | 0.29048 | NA | NA | 38.08 | 639.54 | 1113.52 | 1192.8832 | -7.1272 | 89.6024 | 916.2116 | 95.8438 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.2331 | 73.1669 | 0.26985 | NA | 6.9 | 72.072 | 1113.52 | 1603.03 | 1877.2485 | -17.1063 | 80.3211 | 1495.3843 | 95.1804
[11 empty] | 1998-03-24 | 17:00 | 3938.69 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.7875 | 63.2125 | 0.28371 | 7.4 | 6.31 | 38.324 | 366.86 | 376.32 | 1600.17 | 2257.8311 | -41.0994 | 89.8161 | 1317.0755 | 97.0902 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.2076 | 74.5924 | 0.21379 | 6.31 | NA | 30.326 | 376.32 | 671.22 | 725.8446 | -8.1381 | 91.9414 | 551.0823 | 94.497 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.2357 | 50.3643 | 0.29425 | NA | NA | 38.64 | 671.22 | 1096.16 | 1253.1936 | -14.3258 | 89.7321 | 962.2068 | 95.9842 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.0043 | 73.3957 | 0.26901 | NA | 6.9 | 71.456 | 1096.16 | 1600.17 | 1847.6096 | -15.4633 | 81.0119 | 1471.8848 | 95.1453
[11 empty] | 1998-03-25 | 22:30 | 3947 | 24.4444 | 100 | 70 | 8.7 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 17.1282 | 17.9342 | 12.3093 | 63.8907 | 0.2807 | 7.2 | 6.42 | 40.535 | 356.9 | 373.8 | 1826.11 | 2169.1308 | -18.7842 | 89.156 | 1271.4654 | 96.8119 | 100 | 75 | 8.9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 5.1618 | 73.4382 | 0.21715 | 6.42 | NA | 29.677 | 373.8 | 721.71 | 717.923 | 0.52473 | 92.0607 | 545.8615 | 94.5633 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.9616 | 48.5384 | 0.30532 | NA | NA | 39.41 | 721.71 | 1267.28 | 1349.426 | -6.4821 | 89.4569 | 1035.568 | 96.1944 | 120 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 16.239 | 70.561 | 0.27982 | NA | 6.9 | 68.684 | 1267.28 | 1826.11 | 2117.8965 | -15.9786 | 81.6255 | 1692.5883 | 95.9421
[11 empty] | 1998-03-25 | 12:30 | 3957.68 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 13.2744 | 62.7256 | 0.28591 | 7.4 | 6.32 | 38.056 | 379.31 | 388.92 | 1640.21 | 2342.0629 | -42.7904 | 90.215 | 1365.4915 | 97.213 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.3857 | 74.4143 | 0.21431 | 6.32 | NA | 31.093 | 388.92 | 652.41 | 750.3983 | -15.0194 | 92.0053 | 569.6591 | 94.5418 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.9283 | 50.6717 | 0.29247 | NA | NA | 40.88 | 652.41 | 1082.52 | 1215.0176 | -12.2397 | 89.4888 | 933.7138 | 95.6218 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 13.8231 | 73.5769 | 0.26835 | NA | 7 | 71.071 | 1082.52 | 1640.21 | 1824.2493 | -11.2205 | 81.7261 | 1453.3846 | 95.11
[11 empty] | 1998-03-25 | 15:30 | 3960.62 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 12.9349 | 63.2651 | 0.28348 | 7.4 | 6.29 | 37.788 | 371.84 | 379.68 | 1618.76 | 2282.8788 | -41.0264 | 90.0474 | 1331.2794 | 97.1615 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.2537 | 74.5463 | 0.21393 | 6.29 | NA | 30.621 | 379.68 | 656.37 | 732.3008 | -11.5683 | 91.9351 | 555.9904 | 94.4925 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.9964 | 50.8036 | 0.29171 | NA | NA | 40.18 | 656.37 | 1088.72 | 1223.2648 | -12.3581 | 89.4174 | 939.8174 | 95.7247 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 13.8995 | 73.5005 | 0.26863 | NA | 6.9 | 71.687 | 1088.72 | 1618.76 | 1834.5442 | -13.3302 | 81.1191 | 1461.6321 | 95.0954
[11 empty] | 1998-03-26 | 12:00 | 3981.21 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 13.0457 | 63.1543 | 0.28397 | 7.4 | 6.48 | 39.061 | 366.03 | 383.88 | 1650.22 | 2303.3724 | -39.5797 | 89.8247 | 1343.6262 | 97.0929 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.3142 | 74.4858 | 0.2141 | 6.48 | NA | 30.798 | 383.88 | 644.49 | 740.5649 | -14.9071 | 91.9772 | 562.2224 | 94.5221 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.8158 | 50.9842 | 0.29067 | NA | NA | 40.67 | 644.49 | 1094.92 | 1200.0044 | -9.5975 | 89.4055 | 922.2472 | 95.5901 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 13.9863 | 73.4137 | 0.26895 | NA | 6.9 | 71.533 | 1094.92 | 1650.22 | 1845.4038 | -11.8277 | 81.3658 | 1470.1619 | 95.1343
[11 empty] | 1998-03-26 | 15:30 | 3984.64 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 13.2145 | 62.9855 | 0.28473 | 7.4 | 6.48 | 37.118 | 368.52 | 386.4 | 1644.5 | 2330.7365 | -41.7292 | 90.3939 | 1358.5682 | 97.2679 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.3522 | 74.4478 | 0.21421 | 6.48 | NA | 30.798 | 386.4 | 635.58 | 745.6306 | -17.315 | 92.0295 | 566.0153 | 94.5588 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.6816 | 51.1184 | 0.28991 | NA | NA | 40.95 | 635.58 | 1106.08 | 1182.6396 | -6.9217 | 89.4022 | 909.1098 | 95.4956 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.1441 | 73.2559 | 0.26953 | NA | 6.8 | 71.148 | 1106.08 | 1644.5 | 1865.0301 | -13.4102 | 81.587 | 1485.5551 | 95.2107
[11 empty] | 1998-03-27 | 12:00 | 4005.27 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 17.1282 | 17.9342 | 14.2278 | 61.9722 | 0.28939 | 7.3 | 6.46 | 38.056 | 385.95 | 414.12 | 1697.41 | 2507.5429 | -47.7276 | 90.8104 | 1460.8315 | 97.3949 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.7561 | 74.0439 | 0.21538 | 6.46 | NA | 31.683 | 414.12 | 652.41 | 800.4594 | -22.6927 | 92.3493 | 607.2897 | 94.7829 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.9232 | 50.8768 | 0.29129 | NA | NA | 41.23 | 652.41 | 1130.88 | 1214.6956 | -7.4115 | 90.0439 | 933.5528 | 95.5835 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.4746 | 72.9254 | 0.27075 | NA | 6.9 | 71.764 | 1130.88 | 1697.41 | 1907.5651 | -12.3809 | 82.6707 | 1519.2225 | 95.2763
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A1: Alison Gusses: Please refer to comment in column AJ prior to Base Analyses
Note on W6: S Allgeier (11/17/99): Reviewer entered formula to calculate average system permeate pressure.
Note on AJ6: Alison Gusses: MTCw may be incorrect due to third stage booster pump
Note on DU17: CDM: verified w/ lab data sheets
Note on DU23: CDM: verified w/ lab data sheets
Note on DV17: CDM: verified w/ lab data sheets
Note on DV23: CDM: verified w/ lab data sheets
Note on DW17: CDM: verified w/ lab data sheets
Note on DW23: CDM: verified w/ lab data sheets
Note on EO17: CDM: verified w/ lab data sheets
Note on EO23: CDM: verified w/ lab data sheets
Note on EP17: CDM: verified w/ lab data sheets
Note on EP23: CDM: verified w/ lab data sheets
Note on EQ17: CDM: verified w/ lab data sheets
Note on EQ23: CDM: verified w/ lab data sheets
Note on FI17: CDM: verified w/ lab data sheets
Note on FI23: CDM: verified w/ lab data sheets
Note on FI27: S Allgeier (11/17/99): Since residual was reported a "0", SDS-DBP data is invalid and reported as NR
Note on FJ17: CDM: verified w/ lab data sheets
Note on FJ23: CDM: verified w/ lab data sheets
Note on FK17: CDM: verified w/ lab data sheets
Note on FK23: CDM: verified w/ lab data sheets
Note on GC17: CDM: verified w/ lab data sheets
Note on GC23: CDM: verified w/ lab data sheets
Note on GD17: CDM: verified w/ lab data sheets
Note on GD23: CDM: verified w/ lab data sheets
Note on GE17: CDM: verified w/ lab data sheets
Note on GE23: CDM: verified w/ lab data sheets
Note on GW17: CDM: verified w/ lab data sheets
Note on GW23: CDM: verified w/ lab data sheets
Note on GX17: CDM: verified w/ lab data sheets
Note on GX23: CDM: verified w/ lab data sheets
Note on GY17: CDM: verified w/ lab data sheets
Note on GY23: CDM: verified w/ lab data sheets
Note on HQ17: CDM: verified w/ lab data sheets
Note on HQ23: CDM: verified w/ lab data sheets
Note on HR17: CDM: verified w/ lab data sheets
Note on HR23: CDM: verified w/ lab data sheets
Note on HS17: CDM: verified w/ lab data sheets
Note on HS23: CDM: verified w/ lab data sheets

## Sheet4. Weeks 31-40
FIELD-SET 4: PILOT-SCALE MEMBRANE RESULTS: WEEKS 31-40 (FILE: mempilot.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-7: System And Stage Water Quality For Week 32 | [9 empty] | Field 4-7: System And Stage Water Quality For Week 32 (continued) | [7 empty] | Field 4-8: System And Stage Water Quality For Week 34 | [9 empty] | Field 4-8: System And Stage Water Quality For Week 34 (continued) | [7 empty] | Field 4-9: System And Stage Water Quality For Week 36 | [9 empty] | Field 4-9: System And Stage Water Quality For Week 36 (continued) | [7 empty] | Field 4-10: System And Stage Water Quality For Week 38 | [9 empty] | Field 4-10: System And Stage Water Quality For Week 38 (continued) | [7 empty] | Field 4-11: System And Stage Water Quality For Week 40 | [9 empty] | Field 4-11: System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 34 | [9 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 34 (continued) | [7 empty] | Field 4-13: Membrane Cost Parameters
|  | Stage 1 and 2 -- General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment (from Performance sampling & MDWASD) |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Miami-Dade Water and Sewer Dept. | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 26 | Alkalinity (mg/L as CaCO3) | 176 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.84478 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50382 | [6 empty] | System recovery during sample collection (decimal) | 0.8458 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50202 | [6 empty] | System recovery during sample collection (decimal) | 0.8475 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5075 | [6 empty] | System recovery during sample collection (decimal) | 0.84772 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50254 | [6 empty] | System recovery during sample collection (decimal) | 0.81443 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52577 | [6 empty] | System recovery during sample collection (decimal) | 0.8458 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50202 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 4130871 | Membrane trade name | TFC-S | Temperature normalized MTCW (gfd/psi) | 0.30179 | Calcium Hardness (mg/L as CaCO3) | NA | Antiscalant Addition | King Lee Pre-treat 100 (2 mg/L dose) | Pilot Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 19.65 | HI-14 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.9 | HI-14 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.78 | HI-15 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.93 | HI-15 | [5 empty] | System feed flow rate during sample collection (gpm) | 20 | HI-16 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.15 | HI-16 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.7 | HI-17 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.9 | HI-17 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.4 | HI-18 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.2 | HI-18 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.78 | HI-15 DUP | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.93 | HI-15 DUP |  |  |  | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | 1029 | Membrane element model number | TFC 4921S |  |  | LSI | 0.14 | Sulfuric Acid Addition | pH ~ 6.75 (85 mg/L dose) | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 19.65 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.65 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.78 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.78 | [6 empty] | System influent flow rate during sample collection (gpm) | 20 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 20 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.7 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.78 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.78 |  |  |  |  | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | NA | Cartridge Filtration | 5 um exclusion size | Pilot Scale | 1998-03-28 | 0:00 | 4040.93 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 14.1578 | 62.1756 | 0.25762 | 7.4 | 6.5 | 37.386 | 363.54 | 411.6 | 1664.52 | 2494.7246 | -49.8765 | 90.9169 | 1453.1623 | 97.4273 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.719 | 74.081 | 0.21527 | 6.5 | NA | 31.624 | 411.6 | 639.54 | 795.4533 | -24.379 | 92.3168 | 603.5267 | 94.7601 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.7527 | 51.0473 | 0.29032 | NA | NA | 40.04 | 639.54 | 1164 | 1191.08 | -2.3265 | 90.2721 | 915.31 | 95.6255 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.9314 | 72.4686 | 0.27246 | NA | 6.9 | 71.456 | 1164 | 1664.52 | 1965.1989 | -18.064 | 82.6395 | 1564.5995 | 95.433 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.67 |  |  |  | 1998-03-28 | 9:00 | 4052.93 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 13.2845 | 63.0488 | 0.25405 | 7.3 | 6.48 | 37.788 | 379.31 | 388.92 | 1685.97 | 2343.5548 | -39.0034 | 90.2839 | 1366.2374 | 97.2342 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.3546 | 74.4454 | 0.21422 | 6.48 | NA | 33.158 | 388.92 | 666.27 | 748.3122 | -12.3137 | 91.4743 | 568.6161 | 94.1686 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.1215 | 50.6785 | 0.29243 | NA | NA | 41.51 | 666.27 | 1179 | 1241.0492 | -5.2629 | 89.3269 | 953.6596 | 95.6473 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 15.1228 | 72.2772 | 0.27318 | NA | 7 | 72.457 | 1179 | 1685.97 | 1990.4649 | -18.0605 | 81.3697 | 1584.7324 | 95.4278 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1998-03-29 | 18:20 | 4061.93 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 14.1796 | 62.2204 | 0.25743 | 7.4 | 6.46 | 39.329 | 371.01 | 414.12 | 1664.52 | 2500.4566 | -50.2209 | 90.503 | 1457.2883 | 97.3012 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.7632 | 74.2368 | 0.21482 | 6.46 | NA | 31.211 | 414.12 | 647.46 | 800.9362 | -23.7044 | 92.4633 | 607.5281 | 94.8626 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.8724 | 50.9276 | 0.291 | NA | NA | 39.76 | 647.46 | 1164 | 1206.544 | -3.655 | 90.3989 | 927.002 | 95.7109 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.9377 | 72.4623 | 0.27248 | NA | 6.9 | 70.994 | 1164 | 1664.52 | 1965.5377 | -18.0844 | 82.8567 | 1564.7689 | 95.463 | Parameter | Units | Cp-sys-32 | CF-sys-32 | CC-sys-32 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-32 | CI-s1-32 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-34 | CF-sys-34 | CC-sys-34 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-34 | CI-s1-34 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-36 | CF-sys-36 | CC-sys-36 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-36 | CI-s1-36 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-38 | CF-sys-38 | CC-sys-38 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-38 | CI-s1-38 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 | CF-sys-40 | CC-sys-40 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 | CI-s1-40 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 (dup) | CF-sys-40 (dup) | CC-sys-40 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 (dup) | CI-s1-40 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | BDL |  |  |  | 1998-03-31 | 0:00 | 4088.94 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 13.713 | 62.6203 | 0.25579 | 7.4 | 6.47 | 39.061 | 371.84 | 401.52 | 1641.64 | 2419.2084 | -47.3653 | 90.2717 | 1410.3642 | 97.2304 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 5.5815 | 74.2185 | 0.21487 | 6.47 | NA | 30.68 | 401.52 | 669.24 | 776.1441 | -15.974 | 92.359 | 588.832 | 94.7897 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.1771 | 50.6229 | 0.29275 | NA | NA | 40.67 | 669.24 | 1148 | 1247.5244 | -8.6694 | 89.871 | 958.3822 | 95.7564 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.717 | 72.683 | 0.27165 | NA | 6.9 | 71.148 | 1148 | 1641.64 | 1937.6915 | -18.0339 | 82.2803 | 1542.8457 | 95.3885 | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-08 | 1998-04-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-08 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-06 | 1998-05-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-06 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-20 | 1998-05-20 | 1998-05-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-20 | 1998-05-20 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-03 | 1998-06-03 | 1998-06-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-03 | 1998-06-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1998-03-31 | 11:30 | 4100.89 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 14.2254 | 62.1746 | 0.25762 | 7.3 | 6.41 | 39.798 | 383.46 | 415.8 | 1618.76 | 2508.8778 | -54.9876 | 90.4286 | 1462.3389 | 97.2785 | 100 | 76 | 9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 16.1085 | 5.822 | 73.178 | 0.22013 | 6.41 | NA | 31.624 | 415.8 | 686.07 | 811.8577 | -18.3345 | 92.3944 | 613.8289 | 94.8481 | 76 | 60 | 9.2 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.4977 | 9.3766 | 49.4234 | 0.29334 | NA | NA | 39.41 | 686.07 | 1132 | 1268.064 | -12.0198 | 90.5219 | 977.067 | 95.9665 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.4825 | 72.9175 | 0.27078 | NA | 6.9 | 72.303 | 1132 | 1618.76 | 1909.1111 | -17.9366 | 82.6111 | 1520.5556 | 95.245 | Sampling time | hh:mm | 8:15 | 8:15 | 8:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881 (May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.08 |  |  |  | 1998-03-31 | 20:00 | 4109.11 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 13.9852 | 62.4148 | 0.25663 | 7.4 | 6.45 | 40.267 | 373.5 | 409.92 | 1623.05 | 2467.655 | -52.0381 | 90.1769 | 1438.7875 | 97.2013 | 100 | 76 | 9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 16.1085 | 5.7276 | 73.2724 | 0.21984 | 6.45 | NA | 31.978 | 409.92 | 638.55 | 799.5509 | -25.2135 | 92.199 | 604.7355 | 94.7121 | 76 | 60 | 9.2 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.4977 | 8.7068 | 50.0932 | 0.28941 | NA | NA | 38.08 | 638.55 | 1135 | 1178.973 | -3.8743 | 90.7104 | 908.7615 | 95.8097 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.5277 | 72.8723 | 0.27095 | NA | 6.9 | 71.995 | 1135 | 1623.05 | 1914.537 | -17.9592 | 82.4368 | 1524.7685 | 95.2783 | Operation time | hh.hh | 4288.74 | 4288.74 | 4288.74 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4288.74 | 4288.74 | --- | --- | --- | --- | Operation time | hh.hh | 4492.84 | 4492.84 | 4492.84 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4492.84 | 4492.84 | --- | --- | --- | --- | Operation time | hh.hh | 4765.68 | 4765.68 | 4765.68 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4765.68 | 4765.68 | --- | --- | --- | --- | Operation time | hh.hh | 5102.3 | 5102.3 | 5102.3 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5102.3 | 5102.3 | --- | --- | --- | --- | Operation time | hh.hh | 5435.24 | 5435.24 | 5435.24 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5435.24 | 5435.24 | --- | --- | --- | --- | Operation time | hh.hh | 4492.84 | 4492.84 | 4492.84 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4492.84 | 4492.84 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 130
E-Mail Address (optional) |  | Stage 1 and 2 -- Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 9.16 |  |  |  | 1998-04-01 | 0:15 | 4113.55 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 13.4894 | 62.9106 | 0.25461 | 7.4 | 6.48 | 39.932 | 363.54 | 396.48 | 1633.06 | 2381.2639 | -45.8161 | 89.9284 | 1388.8719 | 97.1249 | 100 | 76 | 9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 16.1085 | 5.5355 | 73.4645 | 0.21927 | 6.48 | NA | 31.211 | 396.48 | 676.17 | 773.046 | -14.3272 | 92.128 | 584.763 | 94.6626 | 76 | 60 | 9.2 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.4977 | 9.2219 | 49.5781 | 0.29242 | NA | NA | 40.18 | 676.17 | 1142 | 1248.561 | -9.3311 | 89.8658 | 962.3655 | 95.8249 | 120 | 70 | 7.6 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.6308 | 72.7692 | 0.27133 | NA | 6.9 | 71.456 | 1142 | 1633.06 | 1927.0656 | -18.0034 | 81.9774 | 1534.5328 | 95.3435 | pH | --- | 5.62 | 6.42 | 7.03 | --- | --- | --- | --- | --- | pH | --- | 5.82 | 6.42 | --- | --- | --- | --- | pH | --- | 5.67 | 6.53 | 7.13 | --- | --- | --- | --- | --- | pH | --- | 5.85 | 6.53 | --- | --- | --- | --- | pH | --- | 5.85 | 6.66 | 7.26 | --- | --- | --- | --- | --- | pH | --- | 5.96 | 6.66 | --- | --- | --- | --- | pH | --- | 5.86 | 6.76 | 7.35 | --- | --- | --- | --- | --- | pH | --- | 6.09 | 6.76 | --- | --- | --- | --- | pH | --- | 5.82 | 6.72 | 7.16 | --- | --- | --- | --- | --- | pH | --- | 6.01 | 6.72 | --- | --- | --- | --- | pH | --- | 5.69 | 6.54 | 7.13 | --- | --- | --- | --- | --- | pH | --- | 5.84 | 6.54 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | ~20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.8125 | Calcium (mg/L) | 56 |  |  |  | 1998-04-01 | 7:10 | 4120.43 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 10.7559 | 65.6441 | 0.24401 | 7.4 | 6.47 | 36.582 | 307.1 | 320.88 | 1521.52 | 1903.4722 | -25.1033 | 88.5995 | 1112.1761 | 96.7108 | 100 | 75 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 4.406 | 74.294 | 0.21465 | 6.47 | NA | 28.143 | 320.88 | 661.32 | 616.6041 | 6.7616 | 91.2294 | 468.7421 | 93.9961 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.0768 | 49.4232 | 0.29986 | NA | NA | 39.62 | 661.32 | 1064 | 1233.284 | -15.9102 | 87.6527 | 947.302 | 95.8176 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 13.609 | 72.391 | 0.27275 | NA | 6.9 | 68.222 | 1064 | 1521.52 | 1794.2372 | -17.924 | 78.7391 | 1429.1186 | 95.2263 | Temperature | oC | 25.7 | 24.4 | 25.2 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.4 | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.4 | 24.7 | --- | --- | --- | --- | --- | Temperature | oC | 23.1 | 23.4 | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 23.6 | --- | --- | --- | --- | Temperature | oC | NA | NA | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | NA | --- | --- | --- | --- | Temperature | oC | 26.4 | 26.9 | 27 | --- | --- | --- | --- | --- | Temperature | oC | 26.5 | 26.9 | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.4 | 24.7 | --- | --- | --- | --- | --- | Temperature | oC | 23.1 | 23.4 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 67%
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.875 | Barium (mg/L) | < 0.05 |  |  |  | 1998-04-02 | 0:01 | 4137.1 | 24.4444 | 100 | 70 | 8.6667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 16.0175 | 15.8475 | 60.4858 | 0.26481 | 7.36 | 6.43 | 63.181 | 493.02 | 492.24 | 2808.52 | 2803.6224 | 0.17439 | 87.1646 | 1647.9312 | 96.166 | 100 | 75 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 6.8066 | 71.6934 | 0.22244 | 6.43 | NA | 38.468 | 492.24 | 1055.34 | 946.012 | 10.3595 | 92.1851 | 719.126 | 94.6507 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 13.5704 | 44.9296 | 0.32985 | NA | NA | 125.86 | 1055.34 | 1964 | 1910.4616 | 2.726 | 74.4312 | 1482.9008 | 91.5126 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 25.0943 | 61.9057 | 0.31894 | NA | 7.6 | 111.804 | 1964 | 2808.52 | 3278.4617 | -16.7327 | 77.2867 | 2621.2308 | 95.7347 | Alkalinity | mg/L as CaCO3 | 16 | 109 | 561 | 615.1639 | -9.6549 | 85.3211 | 362.082 | 95.5811 | Alkalinity | mg/L as CaCO3 | 16 | 109 | 203.4308 | 85.3211 | 156.2154 | 89.7577 | Alkalinity | mg/L as CaCO3 | 16 | 117 | 654 | 671.0098 | -2.6009 | 86.3248 | 394.0049 | 95.9391 | Alkalinity | mg/L as CaCO3 | 15 | 117 | 219.8284 | 87.1795 | 168.4142 | 91.0934 | Alkalinity | mg/L as CaCO3 | 18 | 142 | 748 | 831.1148 | -11.1116 | 87.3239 | 486.5574 | 96.3005 | Alkalinity | mg/L as CaCO3 | 17 | 142 | 270.8071 | 88.0282 | 206.4036 | 91.7637 | Alkalinity | mg/L as CaCO3 | 16 | 142 | 793 | 843.4 | -6.3556 | 88.7324 | 492.7 | 96.7526 | Alkalinity | mg/L as CaCO3 | 15 | 142 | 270.2959 | 89.4366 | 206.148 | 92.7237 | Alkalinity | mg/L as CaCO3 | 17 | 138 | 629 | 669.0556 | -6.3681 | 87.6812 | 403.5278 | 95.7872 | Alkalinity | mg/L as CaCO3 | 17 | 138 | 272.1522 | 87.6812 | 205.0761 | 91.7104 | Alkalinity | mg/L as CaCO3 | 16 | 117 | 650 | 671.0098 | -3.2323 | 86.3248 | 394.0049 | 95.9391 | Alkalinity | mg/L as CaCO3 | 15 | 117 | 219.8284 | 87.1795 | 168.4142 | 91.0934 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | Strontium (mg/L) | 0.49 |  |  |  | 1998-04-02 | 7:05 | 4144.48 | 24.4444 | 100 | 70 | 8.6333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 16.0175 | 11.7354 | 64.6312 | 0.24783 | 7.3 | 6.46 | 35.912 | 334.49 | 353.64 | 1492.92 | 2065.2715 | -38.3377 | 89.845 | 1209.4557 | 97.0307 | 100 | 75 | 8.9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 4.8745 | 73.7255 | 0.21631 | 6.46 | NA | 28.674 | 353.64 | 663.3 | 678.606 | -2.3076 | 91.8918 | 516.123 | 94.4443 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.1027 | 49.3973 | 0.30001 | NA | NA | 39.83 | 663.3 | 1044 | 1236.8924 | -18.4763 | 88.7371 | 950.0962 | 95.8078 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.2505 | 73.7495 | 0.26772 | NA | 6.8 | 65.989 | 1044 | 1492.92 | 1738.0723 | -16.421 | 81.3401 | 1391.0362 | 95.2561 | Total dissolved solids | mg/L | 35 | 333 | 1400 | 1954.9016 | -39.6358 | 89.4895 | 1143.9508 | 96.9404 | Total dissolved solids | mg/L | 33 | 333 | 637.6154 | 90.0901 | 485.3077 | 93.2002 | Total dissolved solids | mg/L | 35 | 331 | 1422 | 1954.6328 | -37.4566 | 89.426 | 1142.8164 | 96.9374 | Total dissolved solids | mg/L | 33 | 331 | 631.4203 | 90.0302 | 481.2102 | 93.1423 | Total dissolved solids | mg/L | 37 | 331 | 1392 | 1964.8689 | -41.1544 | 88.8218 | 1147.9344 | 96.7768 | Total dissolved solids | mg/L | 34 | 331 | 637.0457 | 89.7281 | 484.0228 | 92.9755 | Total dissolved solids | mg/L | 36 | 311 | 1367 | 1841.8333 | -34.7354 | 88.4244 | 1076.4167 | 96.6556 | Total dissolved solids | mg/L | 32 | 311 | 592.8469 | 89.7106 | 451.9235 | 92.9192 | Total dissolved solids | mg/L | 38 | 337 | 1306 | 1649.2778 | -26.2847 | 88.724 | 993.1389 | 96.1737 | Total dissolved solids | mg/L | 37 | 337 | 669.6087 | 89.0208 | 503.3043 | 92.6486 | Total dissolved solids | mg/L | 37 | 329 | 1419 | 1930.6918 | -36.06 | 88.7538 | 1129.8459 | 96.7252 | Total dissolved solids | mg/L | 33 | 329 | 627.4041 | 89.9696 | 478.202 | 93.0992 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | Reactive silica (mg/L as SiO2) | 8.41 |  |  |  | 1998-04-02 | 20:40 | 4157.73 | 24.4444 | 100 | 70 | 8.6333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 16.0175 | 11.7158 | 64.6509 | 0.24775 | 7.3 | 6.47 | 49.044 | 354.41 | 366.24 | 1960.53 | 2075.0055 | -5.839 | 86.6088 | 1220.6228 | 95.9821 | 100 | 76 | 8.9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 5.0299 | 74.0701 | 0.2153 | 6.47 | NA | 30.916 | 366.24 | 858.33 | 701.564 | 18.2641 | 91.5585 | 533.902 | 94.2094 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 11.4115 | 47.5885 | 0.31142 | NA | NA | 76.72 | 858.33 | 1371 | 1577.4112 | -15.0555 | 79.052 | 1217.8706 | 93.7005 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 17.5483 | 69.4517 | 0.28429 | NA | 6.9 | 75.768 | 1371 | 1960.53 | 2290.1969 | -16.8152 | 79.3119 | 1830.5985 | 95.861 | Total hardness | mg/L as CaCO3 | 13 | 190 | 1154 | 1153.3443 | 0.056823 | 93.1579 | 671.6721 | 98.0645 | Total hardness | mg/L as CaCO3 | 11 | 190 | 371.7538 | 94.2105 | 280.8769 | 96.0837 | Total hardness | mg/L as CaCO3 | 10 | 192 | 1119 | 1190.3148 | -6.3731 | 94.7917 | 691.1574 | 98.5532 | Total hardness | mg/L as CaCO3 | 10 | 192 | 375.4782 | 94.7917 | 283.7391 | 96.4756 | Total hardness | mg/L as CaCO3 | 11 | 197 | 1135 | 1230.6721 | -8.4293 | 94.4162 | 713.8361 | 98.459 | Total hardness | mg/L as CaCO3 | 11 | 197 | 388.665 | 94.4162 | 292.8325 | 96.2436 | Total hardness | mg/L as CaCO3 | 11 | 197 | 1081 | 1232.4 | -14.0056 | 94.4162 | 714.7 | 98.4609 | Total hardness | mg/L as CaCO3 | 14 | 197 | 381.8673 | 92.8934 | 289.4337 | 95.163 | Total hardness | mg/L as CaCO3 | 13 | 200 | 974 | 1020.7222 | -4.7969 | 93.5 | 610.3611 | 97.8701 | Total hardness | mg/L as CaCO3 | 13 | 200 | 407.3261 | 93.5 | 303.663 | 95.7189 | Total hardness | mg/L as CaCO3 | 11 | 191 | 1161 | 1178.3443 | -1.4939 | 94.2408 | 684.6721 | 98.3934 | Total hardness | mg/L as CaCO3 | 11 | 191 | 372.4619 | 94.2408 | 281.731 | 96.0956 | Natural Gas Rate ($/ft3) | 0.2714¢/therm
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.293 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | Turbidity (ntu) | 0.5 |  |  |  | 1998-04-03 | 0:05 | 4160.67 | 24.4444 | 100 | 70 | 8.6333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 16.0175 | 12.2126 | 64.1541 | 0.24967 | 7.42 | 6.5 | 52.394 | 371.84 | 383.04 | 2042.04 | 2164.262 | -5.9853 | 86.3215 | 1273.651 | 95.8863 | 100 | 75 | 8.9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 5.2296 | 73.3704 | 0.21736 | 6.5 | NA | 34.397 | 383.04 | 845.46 | 731.683 | 13.4574 | 91.02 | 557.3615 | 93.8286 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 11.1643 | 47.3357 | 0.31308 | NA | NA | 80.78 | 845.46 | 1428 | 1548.9656 | -8.471 | 78.9108 | 1197.2128 | 93.2527 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 18.3018 | 68.6982 | 0.28741 | NA | 6.8 | 77.154 | 1428 | 2042.04 | 2386.6649 | -16.8765 | 79.8575 | 1907.3325 | 95.9549 | Calcium hardness | mg/L as CaCO3 | 9 | 183 | 1086 | 1130.0164 | -4.0531 | 95.082 | 656.5082 | 98.6291 | Calcium hardness | mg/L as CaCO3 | 10 | 183 | 358.6615 | 94.5355 | 270.8308 | 96.3077 | Calcium hardness | mg/L as CaCO3 | 8 | 179 | 1079 | 1116.977 | -3.5197 | 95.5307 | 647.9885 | 98.7654 | Calcium hardness | mg/L as CaCO3 | 9 | 179 | 350.3807 | 94.9721 | 264.6904 | 96.5998 | Calcium hardness | mg/L as CaCO3 | 10 | 184 | 980 | 1150.9836 | -17.4473 | 94.5652 | 667.4918 | 98.5019 | Calcium hardness | mg/L as CaCO3 | 10 | 184 | 363.2995 | 94.5652 | 273.6497 | 96.3457 | Calcium hardness | mg/L as CaCO3 | 10 | 184 | 980 | 1152.6 | -17.6122 | 94.5652 | 668.3 | 98.5037 | Calcium hardness | mg/L as CaCO3 | 11 | 184 | 358.7653 | 94.0217 | 271.3827 | 95.9467 | Calcium hardness | mg/L as CaCO3 | 12 | 188 | 903 | 960.4444 | -6.3615 | 93.617 | 574.2222 | 97.9102 | Calcium hardness | mg/L as CaCO3 | 11 | 188 | 384.2391 | 94.1489 | 286.1196 | 96.1555 | Calcium hardness | mg/L as CaCO3 | 9 | 178 | 1019 | 1105.0066 | -8.4403 | 94.9438 | 641.5033 | 98.597 | Calcium hardness | mg/L as CaCO3 | 10 | 178 | 347.3645 | 94.382 | 262.6822 | 96.1931 | Current Process Water Rate ($/1000 gal) | 0.21*
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 16.375 | SDI | 4.67 |  |  |  | 1998-04-03 | 7:00 | 4167.98 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 16.0175 | 11.3808 | 64.8858 | 0.24686 | 7.3 | 6.56 | 38.793 | 335.32 | 346.92 | 1502.93 | 2006.83 | -33.5278 | 88.8179 | 1176.875 | 96.7037 | 100 | 75 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 4.7675 | 73.7325 | 0.21629 | 6.56 | NA | 29.087 | 346.92 | 655.38 | 664.753 | -1.4302 | 91.6156 | 505.8365 | 94.2497 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.984 | 49.516 | 0.29929 | NA | NA | 40.04 | 655.38 | 1051 | 1221.4928 | -16.222 | 88.4584 | 938.4364 | 95.7333 | 120 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.3411 | 73.4589 | 0.26878 | NA | 7 | 66.297 | 1051 | 1502.93 | 1749.8215 | -16.4273 | 80.8898 | 1400.4107 | 95.2659 | Turbidity | ntu | BMRL | 0.04 | 29.53 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.03 | 0.04 | 0.050154 | 25 | 0.045077 | 33.4471 | Turbidity | ntu | 0.01 | 0.08 | 40 | 0.46397 | 98.8401 | 87.5 | 0.27198 | 96.3233 | Turbidity | ntu | 0.03 | 0.08 | 0.13041 | 62.5 | 0.1052 | 71.4837 | Turbidity | ntu | 0.03 | 0.05 | 38 | 0.16115 | 99.5759 | 40 | 0.10557 | 71.5839 | Turbidity | ntu | 0.01 | 0.05 | 0.091218 | 80 | 0.070609 | 85.8375 | Turbidity | ntu | 0.02 | 0.1 | 34 | 0.54533 | 98.3961 | 80 | 0.32267 | 93.8017 | Turbidity | ntu | 0.03 | 0.1 | 0.17071 | 70 | 0.13536 | 77.8364 | Turbidity | ntu | 0.11 | 0.09 | 33 | 0.0022222 | 99.9933 | -22.2222 | 0.046111 | -138.5542 | Turbidity | ntu | 0.03 | 0.09 | 0.15652 | 66.6667 | 0.12326 | 75.6614 | Turbidity | ntu | 0.01 | 0.07 | 40 | 0.39911 | 99.0022 | 85.7143 | 0.23456 | 95.7367 | Turbidity | ntu | 0.03 | 0.07 | 0.11032 | 57.1429 | 0.090162 | 66.7267 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | Feed flow rate to system, QF-sys (gpm) | 19.2647 | MFI | NA |  |  |  | 1998-04-03 | 20:45 | 4181.85 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 12.204 | 64.0627 | 0.25003 | 7.3 | 6.43 | 37.788 | 345.28 | 360.36 | 1611.61 | 2156.0108 | -33.7799 | 89.5138 | 1258.1854 | 96.9966 | 100 | 75 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 4.9469 | 73.5531 | 0.21682 | 6.43 | NA | 31.683 | 360.36 | 730.62 | 692.3908 | 5.2324 | 91.208 | 526.3754 | 93.9809 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 10.0549 | 48.4451 | 0.30591 | NA | NA | 41.93 | 730.62 | 1127 | 1364.2148 | -21.0483 | 88.3644 | 1047.4174 | 95.9968 | 120 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.4216 | 72.3784 | 0.27279 | NA | 7 | 71.764 | 1127 | 1611.61 | 1900.8397 | -17.9466 | 80.0855 | 1513.9199 | 95.2597 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.56 | 5.53 | 10.5765 | 89.8734 | 8.0532 | 93.0463 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.22 | 5.38 | 10.5819 | 95.9108 | 7.981 | 97.2434 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.46 | 5.42 | 10.5311 | 91.5129 | 7.9755 | 94.2324 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.27 | 5.42 | 10.6226 | 95.0185 | 8.0213 | 96.634 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.17 | 5.81 | 12.063 | 97.074 | 8.9365 | 98.0977 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.22 | 5.74 | 11.3048 | 96.1672 | 8.5224 | 97.4186
|  | Minimum flow rate to the element, QI, min (gpm) | 6.5 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.8897 | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-04-03 | 23:50 | 4184.7 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 12.0312 | 64.2354 | 0.24936 | 7.4 | 6.47 | 38.994 | 348.6 | 357 | 1615.9 | 2127.2334 | -31.6439 | 89.0773 | 1242.1167 | 96.8607 | 100 | 75 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.9474 | 4.8937 | 73.6063 | 0.21666 | 6.47 | NA | 31.86 | 357 | 732.6 | 685.4578 | 6.4349 | 91.0756 | 521.2289 | 93.8875 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 10.1022 | 48.3978 | 0.30621 | NA | NA | 40.67 | 732.6 | 1130 | 1369.1756 | -21.166 | 88.6078 | 1050.8878 | 96.1299 | 120 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.4531 | 72.3469 | 0.27291 | NA | 7 | 72.457 | 1130 | 1615.9 | 1905.5315 | -17.9239 | 79.7039 | 1517.7658 | 95.2261 | Total organic carbon | mg/L | 0.52 | 5.53 | 35.25 | 32.7975 | 6.9573 | 90.5967 | 19.1638 | 97.2865 | UV254 | cm-1 | BMRL | 0.208 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.32 | 5.38 | 36.7 | 33.1353 | 9.713 | 94.052 | 19.2577 | 98.3383 | UV254 | cm-1 | 0.002 | 0.224 | 0.4478 | 99.1071 | 0.3359 | 99.4046 | Total organic carbon | mg/L | 0.38 | 5.42 | 30.2 | 33.4292 | -10.6927 | 92.9889 | 19.4246 | 98.0437 | UV254 | cm-1 | 0.002 | 0.223 | 0.45073 | 99.1031 | 0.33687 | 99.4063 | Total organic carbon | mg/L | 0.39 | 5.42 | 30.25 | 33.4203 | -10.4804 | 92.8044 | 19.4202 | 97.9918 | UV254 | cm-1 | 0.002 | 0.227 | 0.4543 | 99.1189 | 0.34065 | 99.4129 | Total organic carbon | mg/L | 0.17 | 5.81 | 29.45 | 30.5633 | -3.7804 | 97.074 | 18.1867 | 99.0652 | UV254 | cm-1 | 0.002 | 0.238 | 0.49965 | 99.1597 | 0.36883 | 99.4577 | Total organic carbon | mg/L | 0.18 | 5.74 | 34.6 | 36.238 | -4.734 | 96.8641 | 20.989 | 99.1424 | UV254 | cm-1 | 0.005 | 0.228 | 0.45281 | 97.807 | 0.34041 | 98.5312
Plant Name | Hialeah Water Treatment | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  | TOC (mg/L) | 11.35 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-04-04 | 7:40 | 4192.7 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 11.8138 | 64.4528 | 0.24852 | 7.3 | 6.49 | 38.86 | 343.62 | 351.12 | 1527.24 | 2089.3673 | -36.8067 | 88.9326 | 1220.2437 | 96.8154 | 100 | 75 | 9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 16.1085 | 4.8633 | 73.6367 | 0.21876 | 6.49 | NA | 30.208 | 351.12 | 671.22 | 681.9571 | -1.5996 | 91.3967 | 516.5386 | 94.1518 | 75 | 60 | 9 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.4977 | 9.1541 | 49.3459 | 0.2938 | NA | NA | 39.9 | 671.22 | 1068 | 1239.408 | -16.0494 | 88.6364 | 955.314 | 95.8234 | 120 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 13.6763 | 73.1237 | 0.27001 | NA | 6.9 | 67.298 | 1068 | 1527.24 | 1801.8481 | -17.9807 | 80.8333 | 1434.9241 | 95.31 | UV254 | cm-1 | 0.002 | 0.208 | 1.164 | 1.3292 | -14.1907 | 99.0385 | 0.76859 | 99.7398 | SUVA | L/(mg*m) | #VALUE! | 3.7613 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.224 | 1.224 | 1.4472 | -18.2361 | 99.5536 | 0.8356 | 99.8803 | SUVA | L/(mg*m) | 0.90909 | 4.1636 | --- | --- | --- | --- | UV254 | cm-1 | 0.002 | 0.223 | 1.116 | 1.4512 | -30.0341 | 99.1031 | 0.83709 | 99.7611 | SUVA | L/(mg*m) | 0.43478 | 4.1144 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.227 | 1.266 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.74074 | 4.1882 | --- | --- | --- | --- | UV254 | cm-1 | 0.002 | 0.238 | 1.096 | 1.2738 | -16.2206 | 99.1597 | 0.75589 | 99.7354 | SUVA | L/(mg*m) | 1.1765 | 4.0964 | --- | --- | --- | --- | UV254 | cm-1 | 0.004 | 0.228 | 1.286 | 1.4567 | -13.2733 | 98.2456 | 0.84235 | 99.5251 | SUVA | L/(mg*m) | 2.2727 | 3.9721 | --- | --- | --- | ---
Treatment Plant Category | Softening | Feed spacer thickness, T (ft) | 0.00258 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-04-04 | 22:30 | 4207.73 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.412 | 64.9213 | 0.23875 | 7.4 | 6.44 | 37.721 | 322.04 | 339.36 | 1495.78 | 2018.4838 | -34.9452 | 88.8847 | 1178.9219 | 96.8004 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6433 | 75.3567 | 0.20479 | 6.44 | NA | 30.857 | 339.36 | 659.34 | 651.011 | 1.2632 | 90.9073 | 495.1855 | 93.7686 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.0459 | 50.9541 | 0.28145 | NA | NA | 39.76 | 659.34 | 1046 | 1229.3536 | -17.529 | 88.2838 | 944.3468 | 95.7897 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.3556 | 73.6444 | 0.25944 | NA | 6.9 | 68.761 | 1046 | 1495.78 | 1762.6419 | -17.841 | 79.738 | 1404.321 | 95.1036 | SUVA | L/(mg*m) | 0.38462 | 3.7613 | 3.3021 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.3125 | 4.1636 | 3.3351 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.52632 | 4.1144 | 3.6954 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 4.1882 | 4.1851 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.1765 | 4.0964 | 3.7216 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 2.2222 | 3.9721 | 3.7168 | --- | --- | --- | --- | ---
Process Train Name | Hialeah WTP | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 11.1397 | [5 empty] | 1998-04-05 | 10:00 | 4218.04 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 10.6664 | 65.7336 | 0.24367 | 7.3 | 6.45 | 54.069 | 330.34 | 336 | 1440.01 | 1905.4159 | -32.3196 | 83.908 | 1120.7079 | 95.1755 | 100 | 75 | 8.8 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 16.1085 | 4.6583 | 74.0417 | 0.21756 | 6.45 | NA | 28.615 | 336 | 660.33 | 652.8918 | 1.1264 | 91.4836 | 494.4459 | 94.2127 | 75 | 60 | 9 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.4977 | 8.9932 | 49.5068 | 0.29284 | NA | NA | 40.11 | 660.33 | 1007 | 1218.528 | -21.0058 | 88.0625 | 939.429 | 95.7304 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 12.8731 | 74.1269 | 0.26636 | NA | 6.8 | 65.065 | 1007 | 1440.01 | 1697.7523 | -17.8986 | 80.6354 | 1352.3762 | 95.1888 | Bromide | mg/L | 10 | 73 | --- | 415.8852 | --- | 86.3014 | 244.4426 | 95.9091 | [8 empty] | Bromide | mg/L | 18 | 74 | --- | 381.1738 | --- | 75.6757 | 227.5869 | 92.0909 | [8 empty] | Bromide | mg/L | 28 | 73 | --- | 323.082 | --- | 61.6438 | 198.041 | 85.8615 | [8 empty] | Bromide | mg/L | 15 | 78 | --- | 428.7 | --- | 80.7692 | 253.35 | 94.0793 | [8 empty] | Bromide | mg/L | 6 | 34 | --- | 156.8889 | --- | 82.3529 | 95.4444 | 93.7136 | [8 empty] | Bromide | mg/L | 19 | 75 | --- | 382.1738 | --- | 74.6667 | 228.5869 | 91.6881
ICR Treatment Plant Identification Number | 302 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4522 | [5 empty] | 1998-04-05 | 22:55 | 4230.89 | 24.4444 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 16.0175 | 10.9715 | 65.4285 | 0.24481 | 7.4 | 6.47 | 54.404 | 322.04 | 344.4 | 1444.3 | 1958.7111 | -35.6166 | 84.2033 | 1151.5555 | 95.2756 | 100 | 75 | 8.8 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 16.1085 | 4.7802 | 73.9198 | 0.21792 | 6.47 | NA | 28.969 | 344.4 | 638.55 | 669.5866 | -4.8605 | 91.5886 | 506.9933 | 94.2861 | 75 | 60 | 9 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.4977 | 8.6652 | 49.8348 | 0.29091 | NA | NA | 40.95 | 638.55 | 1010 | 1176.39 | -16.4743 | 88.1098 | 907.47 | 95.4875 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 12.8962 | 74.1038 | 0.26644 | NA | 6.8 | 66.374 | 1010 | 1444.3 | 1701.9924 | -17.842 | 80.7276 | 1355.9962 | 95.1051 | SDS-Cl2 dose | mg/L | 3.5 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 12.3 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.2 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4130871 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 0.57721 | [5 empty] | 1998-04-06 | 6:40 | 4238.67 | 24.4444 | 100 | 70 | 8.7333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 16.0175 | 11.2739 | 64.9928 | 0.24645 | 7.3 | 6.49 | 36.649 | 332 | 341.88 | 1431.43 | 1986.1889 | -38.7556 | 89.2802 | 1164.0345 | 96.8516 | 100 | 75 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.9474 | 4.6848 | 73.8152 | 0.21605 | 6.49 | NA | 29.559 | 341.88 | 656.37 | 654.201 | 0.33045 | 91.354 | 498.0405 | 94.0649 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.0158 | 49.4842 | 0.29949 | NA | NA | 38.85 | 656.37 | 1001 | 1224.4884 | -22.3265 | 88.6364 | 940.4292 | 95.8689 | 120 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 12.6825 | 74.1175 | 0.26639 | NA | 7 | 64.911 | 1001 | 1431.43 | 1665.3212 | -16.3397 | 81.0135 | 1333.1606 | 95.131 | SDS-Free Cl2 residual | mg/L | 0.7 | 0.82 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47179 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.77 | 0.72 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46701 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.2 | 1.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46701 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.05 | 1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46939 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.74 | 0.86 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52174 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.83 | 0.81 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46701
Historical Minimum Water Temperature (oC) | 23 | Stage 1 and 2 -- Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-04-06 | 12:00 | 4251.8 | 25.5556 | 100 | 70 | 8.8667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.1233 | 65.01 | 0.23842 | 7.4 | 6.42 | 33.165 | 307.1 | 334.32 | 1424.28 | 1956.6711 | -37.3797 | 90.0799 | 1145.4956 | 97.1047 | 100 | 78 | 8.8 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.5741 | 75.6259 | 0.20406 | 6.42 | NA | 29.382 | 334.32 | 620.73 | 639.258 | -2.9849 | 91.2114 | 486.789 | 93.9641 | 78 | 60 | 8.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.4975 | 51.7025 | 0.27738 | NA | NA | 38.71 | 620.73 | 996 | 1156.1884 | -16.0832 | 88.4213 | 888.4592 | 95.643 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 12.6669 | 72.3331 | 0.26415 | NA | 6.9 | 61.061 | 996 | 1424.28 | 1659.5051 | -16.5154 | 81.7358 | 1327.7525 | 95.4012 | SDS-Cl2 demand | mg/L | 2.8 | 12.18 | --- | 63.2318 | --- | 77.0115 | 37.7059 | 92.5741 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.73 | 12.28 | --- | 64.6641 | --- | 77.7687 | 38.472 | 92.9039 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.3 | 11.1 | --- | 60.0049 | --- | 79.2793 | 35.5525 | 93.5307 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.45 | 11.3 | --- | 60.565 | --- | 78.3186 | 35.9325 | 93.1817 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.46 | 11.64 | --- | 51.93 | --- | 78.866 | 31.785 | 92.2605 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.8 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.67 | 12.19 | --- | 64.4095 | --- | 78.0968 | 38.2998 | 93.0287 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6
Historical Average Water Temperature (oC) | 26 | Design cross-flow velocity (fps) | 0.75 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-04-07 | 3:50 | 4259.82 | 25.5556 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.1595 | 65.2405 | 0.23758 | 7.4 | 6.5 | 30.954 | 298.8 | 325.92 | 1408.55 | 1967.8974 | -39.7109 | 90.5026 | 1146.9087 | 97.3011 | 100 | 78 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.4605 | 75.7395 | 0.20375 | 6.5 | NA | 29.559 | 325.92 | 623.7 | 625.3051 | -0.25735 | 90.9306 | 475.6125 | 93.7851 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.5511 | 51.4489 | 0.27874 | NA | NA | 38.01 | 623.7 | 985 | 1162.5348 | -18.0238 | 88.3376 | 893.1174 | 95.7441 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.6156 | 74.3844 | 0.25686 | NA | 6.6 | 61.908 | 985 | 1408.55 | 1661.9341 | -17.989 | 81.0052 | 1323.4671 | 95.3223 | SDS-Chlorination temp. | oC | 26 | 26 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.75 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.85 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.85 |  |  |  |  | SDS-Chlorination temp. | oC | 27 | 27 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.8 |  |  |  |  | SDS-Chlorination temp. | oC | 26 | 26 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.2 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.85
State Approved Plant Capacity (MGD) | 60 | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1.8603 | [5 empty] | 1998-04-07 | 10:00 | 4266.09 | 25.5556 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.5132 | 64.8868 | 0.23888 | 7.4 | 6.42 | 33.366 | 315.4 | 337.68 | 1447.16 | 2031.6946 | -40.3918 | 90.119 | 1184.6873 | 97.1836 | 100 | 78 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6402 | 75.5598 | 0.20424 | 6.42 | NA | 29.382 | 337.68 | 621.72 | 649.1239 | -4.4078 | 91.2989 | 493.4019 | 94.045 | 78 | 60 | 8.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.4925 | 51.7075 | 0.27735 | NA | NA | 40.04 | 621.72 | 1012 | 1156.8656 | -14.3148 | 88.1426 | 889.2928 | 95.4975 | 120 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.9551 | 73.8449 | 0.25874 | NA | 6.9 | 64.064 | 1012 | 1447.16 | 1707.1531 | -17.9657 | 81.0282 | 1359.5765 | 95.2879 | SDS-Chlorination pH | --- | 5.49 | 6.36 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.63 | 6.43 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.76 | 6.69 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.07 | 6.86 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.89 | 6.71 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.63 | 6.43 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 17 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.0478 | [5 empty] | 1998-04-08 | 6:40 | 4286.75 | 25.5556 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.2309 | 65.1691 | 0.23784 | 7.4 | 6.49 | 32.428 | 312.08 | 329.28 | 1427.14 | 1981.7561 | -38.8621 | 90.1518 | 1155.5181 | 97.1936 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.5262 | 75.4738 | 0.20447 | 6.49 | NA | 28.556 | 329.28 | 632.61 | 633.0726 | -0.073128 | 91.3277 | 481.1763 | 94.0654 | 78 | 60 | 8.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6617 | 51.5383 | 0.27826 | NA | NA | 39.34 | 632.61 | 998 | 1178.4184 | -18.078 | 88.0527 | 905.5142 | 95.6555 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.7722 | 74.2278 | 0.2574 | NA | 6.9 | 63.448 | 998 | 1427.14 | 1683.3381 | -17.9519 | 80.7313 | 1340.6691 | 95.2674 | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 5 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -0.077206 | [5 empty] | 1998-04-08 | 18:00 | 4298.68 | 25.5556 | 100 | 70 | 8.6 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 11.6614 | 64.7386 | 0.24659 | 7.4 | 6.46 | 31.222 | 323.7 | 340.2 | 1685.97 | 2054.5295 | -21.8604 | 90.8225 | 1197.3648 | 97.3924 | 100 | 80 | 8.8 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 15.8998 | 4.7247 | 76.4753 | 0.20791 | 6.46 | NA | 26.255 | 340.2 | 662.31 | 657.2534 | 0.76348 | 92.2825 | 498.7267 | 94.7356 | 80 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.2821 | 52.7179 | 0.28386 | NA | NA | 35.14 | 662.31 | 1179 | 1264.3932 | -7.2428 | 89.6708 | 963.3516 | 96.3523 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 15.1306 | 71.8694 | 0.26585 | NA | 6.9 | 62.216 | 1179 | 1685.97 | 1971.5564 | -16.939 | 81.7119 | 1575.2782 | 96.0505 | SDS-TOX | mg Cl- /L | BMRL | 315 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-32 | CI-s2-32 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 335 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-34 | CI-s2-34 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 33 | 425 | --- | 2603.4918 | --- | 92.2353 | 1514.2459 | 97.8207 | Parameter | Units | Cp-s2-36 | CI-s2-36 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 390 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-38 | CI-s2-38 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 410 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-40 | CI-s2-40 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 335 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-40 (dup) | CI-s2-40 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | Chloride ion rejection = 85 % | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-04-08 | 22:30 | 4302.45 | 25.5556 | 100 | 70 | 8.6 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 15.9641 | 11.6077 | 64.7923 | 0.24639 | 7.4 | 6.5 | 29.614 | 325.36 | 344.4 | 1723.15 | 2036.3747 | -18.1775 | 91.4013 | 1190.3874 | 97.5122 | 100 | 80 | 8.8 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 15.8998 | 4.7624 | 76.4376 | 0.20801 | 6.5 | NA | 26.904 | 344.4 | 663.3 | 661.896 | 0.21167 | 92.1882 | 503.148 | 94.6529 | 80 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.2947 | 52.7053 | 0.28393 | NA | NA | 35.28 | 663.3 | 1205 | 1266.1992 | -5.0788 | 89.7561 | 964.7496 | 96.3431 | 120 | 70 | 8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 15.3417 | 71.6583 | 0.26663 | NA | 6.8 | 63.294 | 1205 | 1723.15 | 1989.9229 | -15.4817 | 81.622 | 1597.4614 | 96.0378 | SDS-CHCl3 | mg/L | BMRL | 45.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-08 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 44 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.23 | 56.1 | --- | 366.5907 | --- | 99.59 | 211.3453 | 99.8912 | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-06 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.28 | 47.5 | --- | 310.358 | --- | 99.4105 | 178.929 | 99.8435 | Sampling date | MM/DD/YY | 1998-05-20 | 1998-05-20 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.92 | 55.4 | --- | 281.34 | --- | 92.9242 | 168.37 | 97.6718 | Sampling date | MM/DD/YY | 1998-06-03 | 1998-06-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | at 500 mg/L NaCL solution | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-04-09 | 7:25 | 4311.5 | 25.5556 | 100 | 70 | 8.6667 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 15.9641 | 11.2113 | 65.122 | 0.24514 | 7.4 | 6.54 | 30.284 | 327.02 | 334.32 | 1710.28 | 1968.5135 | -15.0989 | 90.9416 | 1151.4168 | 97.3698 | 100 | 80 | 9 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 15.8998 | 4.6174 | 76.3826 | 0.20816 | 6.54 | NA | 26.491 | 334.32 | 647.46 | 642.149 | 0.82028 | 92.0762 | 488.2345 | 94.5741 | 80 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.0582 | 52.9418 | 0.28266 | NA | NA | 35.42 | 647.46 | 1196 | 1235.0184 | -3.2624 | 89.4054 | 941.2392 | 96.2369 | 120 | 70 | 8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 15.2083 | 71.7917 | 0.26614 | NA | 6.9 | 64.218 | 1196 | 1710.28 | 1974.1001 | -15.4256 | 80.7915 | 1585.0501 | 95.9485 | SDS-BDCM | mg/L | BMRL | 14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 16.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 20.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 16.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.16 | 20.9 | --- | 111.9256 | --- | 99.2344 | 66.4128 | 99.7591 | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1998-04-09 | 16:00 | 4320.11 | 24.4444 | 100 | 70 | 8.4667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 16.2137 | 16.9767 | 11.3428 | 65.1905 | 0.26042 | 7.3 | 6.42 | 38.391 | 314.57 | 332.64 | 1492.92 | 2012.7069 | -34.8168 | 88.4587 | 1172.6734 | 96.7262 | 100 | 80 | 8.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 4.6976 | 76.5024 | 0.2253 | 6.42 | NA | 25.547 | 332.64 | 626.67 | 657.9761 | -4.9956 | 92.3199 | 495.3081 | 94.8422 | 80 | 60 | 8.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 8.7308 | 52.4692 | 0.29473 | NA | NA | 36.75 | 626.67 | 1044 | 1192.9932 | -14.2714 | 88.952 | 909.8316 | 95.9608 | 120 | 70 | 7.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.263 | 73.937 | 0.26704 | NA | 6.8 | 65.065 | 1044 | 1492.92 | 1738.7281 | -16.4649 | 80.4398 | 1391.364 | 95.3237 | SDS-DBCM | mg/L | BMRL | 3.66 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4288.74 | 4288.74 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 5.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4492.84 | 4492.84 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 2.75 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4765.68 | 4765.68 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.93 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5102.3 | 5102.3 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.99 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5435.24 | 5435.24 | --- | --- | --- | --- | SDS-DBCM | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4492.84 | 4492.84 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-04-09 | 3:40 | 4331.54 | 24.4444 | 100 | 70 | 8.4667 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 16.4971 | 10.8417 | 65.6916 | 0.25113 | 7.4 | 6.65 | 37.788 | 315.4 | 331.8 | 1508.65 | 1912.1145 | -26.7434 | 88.6112 | 1121.9572 | 96.632 | 100 | 80 | 8.8 | 10.2 | 10.2 | 20.4 | 20.4 | 0.50048 | 0.5 | 15.6923 | 16.4307 | 4.6 | 76.6 | 0.2145 | 6.65 | NA | 25.134 | 331.8 | 635.58 | 638.466 | -0.45407 | 92.425 | 485.133 | 94.8192 | 80 | 60 | 8.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 8.8316 | 52.3684 | 0.2953 | NA | NA | 38.85 | 635.58 | 1055 | 1208.4408 | -14.5442 | 88.2911 | 922.0104 | 95.7864 | 120 | 70 | 7.8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 13.2847 | 73.9153 | 0.26712 | NA | 6.8 | 66.374 | 1055 | 1508.65 | 1734.6804 | -14.9823 | 79.9958 | 1394.8402 | 95.2415 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.75 | 6.64 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.81 | 6.77 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.94 | 6.92 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.98 | 6.99 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.97 | 6.87 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.81 | 6.78 | --- | --- | --- | ---
|  | Standard testing pH | 8 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 0.73529 | [5 empty] | 1998-04-10 | 7:45 | 4335.87 | 24.4444 | 100 | 70 | 8.6 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 16.4971 | 11.3564 | 65.0436 | 0.25363 | 7.4 | 6.65 | 36.783 | 322.87 | 337.68 | 1541.54 | 2007.173 | -30.2057 | 89.1071 | 1172.4265 | 96.8627 | 100 | 80 | 9 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 16.4307 | 4.6957 | 76.3043 | 0.21533 | 6.65 | NA | 25.665 | 337.68 | 629.64 | 652.7843 | -3.6758 | 92.3996 | 495.2321 | 94.8176 | 80 | 60 | 8.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 8.7509 | 52.4491 | 0.29484 | NA | NA | 38.36 | 629.64 | 1078 | 1197.2688 | -11.0639 | 88.6401 | 913.4544 | 95.8006 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.7435 | 73.2565 | 0.26952 | NA | 6.8 | 63.602 | 1078 | 1541.54 | 1797.8954 | -16.6298 | 81.165 | 1437.9477 | 95.5769 | SDS-THM4 | mg/L | 0 | 62.76 | --- | 404.339 | --- | 100 | 233.5495 | 100 | Temperature | oC | 24.9 | 25.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 65.98 | --- | 427.8965 | --- | 100 | 246.9383 | 100 | Temperature | oC | 23.3 | 24 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0.23 | 79.75 | --- | 521.6726 | --- | 99.7116 | 300.7113 | 99.9235 | Temperature | oC | 24.3 | 24.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0.28 | 68.33 | --- | 447.1417 | --- | 99.5902 | 257.7358 | 99.8914 | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.08 | 80.29 | --- | 414.7672 | --- | 94.9184 | 247.5286 | 98.3517 | Temperature | oC | 26.4 | 26.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | 0 | #DIV/0! | Temperature | oC | 23.3 | 24 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 to 350 psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 0.48529 | [5 empty] | 1998-04-10 | 20:45 | 4348.97 | 25 | 100 | 70 | 8.6 | 0 | 17.1 | 3.1 |  | 20.2 | 20.2 | 0.84653 | 0 | 15.6641 | 16.134 | 11.588 | 64.812 | 0.24894 | 7.3 | 6.56 | 34.371 | 301.29 | 342.72 | 1570.14 | 2043.6129 | -30.1548 | 89.9711 | 1193.1664 | 97.1193 | 100 | 80 | 9 | 10.2 | 10 | 20.2 | 20.2 | 0.49394 | 0.50495 | 15.6923 | 16.1631 | 4.8045 | 76.1955 | 0.21213 | 6.56 | NA | 24.544 | 342.72 | 601.92 | 667.2595 | -10.8552 | 92.8385 | 504.9898 | 95.1397 | 80 | 60 | 8.8 | 4.8 | 4.95 | 9.75 | 9.75 | 0.48085 | 0.49231 | 14.7692 | 15.2123 | 8.3846 | 52.8154 | 0.28803 | NA | NA | 37.24 | 601.92 | 1098 | 1149.4885 | -4.6893 | 89.134 | 875.7042 | 95.7474 | 120 | 70 | 8 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.54 | 13.8672 | 73.1328 | 0.25351 | NA | 6.9 | 62.139 | 1098 | 1570.14 | 1799.7123 | -14.6211 | 81.8689 | 1448.8561 | 95.7112 | SDS-MCAA* | mg/L | BMRL | 2.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 209 | 378.7087 | 82.5688 | 293.8544 | 93.5342 | SDS-MCAA* | mg/L | BMRL | 3.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 225 | 406.3714 | 84.6154 | 315.6857 | 94.2981 | SDS-MCAA* | mg/L | BMRL | 4.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 281 | 509.6857 | 85.9155 | 395.3429 | 94.9411 | SDS-MCAA* | mg/L | BMRL | 2.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 17 | 294 | 539.0385 | 88.0282 | 416.5192 | 95.9186 | SDS-MCAA* | mg/L | BMRL | 2.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 269 | 540.6364 | 85.5072 | 404.8182 | 95.0595 | SDS-MCAA* | mg/L | BMRL | 3.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 232 | 418.6286 | 83.7607 | 325.3143 | 94.1595
|  | Acceptable range of operating pH values | 4 to 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | -2.1397 | [5 empty] | 1998-04-10 | 23:30 | 4351.56 | 24.4444 | 100 | 70 | 9.4667 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 16.2137 | 16.9767 | 11.4 | 64.1333 | 0.26471 | 7.3 | 6.59 | 40.267 | 308.76 | 336 | 1518.66 | 2024.54 | -33.3109 | 88.0158 | 1180.27 | 96.5883 | 100 | 80 | 9.8 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 4.7319 | 75.4681 | 0.22839 | 6.59 | NA | 26.668 | 336 | 627.66 | 663.7082 | -5.7433 | 92.0631 | 499.8541 | 94.6648 | 80 | 63 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 8.733 | 52.967 | 0.29196 | NA | NA | 37.59 | 627.66 | 1062 | 1194.1272 | -12.4414 | 88.8125 | 910.8936 | 95.8733 | 120 | 70 | 8.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.4902 | 72.7098 | 0.27155 | NA | 6.9 | 66.297 | 1062 | 1518.66 | 1768.6279 | -16.4598 | 80.2687 | 1415.314 | 95.3157 | SDS-DCAA* | mg/L | BMRL | 19 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 41 | 609 | 1116.3398 | 87.6877 | 862.6699 | 95.2473 | SDS-DCAA* | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 41 | 605 | 1099.1714 | 87.6133 | 852.0857 | 95.1883 | SDS-DCAA* | mg/L | BMRL | 22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 42 | 625 | 1135.819 | 87.3112 | 880.4095 | 95.2295 | SDS-DCAA* | mg/L | BMRL | 21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 38 | 592 | 1082.0769 | 87.7814 | 837.0385 | 95.4602 | SDS-DCAA* | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 45 | 640 | 1289.0909 | 86.6469 | 964.5455 | 95.3346 | SDS-DCAA* | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 42 | 609 | 1105.8 | 87.234 | 857.4 | 95.1015
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1998-04-11 | 9:45 | 4361.93 | 24.4444 | 100 | 70 | 9.2333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 16.4971 | 11.5216 | 64.2451 | 0.25678 | 7.3 | 6.62 | 39.128 | 317.06 | 344.4 | 1514.37 | 2038.1672 | -34.5885 | 88.6388 | 1191.2836 | 96.7155 | 100 | 80 | 9.1 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 16.4307 | 4.787 | 76.113 | 0.21587 | 6.62 | NA | 26.314 | 344.4 | 616.77 | 665.6354 | -7.9228 | 92.3595 | 505.0177 | 94.7895 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 8.5667 | 52.6333 | 0.29381 | NA | NA | 37.94 | 616.77 | 1059 | 1172.4468 | -10.7126 | 88.9837 | 894.6084 | 95.759 | 120 | 70 | 8.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.4568 | 72.7432 | 0.27143 | NA | 6.8 | 65.758 | 1059 | 1514.37 | 1763.8814 | -16.4763 | 80.9065 | 1411.4407 | 95.3411 | SDS-TCAA* | mg/L | BMRL | 34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 12 | 401 | 748.4563 | 93.6842 | 574.7282 | 97.9121 | SDS-TCAA* | mg/L | BMRL | 34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 10 | 386 | 715.4476 | 94.7917 | 550.7238 | 98.1842 | SDS-TCAA* | mg/L | BMRL | 46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 11 | 416 | 770.8571 | 94.4162 | 593.4286 | 98.1464 | SDS-TCAA* | mg/L | BMRL | 37 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 10 | 376 | 699.7692 | 94.9239 | 537.8846 | 98.1409 | SDS-TCAA* | mg/L | BMRL | 34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 13 | 414 | 851.4545 | 93.5 | 632.7273 | 97.9454 | SDS-TCAA* | mg/L | BMRL | 34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 11 | 401 | 742.7143 | 94.2408 | 571.8571 | 98.0764
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-04-11 | 16:00 | 4367.95 | 24.4444 | 100 | 70 | 8.9333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 16.2137 | 16.9767 | 10.9296 | 65.137 | 0.26063 | 7.3 | 6.54 | 38.19 | 277.22 | 321.72 | 1368.51 | 1940.5848 | -41.8028 | 88.1294 | 1131.1524 | 96.6238 | 100 | 80 | 9.2 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 17.2361 | 4.5342 | 76.2658 | 0.226 | 6.54 | NA | 25.311 | 321.72 | 620.73 | 635.7375 | -2.4177 | 92.1326 | 478.7287 | 94.7129 | 80 | 62 | 9.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 15.4642 | 8.647 | 53.153 | 0.29094 | NA | NA | 36.47 | 620.73 | 957 | 1181.6196 | -23.4712 | 88.6641 | 901.1748 | 95.9531 | 120 | 70 | 8.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 12.1281 | 74.4719 | 0.26513 | NA | 6.8 | 61.831 | 957 | 1368.51 | 1592.2812 | -16.3514 | 80.7811 | 1274.6406 | 95.1491 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 10 | 375 | 701.0194 | 94.5355 | 538.0097 | 98.1413 | SDS-MBAA* | mg/L | BMRL | 1.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 375 | 695.6857 | 94.9721 | 535.3429 | 98.3188 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 364 | 675.0476 | 95.1087 | 519.5238 | 98.2676 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 373 | 695 | 95.1087 | 534 | 98.3146 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 11 | 380 | 782.5455 | 94.1489 | 581.2727 | 98.1076 | SDS-MBAA* | mg/L | BMRL | 1.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 373 | 691.9333 | 94.9438 | 532.4667 | 98.3098
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1.8603 | [5 empty] | 1998-04-15 | 15:00 | 4376.85 | 25.5556 | 100 | 69 | 9.4667 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.4281 | 11.7673 | 63.266 | 0.25967 | 7.1 | 6.2 | 48.173 | 339.47 | 346.08 | 1714.57 | 2103.7313 | -22.6973 | 86.0804 | 1224.9056 | 96.0672 | 100 | 78 | 10.2 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 4.7137 | 74.0863 | 0.22513 | 6.2 | NA | 38.999 | 346.08 | 668.25 | 674.6567 | -0.95872 | 88.7312 | 510.3683 | 92.3587 | 78 | 61 | 10 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.2208 | 50.2792 | 0.29763 | NA | NA | 45.22 | 668.25 | 1199 | 1266.3588 | -5.6179 | 86.9337 | 967.3044 | 95.3252 | 117 | 69 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.2382 | 69.5618 | 0.27467 | NA | 6.9 | 84.007 | 1199 | 1714.57 | 2016.6615 | -17.6191 | 75.7261 | 1607.8308 | 94.7751 | SDS-DBAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.11 | 0.19039 | 50 | 0.15019 | 86.6839 | SDS-DBAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.03 | 0.15 | 0.25514 | 62.5 | 0.20257 | 85.1904 | SDS-DBAA* | mg/L | BMRL | 1.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 0.86 | 1.6048 | 80 | 1.2324 | 99.1886 | SDS-DBAA* | mg/L | BMRL | 1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 1.6 | 2.9977 | 80 | 2.2988 | 99.13 | SDS-DBAA* | mg/L | BMRL | 1.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 1.59 | 3.3027 | 77.7778 | 2.4464 | 99.1825 | SDS-DBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.04 | 0.032 | 0.02499 | 42.8571 | 0.028495 | -40.3743
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | Zero for extended use | Maximum system recycle flow rate, (QR-sys)max (gpm) | -2.1397 | [5 empty] | 1998-04-16 | 8:30 | 4394.02 | 25.5556 | 100 | 68 | 8 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.4281 | 11.0677 | 64.9323 | 0.253 | 7.4 | 6.32 | 35.644 | 300.46 | 315.84 | 1475.76 | 1968.9964 | -33.4225 | 88.7145 | 1142.4182 | 96.88 | 100 | 80 | 8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 4.4062 | 77.5938 | 0.21496 | 6.32 | NA | 28.792 | 315.84 | 602.91 | 622.9814 | -3.3291 | 90.884 | 469.4107 | 93.8664 | 80 | 61 | 8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 8.3212 | 54.1788 | 0.27621 | NA | NA | 40.67 | 602.91 | 1032 | 1142.6604 | -10.7229 | 87.1232 | 872.7852 | 95.3402 | 118 | 68 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.1106 | 71.8894 | 0.26578 | NA | 7 | 72.688 | 1032 | 1475.76 | 1735.4955 | -17.6001 | 76.9858 | 1383.7477 | 94.747 | SDS-BCAA* | mg/L | BMRL | 6.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.46 | 12.15 | 22.5916 | 91.6817 | 17.3708 | 97.3519 | SDS-BCAA* | mg/L | BMRL | 7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.39 | 11.15 | 20.5778 | 92.7509 | 15.8639 | 97.5416 | SDS-BCAA* | mg/L | BMRL | 7.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.26 | 11.85 | 22.005 | 95.203 | 16.9275 | 98.464 | SDS-BCAA* | mg/L | BMRL | 7.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.44 | 10.9 | 20.1531 | 91.8819 | 15.5265 | 97.1661 | SDS-BCAA* | mg/L | BMRL | 7.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.13 | 13.35 | 27.7718 | 97.7625 | 20.5609 | 99.3677 | SDS-BCAA* | mg/L | BMRL | 6.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.17 | 11.2 | 20.8644 | 97.0383 | 16.0322 | 98.9396
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-04-16 | 16:00 | 4401.5 | 25.5556 | 100 | 68 | 8.6 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.4281 | 11.6843 | 63.7157 | 0.25784 | 7.4 | 6.25 | 41.875 | 327.02 | 337.68 | 1584.44 | 2082.9295 | -31.4616 | 87.5992 | 1210.3048 | 96.5401 | 100 | 80 | 8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 4.7097 | 77.2903 | 0.2158 | 6.25 | NA | 30.857 | 337.68 | 657.36 | 665.9806 | -1.3114 | 90.8621 | 501.8303 | 93.8511 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.0856 | 52.1144 | 0.28715 | NA | NA | 43.47 | 657.36 | 1108 | 1246.6944 | -12.5175 | 87.1269 | 952.0272 | 95.434 | 120 | 68 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.0714 | 71.9286 | 0.26563 | NA | 7 | 78.386 | 1108 | 1584.44 | 1863.0503 | -17.5841 | 76.7869 | 1485.5251 | 94.7233 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.458 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.466 | 0.87343 | 99.5536 | 0.66971 | 99.8507 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.488 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.46 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.502 | 1.0485 | 99.5798 | 0.77527 | 99.871 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.005 | 0.482 | 0.89994 | 97.807 | 0.69097 | 99.2764
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 19.2647 | [5 empty] | 1998-04-17 | 10:25 | 4419.64 | 25.5556 | 100 | 68 | 8.6 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.4281 | 11.9603 | 63.4397 | 0.25896 | 7.4 | 6.44 | 41.607 | 322.04 | 344.4 | 1590.16 | 2130.8787 | -34.004 | 87.919 | 1237.6393 | 96.6382 | 100 | 80 | 8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 4.7957 | 77.2043 | 0.21604 | 6.44 | NA | 31.978 | 344.4 | 653.4 | 678.6915 | -3.8708 | 90.7149 | 511.5458 | 93.7488 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.0052 | 52.1948 | 0.28671 | NA | NA | 44.94 | 653.4 | 1112 | 1237.5216 | -11.2879 | 86.9512 | 945.4608 | 95.2468 | 120 | 68 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.1292 | 71.8708 | 0.26585 | NA | 7 | 78.155 | 1112 | 1590.16 | 1870.153 | -17.6079 | 77.3069 | 1491.0765 | 94.7585 | SDS-CDBAA | mg/L | BMRL | 3.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.7695 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.25641 | 4.1794 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 4.1181 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 4.2202 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.76923 | 3.7603 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 3.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 2.9412 | 4.3036 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-04-17 | 16:00 | 4425.34 | 25.5556 | 100 | 68 | 8.6667 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.4281 | 11.209 | 64.1243 | 0.25619 | 7.4 | 6.41 | 40.468 | 323.7 | 324.24 | 1621.62 | 1998.4948 | -23.2406 | 87.5191 | 1161.3674 | 96.5155 | 100 | 80 | 8 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 4.4926 | 77.5074 | 0.2152 | 6.41 | NA | 31.565 | 324.24 | 661.32 | 637.4022 | 3.6167 | 90.2649 | 480.8211 | 93.4352 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.1266 | 52.0734 | 0.28737 | NA | NA | 44.66 | 661.32 | 1134 | 1253.3136 | -10.5215 | 86.2263 | 957.3168 | 95.3349 | 120 | 68 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.4204 | 71.3796 | 0.26767 | NA | 7 | 78.848 | 1134 | 1621.62 | 1907.7781 | -17.6464 | 75.6822 | 1520.8891 | 94.8157 | SDS-DCBAA | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 16 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1 | 17 | --- | 87.2222 | --- | 94.1176 | 52.1111 | 98.081 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 13 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-04-17 | 22:30 | 4431.87 | 25.5556 | 100 | 70 | 8.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 16.2137 | 16.4281 | 11.5554 | 64.7113 | 0.25387 | 7.5 | 6.47 | 39.597 | 313.74 | 339.36 | 1524.38 | 2050.91 | -34.5406 | 88.3319 | 1195.135 | 96.6868 | 100 | 80 | 9 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 16.6792 | 4.7571 | 76.2429 | 0.21876 | 6.47 | NA | 28.379 | 339.36 | 619.74 | 668.8151 | -7.9187 | 91.6375 | 504.0876 | 94.3702 | 80 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 8.5495 | 53.4505 | 0.27997 | NA | NA | 42.07 | 619.74 | 1066 | 1174.3032 | -10.1598 | 87.6031 | 897.0216 | 95.31 | 118 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 13.4369 | 72.3631 | 0.26404 | NA | 6.9 | 74.228 | 1066 | 1524.38 | 1769.8382 | -16.1022 | 78.1271 | 1417.9191 | 94.765 | SDS-HAA5 | mg/L | 0 | 56.5 | --- | 364.0082 | --- | 100 | 210.2541 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 59.8 | --- | 387.8177 | --- | 100 | 223.8089 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 74 | --- | 485.2459 | --- | 100 | 279.623 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 61.6 | --- | 404.5067 | --- | 100 | 233.0533 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 57.7 | --- | 310.9389 | --- | 100 | 184.3194 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 60 | --- | 389.1148 | --- | 100 | 224.5574 | 100
|  | Stage 3 -- General Information |  | maximum system recycle flow rates. | [6 empty] | 1998-04-18 | 17:50 | 4441.78 | 25.5556 | 100 | 70 | 9 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.4281 | 12.0611 | 63.9389 | 0.25694 | 7.4 | 6.43 | 40.736 | 318.72 | 346.08 | 1607.32 | 2147.6096 | -33.6143 | 88.2293 | 1246.8448 | 96.7329 | 100 | 80 | 9 | 10.7 | 10 | 20.7 | 20.7 | 0.50211 | 0.51691 | 16.4615 | 16.6792 | 4.845 | 76.155 | 0.21902 | 6.43 | NA | 30.444 | 346.08 | 667.26 | 683.8105 | -2.4804 | 91.2032 | 514.9453 | 94.0879 | 80 | 62 | 9.8 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.2248 | 51.9752 | 0.28792 | NA | NA | 43.96 | 667.26 | 1124 | 1265.628 | -12.6004 | 87.2977 | 966.444 | 95.4514 | 120 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.2964 | 72.5036 | 0.26352 | NA | 7 | 77.924 | 1124 | 1607.32 | 1891.1224 | -17.6569 | 77.4838 | 1507.5612 | 94.8311 | SDS-HAA6 | mg/L | 0 | 63.4 | --- | 408.4623 | --- | 100 | 235.9311 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 66.8 | --- | 433.2144 | --- | 100 | 250.0072 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 81.9 | --- | 537.0492 | --- | 100 | 309.4746 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 69 | --- | 453.1 | --- | 100 | 261.05 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 65.3 | --- | 351.8944 | --- | 100 | 208.5972 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 66.9 | --- | 433.863 | --- | 100 | 250.3815 | 100 | Stage 3 Operating Parameters During Sample Collection
|  | Membrane manufacturer | Fluid Systems | [7 empty] | 1998-04-18 | 23:30 | 4456.83 | 25.5556 | 100 | 70 | 8.8333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 16.2137 | 16.4281 | 11.9052 | 64.2615 | 0.25565 | 7.4 | 6.43 | 40.602 | 333.66 | 349.44 | 1541.54 | 2112.8054 | -37.0581 | 88.3808 | 1231.1227 | 96.702 | 100 | 79 | 9.1 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 16.6792 | 4.9519 | 75.4481 | 0.22107 | 6.43 | NA | 25.724 | 349.44 | 635.58 | 692.3867 | -8.9378 | 92.6385 | 520.9133 | 95.0618 | 79 | 62 | 9.2 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 8.7964 | 52.5036 | 0.28502 | NA | NA | 41.23 | 635.58 | 1078 | 1206.156 | -11.8883 | 88.2011 | 920.868 | 95.5227 | 119 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 13.7007 | 72.5993 | 0.26318 | NA | 6.9 | 66.759 | 1078 | 1541.54 | 1795.6549 | -16.4845 | 80.8954 | 1436.8275 | 95.3537 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.40777 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41905 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41905 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42308 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.18182 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41905
|  | Membrane trade name | TFC-S | Summary of the Stage and System Flow Rates | [6 empty] | 1998-04-21 | 18:05 | 4481.61 | 25.5556 | 100 | 70 | 8.7333 | 0 | 17.7 | 3.1 |  | 20.8 | 20.8 | 0.85096 | 0 | 16.2137 | 16.4281 | 12.312 | 63.9546 | 0.25687 | 7.4 | 6.44 | 41.808 | 330.34 | 361.2 | 1568.71 | 2184.8253 | -39.2753 | 88.4252 | 1273.0126 | 96.7158 | 100 | 79 | 9 | 10.7 | 10.1 | 20.8 | 20.8 | 0.50538 | 0.51442 | 16.4615 | 16.6792 | 5.1444 | 75.3556 | 0.22134 | 6.44 | NA | 24.898 | 361.2 | 679.14 | 717.4803 | -5.6454 | 93.1069 | 539.3402 | 95.3836 | 79 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.4639 | 52.0361 | 0.28758 | NA | NA | 39.69 | 679.14 | 1097 | 1293.012 | -17.868 | 89.0116 | 986.076 | 95.975 | 120 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 14.003 | 72.797 | 0.26246 | NA | 6.9 | 63.448 | 1097 | 1568.71 | 1830.4885 | -16.6875 | 82.4341 | 1463.7443 | 95.6654 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.1 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 0.8 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2
|  | Membrane element model number | SC 2540S | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.2647 | [5 empty] | 1998-04-22 | 10:00 | 4495.35 | 25.5556 | 100 | 70 | 8.7333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 11.9238 | 64.3429 | 0.24811 | 7.3 | 6.47 | 41.071 | 338.64 | 357 | 1541.54 | 2109.8964 | -36.8694 | 88.4955 | 1233.4482 | 96.6702 | 100 | 78 | 9 | 10.3 | 10 | 20.3 | 20.3 | 0.49557 | 0.50739 | 15.8462 | 16.0557 | 4.9688 | 75.0312 | 0.21399 | 6.47 | NA | 29.028 | 357 | 669.24 | 694.8112 | -3.8209 | 91.8689 | 525.9056 | 94.4804 | 78 | 62 | 9 | 4.7 | 5 | 9.7 | 9.7 | 0.48085 | 0.48454 | 14.4615 | 14.6528 | 9.2287 | 51.7713 | 0.28303 | NA | NA | 41.44 | 669.24 | 1078 | 1259.372 | -16.8249 | 88.3922 | 964.306 | 95.7026 | 120 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 13.6548 | 73.1452 | 0.26121 | NA | 6.8 | 70.147 | 1078 | 1541.54 | 1793.2505 | -16.3285 | 80.351 | 1435.6253 | 95.1138 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.15 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.25 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.25 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.2 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.4 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.25
|  | Molecular weight cutoff (Daltons) | 300 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | [5 empty] | 1998-04-22 | 15:35 | 4499.84 | 25.5556 | 100 | 70 | 8.7333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 12.0037 | 64.263 | 0.24842 | 7.4 | 6.39 | 41.473 | 341.96 | 359.52 | 1557.27 | 2124.1679 | -36.4033 | 88.4643 | 1241.8439 | 96.6604 | 100 | 79 | 9 | 10.2 | 10.1 | 20.3 | 20.3 | 0.49721 | 0.50246 | 15.6923 | 15.8998 | 4.9684 | 75.5316 | 0.21051 | 6.39 | NA | 29.382 | 359.52 | 685.08 | 692.9267 | -1.1454 | 91.8274 | 526.2233 | 94.4164 | 79 | 62 | 9 | 4.8 | 5 | 9.8 | 9.8 | 0.48412 | 0.4898 | 14.7692 | 14.9645 | 9.5445 | 51.9555 | 0.28803 | NA | NA | 40.18 | 685.08 | 1089 | 1304.184 | -19.7598 | 88.824 | 994.632 | 95.9603 | 120 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 13.8132 | 72.9868 | 0.26178 | NA | 6.8 | 69.454 | 1089 | 1557.27 | 1812.5488 | -16.3927 | 80.6815 | 1450.7744 | 95.2126 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.5147 | [5 empty] | 1998-04-22 | 23:15 | 4507.57 | 24.4444 | 100 | 70 | 9.1667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 16.4971 | 11.4811 | 64.3522 | 0.25636 | 7.4 | 6.44 | 40.2 | 336.15 | 344.4 | 1542.97 | 2032.2194 | -31.7083 | 88.3275 | 1188.3097 | 96.617 | 100 | 78 | 9.4 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.7529 | 4.8246 | 74.7754 | 0.22404 | 6.44 | NA | 28.084 | 344.4 | 636.57 | 676.6916 | -6.3028 | 91.8455 | 510.5458 | 94.4992 | 78 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.7001 | 50.6999 | 0.29231 | NA | NA | 40.67 | 636.57 | 1079 | 1184.798 | -9.8052 | 88.1911 | 910.684 | 95.5341 | 120 | 70 | 8.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.7444 | 13.636 | 72.864 | 0.27098 | NA | 7.1 | 72.534 | 1079 | 1542.97 | 1793.2662 | -16.2217 | 78.939 | 1436.1331 | 94.9494 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.5147 | [5 empty] | 1998-04-23 | 10:00 | 4518.91 | 25.5556 | 100 | 70 | 9.3 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.8515 | 63.8485 | 0.25003 | 7.4 | 6.44 | 35.376 | 320.38 | 341.88 | 1491.49 | 2099.1696 | -40.7431 | 89.6525 | 1220.5248 | 97.1016 | 100 | 78 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.7895 | 74.7105 | 0.21699 | 6.44 | NA | 28.969 | 341.88 | 642.51 | 673.9488 | -4.8931 | 91.5266 | 507.9144 | 94.2965 | 78 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.7899 | 50.6101 | 0.28336 | NA | NA | 40.46 | 642.51 | 1043 | 1196.396 | -14.7072 | 88.1654 | 919.453 | 95.5996 | 118 | 70 | 8.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.2893 | 71.9107 | 0.2657 | NA | 7.1 | 70.609 | 1043 | 1491.49 | 1756.0867 | -17.7404 | 79.3468 | 1399.5434 | 94.9549 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-32 | CI-s3-32 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-34 | CI-s3-34 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-36 | CI-s3-36 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-38 | CI-s3-38 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-40 | CI-s3-40 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-40 (dup) | CI-s3-40 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | [5 empty] | 1998-04-24 | 22:00 | 4535.61 | 25.5556 | 100 | 70 | 9.3 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.9541 | 63.7459 | 0.25043 | 7.4 | 6.3 | 35.242 | 322.04 | 344.4 | 1501.5 | 2116.9059 | -40.9861 | 89.7671 | 1230.6529 | 97.1363 | 100 | 78 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.8253 | 74.6747 | 0.2171 | 6.3 | NA | 29.146 | 344.4 | 638.55 | 678.9553 | -6.3277 | 91.5372 | 511.6776 | 94.3038 | 78 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.7485 | 50.6515 | 0.28313 | NA | NA | 39.34 | 638.55 | 1050 | 1189.8232 | -13.3165 | 88.5772 | 914.1866 | 95.6967 | 118 | 70 | 8.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.3734 | 71.8266 | 0.26601 | NA | 7.2 | 71.456 | 1050 | 1501.5 | 1767.5989 | -17.7222 | 79.252 | 1408.7995 | 94.9279 | Qp/QT (THM4), % | -14.7228 | 42.6386 |  | Qp/QT (HAA5), % | 4.4248 | 52.2124 |  |  |  | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-08 | --- | --- | --- | --- | Qp/QT (THM4), % | -9.124 | 45.438 |  | Qp/QT (HAA5), % | 9.699 | 54.8495 |  |  |  | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | Qp/QT (THM4), % | 9.746 | 55.0176 |  | Qp/QT (HAA5), % | 27.027 | 63.5135 |  |  |  | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-06 | --- | --- | --- | --- | Qp/QT (THM4), % | -5.3931 | 47.5092 |  | Qp/QT (HAA5), % | 12.3377 | 56.1688 |  |  |  | Sampling date | MM/DD/YY | 1998-05-20 | 1998-05-20 | --- | --- | --- | --- | Qp/QT (THM4), % | 10.8778 | 58.1157 |  | Qp/QT (HAA5), % | 6.4125 | 53.2062 |  |  |  | Sampling date | MM/DD/YY | 1998-06-03 | 1998-06-03 | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | 10 | 55 |  |  |  | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.6397 | [5 empty] | 1998-04-25 | 9:35 | 4547.15 | 24.4444 | 100 | 70 | 9.3 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.4971 | 12.1867 | 63.5133 | 0.25974 | 7.4 | 6.32 | 35.108 | 310.42 | 350.28 | 1482.91 | 2157.2661 | -45.4752 | 89.9772 | 1253.7731 | 97.1998 | 100 | 78 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.7529 | 4.9243 | 74.5757 | 0.22464 | 6.32 | NA | 28.556 | 350.28 | 632.61 | 691.7014 | -9.3409 | 91.8477 | 520.9907 | 94.5189 | 78 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.6679 | 50.7321 | 0.29212 | NA | NA | 38.92 | 632.61 | 1037 | 1178.8048 | -13.6745 | 88.8889 | 905.7074 | 95.7028 | 118 | 70 | 8.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 13.2116 | 71.9884 | 0.27427 | NA | 7.1 | 70.301 | 1037 | 1482.91 | 1745.9126 | -17.7356 | 79.9301 | 1391.4563 | 94.9477 | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 59.983 | 29.9915 |  |  |  | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 59.5806 | 29.7903 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 58.2581 | 29.2441 |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 59.9342 | 30.1071 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 75.4031 | 39.7415 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | 0 | 0 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 4.6397 | [5 empty] | 1998-04-26 | 0:05 | 4561.12 | 25.5556 | 100 | 70 | 9.3 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 12.5362 | 63.1638 | 0.25274 | 7.4 | 6.98 | 35.309 | 317.06 | 359.52 | 1490.06 | 2218.3297 | -48.8752 | 90.1788 | 1288.9249 | 97.2606 | 100 | 78 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 5.0586 | 74.4414 | 0.21778 | 6.98 | NA | 29.028 | 359.52 | 639.54 | 710.2462 | -11.0558 | 91.9259 | 534.8831 | 94.573 | 78 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.7609 | 50.6391 | 0.2832 | NA | NA | 39.48 | 639.54 | 1042 | 1191.5952 | -14.3565 | 89.0187 | 915.5676 | 95.6879 | 118 | 70 | 8.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.2788 | 71.9212 | 0.26566 | NA | 7.2 | 70.378 | 1042 | 1490.06 | 1754.5228 | -17.7485 | 80.4245 | 1398.2614 | 94.9667 | SDS-HAA5b, mg/L | NA | 32.4092 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 4288.74 | 4288.74 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 32.6281 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 4492.84 | 4492.84 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 66.788 | 33.287 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 4765.68 | 4765.68 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 32.3343 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 5102.3 | 5102.3 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 51.4235 | 24.1672 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 5435.24 | 5435.24 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 4492.84 | 4492.84 | --- | --- | --- | ---
|  | Stage 3 -- Design Parameters |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | [5 empty] | 1998-04-27 | 0:15 | 4582.94 | 25.5556 | 100 | 70 | 9.3 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.5958 | 64.1042 | 0.24903 | 7.4 | 6.23 | 37.788 | 313.74 | 337.68 | 1532.96 | 2057.0608 | -34.1888 | 88.8095 | 1197.3704 | 96.8441 | 100 | 78 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.7315 | 74.7685 | 0.21682 | 6.23 | NA | 28.556 | 337.68 | 667.26 | 665.73 | 0.2293 | 91.5435 | 501.705 | 94.3082 | 78 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.1697 | 50.2303 | 0.28551 | NA | NA | 39.2 | 667.26 | 1072 | 1245.0752 | -16.1451 | 88.3914 | 956.1676 | 95.9003 | 118 | 70 | 8.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.6794 | 71.5206 | 0.26715 | NA | 7.2 | 71.071 | 1072 | 1532.96 | 1806.0146 | -17.8122 | 78.9532 | 1439.0073 | 95.0611 | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.78 | 6.84 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.94 | 6.99 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | 386.7958 | 209.331 |  | SDS-TOXb, mg Cl- /L | 319.0541 | 176.027 |  |  |  | pH | --- | 6.09 | 7.17 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.14 | 7.21 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.19 | 7.12 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.95 | 7 | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 2.8897 | [5 empty] | 1998-04-28 | 9:30 | 4593.42 | 25.5556 | 98 | 70 | 9.0667 | 0 | 16.9 | 3 |  | 19.9 | 19.9 | 0.84925 | 0 | 15.4809 | 15.6856 | 10.8727 | 64.0606 | 0.24486 | 7.4 | 6.42 | 38.525 | 309.59 | 323.4 | 1341.34 | 1928.1958 | -43.7515 | 88.0875 | 1125.7979 | 96.578 | 98 | 72 | 8.8 | 10.1 | 9.8 | 19.9 | 19.9 | 0.48576 | 0.50754 | 15.5385 | 15.7439 | 4.4311 | 71.7689 | 0.21937 | 6.42 | NA | 30.975 | 323.4 | 622.71 | 624.7768 | -0.3319 | 90.4221 | 474.0884 | 93.4664 | 72 | 60 | 9.4 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.341 | 8.4969 | 48.1031 | 0.29813 | NA | NA | 44.45 | 622.71 | 938 | 1165.5663 | -24.2608 | 86.2554 | 894.1382 | 95.0287 | 117 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.746 | 72.754 | 0.26262 | NA | 7.1 | 78.54 | 938 | 1341.34 | 1568.2707 | -16.9182 | 75.7143 | 1253.1353 | 93.7325 | SDS-CDb, mg/L | NA | 8.1805 |  | SDS-CDb, mg/L | 11.765 | 7.2825 |  |  |  | Temperature | oC | 25.5 | 25.9 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 7.9407 |  | SDS-CDb, mg/L | 11.3537 | 7.0419 |  |  |  | Temperature | oC | 24.7 | 24.1 | --- | --- | --- | --- | SDS-CDb, mg/L | 10.2424 | 6.2585 |  | SDS-CDb, mg/L | 8.7216 | 5.5108 |  |  |  | Temperature | oC | 25.1 | 24 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 7.0954 |  | SDS-CDb, mg/L | 10.2081 | 6.3291 |  |  |  | Temperature | oC | NA | NA | --- | --- | --- | --- | SDS-CDb, mg/L | 10.6414 | 6.305 |  | SDS-CDb, mg/L | 11.0513 | 6.7557 |  |  |  | Temperature | oC | 26.9 | 26.4 | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | 11.238 | 6.954 |  |  |  | Temperature | oC | 24.7 | 24.1 | --- | --- | --- | ---
|  | Active membrane area of membrane element used, A (ft2) | 28 | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-04-28 | 19:35 | 4602.77 | 25.5556 | 98 | 70 | 9.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.9378 | 63.9955 | 0.2422 | 7.4 | 6.32 | 37.654 | 322.04 | 326.76 | 1347.06 | 1936.1167 | -43.7291 | 88.4766 | 1131.4384 | 96.672 | 98 | 72 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.4368 | 71.7632 | 0.21504 | 6.32 | NA | 31.978 | 326.76 | 624.69 | 624.55 | 0.022414 | 90.2136 | 475.655 | 93.2771 | 72 | 60 | 9.4 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.341 | 8.5147 | 48.0853 | 0.29824 | NA | NA | 45.22 | 624.69 | 942 | 1168.6822 | -24.0639 | 86.1611 | 896.6861 | 94.957 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.809 | 73.191 | 0.26105 | NA | 7.2 | 77.924 | 942 | 1347.06 | 1575.6557 | -16.97 | 76.1525 | 1258.8279 | 93.8098 | TOCb, mg/L | NA | 3.3938 |  | TOCb, mg/L | 5.3083 | 2.9142 |  |  |  | Alkalinity | mg/L as CaCO3 | 20 | 342 | 563.7049 | 81.6514 | 452.8525 | 95.5836 | TOCb, mg/L | NA | 3.0808 |  | TOCb, mg/L | 4.8892 | 2.6046 |  |  |  | Alkalinity | mg/L as CaCO3 | 26 | 412 | 690.4262 | 77.7778 | 551.2131 | 95.2831 | TOCb, mg/L | 4.9288 | 2.6471 |  | TOCb, mg/L | 4.0578 | 2.2189 |  |  |  | Alkalinity | mg/L as CaCO3 | 30 | 506 | 849.3443 | 78.8732 | 677.6721 | 95.5731 | TOCb, mg/L | NA | 3.0303 |  | TOCb, mg/L | 4.7994 | 2.5947 |  |  |  | Alkalinity | mg/L as CaCO3 | 29 | 505 | 854.0667 | 79.5775 | 679.5333 | 95.7324 | TOCb, mg/L | 5.1965 | 2.5323 |  | TOCb, mg/L | 5.4483 | 2.8092 |  |  |  | Alkalinity | mg/L as CaCO3 | 46 | 488 | 586.2222 | 66.6667 | 537.1111 | 91.4357 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | 5.184 | 2.682 |  |  |  | Alkalinity | mg/L as CaCO3 | 26 | 429 | 719.6885 | 77.7778 | 574.3443 | 95.4731
|  | Design flux, FW (gfd) | 41.43 | System concentrate waste flow rate, QW-sys (gpm) | 2.8897 | [5 empty] | 1998-04-29 | 0:30 | 4609.68 | 25.5556 | 98 | 70 | 9.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.2913 | 63.642 | 0.24355 | 7.4 | 6.34 | 38.391 | 318.72 | 336.84 | 1364.22 | 1998.2061 | -46.4724 | 88.6026 | 1167.5231 | 96.7118 | 98 | 72 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.5991 | 71.6009 | 0.21553 | 6.34 | NA | 31.27 | 336.84 | 651.42 | 645.5281 | 0.90448 | 90.7167 | 491.184 | 93.6338 | 72 | 60 | 9.4 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.341 | 8.9095 | 47.6905 | 0.30071 | NA | NA | 45.08 | 651.42 | 954 | 1220.6371 | -27.9494 | 86.6168 | 936.0286 | 95.1839 | 117 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.9657 | 72.5343 | 0.26341 | NA | 7.2 | 78.463 | 954 | 1364.22 | 1596.0605 | -16.9944 | 76.7062 | 1275.0302 | 93.8462 | UV254 b, cm-1 | NA | 0.12016 |  | UV254 b, cm-1 | 0.19888 | 0.10044 |  |  |  | Total dissolved solids | mg/L | 55 | 966 | 1593.2459 | 83.4835 | 1279.623 | 95.7019 | UV254 b, cm-1 | NA | 0.12267 |  | UV254 b, cm-1 | 0.20237 | 0.10169 |  |  |  | Total dissolved solids | mg/L | 69 | 1015 | 1697.3607 | 79.1541 | 1356.1803 | 94.9122 | UV254 b, cm-1 | 0.20146 | 0.10141 |  | UV254 b, cm-1 | 0.16327 | 0.082635 |  |  |  | Total dissolved solids | mg/L | 71 | 1040 | 1738.9508 | 78.5498 | 1389.4754 | 94.8902 | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 69 | 983 | 1653.2667 | 77.8135 | 1318.1333 | 94.7653 | UV254 b, cm-1 | 0.21233 | 0.10085 |  | UV254 b, cm-1 | 0.22287 | 0.11243 |  |  |  | Total dissolved solids | mg/L | 105 | 1067 | 1280.7778 | 68.8427 | 1173.8889 | 91.0554 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | 0.2056 | 0.1048 |  |  |  | Total dissolved solids | mg/L | 69 | 1040 | 1740.3934 | 79.0274 | 1390.1967 | 95.0367
|  | Net driving pressure at the design flux, NDP (psi) | 97 | System permeate flow rate, Qp-sys (gpm) | 16.375 | [5 empty] | 1998-04-29 | 6:40 | 4614.01 | 25.5556 | 98 | 70 | 9.4 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 10.9919 | 63.6081 | 0.25098 | 7.3 | 6.34 | 43.081 | 319.55 | 334.32 | 1289.86 | 1950.2267 | -51.1968 | 87.1138 | 1142.2734 | 96.2285 | 98 | 73 | 9.4 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.643 | 71.457 | 0.22687 | 6.34 | NA | 29.913 | 334.32 | 596.97 | 654.1011 | -9.5702 | 91.0526 | 494.2105 | 93.9473 | 73 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.0852 | 48.6148 | 0.29499 | NA | NA | 43.19 | 596.97 | 902 | 1106.4476 | -22.666 | 87.0812 | 851.7088 | 94.929 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.2452 | 73.7548 | 0.25905 | NA | 7.1 | 71.995 | 902 | 1289.86 | 1491.0358 | -15.5967 | 78.4652 | 1196.5179 | 93.983 | Bromideb, mg/L | NA | 46.1377 |  | Bromideb, mg/L | 70.2124 | 40.1062 |  |  |  | Total hardness | mg/L as CaCO3 | 14 | 680 | 1138.5574 | 92.6316 | 909.2787 | 98.4603 | Bromideb, mg/L | NA | 48.5547 |  | Bromideb, mg/L | 68.5686 | 43.2843 |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 672 | 1144.459 | 91.1458 | 908.2295 | 98.1282 | Bromideb, mg/L | 68.6143 | 48.2421 |  | Bromideb, mg/L | 60.8378 | 44.4189 |  |  |  | Total hardness | mg/L as CaCO3 | 19 | 741 | 1261.7869 | 90.3553 | 1001.3934 | 98.1026 | Bromideb, mg/L | NA | 48.0692 |  | Bromideb, mg/L | 70.2273 | 42.6136 |  |  |  | Total hardness | mg/L as CaCO3 | 19 | 706 | 1209.8 | 90.3553 | 957.9 | 98.0165 | Bromideb, mg/L | 30.9542 | 17.7276 |  | Bromideb, mg/L | 32.2045 | 19.1023 |  |  |  | Total hardness | mg/L as CaCO3 | 38 | 759 | 919.2222 | 81 | 839.1111 | 95.4714 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | 69.4 | 44.2 |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 748 | 1275.2787 | 91.0995 | 1011.6393 | 98.3196
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.427 | System feed flow rate, QF-sys (gpm) | 19.2647 | [5 empty] | 1998-04-29 | 15:50 | 4623.01 | 24.4444 | 100 | 70 | 9.4667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.4971 | 12.7314 | 62.8019 | 0.26268 | 7.5 | 6.34 | 38.659 | 356.07 | 367.92 | 1707.42 | 2255.6831 | -32.1106 | 89.4926 | 1311.8015 | 97.053 | 100 | 72 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.7529 | 5.0742 | 71.4258 | 0.23455 | 6.34 | NA | 36.403 | 367.92 | 661.32 | 719.734 | -8.8329 | 90.1057 | 543.827 | 93.3061 | 72 | 60 | 9.9 | 4.6 | 4.8 | 9.4 | 9.4 | 0.4645 | 0.48936 | 14.1538 | 14.8198 | 9.1836 | 46.9164 | 0.31588 | NA | NA | 40.46 | 661.32 | 1194 | 1256.3108 | -5.2187 | 89.003 | 958.8154 | 95.7802 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 15.3583 | 69.6417 | 0.28351 | NA | 7.1 | 70.224 | 1194 | 1707.42 | 2018.1024 | -18.196 | 80.9132 | 1606.0512 | 95.6275 | Alkb, mg/L CaCO3 | NA | 69.3461 |  | Alkb, mg/L CaCO3 | 104.885 | 60.4425 |  |  |  | Calcium hardness | mg/L as CaCO3 | 12 | 341 | 567.5246 | 93.4426 | 454.2623 | 97.3584 | Alkb, mg/L CaCO3 | NA | 71.1076 |  | Alkb, mg/L CaCO3 | 107.204 | 61.602 |  |  |  | Calcium hardness | mg/L as CaCO3 | 15 | 664 | 1132.1311 | 91.6201 | 898.0656 | 98.3297 | Alkb, mg/L CaCO3 | 129.915 | 73.7782 |  | Alkb, mg/L CaCO3 | 108.4865 | 63.2432 |  |  |  | Calcium hardness | mg/L as CaCO3 | 18 | 654 | 1112.7541 | 90.2174 | 883.377 | 97.9624 | Alkb, mg/L CaCO3 | NA | 82.1384 |  | Alkb, mg/L CaCO3 | 126.4545 | 71.2273 |  |  |  | Calcium hardness | mg/L as CaCO3 | 18 | 665 | 1139.4667 | 90.2174 | 902.2333 | 98.005 | Alkb, mg/L CaCO3 | 124.8378 | 67.68 |  | Alkb, mg/L CaCO3 | 130.2409 | 73.6205 |  |  |  | Calcium hardness | mg/L as CaCO3 | 33 | 700 | 848.2222 | 82.4468 | 774.1111 | 95.737 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | 106.9 | 61.45 |  |  |  | Calcium hardness | mg/L as CaCO3 | 16 | 670 | 1141.7377 | 91.0112 | 905.8689 | 98.2337
|  | Temperature at which the MTCW was determined, ToC (oC) | 25 | [7 empty] | 1998-04-30 | 0:30 | 4631.06 | 24.4444 | 100 | 70 | 9.4667 | 0 | 17.7 | 3 |  | 20.7 | 20.7 | 0.85507 | 0 | 16.2137 | 16.9767 | 12.5625 | 62.9709 | 0.2696 | 7.5 | 6.17 | 38.123 | 366.86 | 356.16 | 1690.26 | 2232.5783 | -32.0849 | 89.2961 | 1294.3691 | 97.0547 | 100 | 72 | 9.5 | 10.9 | 9.8 | 20.7 | 20.7 | 0.49884 | 0.52657 | 16.7692 | 17.5583 | 4.9868 | 71.5132 | 0.24553 | 6.17 | NA | 35.695 | 356.16 | 665.28 | 712.5956 | -7.1121 | 89.9778 | 534.3778 | 93.3203 | 72 | 60 | 9.9 | 4.6 | 4.8 | 9.4 | 9.4 | 0.4645 | 0.48936 | 14.1538 | 14.8198 | 9.2566 | 46.8434 | 0.31637 | NA | NA | 39.48 | 665.28 | 1182 | 1265.005 | -7.0224 | 88.9151 | 965.1425 | 95.9094 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 15.1985 | 69.8015 | 0.28287 | NA | 7.1 | 69.916 | 1182 | 1690.26 | 1997.5283 | -18.1788 | 80.3695 | 1589.7641 | 95.6021 | T-Hdb, mg/L CaCO3 | NA | 114.5296 |  | T-Hdb, mg/L CaCO3 | 182.1681 | 97.5841 |  |  |  | Turbidity | ntu | 0.01 | 2.03 | 3.4208 | 75 | 2.7254 | 99.6331 | T-Hdb, mg/L CaCO3 | NA | 109.3028 |  | T-Hdb, mg/L CaCO3 | 174.3478 | 92.1739 |  |  |  | Turbidity | ntu | 0.01 | 11.04 | 18.9961 | 87.5 | 15.018 | 99.9334 | T-Hdb, mg/L CaCO3 | 178.8725 | 94.6673 |  | T-Hdb, mg/L CaCO3 | 146.7297 | 78.8649 |  |  |  | Turbidity | ntu | 0.02 | 20 | 34.4118 | 60 | 27.2059 | 99.9265 | T-Hdb, mg/L CaCO3 | NA | 108.6329 |  | T-Hdb, mg/L CaCO3 | 174.0519 | 92.526 |  |  |  | Turbidity | ntu | 0.02 | 18.64 | 32.2947 | 80 | 25.4673 | 99.9215 | T-Hdb, mg/L CaCO3 | 179.6584 | 91.3236 |  | T-Hdb, mg/L CaCO3 | 188.0087 | 100.5043 |  |  |  | Turbidity | ntu | 0.04 | 12.25 | 14.9633 | 55.5556 | 13.6067 | 99.706 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | 173 | 92 |  |  |  | Turbidity | ntu | 0.01 | 11.6 | 19.96 | 85.7143 | 15.78 | 99.9366
|  | Maximum flow rate to the element, QI, max (gpm) | 2.5 | Calculate the Required System Influent Pressure | [6 empty] | 1998-04-30 | 7:00 | 4638.33 | 25.5556 | 100 | 70 | 9.4667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 11.9072 | 63.6261 | 0.2509 | 7.4 | 6.17 | 40.669 | 328.68 | 356.16 | 1562.99 | 2106.6262 | -34.7818 | 88.5813 | 1231.3931 | 96.6973 | 100 | 74 | 9.6 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.9887 | 72.4113 | 0.22388 | 6.17 | NA | 29.087 | 356.16 | 706.86 | 699.7518 | 1.0056 | 91.8332 | 527.9559 | 94.4906 | 74 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.7366 | 47.4634 | 0.30215 | NA | NA | 39.97 | 706.86 | 1093 | 1320.3988 | -20.805 | 88.7775 | 1013.6294 | 96.0567 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 13.8737 | 71.1263 | 0.26863 | NA | 7 | 68.992 | 1093 | 1562.99 | 1819.7154 | -16.4253 | 80.6289 | 1456.3577 | 95.2627 | Ca-Hdb, mg/L CaCO3 | NA | 108.8088 |  | Ca-Hdb, mg/L CaCO3 | 175.3009 | 92.1504 |  |  |  | Total organic carbon | mg/L | 0.5 | 20.45 | 34.1861 | 90.9584 | 27.318 | 98.1697 | Ca-Hdb, mg/L CaCO3 | NA | 101.301 |  | Ca-Hdb, mg/L CaCO3 | 162.4147 | 85.2074 |  |  |  | Total organic carbon | mg/L | 0.25 | 20.15 | 34.5041 | 95.3532 | 27.327 | 99.0852 | Ca-Hdb, mg/L CaCO3 | 167.042 | 88.2694 |  | Ca-Hdb, mg/L CaCO3 | 136.973 | 73.4865 |  |  |  | Total organic carbon | mg/L | 0.47 | 20.1 | 34.2593 | 91.3284 | 27.1797 | 98.2708 | Ca-Hdb, mg/L CaCO3 | NA | 101.334 |  | Ca-Hdb, mg/L CaCO3 | 162.5325 | 86.2662 |  |  |  | Total organic carbon | mg/L | 0.44 | 18.5 | 31.744 | 91.8819 | 25.122 | 98.2485 | Ca-Hdb, mg/L CaCO3 | 168.855 | 85.7163 |  | Ca-Hdb, mg/L CaCO3 | 176.714 | 94.357 |  |  |  | Total organic carbon | mg/L | 0.43 | 23.35 | 28.4433 | 92.599 | 25.8967 | 98.3396 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | 161.1 | 85.05 |  |  |  | Total organic carbon | mg/L | 0.37 | 19.65 | 33.5569 | 93.554 | 26.6034 | 98.6092
|  | Minimum flow rate to the element, QI, min (gpm) | 0.5 | Osmotic pressure for stage 13, Dp1 (psi) | 8.9 | [5 empty] | 1998-05-01 | 0:22 | 4647.12 | 24.4444 | 100 | 70 | 9.4333 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.4971 | 12.5236 | 63.0431 | 0.26168 | 7.5 | 6.34 | 38.994 | 352.75 | 362.88 | 1664.52 | 2219.8264 | -33.3614 | 89.2543 | 1291.3532 | 96.9804 | 100 | 72 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.7529 | 5.0143 | 71.4857 | 0.23435 | 6.34 | NA | 35.282 | 362.88 | 686.07 | 710.535 | -3.566 | 90.2772 | 536.7075 | 93.4262 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.43 | 46.77 | 0.31687 | NA | NA | 40.18 | 686.07 | 1164 | 1280.2888 | -9.9904 | 88.9275 | 983.1794 | 95.9133 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.7444 | 14.9577 | 70.0423 | 0.28189 | NA | 7 | 69.531 | 1164 | 1664.52 | 1966.6106 | -18.1488 | 80.8391 | 1565.3053 | 95.558 | Notes: | [9 empty] | UV254 | cm-1 | 0.001 | 0.717 | 1.21 | 99.5192 | 0.96349 | 99.8962 | Notes: | [9 empty] | UV254 | cm-1 | 0.003 | 0.741 | 1.2733 | 98.6607 | 1.0072 | 99.7021 | Notes: | [9 empty] | UV254 | cm-1 | 0.003 | 0.743 | 1.2768 | 98.6547 | 1.0099 | 99.7029 | Notes: | [9 empty] | UV254 | cm-1 | 0.003 | 0.7 | 1.2111 | 98.6784 | 0.95557 | 99.6861 | Notes: | [9 empty] | UV254 | cm-1 | 0.012 | 0.759 | 0.925 | 94.958 | 0.842 | 98.5748 | Notes: | [9 empty] | UV254 | cm-1 | 0.004 | 0.755 | 1.2967 | 98.2456 | 1.0259 | 99.6101
|  | Total width of all membrane envelopes in the element, w (ft) | 6.4 | Osmotic pressure for stage 23, Dp2 (psi) | 13.4 | [5 empty] | 1998-05-01 | 7:10 | 4655.82 | 25.5556 | 100 | 70 | 9.9 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 12.002 | 63.098 | 0.253 | 7.4 | 6.32 | 37.319 | 324.53 | 355.32 | 1796.08 | 2119.7126 | -18.0188 | 89.4971 | 1237.5163 | 96.9844 | 100 | 76 | 10.5 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.9633 | 72.5367 | 0.22349 | 6.32 | NA | 29.913 | 355.32 | 730.62 | 697.1617 | 4.5794 | 91.5814 | 526.2408 | 94.3157 | 76 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 10.0559 | 47.9441 | 0.29912 | NA | NA | 41.86 | 730.62 | 1256 | 1364.2792 | -8.621 | 88.2191 | 1047.4496 | 96.0036 | 118 | 70 | 9.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 16.0706 | 68.7294 | 0.278 | NA | 7 | 69.839 | 1256 | 1796.08 | 2097.7917 | -16.7983 | 80.3448 | 1676.8958 | 95.8352 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.2 | 3.5061 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.2 | 3.6774 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.6383 | 3.6965 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.68182 | 3.7838 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 2.7907 | 3.2505 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.0811 | 3.8422 | --- | --- | --- | ---
|  | Feed spacer thickness, T (ft) | 0.00258 | Osmotic pressure for stage 33, Dp3 (psi) | 18.6 | [5 empty] | 1998-05-01 | 20:45 | 4668.19 | 25.5556 | 100 | 70 | 9.8 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 12.4028 | 62.7972 | 0.25422 | 7.4 | 6.86 | 38.458 | 341.13 | 367.08 | 1761.76 | 2190.4021 | -24.3303 | 89.5233 | 1278.741 | 96.9925 | 100 | 76 | 10.4 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 5.0914 | 72.5086 | 0.22358 | 6.86 | NA | 33.276 | 367.08 | 700.92 | 717.7428 | -2.4001 | 90.9349 | 542.4114 | 93.8652 | 76 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.6417 | 48.5583 | 0.29534 | NA | NA | 40.53 | 700.92 | 1232 | 1308.4788 | -6.2077 | 88.9588 | 1004.6994 | 95.966 | 120 | 70 | 9.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 15.7381 | 70.0619 | 0.27271 | NA | 7 | 70.378 | 1232 | 1761.76 | 2056.3769 | -16.7229 | 80.8276 | 1644.1885 | 95.7196 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses due to stage hardware, DPs (psi) | 4 | [5 empty] | 1998-05-02 | 6:40 | 4678.13 | 25.5556 | 100 | 70 | 9.6667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 12.186 | 63.1474 | 0.25281 | 7.4 | 6.3 | 38.324 | 345.28 | 361.2 | 1738.88 | 2152.641 | -23.7947 | 89.3898 | 1256.9205 | 96.951 | 100 | 76 | 10 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 5.0197 | 72.9803 | 0.22214 | 6.3 | NA | 32.096 | 361.2 | 710.82 | 706.9254 | 0.5479 | 91.1141 | 534.0627 | 93.9902 | 76 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.7995 | 48.2005 | 0.29753 | NA | NA | 39.62 | 710.82 | 1216 | 1328.324 | -9.2372 | 89.031 | 1019.572 | 96.1141 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 15.5307 | 69.4693 | 0.27504 | NA | 7 | 69.685 | 1216 | 1738.88 | 2029.5139 | -16.7139 | 80.7074 | 1622.7569 | 95.7058 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-05-02 | 20:30 | 4691.87 | 25.5556 | 100 | 70 | 9.6667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 11.7548 | 63.5786 | 0.25109 | 7.3 | 6.29 | 37.989 | 354.41 | 349.44 | 1774.63 | 2077.4907 | -17.0661 | 89.1286 | 1213.4654 | 96.8694 | 100 | 72 | 10.2 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.834 | 70.966 | 0.22844 | 6.29 | NA | 32.509 | 349.44 | 687.06 | 682.3776 | 0.68151 | 90.6968 | 515.9088 | 93.6987 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.4567 | 46.7433 | 0.3068 | NA | NA | 39.34 | 687.06 | 1241 | 1282.9624 | -3.3813 | 88.742 | 985.0112 | 96.0061 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 15.8663 | 69.1337 | 0.27637 | NA | 7.1 | 69.916 | 1241 | 1774.63 | 2072.0919 | -16.7619 | 79.992 | 1656.5459 | 95.7794 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-05-02 | 23:30 | 4695.24 | 25.5556 | 100 | 70 | 9.6667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 12.6611 | 62.6722 | 0.25472 | 7.4 | 6.32 | 34.974 | 345.28 | 370.44 | 1674.53 | 2231.7352 | -33.2753 | 90.5588 | 1301.0876 | 97.3119 | 100 | 76 | 10.2 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 5.1786 | 72.6214 | 0.22323 | 6.32 | NA | 30.916 | 370.44 | 665.28 | 727.1117 | -9.2941 | 91.6542 | 548.7758 | 94.3664 | 76 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.1275 | 49.0725 | 0.29224 | NA | NA | 40.11 | 665.28 | 1171 | 1240.4364 | -5.9297 | 89.1723 | 952.8582 | 95.7906 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 14.9555 | 70.0445 | 0.27278 | NA | 7.1 | 67.144 | 1171 | 1674.53 | 1954.3817 | -16.7123 | 81.8745 | 1562.6908 | 95.7033 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  | Stage 3 -- Additional Information |  | Mechanical pressure losses per stage, Ls (psi) | 22 | [5 empty] | 1998-05-03 | 10:30 | 4705.91 | 25.5556 | 100 | 70 | 9.6 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 12.2517 | 63.1483 | 0.2528 | 7.4 | 6.31 | 36.582 | 333.66 | 361.2 | 1721.72 | 2162.3063 | -25.5899 | 89.8721 | 1261.7532 | 97.1007 | 100 | 74 | 10 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 5.0314 | 71.9686 | 0.22526 | 6.31 | NA | 31.329 | 361.2 | 689.04 | 707.7312 | -2.7126 | 91.3264 | 534.4656 | 94.1383 | 74 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.4509 | 47.7491 | 0.30034 | NA | NA | 41.72 | 689.04 | 1204 | 1284.5744 | -6.6922 | 88.4496 | 986.8072 | 95.7722 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 15.3608 | 69.6392 | 0.27436 | NA | 7.1 | 70.224 | 1204 | 1721.72 | 2008.6152 | -16.6633 | 80.5581 | 1606.3076 | 95.6282 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 0.75 | Net driving pressure required for permeation, NDP (psi) | 49.7034 | [5 empty] | 1998-05-03 | 20:40 | 4716.1 | 25.5556 | 100 | 70 | 9.5333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 11.8952 | 63.5715 | 0.25112 | 7.4 | 6.26 | 35.108 | 327.02 | 350.28 | 1664.52 | 2098.9763 | -26.101 | 89.9772 | 1224.6281 | 97.1332 | 100 | 74 | 10 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.8774 | 72.1226 | 0.22478 | 6.26 | NA | 30.503 | 350.28 | 661.32 | 686.2074 | -3.7633 | 91.2918 | 518.2437 | 94.1142 | 74 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.0584 | 48.3416 | 0.29666 | NA | NA | 40.88 | 661.32 | 1164 | 1232.1248 | -5.8526 | 88.3293 | 946.7224 | 95.6819 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 14.8293 | 70.1707 | 0.27229 | NA | 7 | 69.454 | 1164 | 1664.52 | 1940.7746 | -16.5967 | 80.1719 | 1552.3873 | 95.526 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Flow weighted system pressure losses, Lsys (psi) | 33.5282 | [5 empty] | 1998-05-04 | 5:40 | 4724.91 | 25.5556 | 100 | 70 | 9.5333 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 15.9641 | 11.7223 | 63.7444 | 0.25044 | 7.4 | 6.14 | 34.907 | 322.04 | 352.8 | 1658.8 | 2061.4749 | -24.2751 | 90.1057 | 1207.1374 | 97.1083 | 100 | 74 | 10 | 10.4 | 10 | 20.4 | 20.4 | 0.49721 | 0.5098 | 16 | 16.2116 | 4.889 | 72.111 | 0.22481 | 6.14 | NA | 31.152 | 352.8 | 663.3 | 687.3139 | -3.6204 | 91.1701 | 520.057 | 94.0099 | 74 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.0618 | 48.3382 | 0.29668 | NA | NA | 42.63 | 663.3 | 1160 | 1234.3164 | -6.4066 | 87.9167 | 948.8082 | 95.507 | 118 | 70 | 9 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 14.6139 | 70.3861 | 0.27145 | NA | 7 | 72.457 | 1160 | 1658.8 | 1907.6858 | -15.004 | 79.4623 | 1533.8429 | 95.2761 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Maximum element recovery (%) | 17 | Required influent pressure to the system, PI (psi) | 83.2317 | [5 empty] | 1998-05-05 | 1:50 | 4735.66 | 25.5556 | 100 | 70 | 9.6 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 15.9641 | 11.8312 | 63.5688 | 0.25113 | 7.4 | 6.45 | 33.634 | 319.55 | 354.48 | 1684.54 | 2079.0273 | -23.4181 | 90.5117 | 1216.7536 | 97.2358 | 100 | 74 | 10 | 10.4 | 10 | 20.4 | 20.4 | 0.49721 | 0.5098 | 16 | 16.2116 | 4.902 | 72.098 | 0.22485 | 6.45 | NA | 31.978 | 354.48 | 667.26 | 689.8821 | -3.3903 | 90.9789 | 522.181 | 93.8761 | 74 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.1237 | 48.0763 | 0.2983 | NA | NA | 42.35 | 667.26 | 1178 | 1242.1772 | -5.448 | 88.0529 | 954.7186 | 95.5641 | 118 | 70 | 9 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 14.8961 | 70.1039 | 0.27255 | NA | 7 | 69.454 | 1178 | 1684.54 | 1940.1254 | -15.1724 | 80.4068 | 1559.0627 | 95.5451 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Variability of design flux (%) | 5 | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-05-05 | 8:00 | 4742.03 | 24.4444 | 100 | 70 | 9.6 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 16.4971 | 12.3654 | 63.0346 | 0.26171 | 7.4 | 6.45 | 35.108 | 333.66 | 370.44 | 1717.43 | 2172.8495 | -26.5175 | 90.5226 | 1271.6447 | 97.2392 | 100 | 72 | 10 | 10.4 | 10 | 20.4 | 20.4 | 0.49721 | 0.5098 | 16 | 16.7529 | 5.1437 | 70.8563 | 0.23643 | 6.45 | NA | 32.037 | 370.44 | 689.04 | 722.3791 | -4.8385 | 91.3516 | 546.4096 | 94.1368 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.4856 | 46.7144 | 0.31724 | NA | NA | 39.34 | 689.04 | 1201 | 1286.764 | -7.141 | 89.3802 | 987.902 | 96.0178 | 118 | 70 | 9 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 15.2548 | 69.7452 | 0.28309 | NA | 7.1 | 65.758 | 1201 | 1717.43 | 1981.4789 | -15.3747 | 82.2487 | 1591.2394 | 95.8675 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Rejection of reference solute and conditions of test | Magnesium Sulfate = 98 % Rejection | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-05-05 | 21:30 | 4755.35 | 24.4444 | 100 | 70 | 9.5333 | 0 | 17.2 | 3.2 |  | 20.4 | 20.4 | 0.84314 | 0 | 15.7557 | 16.4971 | 11.633 | 63.8337 | 0.25844 | 7.4 | 6.45 | 33.969 | 328.68 | 349.44 | 1697.41 | 2045.0966 | -20.4834 | 90.279 | 1197.2683 | 97.1628 | 100 | 72 | 10 | 10.4 | 10 | 20.4 | 20.4 | 0.49721 | 0.5098 | 16 | 16.7529 | 4.8209 | 71.1791 | 0.23536 | 6.45 | NA | 32.273 | 349.44 | 658.35 | 679.2937 | -3.1812 | 90.7644 | 514.3668 | 93.7257 | 72 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.0467 | 47.3533 | 0.31296 | NA | NA | 38.71 | 658.35 | 1187 | 1228.4188 | -3.4894 | 88.9223 | 943.3844 | 95.8967 | 118 | 70 | 9 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.7444 | 15.0584 | 69.9416 | 0.2823 | NA | 7.1 | 66.374 | 1187 | 1697.41 | 1957.4304 | -15.3187 | 81.0056 | 1572.2152 | 95.7783
|  | (e.g., solute type and concentration) | San Diego Tap = 75 % Rejection | [7 empty] | 1998-05-06 | 10:00 | 4768.17 | 25 | 100 | 70 | 8.8667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.2284 | 12.1974 | 63.9359 | 0.25382 | 7.4 | 6.57 | 38.19 | 336.98 | 353.64 | 1650.22 | 2162.22 | -31.0262 | 89.2009 | 1257.93 | 96.9641 | 100 | 78 | 9.2 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.48 | 4.9622 | 74.8378 | 0.22021 | 6.57 | NA | 29.441 | 353.64 | 662.31 | 697.6879 | -5.3416 | 91.6749 | 525.664 | 94.3993 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 9.0882 | 50.7118 | 0.28748 | NA | NA | 39.83 | 662.31 | 1154 | 1234.9916 | -7.0183 | 88.7371 | 948.6508 | 95.8014 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.4229 | 14.7611 | 71.0389 | 0.27341 | NA | 7.2 | 73.92 | 1154 | 1650.22 | 1946.0587 | -17.9272 | 79.0974 | 1550.0293 | 95.2311
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1998-05-06 | 16:30 | 4774.51 | 25 | 100 | 70 | 8.7333 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.2284 | 11.8387 | 64.4279 | 0.25188 | 7.3 | 6.55 | 37.386 | 342.79 | 343.56 | 1605.89 | 2098.9576 | -30.7037 | 89.1181 | 1221.2588 | 96.9387 | 100 | 76 | 9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.48 | 4.8188 | 74.1812 | 0.22216 | 6.55 | NA | 28.733 | 343.56 | 647.46 | 677.6621 | -4.6647 | 91.6367 | 510.6111 | 94.3728 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 8.8867 | 50.1133 | 0.29091 | NA | NA | 38.78 | 647.46 | 1123 | 1207.4456 | -7.5196 | 88.7123 | 927.4528 | 95.8187 | 115 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.4229 | 14.3448 | 69.9552 | 0.27765 | NA | 7.2 | 73.381 | 1123 | 1605.89 | 1892.7206 | -17.8612 | 78.641 | 1507.8603 | 95.1334
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-05-07 | 0:15 | 4781.56 | 25 | 100 | 70 | 9.0667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.2284 | 11.9324 | 64.001 | 0.25356 | 7.4 | 6.56 | 38.324 | 333.66 | 346.92 | 1638.78 | 2116.2037 | -29.1329 | 88.9531 | 1231.5619 | 96.8882 | 100 | 76 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.48 | 4.928 | 73.272 | 0.22492 | 6.56 | NA | 24.957 | 346.92 | 656.37 | 688.595 | -4.9096 | 92.8061 | 517.7575 | 95.1798 | 76 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 9.0291 | 49.7709 | 0.29291 | NA | NA | 37.94 | 656.37 | 1146 | 1225.3256 | -6.922 | 89.0638 | 940.8478 | 95.9675 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.4229 | 14.6581 | 71.1419 | 0.27302 | NA | 7.2 | 73.458 | 1146 | 1638.78 | 1932.5308 | -17.925 | 78.8257 | 1539.2654 | 95.2277
|  | Standard testing pH | 7 | [7 empty] | 1998-05-07 | 8:15 | 4790.07 | 25 | 100 | 70 | 9 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.2284 | 11.9206 | 64.0794 | 0.25325 | 7.4 | 6.59 | 37.788 | 349.43 | 346.08 | 1624.48 | 2113.6208 | -30.1106 | 89.0811 | 1229.8504 | 96.9274 | 100 | 76 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.48 | 4.8691 | 73.3309 | 0.22473 | 6.59 | NA | 27.966 | 346.08 | 641.52 | 683.6704 | -6.5704 | 91.9192 | 514.8752 | 94.5684 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 8.7959 | 50.2041 | 0.29038 | NA | NA | 39.06 | 641.52 | 1136 | 1195.7832 | -5.2626 | 88.7136 | 918.6516 | 95.7481 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.4229 | 14.5193 | 71.2807 | 0.27248 | NA | 7.2 | 73.612 | 1136 | 1624.48 | 1915.0845 | -17.8891 | 78.7298 | 1525.5423 | 95.1747
|  | Acceptable range of operating pressures | 0 to 350 psi | [7 empty] | 1998-05-07 | 16:05 | 4798.08 | 25 | 100 | 70 | 8.9333 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 16.2284 | 10.6268 | 65.4399 | 0.24799 | 7.3 | 6.58 | 39.329 | 294.65 | 314.16 | 1324.18 | 1889.8577 | -42.7191 | 87.4812 | 1102.0089 | 96.4312 | 100 | 76 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.48 | 4.3462 | 73.8538 | 0.22314 | 6.58 | NA | 30.208 | 314.16 | 594 | 615.4968 | -3.619 | 90.3845 | 464.8284 | 93.5013 | 76 | 60 | 9 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.5785 | 8.1244 | 50.8756 | 0.28655 | NA | NA | 41.09 | 594 | 926 | 1113.0584 | -20.2007 | 86.9207 | 853.5292 | 95.1859 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.4229 | 11.6872 | 74.3128 | 0.26137 | NA | 7.2 | 70.84 | 926 | 1324.18 | 1553.1173 | -17.289 | 77.451 | 1239.5587 | 94.2851
|  | Acceptable range of operating pH values | 4 to 11 | [7 empty] | 1998-05-08 | 0:15 | 4805.1 | 25.5556 | 100 | 70 | 9 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.3609 | 64.6391 | 0.24697 | 7.4 | 6.52 | 39.664 | 339.47 | 333.48 | 1603.03 | 2018.0251 | -25.8882 | 88.106 | 1175.7525 | 96.6265 | 100 | 76 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.6853 | 73.5147 | 0.22052 | 6.52 | NA | 27.376 | 333.48 | 615.78 | 658.3251 | -6.9091 | 91.7908 | 495.9025 | 94.4796 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.4222 | 50.5778 | 0.28354 | NA | NA | 38.92 | 615.78 | 1121 | 1146.4912 | -2.274 | 88.3291 | 881.1356 | 95.583 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.329 | 71.471 | 0.26733 | NA | 7.2 | 72.534 | 1121 | 1603.03 | 1889.8751 | -17.8939 | 78.2494 | 1505.4375 | 95.1819
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1998-05-08 | 9:00 | 4814.92 | 25.5556 | 100 | 70 | 9 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.7987 | 64.2013 | 0.24866 | 7.4 | 6.38 | 39.262 | 327.02 | 344.4 | 1565.85 | 2093.8579 | -33.7202 | 88.5999 | 1219.1289 | 96.7795 | 100 | 76 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.8362 | 73.3638 | 0.22098 | 6.38 | NA | 28.438 | 344.4 | 632.61 | 679.7066 | -7.4448 | 91.7427 | 512.0533 | 94.4463 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6474 | 50.3526 | 0.28481 | NA | NA | 40.32 | 632.61 | 1095 | 1177.5168 | -7.5358 | 88.2927 | 905.0634 | 95.5451 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.98 | 71.82 | 0.26603 | NA | 7.2 | 72.072 | 1095 | 1565.85 | 1845.1472 | -17.8368 | 79.0732 | 1470.0736 | 95.0974
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-05-08 | 15:30 | 4821.5 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.0831 | 65.2502 | 0.23755 | 7.2 | 6.62 | 40.535 | 313.74 | 333.48 | 1365.65 | 1964.2072 | -43.8295 | 87.8448 | 1148.8436 | 96.4717 | 100 | 74 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.569 | 73.431 | 0.21016 | 6.62 | NA | 29.913 | 333.48 | 602.91 | 640.1446 | -6.1758 | 91.03 | 486.8123 | 93.8553 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.1719 | 49.8281 | 0.28781 | NA | NA | 43.19 | 602.91 | 955 | 1117.8524 | -17.0526 | 87.0487 | 860.3812 | 94.9801 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.0688 | 73.9312 | 0.25844 | NA | 7.2 | 71.918 | 955 | 1365.65 | 1602.5935 | -17.3502 | 78.4341 | 1278.7967 | 94.3761
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 1998-05-09 | 5:30 | 4835.45 | 25.5556 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.6622 | 65.6045 | 0.23626 | 7.3 | 6.45 | 39.061 | 302.12 | 320.88 | 1409.98 | 1889.6724 | -34.0212 | 87.8269 | 1105.2762 | 96.466 | 100 | 74 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.3847 | 73.6153 | 0.20963 | 6.45 | NA | 29.559 | 320.88 | 586.08 | 615.1737 | -4.9641 | 90.7881 | 468.0268 | 93.6843 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9497 | 50.0503 | 0.28653 | NA | NA | 41.58 | 586.08 | 986 | 1087.02 | -10.2454 | 87.0419 | 836.55 | 95.0296 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.5009 | 73.2991 | 0.26066 | NA | 7.2 | 71.302 | 986 | 1409.98 | 1656.7785 | -17.5037 | 77.7792 | 1321.3893 | 94.604
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-05-09 | 10:00 | 4839.86 | 25.5556 | 100 | 70 | 8.7333 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.0036 | 65.2631 | 0.24461 | 7.4 | 6.41 | 39.664 | 333.66 | 324.24 | 1394.25 | 1955.8091 | -40.2768 | 87.7671 | 1140.0245 | 96.5208 | 100 | 74 | 9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.5167 | 73.4833 | 0.22062 | 6.41 | NA | 29.146 | 324.24 | 614.79 | 637.401 | -3.6778 | 91.011 | 480.8205 | 93.9383 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.3597 | 49.6403 | 0.2889 | NA | NA | 42.21 | 614.79 | 975 | 1141.5636 | -17.0834 | 86.9819 | 878.1768 | 95.1935 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.3463 | 73.4537 | 0.26012 | NA | 7.2 | 71.61 | 975 | 1394.25 | 1637.486 | -17.4457 | 77.9145 | 1306.243 | 94.5179
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-05-09 | 16:30 | 4846.46 | 25.5556 | 100 | 70 | 8.6333 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.3541 | 65.0125 | 0.24555 | 7.8 | 6.68 | 37.319 | 312.08 | 330.96 | 1372.8 | 2014.5017 | -46.744 | 88.724 | 1172.7309 | 96.8178 | 100 | 74 | 8.9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.6115 | 73.4885 | 0.2206 | 6.68 | NA | 29.677 | 330.96 | 594 | 650.6889 | -9.5436 | 91.0331 | 490.8244 | 93.9536 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.0459 | 49.9541 | 0.28708 | NA | NA | 42.91 | 594 | 960 | 1101.0028 | -14.6878 | 87.0347 | 847.5014 | 94.9369 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.1592 | 73.8408 | 0.25875 | NA | 7.2 | 70.301 | 960 | 1372.8 | 1612.4459 | -17.4567 | 78.7585 | 1286.223 | 94.5343
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-05-09 | 23:45 | 4853.69 | 25.5556 | 100 | 70 | 8.6 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 10.689 | 65.711 | 0.24294 | 7.8 | 6.48 | 37.721 | 321.21 | 314.16 | 1354.21 | 1899.0769 | -40.235 | 87.9931 | 1106.6185 | 96.5913 | 100 | 74 | 8.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.3634 | 73.8366 | 0.21956 | 6.48 | NA | 29.087 | 314.16 | 580.14 | 616.6864 | -6.2996 | 90.7413 | 465.4232 | 93.7504 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8497 | 50.1503 | 0.28596 | NA | NA | 42.49 | 580.14 | 947 | 1074.778 | -13.4929 | 86.475 | 827.459 | 94.865 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.97 | 74.03 | 0.25809 | NA | 7.1 | 71.148 | 947 | 1354.21 | 1589.2915 | -17.3593 | 77.3529 | 1268.1457 | 94.3896
[11 empty] | 1998-05-10 | 11:00 | 4865.11 | 25.5556 | 100 | 70 | 8.6333 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.123 | 65.2437 | 0.24468 | 7.8 | 6.56 | 38.257 | 325.36 | 325.92 | 1379.95 | 1975.1879 | -43.1347 | 88.2618 | 1150.5539 | 96.6749 | 100 | 74 | 8.9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.5388 | 73.5612 | 0.22038 | 6.56 | NA | 29.382 | 325.92 | 586.08 | 640.6134 | -9.3048 | 90.9849 | 483.2667 | 93.9201 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.919 | 50.081 | 0.28636 | NA | NA | 43.68 | 586.08 | 965 | 1085.088 | -12.4444 | 86.5979 | 835.584 | 94.7725 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.2044 | 73.7956 | 0.25891 | NA | 7.2 | 71.995 | 965 | 1379.95 | 1619.8703 | -17.3862 | 77.9102 | 1292.4352 | 94.4295
[11 empty] | 1998-05-10 | 22:20 | 4876.2 | 25.5556 | 100 | 70 | 8.6667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 10.4811 | 65.8522 | 0.24242 | 7.3 | 6.67 | 38.056 | 310.42 | 309.12 | 1364.22 | 1863.2203 | -36.5777 | 87.6889 | 1086.1701 | 96.4963 | 100 | 74 | 9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.2853 | 73.7147 | 0.21992 | 6.67 | NA | 29.146 | 309.12 | 589.05 | 606.2353 | -2.9175 | 90.5713 | 457.6776 | 93.6318 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9839 | 50.0161 | 0.28673 | NA | NA | 42.21 | 589.05 | 954 | 1092.1428 | -14.4804 | 86.3451 | 840.5964 | 94.9786 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.0677 | 73.9323 | 0.25843 | NA | 7.1 | 70.994 | 954 | 1364.22 | 1601.5377 | -17.3959 | 77.0335 | 1277.7689 | 94.4439
[11 empty] | 1998-05-11 | 16:00 | 4893.86 | 25.5556 | 100 | 70 | 8.2 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.4585 | 65.3415 | 0.24432 | 7.3 | 6.82 | 41.339 | 304.61 | 337.68 | 1364.22 | 2036.7017 | -49.2942 | 87.7579 | 1187.1909 | 96.5179 | 100 | 72 | 8.2 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.7053 | 73.0947 | 0.22179 | 6.82 | NA | 30.267 | 337.68 | 590.04 | 663.9142 | -12.5202 | 91.0368 | 500.7971 | 93.9562 | 72 | 60 | 8.6 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.341 | 8.0086 | 49.3914 | 0.29035 | NA | NA | 45.01 | 590.04 | 954 | 1101.7008 | -15.4823 | 86.6708 | 845.8704 | 94.6789 | 115 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.0435 | 72.6565 | 0.26297 | NA | 7.2 | 72.765 | 954 | 1364.22 | 1600.239 | -17.3007 | 78.4515 | 1277.1195 | 94.3024
[11 empty] | 1998-05-12 | 8:00 | 4909.83 | 25.5556 | 100 | 70 | 8.6 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.8977 | 64.5023 | 0.2475 | 7.4 | 6.49 | 41.741 | 327.02 | 349.44 | 1435.72 | 2113.5809 | -47.214 | 88.0549 | 1231.5105 | 96.6106 | 100 | 72 | 9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.8411 | 72.1589 | 0.22466 | 6.49 | NA | 33.158 | 349.44 | 594.99 | 685.0862 | -15.1425 | 90.5111 | 517.2631 | 93.5897 | 72 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.0818 | 48.9182 | 0.29316 | NA | NA | 41.44 | 594.99 | 1004 | 1104.256 | -9.9857 | 88.141 | 849.623 | 95.1225 | 116 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.7606 | 72.4394 | 0.26376 | NA | 7.2 | 70.301 | 1004 | 1435.72 | 1688.7126 | -17.6213 | 79.8818 | 1346.3563 | 94.7784
[11 empty] | 1998-05-12 | 16:00 | 4921.64 | 25.5556 | 100 | 70 | 8.6 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.8222 | 64.5778 | 0.24721 | 7.4 | 6.64 | 40.334 | 303.78 | 346.08 | 1374.23 | 2099.0237 | -52.7418 | 88.3455 | 1222.5519 | 96.7008 | 100 | 72 | 9 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.8799 | 72.1201 | 0.22479 | 6.64 | NA | 27.258 | 346.08 | 582.12 | 684.4217 | -17.574 | 92.1238 | 515.2509 | 94.7098 | 72 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9001 | 49.0999 | 0.29208 | NA | NA | 41.02 | 582.12 | 961 | 1079.932 | -12.3759 | 88.1472 | 831.026 | 95.0639 | 114 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.1529 | 72.0471 | 0.26519 | NA | 7.2 | 71.764 | 961 | 1374.23 | 1613.1064 | -17.3826 | 79.2638 | 1287.0532 | 94.4242
[11 empty] | 1998-05-12 | 21:30 | 4923.55 | 25.5556 | 100 | 70 | 8.4 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.5313 | 65.0687 | 0.24534 | 7.4 | 6.54 | 41.138 | 320.38 | 339.36 | 1392.82 | 2049.1661 | -47.1235 | 87.8778 | 1194.2631 | 96.5554 | 100 | 70 | 8.4 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.7644 | 71.8356 | 0.22568 | 6.54 | NA | 28.084 | 339.36 | 587.07 | 669.6937 | -14.0739 | 91.7244 | 504.5269 | 94.4336 | 70 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9764 | 48.0236 | 0.29862 | NA | NA | 40.74 | 587.07 | 974 | 1089.6936 | -11.8782 | 87.995 | 838.3818 | 95.1406 | 114 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.3232 | 71.8768 | 0.26582 | NA | 7.1 | 72.303 | 974 | 1392.82 | 1635.2445 | -17.4053 | 78.6943 | 1304.6222 | 94.4579
[11 empty] | 1998-05-13 | 14:30 | 4940.41 | 25 | 100 | 70 | 8.6667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.7566 | 10.0429 | 66.2904 | 0.23769 | 7.3 | 6.49 | 38.056 | 292.99 | 309.96 | 1202.63 | 1774.7332 | -47.571 | 87.7223 | 1042.3466 | 96.349 | 100 | 74 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.6877 | 4.2157 | 73.7843 | 0.21262 | 6.49 | NA | 28.91 | 309.96 | 552.42 | 591.01 | -6.9856 | 90.673 | 450.485 | 93.5825 | 74 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 7.4736 | 50.5264 | 0.28853 | NA | NA | 40.53 | 552.42 | 841 | 1023.3588 | -21.6836 | 86.9241 | 787.8894 | 94.8559 | 118 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 10.4584 | 75.5416 | 0.25711 | NA | 7.1 | 69.069 | 841 | 1202.63 | 1388.822 | -15.4821 | 77.7168 | 1114.911 | 93.805
[11 empty] | 1998-05-13 | 22:30 | 4948.36 | 25 | 100 | 70 | 8.6 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.7566 | 10.3444 | 66.0556 | 0.23854 | 7.3 | 6.46 | 37.453 | 304.61 | 317.52 | 1189.76 | 1826.268 | -53.4989 | 88.2045 | 1071.894 | 96.5059 | 100 | 76 | 8.8 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.6877 | 4.3168 | 74.8832 | 0.2095 | 6.46 | NA | 29.736 | 317.52 | 541.53 | 605.304 | -11.7766 | 90.6349 | 461.412 | 93.5554 | 76 | 66 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 7.3299 | 54.6701 | 0.26666 | NA | NA | 39.48 | 541.53 | 832 | 1003.416 | -20.6029 | 87.5661 | 772.473 | 94.8891 | 118 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 10.3584 | 75.6416 | 0.25677 | NA | 7.1 | 67.452 | 832 | 1189.76 | 1374.5825 | -15.5344 | 78.7566 | 1103.2912 | 93.8863
[11 empty] | 1998-05-14 | 10:00 | 4959.95 | 25.5556 | 100 | 70 | 8.7 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.2911 | 66.0089 | 0.23482 | 7.4 | 6.85 | 38.056 | 333.66 | 316.68 | 1917.63 | 1817.6545 | 5.2135 | 87.9828 | 1067.1672 | 96.4339 | 100 | 76 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.3183 | 74.6817 | 0.20664 | 6.85 | NA | 28.792 | 316.68 | 550.44 | 604.568 | -9.8336 | 90.9082 | 460.624 | 93.7493 | 76 | 64 | 9.1 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.4621 | 53.4379 | 0.26837 | NA | NA | 39.34 | 550.44 | 1341 | 1020.652 | 23.8887 | 87.5774 | 785.546 | 94.992 | 118 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 17.2368 | 68.7632 | 0.27786 | NA | 7.1 | 68.761 | 1341 | 1917.63 | 2243.8793 | -17.0132 | 78.2869 | 1792.4396 | 96.1638
[11 empty] | 1998-05-14 | 15:30 | 4965.75 | 25.5556 | 100 | 70 | 8.7 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.4561 | 65.8439 | 0.23541 | 7.4 | 6.49 | 37.788 | 328.68 | 320.88 | 1813.24 | 1845.924 | -1.8025 | 88.2236 | 1083.402 | 96.5121 | 100 | 76 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.3654 | 74.6346 | 0.20677 | 6.49 | NA | 29.854 | 320.88 | 556.38 | 611.906 | -9.9799 | 90.6962 | 466.393 | 93.599 | 76 | 66 | 9.1 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.5294 | 54.3706 | 0.26376 | NA | NA | 40.67 | 556.38 | 1268 | 1030.8332 | 18.704 | 87.3255 | 793.6066 | 94.8753 | 118 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 16.2582 | 69.7418 | 0.27396 | NA | 7.1 | 67.991 | 1268 | 1813.24 | 2119.6193 | -16.8968 | 78.8111 | 1693.8096 | 95.9859
[11 empty] | 1998-05-14 | 22:30 | 4972.3 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.6 | 3.05 |  | 19.65 | 19.65 | 0.84478 | 0 | 15.2061 | 15.4072 | 10.0858 | 66.2475 | 0.23257 | 7.4 | 6.49 | 37.252 | 318.72 | 308.28 | 1768.91 | 1783.3832 | -0.8182 | 87.9162 | 1045.8316 | 96.438 | 100 | 76 | 9 | 9.9 | 9.75 | 19.65 | 19.65 | 0.48085 | 0.50382 | 15.2308 | 15.4322 | 4.2094 | 74.7906 | 0.20634 | 6.49 | NA | 29.087 | 308.28 | 552.42 | 591.7683 | -7.1229 | 90.5647 | 450.0241 | 93.5366 | 76 | 66 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.4787 | 54.5213 | 0.26304 | NA | NA | 40.18 | 552.42 | 1237 | 1023.6808 | 17.2449 | 86.9664 | 788.0504 | 94.9013 | 118 | 70 | 8 | 2.1 | 3.05 | 5.15 | 5.15 | 0.55322 | 0.40777 | 18 | 18.238 | 15.7218 | 70.2782 | 0.25951 | NA | 7.1 | 67.452 | 1237 | 1768.91 | 2042.2626 | -15.4532 | 78.1199 | 1639.6313 | 95.8861
[11 empty] | 1998-05-15 | 11:30 | 4985.72 | 25.5556 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.8012 | 64.4655 | 0.24044 | 7.4 | 6.46 | 39.195 | 343.62 | 351.12 | 1771.77 | 2087.5025 | -17.8202 | 88.8371 | 1219.3112 | 96.7855 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.815 | 74.985 | 0.2058 | 6.46 | NA | 31.211 | 351.12 | 731.61 | 674.2934 | 7.8343 | 91.111 | 512.7067 | 93.9125 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 10.0703 | 49.9297 | 0.28722 | NA | NA | 41.86 | 731.61 | 1239 | 1366.18 | -10.2647 | 88.0781 | 1048.895 | 96.0091 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.8943 | 70.1057 | 0.27254 | NA | 7.2 | 75.999 | 1239 | 1771.77 | 2091.8674 | -18.0665 | 78.3553 | 1665.4337 | 95.4367
[11 empty] | 1998-05-15 | 18:05 | 4992.05 | 25.5556 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.2601 | 64.0065 | 0.24216 | 7.4 | 6.42 | 39.664 | 382.63 | 363.72 | 1808.95 | 2167.6317 | -19.8282 | 89.0949 | 1265.6759 | 96.8662 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 5.0161 | 74.7839 | 0.20636 | 6.42 | NA | 30.444 | 363.72 | 734.58 | 700.3968 | 4.6534 | 91.6298 | 532.0584 | 94.2781 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 10.1127 | 49.8873 | 0.28747 | NA | NA | 41.93 | 734.58 | 1265 | 1371.818 | -8.4441 | 88.4719 | 1053.199 | 96.0188 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 16.2444 | 69.7556 | 0.27391 | NA | 7.3 | 76.384 | 1265 | 1808.95 | 2136.6517 | -18.1156 | 78.9992 | 1700.8259 | 95.509
[11 empty] | 1998-05-15 | 23:10 | 4997.12 | 25 | 100 | 70 | 9.5333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.7566 | 11.0569 | 64.4098 | 0.24463 | 7.3 | 6.46 | 38.324 | 317.06 | 337.68 | 1705.99 | 1950.3397 | -14.323 | 88.6508 | 1144.0099 | 96.65 | 100 | 76 | 9.8 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.6877 | 4.6439 | 73.5561 | 0.21328 | 6.46 | NA | 28.084 | 337.68 | 558.36 | 647.276 | -15.9245 | 91.6833 | 492.478 | 94.2974 | 76 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 7.547 | 50.653 | 0.28781 | NA | NA | 41.44 | 558.36 | 1193 | 1033.9264 | 13.3339 | 87.728 | 796.1432 | 94.7949 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 15.2118 | 69.7882 | 0.27831 | NA | 7.1 | 70.224 | 1193 | 1705.99 | 1989.8088 | -16.6366 | 79.204 | 1591.4044 | 95.5873
[11 empty] | 1998-05-16 | 7:20 | 5005.12 | 25.5556 | 100 | 70 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.5495 | 63.9172 | 0.2425 | 7.4 | 6.5 | 39.128 | 322.04 | 344.4 | 1844.7 | 2043.7475 | -10.7902 | 88.6388 | 1194.0737 | 96.7232 | 100 | 78 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7706 | 74.4294 | 0.20734 | 6.5 | NA | 27.435 | 344.4 | 560.34 | 664.5993 | -18.6064 | 92.034 | 504.4997 | 94.5619 | 78 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.5708 | 51.6292 | 0.27777 | NA | NA | 41.79 | 560.34 | 1290 | 1037.406 | 19.5809 | 87.8659 | 798.873 | 94.7689 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 16.6345 | 68.3655 | 0.27948 | NA | 7.1 | 72.842 | 1290 | 1844.7 | 2182.5825 | -18.3164 | 78.8496 | 1736.2913 | 95.8047
[11 empty] | 1998-05-16 | 15:00 | 5013.65 | 25.5556 | 100 | 70 | 9.5333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.7556 | 63.7111 | 0.24329 | 7.4 | 6.9 | 38.726 | 333.66 | 357 | 1807.52 | 2071.5728 | -14.6086 | 89.1524 | 1214.2864 | 96.8108 | 100 | 76 | 9.8 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.9399 | 73.2601 | 0.21065 | 6.9 | NA | 27.671 | 357 | 580.14 | 686.329 | -18.304 | 92.249 | 521.6645 | 94.6956 | 76 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.863 | 50.337 | 0.2849 | NA | NA | 41.58 | 580.14 | 1264 | 1075.6152 | 14.9039 | 88.3529 | 827.8776 | 94.9775 | 118 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 16.1466 | 68.8534 | 0.2775 | NA | 7.1 | 72.226 | 1264 | 1807.52 | 2109.7751 | -16.7221 | 79.7686 | 1686.8875 | 95.7184
[11 empty] | 1998-05-17 | 7:00 | 5028.14 | 25.5556 | 100 | 70 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.9359 | 63.5308 | 0.24398 | 7.4 | 6.46 | 38.994 | 340.3 | 354.48 | 1801.8 | 2110.6854 | -17.1432 | 88.9997 | 1232.5827 | 96.8364 | 100 | 76 | 9.8 | 10.5 | 9.2 | 19.7 | 19.7 | 0.47267 | 0.53299 | 16.1538 | 16.3675 | 5.1497 | 73.0503 | 0.22406 | 6.46 | NA | 26.609 | 354.48 | 558.36 | 728.6806 | -30.5037 | 92.4935 | 541.5803 | 95.0868 | 76 | 60 | 9.8 | 4 | 5 | 9 | 9 | 0.45795 | 0.44444 | 12.3077 | 12.4704 | 7.2271 | 50.9729 | 0.24465 | NA | NA | 42.14 | 558.36 | 1260 | 971.336 | 22.9098 | 88.1122 | 764.848 | 94.4904 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 16.2561 | 68.7439 | 0.27794 | NA | 7.1 | 70.532 | 1260 | 1801.8 | 2132.2765 | -18.3415 | 80.1027 | 1696.1383 | 95.8416
[11 empty] | 1998-05-17 | 14:10 | 5036.06 | 25.5556 | 100 | 70 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4834 | 63.9833 | 0.24225 | 7.4 | 6.45 | 39.195 | 346.94 | 342.72 | 1798.94 | 2032.3425 | -12.9744 | 88.5636 | 1187.5312 | 96.6995 | 100 | 76 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7516 | 73.4484 | 0.21011 | 6.45 | NA | 27.022 | 342.72 | 566.28 | 661.6394 | -16.8396 | 92.1154 | 502.1797 | 94.6191 | 76 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.6504 | 50.5496 | 0.2837 | NA | NA | 42.28 | 566.28 | 1258 | 1048.36 | 16.6645 | 87.6634 | 807.32 | 94.7629 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 16.2214 | 68.7786 | 0.2778 | NA | 7.1 | 71.071 | 1258 | 1798.94 | 2128.4146 | -18.3149 | 79.2627 | 1693.2073 | 95.8026
[11 empty] | 1998-05-17 | 23:00 | 5044.84 | 25.5556 | 100 | 70 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4426 | 64.0241 | 0.2421 | 7.4 | 6.57 | 38.592 | 325.36 | 341.04 | 1724.58 | 2024.6672 | -17.4006 | 88.684 | 1182.8536 | 96.7374 | 100 | 78 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7121 | 74.4879 | 0.20718 | 6.57 | NA | 27.966 | 341.04 | 563.31 | 657.3086 | -16.6868 | 91.7998 | 499.1743 | 94.3975 | 78 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.6295 | 51.5705 | 0.27809 | NA | NA | 40.74 | 563.31 | 1206 | 1044.0744 | 13.4267 | 88.0542 | 803.6922 | 94.9309 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.5517 | 69.4483 | 0.27512 | NA | 7.1 | 68.068 | 1206 | 1724.58 | 2040.4835 | -18.3177 | 80.0411 | 1623.2417 | 95.8067
[11 empty] | 1998-05-18 | 8:30 | 5054.47 | 25.5556 | 100 | 70 | 8.6 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3177 | 65.0823 | 0.23816 | 7.5 | 6.58 | 35.175 | 307.93 | 334.32 | 1701.7 | 1999.5605 | -17.5037 | 89.4786 | 1166.9403 | 96.9857 | 100 | 75 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.5772 | 74.1228 | 0.2082 | 6.58 | NA | 30.208 | 334.32 | 659.34 | 641.5352 | 2.7004 | 90.9643 | 487.9276 | 93.8089 | 75 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.0387 | 49.4613 | 0.28994 | NA | NA | 40.25 | 659.34 | 1190 | 1228.9028 | -3.2691 | 87.9606 | 944.1214 | 95.7368 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.3099 | 70.6901 | 0.27029 | NA | 7.2 | 69.762 | 1190 | 1701.7 | 2011.5079 | -18.2058 | 79.1332 | 1600.7539 | 95.6419
[11 empty] | 1998-05-18 | 15:30 | 5061.42 | 25.5556 | 100 | 70 | 8.8667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.6002 | 64.5332 | 0.24019 | 7.4 | 6.9 | 37.788 | 318.72 | 344.4 | 1716 | 2051.2068 | -19.5342 | 89.0279 | 1197.8034 | 96.8452 | 100 | 78 | 8.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7413 | 75.4587 | 0.20451 | 6.9 | NA | 29.382 | 344.4 | 587.07 | 662.6325 | -12.8711 | 91.4686 | 503.5162 | 94.1646 | 78 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9948 | 51.2052 | 0.28007 | NA | NA | 39.48 | 587.07 | 1200 | 1090.8528 | 9.0956 | 88.5366 | 838.9614 | 95.2942 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.4624 | 70.5376 | 0.27087 | NA | 7.2 | 68.607 | 1200 | 1716 | 2029.6882 | -18.2802 | 80.0793 | 1614.8441 | 95.7515
[11 empty] | 1998-05-18 | 23:50 | 5069.72 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4105 | 64.9229 | 0.23874 | 7.3 | 6.53 | 35.242 | 325.36 | 336.84 | 1633.06 | 2015.7355 | -23.433 | 89.5375 | 1176.2878 | 97.004 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6231 | 75.3769 | 0.20473 | 6.53 | NA | 29.677 | 336.84 | 558.36 | 647.1373 | -15.8997 | 91.1896 | 491.9887 | 93.968 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.5552 | 52.4448 | 0.27345 | NA | NA | 40.88 | 558.36 | 1142 | 1034.4416 | 9.4184 | 87.8637 | 796.4008 | 94.8669 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.6592 | 71.3408 | 0.26782 | NA | 7.1 | 69.377 | 1142 | 1633.06 | 1928.5902 | -18.0967 | 79.4036 | 1535.2951 | 95.4812
[11 empty] | 1998-05-19 | 23:10 | 5093.06 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.0529 | 64.2805 | 0.24113 | 7.3 | 6.9 | 39.262 | 317.06 | 357.84 | 1518.66 | 2131.2575 | -40.338 | 89.0281 | 1244.5488 | 96.8453 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8841 | 75.1159 | 0.20545 | 6.9 | NA | 33.335 | 357.84 | 568.26 | 685.6563 | -20.6589 | 90.6844 | 521.7481 | 93.6109 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.6905 | 52.3094 | 0.27416 | NA | NA | 41.51 | 568.26 | 1062 | 1052.87 | 0.8597 | 88.3998 | 810.565 | 94.8789 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.5732 | 72.4268 | 0.2638 | NA | 7.1 | 68.838 | 1062 | 1518.66 | 1790.3188 | -17.8881 | 80.7629 | 1426.1594 | 95.1732
[11 empty] | 1998-05-19 | 8:00 | 5077.94 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3828 | 64.9506 | 0.23864 | 7.4 | 6.47 | 37.654 | 328.68 | 338.52 | 1670.24 | 2013.3407 | -20.542 | 88.8769 | 1175.9304 | 96.7979 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6671 | 75.3329 | 0.20485 | 6.47 | NA | 28.438 | 338.52 | 587.07 | 651.7661 | -11.0202 | 91.5993 | 495.1431 | 94.2566 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9958 | 52.0042 | 0.27577 | NA | NA | 39.41 | 587.07 | 1168 | 1090.9172 | 6.5996 | 88.3581 | 838.9936 | 95.3027 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.9398 | 71.0602 | 0.26888 | NA | 7.2 | 74.844 | 1168 | 1670.24 | 1969.6477 | -17.926 | 77.8908 | 1568.8239 | 95.2293
[11 empty] | 1998-05-19 | 17:00 | 5087.13 | 25.5556 | 100 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.7947 | 64.5386 | 0.24017 | 7.3 | 6.94 | 38.525 | 322.04 | 350.28 | 1798.94 | 2085.7162 | -15.9414 | 89.0017 | 1217.9981 | 96.837 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8591 | 75.1409 | 0.20538 | 6.94 | NA | 27.435 | 350.28 | 580.14 | 676.4193 | -16.5959 | 92.1677 | 513.3497 | 94.6557 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8834 | 52.1166 | 0.27517 | NA | NA | 40.18 | 580.14 | 1258 | 1076.9032 | 14.3956 | 88.5292 | 828.5216 | 95.1504 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 16.2056 | 69.7944 | 0.27375 | NA | 7.2 | 72.226 | 1258 | 1798.94 | 2127.5676 | -18.2678 | 79.3805 | 1692.7838 | 95.7333
[11 empty] | 1998-05-20 | 11:00 | 5105.31 | 25.5556 | 100 | 70 | 8.8667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4184 | 64.7149 | 0.23951 | 7.3 | 6.91 | 38.391 | 305.44 | 340.2 | 1786.07 | 2020.2701 | -13.1126 | 88.7152 | 1180.2351 | 96.7472 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6994 | 75.1006 | 0.20549 | 6.91 | NA | 27.966 | 340.2 | 680.13 | 655.6201 | 3.6037 | 91.7795 | 497.91 | 94.3833 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.3596 | 50.4404 | 0.28432 | NA | NA | 39.06 | 680.13 | 1249 | 1269.9144 | -1.6745 | 88.5185 | 975.0222 | 95.9939 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 16.1089 | 69.6911 | 0.27416 | NA | 7.1 | 70.301 | 1249 | 1786.07 | 2113.3793 | -18.3257 | 79.3354 | 1681.1896 | 95.8184
[11 empty] | 1998-05-20 | 17:00 | 5111.52 | 25.5556 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.6282 | 64.6384 | 0.2398 | 7.3 | 6.85 | 38.726 | 323.7 | 346.08 | 1773.2 | 2057.0173 | -16.0059 | 88.8101 | 1201.5486 | 96.777 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7933 | 75.2067 | 0.2052 | 6.85 | NA | 27.612 | 346.08 | 586.08 | 667.7977 | -13.9431 | 92.0215 | 506.9388 | 94.5532 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9824 | 51.8176 | 0.27676 | NA | NA | 39.34 | 586.08 | 1240 | 1089.0808 | 12.1709 | 88.6327 | 837.5804 | 95.3031 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.9743 | 70.0257 | 0.27285 | NA | 7.1 | 71.148 | 1240 | 1773.2 | 2097.1581 | -18.2697 | 79.4417 | 1668.5791 | 95.736
[11 empty] | 1998-05-20 | 23:10 | 5117.07 | 25.5556 | 100 | 70 | 8.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3358 | 64.9309 | 0.23872 | 7.3 | 6.86 | 38.056 | 312.08 | 337.68 | 1598.74 | 2005.5869 | -25.448 | 88.7302 | 1171.6335 | 96.7519 | 100 | 78 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6553 | 75.3447 | 0.20482 | 6.86 | NA | 28.379 | 337.68 | 629.64 | 650.1371 | -3.2554 | 91.5959 | 493.9086 | 94.2542 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6163 | 51.1837 | 0.28019 | NA | NA | 39.48 | 629.64 | 1118 | 1172.5872 | -4.8826 | 88.3085 | 901.1136 | 95.6188 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.328 | 71.672 | 0.26658 | NA | 7.1 | 69.608 | 1118 | 1598.74 | 1886.8208 | -18.0192 | 79.3864 | 1502.4104 | 95.3669
[11 empty] | 1998-05-21 | 7:30 | 5125.58 | 25.5556 | 100 | 70 | 9.2667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3699 | 64.3634 | 0.24082 | 7.4 | 6.81 | 36.314 | 318.72 | 336.84 | 1691.69 | 2009.7681 | -18.8024 | 89.2192 | 1173.304 | 96.905 | 100 | 78 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6773 | 74.5227 | 0.20708 | 6.81 | NA | 26.078 | 336.84 | 619.74 | 650.773 | -5.0074 | 92.258 | 493.8065 | 94.719 | 78 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.4616 | 50.7384 | 0.28265 | NA | NA | 40.18 | 619.74 | 1183 | 1152.9352 | 2.5414 | 88.0715 | 886.3376 | 95.4667 | 118 | 70 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.2079 | 70.5921 | 0.27066 | NA | 7.2 | 70.224 | 1183 | 1691.69 | 1999.0357 | -18.168 | 79.1521 | 1591.0179 | 95.5862
[11 empty] | 1998-05-21 | 18:45 | 5136.55 | 25.5556 | 100 | 70 | 9.2 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.6331 | 64.1669 | 0.24156 | 7.4 | 6.66 | 36.917 | 323.7 | 344.4 | 1698.84 | 2056.0554 | -21.027 | 89.2808 | 1200.2277 | 96.9242 | 100 | 78 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7786 | 74.4214 | 0.20736 | 6.66 | NA | 26.904 | 344.4 | 618.75 | 665.1358 | -7.4967 | 92.1882 | 504.7679 | 94.67 | 78 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.4389 | 50.7611 | 0.28252 | NA | NA | 40.74 | 618.75 | 1188 | 1150.5192 | 3.1549 | 88.1707 | 884.6346 | 95.3947 | 118 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.2668 | 70.7332 | 0.27012 | NA | 7.2 | 70.917 | 1188 | 1698.84 | 2007.1942 | -18.1509 | 79.4085 | 1597.5971 | 95.561
[11 empty] | 1998-05-21 | 23:45 | 5141.63 | 25.5556 | 100 | 70 | 9.4333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3155 | 64.2512 | 0.24124 | 7.4 | 6.63 | 38.592 | 305.44 | 337.68 | 1578.72 | 2002.6032 | -26.8498 | 88.5714 | 1170.1416 | 96.7019 | 100 | 78 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6349 | 74.5651 | 0.20696 | 6.63 | NA | 29.736 | 337.68 | 609.84 | 648.7663 | -6.383 | 91.194 | 493.2231 | 93.9711 | 78 | 60 | 9.5 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.2894 | 51.2106 | 0.28004 | NA | NA | 42.07 | 609.84 | 1104 | 1132.1884 | -2.5533 | 87.5415 | 871.0142 | 95.17 | 118 | 70 | 9 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.0967 | 70.9033 | 0.26947 | NA | 7.1 | 72.534 | 1104 | 1578.72 | 1860.4084 | -17.8428 | 78.5199 | 1482.2042 | 95.1063
[11 empty] | 1998-05-22 | 10:45 | 5152.81 | 25 | 100 | 70 | 8.9667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.6623 | 11.1401 | 64.8933 | 0.24135 | 7.4 | 6.65 | 36.046 | 329.51 | 331.8 | 1590.16 | 1968.3055 | -23.7803 | 89.1362 | 1150.0527 | 96.8657 | 100 | 78 | 9.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.6877 | 4.5888 | 75.2112 | 0.20858 | 6.65 | NA | 27.966 | 331.8 | 668.25 | 641.8986 | 3.9433 | 91.5714 | 486.8493 | 94.2557 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 9.1821 | 50.6179 | 0.28801 | NA | NA | 39.34 | 668.25 | 1112 | 1246.8472 | -12.1265 | 88.1435 | 957.5486 | 95.8916 | 115 | 70 | 8.5 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.54 | 14.0681 | 69.9319 | 0.26512 | NA | 7.1 | 69.916 | 1112 | 1590.16 | 1841.4588 | -15.8034 | 78.9283 | 1476.7294 | 95.2655
[11 empty] | 1998-05-22 | 18:35 | 5160.34 | 25.5556 | 100 | 70 | 8.9667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.4072 | 10.8984 | 65.1349 | 0.23654 | 7.4 | 6.58 | 36.582 | 323.7 | 325.92 | 1630.2 | 1926.9236 | -18.2017 | 88.7758 | 1126.4218 | 96.7524 | 100 | 78 | 9.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 4.4929 | 75.3071 | 0.20492 | 6.58 | NA | 28.438 | 325.92 | 682.11 | 629.5356 | 7.7076 | 91.2745 | 477.7278 | 94.0472 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.3987 | 50.4012 | 0.28454 | NA | NA | 38.36 | 682.11 | 1140 | 1274.36 | -11.786 | 88.2302 | 978.235 | 96.0787 | 115 | 70 | 8.5 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.238 | 14.4493 | 69.5507 | 0.26223 | NA | 7.1 | 69.685 | 1140 | 1630.2 | 1889.2205 | -15.8889 | 78.619 | 1514.6102 | 95.3991
[11 empty] | 1998-05-23 | 0:05 | 5165.62 | 25.5556 | 100 | 70 | 8.9667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.4072 | 11.5615 | 64.4719 | 0.23898 | 7.4 | 6.56 | 35.778 | 318.72 | 342.72 | 1624.48 | 2041.1324 | -25.6484 | 89.5606 | 1191.9262 | 96.9983 | 100 | 78 | 9.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 4.7359 | 75.0641 | 0.20559 | 6.56 | NA | 29.146 | 342.72 | 636.57 | 662.7594 | -4.1141 | 91.4957 | 502.7397 | 94.2026 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.7288 | 51.0712 | 0.2808 | NA | NA | 38.71 | 636.57 | 1136 | 1186.6012 | -4.4543 | 88.7051 | 911.5856 | 95.7536 | 118 | 70 | 8.5 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.238 | 14.363 | 71.137 | 0.25638 | NA | 7.1 | 72.072 | 1136 | 1624.48 | 1880.7496 | -15.7755 | 78.9706 | 1508.3748 | 95.2219
[11 empty] | 1998-05-23 | 7:00 | 5172.85 | 24.4444 | 100 | 70 | 9 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.9216 | 11.0603 | 64.9397 | 0.24518 | 7.4 | 6.46 | 35.644 | 322.87 | 329.28 | 1610.18 | 1954.0659 | -21.357 | 89.1752 | 1141.6729 | 96.8779 | 100 | 78 | 9.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 4.5401 | 75.2599 | 0.2119 | 6.46 | NA | 28.674 | 329.28 | 651.42 | 636.0841 | 2.3542 | 91.2919 | 482.682 | 94.0594 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.9568 | 51.0432 | 0.29034 | NA | NA | 37.94 | 651.42 | 1126 | 1215.8216 | -7.9771 | 88.4779 | 933.6208 | 95.9363 | 118 | 70 | 8.8 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 14.2478 | 70.9522 | 0.26563 | NA | 7.2 | 70.609 | 1126 | 1610.18 | 1864.7737 | -15.8115 | 78.5565 | 1495.3869 | 95.2782
[11 empty] | 1998-05-24 | 0:05 | 5189.88 | 24.4444 | 100 | 70 | 8.9667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.9216 | 11.3035 | 64.7298 | 0.24597 | 7.4 | 6.38 | 37.587 | 328.68 | 337.68 | 1640.21 | 1998.1946 | -21.8255 | 88.869 | 1167.9373 | 96.7818 | 100 | 78 | 9.1 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 4.6607 | 75.2393 | 0.21196 | 6.38 | NA | 29.087 | 337.68 | 670.23 | 652.6357 | 2.6251 | 91.3862 | 495.1579 | 94.1257 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.2243 | 50.7757 | 0.29187 | NA | NA | 38.43 | 670.23 | 1147 | 1251.486 | -9.1095 | 88.6194 | 960.858 | 96.0004 | 118 | 70 | 8.8 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 14.5136 | 70.6864 | 0.26663 | NA | 7.2 | 71.918 | 1147 | 1640.21 | 1899.5574 | -15.8118 | 78.7023 | 1523.2787 | 95.2787
[11 empty] | 1998-05-24 | 13:30 | 5203.68 | 24.4444 | 100 | 70 | 8.8667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.9216 | 11.5894 | 64.5439 | 0.24668 | 7.4 | 6.4 | 36.716 | 314.57 | 344.4 | 1621.62 | 2046.9181 | -26.2267 | 89.3391 | 1195.6591 | 96.9292 | 100 | 78 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 4.7684 | 75.2316 | 0.21198 | 6.4 | NA | 28.674 | 344.4 | 656.37 | 666.6358 | -1.564 | 91.6742 | 505.5179 | 94.3278 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.025 | 50.975 | 0.29073 | NA | NA | 38.22 | 656.37 | 1134 | 1225.068 | -8.0307 | 88.9024 | 940.719 | 95.9372 | 118 | 70 | 8.6 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 14.3485 | 71.0515 | 0.26526 | NA | 7.1 | 71.148 | 1134 | 1621.62 | 1877.9964 | -15.8099 | 79.3415 | 1505.9982 | 95.2757
[11 empty] | 1998-05-24 | 18:35 | 5208.41 | 24.4444 | 100 | 70 | 8.8667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.9216 | 11.959 | 64.1743 | 0.2481 | 7.4 | 6.38 | 36.984 | 315.4 | 354.48 | 1623.05 | 2111.2912 | -30.0817 | 89.5667 | 1232.8856 | 97.0002 | 100 | 78 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 4.9207 | 75.0793 | 0.21241 | 6.38 | NA | 28.674 | 354.48 | 638.55 | 687.0036 | -7.5881 | 91.911 | 520.7418 | 94.4936 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.7628 | 51.2372 | 0.28924 | NA | NA | 38.36 | 638.55 | 1135 | 1190.7248 | -4.9097 | 89.1785 | 914.6374 | 95.806 | 118 | 70 | 8.6 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 14.3433 | 71.0567 | 0.26524 | NA | 7.1 | 72.534 | 1135 | 1623.05 | 1878.7262 | -15.7528 | 79.5379 | 1506.8631 | 95.1864
[11 empty] | 1998-05-25 | 0:04 | 5212.58 | 24.4444 | 100 | 70 | 8.8667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.9216 | 11.1744 | 64.9589 | 0.2451 | 7.4 | 6.4 | 37.654 | 325.36 | 334.32 | 1630.2 | 1975.8719 | -21.2043 | 88.7371 | 1155.0959 | 96.7402 | 100 | 78 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 4.6055 | 75.3945 | 0.21152 | 6.4 | NA | 29.382 | 334.32 | 647.46 | 645.5454 | 0.29571 | 91.2114 | 489.9327 | 94.0028 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 8.8949 | 51.1051 | 0.28999 | NA | NA | 38.22 | 647.46 | 1140 | 1207.9608 | -5.9615 | 88.5678 | 927.7104 | 95.8802 | 118 | 70 | 8.6 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 14.416 | 70.984 | 0.26551 | NA | 7.1 | 72.149 | 1140 | 1630.2 | 1887.4957 | -15.7831 | 78.4192 | 1513.7478 | 95.2338
[11 empty] | 1998-05-25 | 13:30 | 5227.81 | 25 | 100 | 70 | 8.8 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.6623 | 11.4693 | 64.7307 | 0.24196 | 7.4 | 6.51 | 37.386 | 318.72 | 341.88 | 1633.06 | 2026.7468 | -24.1073 | 89.0646 | 1184.3134 | 96.8432 | 100 | 78 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.6877 | 4.7277 | 75.2723 | 0.20841 | 6.51 | NA | 28.851 | 341.88 | 641.52 | 661.3632 | -3.0932 | 91.5611 | 501.6216 | 94.2485 | 78 | 60 | 8.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 8.802 | 51.398 | 0.28364 | NA | NA | 38.64 | 641.52 | 1142 | 1196.1696 | -4.7434 | 88.6978 | 918.8448 | 95.7947 | 118 | 70 | 8.6 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.54 | 14.4461 | 70.9539 | 0.2613 | NA | 7.2 | 71.918 | 1142 | 1633.06 | 1891.0574 | -15.7984 | 78.964 | 1516.5287 | 95.2577
[11 empty] | 1998-05-25 | 16:00 | 5229.95 | 25 | 100 | 70 | 8.8 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.6623 | 11.5945 | 64.6055 | 0.24243 | 7.4 | 6.46 | 36.582 | 323.7 | 344.4 | 1644.5 | 2047.6596 | -24.5156 | 89.378 | 1196.0298 | 96.9414 | 100 | 78 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.6877 | 4.7595 | 75.2405 | 0.2085 | 6.46 | NA | 29.264 | 344.4 | 645.48 | 666.0336 | -3.1842 | 91.5029 | 505.2168 | 94.2076 | 78 | 60 | 8.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 8.866 | 51.334 | 0.28399 | NA | NA | 38.22 | 645.48 | 1150 | 1204.1592 | -4.7095 | 88.9024 | 924.8196 | 95.8673 | 118 | 70 | 8.6 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.54 | 14.5458 | 70.8542 | 0.26166 | NA | 7.2 | 72.534 | 1150 | 1644.5 | 1904.2262 | -15.7936 | 78.939 | 1527.1131 | 95.2503
[11 empty] | 1998-05-26 | 13:00 | 5238.78 | 24.4444 | 100 | 70 | 8.8333 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.9216 | 11.7073 | 64.4594 | 0.247 | 7.4 | 6.41 | 37.788 | 315.4 | 348.6 | 1624.48 | 2068.4264 | -27.3285 | 89.1601 | 1208.5132 | 96.8732 | 100 | 78 | 9 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.9474 | 4.8265 | 75.1735 | 0.21214 | 6.41 | NA | 29.028 | 348.6 | 656.37 | 674.7611 | -2.8019 | 91.673 | 511.6806 | 94.3269 | 78 | 60 | 8.9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.8198 | 9.0229 | 51.0771 | 0.29015 | NA | NA | 38.36 | 656.37 | 1136 | 1224.9392 | -7.8292 | 88.996 | 940.6546 | 95.922 | 118 | 70 | 8.6 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.847 | 14.3537 | 71.0463 | 0.26528 | NA | 7.2 | 72.765 | 1136 | 1624.48 | 1880.2645 | -15.7456 | 79.1265 | 1508.1323 | 95.1752
[11 empty] | 1998-05-26 | 8:50 | 5247.03 | 25.5556 | 100 | 70 | 9.1667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.4072 | 10.9363 | 64.8971 | 0.23741 | 7.6 | 6.42 | 35.577 | 288.84 | 325.92 | 1409.98 | 1932.4846 | -37.0576 | 89.0841 | 1129.2023 | 96.8494 | 100 | 78 | 9.5 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 4.5009 | 74.9991 | 0.20576 | 6.42 | NA | 27.907 | 325.92 | 595.98 | 630.0776 | -5.7213 | 91.4375 | 477.9988 | 94.1617 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.1106 | 51.6894 | 0.27745 | NA | NA | 40.46 | 595.98 | 986 | 1107.0584 | -12.2777 | 87.5859 | 851.5192 | 95.2485 | 118 | 70 | 8.8 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.238 | 12.4046 | 72.7954 | 0.25054 | NA | 7.4 | 67.144 | 986 | 1409.98 | 1629.1992 | -15.5477 | 79.3986 | 1307.5996 | 94.8651
[11 empty] | 1998-05-26 | 20:00 | 5257.53 | 25.5556 | 100 | 70 | 9.2 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.4072 | 10.9694 | 64.8306 | 0.23765 | 7.6 | 6.42 | 38.056 | 333.66 | 329.28 | 1397.11 | 1940.7195 | -38.9096 | 88.4427 | 1134.9997 | 96.647 | 100 | 78 | 9.6 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 4.5615 | 74.8385 | 0.20621 | 6.42 | NA | 27.258 | 329.28 | 614.79 | 637.5293 | -3.6987 | 91.7219 | 483.4046 | 94.3612 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.3893 | 51.4107 | 0.27895 | NA | NA | 40.18 | 614.79 | 977 | 1143.4312 | -17.0349 | 87.7976 | 879.1106 | 95.4295 | 118 | 70 | 8.8 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.238 | 12.2404 | 72.9596 | 0.24997 | NA | 7.3 | 70.301 | 977 | 1397.11 | 1611.6893 | -15.3588 | 78.6501 | 1294.3447 | 94.5686
[11 empty] | 1998-05-27 | 0:05 | 5261.62 | 25.5556 | 100 | 70 | 9.1667 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.4072 | 11.3262 | 64.5071 | 0.23884 | 7.6 | 6.43 | 36.984 | 323.7 | 337.68 | 1405.69 | 2001.5312 | -42.3878 | 89.0476 | 1169.6056 | 96.8379 | 100 | 78 | 9.5 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 4.683 | 74.817 | 0.20627 | 6.43 | NA | 27.612 | 337.68 | 605.88 | 654.1412 | -7.9655 | 91.823 | 495.9106 | 94.4321 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.2623 | 51.5377 | 0.27826 | NA | NA | 39.97 | 605.88 | 983 | 1126.5172 | -14.5999 | 88.1633 | 866.1986 | 95.3856 | 118 | 70 | 8.8 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.238 | 12.31 | 72.89 | 0.25021 | NA | 7.4 | 71.148 | 983 | 1405.69 | 1621.2964 | -15.3381 | 78.9303 | 1302.1482 | 94.5361
[11 empty] | 1998-05-27 | 8:40 | 5270.66 | 25.5556 | 100 | 70 | 9.3667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 10.2252 | 65.4081 | 0.24407 | 7.4 | 6.42 | 36.515 | 296.31 | 307.44 | 1186.9 | 1810.6368 | -52.5518 | 88.1229 | 1059.0384 | 96.5521 | 100 | 78 | 9.6 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.2087 | 75.1913 | 0.2156 | 6.42 | NA | 31.506 | 307.44 | 554.4 | 597.3101 | -7.7399 | 89.7521 | 452.375 | 93.0354 | 78 | 60 | 9.5 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.341 | 7.5466 | 51.9534 | 0.27604 | NA | NA | 40.81 | 554.4 | 830 | 1036.5457 | -24.885 | 86.7259 | 795.4729 | 94.8697 | 120 | 70 | 9 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.2906 | 75.7094 | 0.25237 | NA | 7.3 | 70.455 | 830 | 1186.9 | 1369.0319 | -15.3452 | 77.0833 | 1099.516 | 93.5922
[11 empty] | 1998-05-27 | 16:00 | 5278.32 | 25 | 100 | 70 | 8.7333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.7566 | 11.7147 | 64.552 | 0.24409 | 7.2 | 6.55 | 38.994 | 338.64 | 356.16 | 1903.33 | 2064.7639 | -8.4817 | 89.0515 | 1210.462 | 96.7786 | 100 | 78 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.6877 | 4.8999 | 75.1001 | 0.20889 | 6.55 | NA | 29.5 | 356.16 | 696.96 | 682.82 | 2.0288 | 91.7172 | 519.49 | 94.3214 | 78 | 60 | 9 | 4.6 | 4.9 | 9.5 | 9.5 | 0.47104 | 0.48421 | 14.1538 | 14.5785 | 9.6434 | 50.3566 | 0.2895 | NA | NA | 40.67 | 696.96 | 1331 | 1313.069 | 1.3472 | 88.581 | 1005.0145 | 95.9533 | 118 | 70 | 8.2 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 17.0241 | 68.7759 | 0.28241 | NA | 7.1 | 74.459 | 1331 | 1903.33 | 2222.7388 | -16.7816 | 79.0939 | 1776.8694 | 95.8095
[11 empty] | 1998-05-28 | 0:20 | 5286.56 | 25.5556 | 100 | 70 | 9.2 | 0 | 16.6 | 3.1 |  | 19.7 | 19.7 | 0.84264 | 0 | 15.2061 | 15.4072 | 11.5225 | 64.2775 | 0.2397 | 7.2 | 6.45 | 37.788 | 313.74 | 351.12 | 1452.88 | 2028.9623 | -39.6511 | 89.2379 | 1190.0412 | 96.8246 | 100 | 78 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8221 | 74.5779 | 0.20693 | 6.45 | NA | 30.739 | 351.12 | 686.07 | 674.7702 | 1.647 | 91.2454 | 512.9451 | 94.0074 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.4249 | 50.3751 | 0.28468 | NA | NA | 40.53 | 686.07 | 1016 | 1279.9668 | -25.981 | 88.4569 | 983.0184 | 95.877 | 118 | 70 | 8.8 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.238 | 12.6179 | 72.5821 | 0.25127 | NA | 7.1 | 73.458 | 1016 | 1452.88 | 1654.4962 | -13.877 | 79.0789 | 1335.2481 | 94.4986
[11 empty] | 1998-05-28 | 8:00 | 5293.83 | 25.5556 | 100 | 70 | 8.8667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.3361 | 64.7972 | 0.23921 | 7.4 | 6.43 | 38.324 | 332.83 | 345.24 | 1322.75 | 1998.6262 | -51.0963 | 88.8993 | 1171.9331 | 96.7298 | 100 | 78 | 9 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.7219 | 75.2781 | 0.205 | 6.43 | NA | 30.444 | 345.24 | 651.42 | 660.036 | -1.3226 | 91.1818 | 502.638 | 93.9432 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.9251 | 51.0749 | 0.28078 | NA | NA | 40.11 | 651.42 | 925 | 1213.8252 | -31.2243 | 88.382 | 932.6226 | 95.6992 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.5182 | 73.8818 | 0.25861 | NA | 7.2 | 74.844 | 925 | 1322.75 | 1528.3365 | -15.5424 | 78.3212 | 1226.6683 | 93.8986
[11 empty] | 1998-05-28 | 14:30 | 5300.26 | 25 | 100 | 70 | 8.9333 | 0 | 16.6 | 3.1 |  | 19.7 | 19.7 | 0.84264 | 0 | 15.2061 | 15.6623 | 11.4545 | 64.6122 | 0.2424 | 7.3 | 6.47 | 37.118 | 337.81 | 348.6 | 1497.21 | 2016.5359 | -34.6862 | 89.3523 | 1182.5679 | 96.8612 | 100 | 78 | 9.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.6877 | 4.7957 | 75.0043 | 0.20916 | 6.47 | NA | 29.972 | 348.6 | 660.33 | 670.4793 | -1.537 | 91.4022 | 509.5397 | 94.1178 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 9.0603 | 50.9397 | 0.28619 | NA | NA | 39.76 | 660.33 | 1047 | 1231.2544 | -17.5983 | 88.5944 | 945.7922 | 95.7961 | 118 | 70 | 8.6 | 2.1 | 3.1 | 5.2 | 5.2 | 0.55997 | 0.40385 | 18 | 18.54 | 13.0226 | 72.3774 | 0.25616 | NA | 7.1 | 74.228 | 1047 | 1497.21 | 1705.9746 | -13.9436 | 78.7068 | 1376.4873 | 94.6074
[11 empty] | 1998-05-28 | 23:45 | 5309.71 | 25 | 100 | 70 | 8.9333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.7566 | 11.1933 | 64.8733 | 0.24288 | 7.4 | 6.48 | 37.989 | 318.72 | 341.04 | 1462.89 | 1973.6051 | -34.9114 | 88.8608 | 1157.3225 | 96.7175 | 100 | 78 | 9.2 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.6877 | 4.6625 | 75.1375 | 0.20879 | 6.48 | NA | 30.208 | 341.04 | 646.47 | 651.872 | -0.83561 | 91.1424 | 496.456 | 93.9153 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 8.8621 | 51.1379 | 0.28508 | NA | NA | 39.48 | 646.47 | 1023 | 1204.9008 | -17.7811 | 88.4236 | 925.6854 | 95.7351 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 12.8606 | 72.5394 | 0.26776 | NA | 7.1 | 73.766 | 1023 | 1462.89 | 1696.6499 | -15.9793 | 78.3703 | 1359.825 | 94.5753
[11 empty] | 1998-05-29 | 15:45 | 5325.62 | 25 | 100 | 70 | 9 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.7566 | 10.8345 | 65.1655 | 0.24179 | 7.3 | 6.52 | 36.783 | 312.08 | 330.12 | 1441.44 | 1910.3548 | -32.531 | 88.8577 | 1120.2374 | 96.7165 | 100 | 78 | 9.2 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.6877 | 4.5066 | 75.2934 | 0.20835 | 6.52 | NA | 29.677 | 330.12 | 639.54 | 630.563 | 1.4037 | 91.0102 | 480.3415 | 93.8217 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.5785 | 8.768 | 51.032 | 0.28567 | NA | NA | 38.99 | 639.54 | 1008 | 1192.046 | -18.2585 | 88.1891 | 915.793 | 95.7425 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.4229 | 12.6699 | 72.7301 | 0.26705 | NA | 7 | 72.842 | 1008 | 1441.44 | 1671.6605 | -15.9716 | 77.9347 | 1339.8303 | 94.5633
[11 empty] | 1998-05-29 | 22:45 | 5332.54 | 25.5556 | 100 | 70 | 9 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.904 | 65.096 | 0.23811 | 7.3 | 6.5 | 36.582 | 315.4 | 331.8 | 1444.3 | 1922.1679 | -33.0865 | 88.9747 | 1126.984 | 96.754 | 100 | 78 | 9.2 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.5159 | 75.2841 | 0.20499 | 6.5 | NA | 30.739 | 331.8 | 637.56 | 632.861 | 0.73703 | 90.7357 | 482.3305 | 93.627 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.7483 | 51.0517 | 0.28091 | NA | NA | 38.36 | 637.56 | 1010 | 1188.824 | -17.7053 | 88.4388 | 913.192 | 95.7993 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 12.7012 | 72.6988 | 0.26282 | NA | 7 | 72.534 | 1010 | 1444.3 | 1675.2985 | -15.9938 | 78.1392 | 1342.6492 | 94.5977
[11 empty] | 1998-05-30 | 9:45 | 5343.71 | 25.5556 | 100 | 70 | 9.2333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.5705 | 65.1961 | 0.23774 | 7.3 | 6.49 | 39.731 | 312.08 | 325.92 | 1401.4 | 1867.6478 | -33.2701 | 87.8096 | 1096.7839 | 96.3775 | 100 | 78 | 9.5 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.4295 | 75.0705 | 0.20557 | 6.49 | NA | 30.621 | 325.92 | 604.89 | 621.219 | -2.6995 | 90.6047 | 473.5695 | 93.534 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.2059 | 51.3941 | 0.27904 | NA | NA | 42.84 | 604.89 | 980 | 1121.976 | -14.4873 | 86.8557 | 863.433 | 95.0384 | 120 | 70 | 8.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 12.302 | 73.898 | 0.25855 | NA | 7.3 | 71.995 | 980 | 1401.4 | 1624.3906 | -15.912 | 77.9102 | 1302.1953 | 94.4713
[11 empty] | 1998-05-30 | 17:00 | 5352.18 | 25.5556 | 100 | 70 | 9 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.0767 | 64.9233 | 0.23874 | 7.4 | 6.47 | 37.788 | 320.38 | 337.68 | 1354.21 | 1953.2272 | -44.2337 | 88.8095 | 1145.4536 | 96.701 | 100 | 78 | 9.4 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.5855 | 75.0145 | 0.20572 | 6.47 | NA | 31.978 | 337.68 | 629.64 | 643.382 | -2.1825 | 90.5301 | 490.531 | 93.4809 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6061 | 51.1939 | 0.28013 | NA | NA | 40.18 | 629.64 | 947 | 1171.9432 | -23.7532 | 88.1012 | 900.7916 | 95.5395 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.8768 | 73.5232 | 0.25987 | NA | 7.3 | 70.378 | 947 | 1354.21 | 1569.1188 | -15.8697 | 79.1584 | 1258.0594 | 94.4058
[11 empty] | 1998-05-30 | 22:45 | 5352.53 | 25.5556 | 100 | 70 | 9.0667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.315 | 64.6184 | 0.23987 | 7.4 | 6.47 | 38.056 | 322.04 | 344.4 | 1361.36 | 1994.7048 | -46.5229 | 88.9501 | 1169.5524 | 96.7461 | 100 | 78 | 9.4 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.6872 | 74.9128 | 0.206 | 6.47 | NA | 31.919 | 344.4 | 635.58 | 656.881 | -3.3514 | 90.732 | 500.6405 | 93.6244 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6806 | 51.1194 | 0.28054 | NA | NA | 41.02 | 635.58 | 952 | 1182.5752 | -24.2201 | 88.0894 | 909.0776 | 95.4877 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.9341 | 73.4659 | 0.26007 | NA | 7.2 | 71.148 | 952 | 1361.36 | 1577.1208 | -15.8489 | 79.3415 | 1264.5604 | 94.3737
[11 empty] | 1998-05-31 | 8:25 | 5366.24 | 25.5556 | 100 | 70 | 9.0667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.7095 | 65.2239 | 0.23764 | 7.4 | 6.66 | 39.329 | 316.23 | 329.28 | 1322.75 | 1891.2741 | -42.9805 | 88.0561 | 1110.277 | 96.4577 | 100 | 78 | 9.4 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.4781 | 75.1219 | 0.20543 | 6.66 | NA | 30.739 | 329.28 | 611.82 | 627.821 | -2.6153 | 90.6648 | 478.5505 | 93.5766 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.3224 | 51.4776 | 0.27859 | NA | NA | 41.79 | 611.82 | 925 | 1136.2476 | -22.8376 | 87.3087 | 874.0338 | 95.2187 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.5589 | 73.8411 | 0.25875 | NA | 7.3 | 71.841 | 925 | 1322.75 | 1530.4677 | -15.7035 | 78.1824 | 1227.7338 | 94.1485
[11 empty] | 1998-06-01 | 0:20 | 5382.16 | 25.5556 | 100 | 70 | 9.0667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.7803 | 65.153 | 0.2379 | 7.4 | 6.97 | 39.932 | 318.72 | 331.8 | 1335.62 | 1904.1212 | -42.5646 | 87.965 | 1117.9606 | 96.4281 | 100 | 78 | 9.4 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.5133 | 75.0867 | 0.20552 | 6.97 | NA | 30.916 | 331.8 | 610.83 | 632.684 | -3.5778 | 90.6823 | 482.242 | 93.5891 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.3192 | 51.4808 | 0.27857 | NA | NA | 41.02 | 610.83 | 934 | 1135.0552 | -21.5263 | 87.6371 | 872.9426 | 95.301 | 118 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.6715 | 73.7285 | 0.25915 | NA | 7.2 | 72.534 | 934 | 1335.62 | 1545.363 | -15.7038 | 78.1392 | 1239.6815 | 94.149
[11 empty] | 1998-06-01 | 8:00 | 5390.5 | 25.5556 | 100 | 78 | 9.1333 | 0 | 16.5 | 3.1 |  | 19.6 | 19.6 | 0.84184 | 0 | 15.1145 | 15.3144 | 10.1793 | 69.6873 | 0.21976 | 7.5 | 6.51 | 40.334 | 316.23 | 318.36 | 1364.22 | 1798.1758 | -31.8098 | 87.3307 | 1058.2679 | 96.1887 | 100 | 78 | 9.5 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 4.3582 | 75.1418 | 0.20537 | 6.51 | NA | 29.795 | 318.36 | 591.03 | 612.8748 | -3.6961 | 90.6411 | 465.6174 | 93.601 | 78 | 60 | 9.5 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.0618 | 51.4382 | 0.2788 | NA | NA | 38.85 | 591.03 | 954 | 1099.0356 | -15.2029 | 87.7968 | 845.0328 | 95.4025 | 120 | 78 | 8.4 | 2 | 3.1 | 5.1 | 5.1 | 0.55322 | 0.39216 | 17.1429 | 17.3696 | 11.5878 | 79.0122 | 0.21983 | NA | 7.3 | 77.847 | 954 | 1364.22 | 1519.26 | -11.3647 | 75.5475 | 1236.63 | 93.7049
[11 empty] | 1998-06-01 | 19:40 | 5401.59 | 25.5556 | 100 | 76 | 9.1333 | 0 | 16.6 | 3.1 |  | 19.7 | 19.7 | 0.84264 | 0 | 15.2061 | 15.4072 | 11.0658 | 67.8009 | 0.22724 | 7.5 | 7.15 | 41.808 | 353.58 | 342.72 | 1438.58 | 1954.0552 | -35.8322 | 87.8011 | 1148.3876 | 96.3594 | 100 | 78 | 9.6 | 10.4 | 9.3 | 19.7 | 19.7 | 0.47431 | 0.52792 | 16 | 16.2116 | 4.8661 | 74.5339 | 0.21751 | 7.15 | NA | 30.621 | 342.72 | 630.63 | 691.7339 | -9.6893 | 91.0653 | 517.227 | 94.0798 | 78 | 60 | 9.4 | 4.6 | 4.6 | 9.2 | 9.2 | 0.45141 | 0.5 | 14.1538 | 14.341 | 8.8546 | 50.7454 | 0.28261 | NA | NA | 40.32 | 630.63 | 1006 | 1220.94 | -21.3658 | 88.2353 | 925.785 | 95.6448 | 120 | 76 | 8.4 | 1.6 | 3.1 | 4.7 | 4.7 | 0.52624 | 0.34043 | 13.7143 | 13.8956 | 11.6642 | 77.9358 | 0.1783 | NA | 7.3 | 78.848 | 1006 | 1438.58 | 1484.5301 | -3.1941 | 76.9935 | 1245.265 | 93.6682
[11 empty] | 1998-06-02 | 8:00 | 5414.19 | 25.5556 | 100 | 70 | 8.9333 | 0 | 15.5 | 3.1 |  | 18.6 | 18.6 | 0.83333 | 0 | 14.1985 | 14.3862 | 10.2682 | 65.7984 | 0.21864 | 7.5 | 6.8 | 39.262 | 322.04 | 332.64 | 1395.68 | 1799.53 | -28.9357 | 88.1968 | 1066.085 | 96.3172 | 100 | 78 | 9.2 | 9.9 | 8.7 | 18.6 | 18.6 | 0.4465 | 0.53226 | 15.2308 | 15.4322 | 4.7339 | 75.0661 | 0.20558 | 6.8 | NA | 30.916 | 332.64 | 616.77 | 675.9811 | -9.6002 | 90.7059 | 504.3106 | 93.8697 | 78 | 60 | 9.2 | 4.6 | 4.6 | 9.2 | 9.2 | 0.45141 | 0.5 | 14.1538 | 14.341 | 8.6772 | 51.1228 | 0.28052 | NA | NA | 38.29 | 616.77 | 976 | 1195.25 | -22.4641 | 88.4891 | 906.01 | 95.7738 | 120 | 70 | 8.4 | 1 | 3.1 | 4.1 | 4.1 | 0.48576 | 0.2439 | 8.5714 | 8.6848 | 10.4472 | 76.1528 | 0.11404 | NA | 7.3 | 76.384 | 976 | 1395.68 | 1266.1987 | 9.2773 | 77.037 | 1121.0994 | 93.1867
[11 empty] | 1998-06-02 | 17:00 | 5420.28 | 26.1111 | 100 | 100 | 8.6 | 0 | 16 | 3.4 |  | 19.4 | 19.4 | 0.82474 | 0 | 14.6565 | 14.6084 | 9.6013 | 81.7987 | 0.17859 | 7.5 | 6.87 | 38.726 | 316.23 | 325.08 | 1368.51 | 1672.6282 | -22.2226 | 88.0872 | 998.8541 | 96.123 | 100 | 76 | 9.8 | 10.4 | 9 | 19.4 | 19.4 | 0.4645 | 0.53608 | 16 | 15.9475 | 4.6496 | 73.5504 | 0.21682 | 6.87 | NA | 30.385 | 325.08 | 610.83 | 665.6164 | -8.9692 | 90.6531 | 495.3482 | 93.8659 | 76 | 60 | 9.8 | 4.6 | 4.6 | 9.2 | 9.2 | 0.45141 | 0.5 | 14.1538 | 14.1074 | 8.5976 | 49.6024 | 0.28441 | NA | NA | 37.66 | 610.83 | 957 | 1184 | -23.72 | 88.4152 | 897.415 | 95.8035 | 140 | 100 | 6.2 | 1 | 3.4 | 4.4 | 4.4 | 0.52624 | 0.22727 | 8.5714 | 8.5433 | 10.1065 | 103.6935 | 0.08239 | NA | 7.4 | 75.922 | 957 | 1368.51 | 1216.1406 | 11.134 | 76.6451 | 1086.5703 | 93.0127
[11 empty] | 1998-06-03 | 0:25 | 5427.51 | 25.5556 | 100 | 100 | 8.6 | 0 | 16 | 3.1 |  | 19.1 | 19.1 | 0.8377 | 0 | 14.6565 | 14.8503 | 10.1836 | 81.2164 | 0.18285 | 7.4 | 6.74 | 38.994 | 318.72 | 323.4 | 1372.8 | 1791.3019 | -30.4853 | 87.9425 | 1057.351 | 96.3121 | 100 | 76 | 9.8 | 10.4 | 8.7 | 19.1 | 19.1 | 0.45468 | 0.5445 | 16 | 16.2116 | 4.673 | 73.527 | 0.22048 | 6.74 | NA | 30.916 | 323.4 | 611.82 | 673.036 | -10.0056 | 90.4403 | 498.218 | 93.7947 | 76 | 60 | 9.8 | 4.6 | 4.6 | 9.2 | 9.2 | 0.45141 | 0.5 | 14.1538 | 14.341 | 8.6051 | 49.5949 | 0.28916 | NA | NA | 38.15 | 611.82 | 960 | 1185.49 | -23.4885 | 88.2035 | 898.655 | 95.7548 | 140 | 100 | 6.2 | 1 | 3.1 | 4.1 | 4.1 | 0.48576 | 0.2439 | 8.5714 | 8.6848 | 10.2703 | 103.5297 | 0.083887 | NA | 7.4 | 75.614 | 960 | 1372.8 | 1245.2858 | 9.2886 | 76.619 | 1102.6429 | 93.1425
[11 empty] | 1998-06-03 | 12:55 | 5440.25 | 26.1111 | 100 | 100 | 7.3667 | 0 | 16 | 3.6 |  | 19.6 | 19.6 | 0.81633 | 0 | 14.6565 | 14.6084 | 8.9651 | 83.6682 | 0.1746 | 7.5 | 6.62 | 29.212 | 266.43 | 307.44 | 1259.83 | 1544.0089 | -22.5569 | 90.4983 | 925.7244 | 96.8444 | 100 | 78 | 8.5 | 10.2 | 9.4 | 19.6 | 19.6 | 0.47431 | 0.52041 | 15.6923 | 15.6409 | 4.2774 | 76.2226 | 0.2052 | 6.62 | NA | 30.149 | 307.44 | 549.45 | 608.3302 | -10.7162 | 90.1935 | 457.8851 | 93.4156 | 78 | 60 | 8.8 | 4.8 | 4.2 | 9 | 9 | 0.43178 | 0.53333 | 14.7692 | 14.7208 | 8.0138 | 52.1862 | 0.28208 | NA | NA | 39.48 | 549.45 | 881 | 1132.2729 | -28.5213 | 87.1585 | 840.8614 | 95.3048 | 142 | 100 | 4.8 | 1 | 3.6 | 4.6 | 4.6 | 0.55322 | 0.21739 | 8.5714 | 8.5433 | 8.8006 | 107.3994 | 0.079547 | NA | 7.1 | 108.262 | 881 | 1259.83 | 1095.6494 | 13.032 | 64.786 | 988.3247 | 89.0459
[11 empty] | 1998-06-04 | 15:10 | 5447.98 | 26.6667 | 98 | 72 | 9.8667 | 0 | 17.1 | 3 | X | 20.1 | 20.1 | 0.85075 | 0 | 15.6641 | 15.3585 | 11.1296 | 64.0038 | 0.23996 | 7.1 | 5.55 | 40.2 | 301.29 | 329.28 | 1465.75 | 1977.036 | -34.8822 | 87.7915 | 1153.158 | 96.5139 | 98 | 72 | 9.8 | 10.2 | 9.9 | 20.1 | 20.1 | 0.49066 | 0.50746 | 15.6923 | 15.3861 | 4.5144 | 70.6856 | 0.21767 | 5.55 | NA | 31.329 | 329.28 | 647.46 | 636.2598 | 1.7299 | 90.4856 | 482.7699 | 93.5106 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 13.8777 | 8.7988 | 47.4012 | 0.29277 | NA | NA | 44.8 | 647.46 | 1025 | 1201.9072 | -17.2592 | 86.3946 | 924.6836 | 95.1551 | 110 | 72 | 10 | 2.3 | 3 | 5.3 | 5.3 | 0.55997 | 0.43396 | 19.7143 | 19.3296 | 13.0906 | 67.9094 | 0.28464 | NA | 7.1 | 78.694 | 1025 | 1465.75 | 1750.5013 | -19.427 | 76.1012 | 1387.7506 | 94.3294
[11 empty] | 1998-06-05 | 5:00 | 5461.18 | 26.6667 | 100 | 72 | 9.8667 | 0 | 17 | 3 |  | 20 | 20 | 0.85 | 0 | 15.5725 | 15.2687 | 11.2438 | 64.8896 | 0.2353 | 7.4 | 6.62 | 41.004 | 303.78 | 334.32 | 1458.6 | 1996.444 | -36.874 | 87.7351 | 1165.382 | 96.4815 | 100 | 72 | 9.8 | 10.2 | 9.8 | 20 | 20 | 0.48739 | 0.51 | 15.6923 | 15.3861 | 4.5941 | 71.6059 | 0.21487 | 6.62 | NA | 32.155 | 334.32 | 648.45 | 648.8183 | -0.056792 | 90.382 | 491.5691 | 93.4587 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 13.8777 | 8.9318 | 47.2682 | 0.29359 | NA | NA | 36.68 | 648.45 | 1020 | 1211.2784 | -18.7528 | 89.0285 | 929.8642 | 96.0553 | 110 | 72 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 18.4892 | 12.8645 | 68.1355 | 0.27136 | NA | 7.1 | 78.694 | 1020 | 1458.6 | 1710.2911 | -17.2557 | 76.4615 | 1365.1455 | 94.2355
[11 empty] | 1998-06-05 | 8:10 | 5464.4 | 26.6667 | 100 | 72 | 9.8667 | 0 | 17.3 | 3 |  | 20.3 | 20.3 | 0.85222 | 0 | 15.8473 | 15.5381 | 10.9546 | 65.1788 | 0.23839 | 7.4 | 6.6 | 40.468 | 308.76 | 322.56 | 1452.88 | 1949.2905 | -34.1673 | 87.4541 | 1135.9253 | 96.4374 | 100 | 72 | 9.8 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 15.6878 | 4.4348 | 71.7652 | 0.2186 | 6.6 | NA | 31.801 | 322.56 | 651.42 | 628.0038 | 3.5946 | 90.1411 | 475.2819 | 93.309 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 13.8777 | 8.8965 | 47.3035 | 0.29338 | NA | NA | 42.07 | 651.42 | 1016 | 1212.022 | -19.2935 | 86.9575 | 931.721 | 95.4847 | 110 | 72 | 10 | 2.3 | 3 | 5.3 | 5.3 | 0.55997 | 0.43396 | 19.7143 | 19.3296 | 12.9533 | 68.0467 | 0.28406 | NA | 7.1 | 79.618 | 1016 | 1452.88 | 1733.8929 | -19.3418 | 75.3168 | 1374.9464 | 94.2094
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A1: Alison Gusses: Please refer to comment in column AJ prior to Base Analyses
Note on W6: S Allgeier (11/17/99): Reviewer entered formula to calculate average system permeate pressure.
Note on AJ6: Alison Gusses: MTCw may be incorrect due to third stage booster pump
Note on DU17: CDM: verified w/ lab data sheets
Note on DU23: CDM: verified w/ lab data sheets
Note on DV17: CDM: verified w/ lab data sheets
Note on DV23: CDM: verified w/ lab data sheets
Note on DW17: CDM: verified w/ lab data sheets
Note on DW23: CDM: verified w/ lab data sheets
Note on EO17: CDM: verified w/ lab data sheets
Note on EO23: CDM: verified w/ lab data sheets
Note on EP17: CDM: verified w/ lab data sheets
Note on EP23: CDM: verified w/ lab data sheets
Note on EQ17: CDM: verified w/ lab data sheets
Note on EQ23: CDM: verified w/ lab data sheets
Note on FI17: CDM: verified w/ lab data sheets
Note on FI23: CDM: verified w/ lab data sheets
Note on FJ17: CDM: verified w/ lab data sheets
Note on FJ23: CDM: verified w/ lab data sheets
Note on FK17: CDM: verified w/ lab data sheets
Note on FK23: CDM: verified w/ lab data sheets
Note on GC17: CDM: verified w/ lab data sheets
Note on GC23: CDM: verified w/ lab data sheets
Note on GD17: CDM: verified w/ lab data sheets
Note on GD23: CDM: verified w/ lab data sheets
Note on GE17: CDM: verified w/ lab data sheets
Note on GE23: CDM: verified w/ lab data sheets
Note on GW17: CDM: verified w/ lab data sheets
Note on GW23: CDM: verified w/ lab data sheets
Note on GX17: CDM: verified w/ lab data sheets
Note on GX23: CDM: verified w/ lab data sheets
Note on GX25: Alison Gusses: verified by consultant
Note on GY17: CDM: verified w/ lab data sheets
Note on GY23: CDM: verified w/ lab data sheets
Note on HQ17: CDM: verified w/ lab data sheets
Note on HQ23: CDM: verified w/ lab data sheets
Note on HR17: CDM: verified w/ lab data sheets
Note on HR23: CDM: verified w/ lab data sheets
Note on HS17: CDM: verified w/ lab data sheets
Note on HS23: CDM: verified w/ lab data sheets

## Sheet5. Weeks 41-50
FIELD-SET 5: PILOT-SCALE MEMBRANE RESULTS: WEEKS 41-50 (FILE: mempilot.xls)
Field 5-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 5-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 5-4: Foulants And Fouling Indices1 |  | Field 5-5: Pretreatment Used Prior To Membranes1 |  |  | Field 5-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 5-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 5-7: System And Stage Water Quality For Week 42 | [9 empty] | Field 5-7: System And Stage Water Quality For Week 42 (continued) | [7 empty] | Field 5-8: System And Stage Water Quality For Week 44 | [9 empty] | Field 5-8: System And Stage Water Quality For Week 44 (continued) | [7 empty] | Field 5-9: System And Stage Water Quality For Week 46 | [9 empty] | Field 5-9: System And Stage Water Quality For Week 46 (continued) | [7 empty] | Field 5-10: System And Stage Water Quality For Week 48 | [9 empty] | Field 5-10: System And Stage Water Quality For Week 48 (continued) | [7 empty] | Field 5-11: System And Stage Water Quality For Week 50 | [9 empty] | Field 5-11: System And Stage Water Quality For Week 50 (continued) | [7 empty] | Field 5-12: Duplicate Analysis Of System And Stage Water Quality For Week 44 | [9 empty] | Field 5-12: Duplicate Analysis Of System And Stage Water Quality For Week 44 (continued) | [7 empty] | Field 5-13: Membrane Cost Parameters
|  | Stage 1 and 2 -- General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment (from Performance sampling & MDWASD) |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Miami-Dade Water and Sewer Dept. | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 26 | Alkalinity (mg/L as CaCO3) | 176 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.84343 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51515 | [6 empty] | System recovery during sample collection (decimal) | 0.84343 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.84343 | [6 empty] | System recovery during sample collection (decimal) | 0.84343 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5101 | [6 empty] | System recovery during sample collection (decimal) | 0.84343 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5101 | [6 empty] | System recovery during sample collection (decimal) | 0.84772 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50761 | [6 empty] | System recovery during sample collection (decimal) | 0.84343 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 4130871 | Membrane trade name | TFC-S | Temperature normalized MTCW (gfd/psi) | 0.30179 | Calcium Hardness (mg/L as CaCO3) | NA | Antiscalant Addition | King Lee Pre-treat 100 (2 mg/L dose) | Pilot Scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 19.8 | HI - 19 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.2 | HI - 19 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.8 | HI - 20 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 19.8 | HI - 20 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.8 | HI - 21 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.1 | HI - 21 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.8 | HI - 22 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10.1 | HI - 22 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.7 | HI - 23 | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10 | HI - 23 | [5 empty] | System feed flow rate during sample collection (gpm) | 19.8 | HI - 20 DUP | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.9 |  | HI - 20 DUP |  |  | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | 1029 | Membrane element model number | TFC 4921S |  |  | LSI | 0.14 | Sulfuric Acid Addition | pH ~ 6.75 (85 mg/L dose) | Pilot Scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 19.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.7 | [6 empty] | System influent flow rate during sample collection (gpm) | 19.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.8 |  |  |  |  | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 300 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | NA | Cartridge Filtration | 5 um exclusion size | Pilot Scale | 1998-06-06 | 12:10 | 5493.04 | 26.6667 | 100 | 72 | 9.8667 | 0 | 17.3 | 3 |  | 20.3 | 20.3 | 0.85222 | 0 | 15.8473 | 15.5381 | 10.8633 | 65.27 | 0.23806 | 7.4 | 6.54 | 41.138 | 330.34 | 320.88 | 1100 | 1934.0589 | -75.8235 | 87.1796 | 1127.4694 | 96.3513 | 100 | 72 | 9.8 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 15.6878 | 4.4065 | 71.7935 | 0.21851 | 6.54 | NA | 31.978 | 320.88 | 635.58 | 624.373 | 1.7633 | 90.0343 | 472.6265 | 93.234 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 13.8777 | 8.6796 | 47.5204 | 0.29204 | NA | NA | 41.09 | 635.58 | 1061.44 | 1182.5108 | -11.4063 | 87.1946 | 909.0454 | 95.4799 | 110 | 72 | 10 | 2.3 | 3 | 5.3 | 5.3 | 0.55997 | 0.43396 | 19.7143 | 19.3296 | 13.5904 | 67.4096 | 0.28675 | NA | 7.1 | 79.002 | 1061.44 | 1573 | 1814.6425 | -15.3619 | 75.3796 | 1438.0412 | 94.5063 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 25
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design system recovery, R (decimal) | 0.85 | Total iron (mg/L) | 0.67 |  |  |  | 1998-06-07 | 10:50 | 5515.18 | 26.6667 | 100 | 72 | 9.8667 | 0 | 17.3 | 3 |  | 20.3 | 20.3 | 0.85222 | 0 | 15.8473 | 15.5381 | 11.3096 | 64.8237 | 0.2397 | 7.4 | 6.47 | 41.406 | 313.74 | 332.64 | 1074 | 2012.0894 | -87.3454 | 87.5523 | 1172.3647 | 96.4682 | 100 | 72 | 9.8 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 15.6878 | 4.5823 | 71.6177 | 0.21905 | 6.47 | NA | 32.214 | 332.64 | 645.48 | 648.239 | -0.42744 | 90.3157 | 490.4395 | 93.4316 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 13.8777 | 8.818 | 47.382 | 0.29289 | NA | NA | 41.51 | 645.48 | 1046.56 | 1201.1324 | -14.7696 | 87.521 | 923.3062 | 95.5042 | 110 | 72 | 10 | 2.3 | 3 | 5.3 | 5.3 | 0.55997 | 0.43396 | 19.7143 | 19.3296 | 13.375 | 67.625 | 0.28583 | NA | 7.1 | 79.695 | 1046.56 | 1535.82 | 1787.8232 | -16.4084 | 76.0417 | 1417.1916 | 94.3766 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | NA |  |  |  | 1998-06-07 | 20:00 | 5525.31 | 25.5556 | 100 | 78 | 9.8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.2668 | 68.9332 | 0.22486 | 7.5 | 6.41 | 38.592 | 316.23 | 309.96 | 1034 | 1820.5752 | -76.0711 | 87.5494 | 1065.2676 | 96.3772 | 100 | 72 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.1795 | 72.0205 | 0.21427 | 6.41 | NA | 32.273 | 309.96 | 648.45 | 590.4805 | 8.9397 | 89.588 | 450.2203 | 92.8317 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.8726 | 47.3274 | 0.30302 | NA | NA | 40.74 | 648.45 | 1087.48 | 1207.5432 | -11.0405 | 86.8564 | 927.9966 | 95.6099 | 120 | 78 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.8173 | 75.3827 | 0.25346 | NA | 7.2 | 76.461 | 1087.48 | 1478.62 | 1828.8939 | -23.6892 | 75.332 | 1458.187 | 94.7564 | Parameter | Units | Cp-sys-42 | CF-sys-42 | CC-sys-42 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-42 | CI-s1-42 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-44 | CF-sys-44 | CC-sys-44 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-44 | CI-s1-44 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-46 | CF-sys-46 | CC-sys-46 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-46 | CI-s1-46 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-48 | CF-sys-48 | CC-sys-48 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-48 | CI-s1-48 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-50 | CF-sys-50 | CC-sys-50 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-50 | CI-s1-50 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-50 (dup) | CF-sys-50 (dup) | CC-sys-50 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-50 (dup) | CI-s1-50 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophilic | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | BDL |  |  |  | 1998-06-07 | 22:00 | 5526.37 | 25.5556 | 100 | 76 | 9.8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.9476 | 68.2524 | 0.2271 | 7.5 | 6.43 | 37.788 | 304.61 | 300.72 | 1047 | 1764.3748 | -68.5172 | 87.4342 | 1032.5474 | 96.3403 | 100 | 72 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.0484 | 72.1516 | 0.21389 | 6.43 | NA | 31.742 | 300.72 | 635.58 | 572.4427 | 9.9338 | 89.4447 | 436.5813 | 92.7294 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6908 | 47.5092 | 0.30186 | NA | NA | 40.32 | 635.58 | 1058.96 | 1183.2192 | -11.7341 | 86.5922 | 909.3996 | 95.5663 | 120 | 76 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.437 | 74.763 | 0.25556 | NA | 7.1 | 75.768 | 1058.96 | 1497.21 | 1779.9675 | -18.8856 | 74.8045 | 1419.4637 | 94.6622 | Sampling date | MM/DD/YY | 1998-06-17 | 1998-06-17 | 1998-06-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-17 | 1998-06-17 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-15 | 1998-07-15 | 1998-07-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-15 | 1998-07-15 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-29 | 1998-07-29 | 1998-07-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-29 | 1998-07-29 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | 1998-08-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1998-06-08 | 8:00 | 5536.51 | 26.1111 | 100 | 78 | 9.8667 | 0 | 17.1 | 3 |  | 20.1 | 20.1 | 0.85075 | 0 | 15.6641 | 15.6128 | 10.8431 | 68.2902 | 0.22862 | 7.5 | 6.41 | 35.041 | 326.19 | 316.68 | 1011 | 1922.0223 | -90.111 | 88.9349 | 1119.3511 | 96.8695 | 100 | 75 | 9.8 | 10.3 | 9.8 | 20.1 | 20.1 | 0.48903 | 0.51244 | 15.8462 | 15.7942 | 4.3576 | 73.3424 | 0.21535 | 6.41 | NA | 31.034 | 316.68 | 694.98 | 616.8998 | 11.2349 | 90.2002 | 466.7899 | 93.3516 | 75 | 62 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.1074 | 9.601 | 49.099 | 0.28733 | NA | NA | 37.38 | 694.98 | 1142.04 | 1299.972 | -13.8289 | 88.1963 | 997.476 | 96.2525 | 120 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 18.7953 | 14.5429 | 74.4571 | 0.25243 | NA | 7.2 | 77.924 | 1142.04 | 1445.73 | 1922.3917 | -32.9703 | 75.3935 | 1532.2159 | 94.9143 | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5881 (May 1998)
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0.08 |  |  |  | 1998-06-08 | 20:00 | 5544.52 | 25.5556 | 100 | 78 | 9.8667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.7072 | 67.4261 | 0.23676 | 7.4 | 6.42 | 34.907 | 305.44 | 337.68 | 1018 | 2073.5785 | -103.6914 | 89.6627 | 1205.6293 | 97.1047 | 100 | 75 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.6385 | 73.0615 | 0.22189 | 6.42 | NA | 34.633 | 337.68 | 659.34 | 659.2809 | 0.0089638 | 89.7438 | 498.4804 | 93.0523 | 75 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.9989 | 48.7011 | 0.29447 | NA | NA | 42.98 | 659.34 | 1071.36 | 1226.3912 | -14.4705 | 87.272 | 942.8656 | 95.4416 | 120 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.6275 | 75.3725 | 0.25349 | NA | 7.2 | 74.228 | 1071.36 | 1455.74 | 1802.5901 | -23.8264 | 78.0182 | 1436.9751 | 94.8344 | Operation time | hh.hh | 5752.18 | 5752.18 | 5752.18 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5752.18 | 5752.18 | --- | --- | --- | --- | Operation time | hh.hh | 5973.25 | 5973.25 | 5973.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5973.25 | 5973.25 | --- | --- | --- | --- | Operation time | hh.hh | 6167.4 | 6167.4 | 6167.4 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6167.4 | 6167.4 | --- | --- | --- | --- | Operation time | hh.hh | 6452.2 | 6452.2 | 6452.2 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6452.2 | 6452.2 | --- | --- | --- | --- | Operation time | hh.hh | 6694.8 | 6694.8 | 6694.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6694.8 | 6694.8 | --- | --- | --- | --- | Operation time | hh.hh | 5973.25 | 5973.25 | 5973.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5973.25 | 5973.25 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 130
E-Mail Address (optional) |  | Stage 1 and 2 -- Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 9.16 |  |  |  | 1998-06-09 | 10:45 | 5560.44 | 25.5556 | 100 | 79 | 9.8667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 10.6601 | 68.9732 | 0.23145 | 7.5 | 6.3 | 35.912 | 303.78 | 318.36 | 1021 | 1885.4908 | -84.671 | 88.7197 | 1101.9254 | 96.741 | 100 | 75 | 9.8 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.3501 | 73.3499 | 0.22102 | 6.3 | NA | 33.158 | 318.36 | 575.19 | 617.9661 | -7.4369 | 89.5847 | 468.1631 | 92.9174 | 75 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8071 | 49.8929 | 0.28744 | NA | NA | 40.46 | 575.19 | 1118.48 | 1067.1416 | 4.59 | 87.2911 | 821.1658 | 95.0729 | 118 | 79 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 14.1824 | 74.3176 | 0.25709 | NA | 7.2 | 71.687 | 1118.48 | 1460.03 | 1861.3654 | -27.4882 | 77.4824 | 1489.9227 | 95.1885 | pH | --- | 5.88 | 6.78 | 7.34 | --- | --- | --- | --- | --- | pH | --- | 6.05 | 6.78 | --- | --- | --- | --- | pH | --- | 5.75 | 6.52 | 7.02 | --- | --- | --- | --- | --- | pH | --- | 5.81 | 6.52 | --- | --- | --- | --- | pH | --- | 5.95 | 6.76 | 7.29 | --- | --- | --- | --- | --- | pH | --- | 6 | 6.76 | --- | --- | --- | --- | pH | --- | 5.73 | 6.57 | 7.08 | --- | --- | --- | --- | --- | pH | --- | 5.81 | 6.57 | --- | --- | --- | --- | pH | --- | 5.75 | 6.49 | 6.99 | --- | --- | --- | --- | --- | pH | --- | 5.86 | 6.49 | --- | --- | --- | --- | pH | --- | 5.74 | 6.49 | 7 | --- | --- | --- | --- | --- | pH | --- | 5.83 | 6.68 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | ~20
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.8125 | Calcium (mg/L) | 56 |  |  |  | 1998-06-09 | 16:00 | 5568.21 | 25.5556 | 100 | 78 | 9.8667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 12.149 | 66.9843 | 0.23833 | 7.4 | 6.32 | 35.242 | 308.76 | 349.44 | 1112 | 2150.8419 | -93.421 | 89.9147 | 1250.1409 | 97.181 | 100 | 75 | 9.8 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.8392 | 72.8608 | 0.2225 | 6.32 | NA | 33.276 | 349.44 | 637.56 | 684.961 | -7.4347 | 90.4773 | 517.2005 | 93.5661 | 75 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.7023 | 48.9977 | 0.29269 | NA | NA | 41.51 | 637.56 | 1111.04 | 1185.926 | -6.7402 | 88.121 | 911.743 | 95.4472 | 118 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.1308 | 73.8692 | 0.25865 | NA | 7.2 | 77.077 | 1111.04 | 1590.16 | 1869.2795 | -17.5529 | 77.9427 | 1490.1598 | 94.8276 | Temperature | oC | 25.5 | 25.9 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 25.5 | 25.9 | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.7 | 23.6 | --- | --- | --- | --- | Temperature | oC | 25 | 25.8 | 26.8 | --- | --- | --- | --- | --- | Temperature | oC | 26.5 | 25.8 | --- | --- | --- | --- | Temperature | oC | 27.1 | 26.4 | 27.2 | --- | --- | --- | --- | --- | Temperature | oC | 26.9 | 26.4 | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.1 | 26.1 | --- | --- | --- | --- | --- | Temperature | oC | 25.1 | 25.1 | --- | --- | --- | --- | Temperature | oC | 24.1 | 23.6 | 25.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.9 | 24.7 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 67%
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.875 | Barium (mg/L) | < 0.05 |  |  |  | 1998-06-10 | 9:00 | 5585.85 | 26.1111 | 100 | 78 | 9.7667 | 0 | 17.1 | 3.1 |  | 20.2 | 20.2 | 0.84653 | 0 | 15.6641 | 15.6128 | 11.1888 | 68.0445 | 0.22945 | 7.5 | 6.31 | 33.232 | 277.22 | 330.96 | 855 | 1973.2661 | -130.7914 | 89.9589 | 1152.113 | 97.1156 | 100 | 78 | 9.5 | 10.3 | 9.9 | 20.2 | 20.2 | 0.4923 | 0.5099 | 15.8462 | 15.7942 | 4.5909 | 74.9091 | 0.21084 | 6.31 | NA | 28.969 | 330.96 | 540.54 | 645.1527 | -19.3534 | 91.247 | 488.0563 | 94.0644 | 78 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.1074 | 7.3441 | 51.8559 | 0.27205 | NA | NA | 37.52 | 540.54 | 866.76 | 1003.3184 | -15.755 | 88.6633 | 771.9292 | 95.1395 | 120 | 78 | 10 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 18.7953 | 10.8867 | 78.1133 | 0.24062 | NA | 7.2 | 63.217 | 866.76 | 1222.65 | 1437.0163 | -17.5329 | 80.8989 | 1151.8882 | 94.5119 | Alkalinity | mg/L as CaCO3 | 17 | 146 | 751 | 840.9355 | -11.9754 | 88.3562 | 493.4677 | 96.555 | Alkalinity | mg/L as CaCO3 | 16 | 146 | 284.125 | 89.0411 | 215.0625 | 92.5603 | Alkalinity | mg/L as CaCO3 | 17 | 115 | 538 | 642.9355 | -19.5047 | 85.2174 | 378.9677 | 95.5141 | Alkalinity | mg/L as CaCO3 | 19 | 115 | #DIV/0! | 83.4783 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 | 17 | 141 | NA | 809 | #VALUE! | 87.9433 | 475 | 96.4211 | Alkalinity | mg/L as CaCO3 | 17 | 141 | 270.1134 | 87.9433 | 205.5567 | 91.7298 | Alkalinity | mg/L as CaCO3 | 17 | 123 | 571 | 694.0323 | -21.5468 | 86.1789 | 408.5161 | 95.8386 | Alkalinity | mg/L as CaCO3 | 16 | 123 | 234.4124 | 86.9919 | 178.7062 | 91.0468 | Alkalinity | mg/L as CaCO3 | 17 | 114 | 557 | 653.9667 | -17.4087 | 85.0877 | 383.9833 | 95.5727 | Alkalinity | mg/L as CaCO3 | 19 | 114 | 211.9381 | 83.3333 | 162.9691 | 88.3413 | Alkalinity | mg/L as CaCO3 | 16 | 115 | 550 | 648.3226 | -17.8768 | 86.087 | 381.6613 | 95.8078 | Alkalinity | mg/L as CaCO3 | 19 | 205 | 391 | 83.4783 | 298 | 93.6242 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | Strontium (mg/L) | 0.49 |  |  |  | 1998-06-10 | 19:15 | 5595.6 | 25.5556 | 100 | 78 | 9.7667 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 11.7152 | 67.5181 | 0.23644 | 7.4 | 6.3 | 36.381 | 300.46 | 339.36 | 968 | 2076.4396 | -114.5082 | 89.2795 | 1207.8998 | 96.9881 | 100 | 75 | 9.5 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 4.7391 | 73.2609 | 0.22129 | 6.3 | NA | 29.736 | 339.36 | 629.64 | 667.9406 | -6.0829 | 91.2376 | 503.6503 | 94.0959 | 75 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.6041 | 49.0959 | 0.2921 | NA | NA | 40.32 | 629.64 | 1108.56 | 1171.8144 | -5.706 | 88.1188 | 900.7272 | 95.5236 | 118 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.158 | 73.842 | 0.25875 | NA | 7.2 | 72.611 | 1108.56 | 1384.24 | 1868.2559 | -34.9662 | 78.6035 | 1488.408 | 95.1216 | Total dissolved solids | mg/L | 35 | 328 | 1355 | 1906.4194 | -40.6952 | 89.3293 | 1117.2097 | 96.8672 | Total dissolved solids | mg/L | 32 | 328 | 642.5 | 90.2439 | 485.25 | 93.4055 | Total dissolved solids | mg/L | 36.2 | 327 | 1379 | 1893.5677 | -37.3146 | 88.9297 | 1110.2839 | 96.7396 | Total dissolved solids | mg/L | 37.5 | 327 | #DIV/0! | 88.5321 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L | 36 | 324 | 1334 | 1875.4839 | -40.591 | 88.8889 | 1099.7419 | 96.7265 | Total dissolved solids | mg/L | 34 | 324 | 625.9588 | 89.5062 | 474.9794 | 92.8418 | Total dissolved solids | mg/L | 37 | 333 | 1322 | 1927.5806 | -45.8079 | 88.8889 | 1130.2903 | 96.7265 | Total dissolved solids | mg/L | 34 | 333 | 644.3299 | 89.7898 | 488.6649 | 93.0423 | Total dissolved solids | mg/L | 39 | 330 | 1410 | 1949.9 | -38.2908 | 88.1818 | 1139.95 | 96.5788 | Total dissolved solids | mg/L | 38 | 330 | 631.0309 | 88.4848 | 480.5155 | 92.0918 | Total dissolved solids | mg/L | 35.8 | 327 | 1385 | 1895.7226 | -36.8753 | 89.052 | 1111.3613 | 96.7787 | Total dissolved solids | mg/L | 42 | 610 | 1178 | 87.156 | 894 | 95.302 | Fuel Oil Rate ($/gal) | NA
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | Reactive silica (mg/L as SiO2) | 8.41 |  |  |  | 1998-06-10 | 22:00 | 5598.29 | 25.5556 | 100 | 76 | 9.7333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.2354 | 66.0313 | 0.23474 | 7.4 | 6.32 | 34.438 | 288.01 | 357.84 | 927 | 2158.1111 | -132.8059 | 90.3761 | 1257.9756 | 97.2624 | 100 | 76 | 9.5 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.941 | 73.559 | 0.20979 | 6.32 | NA | 29.559 | 357.84 | 600.93 | 689.4708 | -14.734 | 91.7396 | 523.6554 | 94.3553 | 76 | 60 | 9.7 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.2135 | 50.0865 | 0.28633 | NA | NA | 38.36 | 600.93 | 1082.52 | 1118.4944 | -3.3232 | 89.2801 | 859.7122 | 95.538 | 118 | 76 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.82 | 73.18 | 0.26109 | NA | 7.1 | 71.302 | 1082.52 | 1325.61 | 1824.0799 | -37.6031 | 80.0743 | 1453.2999 | 95.0938 | Total hardness | mg/L as CaCO3 | 10 | 193 | 1054 | 1178.8387 | -11.8443 | 94.8187 | 685.9194 | 98.5421 | Total hardness | mg/L as CaCO3 | 10 | 193 | 387.4375 | 94.8187 | 290.2188 | 96.5543 | Total hardness | mg/L as CaCO3 | 12 | 193 | 1096 | 1168.0645 | -6.5752 | 93.7824 | 680.5323 | 98.2367 | Total hardness | mg/L as CaCO3 | 14 | 193 | #DIV/0! | 92.7461 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 | 11 | 195 | 1057 | 1186.2258 | -12.2257 | 94.359 | 690.6129 | 98.4072 | Total hardness | mg/L as CaCO3 | 12 | 195 | 385.5464 | 93.8462 | 290.2732 | 95.866 | Total hardness | mg/L as CaCO3 | 12 | 199 | 996 | 1206.3871 | -21.1232 | 93.9698 | 702.6935 | 98.2923 | Total hardness | mg/L as CaCO3 | 12 | 199 | 393.7113 | 93.9698 | 296.3557 | 95.9508 | Total hardness | mg/L as CaCO3 | 13 | 201 | 1121 | 1247.5333 | -11.2875 | 93.5323 | 724.2667 | 98.2051 | Total hardness | mg/L as CaCO3 | 13 | 201 | 394.8144 | 93.5323 | 297.9072 | 95.6362 | Total hardness | mg/L as CaCO3 | 12 | 192 | 1056 | 1161.6774 | -10.0073 | 93.75 | 676.8387 | 98.2271 | Total hardness | mg/L as CaCO3 | 11 | 386 | 761 | 94.2708 | 573.5 | 98.082 | Natural Gas Rate ($/ft3) | 0.2714¢/therm
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.293 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | Turbidity (ntu) | 0.5 |  |  |  | 1998-06-11 | 10:00 | 5610.28 | 25.5556 | 100 | 76 | 9.7667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4713 | 66.762 | 0.23217 | 7.5 | 6.31 | 33.634 | 297.97 | 336.84 | 878 | 2024.6867 | -130.6021 | 90.0148 | 1180.7634 | 97.1515 | 100 | 75 | 9.5 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.64 | 73.36 | 0.21036 | 6.31 | NA | 28.556 | 336.84 | 592.02 | 648.2698 | -9.5013 | 91.5224 | 492.5549 | 94.2025 | 75 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.1059 | 49.5941 | 0.28917 | NA | NA | 36.82 | 592.02 | 871.72 | 1102.804 | -26.509 | 89.069 | 847.412 | 95.655 | 120 | 76 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.8896 | 77.1104 | 0.24778 | NA | 7.2 | 74.921 | 871.72 | 1255.54 | 1456.0393 | -15.9692 | 77.7577 | 1163.8796 | 93.5628 | Calcium hardness | mg/L as CaCO3 | 9 | 182 | 1012 | 1113.9677 | -10.0759 | 95.0549 | 647.9839 | 98.6111 | Calcium hardness | mg/L as CaCO3 | 9 | 182 | 365.8125 | 95.0549 | 273.9062 | 96.7142 | Calcium hardness | mg/L as CaCO3 | 10 | 180 | 1059 | 1095.8065 | -3.4756 | 94.4444 | 637.9032 | 98.4324 | Calcium hardness | mg/L as CaCO3 | 12 | 180 | #DIV/0! | 93.3333 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | 10 | 182 | 1012 | 1108.5806 | -9.5435 | 94.5055 | 645.2903 | 98.4503 | Calcium hardness | mg/L as CaCO3 | 10 | 182 | 361.0928 | 94.5055 | 271.5464 | 96.3174 | Calcium hardness | mg/L as CaCO3 | 9 | 189 | 965 | 1158.6774 | -20.0702 | 95.2381 | 673.8387 | 98.6644 | Calcium hardness | mg/L as CaCO3 | 10 | 189 | 375.3814 | 94.709 | 282.1907 | 96.4563 | Calcium hardness | mg/L as CaCO3 | 12 | 185 | 1079 | 1148.0333 | -6.3979 | 93.5135 | 666.5167 | 98.1996 | Calcium hardness | mg/L as CaCO3 | 12 | 185 | 363.3505 | 93.5135 | 274.1753 | 95.6232 | Calcium hardness | mg/L as CaCO3 | 10 | 179 | 1035 | 1089.4194 | -5.2579 | 94.4134 | 634.2097 | 98.4232 | Calcium hardness | mg/L as CaCO3 | 9 | 375 | 741 | 94.9721 | 558 | 98.3871 | Current Process Water Rate ($/1000 gal) | 0.21*
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Permeate flow rate from system, Qp-sys (gpm) | 16.375 | SDI | 4.67 |  |  |  | 1998-06-11 | 20:00 | 5620.41 | 25.5556 | 100 | 78 | 9.6333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.9696 | 67.397 | 0.22998 | 7.5 | 6.41 | 33.902 | 304.61 | 350.28 | 854 | 2111.4509 | -147.2425 | 90.3215 | 1230.8654 | 97.2457 | 100 | 76 | 9.5 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8325 | 73.6675 | 0.20948 | 6.41 | NA | 29.205 | 350.28 | 578.16 | 674.6313 | -16.6859 | 91.6624 | 512.4556 | 94.301 | 76 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8974 | 50.5026 | 0.28397 | NA | NA | 37.24 | 578.16 | 921.32 | 1075.8064 | -16.7679 | 89.3685 | 826.9832 | 95.4969 | 120 | 78 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.5801 | 77.6199 | 0.24615 | NA | 7.1 | 73.997 | 921.32 | 1221.22 | 1542.6902 | -26.3237 | 78.8749 | 1232.0051 | 93.9938 | Turbidity | ntu | 0.02 | 0.05 | 33.95 | 0.21161 | 99.3767 | 60 | 0.13081 | 84.7102 | Turbidity | ntu | 0.04 | 0.05 | 0.060625 | 20 | 0.055313 | 27.6836 | Turbidity | ntu | 0.01 | 0.05 | 36 | 0.26548 | 99.2625 | 80 | 0.15774 | 93.6605 | Turbidity | ntu | 0.03 | 0.05 | #DIV/0! | 40 | #DIV/0! | #DIV/0! | Turbidity | ntu | 0 | 0.04 | 33 | 0.25548 | 99.2258 | 100 | 0.14774 | 100 | Turbidity | ntu | 0.01 | 0.04 | 0.071237 | 75 | 0.055619 | 82.0204 | Turbidity | ntu | BMRL | 0.07 | 32 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.07 | 0.12206 | 71.4286 | 0.096031 | 79.1734 | Turbidity | ntu | BMRL | 0.06 | 37.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.04 | 0.06 | 0.080619 | 33.3333 | 0.070309 | 43.1085 | Turbidity | ntu | BMRL | 0.05 | 36 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | Feed flow rate to system, QF-sys (gpm) | 19.2647 | MFI | NA |  |  |  | 1998-06-12 | 9:00 | 5633.31 | 25.5556 | 100 | 78 | 9.3333 | 0 | 16.3 | 3 |  | 19.3 | 19.3 | 0.84456 | 0 | 14.9313 | 15.1287 | 10.8608 | 68.8059 | 0.21988 | 7.5 | 6.39 | 33.701 | 264.77 | 325.92 | 769 | 1913.6432 | -148.8483 | 89.6597 | 1119.7816 | 96.9904 | 100 | 78 | 9.2 | 9.9 | 9.4 | 19.3 | 19.3 | 0.4694 | 0.51295 | 15.2308 | 15.4322 | 4.5918 | 75.2082 | 0.20519 | 6.39 | NA | 25.134 | 325.92 | 497.97 | 642.7053 | -29.0651 | 92.2883 | 484.3126 | 94.8104 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.7614 | 53.2386 | 0.26937 | NA | NA | 34.86 | 497.97 | 796.08 | 924.0312 | -16.0727 | 89.3041 | 711.0006 | 95.0971 | 120 | 78 | 9.8 | 1.8 | 3 | 4.8 | 4.8 | 0.52624 | 0.375 | 15.4286 | 15.6326 | 9.5893 | 79.6107 | 0.19636 | NA | 7.2 | 58.443 | 796.08 | 1099.67 | 1238.6622 | -12.6394 | 82.0683 | 1017.3711 | 94.2555 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.16 | 5.65 | 11.4831 | 97.1681 | 8.5666 | 98.1323 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.41 | 5.75 | #DIV/0! | 92.8696 | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.21 | 5.63 | 11.2735 | 96.27 | 8.4518 | 97.5153 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.16 | 5.21 | 10.4682 | 96.929 | 7.8391 | 97.959 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.47 | 1.89 | 3.3539 | 75.1323 | 2.622 | 82.0745 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.16 | 11.5 | 22.84 | 97.0642 | 17.17 | 99.0681
|  | Minimum flow rate to the element, QI, min (gpm) | 6.5 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.8897 | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-06-12 | 16:00 | 5640.31 | 25.5556 | 100 | 78 | 9.3333 | 0 | 16.5 | 3 |  | 19.5 | 19.5 | 0.84615 | 0 | 15.1145 | 15.3144 | 10.8297 | 68.837 | 0.22247 | 7.5 | 6.62 | 33.768 | 308.76 | 322.56 | 789 | 1910.916 | -142.1947 | 89.5312 | 1116.738 | 96.9762 | 100 | 76 | 9.2 | 9.9 | 9.6 | 19.5 | 19.5 | 0.47594 | 0.50769 | 15.2308 | 15.4322 | 4.4828 | 74.3172 | 0.20765 | 6.62 | NA | 26.786 | 322.56 | 515.79 | 627.5769 | -21.673 | 91.6958 | 475.0685 | 94.3617 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.0032 | 51.9968 | 0.27581 | NA | NA | 36.12 | 515.79 | 892.8 | 957.0864 | -7.2005 | 88.8021 | 736.4382 | 95.0953 | 120 | 78 | 9.8 | 2 | 3 | 5 | 5 | 0.53973 | 0.4 | 17.1429 | 17.3696 | 11.0611 | 78.1389 | 0.22229 | NA | 7.1 | 63.217 | 892.8 | 1128.27 | 1445.8553 | -28.148 | 80.4015 | 1169.3277 | 94.5937 | Total organic carbon | mg/L | 0.12 | 5.65 | 29 | 35.4406 | -22.2091 | 97.8761 | 20.5453 | 99.4159 | UV254 | cm-1 | 0.004 | 0.23 | 0.47013 | 98.2609 | 0.35006 | 98.8573 | Total organic carbon | mg/L | 0.13 | 5.75 | 30.3 | 36.0255 | -18.896 | 97.7391 | 20.8877 | 99.3776 | UV254 | cm-1 | 0.001 | 0.218 | #DIV/0! | 99.5413 | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 0.26 | 5.63 | 29.65 | 34.5587 | -16.5555 | 95.3819 | 20.0944 | 98.7061 | UV254 | cm-1 | 0.001 | 0.228 | 0.46436 | 99.5614 | 0.34618 | 99.7111 | Total organic carbon | mg/L | 0.15 | 5.21 | 28.6 | 32.4687 | -13.527 | 97.1209 | 18.8394 | 99.2038 | UV254 | cm-1 | 0.002 | 0.221 | 0.44903 | 99.095 | 0.33502 | 99.403 | Total organic carbon | mg/L | 0.34 | 1.89 | 35.25 | 10.5183 | 70.1608 | 82.0106 | 6.2042 | 94.5198 | UV254 | cm-1 | 0.006 | 0.205 | 0.41015 | 97.0732 | 0.30758 | 98.0493 | Total organic carbon | mg/L | 0.09 | 5.45 | 30.4 | 34.3248 | -12.9107 | 98.3486 | 19.8874 | 99.5475 | UV254 | cm-1 | 0.001 | 0.465 | 0.929 | 99.5349 | 0.697 | 99.8565
Plant Name | Hialeah Water Treatment | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  | TOC (mg/L) | 11.35 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-06-13 | 16:00 | 5660.74 | 25.5556 | 100 | 78 | 9.4 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 8.4076 | 71.1924 | 0.21772 | 7.5 | 6.43 | 32.294 | 283.03 | 254.52 | 693 | 1491.5781 | -115.2349 | 87.3118 | 873.049 | 96.301 | 100 | 76 | 9.4 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.3939 | 75.2061 | 0.2052 | 6.43 | NA | 29.028 | 254.52 | 469.26 | 482.3129 | -2.7816 | 88.595 | 368.4165 | 92.1209 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.3054 | 52.6946 | 0.27215 | NA | NA | 37.38 | 469.26 | 903.96 | 866.5896 | 4.1341 | 85.3135 | 667.9248 | 94.4036 | 120 | 78 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.3923 | 77.8077 | 0.24556 | NA | 7.2 | 70.378 | 903.96 | 990.99 | 1515.2535 | -52.903 | 72.3487 | 1209.6067 | 94.1817 | UV254 | cm-1 | 0.002 | 0.23 | 1.208 | 1.4583 | -20.7167 | 99.1304 | 0.84413 | 99.7631 | SUVA | L/(mg*m) | 2.5 | 4.0708 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.218 | 1.102 | 1.387 | -25.8621 | 99.5413 | 0.8025 | 99.8754 | SUVA | L/(mg*m) | 0.2439 | 3.7913 | --- | --- | --- | --- | UV254 | cm-1 | 0.001 | 0.228 | 1.044 | 1.4509 | -38.9723 | 99.5614 | 0.83944 | 99.8809 | SUVA | L/(mg*m) | 0.47619 | 4.0497 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.221 | 1.226 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.25 | 4.2418 | --- | --- | --- | --- | UV254 | cm-1 | 0.003 | 0.205 | 1.078 | 1.3295 | -23.3271 | 98.5366 | 0.76723 | 99.609 | SUVA | L/(mg*m) | 1.2766 | 10.8466 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.215 | 0.57 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.625 | 4.0435 | --- | --- | --- | ---
Treatment Plant Category | Softening | Feed spacer thickness, T (ft) | 0.00258 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-06-13 | 23:30 | 5672.02 | 25.5556 | 100 | 78 | 9.7667 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 10.9987 | 68.2346 | 0.22716 | 7.4 | 6.41 | 36.314 | 307.1 | 341.04 | 1003 | 1931.3288 | -92.5552 | 89.352 | 1136.1844 | 96.8039 | 100 | 76 | 9.8 | 9.9 | 10 | 19.9 | 19.9 | 0.48903 | 0.49749 | 15.2308 | 15.4322 | 4.639 | 73.561 | 0.20979 | 6.41 | NA | 30.739 | 341.04 | 580.14 | 648.238 | -11.7382 | 90.9867 | 494.639 | 93.7856 | 76 | 60 | 9.5 | 4.6 | 5.1 | 9.7 | 9.7 | 0.48412 | 0.47423 | 14.1538 | 14.341 | 7.8347 | 50.6653 | 0.28305 | NA | NA | 40.18 | 580.14 | 1071.36 | 1067.1627 | 0.39177 | 88.2184 | 823.6514 | 95.1217 | 120 | 78 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 13.3762 | 75.6238 | 0.25265 | NA | 7.2 | 75.922 | 1071.36 | 1434.29 | 1755.7236 | -22.4106 | 77.7381 | 1413.5418 | 94.629 | SUVA | L/(mg*m) | 1.6667 | 4.0708 | 4.1655 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.76923 | 3.7913 | 3.637 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.38462 | 4.0497 | 3.5211 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 4.2418 | 4.2867 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.88235 | 10.8466 | 3.0582 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 3.945 | 1.875 | --- | --- | --- | --- | ---
Process Train Name | Hialeah WTP | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 11.1397 | [5 empty] | 1998-06-13 | 6:45 | 5679.13 | 25.5556 | 100 | 78 | 9.7333 | 0 | 16.5 | 3.2 |  | 19.7 | 19.7 | 0.83756 | 0 | 15.1145 | 15.3144 | 8.451 | 70.8156 | 0.21626 | 7.5 | 6.4 | 37.654 | 316.23 | 273.84 | 826 | 1491.6741 | -80.5901 | 86.2496 | 882.757 | 95.7345 | 100 | 76 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.6225 | 74.7775 | 0.20637 | 6.4 | NA | 33.158 | 273.84 | 492.03 | 516.9779 | -5.0704 | 87.8915 | 395.409 | 91.6143 | 76 | 60 | 9.6 | 4.6 | 5.1 | 9.7 | 9.7 | 0.48412 | 0.47423 | 14.1538 | 14.341 | 6.6172 | 51.7828 | 0.27695 | NA | NA | 35.98 | 492.03 | 922.56 | 903.3692 | 2.0802 | 86.8609 | 697.6996 | 94.8431 | 120 | 78 | 10 | 2 | 3.2 | 5.2 | 5.2 | 0.56672 | 0.38462 | 17.1429 | 17.3696 | 11.1758 | 77.8242 | 0.22319 | NA | 7.2 | 71.071 | 922.56 | 1181.18 | 1454.7406 | -23.1599 | 74.0465 | 1188.6503 | 94.0209 | Bromide | mg/L | 7 | 42 | --- | 230.5484 | --- | 83.3333 | 136.2742 | 94.8633 | [8 empty] | Bromide | mg/L | 23 | 63 | --- | 278.4839 | --- | 63.4921 | 170.7419 | 86.5294 | [8 empty] | Bromide | mg/L | 8 | 32 | --- | 161.2903 | --- | 75 | 96.6452 | 91.7223 | [8 empty] | Bromide | mg/L | 9 | 12 | --- | 28.1613 | --- | 25 | 20.0806 | 55.1807 | [8 empty] | Bromide | mg/L | 12 | 13 | --- | 18.5667 | --- | 7.6923 | 15.7833 | 23.9704 | [8 empty] | Bromide | mg/L | 8 | 51 | --- | 282.6452 | --- | 84.3137 | 166.8226 | 95.2045
ICR Treatment Plant Identification Number | 302 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 5.4522 | [5 empty] | 1998-06-14 | 23:00 | 5695.21 | 25.5556 | 100 | 78 | 9.8 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 11.3696 | 67.8304 | 0.22851 | 7.4 | 6.44 | 34.438 | 313.74 | 349.44 | 924 | 1993.3567 | -115.7312 | 90.1448 | 1171.3983 | 97.0601 | 100 | 76 | 9.8 | 9.9 | 10 | 19.9 | 19.9 | 0.48903 | 0.49749 | 15.2308 | 15.4322 | 4.7469 | 73.4531 | 0.2101 | 6.44 | NA | 31.919 | 349.44 | 609.84 | 663.7858 | -8.8459 | 90.8657 | 506.6129 | 93.6995 | 76 | 60 | 9.6 | 4.6 | 5.1 | 9.7 | 9.7 | 0.48412 | 0.47423 | 14.1538 | 14.341 | 8.2453 | 50.1547 | 0.28594 | NA | NA | 41.58 | 609.84 | 1018.04 | 1122.3882 | -10.2499 | 88.101 | 866.1141 | 95.1992 | 120 | 78 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 12.6835 | 76.3165 | 0.25036 | NA | 7.1 | 74.151 | 1018.04 | 1321.32 | 1666.9637 | -26.159 | 78.78 | 1342.5018 | 94.4767 | SDS-Cl2 dose | mg/L | 3.6 | 12.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.6 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.4 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.6 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.6 | 12 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.6 | 13 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | 4130871 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 0.57721 | [5 empty] | 1998-06-15 | 11:30 | 5708.59 | 25.5556 | 100 | 78 | 9.3333 | 0 | 16.3 | 3 |  | 19.3 | 19.3 | 0.84456 | 0 | 14.9313 | 15.1287 | 9.6296 | 70.037 | 0.21601 | 7.6 | 6.64 | 34.907 | 253.15 | 294 | 705 | 1701.7386 | -141.3814 | 88.1269 | 997.8693 | 96.5018 | 100 | 76 | 9 | 9.9 | 9.4 | 19.3 | 19.3 | 0.4694 | 0.51295 | 15.2308 | 15.4322 | 4.0342 | 74.9658 | 0.20586 | 6.64 | NA | 29.736 | 294 | 473.22 | 572.3206 | -20.9418 | 89.8857 | 433.1603 | 93.1351 | 76 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.4072 | 52.5928 | 0.27268 | NA | NA | 34.37 | 473.22 | 727.88 | 876.962 | -20.4817 | 88.3095 | 675.091 | 94.9088 | 120 | 78 | 10 | 1.8 | 3 | 4.8 | 4.8 | 0.52624 | 0.375 | 15.4286 | 15.6326 | 8.7187 | 80.2813 | 0.19472 | NA | 7.2 | 57.211 | 727.88 | 1008.15 | 1130.2814 | -12.1144 | 80.5405 | 929.0807 | 93.8422 | SDS-Free Cl2 residual | mg/L | 0.7 | 0.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.44792 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.98 | 0.78 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46465 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.09 | 0.86 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.45361 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.98 | 0.78 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.45361 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.71 | 0.9 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46392 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1 | 0.92 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46465
Historical Minimum Water Temperature (oC) | 23 | Stage 1 and 2 -- Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-06-15 | 19:30 | 5716.06 | 25.5556 | 100 | 78 | 9.5333 | 0 | 16.5 | 3 |  | 19.5 | 19.5 | 0.84615 | 0 | 15.1145 | 15.3144 | 8.272 | 71.1947 | 0.21511 | 7.4 | 6.5 | 34.773 | 300.46 | 255.36 | 824 | 1468.5885 | -78.2268 | 86.3828 | 861.9742 | 95.9659 | 100 | 76 | 9 | 9.9 | 9.6 | 19.5 | 19.5 | 0.47594 | 0.50769 | 15.2308 | 15.4322 | 3.3946 | 75.6054 | 0.20411 | 6.5 | NA | 31.388 | 255.36 | 566.28 | 486.3311 | 14.1183 | 87.7083 | 370.8456 | 91.5361 | 76 | 60 | 9.6 | 4.6 | 5.1 | 9.7 | 9.7 | 0.48412 | 0.47423 | 14.1538 | 14.341 | 7.7047 | 50.6953 | 0.28289 | NA | NA | 35.28 | 566.28 | 849.4 | 1045.2212 | -23.0541 | 86.1842 | 805.7506 | 95.6215 | 120 | 78 | 10 | 2 | 3 | 5 | 5 | 0.53973 | 0.4 | 17.1429 | 17.3696 | 10.4773 | 78.5227 | 0.2212 | NA | 7.1 | 63.602 | 849.4 | 1178.32 | 1373.2653 | -16.5443 | 75.0932 | 1111.3327 | 94.277 | SDS-Cl2 demand | mg/L | 2.9 | 12.2 | --- | 62.3 | --- | 76.2295 | 37.25 | 92.2148 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.3 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.62 | 12.22 | --- | 63.9361 | --- | 78.5597 | 38.0781 | 93.1194 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.31 | 12.14 | --- | 65.0952 | --- | 80.972 | 38.6176 | 94.0183 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.4 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.62 | 12.22 | --- | 63.9361 | --- | 78.5597 | 38.0781 | 93.1194 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.4 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.89 | 11.1 | --- | 56.8023 | --- | 73.964 | 33.9512 | 91.4878 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.6 | 12.08 | --- | 63.1497 | --- | 78.4768 | 37.6148 | 93.0878 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.6
Historical Average Water Temperature (oC) | 26 | Design cross-flow velocity (fps) | 0.75 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-06-16 | 10:00 | 5730.31 | 25.5556 | 100 | 78 | 9.3333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 6.0508 | 73.6159 | 0.21055 | 7.5 | 6.47 | 32.428 | 273.9 | 192.36 | 824 | 1082.6481 | -31.3893 | 83.142 | 637.5041 | 94.9133 | 100 | 76 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 2.4761 | 76.5239 | 0.20166 | 6.47 | NA | 27.848 | 192.36 | 491.04 | 358.5507 | 26.9814 | 85.523 | 275.4553 | 89.8902 | 76 | 60 | 9 | 4.6 | 5.1 | 9.7 | 9.7 | 0.48412 | 0.47423 | 14.1538 | 14.341 | 6.6252 | 52.3748 | 0.27382 | NA | NA | 34.44 | 491.04 | 794.84 | 902.8753 | -13.5921 | 82.0961 | 696.9576 | 95.0585 | 120 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 9.902 | 79.098 | 0.24155 | NA | 7.2 | 70.301 | 794.84 | 1178.32 | 1326.1686 | -12.5474 | 63.4534 | 1060.5043 | 93.371 | SDS-Chlorination temp. | oC | 27 | 27 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.6 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.9 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.7 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.7 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.7 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.9
State Approved Plant Capacity (MGD) | 60 | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 1.8603 | [5 empty] | 1998-06-16 | 17:00 | 5737.39 | 25.5556 | 100 | 78 | 9.3333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 7.467 | 72.1997 | 0.21468 | 7.4 | 6.55 | 33.634 | 269.75 | 231 | 792 | 1329.6707 | -67.8877 | 85.4398 | 780.3354 | 95.6898 | 100 | 76 | 9 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.0363 | 75.9637 | 0.20315 | 6.55 | NA | 29.264 | 231 | 496.98 | 434.7945 | 12.5127 | 87.3316 | 332.8973 | 91.2093 | 76 | 60 | 9 | 4.6 | 5.1 | 9.7 | 9.7 | 0.48412 | 0.47423 | 14.1538 | 14.341 | 6.7124 | 52.2876 | 0.27427 | NA | NA | 34.37 | 496.98 | 773.76 | 914.2361 | -18.155 | 85.1212 | 705.608 | 95.129 | 120 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 9.635 | 79.365 | 0.24074 | NA | 7.2 | 68.761 | 773.76 | 1132.56 | 1290.7593 | -13.9683 | 70.2333 | 1032.2596 | 93.3388 | SDS-Chlorination pH | --- | 6.14 | 6.76 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.71 | 6.54 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 6.09 | 6.84 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.71 | 6.54 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.75 | 6.62 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 5.71 | 6.54 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 17 | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.0478 | [5 empty] | 1998-06-17 | 23:30 | 5768.85 | 25.5556 | 100 | 78 | 9.8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.0072 | 67.1928 | 0.23068 | 7.4 | 6.44 | 40.468 | 302.12 | 357.84 | 902 | 2124.5441 | -135.537 | 88.691 | 1241.1921 | 96.7396 | 100 | 76 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.9303 | 73.2697 | 0.21062 | 6.44 | NA | 30.267 | 357.84 | 595.98 | 688.7556 | -15.5669 | 91.5418 | 523.2978 | 94.2161 | 76 | 60 | 9.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.084 | 50.316 | 0.28502 | NA | NA | 42.28 | 595.98 | 850.64 | 1105.384 | -29.9473 | 88.1847 | 850.682 | 95.0299 | 120 | 78 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.6331 | 78.3669 | 0.24381 | NA | 7.2 | 72.611 | 850.64 | 1289.86 | 1421.1946 | -10.1821 | 79.7085 | 1135.9173 | 93.6077 | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 5 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -0.57721 | [5 empty] | 1998-06-18 | 8:30 | 5776.82 | 25.5556 | 100 | 76 | 9.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4744 | 66.8589 | 0.23183 | 7.3 | 6.42 | 38.592 | 283.86 | 341.88 | 869 | 2030.1832 | -133.6229 | 88.7118 | 1186.0316 | 96.7461 | 100 | 78 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.6999 | 74.7001 | 0.20659 | 6.42 | NA | 29.618 | 341.88 | 558.36 | 657.3283 | -17.7248 | 91.3367 | 499.6042 | 94.0717 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.5562 | 52.0438 | 0.27556 | NA | NA | 40.81 | 558.36 | 810.96 | 1034.506 | -27.5656 | 88.0631 | 796.433 | 94.8759 | 120 | 76 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.1213 | 77.8787 | 0.24534 | NA | 7.1 | 70.378 | 810.96 | 1242.67 | 1354.0535 | -8.9632 | 79.4144 | 1082.5067 | 93.4986 | SDS-TOX | mg Cl- /L | BMRL | 235 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-42 | CI-s2-42 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 355 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-44 | CI-s2-44 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 360 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-46 | CI-s2-46 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 380 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-48 | CI-s2-48 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 360 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-50 | CI-s2-50 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | BMRL | 345 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-50 (dup) | CI-s2-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | Chloride ion rejection = 85 % | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-06-18 | 14:40 | 5783.03 | 25.5556 | 100 | 76 | 9.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.8088 | 66.5246 | 0.233 | 7.4 | 6.91 | 38.994 | 294.65 | 351.12 | 870 | 2088.6214 | -140.0714 | 88.8944 | 1219.8707 | 96.8034 | 100 | 78 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8283 | 74.5717 | 0.20694 | 6.91 | NA | 30.326 | 351.12 | 562.32 | 675.1874 | -20.0717 | 91.3631 | 513.1537 | 94.0903 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.611 | 51.989 | 0.27585 | NA | NA | 41.02 | 562.32 | 810.96 | 1041.916 | -28.4793 | 88.3174 | 802.118 | 94.886 | 120 | 76 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.1202 | 77.8798 | 0.24533 | NA | 7.2 | 70.455 | 810.96 | 1244.1 | 1353.997 | -8.8335 | 79.9342 | 1082.4785 | 93.4913 | SDS-CHCl3 | mg/L | 0.2 | 34.8 | --- | 221.1935 | --- | 99.4253 | 127.9968 | 99.8437 | Sampling date | MM/DD/YY | 1998-06-17 | 1998-06-17 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.29 | 41.2 | --- | 261.5861 | --- | 99.2961 | 151.3931 | 99.8084 | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.25 | 47.5 | --- | 302.0403 | --- | 99.4737 | 174.7702 | 99.857 | Sampling date | MM/DD/YY | 1998-07-15 | 1998-07-15 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | BMRL | 33.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-29 | 1998-07-29 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.39 | 35.4 | --- | 230.289 | --- | 98.8983 | 132.8445 | 99.7064 | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 0.57 | 41.8 | --- | 263.91 | --- | 98.6364 | 152.855 | 99.6271 | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) | at 500 mg/L NaCL solution | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-06-18 | 23:25 | 5791.91 | 25.5556 | 100 | 76 | 9.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.5826 | 66.7507 | 0.23221 | 7.4 | 6.44 | 39.932 | 297.14 | 346.08 | 884 | 2050.3039 | -131.9348 | 88.4616 | 1198.1919 | 96.6673 | 100 | 78 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7577 | 74.6423 | 0.20675 | 6.44 | NA | 29.972 | 346.08 | 540.54 | 665.4136 | -23.1016 | 91.3396 | 505.7468 | 94.0737 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.3063 | 52.2937 | 0.27424 | NA | NA | 40.11 | 540.54 | 858.08 | 1000.9356 | -16.6483 | 88.4102 | 770.7378 | 94.7959 | 120 | 76 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.7126 | 77.2874 | 0.24721 | NA | 7.2 | 74.228 | 858.08 | 1264.12 | 1432.9048 | -13.352 | 78.5518 | 1145.4924 | 93.52 | SDS-BDCM | mg/L | 0.11 | 13.4 | --- | 84.9945 | --- | 99.1791 | 49.1973 | 99.7764 | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.11 | 11.7 | --- | 74.1365 | --- | 99.0598 | 42.9182 | 99.7437 | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 18.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | 14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.14 | 12.7 | --- | 82.6173 | --- | 98.8976 | 47.6587 | 99.7062 | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.25 | 15.3 | --- | 96.3758 | --- | 98.366 | 55.8379 | 99.5523 | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1998-06-19 | 10:00 | 5802.85 | 25.5556 | 100 | 78 | 9.5333 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 10.9343 | 68.5323 | 0.22617 | 7.5 | 6.47 | 35.577 | 331.17 | 338.52 | 1142 | 1919.5038 | -68.0826 | 89.4904 | 1129.0119 | 96.8488 | 100 | 78 | 9.6 | 10.1 | 9.8 | 19.9 | 19.9 | 0.48576 | 0.50754 | 15.5385 | 15.7439 | 4.73 | 74.67 | 0.21085 | 6.47 | NA | 26.373 | 338.52 | 641.52 | 660.2225 | -2.9153 | 92.2093 | 499.3713 | 94.7188 | 78 | 60 | 9.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 8.6936 | 51.1064 | 0.26841 | NA | NA | 37.8 | 641.52 | 1122.2 | 1172.7936 | -4.5084 | 88.8337 | 907.1568 | 95.8331 | 120 | 78 | 9.8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 14.199 | 75.001 | 0.25475 | NA | 7.2 | 65.527 | 1122.2 | 1633.06 | 1848.6627 | -13.2024 | 80.6431 | 1485.4313 | 95.5887 | SDS-DBCM | mg/L | BMRL | 3.23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5752.18 | 5752.18 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 2.66 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5973.25 | 5973.25 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.58 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6167.4 | 6167.4 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.08 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6452.2 | 6452.2 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 3.33 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6694.8 | 6694.8 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 2.88 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5973.25 | 5973.25 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-06-19 | 17:55 | 5810.2 | 25.5556 | 100 | 78 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.9585 | 67.5082 | 0.2296 | 7.4 | 6.61 | 36.716 | 282.2 | 352.8 | 1012 | 2112.3343 | -108.7287 | 89.593 | 1232.5671 | 97.0212 | 100 | 78 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.9086 | 74.4914 | 0.20717 | 6.61 | NA | 26.668 | 352.8 | 648.45 | 682.2599 | -5.214 | 92.441 | 517.5299 | 94.8471 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.9134 | 50.8866 | 0.28182 | NA | NA | 37.94 | 648.45 | 845.68 | 1210.1192 | -43.0942 | 89.246 | 929.2846 | 95.9173 | 120 | 78 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.6095 | 78.5905 | 0.24311 | NA | 7.2 | 69.377 | 845.68 | 1447.16 | 1414.9689 | 2.2244 | 80.3353 | 1130.3244 | 93.8622 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.03 | 6.97 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.85 | 6.72 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.06 | 7.01 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.85 | 6.74 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.81 | 6.75 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.83 | 6.68 | --- | --- | --- | ---
|  | Standard testing pH | 8 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 0.73529 | [5 empty] | 1998-06-20 | 18:15 | 5834.61 | 25.5556 | 100 | 78 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.0119 | 67.4547 | 0.22978 | 7.4 | 6.63 | 36.984 | 298.8 | 354.48 | 944 | 2121.8744 | -124.7748 | 89.5667 | 1238.1772 | 97.013 | 100 | 78 | 9.6 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.901 | 74.499 | 0.20715 | 6.63 | NA | 28.851 | 354.48 | 582.12 | 683.4317 | -17.4039 | 91.861 | 518.9559 | 94.4406 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.942 | 51.858 | 0.27654 | NA | NA | 38.15 | 582.12 | 812.2 | 1082.5724 | -33.2889 | 89.2378 | 832.3462 | 95.4166 | 120 | 78 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.1256 | 79.0744 | 0.24163 | NA | 7.2 | 71.302 | 812.2 | 1349.92 | 1355.5252 | -0.41522 | 79.8855 | 1083.8626 | 93.4215 | SDS-THM4 | mg/L | 0.31 | 51.43 | --- | 326.8184 | --- | 99.3972 | 189.1242 | 99.8361 | Temperature | oC | 25.3 | 25.5 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0.4 | 55.56 | --- | 352.7123 | --- | 99.2801 | 204.1361 | 99.8041 | Temperature | oC | 24.9 | 24.7 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0.25 | 69.48 | --- | 442.4287 | --- | 99.6402 | 255.9544 | 99.9023 | Temperature | oC | 25.6 | 26.8 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 50.88 | --- | 324.9755 | --- | 100 | 187.9277 | 100 | Temperature | oC | 27 | 27.1 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0.53 | 51.43 | --- | 334.7733 | --- | 98.9695 | 193.1017 | 99.7255 | Temperature | oC | 24.6 | 25.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0.82 | 59.98 | --- | 378.6806 | --- | 98.6329 | 219.3303 | 99.6261 | Temperature | oC | 24.9 | 24.7 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 0 to 350 psi | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 0.48529 | [5 empty] | 1998-06-21 | 13:00 | 5853.57 | 25.5556 | 100 | 76 | 9.2667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.2838 | 67.4496 | 0.2298 | 7.4 | 6.84 | 36.381 | 292.16 | 341.88 | 928 | 1987.6327 | -114.1846 | 89.3585 | 1164.7563 | 96.8765 | 100 | 78 | 9.4 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.7131 | 74.8869 | 0.20607 | 6.84 | NA | 27.671 | 341.88 | 560.34 | 656.089 | -17.0877 | 91.9062 | 498.9845 | 94.4545 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.6322 | 52.3678 | 0.27385 | NA | NA | 37.59 | 560.34 | 823.36 | 1041.27 | -26.4659 | 89.0049 | 800.805 | 95.306 | 120 | 76 | 9.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.1913 | 78.4087 | 0.24368 | NA | 7.1 | 71.148 | 823.36 | 1327.04 | 1357.1879 | -2.2718 | 79.1892 | 1090.2739 | 93.4743 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 293 | 514.4906 | 86.3014 | 403.7453 | 95.0464 | SDS-MCAA* | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 203 | 362.6981 | 83.4783 | 282.8491 | 93.2826 | SDS-MCAA* | mg/L | BMRL | 2.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 21 | 335 | 595.6792 | 85.1064 | 465.3396 | 95.4872 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 223 | 392.3585 | 84.5528 | 307.6792 | 93.8247 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 25 | 222 | 392.4808 | 78.0702 | 307.2404 | 91.863 | SDS-MCAA* | mg/L | BMRL | 2.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 205 | 366.434 | 83.4783 | 285.717 | 93.3501
|  | Acceptable range of operating pH values | 4 to 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | -2.1397 | [5 empty] | 1998-06-21 | 18:25 | 5858.13 | 25.5556 | 100 | 76 | 9.2667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.3546 | 67.3788 | 0.23004 | 7.4 | 6.56 | 36.984 | 290.5 | 344.4 | 935 | 2000.4797 | -113.9551 | 89.2613 | 1172.4399 | 96.8456 | 100 | 78 | 9.4 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.7607 | 74.8393 | 0.2062 | 6.56 | NA | 27.022 | 344.4 | 518.76 | 661.778 | -27.5692 | 92.1539 | 503.089 | 94.6288 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.02 | 52.98 | 0.27069 | NA | NA | 37.94 | 518.76 | 828.32 | 961.1144 | -16.0318 | 88.9837 | 739.9372 | 94.8725 | 120 | 76 | 9.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.2355 | 78.3645 | 0.24382 | NA | 7.2 | 72.842 | 828.32 | 1337.05 | 1364.4657 | -2.0505 | 78.8496 | 1096.3928 | 93.3562 | SDS-DCAA* | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 41 | 612 | 1075.2642 | 87.5 | 843.6321 | 95.1401 | SDS-DCAA* | mg/L | BMRL | 22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 41.9 | 601 | 1086.2566 | 87.1865 | 843.6283 | 95.0334 | SDS-DCAA* | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 44 | 607 | 1074.3962 | 86.4198 | 840.6981 | 94.7663 | SDS-DCAA* | mg/L | BMRL | 21 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 42 | 603 | 1068.7358 | 87.3874 | 835.8679 | 94.9753 | SDS-DCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 43 | 598 | 1078.2885 | 86.9697 | 838.1442 | 94.8696 | SDS-DCAA* | mg/L | BMRL | 23 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 42 | 610 | 1102.9811 | 87.156 | 856.4906 | 95.0963
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1998-06-22 | 8:30 | 5872.91 | 25.5556 | 100 | 78 | 9.2 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.0812 | 68.7188 | 0.22556 | 7.5 | 6.43 | 34.304 | 291.33 | 334.32 | 824 | 1950.5352 | -136.7154 | 89.7392 | 1142.4276 | 96.9973 | 100 | 78 | 9.2 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.6163 | 75.1837 | 0.20941 | 6.43 | NA | 30.739 | 334.32 | 540.54 | 650.4198 | -20.3278 | 90.8055 | 492.3699 | 93.7569 | 78 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 7.2153 | 52.7847 | 0.25988 | NA | NA | 39.48 | 540.54 | 882.88 | 981.4728 | -11.1672 | 88.191 | 761.0064 | 94.8121 | 120 | 78 | 9.4 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.9434 | 78.6566 | 0.24291 | NA | 7.2 | 75.152 | 882.88 | 1178.32 | 1456.1063 | -23.5748 | 77.5209 | 1169.4932 | 93.574 | SDS-TCAA* | mg/L | BMRL | 25 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 12 | 414 | 740.1509 | 93.7824 | 577.0755 | 97.9205 | SDS-TCAA* | mg/L | BMRL | 32 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 10 | 396 | 731.0189 | 94.8187 | 563.5094 | 98.2254 | SDS-TCAA* | mg/L | BMRL | 38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 13 | 401 | 723.1132 | 93.3333 | 562.0566 | 97.6871 | SDS-TCAA* | mg/L | BMRL | 36 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 11 | 377 | 680.8491 | 94.4724 | 528.9245 | 97.9203 | SDS-TCAA* | mg/L | BMRL | 28 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 12 | 387 | 711.5192 | 94.0299 | 549.2596 | 97.8152 | SDS-TCAA* | mg/L | BMRL | 34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 11 | 386 | 711.4717 | 94.2708 | 548.7358 | 97.9954
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-06-23 | 0:15 | 5888.62 | 25.5556 | 100 | 78 | 9.2667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.7398 | 67.9936 | 0.22796 | 7.4 | 6.48 | 35.778 | 300.46 | 346.08 | 865 | 2073.4278 | -139.7026 | 89.6619 | 1209.7539 | 97.0425 | 100 | 78 | 9.4 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.7817 | 74.8183 | 0.20626 | 6.48 | NA | 28.379 | 346.08 | 556.38 | 667.0228 | -19.8862 | 91.7999 | 506.5514 | 94.3976 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.558 | 52.442 | 0.27346 | NA | NA | 38.71 | 556.38 | 863.04 | 1032.6364 | -19.651 | 88.8147 | 794.5082 | 95.1278 | 120 | 78 | 9.4 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.7825 | 78.8175 | 0.24241 | NA | 7.2 | 74.074 | 863.04 | 1236.95 | 1441.6151 | -16.5459 | 78.5963 | 1152.3275 | 93.5718 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 10 | 390 | 698.3019 | 94.5055 | 544.1509 | 98.1623 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 349 | 644.0943 | 95 | 496.5472 | 98.1875 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 12 | 389 | 701.9811 | 93.4066 | 545.4906 | 97.8001 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 10 | 365 | 659.717 | 94.709 | 512.3585 | 98.0482 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 12 | 380 | 698.4615 | 93.5135 | 539.2308 | 97.7746 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 9 | 375 | 692.6604 | 94.9721 | 533.8302 | 98.3141
|  | Maximum permissible turbidity (ntu) | 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 1.8603 | [5 empty] | 1998-06-23 | 8:00 | 5896.79 | 25.5556 | 100 | 78 | 9.2 | 0 | 16.3 | 3 |  | 19.3 | 19.3 | 0.84456 | 0 | 14.9313 | 15.1287 | 11.534 | 68.266 | 0.22161 | 7.4 | 6.46 | 34.907 | 292.16 | 345.24 | 823 | 2031.3826 | -146.8266 | 89.8891 | 1188.3113 | 97.0625 | 100 | 78 | 9.2 | 9.9 | 9.4 | 19.3 | 19.3 | 0.4694 | 0.51295 | 15.2308 | 15.4322 | 4.7913 | 75.0087 | 0.20574 | 6.46 | NA | 31.388 | 345.24 | 538.56 | 675.7863 | -25.4802 | 90.9084 | 510.5131 | 93.8517 | 78 | 60 | 9 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.355 | 52.645 | 0.27241 | NA | NA | 34.79 | 538.56 | 881.64 | 1002.0284 | -13.6551 | 89.923 | 770.2942 | 95.4835 | 120 | 78 | 9.4 | 1.8 | 3 | 4.8 | 4.8 | 0.52624 | 0.375 | 15.4286 | 15.6326 | 10.5434 | 79.0566 | 0.19774 | NA | 7.2 | 70.609 | 881.64 | 1176.89 | 1368.2586 | -16.2605 | 79.5479 | 1124.9493 | 93.7234 | SDS-DBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 2.65 | 4.7838 | 60 | 3.7169 | 99.4619 | SDS-DBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 0.14 | 0.25283 | 80 | 0.19642 | 94.9087 | SDS-DBAA* | mg/L | BMRL | 1.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 3.1 | 5.6653 | 75 | 4.3826 | 99.7718 | SDS-DBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.01 | 0.16 | 0.28453 | 85.7143 | 0.22226 | 95.5008 | SDS-DBAA* | mg/L | BMRL | 1.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | Zero for extended use | Maximum system recycle flow rate, (QR-sys)max (gpm) | -2.1397 | [5 empty] | 1998-06-26 | 8:00 | 5918.21 | 25.5556 | 100 | 72 | 8.4 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.9538 | 67.6462 | 0.22913 | 9.5 | 6.51 | 36.783 | 294.65 | 299.88 | 837 | 1764.4533 | -110.8068 | 87.7341 | 1032.1666 | 96.4363 | 100 | 78 | 8.2 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.2008 | 76.5992 | 0.20554 | 6.51 | NA | 24.603 | 299.88 | 497.97 | 589.4943 | -18.3795 | 91.7957 | 444.6872 | 94.4673 | 78 | 60 | 8.5 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.6436 | 53.8564 | 0.2547 | NA | NA | 36.61 | 497.97 | 844.44 | 903.9668 | -7.0493 | 87.7918 | 700.9684 | 94.7772 | 120 | 72 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.7788 | 76.7212 | 0.24904 | NA | 9.2 | 55.748 | 844.44 | 1196.91 | 1422.8141 | -18.8739 | 81.4099 | 1133.6271 | 95.0823 | SDS-BCAA* | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.23 | 10.75 | 19.2851 | 95.9292 | 15.0175 | 98.4685 | SDS-BCAA* | mg/L | BMRL | 6.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.11 | 11.75 | 21.8526 | 98.087 | 16.8013 | 99.3453 | SDS-BCAA* | mg/L | BMRL | 7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.38 | 11.75 | 21.1892 | 93.2504 | 16.4696 | 97.6927 | SDS-BCAA* | mg/L | BMRL | 7.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.2 | 10 | 18.1358 | 96.1612 | 14.0679 | 98.5783 | SDS-BCAA* | mg/L | BMRL | 6.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 2.18 | 11.45 | 19.4721 | -15.3439 | 15.4611 | 85.9001 | SDS-BCAA* | mg/L | BMRL | 6.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.16 | 11.5 | 21.3423 | 97.0642 | 16.4211 | 99.0256
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-06-27 | 0:00 | 5933.51 | 25.5556 | 100 | 72 | 8.4 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.8686 | 67.7314 | 0.22885 | 8.6 | 6.51 | 36.515 | 300.46 | 297.36 | 840 | 1749.3972 | -108.2616 | 87.7203 | 1023.3786 | 96.4319 | 100 | 78 | 8.2 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.1543 | 76.6457 | 0.20541 | 6.51 | NA | 25.134 | 297.36 | 504.9 | 583.7644 | -15.6198 | 91.5476 | 440.5622 | 94.295 | 78 | 60 | 8.5 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.7353 | 53.7647 | 0.25514 | NA | NA | 37.17 | 504.9 | 861.8 | 916.5024 | -6.3475 | 87.5 | 710.7012 | 94.77 | 120 | 72 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.9971 | 76.5029 | 0.24975 | NA | 7.8 | 57.134 | 861.8 | 1201.2 | 1451.8884 | -20.8698 | 80.7863 | 1156.8442 | 95.0612 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.002 | 0.479 | 0.866 | 99.1304 | 0.6725 | 99.7026 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.467 | 0.87145 | 99.5413 | 0.66923 | 99.8506 | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.472 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.481 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.002 | 0.464 | 0.86381 | 99.0244 | 0.6639 | 99.6988 | SDS-TBAA | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.001 | 0.465 | 0.86772 | 99.5349 | 0.66636 | 99.8499
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 19.2647 | [5 empty] | 1998-06-27 | 9:00 | 5942.88 | 25.5556 | 100 | 72 | 9.4667 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 9.7133 | 66.82 | 0.23891 | 7.2 | 6.47 | 39.999 | 278.05 | 297.36 | 773 | 1725.2985 | -123.1951 | 86.5486 | 1011.3292 | 96.0449 | 100 | 74 | 9.2 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.0594 | 73.7406 | 0.21985 | 6.47 | NA | 31.211 | 297.36 | 519.75 | 576.9509 | -11.0055 | 89.504 | 437.1554 | 92.8604 | 74 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.9578 | 50.6422 | 0.28318 | NA | NA | 43.19 | 519.75 | 804.76 | 958.1852 | -19.0647 | 85.4755 | 738.9676 | 94.1554 | 120 | 72 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.0321 | 76.1679 | 0.25085 | NA | 6.8 | 64.295 | 804.76 | 1105.39 | 1330.2513 | -20.3423 | 78.3781 | 1067.5056 | 93.9771 | SDS-CDBAA | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.86957 | 4.4558 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.90909 | 3.9745 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 4.017 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 4.81 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.091743 | 4.0524 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | 2.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.625 | 4.0435 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-06-28 | 5:25 | 5963.01 | 25.5556 | 100 | 72 | 9.1333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 9.6625 | 67.2041 | 0.23755 | 7.2 | 6.43 | 39.664 | 282.2 | 295.68 | 778 | 1716.1559 | -120.5856 | 86.5855 | 1005.9179 | 96.0569 | 100 | 78 | 9.2 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 4.0185 | 75.7815 | 0.21393 | 6.43 | NA | 32.214 | 295.68 | 518.76 | 572.4524 | -10.3501 | 89.1051 | 434.0662 | 92.5786 | 78 | 60 | 9.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.9392 | 52.6608 | 0.27233 | NA | NA | 43.47 | 518.76 | 798.56 | 956.0268 | -19.7188 | 85.2983 | 737.3934 | 94.1049 | 120 | 72 | 8.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 9.9575 | 77.2425 | 0.24736 | NA | 7.4 | 63.602 | 798.56 | 1112.54 | 1320.1431 | -18.6603 | 78.4896 | 1059.3515 | 93.9961 | SDS-DCBAA | mg/L | BMRL | 10 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 14 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 15 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 11 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-06-29 | 14:00 | 5978.87 | 25.5556 | 100 | 70 | 8.9333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 9.2072 | 66.8594 | 0.23877 | 7.4 | 6.56 | 39.128 | 268.92 | 283.08 | 767 | 1636.6201 | -113.3794 | 86.1778 | 959.8501 | 95.9235 | 100 | 78 | 9 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 3.8398 | 76.1602 | 0.21286 | 6.56 | NA | 31.329 | 283.08 | 510.84 | 547.5457 | -7.1854 | 88.9328 | 415.3128 | 92.4565 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.8287 | 52.9713 | 0.27073 | NA | NA | 43.12 | 510.84 | 779.96 | 941.1424 | -20.6655 | 84.7676 | 725.9912 | 94.0605 | 120 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 9.7149 | 76.6851 | 0.24916 | NA | 7.3 | 62.909 | 779.96 | 1096.81 | 1288.8349 | -17.5076 | 77.777 | 1034.3975 | 93.9183 | SDS-HAA5 | mg/L | 0 | 43.3 | --- | 276.5613 | --- | 100 | 159.9306 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 57.1 | --- | 364.7032 | --- | 100 | 210.9016 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 65 | --- | 415.1613 | --- | 100 | 240.0806 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 58.3 | --- | 372.3677 | --- | 100 | 215.3339 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 47.2 | --- | 309.9467 | --- | 100 | 178.5733 | 100 | [8 empty] | SDS-HAA5 | mg/L | 0 | 60.5 | --- | 386.4194 | --- | 100 | 223.4597 | 100
|  | Stage 3 -- General Information |  | maximum system recycle flow rates. | [6 empty] | 1998-06-30 | 5:25 | 5988.66 | 25.5556 | 100 | 70 | 8.9333 | 0 | 17.2 | 3.1 |  | 20.3 | 20.3 | 0.84729 | 0 | 15.7557 | 15.9641 | 9.1172 | 66.9495 | 0.23845 | 7.4 | 6.35 | 38.994 | 269.75 | 280.56 | 764 | 1620.8617 | -112.1547 | 86.1014 | 950.7108 | 95.8984 | 100 | 78 | 9 | 10.4 | 9.9 | 20.3 | 20.3 | 0.49394 | 0.51232 | 16 | 16.2116 | 3.8104 | 76.1896 | 0.21278 | 6.35 | NA | 30.739 | 280.56 | 512.82 | 542.9982 | -5.8848 | 89.0437 | 411.7791 | 92.5351 | 78 | 60 | 9.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 6.8454 | 52.9546 | 0.27082 | NA | NA | 43.96 | 512.82 | 783.68 | 944.1712 | -20.4792 | 84.3313 | 728.4956 | 93.9656 | 120 | 70 | 8.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 9.7611 | 76.6389 | 0.24931 | NA | 7.2 | 63.217 | 783.68 | 1092.52 | 1294.9763 | -18.5311 | 77.4676 | 1039.3282 | 93.9175 | SDS-HAA6 | mg/L | 0 | 49.8 | --- | 318.0774 | --- | 100 | 183.9387 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 63.8 | --- | 407.4968 | --- | 100 | 235.6484 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 72 | --- | 459.871 | --- | 100 | 265.9355 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 65.7 | --- | 419.6323 | --- | 100 | 242.6661 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 53.7 | --- | 352.63 | --- | 100 | 203.165 | 100 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 67.4 | --- | 430.4903 | --- | 100 | 248.9452 | 100 | Stage 3 Operating Parameters During Sample Collection
|  | Membrane manufacturer | Fluid Systems | [7 empty] | 1998-06-30 | 9:55 | 5993.18 | 25.5556 | 100 | 70 | 8.3667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.9359 | 66.6975 | 0.23239 | 7.4 | 6.43 | 46.498 | 293.82 | 309.12 | 874 | 1771.0491 | -102.6372 | 84.9579 | 1040.0846 | 95.5294 | 100 | 78 | 8.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.1686 | 76.6314 | 0.20138 | 6.43 | NA | 32.155 | 309.12 | 610.83 | 588.9112 | 3.5884 | 89.5979 | 449.0156 | 92.8388 | 78 | 60 | 8.5 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.2927 | 52.2073 | 0.27469 | NA | NA | 42.84 | 610.83 | 891.56 | 1133.3808 | -27.1233 | 86.1413 | 872.1054 | 95.0877 | 120 | 70 | 8.4 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.3259 | 75.2741 | 0.25383 | NA | 7.4 | 62.832 | 891.56 | 1249.82 | 1499.2939 | -19.9608 | 79.6739 | 1195.4269 | 94.744 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41509 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41509 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41509 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41509 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42308 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.41509
|  | Membrane trade name | TFC-S | Summary of the Stage and System Flow Rates | [6 empty] | 1998-06-30 | 14:00 | 5997.57 | 25.5556 | 100 | 70 | 8.4667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.506 | 67.0274 | 0.23125 | 7.3 | 6.34 | 44.421 | 287.18 | 295.68 | 857 | 1694.3551 | -97.7077 | 84.9767 | 995.0176 | 95.5357 | 100 | 76 | 8.4 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.9779 | 75.6221 | 0.20407 | 6.34 | NA | 31.388 | 295.68 | 580.14 | 562.6689 | 3.0115 | 89.3845 | 429.1744 | 92.6864 | 76 | 60 | 8.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8476 | 51.5524 | 0.27818 | NA | NA | 42.63 | 580.14 | 877.92 | 1074.6492 | -22.4086 | 85.5824 | 827.3946 | 94.8477 | 120 | 70 | 8.4 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.1416 | 75.4584 | 0.25321 | NA | 7.4 | 62.678 | 877.92 | 1225.51 | 1475.7641 | -20.4204 | 78.8021 | 1176.8421 | 94.6741 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2
|  | Membrane element model number | SC 2540S | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.2647 | [5 empty] | 1998-07-01 | 0:30 | 6007.12 | 25.5556 | 100 | 70 | 8.4667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.4855 | 67.0478 | 0.23118 | 7.2 | 6.36 | 43.282 | 286.35 | 294 | 862 | 1689.6635 | -96.0167 | 85.2782 | 991.8318 | 95.6362 | 100 | 76 | 8.4 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.9437 | 75.6563 | 0.20398 | 6.36 | NA | 31.978 | 294 | 578.16 | 558.6957 | 3.3666 | 89.1231 | 426.3478 | 92.4996 | 76 | 60 | 8.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8095 | 51.5905 | 0.27798 | NA | NA | 43.26 | 578.16 | 886.6 | 1070.268 | -20.716 | 85.2857 | 824.214 | 94.7514 | 120 | 70 | 8.4 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.2476 | 75.3524 | 0.25356 | NA | 7.4 | 63.602 | 886.6 | 1232.66 | 1490.1319 | -20.8875 | 78.3667 | 1188.3659 | 94.6479 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.2 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.3
|  | Molecular weight cutoff (Daltons) | 300 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.75 | [5 empty] | 1998-07-01 | 7:30 | 6014.62 | 25.5556 | 100 | 70 | 8.4667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.5923 | 66.941 | 0.23155 | 7.3 | 6.23 | 43.818 | 272.24 | 297.36 | 846 | 1708.7438 | -101.9792 | 85.2643 | 1003.0519 | 95.6315 | 100 | 78 | 8.4 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.9969 | 76.6031 | 0.20146 | 6.23 | NA | 31.801 | 297.36 | 595.98 | 565.6288 | 5.0927 | 89.3056 | 431.4944 | 92.63 | 78 | 60 | 8.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.0738 | 52.3262 | 0.27407 | NA | NA | 42.98 | 595.98 | 870.48 | 1104.74 | -26.9116 | 85.5461 | 850.36 | 94.9457 | 120 | 70 | 8.4 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.0252 | 75.5748 | 0.25282 | NA | 7.4 | 63.756 | 870.48 | 1209.78 | 1462.0776 | -20.8548 | 78.5593 | 1166.2788 | 94.5334 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.5147 | [5 empty] | 1998-07-01 | 14:30 | 6021.84 | 25.5556 | 100 | 70 | 8.4333 | 0 | 16.6 | 3 |  | 19.6 | 19.6 | 0.84694 | 0 | 15.2061 | 15.4072 | 9.3678 | 67.1989 | 0.22928 | 7.3 | 6.4 | 43.617 | 278.88 | 292.32 | 822 | 1668.4766 | -102.9777 | 85.079 | 980.3983 | 95.5511 | 100 | 76 | 8.2 | 9.9 | 9.7 | 19.6 | 19.6 | 0.47922 | 0.5051 | 15.2308 | 15.4322 | 3.9551 | 75.8449 | 0.20347 | 6.4 | NA | 30.444 | 292.32 | 587.07 | 559.5955 | 4.6799 | 89.5854 | 425.9578 | 92.8528 | 76 | 60 | 8.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.956 | 51.444 | 0.27877 | NA | NA | 42.14 | 587.07 | 848.16 | 1088.4056 | -28.3255 | 85.5843 | 837.7378 | 94.9698 | 120 | 70 | 8.5 | 2.1 | 3 | 5.1 | 5.1 | 0.54648 | 0.41176 | 18 | 18.238 | 10.604 | 75.896 | 0.2403 | NA | 7.2 | 62.678 | 848.16 | 1175.46 | 1397.9974 | -18.9319 | 78.5584 | 1123.0787 | 94.4191 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.5147 | [5 empty] | 1998-07-02 | 0:15 | 6031.48 | 25.5556 | 100 | 70 | 8.4333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.3367 | 67.2299 | 0.23055 | 7.2 | 6.33 | 43.014 | 273.9 | 289.8 | 825 | 1663.5754 | -101.6455 | 85.1573 | 976.6877 | 95.5959 | 100 | 76 | 8.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 3.8947 | 75.9053 | 0.20331 | 6.33 | NA | 31.034 | 289.8 | 588.06 | 551.2065 | 6.267 | 89.2912 | 420.5032 | 92.6198 | 76 | 60 | 8.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.9582 | 51.4418 | 0.27878 | NA | NA | 42.98 | 588.06 | 853.12 | 1089.5336 | -27.7116 | 85.1691 | 838.7968 | 94.876 | 120 | 70 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.7732 | 75.7268 | 0.25231 | NA | 7.2 | 64.834 | 853.12 | 1179.75 | 1431.1964 | -21.3135 | 77.628 | 1142.1582 | 94.3236 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-42 | CI-s3-42 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-44 | CI-s3-44 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-46 | CI-s3-46 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-48 | CI-s3-48 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-50 | CI-s3-50 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-50 (dup) | CI-s3-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane hydrophobicity | Hydrophilic | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.875 | [5 empty] | 1998-07-02 | 9:15 | 6040.42 | 25.5556 | 100 | 70 | 8.4333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 9.6469 | 66.9197 | 0.23162 | 7.2 | 6.39 | 43.215 | 280.54 | 298.2 | 832 | 1717.6165 | -106.4443 | 85.508 | 1007.9082 | 95.7124 | 100 | 76 | 8.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.0069 | 75.7931 | 0.20361 | 6.39 | NA | 31.978 | 298.2 | 580.14 | 567.1386 | 2.2411 | 89.2763 | 432.6693 | 92.6091 | 76 | 60 | 8.6 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 7.8354 | 51.5646 | 0.27812 | NA | NA | 43.47 | 580.14 | 830.8 | 1073.8764 | -29.2581 | 85.4225 | 827.0082 | 94.7437 | 120 | 70 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.4871 | 76.0129 | 0.25136 | NA | 7.2 | 63.448 | 830.8 | 1189.76 | 1393.5248 | -17.1265 | 78.723 | 1112.1624 | 94.2951 | Qp/QT (THM4), % | -40.2387 | 30.1839 |  | Qp/QT (HAA5), % | -24.7113 | 37.6443 |  |  |  | Sampling date | MM/DD/YY | 1998-06-17 | 1998-06-17 | --- | --- | --- | --- | Qp/QT (THM4), % | -29.8042 | 35.4605 |  | Qp/QT (HAA5), % | 5.4291 | 52.7145 |  |  |  | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | Qp/QT (THM4), % | -3.64 | 48.3605 |  | Qp/QT (HAA5), % | 16.9231 | 58.4615 |  |  |  | Sampling date | MM/DD/YY | 1998-07-15 | 1998-07-15 | --- | --- | --- | --- | Qp/QT (THM4), % | -41.5094 | 29.2453 |  | Qp/QT (HAA5), % | 7.3756 | 53.6878 |  |  |  | Sampling date | MM/DD/YY | 1998-07-29 | 1998-07-29 | --- | --- | --- | --- | Qp/QT (THM4), % | -40.4126 | 30.3143 |  | Qp/QT (HAA5), % | -14.4068 | 42.7966 |  |  |  | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | --- | --- | --- | --- | Qp/QT (THM4), % | -20.3178 | 40.5341 |  | Qp/QT (HAA5), % | 10.7438 | 55.3719 |  |  |  | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 4.6397 | [5 empty] | 1998-07-06 | 10:10 | 6065.13 | 25.5556 | 100 | 72 | 10.4 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 4.6872 | 70.9128 | 0.21858 | 8 | 6.99 | 32.361 | 294.65 | 159.264 | 756 | 842.9027 | -11.4951 | 79.6809 | 501.0834 | 93.5418 | 100 | 80 | 10.2 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 1.984 | 77.816 | 0.20232 | 6.99 | NA | 28.792 | 159.264 | 508.86 | 295.1163 | 42.0044 | 81.9218 | 227.1901 | 87.3269 | 80 | 60 | 10 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.8054 | 53.1946 | 0.25787 | NA | NA | 36.26 | 508.86 | 808.48 | 924.748 | -14.3811 | 77.2328 | 716.804 | 94.9414 | 120 | 72 | 11 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.0429 | 74.9571 | 0.2549 | NA | 7.6 | 67.221 | 808.48 | 1081.08 | 1334.5348 | -23.4446 | 57.7927 | 1071.5074 | 93.7265 | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 32.1862 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 52.5653 | 26.4827 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 57.7642 | 29.0071 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 47.1273 | 23.5636 |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 29.6465 |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 53.624 | 27.222 |  |  |  | Sampling time | hh:mm | 8:30 | 8:30 | --- | --- | --- | ---
|  |  |  | Influent flow rate to stage 3, QI-s(3) (gpm) | 4.6397 | [5 empty] | 1998-07-09 | 4:30 | 6072.36 | 25.5556 | 98 | 70 | 10.2333 | 0 | 16.95 | 3.1 |  | 20.05 | 20.05 | 0.84539 | 0 | 15.5267 | 15.732 | 11.9702 | 61.7965 | 0.25458 | 7.6 | 6.33 | 35.577 | 346.94 | 356.16 | 1077 | 2109.0251 | -95.8241 | 90.011 | 1232.5926 | 97.1136 | 98 | 73 | 10.2 | 10.15 | 9.9 | 20.05 | 20.05 | 0.48985 | 0.50623 | 15.6154 | 15.8219 | 4.8921 | 70.4079 | 0.22472 | 6.33 | NA | 32.745 | 356.16 | 651.42 | 687.742 | -5.5758 | 90.8061 | 521.951 | 93.7264 | 73 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.8546 | 47.6454 | 0.30099 | NA | NA | 44.94 | 651.42 | 1109.8 | 1209.3816 | -8.9729 | 87.3821 | 930.4008 | 95.1698 | 119 | 70 | 10.5 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 14.0908 | 69.9092 | 0.2733 | NA | 7.1 | 69.762 | 1109.8 | 1540.11 | 1847.8915 | -19.9844 | 80.4127 | 1478.8457 | 95.2827 | SDS-HAA5b, mg/L | NA | 30.2304 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 5752.18 | 5752.18 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 36.8521 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 5973.25 | 5973.25 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 33.5657 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 6167.4 | 6167.4 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 41.25 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 6452.2 | 6452.2 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 32.8916 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 6694.8 | 6694.8 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | 35.9768 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 5973.25 | 5973.25 | --- | --- | --- | ---
|  | Stage 3 -- Design Parameters |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.75 | [5 empty] | 1998-07-09 | 22:45 | 6078.34 | 25.5556 | 98 | 70 | 10.2667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.3195 | 62.4138 | 0.24834 | 7.4 | 6.34 | 34.572 | 329.51 | 341.04 | 1042 | 1992.0128 | -91.1721 | 89.8628 | 1166.5264 | 97.0363 | 98 | 72 | 10.2 | 9.9 | 9.9 | 19.8 | 19.8 | 0.48576 | 0.5 | 15.2308 | 15.4322 | 4.6448 | 70.1552 | 0.21997 | 6.34 | NA | 31.388 | 341.04 | 607.86 | 650.692 | -7.0464 | 90.7964 | 495.866 | 93.6701 | 72 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.2421 | 47.7579 | 0.30029 | NA | NA | 43.33 | 607.86 | 1082.52 | 1127.2276 | -4.13 | 87.2947 | 867.5438 | 95.0054 | 120 | 70 | 10.6 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 13.7442 | 70.6558 | 0.27042 | NA | 7.2 | 68.068 | 1082.52 | 1490.06 | 1802.4537 | -20.9652 | 80.0411 | 1442.4868 | 95.2812 | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 6.13 | 7.23 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.9 | 6.9 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 6.12 | 7.23 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.92 | 6.96 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.92 | 6.92 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.88 | 6.87 | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 2.8897 | [5 empty] | 1998-07-10 | 8:30 | 6087.99 | 25.5556 | 98 | 70 | 10 | 0 | 17.2 | 3 |  | 20.2 | 20.2 | 0.85149 | 0 | 15.7557 | 15.9641 | 4.8527 | 69.1473 | 0.23087 | 7.4 | 6.37 | 35.108 | 300.46 | 160.608 | 765 | 880.1413 | -15.0512 | 78.1406 | 520.3747 | 93.2533 | 98 | 75 | 10 | 10.4 | 9.8 | 20.2 | 20.2 | 0.49066 | 0.51485 | 16 | 16.2116 | 1.9562 | 74.5438 | 0.21748 | 6.37 | NA | 32.804 | 160.608 | 611.82 | 296.2367 | 51.5811 | 79.5751 | 228.4224 | 85.6389 | 75 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.3173 | 49.1827 | 0.29159 | NA | NA | 42.14 | 611.82 | 810.96 | 1135.9256 | -40.0717 | 73.7622 | 873.8728 | 95.1778 | 120 | 70 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.1318 | 74.8682 | 0.2552 | NA | 7.2 | 69.608 | 810.96 | 1093.95 | 1354.6181 | -23.8282 | 56.6597 | 1082.7891 | 93.5714 | SDS-CDb, mg/L | NA | 9.3929 |  | SDS-CDb, mg/L | NA | 8.6991 |  |  |  | Temperature | oC | 26.1 | 26.5 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 8.8158 |  | SDS-CDb, mg/L | 11.6988 | 7.1594 |  |  |  | Temperature | oC | 25.3 | 25.1 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 7.3862 |  | SDS-CDb, mg/L | 10.4765 | 6.3932 |  |  |  | Temperature | oC | 26.9 | 26.3 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 9.4125 |  | SDS-CDb, mg/L | 11.5119 | 7.066 |  |  |  | Temperature | oC | 27.2 | 27.2 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 8.6112 |  | SDS-CDb, mg/L | NA | 7.5864 |  |  |  | Temperature | oC | 25.6 | 25.2 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | 8.2374 |  | SDS-CDb, mg/L | 11.0615 | 6.8307 |  |  |  | Temperature | oC | 25.3 | 25.1 | --- | --- | --- | ---
|  | Active membrane area of membrane element used, A (ft2) | 28 | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-07-11 | 16:10 | 6095.55 | 25.5556 | 98 | 70 | 10 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 4.7913 | 69.2087 | 0.22396 | 7.4 | 6.28 | 34.974 | 298.8 | 161.616 | 768 | 866.5898 | -12.8372 | 78.3598 | 514.1029 | 93.1971 | 98 | 72 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 1.9512 | 73.2488 | 0.21068 | 6.28 | NA | 31.978 | 161.616 | 618.75 | 292.5768 | 52.7149 | 80.2136 | 227.0964 | 85.9188 | 72 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.4022 | 47.5978 | 0.3013 | NA | NA | 43.26 | 618.75 | 812.2 | 1148.2008 | -41.3692 | 73.2328 | 883.4754 | 95.1034 | 120 | 70 | 10.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 10.1477 | 74.6523 | 0.25594 | NA | 7.2 | 69.685 | 812.2 | 1098.24 | 1356.711 | -23.535 | 56.8824 | 1084.4555 | 93.5742 | TOCb, mg/L | NA | 3.9808 |  | TOCb, mg/L | NA | 3.5683 |  |  |  | Alkalinity | mg/L as CaCO3 | 27 | 507 | 847.6452 | 81.5068 | 677.3226 | 96.0137 | TOCb, mg/L | NA | 3.7571 |  | TOCb, mg/L | 5.4449 | 2.7874 |  |  |  | Alkalinity | mg/L as CaCO3 | 23 | 345 | 573.5161 | 80 | 459.2581 | 94.9919 | TOCb, mg/L | NA | 3.033 |  | TOCb, mg/L | 4.7212 | 2.4906 |  |  |  | Alkalinity | mg/L as CaCO3 | 29 | 508 | 847.9355 | 79.4326 | 677.9677 | 95.7225 | TOCb, mg/L | NA | 3.7302 |  | TOCb, mg/L | 4.8368 | 2.4934 |  |  |  | Alkalinity | mg/L as CaCO3 | 25 | 388 | 645.6129 | 79.6748 | 516.8065 | 95.1626 | TOCb, mg/L | NA | 1.4201 |  | TOCb, mg/L | NA | 1.2267 |  |  |  | Alkalinity | mg/L as CaCO3 | 17 | 367 | 623.6667 | 85.0877 | 495.3333 | 96.568 | TOCb, mg/L | NA | 3.2774 |  | TOCb, mg/L | 4.8741 | 2.4821 |  |  |  | Alkalinity | mg/L as CaCO3 | 24 | 351 | 583.0645 | 79.1304 | 467.0323 | 94.8612
|  | Design flux, FW (gfd) | 41.43 | System concentrate waste flow rate, QW-sys (gpm) | 2.8897 | [5 empty] | 1998-07-11 | 23:30 | 6102.87 | 25.5556 | 98 | 72 | 9.9333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.8973 | 64.1694 | 0.24155 | 7.4 | 6.29 | 38.726 | 320.38 | 326.76 | 848 | 1930.1493 | -127.6119 | 88.1485 | 1128.4546 | 96.5682 | 98 | 72 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.4181 | 70.7819 | 0.21802 | 6.29 | NA | 33.217 | 326.76 | 597.96 | 623.2983 | -4.2375 | 89.8344 | 475.0292 | 93.0074 | 72 | 60 | 10 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.1538 | 47.8462 | 0.29973 | NA | NA | 39.48 | 597.96 | 890.32 | 1111.7616 | -24.8721 | 87.9177 | 854.8608 | 95.3817 | 120 | 72 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.2585 | 74.7415 | 0.25563 | NA | 7.2 | 66.528 | 890.32 | 1212.64 | 1494.4341 | -23.2381 | 79.6401 | 1192.3771 | 94.4206 | UV254 b, cm-1 | NA | 0.16118 |  | UV254 b, cm-1 | NA | 0.14417 |  |  |  | Total dissolved solids | mg/L | 65 | 1019 | 1696.0323 | 80.1829 | 1357.5161 | 95.2118 | UV254 b, cm-1 | NA | 0.14105 |  | UV254 b, cm-1 | 0.20622 | 0.10361 |  |  |  | Total dissolved solids | mg/L | 34.1 | 963 | 1622.2194 | 89.5719 | 1292.6097 | 97.3619 | UV254 b, cm-1 | NA | 0.11822 |  | UV254 b, cm-1 | 0.18958 | 0.095292 |  |  |  | Total dissolved solids | mg/L | 68 | 1081 | 1799.9032 | 79.0123 | 1440.4516 | 95.2793 | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 65 | 992 | 1649.871 | 80.4805 | 1320.9355 | 95.0792 | UV254 b, cm-1 | NA | 0.14377 |  | UV254 b, cm-1 | NA | 0.11855 |  |  |  | Total dissolved solids | mg/L | 68 | 983 | 1654 | 79.3939 | 1318.5 | 94.8426 | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 65.8 | 977 | 1623.6581 | 79.8777 | 1300.329 | 94.9397
|  | Net driving pressure at the design flux, NDP (psi) | 97 | System permeate flow rate, Qp-sys (gpm) | 16.375 | [5 empty] | 1998-07-12 | 10:00 | 6113.57 | 25.5556 | 98 | 72 | 9.5333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.3014 | 65.1653 | 0.23786 | 7.4 | 6.39 | 41.138 | 312.08 | 320.04 | 856 | 1822.5121 | -112.9103 | 87.146 | 1071.276 | 96.1599 | 98 | 72 | 9 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 4.3156 | 71.6844 | 0.21745 | 6.39 | NA | 34.279 | 320.04 | 564.3 | 611.6329 | -8.3879 | 89.2892 | 465.8364 | 92.6414 | 72 | 60 | 9.8 | 4.5 | 5.1 | 9.6 | 9.6 | 0.48085 | 0.46875 | 13.8462 | 14.0293 | 7.5555 | 48.6445 | 0.2884 | NA | NA | 40.04 | 564.3 | 906.44 | 1026.8824 | -13.2874 | 87.4891 | 795.5912 | 94.9673 | 120 | 72 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.4139 | 74.7861 | 0.25548 | NA | 7.2 | 63.987 | 906.44 | 1224.08 | 1504.3099 | -22.8931 | 80.0066 | 1205.3749 | 94.6915 | Bromideb, mg/L | NA | 31.4356 |  | Bromideb, mg/L | NA | 28.8245 |  |  |  | Total hardness | mg/L as CaCO3 | 19 | 725 | 1226.0323 | 90.1554 | 975.5161 | 98.0523 | Bromideb, mg/L | NA | 48.8158 |  | Bromideb, mg/L | 60.8284 | 41.9142 |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 671 | 1135.129 | 91.1917 | 903.0645 | 98.1175 | Bromideb, mg/L | NA | 20.3935 |  | Bromideb, mg/L | 27.9385 | 17.9692 |  |  |  | Total hardness | mg/L as CaCO3 | 19 | 720 | 1217.4839 | 90.2564 | 968.7419 | 98.0387 | Bromideb, mg/L | NA | 11.1226 |  | Bromideb, mg/L | 11.7787 | 10.3894 |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 674 | 1140.2581 | 91.4573 | 907.129 | 98.126 | Bromideb, mg/L | NA | 12.6969 |  | Bromideb, mg/L | NA | 12.572 |  |  |  | Total hardness | mg/L as CaCO3 | 18 | 693 | 1188 | 91.0448 | 940.5 | 98.0861 | Bromideb, mg/L | NA | 33.5703 |  | Bromideb, mg/L | 46.3802 | 27.1901 |  |  |  | Total hardness | mg/L as CaCO3 | 17 | 696 | 1177.871 | 91.1458 | 936.9355 | 98.1856
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.427 | System feed flow rate, QF-sys (gpm) | 19.2647 | [5 empty] | 1998-07-12 | 16:00 | 6122.85 | 25.5556 | 98 | 72 | 9.8667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.7614 | 64.3719 | 0.24079 | 7.4 | 6.36 | 39.798 | 327.02 | 324.24 | 852 | 1907.6338 | -123.9007 | 87.7258 | 1115.9369 | 96.4337 | 98 | 72 | 9.8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.3704 | 70.8296 | 0.21788 | 6.36 | NA | 33.866 | 324.24 | 590.04 | 617.577 | -4.667 | 89.5553 | 470.9085 | 92.8084 | 72 | 60 | 9.8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 8.0331 | 48.1669 | 0.29774 | NA | NA | 39.83 | 590.04 | 917.6 | 1096.2332 | -19.4674 | 87.7159 | 843.1366 | 95.276 | 120 | 72 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.645 | 74.355 | 0.25696 | NA | 7.2 | 65.527 | 917.6 | 1218.36 | 1542.4535 | -26.6008 | 79.7906 | 1230.0268 | 94.6727 | Alkb, mg/L CaCO3 | NA | 107.0628 |  | Alkb, mg/L CaCO3 | NA | 97.4388 |  |  |  | Calcium hardness | mg/L as CaCO3 | 15 | 678 | 1148.5161 | 91.7582 | 913.2581 | 98.3575 | Alkb, mg/L CaCO3 | NA | 80.2487 |  | Alkb, mg/L CaCO3 | 109.6795 | 63.3398 |  |  |  | Calcium hardness | mg/L as CaCO3 | 14 | 605 | 1024.4194 | 92.2222 | 814.7097 | 98.2816 | Alkb, mg/L CaCO3 | NA | 81.0329 |  | Alkb, mg/L CaCO3 | 120.0154 | 68.5077 |  |  |  | Calcium hardness | mg/L as CaCO3 | 17 | 663 | 1121.4516 | 90.6593 | 892.2258 | 98.0947 | Alkb, mg/L CaCO3 | NA | 92 |  | Alkb, mg/L CaCO3 | 115.1818 | 66.0909 |  |  |  | Calcium hardness | mg/L as CaCO3 | 16 | 626 | 1058.9032 | 91.5344 | 842.4516 | 98.1008 | Alkb, mg/L CaCO3 | NA | 84.5951 |  | Alkb, mg/L CaCO3 | NA | 72.4873 |  |  |  | Calcium hardness | mg/L as CaCO3 | 18 | 665 | 1139.4667 | 90.2703 | 902.2333 | 98.005 | Alkb, mg/L CaCO3 | NA | 74.8712 |  | Alkb, mg/L CaCO3 | 104.3636 | 60.1818 |  |  |  | Calcium hardness | mg/L as CaCO3 | 16 | 625 | 1057.1935 | 91.0615 | 841.0968 | 98.0977
|  | Temperature at which the MTCW was determined, ToC (oC) | 25 | [7 empty] | 1998-07-12 | 22:30 | 6125.83 | 25.5556 | 98 | 72 | 9.5333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.7245 | 64.7422 | 0.23941 | 7.4 | 6.33 | 40.602 | 317.06 | 330.96 | 852 | 1895.1466 | -122.4351 | 87.7321 | 1113.0533 | 96.3522 | 98 | 72 | 9 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 4.4787 | 71.5213 | 0.21795 | 6.33 | NA | 34.397 | 330.96 | 572.22 | 633.5753 | -10.7223 | 89.6069 | 482.2677 | 92.8677 | 72 | 60 | 9.8 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 7.7146 | 48.4854 | 0.28935 | NA | NA | 40.18 | 572.22 | 920.08 | 1051.056 | -14.2353 | 87.8596 | 811.638 | 95.0495 | 120 | 72 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.5643 | 74.6357 | 0.256 | NA | 7.2 | 66.528 | 920.08 | 1218.36 | 1525.8266 | -25.2361 | 79.8985 | 1222.9533 | 94.5601 | T-Hdb, mg/L CaCO3 | NA | 137.7635 |  | T-Hdb, mg/L CaCO3 | NA | 124.1109 |  |  |  | Turbidity | ntu | 0.02 | 18.95 | 32.3842 | 60 | 25.6671 | 99.9221 | T-Hdb, mg/L CaCO3 | NA | 128.8165 |  | T-Hdb, mg/L CaCO3 | 183.1734 | 97.5867 |  |  |  | Turbidity | ntu | 0.01 | 9.5 | 16.2348 | 80 | 12.8674 | 99.9223 | T-Hdb, mg/L CaCO3 | NA | 106.0166 |  | T-Hdb, mg/L CaCO3 | 163.8615 | 87.4308 |  |  |  | Turbidity | ntu | BMRL | 19.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | 144.3113 |  | T-Hdb, mg/L CaCO3 | 185.2075 | 98.6038 |  |  |  | Turbidity | ntu | 0.01 | 10.05 | 17.1752 | 85.7143 | 13.6126 | 99.9265 | T-Hdb, mg/L CaCO3 | NA | 144.009 |  | T-Hdb, mg/L CaCO3 | NA | 120.5424 |  |  |  | Turbidity | ntu | 0.03 | 7.75 | 13.4113 | 50 | 10.5807 | 99.7165 | T-Hdb, mg/L CaCO3 | NA | 119.0385 |  | T-Hdb, mg/L CaCO3 | 172.6612 | 92.3306 |  |  |  | Turbidity | ntu | 0.03 | 8.4 | 14.34 | 40 | 11.37 | 99.7361
|  | Maximum flow rate to the element, QI, max (gpm) | 2.5 | Calculate the Required System Influent Pressure | [6 empty] | 1998-07-13 | 6:45 | 6134.21 | 25.5556 | 98 | 72 | 9.5333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.6469 | 64.8197 | 0.23912 | 7.4 | 6.25 | 39.463 | 313.74 | 320.88 | 860 | 1887.4346 | -119.4691 | 87.7016 | 1104.1573 | 96.426 | 98 | 72 | 9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 15.5881 | 4.3433 | 71.6567 | 0.21754 | 6.25 | NA | 34.279 | 320.88 | 570.24 | 616.3449 | -8.0852 | 89.3172 | 468.6125 | 92.685 | 72 | 60 | 9.8 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 7.6747 | 48.5253 | 0.28911 | NA | NA | 40.95 | 570.24 | 892.8 | 1046.601 | -17.2268 | 87.2382 | 808.4205 | 94.9346 | 120 | 72 | 9.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.3145 | 74.8855 | 0.25514 | NA | 7.2 | 64.911 | 892.8 | 1229.8 | 1499.9186 | -21.9644 | 79.7709 | 1196.3593 | 94.5743 | Ca-Hdb, mg/L CaCO3 | NA | 129.7819 |  | Ca-Hdb, mg/L CaCO3 | NA | 116.8753 |  |  |  | Total organic carbon | mg/L | 0.2 | 20.35 | 34.65 | 96.4602 | 27.5 | 99.2727 | Ca-Hdb, mg/L CaCO3 | NA | 119.7172 |  | Ca-Hdb, mg/L CaCO3 | 170.7706 | 90.3853 |  |  |  | Total organic carbon | mg/L | 0.22 | 19.05 | 32.4132 | 96.1739 | 25.7316 | 99.145 | Ca-Hdb, mg/L CaCO3 | NA | 98.8199 |  | Ca-Hdb, mg/L CaCO3 | 152.8923 | 81.4462 |  |  |  | Total organic carbon | mg/L | 0.28 | 19.45 | 33.0545 | 95.0266 | 26.2523 | 98.9334 | Ca-Hdb, mg/L CaCO3 | NA | 136.3585 |  | Ca-Hdb, mg/L CaCO3 | 175.7238 | 92.3619 |  |  |  | Total organic carbon | mg/L | 0.33 | 18.6 | 31.5658 | 93.666 | 25.0829 | 98.6844 | Ca-Hdb, mg/L CaCO3 | NA | 132.5562 |  | Ca-Hdb, mg/L CaCO3 | NA | 110.9619 |  |  |  | Total organic carbon | mg/L | 0.13 | 18.35 | 31.7113 | 93.1217 | 25.0307 | 99.4806 | Ca-Hdb, mg/L CaCO3 | NA | 110.4973 |  | Ca-Hdb, mg/L CaCO3 | 160.843 | 85.4215 |  |  |  | Total organic carbon | mg/L | 0.27 | 19.05 | 32.3777 | 95.0459 | 25.7139 | 98.95
|  | Minimum flow rate to the element, QI, min (gpm) | 0 | Osmotic pressure for stage 13, Dp1 (psi) | 8.9 | [5 empty] | 1998-07-13 | 6:00 | 6143.33 | 25.5556 | 98 | 72 | 8.9333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.5961 | 65.4706 | 0.23675 | 7.4 | 6.26 | 39.128 | 311.25 | 319.2 | 872 | 1878.2675 | -115.3976 | 87.7419 | 1098.7337 | 96.4388 | 98 | 72 | 9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 15.5881 | 4.317 | 71.683 | 0.21746 | 6.26 | NA | 34.338 | 319.2 | 568.26 | 612.8722 | -7.8507 | 89.2425 | 466.0361 | 92.6319 | 72 | 60 | 9 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 7.645 | 49.355 | 0.28425 | NA | NA | 41.02 | 568.26 | 899 | 1042.776 | -15.9929 | 87.1491 | 805.518 | 94.9076 | 120 | 72 | 8.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.3918 | 75.8081 | 0.25204 | NA | 7.2 | 65.45 | 899 | 1246.96 | 1510.27 | -21.1162 | 79.4956 | 1204.635 | 94.5668 | Notes: | [9 empty] | UV254 | cm-1 | 0.004 | 0.736 | 1.2555 | 98.2609 | 0.99574 | 99.5983 | Notes: | [9 empty] | UV254 | cm-1 | 0.002 | 0.697 | 1.1902 | 99.0826 | 0.94361 | 99.788 | Notes: | [9 empty] | UV254 | cm-1 | 0.001 | 0.68 | 1.1619 | 99.5614 | 0.92094 | 99.8914 | Notes: | [9 empty] | UV254 | cm-1 | 0.02 | 0.685 | 1.1569 | 90.9502 | 0.92097 | 97.8284 | Notes: | [9 empty] | UV254 | cm-1 | 0.004 | 0.669 | 1.1567 | 98.0488 | 0.91283 | 99.5618 | Notes: | [9 empty] | UV254 | cm-1 | 0.002 | 0.697 | 1.1902 | 99.0698 | 0.94361 | 99.788
|  | Total width of all membrane envelopes in the element, w (ft) | 6.4 | Osmotic pressure for stage 23, Dp2 (psi) | 13.4 | [5 empty] | 1998-07-13 | 22:35 | 6150.19 | 25.5556 | 98 | 72 | 9.8 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.6983 | 64.5017 | 0.2403 | 7.4 | 6.31 | 38.793 | 317.06 | 328.44 | 864 | 1888.7964 | -118.6107 | 88.1887 | 1108.6182 | 96.5008 | 98 | 72 | 9.8 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.4883 | 70.7117 | 0.22265 | 6.31 | NA | 33.276 | 328.44 | 566.28 | 635.7757 | -12.2723 | 89.8685 | 482.1079 | 93.0978 | 72 | 60 | 9.8 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 7.5476 | 48.6524 | 0.28195 | NA | NA | 42.14 | 566.28 | 912.64 | 1027.5232 | -12.588 | 87.1697 | 796.9016 | 94.712 | 120 | 72 | 9.8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.4123 | 74.7877 | 0.25548 | NA | 7.2 | 70.301 | 912.64 | 1235.52 | 1510.429 | -22.2505 | 78.5955 | 1211.5345 | 94.1974 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 2 | 3.6167 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.90909 | 3.6588 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.35714 | 3.4961 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 6.0606 | 3.6828 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 3.0769 | 3.6458 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.74074 | 3.6588 | --- | --- | --- | ---
|  | Feed spacer thickness, T (ft) | 0.00258 | Osmotic pressure for stage 33, Dp3 (psi) | 18.6 | [5 empty] | 1998-07-14 | 7:35 | 6159 | 25.5556 | 98 | 72 | 9.7 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 4.496 | 70.804 | 0.21891 | 7.8 | 6.31 | 37.051 | 318.72 | 161.616 | 860 | 811.6896 | 5.6175 | 77.0747 | 486.6528 | 92.3866 | 98 | 72 | 9.8 | 10.1 | 9.8 | 19.9 | 19.9 | 0.48576 | 0.50754 | 15.5385 | 15.7439 | 2.1799 | 73.0201 | 0.21561 | 6.31 | NA | 17.759 | 161.616 | 554.4 | 309.8768 | 44.1059 | 89.0116 | 235.7464 | 92.4669 | 72 | 60 | 9.8 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 7.6245 | 48.5755 | 0.2824 | NA | NA | 24.92 | 554.4 | 841.96 | 1020.3424 | -21.1866 | 84.5807 | 787.3712 | 96.835 | 120 | 72 | 9.5 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 10.6434 | 75.8566 | 0.25188 | NA | 7.4 | 49.896 | 841.96 | 1229.8 | 1386.504 | -12.7422 | 69.1268 | 1114.232 | 95.5219 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses due to stage hardware, DPs (psi) | 4 | [5 empty] | 1998-07-15 | 23:20 | 6183.22 | 25.5556 | 98 | 72 | 8.4333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.7478 | 64.8189 | 0.23913 | 7.4 | 6.52 | 35.577 | 337.81 | 353.64 | 972 | 2067.0762 | -112.6622 | 89.9398 | 1210.3581 | 97.0606 | 98 | 72 | 8.4 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 4.8845 | 71.7155 | 0.21736 | 6.52 | NA | 30.208 | 353.64 | 614.79 | 683.6727 | -11.2043 | 91.458 | 518.6563 | 94.1757 | 72 | 60 | 8.8 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 8.3247 | 48.8753 | 0.28704 | NA | NA | 40.67 | 614.79 | 388.12 | 1131.498 | -191.533 | 88.4996 | 873.144 | 95.3421 | 120 | 72 | 8.1 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 4.3685 | 83.5315 | 0.22873 | NA | 7.2 | 65.681 | 388.12 | 1389.96 | 616.9477 | 55.614 | 81.4272 | 502.5338 | 86.93 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-07-16 | 7:35 | 6191.28 | 25.5556 | 98 | 72 | 8.4667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.1008 | 64.4325 | 0.24056 | 7.4 | 6.53 | 36.314 | 340.3 | 356.16 | 974 | 2136.6361 | -119.3672 | 89.804 | 1246.398 | 97.0865 | 98 | 72 | 8.4 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 15.5881 | 4.945 | 71.655 | 0.21754 | 6.53 | NA | 29.854 | 356.16 | 615.78 | 692.5579 | -12.4684 | 91.6178 | 524.359 | 94.3066 | 72 | 60 | 8.8 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 8.3361 | 48.864 | 0.28711 | NA | NA | 40.88 | 615.78 | 394.32 | 1133.19 | -187.3783 | 88.522 | 874.485 | 95.3252 | 120 | 72 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 4.503 | 83.297 | 0.22938 | NA | 7.2 | 64.834 | 394.32 | 1392.82 | 635.9431 | 54.3413 | 81.7964 | 515.1315 | 87.4141 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  |  |  | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-07-16 | 16:00 | 6200.24 | 25.5556 | 98 | 72 | 8 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 11.4957 | 65.5043 | 0.23663 | 7.4 | 6.45 | 34.304 | 351.09 | 352.8 | 1012 | 2014.951 | -99.1058 | 90.2766 | 1183.8755 | 97.1024 | 98 | 72 | 7.8 | 10 | 9.9 | 19.9 | 19.9 | 0.48739 | 0.50251 | 15.3846 | 15.5881 | 4.8729 | 72.3271 | 0.21552 | 6.45 | NA | 29.028 | 352.8 | 626.67 | 679.8424 | -8.4849 | 91.7721 | 516.3212 | 94.3779 | 72 | 60 | 8.2 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 8.5153 | 49.2847 | 0.28466 | NA | NA | 39.41 | 626.67 | 460.04 | 1155.204 | -151.1095 | 88.8294 | 890.937 | 95.5766 | 120 | 72 | 8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 5.2288 | 82.7712 | 0.23084 | NA | 7.2 | 70.917 | 460.04 | 1447.16 | 727.5621 | 49.7248 | 79.8988 | 593.801 | 88.0571 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  | Stage 3 -- Additional Information |  | Mechanical pressure losses per stage, Ls (psi) | 22 | [5 empty] | 1998-07-16 | 23:15 | 6206.96 | 25.5556 | 98 | 72 | 8.4333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.5915 | 64.9751 | 0.23855 | 7.4 | 6.52 | 36.448 | 345.28 | 350.28 | 984 | 2040.9234 | -107.4109 | 89.5946 | 1195.6017 | 96.9515 | 98 | 72 | 8.4 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 4.8141 | 71.7859 | 0.21715 | 6.52 | NA | 31.506 | 350.28 | 610.83 | 675.5596 | -10.597 | 91.0055 | 512.9198 | 93.8575 | 72 | 60 | 8.8 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 8.2551 | 48.9449 | 0.28663 | NA | NA | 41.51 | 610.83 | 978.36 | 1123.218 | -14.8062 | 88.1495 | 867.024 | 95.2124 | 120 | 72 | 8.1 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 12.333 | 75.567 | 0.25284 | NA | 7.2 | 68.068 | 978.36 | 1407.12 | 1624.3737 | -15.4396 | 80.5675 | 1301.3668 | 94.7695 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 0.75 | Net driving pressure required for permeation, NDP (psi) | 49.7034 | [5 empty] | 1998-07-17 | 11:10 | 6218.84 | 25.5556 | 98 | 72 | 8.4333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.6077 | 64.959 | 0.23861 | 7.4 | 6.57 | 36.85 | 350.26 | 351.12 | 990 | 2044.1229 | -106.4771 | 89.505 | 1197.6215 | 96.9231 | 98 | 72 | 8.4 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 4.8197 | 71.7803 | 0.21716 | 6.57 | NA | 31.978 | 351.12 | 618.75 | 676.7751 | -9.3778 | 90.8926 | 513.9476 | 93.778 | 72 | 60 | 8.8 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 8.3761 | 48.8239 | 0.28734 | NA | NA | 41.09 | 618.75 | 961 | 1138.644 | -18.4853 | 88.2974 | 878.697 | 95.3238 | 120 | 72 | 8.1 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 12.0905 | 75.8095 | 0.25203 | NA | 7.2 | 68.607 | 961 | 1415.7 | 1594.3112 | -12.6165 | 80.4605 | 1277.6556 | 94.6302 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | < 5:1 | Flow weighted system pressure losses, Lsys (psi) | 33.5282 | [5 empty] | 1998-07-17 | 17:00 | 6285.28 | 25.5556 | 98 | 72 | 8.3333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 12.2644 | 64.4023 | 0.24067 | 7.5 | 6.5 | 38.391 | 349.43 | 370.44 | 1012 | 2159.2201 | -113.3617 | 89.6364 | 1264.83 | 96.9647 | 98 | 74 | 8.6 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 5.1337 | 72.2663 | 0.2157 | 6.5 | NA | 30.503 | 370.44 | 581.13 | 717.3145 | -23.4344 | 91.7657 | 543.8772 | 94.3916 | 74 | 60 | 8.4 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 7.8539 | 50.7461 | 0.27646 | NA | NA | 39.48 | 581.13 | 925.04 | 1068.615 | -15.521 | 89.3424 | 824.8725 | 95.2138 | 120 | 72 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.549 | 76.451 | 0.24992 | NA | 7.2 | 72.611 | 925.04 | 1447.16 | 1529.9896 | -5.7236 | 80.3987 | 1227.5148 | 94.0847 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Maximum element recovery (%) | 17 | Required influent pressure to the system, PI (psi) | 83.2317 | [5 empty] | 1998-07-17 | 22:30 | 6230.19 | 25.5556 | 98 | 72 | 8.3333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 12.3563 | 64.3103 | 0.24102 | 7.4 | 6.55 | 39.262 | 348.6 | 373.8 | 1001 | 2175.9886 | -117.3815 | 89.4965 | 1274.8943 | 96.9204 | 98 | 72 | 8.6 | 10 | 9.8 | 19.8 | 19.8 | 0.48412 | 0.50505 | 15.3846 | 15.5881 | 5.1782 | 71.2218 | 0.21887 | 6.55 | NA | 30.916 | 373.8 | 558.36 | 723.6816 | -29.6084 | 91.7293 | 548.7408 | 94.366 | 72 | 60 | 8.4 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 14.0293 | 7.5298 | 50.0701 | 0.28019 | NA | NA | 39.06 | 558.36 | 932.48 | 1025.73 | -10.0002 | 89.5506 | 792.045 | 95.0685 | 120 | 72 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 11.6717 | 76.3283 | 0.25032 | NA | 7.2 | 70.994 | 932.48 | 1431.43 | 1543.8572 | -7.8542 | 81.0075 | 1238.1686 | 94.2662 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Variability of design flux (%) | 5 | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-07-20 | 11:00 | 6250.68 | 25.5556 | 100 | 72 | 9.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.7955 | 65.1378 | 0.23796 | 7.5 | 6.48 | 34.304 | 302.95 | 346.08 | 811 | 2081.6331 | -156.6749 | 90.0878 | 1213.8565 | 97.174 | 100 | 78 | 9.5 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.8293 | 74.6707 | 0.21085 | 6.48 | NA | 29.618 | 346.08 | 705.87 | 679.0244 | 3.8032 | 91.4419 | 512.5522 | 94.2215 | 78 | 60 | 9.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 9.6142 | 50.1858 | 0.27333 | NA | NA | 38.22 | 705.87 | 920.08 | 1293.402 | -40.575 | 88.9563 | 999.636 | 96.1766 | 120 | 72 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.5516 | 75.9484 | 0.25157 | NA | 7.3 | 74.844 | 920.08 | 1159.73 | 1539.9197 | -32.7826 | 78.3738 | 1229.9999 | 93.9151 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Rejection of reference solute and conditions of test | Magnesium Sulfate = 98 % Rejection | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-07-21 | 1:00 | 6257.4 | 25.5556 | 100 | 72 | 8.9 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.07 | 65.03 | 0.23835 | 7.5 | 6.57 | 33.768 | 310.42 | 352.8 | 784 | 2128.7448 | -171.5236 | 90.4286 | 1240.7724 | 97.2785 | 100 | 76 | 9.5 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.922 | 73.578 | 0.21398 | 6.57 | NA | 30.267 | 352.8 | 690.03 | 692.1316 | -0.30457 | 91.4209 | 522.4658 | 94.2069 | 76 | 60 | 9.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 9.38 | 49.42 | 0.27757 | NA | NA | 38.64 | 690.03 | 927.52 | 1263.2532 | -36.1969 | 89.0476 | 976.6416 | 96.0436 | 120 | 72 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.6606 | 76.3394 | 0.25028 | NA | 7.2 | 74.305 | 927.52 | 1121.12 | 1553.211 | -38.541 | 78.9385 | 1240.3655 | 94.0094
|  | (e.g., solute type and concentration) | San Diego Tap = 75 % Rejection | [7 empty] | 1998-07-21 | 12:30 | 6268.66 | 25.5556 | 100 | 72 | 8.5667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.1083 | 65.3251 | 0.23727 | 7.4 | 6.56 | 34.438 | 311.25 | 354.48 | 790 | 2136.0471 | -170.3857 | 90.2849 | 1245.2636 | 97.2345 | 100 | 72 | 8.5 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.9458 | 72.5542 | 0.217 | 6.56 | NA | 30.385 | 354.48 | 707.85 | 695.4549 | 1.7511 | 91.4283 | 524.9675 | 94.212 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 9.6467 | 47.3533 | 0.28968 | NA | NA | 37.94 | 707.85 | 925.04 | 1297.3708 | -40.2502 | 89.297 | 1002.6104 | 96.2159 | 120 | 72 | 8.2 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.6088 | 76.1912 | 0.25077 | NA | 7.2 | 75.614 | 925.04 | 1129.7 | 1547.9524 | -37.0233 | 78.669 | 1236.4962 | 93.8848
|  | Variability of rejection of reference solute (%) | 0 | [7 empty] | 1998-07-21 | 18:00 | 6275.15 | 25.5556 | 100 | 72 | 8.8333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.5805 | 65.5862 | 0.23633 | 7.5 | 6.5 | 32.428 | 299.63 | 338.52 | 873 | 2042.4321 | -133.9556 | 90.4207 | 1190.4761 | 97.276 | 100 | 75 | 9 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.7185 | 73.7815 | 0.21339 | 6.5 | NA | 29.323 | 338.52 | 714.78 | 663.821 | 7.1293 | 91.3379 | 501.1705 | 94.1491 | 75 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 9.7152 | 48.7848 | 0.28118 | NA | NA | 40.11 | 714.78 | 894.04 | 1308.4896 | -46.3569 | 88.1514 | 1011.6348 | 96.0351 | 120 | 72 | 8.5 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 11.1831 | 76.3169 | 0.25036 | NA | 7.2 | 75.768 | 894.04 | 1248.39 | 1494.1061 | -19.6826 | 77.6179 | 1194.0731 | 93.6547
|  | Standard testing recovery (%) | 15 | [7 empty] | 1998-07-23 | 13:20 | 6313.8 | 25.5556 | 98 | 70 | 8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.4568 | 63.5432 | 0.24393 | 7.6 | 6.44 | 58.826 | 370.18 | 388.08 | 1138 | 2220.9273 | -95.1606 | 84.8418 | 1304.5036 | 95.4905 | 98 | 70 | 8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 5.3748 | 70.6252 | 0.21851 | 6.44 | NA | 30.975 | 388.08 | 718.74 | 748.8289 | -4.1863 | 92.0184 | 568.4545 | 94.551 | 70 | 60 | 8.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.8947 | 46.9053 | 0.30574 | NA | NA | 41.02 | 718.74 | 1140.8 | 1342.2424 | -17.658 | 89.43 | 1030.4912 | 96.0194 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.6333 | 51.5667 | 0.37052 | NA | 7 | 70.07 | 1140.8 | 1627.34 | 1926.002 | -18.3528 | 81.9444 | 1533.401 | 95.4304
|  | Standard testing pH | 7 | [7 empty] | 1998-07-23 | 19:20 | 6319.85 | 25.5556 | 98 | 72 | 7.9333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 13.3657 | 63.7009 | 0.24332 | 7.4 | 6.42 | 59.161 | 392.59 | 412.44 | 1156 | 2379.0264 | -105.7981 | 85.6559 | 1395.7332 | 95.7613 | 98 | 70 | 8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 5.7272 | 70.2728 | 0.2196 | 6.42 | NA | 31.919 | 412.44 | 735.57 | 796.8439 | -8.3301 | 92.2609 | 604.6419 | 94.721 | 70 | 60 | 8 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 10.1292 | 46.8708 | 0.30597 | NA | NA | 41.79 | 735.57 | 1169.32 | 1373.8476 | -17.4912 | 89.8676 | 1054.7088 | 96.0378 | 78 | 72 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.0062 | 52.1938 | 0.36607 | NA | 7.3 | 71.302 | 1169.32 | 1653.08 | 1974.5332 | -19.4457 | 82.7122 | 1571.9266 | 95.464
|  | Acceptable range of operating pressures | 0 to 350 psi | [7 empty] | 1998-07-24 | 7:45 | 6332.12 | 25.5556 | 98 | 70 | 8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.744 | 63.256 | 0.24504 | 7.4 | 6.32 | 57.955 | 380.14 | 394.8 | 1162 | 2269.9038 | -95.3446 | 85.3204 | 1332.3519 | 95.6502 | 98 | 70 | 8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 5.475 | 70.525 | 0.21882 | 6.32 | NA | 31.034 | 394.8 | 732.6 | 762.2779 | -4.051 | 92.1393 | 578.5389 | 94.6358 | 70 | 60 | 8.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 10.1012 | 46.6988 | 0.3071 | NA | NA | 40.74 | 732.6 | 1171.8 | 1369.1112 | -16.8383 | 89.6809 | 1050.8556 | 96.1232 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 15.0591 | 51.1409 | 0.37361 | NA | 7.2 | 69.916 | 1171.8 | 1661.66 | 1979.8483 | -19.1488 | 82.2908 | 1575.8241 | 95.5632
|  | Acceptable range of operating pH values | 4 to 11 | [7 empty] | 1998-07-24 | 18:00 | 6340.36 | 25.5556 | 98 | 70 | 8.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 12.2823 | 63.651 | 0.24352 | 7.4 | 6.5 | 55.878 | 362.71 | 380.52 | 1106 | 2187.6938 | -97.8023 | 85.3154 | 1284.1069 | 95.6485 | 98 | 70 | 8.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 5.2663 | 70.5337 | 0.21879 | 6.5 | NA | 30.621 | 380.52 | 721.71 | 733.9894 | -1.7014 | 91.9529 | 557.2547 | 94.505 | 70 | 60 | 8.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.9483 | 46.8517 | 0.30609 | NA | NA | 40.32 | 721.71 | 1137.08 | 1348.5888 | -18.601 | 89.404 | 1035.1494 | 96.1049 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.5919 | 51.6081 | 0.37022 | NA | 7.2 | 69.377 | 1137.08 | 1581.58 | 1920.0622 | -21.4015 | 81.7678 | 1528.5711 | 95.4613
|  | Typical pressure drop across a single element (psi) | 5 | [7 empty] | 1998-07-24 | 23:00 | 6347.48 | 25.5556 | 98 | 70 | 8.1333 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3211 | 64.5456 | 0.24014 | 7.5 | 6.51 | 54.404 | 341.96 | 353.64 | 1064 | 2019.3871 | -89.792 | 84.616 | 1186.5135 | 95.4148 | 98 | 70 | 8.2 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8635 | 70.9365 | 0.21755 | 6.51 | NA | 30.503 | 353.64 | 713.79 | 680.0743 | 4.7235 | 91.3746 | 516.8572 | 94.0984 | 70 | 60 | 8.4 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.847 | 46.753 | 0.30674 | NA | NA | 39.34 | 713.79 | 1113.52 | 1334.284 | -19.8258 | 88.8757 | 1024.037 | 96.1583 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 14.2784 | 51.9216 | 0.36799 | NA | 7.3 | 68.761 | 1113.52 | 1521.52 | 1879.6766 | -23.5394 | 80.5562 | 1496.5983 | 95.4055
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-07-25 | 21:00 | 6369.98 | 25.5556 | 98 | 70 | 8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.2066 | 64.7934 | 0.23922 | 7.5 | 6.3 | 54.069 | 336.98 | 350.28 | 1044 | 1999.1879 | -91.4931 | 84.5641 | 1174.734 | 95.3973 | 98 | 70 | 8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8245 | 71.1755 | 0.21682 | 6.3 | NA | 29.736 | 350.28 | 698.94 | 674.0949 | 3.5547 | 91.5108 | 512.1874 | 94.1943 | 70 | 60 | 8.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.6434 | 47.1566 | 0.30412 | NA | NA | 38.43 | 698.94 | 1082.52 | 1306.6092 | -20.7007 | 89.0288 | 1002.7746 | 96.1676 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.8652 | 52.3348 | 0.36508 | NA | 7.2 | 67.991 | 1082.52 | 1492.92 | 1826.5079 | -22.3447 | 80.5895 | 1454.514 | 95.3255
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 1998-07-26 | 2:00 | 6375.44 | 25.5556 | 98 | 70 | 8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.3045 | 64.6955 | 0.23958 | 7.4 | 6.33 | 54.002 | 340.3 | 352.8 | 1095 | 2016.1089 | -84.1195 | 84.6933 | 1184.4544 | 95.4408 | 98 | 70 | 8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.8553 | 71.1447 | 0.21691 | 6.33 | NA | 30.208 | 352.8 | 707.85 | 678.6838 | 4.1204 | 91.4376 | 515.7419 | 94.1428 | 70 | 60 | 8.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.7766 | 47.0234 | 0.30498 | NA | NA | 38.22 | 707.85 | 1085 | 1323.9096 | -22.0193 | 89.1667 | 1015.8798 | 96.2377 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.9149 | 52.2851 | 0.36543 | NA | 7.2 | 66.836 | 1085 | 1565.85 | 1831.6536 | -16.975 | 81.0556 | 1458.3268 | 95.4169
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-07-27 | :15 | 6390.7 | 25.5556 | 98 | 70 | 8 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.4482 | 64.5518 | 0.24012 | 7.4 | 6.2 | 54.404 | 341.96 | 357 | 1040 | 2041.4511 | -96.2934 | 84.7608 | 1199.2255 | 95.4634 | 98 | 70 | 8 | 9.9 | 9.8 | 19.7 | 19.7 | 0.48249 | 0.50254 | 15.2308 | 15.4322 | 4.9257 | 71.0743 | 0.21713 | 6.2 | NA | 29.736 | 357 | 710.82 | 687.6034 | 3.2662 | 91.6706 | 522.3017 | 94.3067 | 70 | 60 | 8.2 | 4.6 | 5 | 9.6 | 9.6 | 0.47758 | 0.47917 | 14.1538 | 14.341 | 9.8138 | 46.9862 | 0.30522 | NA | NA | 38.64 | 710.82 | 1078.8 | 1329.2256 | -23.2133 | 89.1765 | 1020.0228 | 96.2118 | 78 | 70 | 7.8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.8449 | 52.3551 | 0.36494 | NA | 7.2 | 65.758 | 1078.8 | 1487.2 | 1821.6975 | -22.4918 | 81.5804 | 1450.2487 | 95.4657
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-07-27 | 10:40 | 6407.12 | 25.5556 | 98 | 70 | 8.4 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 10.7066 | 64.8934 | 0.23885 | 7.4 | 6.23 | 57.888 | 318.72 | 347.76 | 1036 | 1909.3285 | -84.2981 | 83.354 | 1128.5443 | 94.8706 | 98 | 70 | 8.4 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.8108 | 70.7892 | 0.22241 | 6.23 | NA | 31.388 | 347.76 | 748.44 | 677.1783 | 9.5214 | 90.9742 | 512.4691 | 93.8751 | 70 | 60 | 8.8 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 10.1586 | 46.0414 | 0.29794 | NA | NA | 42.98 | 748.44 | 1024.24 | 1369.2448 | -33.684 | 87.6409 | 1058.8424 | 95.9409 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 12.9003 | 74.0997 | 0.25785 | NA | 7.2 | 72.072 | 1024.24 | 1481.48 | 1699.9721 | -14.7482 | 79.2754 | 1362.1061 | 94.7088
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-07-27 | 16:20 | 6412.71 | 25.5556 | 98 | 70 | 8.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.1829 | 64.7505 | 0.23938 | 7.4 | 6.24 | 57.218 | 322.04 | 352.8 | 1042 | 1998.2065 | -91.7665 | 83.7817 | 1175.5032 | 95.1325 | 98 | 70 | 8 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.9148 | 71.0852 | 0.22148 | 6.24 | NA | 30.739 | 352.8 | 742.5 | 691.635 | 6.8505 | 91.2871 | 522.2175 | 94.1138 | 70 | 60 | 8.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 10.062 | 46.738 | 0.2935 | NA | NA | 43.75 | 742.5 | 1035.4 | 1357.4 | -31.0991 | 87.5992 | 1049.95 | 95.8331 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 13.155 | 73.845 | 0.25874 | NA | 7.2 | 72.842 | 1035.4 | 1490.06 | 1741.2759 | -16.8594 | 79.3532 | 1388.3379 | 94.7533
[11 empty] | 1998-07-28 | 0:00 | 6420.31 | 25.5556 | 98 | 70 | 8.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.7713 | 65.1621 | 0.23787 | 7.5 | 6.23 | 59.697 | 317.06 | 344.4 | 913 | 1929.2467 | -111.3085 | 82.6664 | 1136.8233 | 94.7488 | 98 | 70 | 8 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.7389 | 71.2611 | 0.22093 | 6.23 | NA | 33.866 | 344.4 | 792.99 | 671.1076 | 15.37 | 90.1667 | 507.7538 | 93.3302 | 70 | 60 | 8.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 10.7518 | 46.0482 | 0.29789 | NA | NA | 46.34 | 792.99 | 1018.04 | 1450.042 | -42.4347 | 86.5447 | 1121.516 | 95.8681 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.8893 | 74.1107 | 0.25781 | NA | 7.3 | 74.921 | 1018.04 | 1305.59 | 1709.6606 | -30.9493 | 78.2459 | 1363.8503 | 94.5067
[11 empty] | 1998-07-28 | 7:55 | 6428.3 | 25.5556 | 98 | 70 | 8.0667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 10.8526 | 65.0808 | 0.23817 | 7.4 | 6.22 | 59.228 | 319.55 | 346.08 | 915 | 1942.8895 | -112.3376 | 82.886 | 1144.4847 | 94.8249 | 98 | 70 | 8 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.7906 | 71.2094 | 0.22109 | 6.22 | NA | 32.155 | 346.08 | 801.9 | 676.3553 | 15.6559 | 90.7088 | 511.2176 | 93.7101 | 70 | 60 | 8.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 10.8901 | 45.9099 | 0.29879 | NA | NA | 45.64 | 801.9 | 1019.28 | 1467.4088 | -43.9652 | 86.8123 | 1134.6544 | 95.9776 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.8968 | 74.1032 | 0.25784 | NA | 7.2 | 75.614 | 1019.28 | 1308.45 | 1711.3017 | -30.7885 | 78.1513 | 1365.2909 | 94.4617
[11 empty] | 1998-07-31 | 12:30 | 6505 | 26.1111 | 95 | 70 | 8.6333 | 0 | 16.6 | 3.05 |  | 19.65 | 19.65 | 0.84478 | 0 | 15.2061 | 15.1562 | 10.1184 | 63.7483 | 0.23775 | 7.4 | 6.44 | 38.056 | 323.7 | 309.96 | 926 | 1789.831 | -93.2863 | 87.7223 | 1049.8955 | 96.3753 | 95 | 71 | 8.9 | 10 | 9.65 | 19.65 | 19.65 | 0.47922 | 0.50891 | 15.3846 | 15.3342 | 4.2309 | 69.8691 | 0.21947 | 6.44 | NA | 31.27 | 309.96 | 592.02 | 598.7579 | -1.1381 | 89.9116 | 454.359 | 93.1178 | 71 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.4941 | 7.8911 | 48.6089 | 0.2776 | NA | NA | 44.03 | 592.02 | 954.8 | 1074.2512 | -12.5106 | 85.7949 | 833.1356 | 94.7151 | 120 | 70 | 8 | 2.2 | 3.05 | 5.25 | 5.25 | 0.55997 | 0.41905 | 18.8571 | 18.7953 | 12.0465 | 74.9535 | 0.25076 | NA | 7.1 | 69.454 | 954.8 | 1324.18 | 1593.4102 | -20.3318 | 77.5926 | 1274.1051 | 94.5488
[11 empty] | 1998-08-01 | 7:55 | 6524.33 | 26.1111 | 95 | 70 | 8.6333 | 0 | 16.6 | 3.1 |  | 19.7 | 19.7 | 0.84264 | 0 | 15.2061 | 15.1562 | 10.1831 | 63.6836 | 0.23799 | 7.4 | 6.4 | 37.252 | 325.36 | 314.16 | 924 | 1796.9577 | -94.4759 | 88.1423 | 1055.5588 | 96.4709 | 95 | 71 | 8.9 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 15.3342 | 4.2782 | 69.8218 | 0.21962 | 6.4 | NA | 31.86 | 314.16 | 584.1 | 605.1909 | -3.6108 | 89.8587 | 459.6755 | 93.069 | 71 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.4941 | 7.7851 | 48.7149 | 0.277 | NA | NA | 43.47 | 584.1 | 963.48 | 1059.8544 | -10.0027 | 86.1631 | 821.9772 | 94.7115 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 18.7953 | 12.1095 | 74.8905 | 0.25097 | NA | 7.1 | 69.685 | 963.48 | 1321.32 | 1597.7861 | -20.9235 | 77.8186 | 1280.6331 | 94.5586
[11 empty] | 1998-08-01 | 17:00 | 6533.45 | 26.1111 | 96 | 70 | 8.6333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.2475 | 11.0569 | 63.3098 | 0.24084 | 7.4 | 6.31 | 38.324 | 320.38 | 337.68 | 846 | 1950.3397 | -130.5366 | 88.6508 | 1144.0099 | 96.65 | 96 | 71 | 8.9 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.4875 | 4.6324 | 69.9676 | 0.22135 | 6.31 | NA | 33.04 | 337.68 | 611.82 | 654.8825 | -7.0384 | 90.2156 | 496.2812 | 93.3425 | 71 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.4941 | 8.1338 | 48.3662 | 0.279 | NA | NA | 46.97 | 611.82 | 952.32 | 1108.888 | -16.4407 | 86.0904 | 860.354 | 94.5406 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 18.7953 | 12.0011 | 74.9989 | 0.25061 | NA | 7.2 | 66.528 | 952.32 | 1209.78 | 1580.9466 | -30.6805 | 80.2985 | 1266.6333 | 94.7477
[11 empty] | 1998-08-01 | 23:15 | 6539.13 | 25.5556 | 98 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.6637 | 63.6696 | 0.24344 | 7.4 | 6.38 | 37.788 | 319.55 | 346.08 | 844 | 2062.2388 | -144.3411 | 89.0811 | 1204.1594 | 96.8619 | 98 | 72 | 9 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.7861 | 71.2139 | 0.22108 | 6.38 | NA | 32.45 | 346.08 | 615.78 | 676.0449 | -9.7868 | 90.6236 | 511.0624 | 93.6505 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 8.2009 | 48.7991 | 0.2811 | NA | NA | 46.27 | 615.78 | 949.84 | 1116.9488 | -17.5934 | 86.6303 | 866.3644 | 94.6593 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.0835 | 74.9165 | 0.25504 | NA | 7.2 | 65.681 | 949.84 | 1206.92 | 1598.2233 | -32.4216 | 81.0214 | 1274.0316 | 94.8446
[11 empty] | 1998-08-02 | 13:45 | 6554.14 | 25.5556 | 98 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 11.7844 | 63.5489 | 0.24391 | 7.4 | 6.39 | 37.118 | 317.06 | 348.6 | 850 | 2082.5165 | -145.0019 | 89.3523 | 1215.5582 | 96.9464 | 98 | 72 | 9 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 4.8336 | 71.1664 | 0.22123 | 6.39 | NA | 31.86 | 348.6 | 621.72 | 681.8369 | -9.6694 | 90.8606 | 515.2184 | 93.8162 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 8.2956 | 48.7044 | 0.28165 | NA | NA | 45.64 | 621.72 | 947.36 | 1128.6704 | -19.1385 | 86.9076 | 875.1952 | 94.7852 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 12.057 | 74.943 | 0.25495 | NA | 7.2 | 65.142 | 947.36 | 1215.5 | 1594.3199 | -31.1658 | 81.3133 | 1270.8399 | 94.8741
[11 empty] | 1998-08-02 | 20:20 | 6560.86 | 25.5556 | 98 | 70 | 8.6667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.1513 | 64.1821 | 0.2415 | 7.4 | 6.35 | 39.128 | 318.72 | 341.04 | 916 | 1967.4692 | -114.7892 | 88.5269 | 1154.2546 | 96.6101 | 98 | 72 | 9 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.705 | 71.295 | 0.22083 | 6.35 | NA | 31.624 | 341.04 | 595.98 | 663.2154 | -11.2815 | 90.7272 | 502.1277 | 93.702 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 7.9047 | 49.0953 | 0.27941 | NA | NA | 47.04 | 595.98 | 801.04 | 1079.0472 | -34.7058 | 86.2069 | 837.5136 | 94.3834 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 9.9202 | 77.0798 | 0.24788 | NA | 7.2 | 68.838 | 801.04 | 1309.88 | 1320.6672 | -0.82353 | 79.8153 | 1060.8536 | 93.5111
[11 empty] | 1998-08-03 | 7:30 | 6571.96 | 25.5556 | 98 | 70 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.5 | 8.1695 | 67.1639 | 0.23078 | 7.4 | 6.34 | 40.267 | 261.45 | 256.2 | 703 | 1458.227 | -107.4292 | 84.283 | 857.2135 | 95.3026 | 98 | 72 | 9 | 10.1 | 9.6 | 19.7 | 19.7 | 0.47922 | 0.51269 | 15.5385 | 15.7439 | 3.4433 | 72.5567 | 0.21699 | 6.34 | NA | 30.562 | 256.2 | 511.83 | 493.59 | 3.5637 | 88.071 | 374.895 | 91.8479 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.7656 | 50.2344 | 0.27307 | NA | NA | 42 | 511.83 | 744 | 925.2804 | -24.3656 | 83.6066 | 718.5552 | 94.1549 | 120 | 70 | 8 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 19.1065 | 9.2546 | 77.7454 | 0.24576 | NA | 7.2 | 66.836 | 744 | 1005.29 | 1240.5869 | -23.4059 | 73.9126 | 992.2935 | 93.2645
[11 empty] | 1998-08-03 | 19:30 | 6583.88 | 25.5556 | 98 | 70 | 8.6667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.4615 | 63.8718 | 0.24267 | 7.4 | 6.35 | 39.128 | 315.4 | 349.44 | 816 | 2021.1208 | -147.6864 | 88.8027 | 1185.2804 | 96.6988 | 98 | 72 | 9 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.8328 | 71.1672 | 0.22122 | 6.35 | NA | 31.624 | 349.44 | 532.62 | 680.3618 | -27.7387 | 90.9501 | 514.9009 | 93.8582 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 7.0115 | 49.9885 | 0.27441 | NA | NA | 45.71 | 532.62 | 840.72 | 961.1008 | -14.3188 | 86.9191 | 746.8604 | 93.8797 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.5308 | 76.4692 | 0.24986 | NA | 7.2 | 63.448 | 840.72 | 1166.88 | 1392.3324 | -19.321 | 81.8429 | 1116.5262 | 94.3174
[11 empty] | 1998-08-04 | 5:20 | 6593.74 | 25.5556 | 98 | 70 | 8.7333 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.1884 | 64.0783 | 0.24189 | 7.4 | 6.42 | 38.123 | 296.31 | 341.04 | 803 | 1972.8832 | -145.6891 | 88.8215 | 1156.9616 | 96.7049 | 98 | 72 | 9 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.7248 | 71.2752 | 0.22089 | 6.42 | NA | 30.326 | 341.04 | 510.84 | 664.5669 | -30.093 | 91.1078 | 502.8035 | 93.9686 | 72 | 60 | 9.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.719 | 50.081 | 0.27391 | NA | NA | 44.24 | 510.84 | 808.48 | 921.448 | -13.9729 | 87.0279 | 716.144 | 93.8225 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.1148 | 76.8852 | 0.24851 | NA | 7.2 | 61.908 | 808.48 | 1148.29 | 1338.3053 | -16.5477 | 81.8473 | 1073.3926 | 94.2325
[11 empty] | 1998-08-04 | 19:40 | 6608.13 | 25.5556 | 98 | 70 | 8.6667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 11.0519 | 64.2814 | 0.24113 | 7.4 | 6.33 | 38.458 | 300.46 | 337.68 | 836 | 1949.6179 | -133.2079 | 88.6111 | 1143.6489 | 96.6373 | 98 | 72 | 9 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 4.6584 | 71.3416 | 0.22068 | 6.33 | NA | 31.329 | 337.68 | 562.32 | 656.664 | -16.7776 | 90.7223 | 497.172 | 93.6986 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 7.418 | 49.582 | 0.27666 | NA | NA | 47.18 | 562.32 | 872.96 | 1015.6432 | -16.3448 | 86.0282 | 788.9816 | 94.0201 | 120 | 70 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 10.8946 | 76.1054 | 0.25105 | NA | 7.2 | 68.838 | 872.96 | 1195.48 | 1443.6272 | -20.7571 | 79.6144 | 1158.2936 | 94.0569
[11 empty] | 1998-08-06 | 7:00 | 6643.57 | 25.5556 | 100 | 72 | 8.6667 | 0 | 16.7 | 3.1 |  | 19.8 | 19.8 | 0.84343 | 0 | 15.2977 | 15.5 | 4.8262 | 72.5071 | 0.21377 | 7.7 | 6.35 | 32.294 | 231.57 | 162.96 | 720 | 866.8704 | -20.3987 | 80.1829 | 514.9152 | 93.7283 | 100 | 77 | 9 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.7439 | 2.0868 | 77.4132 | 0.20338 | 6.35 | NA | 25.724 | 162.96 | 454.41 | 305.8552 | 32.6918 | 84.2145 | 234.4076 | 89.026 | 77 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.0214 | 53.4786 | 0.2565 | NA | NA | 36.26 | 454.41 | 735.32 | 822.382 | -11.84 | 77.7491 | 638.396 | 94.3201 | 120 | 72 | 8 | 2.2 | 3.1 | 5.3 | 5.3 | 0.56672 | 0.41509 | 18.8571 | 19.1065 | 9.1831 | 78.8169 | 0.24242 | NA | 7.2 | 57.519 | 735.32 | 1029.6 | 1216.3401 | -18.1371 | 64.7036 | 975.83 | 94.1056
[11 empty] | 1998-08-06 | 16:00 | 6652.45 | 25.5556 | 100 | 72 | 8.6667 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 4.7393 | 72.594 | 0.21352 | 7.6 | 6.32 | 32.495 | 232.4 | 163.8 | 724 | 849.048 | -17.2718 | 80.1618 | 506.424 | 93.5834 | 100 | 78 | 9 | 10.1 | 9.8 | 19.9 | 19.9 | 0.48576 | 0.50754 | 15.5385 | 15.7439 | 2.0878 | 77.9122 | 0.20207 | 6.32 | NA | 26.019 | 163.8 | 457.38 | 305.7988 | 33.1412 | 84.1154 | 234.7994 | 88.9186 | 78 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.0561 | 53.9439 | 0.25429 | NA | NA | 36.82 | 457.38 | 729.12 | 827.4728 | -13.4892 | 77.5214 | 642.4264 | 94.2686 | 120 | 72 | 8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 9.0267 | 78.9733 | 0.24194 | NA | 7.2 | 57.365 | 729.12 | 1035.32 | 1190.9516 | -15.0322 | 64.9786 | 960.0358 | 94.0247
[11 empty] | 1998-08-07 | 14:05 | 6674.52 | 25.5556 | 100 | 72 | 8.6667 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 4.7162 | 72.6171 | 0.21345 | 7.6 | 6.35 | 32.294 | 234.06 | 162.96 | 720 | 844.8732 | -17.3435 | 80.1829 | 503.9166 | 93.5914 | 100 | 78 | 9 | 10.1 | 9.8 | 19.9 | 19.9 | 0.48576 | 0.50754 | 15.5385 | 15.7439 | 2.0715 | 77.9285 | 0.20203 | 6.35 | NA | 26.255 | 162.96 | 463.32 | 303.8498 | 34.419 | 83.8887 | 233.4049 | 88.7513 | 78 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.1436 | 53.8564 | 0.25471 | NA | NA | 36.68 | 463.32 | 725.4 | 838.7632 | -15.6277 | 77.4914 | 651.0416 | 94.366 | 120 | 72 | 8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 8.9757 | 79.0243 | 0.24178 | NA | 7.2 | 57.442 | 725.4 | 1029.6 | 1184.6211 | -15.0564 | 64.7509 | 955.0106 | 93.9852
[11 empty] | 1998-08-08 | 7:00 | 6691.43 | 25.5556 | 100 | 72 | 8.7333 | 0 | 16.7 | 3.2 |  | 19.9 | 19.9 | 0.8392 | 0 | 15.2977 | 15.5 | 4.862 | 72.4046 | 0.21407 | 7.6 | 6.33 | 34.974 | 243.19 | 169.68 | 814 | 872.6769 | -7.2085 | 79.3883 | 521.1785 | 93.2894 | 100 | 78 | 9 | 10.1 | 9.8 | 19.9 | 19.9 | 0.48576 | 0.50754 | 15.5385 | 15.7439 | 2.1483 | 77.8517 | 0.20223 | 6.33 | NA | 27.907 | 169.68 | 495.99 | 315.793 | 36.3308 | 83.5532 | 242.7365 | 88.5032 | 78 | 60 | 9.2 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.7175 | 6.5758 | 53.2242 | 0.25773 | NA | NA | 39.34 | 495.99 | 760.12 | 897.842 | -18.1185 | 76.8152 | 696.916 | 94.3551 | 120 | 72 | 8 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 19.1065 | 9.3512 | 78.6488 | 0.24293 | NA | 7.2 | 64.218 | 760.12 | 1164.02 | 1238.5526 | -6.403 | 62.1535 | 999.3363 | 93.5739
[11 empty] | 1998-08-12 | 8:30 | 6696.53 | 26.1111 | 100 | 70 | 10 | 0 | 16.8 | 3 |  | 19.8 | 19.8 | 0.84848 | 0 | 15.3893 | 15.3389 | 9.6949 | 65.3051 | 0.23488 | 7.4 | 6.38 | 35.51 | 285.52 | 290.64 | 795 | 1719.368 | -116.2727 | 87.7821 | 1005.004 | 96.4667 | 100 | 72 | 10 | 10.1 | 9.7 | 19.8 | 19.8 | 0.48249 | 0.5101 | 15.5385 | 15.4875 | 3.8723 | 72.1277 | 0.21472 | 6.38 | NA | 35.99 | 290.64 | 485.1 | 555.791 | -14.5725 | 87.617 | 423.2155 | 91.4961 | 72 | 60 | 10 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 13.8008 | 6.4412 | 49.5588 | 0.27847 | NA | NA | 40.88 | 485.1 | 768.8 | 884.898 | -15.1012 | 85.9345 | 684.999 | 94.0321 | 120 | 70 | 10 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 18.7953 | 9.5946 | 75.4054 | 0.24926 | NA | 7 | 66.759 | 768.8 | 1136.85 | 1283.6301 | -12.9111 | 77.0303 | 1026.215 | 93.4946
[11 empty] | 1998-08-12 | 14:30 | 6703.14 | 26.1111 | 100 | 72 | 9.6667 | 0 | 16.8 | 3.2 |  | 20 | 20 | 0.84 | 0 | 15.3893 | 15.3389 | 9.436 | 66.8973 | 0.22929 | 7.4 | 6.36 | 35.376 | 280.54 | 295.68 | 802 | 1662.276 | -107.2663 | 88.0357 | 978.978 | 96.3864 | 100 | 72 | 10 | 10.2 | 9.8 | 20 | 20 | 0.48739 | 0.51 | 15.6923 | 15.6409 | 3.9726 | 72.0274 | 0.21715 | 6.36 | NA | 34.397 | 295.68 | 514.8 | 567.6276 | -10.2618 | 88.3668 | 431.6538 | 92.0313 | 72 | 60 | 9 | 4.4 | 5 | 9.4 | 9.4 | 0.47104 | 0.46809 | 13.5385 | 13.4941 | 6.8265 | 50.1735 | 0.26895 | NA | NA | 40.74 | 514.8 | 767.56 | 931.9728 | -21.4202 | 86.2216 | 723.3864 | 94.3682 | 120 | 72 | 10 | 2.2 | 3.2 | 5.4 | 5.4 | 0.58021 | 0.40741 | 18.8571 | 18.7953 | 9.4129 | 76.5871 | 0.24541 | NA | 7.2 | 67.067 | 767.56 | 1146.86 | 1249.1489 | -8.919 | 77.3177 | 1008.3545 | 93.3489
[11 empty] | 1998-08-14 | 9:00 | 6744.35 | 26.1111 | 100 | 71 | 8.6667 | 0 | 16.7 | 3 |  | 19.7 | 19.7 | 0.84772 | 0 | 15.2977 | 15.2475 | 10.3736 | 66.4597 | 0.22943 | 7.3 | 6.24 | 39.128 | 311.25 | 313.32 | 815 | 1839.6555 | -125.7246 | 87.5118 | 1076.4877 | 96.3652 | 100 | 72 | 8.8 | 10 | 9.7 | 19.7 | 19.7 | 0.48085 | 0.50761 | 15.3846 | 15.3342 | 4.2842 | 72.9158 | 0.2103 | 6.24 | NA | 30.621 | 313.32 | 560.34 | 604.7623 | -7.9277 | 90.2269 | 459.0411 | 93.3294 | 72 | 60 | 8.9 | 4.5 | 5 | 9.5 | 9.5 | 0.47431 | 0.47368 | 13.8462 | 13.8008 | 7.5027 | 49.5973 | 0.27826 | NA | NA | 42.91 | 560.34 | 886.6 | 1026.027 | -15.726 | 86.3047 | 793.1835 | 94.5902 | 120 | 71 | 8.3 | 2.2 | 3 | 5.2 | 5.2 | 0.55322 | 0.42308 | 18.8571 | 18.7953 | 11.1898 | 76.0102 | 0.24727 | NA | 7 | 67.837 | 886.6 | 1165.45 | 1487.0262 | -27.5924 | 78.349 | 1186.8131 | 94.2841
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on W6: S Allgeier (11/17/99): Reviewer entered formula to calculate average system permeate pressure.
Note on DU16: CDM: verified w/ lab data sheets
Note on DU17: CDM: verified w/ lab data sheets
Note on DU23: CDM: verified w/ lab data sheets
Note on DV16: CDM: verified w/ lab data sheets
Note on DV17: CDM: verified w/ lab data sheets
Note on DV23: CDM: verified w/ lab data sheets
Note on DW16: CDM: verified w/ lab data sheets
Note on DW17: CDM: verified w/ lab data sheets
Note on DW23: CDM: verified w/ lab data sheets
Note on EO16: CDM: verified w/ lab data sheets
Note on EO17: CDM: verified w/ lab data sheets
Note on EO23: CDM: verified w/ lab data sheets
Note on EP16: CDM: verified w/ lab data sheets
Note on EP17: CDM: verified w/ lab data sheets
Note on EP23: CDM: verified w/ lab data sheets
Note on EQ16: CDM: verified w/ lab data sheets
Note on EQ17: CDM: verified w/ lab data sheets
Note on EQ23: CDM: verified w/ lab data sheets
Note on FI16: CDM: verified w/ lab data sheets
Note on FI17: CDM: verified w/ lab data sheets
Note on FI23: CDM: verified w/ lab data sheets
Note on FJ16: CDM: verified w/ lab data sheets
Note on FJ17: CDM: verified w/ lab data sheets
Note on FJ23: CDM: verified w/ lab data sheets
Note on FK16: CDM: verified w/ lab data sheets as 145 but exceptionally low value for concentrate
Note on FK17: CDM: verified w/ lab data sheets
Note on FK23: CDM: verified w/ lab data sheets
Note on GC16: CDM: verified w/ lab data sheets
Note on GC17: CDM: verified w/ lab data sheets
Note on GC23: CDM: verified w/ lab data sheets
Note on GD16: CDM: verified w/ lab data sheets
Note on GD17: CDM: verified w/ lab data sheets
Note on GD23: CDM: verified w/ lab data sheets
Note on GE16: CDM: verified w/ lab data sheets
Note on GE17: CDM: verified w/ lab data sheets
Note on GE23: CDM: verified w/ lab data sheets
Note on GW16: CDM: verified w/ lab data sheets
Note on GW17: CDM: verified w/ lab data sheets
Note on GW23: CDM: verified w/ lab data sheets
Note on GX16: CDM: verified w/ lab data sheets
Note on GX17: CDM: verified w/ lab data sheets
Note on GX22: Alison Gusses: Data verified by consultant
Note on GX23: CDM: verified w/ lab data sheets
Note on GY16: CDM: verified w/ lab data sheets
Note on GY17: CDM: verified w/ lab data sheets
Note on GY23: CDM: verified w/ lab data sheets
Note on HQ16: CDM: verified w/ lab data sheets
Note on HQ17: CDM: verified w/ lab data sheets
Note on HQ23: CDM: originally entered as 0.008, verified as 0.000
Note on HR16: CDM: verified w/ lab data sheets
Note on HR17: CDM: verified w/ lab data sheets
Note on HR23: CDM: verified w/ lab data sheets
Note on HS16: CDM: verified w/ lab data sheets
Note on HS17: CDM: verified w/ lab data sheets
Note on HS23: CDM: verified w/ lab data sheets

## 23DUP
Field 5-12: Duplicate Analysis Of System And Stage Water Quality For Week 50 | [9 empty] | Field 5-12: Duplicate Analysis Of System And Stage Water Quality For Week 50 (continued)
System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection
|  | System recovery during sample collection (decimal) | 0.84772 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.50761
|  | System feed flow rate during sample collection (gpm) | 19.7 | HI - 23 DUP | [7 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 10 |  | HI - 23 DUP
|  | System influent flow rate during sample collection (gpm) | 19.7 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 19.7
System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters
Parameter | Units | Cp-sys-50 (dup) | CF-sys-50 (dup) | CC-sys-50 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-50 (dup) | CI-s1-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | 1998-08-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | --- | --- | --- | ---
Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | ---
Operation time | hh.hh | 6694.8 | 6694.8 | 6694.8 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6694.8 | 6694.8 | --- | --- | --- | ---
pH | --- | 5.75 | 6.56 | 7 | --- | --- | --- | --- | --- | pH | --- | 5.77 | 6.56 | --- | --- | --- | ---
Temperature | oC | 25.4 | 25.1 | 26.1 | --- | --- | --- | --- | --- | Temperature | oC | 25.1 | 25.1 | --- | --- | --- | ---
Alkalinity | mg/L as CaCO3 | 17 | 115 | 582 | 11.7594 | 97.9795 | 85.2174 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 | 17 | 115 | 216.0309 | 85.2174 | 165.5155 | 89.7291
Total dissolved solids | mg/L | 40 | 330 | 1404 | 24.492 | 98.2556 | 87.8788 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L | 37 | 330 | 632.0619 | 88.7879 | 481.0309 | 92.3082
Total hardness | mg/L as CaCO3 | 15 | 185 | 1069 | 5.9091 | 99.4472 | 91.8919 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 | 13 | 185 | 362.3196 | 92.973 | 273.6598 | 95.2496
Calcium hardness | mg/L as CaCO3 | 12 | 183 | 1065 | 2.8556 | 99.7319 | 93.4426 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | 11 | 183 | 360.3196 | 93.9891 | 271.6598 | 95.9508
Turbidity | ntu | BMRL | 0.06 | 37.05 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.06 | 0.06 | 0.06 | 0 | 0.06 | 0
Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.53 | 6.14 | 11.9235 | 91.3681 | 9.0318 | 94.1318
Total organic carbon | mg/L | 0.16 | 6.14 | 33.1 | -0.15979 | 100.4827 | 97.3941 | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.003 | 0.205 | 0.41325 | 98.5366 | 0.30912 | 99.0295
UV254 | cm-1 | 0.003 | 0.205 | 1.08 | -0.0078021 | 100.7224 | 98.5366 | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | 0.56604 | 3.3388 | --- | --- | --- | ---
SUVA | L/(mg*m) | 1.875 | 3.3388 | 3.2628 | --- | --- | --- | --- | ---
Bromide | mg/L | 9 | 16 | --- | 8.6257 | --- | 43.75 | #DIV/0! | #DIV/0!
SDS-Cl2 dose | mg/L | 3.6 | 12 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
SDS-Free Cl2 residual | mg/L | 0.73 | 1.08 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.46392
SDS-Cl2 demand | mg/L | 2.87 | 10.92 | --- | 2.4395 | --- | 73.7179 | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.5
SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.7
SDS-Chlorination pH | --- | 5.75 | 6.62 | --- | --- | --- | --- | --- | ---
SDS-Incubation time | hours | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
SDS-TOX | mg Cl- /L | BMRL | 355 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-50 (dup) | CI-s2-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
SDS-CHCl3 | mg/L | 0.46 | 32.5 | --- | -1.2534 | --- | 98.5846 | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | --- | --- | --- | ---
SDS-BDCM | mg/L | BMRL | 13.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | ---
SDS-DBCM | mg/L | BMRL | 3.54 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6694.8 | 6694.8 | --- | --- | --- | ---
SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.79 | 6.74 | --- | --- | --- | ---
SDS-THM4 | mg/L | 0.46 | 49.84 | --- | -2.1806 | --- | 99.077 | #DIV/0! | #DIV/0! | Temperature | oC | 24.6 | 25.3 | --- | --- | --- | ---
SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 220 | 393.9423 | 83.4783 | 306.9712 | 93.8105
SDS-DCAA* | mg/L | BMRL | 17 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 45 | 599 | 1078.4231 | 86.3636 | 838.7115 | 94.6346
SDS-TCAA* | mg/L | BMRL | 30 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 15 | 401 | 735.0385 | 91.8919 | 568.0192 | 97.3592
SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 12 | 365 | 670.4808 | 93.4426 | 517.7404 | 97.6822
SDS-DBAA* | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.02 | 0.15 | 0.2625 | 66.6667 | 0.20625 | 90.303
SDS-BCAA* | mg/L | BMRL | 6.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 3 | 9.7 | 15.4981 | 51.1401 | 12.599 | 76.1887
SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.464 | 0.86294 | 98.5366 | 0.66347 | 99.5478
SDS-CDBAA | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.1 | 4.7835 | --- | --- | --- | ---
SDS-DCBAA | mg/L | BMRL | 12 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
SDS-HAA5 | mg/L | 0 | 48.3 | --- | -2.5829 | --- | 100 | #DIV/0! | #DIV/0!
SDS-HAA6 | mg/L | 0 | 54.4 | --- | -2.9091 | --- | 100 | #DIV/0! | #DIV/0! | Stage 3 Operating Parameters During Sample Collection
BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.42308
*: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 2.2
[12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.2
Stage 3 Permeate and Influent Water Quality Parameters
[10 empty] | Parameter | Units | Cp-s3-50 (dup) | CI-s3-50 (dup) | CC(calc) | RF (%) | CB | RB (%)
[10 empty] | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | --- | --- | --- | ---
[10 empty] | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | ---
[10 empty] | Operation time | hh.hh | 6694.8 | 6694.8 | --- | --- | --- | ---
[10 empty] | pH | --- | 5.89 | 6.92 | --- | --- | --- | ---
[10 empty] | Temperature | oC | 25.6 | 25.2 | --- | --- | --- | ---
[10 empty] | Alkalinity | mg/L as CaCO3 | 25 | 386 | 650.7333 | 78.2609 | 518.3667 | 95.1772
[10 empty] | Total dissolved solids | mg/L | 69 | 992 | 1668.8667 | 79.0909 | 1330.4333 | 94.8137
[10 empty] | Total hardness | mg/L as CaCO3 | 21 | 665 | 1137.2667 | 88.6486 | 901.1333 | 97.6696
[10 empty] | Calcium hardness | mg/L as CaCO3 | 17 | 658 | 1128.0667 | 90.7104 | 893.0333 | 98.0964
[10 empty] | Turbidity | ntu | BMRL | 11.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | Total organic carbon | mg/L | 0.04 | 18.8 | 32.5573 | 99.3485 | 25.6787 | 99.8442
[10 empty] | UV254 | cm-1 | 0.004 | 0.669 | 1.1567 | 98.0488 | 0.91283 | 99.5618
[10 empty] | SUVA | L/(mg*m) | 10 | 3.5585 | --- | --- | --- | ---