## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Fort Worth Water Department | Carbon manufacturer | Calgon Corporation | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2200012 | Carbon trade name | Filtrasorb - F820 | mesh size | (mm) | Coagulation | 50% Ferric Sulfate solution - Avg. Dose = 48 mg/L; Range = 38 to 100 mg/L / CATFLOC Polymer - Avg. Dose = 1 mg/L; Range = -- | Pilot-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | 1503 | Carbon type | Bituminous | 4 | 4.75 | Rapid Mixing | Rapid mix basins with mixing paddles | Pilot-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 3.6 | 6 | 3.35 | Flocculation | 3-flocculation stages with floc paddles operating at 60, 50, and 35 rpm | Pilot-scale | START | --- | 1998-04-14 | 15:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 15:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-14 | 15:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 57
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 76.2 | 8 | 2.36 | Sedimentation | Basin includes a tube settler and has a detention time of 1 1/2 hours | Pilot-scale | Avg-A1 | Y | 1998-04-15 | 17:00 | 26 | 78 | 156 | 7.66 | 1.76 | 95 | 22.4 | 107 | 97 | BMRL | 50 | 3.15 | NR | #VALUE! | 3 | 0.03 | 2.97 | 19.4 | 8.38 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | Avg-A1 | Y | 1998-04-15 | 17:00 | 26 | 156 | 8.2 | 0.31 | 22.4 | BMRL | BMRL | 0 | -- | 1 | 0.63 | 0.37 | 19.2 | 8.23 | 24 | NR | NR | NR | NR | NR | NR | BMRL | NR | NR | BMRL | NR | NR | BMRL | BMRL | NR | NR | NR | Avg-A1 | Y | 1998-04-15 | 17:00 | 26 | 78 | 8.5 | 0.23 | 23.2 | BMRL | BMRL | 0 | -- | 1 | 0.68 | 0.32 | 19.2 | 7.96 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1 | 1 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 505.7 | 10 | 2 | Filtration | 3"-dia. dual media (sand/anthracite with gravel support), declining rate columns | Pilot-scale | A2 | N | 1998-04-29 | 16:30 | 281.5 | 844.5 | 1689 | 7.58 | 0.33 | 85 | 22 | 109 | 97 | BMRL | 49 | 3.5 | 0.084 | 2.4 | 3 | 0 | 3 | 20.2 | 7.9 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A2 | N | 1998-04-29 | 16:30 | 281.5 | 1689 | 7.45 | 0.28 | 21 | BMRL | 0.8 | 0.01 | 1.25 | 1.5 | 0.8 | 0.7 | 20.4 | 7.72 | 24 | 26 | 2.9 | 5.7 | 8.9 | 3 | 20.5 | BMRL | 1.9 | 2.3 | BMRL | 2.8 | 2.5 | BMRL | 2.5 | 2.1 | 7 | 9.5 | A2 | N | 1998-04-29 | 16:30 | 281.5 | 844.5 | 8 | 0.25 | 21 | BMRL | BMRL | 0.001 | -- | 1 | 0.7 | 0.3 | 20.4 | 7.8 | 24 | BMRL | BMRL | BMRL | 1.1 | BMRL | 1.1 | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1.2 | 1.2 | Construction Contingencies (% of construction costs) | 25
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A3 | N | 1998-05-19 | 11:30 | 756.5 | 2269.5 | 4539 | 7.47 | 0.63 | 70 | 24 | 102 | 87 | BMRL | 52 | 3.5 | 0.082 | 2.3429 | 3.5 | 0.48 | 3.02 | 24.3 | 8.01 | 24 | 285 | 98 | 29 | 6.9 | BMRL | 133.9 | 3 | 25 | 15 | BMRL | 1.7 | 8.7 | BMRL | BMRL | 5.9 | 44.7 | 53.4 | A3 | N | 1998-04-30 | 14:00 | 303 | 1818 | 7.4 | 0.33 | 24 | BMRL | 0.7 | 0.01 | 1.4286 | 1 | 0.27 | 0.73 | 22 | 7.77 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A3 | N | 1998-05-19 | 11:30 | 756.5 | 2269.5 | 6.85 | 0.35 | 24 | BMRL | 0.6 | 0.004 | 0.66667 | 1 | 0.41 | 0.59 | 24.3 | 7.91 | 24 | BMRL | 1.2 | 1.5 | 4.8 | 7 | 14.5 | BMRL | BMRL | BMRL | BMRL | 2.5 | BMRL | BMRL | BMRL | BMRL | 2.5 | 2.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 20 | 16 | 1.18 |  |  |  | A4 | N | 1998-05-21 | 15:00 | 808 | 2424 | 4848 | 7.43 | 1.43 | 75 | 25 | 99 | 85 | BMRL | NR | 3.6 | 0.092 | 2.5556 | 3.5 | 0.18 | 3.32 | NA | 8.1 | 24 | 280 | 69 | 20 | 6.5 | BMRL | 95.5 | 3.6 | 23 | 11 | BMRL | 2.2 | 8.3 | BMRL | 2.2 | 4.8 | 39.8 | 48.1 | A4 | N | 1998-05-08 | 14:00 | 495 | 2970 | 7.3 | 0.23 | 24 | BMRL | 1.2 | 0.022 | 1.8333 | 1.5 | 0.61 | 0.89 | 19 | 8.2 | 24 | 82 | 10 | 11 | 10 | 1.9 | 32.9 | BMRL | 5 | 2.6 | BMRL | 3.2 | 5 | NR | 2.5 | 3.4 | 10.8 | 15.8 | A4 | N | 1998-05-21 | 15:00 | 808 | 2424 | 7.43 | 0.71 | 25 | BMRL | 0.6 | 0.006 | 1 | 1 | 0.29 | 0.71 | NA | 8.25 | 24 | BMRL | 1.2 | 2.3 | 5.3 | 4.9 | 13.7 | BMRL | BMRL | BMRL | BMRL | 2.1 | 1 | BMRL | BMRL | BMRL | 2.1 | 3.1 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6095.24
FAX Number |  | Flow rate, Q (L/hr) | 24 | 20 | 0.85 |  |  |  | A5 | N | 1998-05-28 | 16:00 | 977 | 2931 | 5862 | 7.57 | 0.35 | 74 | 24 | 108 | 95 | BMRL | 52 | 3.4 | 0.076 | 2.2353 | 2.5 | 0 | 2.5 | 24.7 | 7.75 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A5 | N | 1998-05-11 | 14:00 | 567 | 3402 | 7.21 | 0.27 | 24 | BMRL | 1.5 | 0.029 | 1.9333 | 1 | 0.52 | 0.48 | 19 | 8.31 | 24 | 86 | 13 | 14 | 12 | 1.8 | 40.8 | BMRL | 6.4 | 4.3 | BMRL | 3.4 | 6 | NR | 2.8 | 4.6 | 14.1 | 20.1 | A5 | N | 1998-05-28 | 16:00 | 977 | 2931 | 7.22 | 0.28 | 24 | BMRL | 0.8 | 0.015 | 1.875 | 1 | 0 | 1 | 24.4 | 8.69 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1998-06-04 | 10:00 | 1139 | 3417 | 6834 | 7.42 | 0.31 | 65 | 25.8 | 93 | 80 | BMRL | 52 | 3.6 | 0.076 | 2.1111 | 3 | 0.98 | 2.02 | 22.9 | 7.8 | 24 | 320 | 72 | 21 | 6.6 | BMRL | 99.6 | 4.2 | 25 | 23 | BMRL | 1.6 | 9 | BMRL | 2.4 | 9.5 | 53.8 | 62.8 | A6 | N | 1998-05-12 | 11:00 | 588 | 3528 | 7.42 | 0.34 | 24 | BMRL | 1.7 | 0.038 | 2.2353 | 1.5 | 0.38 | 1.12 | 24 | 7.89 | 24 | 105 | 16 | 14 | 10 | 1.2 | 41.2 | BMRL | 7.3 | 4.9 | BMRL | 2.9 | 6.2 | NR | 2.2 | 4.4 | 15.1 | 21.3 | A6 | N | 1998-06-04 | 10:00 | 1139 | 3417 | 7.22 | 0.14 | 25.4 | BMRL | 1.6 | 0.025 | 1.5625 | 1 | 0.56 | 0.44 | 23.1 | 7.6 | 24 | 74 | 7.5 | 9.7 | 11 | 2.4 | 30.6 | BMRL | 4.3 | 3 | BMRL | 3.8 | 5.4 | BMRL | 3.1 | 4.4 | 11.1 | 16.5 | Labor Rate + Fringe ($/work-hour) | 27.2
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | Avg-A7 | Y | 1998-06-13 | 16:30 | 1361.5 | 4084.5 | 8169 | 7.52 | 0.21 | 71.5 | 25.3 | 98 | 85 | 0.09 | 51.5 | 3.15 | 0.066 | 2.0952 | 2 | 0.96 | 1.04 | 24.1 | 7.66 | 24 | 196 | 47.5 | 21 | 8.15 | BMRL | 76.65 | BMRL | 14 | 9.8 | BMRL | 1.8 | 6.85 | BMRL | BMRL | 5.25 | 25.6 | 32.45 | Avg-A7 | Y | 1998-05-15 | 15:00 | 664 | 3984 | 7.31 | 0.32 | 24 | 0.06 | 1.95 | 0.04 | 2.0513 | 1.5 | 0.64 | 0.86 | 22.5 | 7.9 | 24 | 115 | NR | NR | NR | NR | NR | BMRL | 8.7 | 5.75 | BMRL | 2.85 | NR | BMRL | 2.1 | 4.6 | 17.3 | 17.3 | Avg-A7 | Y | 1998-06-13 | 16:30 | 1361.5 | 4084.5 | 7.32 | 0.13 | 25.7 | BMRL | 1.45 | 0.034 | 2.3448 | 1 | NR | #VALUE! | 24.1 | 7.66 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | Labor Overhead Factor (% of labor) | 33
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 4104.5588 | 50 | 0.3 |  |  |  | A8 | N | 1998-07-15 | 9:30 | 2074.5 | 6223.5 | 12447 | 7.21 | 0.4 | 68 | 25.1 | 96 | 82 | BMRL | 69 | 3.4 | 0.079 | 2.3235 | 2 | 0.06 | 1.94 | 25.1 | 7.91 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A8 | N | 1998-05-27 | 11:00 | 948 | 5688 | 7.34 | 0.26 | 24 | 0.09 | 1.9 | 0.038 | 2 | 1.5 | 0.51 | 0.99 | 24.2 | 7.9 | 24 | 120 | 21 | 17 | 11 | 1.3 | 50.3 | BMRL | 8.8 | 6.3 | BMRL | 2.8 | 6.6 | BMRL | 2.9 | 6 | 17.9 | 24.5 | A8 | N | 1998-07-15 | 9:30 | 2074.5 | 6223.5 | 7.36 | 0.16 | 25.8 | BMRL | 1.6 | 0.031 | 1.9375 | 1 | 0.21 | 0.79 | 25.1 | 7.93 | 24 | 70 | 12 | 13 | 13 | 3.2 | 41.2 | BMRL | 3.8 | 1.7 | BMRL | 3.8 | 4.7 | BMRL | BMRL | 2.3 | 9.3 | 14 | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 8209.1176 | 60 | 0.25 |  |  |  | A9 | N | 1998-08-03 | 9:30 | 2530.5 | 7591.5 | 15183 | 7.5 | 1.11 | 49 | 28.4 | 67 | 52 | BMRL | 67 | 4.7 | 0.1 | 2.1277 | 3 | 0.05 | 2.95 | 24.8 | 7.72 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A9 | N | 1998-05-28 | 10:30 | 971.5 | 5829 | 7.33 | 0.27 | 24 | BMRL | 1.8 | 0.04 | 2.2222 | 1.5 | 0.43 | 1.07 | 24 | 7.64 | 24 | 105 | 21 | 17 | 11 | 1.2 | 50.2 | BMRL | 9.6 | 7.9 | BMRL | 3.1 | 7.1 | BMRL | 3.8 | 8.2 | 20.6 | 27.7 | A9 | N | 1998-08-03 | 9:30 | 2530.5 | 7591.5 | 7.18 | 0.41 | 27.5 | BMRL | 2.3 | 0.042 | 1.8261 | 1.5 | 0.1 | 1.4 | 24.2 | 7.95 | 24 | 120 | 18 | 16 | 13 | 2.1 | 49.1 | BMRL | 6.8 | 3.7 | BMRL | 3.1 | 5.5 | BMRL | BMRL | 3.2 | 13.6 | 19.1 | Fuel Oil Rate ($/gal) | NA
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-08-04 | 9:30 | 2554.5 | 7663.5 | 15327 | 7.32 | 0.81 | 52 | 24.2 | 67 | 52 | 0.07 | 71 | 4.9 | 0.117 | 2.3878 | 3.5 | 0 | 3.5 | 24.1 | 7.72 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A10 | N | 1998-06-03 | 10:30 | 1115.5 | 6693 | 7.2 | 0.18 | 24.2 | BMRL | 2.2 | 0.047 | 2.1364 | 1.5 | 0.03 | 1.47 | 23.8 | 7.87 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A10 | N | 1998-08-04 | 9:30 | 2554.5 | 7663.5 | 7.31 | 0.46 | 24.9 | 0.06 | 2.7 | 0.055 | 2.037 | 1.7 | 0.04 | 1.66 | 24 | 7.85 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | Natural Gas Rate ($/ft3) | 5.3
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-08-08 | 11:30 | 2652.5 | 7957.5 | 15915 | 7.45 | 0.96 | 65 | 26.1 | 90 | 75 | BMRL | 66 | 4.1 | 0.078 | 1.9024 | 2.5 | 0.1 | 2.4 | 23.5 | 7.78 | 24 | 250 | 55 | 25 | 9.8 | BMRL | 89.8 | BMRL | 16 | 12 | BMRL | 1.8 | 7.2 | BMRL | 2.2 | 5.6 | 29.8 | 37 | A11 | N | 1998-06-05 | 11:00 | 1164 | 6984 | 7.87 | 0.26 | 23.8 | NR | 2.4 | 0.052 | 2.1667 | 1.5 | 0.48 | 1.02 | 24.4 | 7.62 | 24 | 165 | 28 | 16 | 8.4 | BMRL | 52.4 | BMRL | 13 | 12 | BMRL | 2.4 | 7.7 | BMRL | 2.2 | 6.9 | 27.4 | 35.1 | A11 | N | 1998-08-08 | 11:30 | 2652.5 | 7957.5 | 7.23 | 0.47 | 25.6 | BMRL | 2.2 | 0.038 | 1.7273 | 1.5 | 0.18 | 1.32 | 23.5 | 7.79 | 24 | 110 | 17 | 17 | 14 | 2.6 | 50.6 | BMRL | 6.2 | 3.9 | BMRL | 3 | 5.4 | BMRL | 2.3 | 3.3 | 13.1 | 18.5 | Current Process Water Rate ($/1000 gal) | 0.15
FAX Number |  | Carbon particle diameter, d (mm) | 1.605 | [5 empty] | A12 | N | 1998-08-31 | 10:00 | 3035 | 9105 | 18210 | 8.07 | 1.35 | 85 | 26.2 | 90 | 72 | BMRL | 100 | 2.8 | 0.063 | 2.25 | 3.5 | 0.68 | 2.82 | 21.6 | 7.95 | 24 | 220 | 49 | 30 | 17 | 2.3 | 98.3 | 2.6 | 14 | 12 | BMRL | 3.3 | 8.8 | BMRL | 4.6 | 9.9 | 31.9 | 40.7 | A12 | N | 1998-06-18 | 10:00 | 1475 | 8850 | 7.39 | 0.11 | 24.7 | BMRL | 2.1 | 0.051 | 2.4286 | 1.5 | 0.52 | 0.98 | 25.2 | 7.7 | 24 | 165 | 30 | 18 | 10 | 1.1 | 59.1 | BMRL | 11 | 8.9 | BMRL | 2.8 | 7.2 | BMRL | 2.4 | 6.2 | 22.7 | 29.9 | A12 | N | 1998-08-31 | 10:00 | 3035 | 9105 | 7.76 | 0.54 | 25.6 | BMRL | 2.6 | 0.026 | 1 | 1.5 | 0.32 | 1.18 | 21.4 | 7.89 | 24 | 94 | 11 | 16 | 20 | 7.2 | 54.2 | BMRL | 3.6 | 1.9 | 1 | 5.6 | 5.1 | BMRL | 2.8 | 2.8 | 12.1 | 17.2 | Modifications to Existing Plant (% of construction costs) | 33
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0045604 | [5 empty] | A13 | N | 1998-09-16 | 9:00 | 3418 | 10254 | 20508 | 7.8 | 0.48 | 67 | 24.1 | 98 | 82 | BMRL | 62 | 3.4 | 0.063 | 1.8529 | 3 | 0.47 | 2.53 | 24.8 | 7.75 | 24 | 275 | 48 | 21 | 11 | 1.2 | 81.2 | BMRL | 19 | 15 | BMRL | 2.8 | 8.1 | BMRL | 6.9 | 6.9 | 36.8 | 44.9 | A13 | N | 1998-07-02 | 9:30 | 1810.5 | 10863 | 7.35 | 0.29 | 25.3 | BMRL | 3 | 0.059 | 1.9667 | 1.5 | 0 | 1.5 | 24.8 | 7.83 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A13 | N | 1998-09-16 | 9:00 | 3418 | 10254 | 7.41 | 0.2 | 24.1 | BMRL | 2.3 | 0.032 | 1.3913 | 2 | 0.76 | 1.24 | 24.3 | 7.98 | 24 | 110 | 17 | 15 | 13 | 2.8 | 47.8 | BMRL | 7.8 | 5.5 | BMRL | 4.3 | 6.6 | BMRL | BMRL | 3.4 | 17.6 | 24.2
|  | Hydraulic loading rate1, v (m/hr) | 5.2627 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1998-10-07 | 9:00 | 3922 | 11766 | 23532 | 7.52 | 0.79 | 63 | 21.5 | 85 | 72 | BMRL | 75 | 2.8 | 0.049 | 1.75 | 3 | 0.47 | 2.53 | 23.8 | 7.94 | 24 | 230 | 49 | 24 | 11 | 1.1 | 85.1 | 2.8 | 16 | 11 | BMRL | 2.3 | 7.2 | BMRL | 2.6 | 6.1 | 32.1 | 39.3 | A14 | N | 1998-07-16 | 9:30 | 2098.5 | 12591 | 7.4 | 0.22 | 24.7 | BMRL | 2.3 | 0.052 | 2.2609 | 1.5 | 0.3 | 1.2 | 25.3 | 8.02 | 24 | 125 | 24 | 17 | 11 | 1.5 | 53.5 | BMRL | 7.7 | 3.8 | BMRL | 2.7 | 5.9 | BMRL | BMRL | 3.5 | 14.2 | 20.1 | A14 | N | 1998-10-07 | 9:00 | 3922 | 11766 | 7.06 | 0.26 | 23.9 | BMRL | 2 | 0.026 | 1.3 | 2 | 0.45 | 1.55 | 23.8 | 7.94 | 24 | 115 | 23 | 19 | 15 | 2.8 | 59.8 | BMRL | 7.5 | 4.7 | BMRL | 3.7 | 6 | BMRL | 2.7 | 4.2 | 15.9 | 21.9
Plant Name | Rolling Hills WTP | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Avg-A15 | Y | 1998-11-14 | 17:00 | 4842 | 14526 | 29052 | 7.46 | 0.89 | 69.5 | NA | 81 | 69 | 0.1 | 71 | 4.1 | 0.073 | 1.7805 | 4 | 0.76 | 3.24 | 18.4 | 8.14 | 24 | 267.5 | 68 | 22.5 | 8.05 | BMRL | 98.55 | 2.5 | 20.5 | 16.5 | BMRL | 1.75 | 8.3 | BMRL | BMRL | 6 | 41.25 | 49.55 | A15 | N | 1998-08-31 | 10:00 | 3035 | 18210 | 7.92 | 0.46 | 26.6 | BMRL | 2.2 | 0.038 | 1.7273 | 2.5 | 0.48 | 2.02 | 21.8 | 7.83 | 24 | 150 | 25 | 24 | 20 | 4.1 | 73.1 | BMRL | 8 | 5.7 | 1.1 | 4.3 | 7.1 | BMRL | 3.5 | 6 | 19.1 | 26.2 | Avg-A15 | Y | 1998-11-14 | 17:00 | 4842 | 14526 | 7.09 | 0.35 | 21.3 | BMRL | 2.25 | 0.038 | 1.6889 | 2 | 0.63 | 1.37 | 18.6 | 8.07 | 24 | NR | 22 | 16 | 12 | 1.7 | 51.7 | BMRL | 7.15 | 4.65 | BMRL | 3.05 | 5.8 | BMRL | 2 | 3.5 | 14.85 | 20.65
Treatment Plant Category | CONV |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run.
Process Train Name | Conventional Train | 10-Minute EBCT Run
ICR Treatment Plant Identification Number | 646 | Empty bed contact time, EBCT (min) | 10
PWSID Number of Plant (if assigned) | TX2200012960920162238 | Estimated run time, t (days) | 57.0078
Historical Minimum Water Temperature (oC) | 5 | Pilot column bed length, l (m) | 0.87712
Historical Average Water Temperature (oC) | NA | Mass GAC required, m (kg) | 2.0228
State Approved Plant Capacity (MGD) | 160
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 114.0155
|  | Pilot column bed length, l (m) | 1.7542 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 4.0456 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A1 | Primary | 1998-04-15 | 17:00 | 26 | 78 | 156 | 7.66 | 1.76 | 95 | 22.4 | 113 | 102 | BMRL | 50 | 3.1 | 0.141 | 4.5484 | 3 | 0.03 | 2.97 | 19.4 | 8.38 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | A1 | Primary | 1998-04-15 | 17:00 | 26 | 156 | 8.2 | 0.31 | 22.4 | BMRL | BMRL | 0 | -- | 1 | 0.63 | 0.37 | 19.2 | 8.23 | 24 | 46 | 7.9 | 5 | 4.4 | BMRL | 17.3 | BMRL | 4.9 | 2.7 | BMRL | 1.5 | 2.3 | BMRL | BMRL | 1.6 | 9.1 | 11.4 | A1 | Primary | 1998-04-15 | 17:00 | 26 | 78 | 8.5 | 0.23 | 23.2 | BMRL | BMRL | 0 | -- | 1 | 0.68 | 0.32 | 19.2 | 7.96 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1 | 1
[9 empty] | D-A1 | Duplicate | 1998-04-15 | 17:00 | 26 | 78 | 156 | 7.66 | 1.76 | 95 | 22.4 | 101 | 92 | BMRL | 50 | 3.2 | 0.141 | 4.4062 | 3 | 0.03 | 2.97 | 19.4 | 8.1 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | D-A1 | Duplicate | 1998-04-15 | 17:00 | 26 | 156 | 8.2 | 0.31 | 22.4 | BMRL | BMRL | 0 | -- | 1 | 0.63 | 0.37 | 19.2 | 8.23 | 24 | BMRL | 1 | 1.2 | 1.9 | 1.3 | 5.4 | BMRL | BMRL | 1.1 | BMRL | 1 | BMRL | BMRL | BMRL | NR | 2.1 | 2.1 | D-A1 | Duplicate | 1998-04-15 | 17:00 | 26 | 78 | 8.5 | 0.23 | 23.2 | BMRL | BMRL | 0 | -- | 1 | 0.68 | 0.32 | 19.2 | 7.96 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | NR | 1 | 1
[9 empty] | Avg-A1 | Average | --- | --- | --- | --- | --- | 7.66 | 1.76 | 95 | 22.4 | 107 | 97 | BMRL | 50 | 3.15 | 0.141 | 4.4773 | 3 | 0.03 | 2.97 | 19.4 | 8.24 | 24 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | Avg-A1 | Average | --- | --- | --- | --- | 8.2 | 0.31 | 22.4 | BMRL | BMRL | 0 | -- | 1 | 0.63 | 0.37 | 19.2 | 8.23 | 24 | 46 | 4.45 | 3.1 | 3.15 | 1.3 | 11.35 | BMRL | 4.9 | 1.9 | BMRL | 1.25 | 2.3 | BMRL | BMRL | 1.6 | 5.6 | 6.75 | Avg-A1 | Average | --- | --- | --- | --- | 8.5 | 0.23 | 23.2 | BMRL | BMRL | 0 | -- | 1 | 0.68 | 0.32 | 19.2 | 7.96 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 1 | 1
[9 empty] | RPD-A1 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 11.215 | 10.3093 | -- | 0 | 3.1746 | 0 | 3.1746 | 0 | 0 | 0 | 0 | 3.3981 | 0 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | RPD-A1 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | -- | 155.0562 | 122.5806 | 79.3651 | -- | 104.8458 | -- | -- | 84.2105 | -- | 40 | -- | -- | -- | -- | 125 | 137.7778 | RPD-A1 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | -- | -- | -- | 0 | 0 | 0 | 0 | 0 | 0 | -- | -- | -- | -- | -- | -- | -- | -- | 0 | -- | -- | -- | -- | -- | -- | 0 | 0
[9 empty] | A7 | Primary | 1998-06-13 | 16:30 | 1361.5 | 4084.5 | 8169 | 7.52 | 0.21 | 71 | 26.3 | 98 | 85 | 0.09 | 52 | 3 | 0.066 | 2.2 | 2 | 0.96 | 1.04 | 23.9 | 7.64 | 24 | 200 | 48 | 21 | 8.2 | BMRL | 77.2 | BMRL | 14 | 9.8 | BMRL | 1.8 | 6.9 | BMRL | BMRL | 5.3 | 25.6 | 32.5 | A7 | Primary | 1998-05-15 | 15:00 | 664 | 3984 | 7.31 | 0.32 | 24 | 0.06 | 1.9 | 0.04 | 2.1053 | 1.5 | 0.54 | 0.96 | 22.5 | 7.9 | 24 | 115 | 29 | 21 | 13 | 1.4 | 64.4 | BMRL | 8.8 | 5.6 | BMRL | 2.9 | 6.5 | BMRL | 2 | 4.5 | 17.3 | 23.8 | A7 | Primary | 1998-06-13 | 16:30 | 1361.5 | 4084.5 | 7.32 | 0.13 | 25.7 | BMRL | 1.4 | 0.034 | 2.4286 | 1 | 0.96 | 0.04 | 24.1 | 7.66 | 24 | 76 | 12 | 12 | 11 | 1.8 | 36.8 | BMRL | 4.6 | 3.3 | BMRL | 3 | 5.2 | BMRL | 2.7 | 4.3 | 10.9 | 16.1
[9 empty] | D-A7 | Duplicate | 1998-06-13 | 16:30 | 1361.5 | 4084.5 | 8169 | 7.52 | 0.21 | 72 | 26.3 | 98 | 85 | BMRL | 51 | 3.3 | 0.066 | 2 | 2 | 0.96 | 1.04 | 23.9 | 7.64 | 24 | 192 | 47 | 21 | 8.1 | BMRL | 76.1 | BMRL | 14 | 9.8 | BMRL | 1.8 | 6.8 | BMRL | BMRL | 5.2 | 25.6 | 32.4 | D-A7 | Duplicate | 1998-05-15 | 15:00 | 664 | 3984 | 7.31 | 0.32 | 24 | BMRL | 2 | 0.04 | 2 | 1.5 | 0.54 | 0.96 | 22.5 | 7.9 | 24 | 115 | 21 | 16 | 10 | 1.1 | 48.1 | BMRL | 8.6 | 5.9 | BMRL | 2.8 | 8.6 | BMRL | 2.2 | 4.7 | 17.3 | 25.9 | D-A7 | Duplicate | 1998-06-13 | 16:30 | 1361.5 | 4084.5 | 7.32 | 0.13 | 25.7 | BMRL | 1.5 | 0.034 | 2.2667 | 1 | 0.2 | 0.8 | 24.1 | 7.62 | 24 | 64 | 8.5 | 11 | 11 | 2.8 | 33.3 | BMRL | 3.3 | 1.8 | BMRL | 3.5 | 6.9 | BMRL | BMRL | 5.3 | 8.6 | 15.5
[9 empty] | Avg-A7 | Average | --- | --- | --- | --- | --- | 7.52 | 0.21 | 71.5 | 26.3 | 98 | 85 | 0.09 | 51.5 | 3.15 | 0.066 | 2.1 | 2 | 0.96 | 1.04 | 23.9 | 7.64 | 24 | 196 | 47.5 | 21 | 8.15 | BMRL | 76.65 | BMRL | 14 | 9.8 | BMRL | 1.8 | 6.85 | BMRL | BMRL | 5.25 | 25.6 | 32.45 | Avg-A7 | Average | --- | --- | --- | --- | 7.31 | 0.32 | 24 | 0.06 | 1.95 | 0.04 | 2.0526 | 1.5 | 0.54 | 0.96 | 22.5 | 7.9 | 24 | 115 | 25 | 18.5 | 11.5 | 1.25 | 56.25 | BMRL | 8.7 | 5.75 | BMRL | 2.85 | 7.55 | BMRL | 2.1 | 4.6 | 17.3 | 24.85 | Avg-A7 | Average | --- | --- | --- | --- | 7.32 | 0.13 | 25.7 | BMRL | 1.45 | 0.034 | 2.3476 | 1 | 0.58 | 0.42 | 24.1 | 7.64 | 24 | 70 | 10.25 | 11.5 | 11 | 2.3 | 35.05 | BMRL | 3.95 | 2.55 | BMRL | 3.25 | 6.05 | BMRL | 2.7 | 4.8 | 9.75 | 15.8
[9 empty] | RPD-A7 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 1.3986 | 0 | 0 | 0 | -- | 1.9417 | 9.5238 | 0 | 9.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0816 | 2.1053 | 0 | 1.227 | -- | 1.4351 | -- | 0 | 0 | -- | 0 | 1.4599 | -- | -- | 1.9048 | 0 | 0.30817 | RPD-A7 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | 5.1282 | 0 | 5.1282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 27.027 | 26.087 | 24 | 28.9778 | -- | 2.2989 | 5.2174 | -- | 3.5088 | 27.8146 | -- | 9.5238 | 4.3478 | 0 | 8.4507 | RPD-A7 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | -- | 6.8966 | 0 | 6.8966 | 0 | 131.0345 | 180.9524 | 0 | 0.52356 | 0 | 17.1429 | 34.1463 | 8.6957 | 0 | 43.4783 | 9.9857 | -- | 32.9114 | 58.8235 | -- | 15.3846 | 28.0992 | -- | -- | 20.8333 | 23.5897 | 3.7975
[9 empty] | A15 | Primary | 1998-11-14 | 17:00 | 4842 | 14526 | 29052 | 7.49 | 0.9 | 70 | -- | 81 | 69 | BMRL | 72 | 3.9 | 0.072 | 1.8462 | 4 | 0.83 | 3.17 | 18.3 | 8.13 | 24 | 270 | 70 | 23 | 8.2 | BMRL | 101.2 | BMRL | 21 | 18 | BMRL | 1.8 | 8.5 | BMRL | BMRL | 6.2 | 40.8 | 49.3 |  | Primary | [34 empty] | A15 | Primary | 1998-11-14 | 17:00 | 4842 | 14526 | 7.08 | 0.32 | 21 | BMRL | 2.2 | 0.04 | 1.8182 | 2 | 0.59 | 1.41 | 18.7 | 7.96 | 24 | NR | 22 | 16 | 12 | 1.7 | 51.7 | BMRL | 6.9 | 4.7 | BMRL | 3 | 5.7 | BMRL | BMRL | 3.5 | 14.6 | 20.3
[9 empty] | D-A15 | Duplicate | 1998-11-14 | 17:00 | 4842 | 14526 | 29052 | 7.42 | 0.88 | 69 | -- | 81 | 69 | 0.1 | 70 | 4.3 | 0.074 | 1.7209 | 4 | 0.69 | 3.31 | 18.4 | 8.14 | 24 | 265 | 66 | 22 | 7.9 | BMRL | 95.9 | 2.5 | 20 | 15 | BMRL | 1.7 | 8.1 | BMRL | BMRL | 5.8 | 39.2 | 47.3 | -- | Duplicate | [34 empty] | D-A15 | Duplicate | 1998-11-14 | 17:00 | 4842 | 14526 | 7.09 | 0.38 | 21.6 | BMRL | 2.3 | 0.036 | 1.5652 | 2 | 0.66 | 1.34 | 18.4 | 8.18 | 24 | NR | 22 | 16 | 12 | 1.7 | 51.7 | BMRL | 7.4 | 4.6 | BMRL | 3.1 | 5.9 | BMRL | 2 | 3.5 | 15.1 | 21
[9 empty] | Avg-A15 | Average | --- | --- | --- | --- | --- | 7.455 | 0.89 | 69.5 | -- | 81 | 69 | 0.1 | 71 | 4.1 | 0.073 | 1.7835 | 4 | 0.76 | 3.24 | 18.35 | 8.135 | 24 | 267.5 | 68 | 22.5 | 8.05 | BMRL | 98.55 | 2.5 | 20.5 | 16.5 | BMRL | 1.75 | 8.3 | BMRL | BMRL | 6 | 40 | 48.3 | -- | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | BMRL | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | BMRL | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | BMRL | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Avg-A15 | Average | --- | --- | --- | --- | 7.085 | 0.35 | 21.3 | BMRL | 2.25 | 0.038 | 1.6917 | 2 | 0.625 | 1.375 | 18.55 | 8.07 | 24 | #DIV/0! | 22 | 16 | 12 | 1.7 | 51.7 | BMRL | 7.15 | 4.65 | BMRL | 3.05 | 5.8 | BMRL | 2 | 3.5 | 14.85 | 20.65
[9 empty] | RPD-A15 | RPD | --- | --- | --- | --- | --- | 0.93897 | 2.2472 | 1.4388 | -- | 0 | 0 | -- | 2.8169 | 9.7561 | 2.7397 | 7.0211 | 0 | 18.4211 | 4.321 | 0.54496 | 0.12293 | 0 | 1.8692 | 5.8824 | 4.4444 | 3.7267 | -- | 5.378 | -- | 4.878 | 18.1818 | -- | 5.7143 | 4.8193 | -- | -- | 6.6667 | 4 | 4.1408 | -- | RPD | --- | --- | --- | --- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | RPD-A15 | RPD | --- | --- | --- | --- | 0.14114 | 17.1429 | 2.8169 | -- | 4.4444 | 10.5263 | 14.9533 | 0 | 11.2 | 5.0909 | 1.6173 | 2.7261 | 0 | #VALUE! | 0 | 0 | 0 | 0 | 0 | -- | 6.993 | 2.1505 | -- | 3.2787 | 3.4483 | -- | -- | 0 | 3.367 | 3.3898
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on U45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on U49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on V45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on V49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on X45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on X49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AB5: Reviewer M.H. (11/13/99): Per Consultant: "The spike in bromide and the brominated DBP species is likely the result of a change in raw water blend at the plant. Lake Benbrook water was treated at the plant from late August to mid-September. This water is higher in bromide than the two reservoirs."
Note on AG5: Reviewer M.H. (11/13/99): Responding to the reviewer's comment requesting an explanation about the high rate of Cl2 residuals below 0.1 mg/L, consultant wrote: "The appropriate chlorine dose to target the chlorine residual for the SDS tests was determined by utilizing a portion of the influent/effluent samples to prepare a calibration curve. A possible explaination for the difference in chlorine demand could stem from the differences in incubation temperatures during the calibration process or during preparation of the actual samples."
Note on AG45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AG49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AI45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AI49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AJ45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AJ49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AK5: Reviewer M.H. (11/13/99): Per Consultant: "The incubation time was the measured time."
Note on AK45: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AK49: Reviewer M.H. (11/13/99): Per Consultant: "The initial temperature, pH, and turbidity values were taken from a collective sample. Two readings were not obtained. Therefore, the RPD was zero. For the SDS chlorination results, a check of the daily operator data indicates that these results were obtained from two distinct samples."
Note on AL15: Reviewer M.H. (11/13/99): Per Consultant: "A possible explanation for the drop in influent DBPs at the start of the tests is a change in the raw water blend at the plant."
Note on AQ15: Reviewer M.H. (11/13/99): Per Consultant: "A possible explanation for the drop in influent DBPs at the start of the tests is a change in the raw water blend at the plant."
Note on BA15: Reviewer M.H. (11/13/99): Per Consultant: "A possible explanation for the drop in influent DBPs at the start of the tests is a change in the raw water blend at the plant."
Note on BB15: Reviewer M.H. (11/13/99): Per Consultant: "A possible explanation for the drop in influent DBPs at the start of the tests is a change in the raw water blend at the plant."
Note on BD50: Reviewer M.H. (11/13/99): Per Consultant: "The 10-minute EBCT column was shut off after reaching breakthrough criteria. The 3rd duplicate was inadvertently not obtained before shutdown."
Note on BM5: Reviewer M.H. (11/13/99): Per Consultant: "The MRL for ammonia is 0.05mg/L. Most of the detected results range from 0.06mg/L to 0.09mg/L with the exception of sample A11 from the 10-minute column. The reason for the spike is unknown. There is no additional TOC data to verify the spike. The remainder of the data for the sample does not indicate a change in raw water blend. The ammonia result for sample A11 was considered an outlier and changed to 'NR'."
Note on BR5: Reviewer M.H. (11/13/99): Responding to the reviewer's comment requesting an explanation about the high rate of Cl2 residuals below 0.1 mg/L, consultant wrote: "The appropriate chlorine dose to target the chlorine residual for the SDS tests was determined by utilizing a portion of the influent/effluent samples to prepare a calibration curve. A possible explaination for the difference in chlorine demand could stem from the differences in incubation temperatures during the calibration process or during preparation of the actual samples."
Note on BV5: Reviewer M.H. (11/13/99): Per Consultant: "The incubation time was the measured time."
Note on CB45: Reviewer M.H. (11/13/99): Per Consultant: "The DBP results were verified. The reason for the high RPDs is not known. Data with RPDs >=40% were changed to 'NR'."
Note on CB49: Reviewer M.H. (11/13/99): Per Consultant: "The DBP results were verified. The reason for the high RPDs is not known. Data with RPDs >=40% were changed to 'NR'."
Note on CL45: Reviewer M.H. (11/13/99): Per Consultant: "The DBP results were verified. The reason for the high RPDs is not known. Data with RPDs >=40% were changed to 'NR'."
Note on CM45: Reviewer M.H. (11/13/99): Per Consultant: "The DBP results were verified. The reason for the high RPDs is not known. Data with RPDs >=40% were changed to 'NR'."
Note on DC5: Reviewer M.H. (11/13/99): Responding to the reviewer's comment requesting an explanation about the high rate of Cl2 residuals below 0.1 mg/L, consultant wrote: "The appropriate chlorine dose to target the chlorine residual for the SDS tests was determined by utilizing a portion of the influent/effluent samples to prepare a calibration curve. A possible explaination for the difference in chlorine demand could stem from the differences in incubation temperatures during the calibration process or during preparation of the actual samples."
Note on DG5: Reviewer M.H. (11/13/99): Per Consultant: "The incubation time was the measured time."
Note on DK5: Reviewer M.H. (11/13/99): Per Consultant: "The spike in bromide and the brominated DBP species is likely the result of a change in raw water blend at the plant. Lake Benbrook water was treated at the plant from late August to mid-September. This water is higher in bromide than the two reservoirs."
Note on DR5: Reviewer M.H. (11/13/99): Per Consultant: "The spike in bromide and the brominated DBP species is likely the result of a change in raw water blend at the plant. Lake Benbrook water was treated at the plant from late August to mid-September. This water is higher in bromide than the two reservoirs."