## FldSys. Additional Data
Field 1-6: Membrane Performance Data During Operation With The Test Water | [17 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water | [8 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water
Date | Time | Operation time | Conductivity (mS/cm) |  |  | TDS (mg/L) |  |  | Date | Time | Operation time | Conductivity (mS/cm) | [5 empty] | Date | Time | Operation time | Conductivity (mS/cm) | [5 empty] | Date | Time | Operation time | Conductivity (mS/cm)
MM/DD/YY | hh:mm | hh.hh | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC | MM/DD/YY | hh:mm | hh.hh | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC | MM/DD/YY | hh:mm | hh.hh | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC | MM/DD/YY | hh:mm | hh.hh | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC
1998-05-03 | 18:00 | 0 | 0.604 | 0.728 | 1.038 | 332.2 | 400.4 | 570.9 | 1998-07-27 | 11:00 | 0 | NR | NR | NR | NR | NR | NR | 1998-12-17 | 15:00 | 0 | 0.29 | 0.824 | 2.13 | 159.5 | 453.2 | 1171.5 | 1999-02-09 | 12:00 | 0 | 0.251 | 0.793 | 1.921 | 138.05 | 436.15 | 1056.55
1998-05-04 | 0:45 | 6.75 | 0.181 | 0.728 | 2.17 | 99.55 | 400.4 | 1193.5 | 1998-07-27 | 18:00 | 7 | 0.193 | 0.772 | 2.09 | 106.15 | 424.6 | 1149.5 | 1998-12-17 | 21:00 | 6 | 0.238 | 0.823 | 2.18 | 130.9 | 452.65 | 1199 | 1999-02-09 | 18:00 | 6 | 0.318 | 0.777 | 2.02 | 174.9 | 427.35 | 1111
1998-05-04 | 9:00 | 15 | NR | NR | NR | NR | NR | NR | 1998-07-28 | 3:45 | 16.75 | NR | NR | NR | NR | NR | NR | 1998-12-18 | 3:00 | 12 | 0.238 | 0.84 | 2.17 | 130.9 | 462 | 1193.5 | 1999-02-10 | 0:00 | 12 | 0.326 | 0.775 | 2.09 | 179.3 | 426.25 | 1149.5
1998-05-04 | 17:00 | 23 | 0.184 | 0.737 | 1.834 | 101.2 | 405.35 | 1008.7 | 1998-07-30 | 18:00 | 79 | 0.247 | 0.882 | 2.05 | 135.85 | 485.1 | 1127.5 | 1998-12-18 | 9:30 | 18.5 | 0.373 | 0.809 | 3.5 | 205.15 | 444.95 | 1925 | 1999-02-10 | 9:00 | 21 | 0.26 | 0.78 | 1.921 | 143 | 429 | 1056.55
1998-05-05 | 2:00 | 32 | 0.244 | 0.729 | 1.812 | 134.2 | 400.95 | 996.6 | 1998-07-31 | 6:00 | 91 | NR | NR | NR | NR | NR | NR | 1998-12-18 | 15:00 | 24 | 0.245 | 0.861 | 2.17 | 134.75 | 473.55 | 1193.5 | 1999-02-10 | 18:00 | 30 | 0.352 | 0.781 | 1.923 | 193.6 | 429.55 | 1057.65
1998-05-05 | 9:00 | 39 | 0.24 | 0.664 | 1.576 | 132 | 365.2 | 866.8 | 1998-07-31 | 9:30 | 94.5 | 0.308 | 1.082 | 2.73 | 169.4 | 595.1 | 1501.5 | 1998-12-18 | 21:00 | 30 | 0.213 | 0.801 | 2.03 | 117.15 | 440.55 | 1116.5 | 1999-02-11 | 1:00 | 37 | 0.297 | 0.772 | 1.77 | 163.35 | 424.6 | 973.5
1998-05-05 | 18:00 | 48 | 0.209 | 0.77 | 1.852 | 114.95 | 423.5 | 1018.6 | 1998-07-31 | 20:00 | 105 | 0.232 | 0.897 | 2.48 | 127.6 | 493.35 | 1364 | 1998-12-19 | 3:00 | 36 | 0.235 | 0.836 | 2.18 | 129.25 | 459.8 | 1199 | 1999-02-11 | 9:00 | 45 | 0.295 | 0.781 | 1.945 | 162.25 | 429.55 | 1069.75
1998-05-06 | 1:30 | 55.5 | 0.198 | 0.767 | 1.731 | 108.9 | 421.85 | 952.05 | 1998-08-01 | 6:45 | 115.75 | 0.3 | 0.905 | 3.05 | 165 | 497.75 | 1677.5 | 1998-12-19 | 9:00 | 42 | 0.209 | 0.78 | 1.695 | 114.95 | 429 | 932.25 | 1999-02-11 | 18:00 | 54 | 0.313 | 0.8 | 1.896 | 172.15 | 440 | 1042.8
1998-05-06 | 9:00 | 63 | 0.238 | 0.868 | 1.745 | 130.9 | 477.4 | 959.75 | 1998-08-01 | 14:00 | 123 | 0.243 | 0.872 | 2.34 | 133.65 | 479.6 | 1287 | 1998-12-19 | 21:00 | 54 | 0.229 | 0.797 | 2.08 | 125.95 | 438.35 | 1144 | 1999-02-12 | 1:00 | 61 | 0.262 | 0.762 | 1.794 | 144.1 | 419.1 | 986.7
1998-05-06 | 9:20 | 63.3333 | NR | NR | NR | NR | NR | NR | 1998-08-01 | 20:15 | 129.25 | 0.28 | 0.902 | 2.41 | 154 | 496.1 | 1325.5 | 1998-12-20 | 3:00 | 60 | 0.217 | 0.803 | 1.998 | 119.35 | 441.65 | 1098.9 | 1999-02-12 | 13:00 | 73 | 0.29 | 0.808 | 1.758 | 159.5 | 444.4 | 966.9
1998-05-07 | 3:00 | 81 | NR | NR | NR | NR | NR | NR | 1998-08-02 | 5:00 | 138 | 0.245 | 0.875 | 2.34 | 134.75 | 481.25 | 1287 | 1998-12-20 | 8:40 | 65.6667 | 0.211 | 0.785 | 1.982 | 116.05 | 431.75 | 1090.1 | 1999-02-12 | 18:00 | 78 | 0.238 | 0.787 | 1.451 | 130.9 | 432.85 | 798.05
1998-05-18 | 13:30 | 87 | NR | NR | NR | NR | NR | NR | 1998-08-02 | 13:30 | 146.5 | 0.252 | 0.929 | 2.24 | 138.6 | 510.95 | 1232 | 1998-12-20 | 21:00 | 78 | 0.244 | 0.805 | 2.07 | 134.2 | 442.75 | 1138.5 | 1999-02-13 | 1:00 | 85 | 0.303 | 0.79 | 1.767 | 166.65 | 434.5 | 971.85
1998-05-18 | 18:00 | 91.5 | 0.292 | 0.749 | 2.23 | 160.6 | 411.95 | 1226.5 | 1998-08-02 | 18:00 | 151 | 0.253 | 0.913 | 2.22 | 139.15 | 502.15 | 1221 | 1998-12-21 | 3:00 | 84 | 0.222 | 0.801 | 2.08 | 122.1 | 440.55 | 1144 | 1999-02-13 | 13:00 | 97 | 0.279 | 0.789 | 1.796 | 153.45 | 433.95 | 987.8
1998-05-19 | 3:30 | 101 | 0.365 | 0.775 | 2.28 | 200.75 | 426.25 | 1254 | 1998-08-03 | 1:00 | 158 | 0.25 | 0.919 | 2.23 | 137.5 | 505.45 | 1226.5 | 1998-12-21 | 9:00 | 90 | 0.264 | 0.948 | 2.01 | 145.2 | 521.4 | 1105.5 | 1999-02-13 | 17:00 | 101 | 0.241 | 0.774 | 1.425 | 132.55 | 425.7 | 783.75
1998-05-19 | 9:00 | 106.5 | 0.302 | 0.775 | 2.23 | 166.1 | 426.25 | 1226.5 | 1998-08-03 | 9:00 | 166 | NR | NR | NR | NR | NR | NR | 1998-12-21 | 21:00 | 102 | 0.233 | 0.791 | 1.957 | 128.15 | 435.05 | 1076.35 | 1999-02-14 | 3:00 | 111 | 0.289 | 0.775 | 1.787 | 158.95 | 426.25 | 982.85
1998-05-19 | 18:00 | 115.5 | 0.305 | 0.737 | 2.3 | 167.75 | 405.35 | 1265 | 1998-08-03 | 18:00 | 175 | 0.287 | 0.923 | 2.41 | 157.85 | 507.65 | 1325.5 | 1998-12-22 | 1:00 | 106 | 0.25 | 0.802 | 1.967 | 137.5 | 441.1 | 1081.85 | 1999-02-14 | 14:15 | 122.25 | 0.2 | 0.766 | 1.327 | 110 | 421.3 | 729.85
1998-05-20 | 5:45 | 127.25 | 0.271 | 0.757 | 2.3 | 149.05 | 416.35 | 1265 | 1998-08-04 | 6:15 | 187.25 | 0.217 | 0.925 | 2.18 | 119.35 | 508.75 | 1199 | 1998-12-22 | 11:00 | 116 | 0.244 | 0.795 | 1.884 | 134.2 | 437.25 | 1036.2 | 1999-02-14 | 18:00 | 126 | 0.292 | 0.778 | 1.828 | 160.6 | 427.9 | 1005.4
1998-05-20 | 3:00 | 124.5 | 0.331 | 0.807 | 2.34 | 182.05 | 443.85 | 1287 | 1998-08-04 | 9:00 | 190 | NR | NR | NR | NR | NR | NR | 1998-12-22 | 21:00 | 126 | 0.226 | 0.794 | 1.828 | 124.3 | 436.7 | 1005.4 | 1999-02-15 | 3:00 | 135 | 0.29 | 0.787 | 1.818 | 159.5 | 432.85 | 999.9
1998-05-21 | 11:00 | 156.5 | 0.43 | 0.83 | 1.75 | 236.5 | 456.5 | 962.5 | 1998-08-04 | 18:00 | 199 | 0.242 | 0.914 | 2.32 | 133.1 | 502.7 | 1276 | 1998-12-23 | 3:00 | 132 | 0.245 | 0.798 | 1.875 | 134.75 | 438.9 | 1031.25 | 1999-02-15 | 8:30 | 140.5 | 0.231 | 0.763 | 1.449 | 127.05 | 419.65 | 796.95
1998-05-21 | 18:00 | 163.5 | 0.251 | 0.743 | 2.18 | 138.05 | 408.65 | 1199 | 1998-08-05 | 6:00 | 211 | 0.17 | 0.91 | 2.16 | 93.5 | 500.5 | 1188 | 1998-12-23 | 8:30 | 137.5 | 0.22 | 0.787 | 1.849 | 121 | 432.85 | 1016.95 | 1999-02-15 | 18:00 | 150 | 0.302 | 0.782 | 1.843 | 166.1 | 430.1 | 1013.65
1998-05-22 | 3:00 | 172.5 | 0.248 | 0.75 | 2.2 | 136.4 | 412.5 | 1210 | 1998-08-05 | 9:00 | 214 | NR | NR | NR | NR | NR | NR | 1998-12-23 | 21:00 | 150 | 0.224 | 0.791 | 1.795 | 123.2 | 435.05 | 987.25 | 1999-02-16 | 3:00 | 159 | 0.293 | 0.78 | 1.824 | 161.15 | 429 | 1003.2
1998-05-22 | 9:00 | 178.5 | 0.395 | 0.835 | 2.13 | 217.25 | 459.25 | 1171.5 | 1998-08-05 | 18:00 | 223 | 0.268 | 0.903 | 2.29 | 147.4 | 496.65 | 1259.5 | 1998-12-24 | 3:00 | 156 | 0.243 | 0.804 | 1.882 | 133.65 | 442.2 | 1035.1 | 1999-02-16 | 9:00 | 165 | 0.285 | 0.912 | 1.653 | 156.75 | 501.6 | 909.15
1998-05-22 | 19:30 | 189 | 0.223 | 0.721 | 2.1 | 122.65 | 396.55 | 1155 | 1998-08-06 | 4:45 | 233.75 | 0.23 | 0.931 | 2.22 | 126.5 | 512.05 | 1221 | 1998-12-24 | 9:00 | 162 | 0.284 | 0.788 | 1.783 | 156.2 | 433.4 | 980.65 | 1999-02-16 | 18:00 | 174 | 0.308 | 0.78 | 1.842 | 169.4 | 429 | 1013.1
1998-05-23 | 1:30 | 195 | 0.226 | 0.769 | 1.99 | 124.3 | 422.95 | 1094.5 | 1998-08-06 | 10:00 | 239 | 0.203 | 0.923 | 2.02 | 111.65 | 507.65 | 1111 | 1998-12-24 | 18:00 | 171 | 0.253 | 0.782 | 1.943 | 139.15 | 430.1 | 1068.65 | 1999-02-17 | 5:00 | 185 | 0.295 | 0.778 | 1.819 | 162.25 | 427.9 | 1000.45
1998-05-23 | 11:45 | 205.25 | 0.23 | 0.698 | 2.12 | 126.5 | 383.9 | 1166 | 1998-08-06 | 18:00 | 247 | 0.251 | 0.89 | 2.25 | 138.05 | 489.5 | 1237.5 | 1998-12-25 | 5:00 | 182 | 0.256 | 0.787 | 1.961 | 140.8 | 432.85 | 1078.55 | 1999-02-17 | 10:00 | 190 | 0.287 | 0.73 | 1.776 | 157.85 | 401.5 | 976.8
1998-05-23 | 21:00 | 214.5 | 0.228 | 0.712 | 2 | 125.4 | 391.6 | 1100 | 1998-08-07 | 6:00 | 259 | NR | NR | NR | NR | NR | NR | 1998-12-25 | 9:00 | 186 | 0.243 | 0.804 | 1.943 | 133.65 | 442.2 | 1068.65 | 1999-02-17 | 18:00 | 198 | 0.301 | 0.774 | 1.81 | 165.55 | 425.7 | 995.5
1998-05-24 | 4:00 | 221.5 | 0.231 | 0.707 | 2.11 | 127.05 | 388.85 | 1160.5 | 1998-08-07 | 9:00 | 262 | 0.286 | 1.046 | 2.2 | 157.3 | 575.3 | 1210 | 1998-12-25 | 21:00 | 198 | 0.224 | 0.795 | 1.863 | 123.2 | 437.25 | 1024.65 | 1999-02-18 | 3:00 | 207 | 0.301 | 0.782 | 1.804 | 165.55 | 430.1 | 992.2
1998-05-24 | 11:30 | 229 | 0.275 | 0.69 | 2.02 | 151.25 | 379.5 | 1111 | 1998-08-07 | 18:05 | 271.0833 | 0.199 | 0.902 | 2.03 | 109.45 | 496.1 | 1116.5 | 1998-12-26 | 3:00 | 204 | 0.238 | 0.799 | 1.958 | 130.9 | 439.45 | 1076.9 | 1999-02-18 | 9:00 | 213 | 0.29 | 0.83 | 1.605 | 159.5 | 456.5 | 882.75
1998-05-24 | 18:00 | 235.5 | 0.258 | 0.701 | 2.11 | 141.9 | 385.55 | 1160.5 | 1998-08-08 | 5:30 | 282.5 | 0.221 | 0.895 | 2.36 | 121.55 | 492.25 | 1298 | 1998-12-26 | 8:45 | 209.75 | 0.192 | 0.765 | 1.974 | 105.6 | 420.75 | 1085.7 | 1999-02-18 | 18:00 | 222 | 0.313 | 0.768 | 1.928 | 172.15 | 422.4 | 1060.4
1998-05-25 | 1:45 | 243.25 | 0.217 | 0.692 | 1.95 | 119.35 | 380.6 | 1072.5 | 1998-08-08 | 13:30 | 290.5 | 0.244 | 0.898 | 2.37 | 134.2 | 493.9 | 1303.5 | 1998-12-26 | 21:00 | 222 | 0.233 | 0.786 | 1.832 | 128.15 | 432.3 | 1007.6 | 1999-02-19 | 1:00 | 229 | 0.307 | 0.774 | 1.94 | 168.85 | 425.7 | 1067
1998-05-25 | 13:00 | 254.5 | 0.268 | 0.69 | 2.03 | 147.4 | 379.5 | 1116.5 | 1998-08-08 | 16:45 | 293.75 | 0.195 | 0.885 | 1.998 | 107.25 | 486.75 | 1098.9 | 1998-12-27 | 3:00 | 228 | 0.238 | 0.784 | 1.943 | 130.9 | 431.2 | 1068.65 | 1999-02-19 | 15:00 | 243 | 0.295 | 0.785 | 1.808 | 162.25 | 431.75 | 994.4
1998-05-25 | 18:00 | 259.5 | 0.255 | 0.703 | 2.04 | 140.25 | 386.65 | 1122 | 1998-08-09 | 1:00 | 302 | 0.232 | 0.896 | 2.38 | 127.6 | 492.8 | 1309 | 1998-12-27 | 10:00 | 235 | 0.189 | 0.787 | 1.874 | 103.95 | 432.85 | 1030.7 | 1999-02-19 | 16:45 | 244.75 | 0.221 | 0.779 | 1.444 | 121.55 | 428.45 | 794.2
1998-05-26 | 3:45 | 269.25 | 0.245 | 0.705 | 2.01 | 134.75 | 387.75 | 1105.5 | 1998-08-09 | 14:00 | 315 | 0.259 | 0.809 | 2.16 | 142.45 | 444.95 | 1188 | 1998-12-27 | 18:00 | 243 | 0.264 | 0.777 | 1.894 | 145.2 | 427.35 | 1041.7 | 1999-02-20 | 7:00 | 259 | 0.289 | 0.783 | 1.828 | 158.95 | 430.65 | 1005.4
1998-05-26 | 9:00 | 274.5 | 0.37 | 0.814 | 2.05 | 203.5 | 447.7 | 1127.5 | 1998-08-10 | 9:30 | 334.5 | NR | NR | NR | NR | NR | NR | 1998-12-28 | 3:00 | 252 | 0.264 | 0.781 | 1.896 | 145.2 | 429.55 | 1042.8 | 1999-02-20 | 14:45 | 266.75 | 0.225 | 0.769 | 1.478 | 123.75 | 422.95 | 812.9
1998-05-26 | 18:00 | 283.5 | 0.27 | 0.77 | 2.28 | 148.5 | 423.5 | 1254 | 1998-08-10 | 18:00 | 343 | 0.296 | 0.894 | 2.64 | 162.8 | 491.7 | 1452 | 1998-12-28 | 9:00 | 258 | 0.258 | 0.761 | 1.82 | 141.9 | 418.55 | 1001 | 1999-02-20 | 21:00 | 273 | 0.278 | 0.784 | 1.855 | 152.9 | 431.2 | 1020.25
1998-05-27 | 3:45 | 293.25 | 0.158 | 0.76 | 2.04 | 86.9 | 418 | 1122 | 1998-08-11 | 2:30 | 351.5 | 0.248 | 0.855 | 2.49 | 136.4 | 470.25 | 1369.5 | 1998-12-28 | 18:00 | 267 | 0.257 | 0.753 | 1.937 | 141.35 | 414.15 | 1065.35 | 1999-02-21 | 3:00 | 279 | 0.288 | 0.782 | 1.828 | 158.4 | 430.1 | 1005.4
1998-05-27 | 9:00 | 298.5 | 0.342 | 0.733 | 2.02 | 188.1 | 403.15 | 1111 | 1998-08-11 | 9:00 | 358 | 0.247 | 1 | 2.39 | 135.85 | 550 | 1314.5 | 1998-12-29 | 3:00 | 276 | 0.281 | 0.748 | 1.96 | 154.55 | 411.4 | 1078 | 1999-02-21 | 11:00 | 287 | 0.261 | 0.779 | 1.807 | 143.55 | 428.45 | 993.85
1998-05-27 | 18:00 | 307.5 | 0.288 | 0.818 | 2.4 | 158.4 | 449.9 | 1320 | 1998-08-11 | 18:00 | 367 | 0.218 | 0.836 | 1.824 | 119.9 | 459.8 | 1003.2 | 1998-12-29 | 11:00 | 284 | 0.243 | 0.703 | 1.785 | 133.65 | 386.65 | 981.75 | 1999-02-21 | 18:00 | 294 | 0.311 | 0.791 | 1.904 | 171.05 | 435.05 | 1047.2
1998-05-28 | 2:30 | 316 | 0.183 | 0.772 | 2.02 | 100.65 | 424.6 | 1111 | 1998-08-12 | 1:00 | 374 | 0.222 | 0.838 | 1.982 | 122.1 | 460.9 | 1090.1 | 1998-12-29 | 18:00 | 291 | 0.19 | 0.748 | 1.664 | 104.5 | 411.4 | 915.2 | 1999-02-22 | 3:00 | 303 | 0.287 | 0.783 | 1.876 | 157.85 | 430.65 | 1031.8
1998-05-28 | 9:00 | 322.5 | NR | NR | NR | NR | NR | NR | 1998-08-12 | 9:00 | 382 | NR | NR | NR | NR | NR | NR | 1998-12-30 | 5:00 | 302 | 0.26 | 0.76 | 2.02 | 143 | 418 | 1111 | 1999-02-22 | 9:00 | 309 | 0.284 | 0.765 | 1.882 | 156.2 | 420.75 | 1035.1
1998-05-28 | 18:00 | 331.5 | 0.251 | 0.88 | 2.38 | 138.05 | 484 | 1309 | 1998-08-12 | 19:30 | 392.5 | 0.285 | 0.856 | 2.49 | 156.75 | 470.8 | 1369.5 | 1998-12-30 | 11:00 | 308 | 0.258 | 0.68 | 1.774 | 141.9 | 374 | 975.7 | 1999-02-22 | 18:00 | 318 | 0.317 | 0.79 | 1.906 | 174.35 | 434.5 | 1048.3
1998-05-29 | 6:30 | 344 | 0.252 | 0.757 | 2.38 | 138.6 | 416.35 | 1309 | 1998-08-13 | 1:00 | 398 | 0.293 | 0.863 | 2.5 | 161.15 | 474.65 | 1375 | 1998-12-30 | 18:00 | 315 | 0.224 | 0.734 | 1.808 | 123.2 | 403.7 | 994.4 | 1999-02-23 | 1:00 | 325 | 0.307 | 0.801 | 1.919 | 168.85 | 440.55 | 1055.45
1998-05-29 | 9:45 | 347.25 | 0.19 | 0.709 | 2.18 | 104.5 | 389.95 | 1199 | 1998-08-13 | 13:00 | 410 | 0.407 | 1.031 | 2.81 | 223.85 | 567.05 | 1545.5 | 1998-12-31 | 3:00 | 324 | 0.223 | 0.741 | 1.807 | 122.65 | 407.55 | 993.85 | 1999-02-23 | 9:00 | 333 | 0.284 | 0.765 | 1.882 | 156.2 | 420.75 | 1035.1
1998-05-29 | 19:15 | 356.75 | 0.107 | 0.374 | 1.156 | 58.85 | 205.7 | 635.8 | 1998-08-13 | 18:00 | 415 | NR | NR | NR | NR | NR | NR | 1998-12-31 | 10:00 | 331 | 0.22 | 0.812 | 1.65 | 121 | 446.6 | 907.5 | 1999-02-23 | 18:00 | 342 | 0.302 | 0.772 | 1.848 | 166.1 | 424.6 | 1016.4
1998-05-30 | 6:00 | 367.5 | 0.234 | 0.745 | 2.28 | 128.7 | 409.75 | 1254 | 1998-08-14 | 2:30 | 423.5 | 0.248 | 0.898 | 2.11 | 136.4 | 493.9 | 1160.5 | 1998-12-31 | 18:00 | 339 | 0.235 | 0.754 | 1.928 | 129.25 | 414.7 | 1060.4 | 1999-02-24 | 8:00 | 356 | 0.282 | 0.777 | 1.84 | 155.1 | 427.35 | 1012
1998-05-30 | 13:00 | 374.5 | 0.215 | 0.766 | 2.18 | 118.25 | 421.3 | 1199 | 1998-08-14 | 9:00 | 430 | NR | NR | NR | NR | NR | NR | 1999-01-01 | 7:00 | 352 | 0.239 | 0.757 | 1.941 | 131.45 | 416.35 | 1067.55 | 1999-02-24 | 9:00 | 357 | 0.274 | 0.82 | 1.677 | 150.7 | 451 | 922.35
1998-05-30 | 19:30 | 381 | 0.192 | 0.736 | 2.19 | 105.6 | 404.8 | 1204.5 | 1998-08-14 | 18:00 | 439 | 0.24 | 0.862 | 2.36 | 132 | 474.1 | 1298 | 1999-01-01 | 13:00 | 358 | 0.227 | 0.799 | 1.852 | 124.85 | 439.45 | 1018.6 | 1999-02-24 | 18:00 | 366 | 0.279 | 0.743 | 1.81 | 153.45 | 408.65 | 995.5
1998-05-31 | 2:00 | 387.5 | 0.22 | 0.769 | 1.883 | 121 | 422.95 | 1035.65 | 1998-08-15 | 1:30 | 446.5 | 0.238 | 0.873 | 2.56 | 130.9 | 480.15 | 1408 | 1999-01-01 | 16:00 | 361 | 0.218 | 0.746 | 1.856 | 119.9 | 410.3 | 1020.8 | 1999-02-25 | 3:00 | 375 | 0.277 | 0.756 | 1.823 | 152.35 | 415.8 | 1002.65
1998-05-31 | 12:00 | 397.5 | 0.202 | 0.758 | 1.998 | 111.1 | 416.9 | 1098.9 | 1998-08-15 | 13:30 | 458.5 | 0.215 | 0.846 | 2.2 | 118.25 | 465.3 | 1210 | 1999-01-02 | 1:00 | 370 | 0.201 | 0.75 | 1.639 | 110.55 | 412.5 | 901.45 | 1999-02-25 | 9:00 | 381 | 0.276 | 0.713 | 1.798 | 151.8 | 392.15 | 988.9
1998-05-31 | 19:00 | 404.5 | 0.239 | 0.786 | 2.19 | 131.45 | 432.3 | 1204.5 | 1998-08-15 | 19:30 | 464.5 | 0.22 | 0.848 | 2.3 | 121 | 466.4 | 1265 | 1999-01-02 | 11:00 | 380 | 0.17 | 0.739 | 1.634 | 93.5 | 406.45 | 898.7 | 1999-02-25 | 18:00 | 390 | 0.29 | 0.762 | 1.848 | 159.5 | 419.1 | 1016.4
1998-06-01 | 1:00 | 410.5 | 0.199 | 0.803 | 1.956 | 109.45 | 441.65 | 1075.8 | 1998-08-16 | 2:30 | 471.5 | 0.228 | 0.862 | 2.42 | 125.4 | 474.1 | 1331 | 1999-01-02 | 17:30 | 386.5 | 0.218 | 0.741 | 1.689 | 119.9 | 407.55 | 928.95 | 1999-02-26 | 3:00 | 399 | 0.274 | 0.767 | 1.813 | 150.7 | 421.85 | 997.15
1998-06-01 | 9:00 | 418.5 | 0.272 | 0.679 | 2.12 | 149.6 | 373.45 | 1166 | 1998-08-16 | 9:00 | 478 | NR | NR | NR | NR | NR | NR | 1999-01-03 | 3:00 | 396 | 0.2 | 0.742 | 1.635 | 110 | 408.1 | 899.25 | 1999-02-26 | 13:00 | 409 | 0.262 | 0.775 | 1.806 | 144.1 | 426.25 | 993.3
1998-06-01 | 18:00 | 427.5 | 0.297 | 0.848 | 2.39 | 163.35 | 466.4 | 1314.5 | 1998-08-16 | 18:00 | 487 | 0.272 | 0.826 | 2.04 | 149.6 | 454.3 | 1122 | 1999-01-03 | 9:00 | 402 | 0.2 | 0.757 | 1.669 | 110 | 416.35 | 917.95 | 1999-02-26 | 21:00 | 417 | 0.272 | 0.768 | 1.811 | 149.6 | 422.4 | 996.05
1998-06-02 | 3:15 | 436.75 | NR | NR | NR | NR | NR | NR | 1998-08-17 | 2:30 | 495.5 | 0.217 | 0.844 | 2.23 | 119.35 | 464.2 | 1226.5 | 1999-01-03 | 18:00 | 411 | 0.281 | 0.796 | 1.983 | 154.55 | 437.8 | 1090.65 | 1999-02-27 | 1:00 | 421 | 0.273 | 0.774 | 1.809 | 150.15 | 425.7 | 994.95
1998-06-02 | 18:00 | 451.5 | 0.248 | 0.776 | 2.5 | 136.4 | 426.8 | 1375 | 1998-08-17 | 9:00 | 502 | NR | NR | NR | NR | NR | NR | 1999-01-04 | 3:00 | 420 | 0.28 | 0.801 | 1.985 | 154 | 440.55 | 1091.75 | 1999-02-27 | 13:00 | 433 | 0.263 | 0.769 | 1.803 | 144.65 | 422.95 | 991.65
1998-06-03 | 2:30 | 460 | NR | NR | NR | NR | NR | NR | 1998-08-17 | 21:00 | 514 | 0.218 | 0.804 | 2.4 | 119.9 | 442.2 | 1320 | 1999-01-04 | 10:30 | 427.5 | 0.259 | 0.778 | 1.895 | 142.45 | 427.9 | 1042.25 | 1999-02-27 | 18:15 | 438.25 | 0.207 | 0.751 | 1.504 | 113.85 | 413.05 | 827.2
1998-06-03 | 2:30 | 460 | NR | NR | NR | NR | NR | NR | 1998-08-18 | 4:45 | 521.75 | 0.226 | 0.808 | 2.35 | 124.3 | 444.4 | 1292.5 | 1999-01-04 | 18:00 | 435 | 0.225 | 0.78 | 1.946 | 123.75 | 429 | 1070.3 | 1999-02-28 | 3:00 | 447 | 0.274 | 0.722 | 1.628 | 150.7 | 397.1 | 895.4
1998-06-03 | 18:00 | 475.5 | 0.233 | 0.912 | 2.25 | 128.15 | 501.6 | 1237.5 | 1998-08-18 | 9:00 | 526 | 0.324 | 0.802 | 2.3 | 178.2 | 441.1 | 1265 | 1999-01-05 | 3:00 | 444 | 0.251 | 0.788 | 1.966 | 138.05 | 433.4 | 1081.3 | 1999-02-28 | 8:30 | 452.5 | 0.186 | 0.739 | 1.204 | 102.3 | 406.45 | 662.2
1998-06-04 | 6:30 | 488 | 0.245 | 0.755 | 2.49 | 134.75 | 415.25 | 1369.5 | 1998-08-18 | 18:00 | 535 | 0.235 | 0.814 | 2.4 | 129.25 | 447.7 | 1320 | 1999-01-05 | 13:00 | 454 | 0.233 | 0.818 | 1.961 | 128.15 | 449.9 | 1078.55 | 1999-02-28 | 18:00 | 462 | 0.3 | 0.755 | 1.954 | 165 | 415.25 | 1074.7
1998-06-04 | 9:00 | 490.5 | 0.222 | 0.754 | 2.35 | 122.1 | 414.7 | 1292.5 | 1998-08-19 | 4:00 | 545 | 0.245 | 0.812 | 2.35 | 134.75 | 446.6 | 1292.5 | 1999-01-05 | 18:00 | 459 | 0.257 | 0.82 | 1.976 | 141.35 | 451 | 1086.8 | 1999-03-01 | 3:00 | 471 | 0.287 | 0.821 | 1.885 | 157.85 | 451.55 | 1036.75
1998-06-04 | 18:00 | 499.5 | 0.25 | 0.83 | 2.36 | 137.5 | 456.5 | 1298 | 1998-08-19 | 9:00 | 550 | 0.375 | 0.799 | 2.24 | 206.25 | 439.45 | 1232 | 1999-01-06 | 1:00 | 466 | 0.266 | 0.82 | 2.02 | 146.3 | 451 | 1111 | 1999-03-01 | 9:00 | 477 | 0.276 | 0.833 | 1.7 | 151.8 | 458.15 | 935
1998-06-05 | 5:45 | 511.25 | 0.213 | 0.775 | 2.32 | 117.15 | 426.25 | 1276 | 1998-08-19 | 18:00 | 559 | 0.212 | 0.815 | 2.46 | 116.6 | 448.25 | 1353 | 1999-01-06 | 13:00 | 478 | 0.255 | 0.827 | 2.01 | 140.25 | 454.85 | 1105.5 | 1999-03-01 | 18:00 | 486 | 0.277 | 0.768 | 1.827 | 152.35 | 422.4 | 1004.85
1998-06-05 | 11:00 | 516.5 | NR | NR | NR | NR | NR | NR | 1998-08-20 | 6:00 | 571 | 0.226 | 0.811 | 2.3 | 124.3 | 446.05 | 1265 | 1999-01-06 | 18:00 | 483 | 0.29 | 0.822 | 2.05 | 159.5 | 452.1 | 1127.5 | 1999-03-02 | 1:00 | 493 | 0.272 | 0.774 | 1.808 | 149.6 | 425.7 | 994.4
1998-06-05 | 19:30 | 525 | 0.208 | 0.709 | 2.13 | 114.4 | 389.95 | 1171.5 | 1998-08-20 | 9:00 | 574 | 0.292 | 1.025 | 2.9 | 160.6 | 563.75 | 1595 | 1999-01-07 | 1:00 | 490 | 0.279 | 0.819 | 2.03 | 153.45 | 450.45 | 1116.5 | 1999-03-02 | 13:00 | 505 | 0.266 | 0.79 | 1.737 | 146.3 | 434.5 | 955.35
1998-06-06 | 6:45 | 536.25 | 0.206 | 0.721 | 2.13 | 113.3 | 396.55 | 1171.5 | 1998-08-20 | 18:00 | 583 | NR | NR | NR | NR | NR | NR | 1999-01-07 | 9:50 | 498.8333 | 0.187 | 0.769 | 1.856 | 102.85 | 422.95 | 1020.8 | 1999-03-02 | 18:00 | 510 | 0.285 | 0.771 | 1.784 | 156.75 | 424.05 | 981.2
1998-06-06 | 11:30 | 541 | 0.208 | 0.752 | 2.25 | 114.4 | 413.6 | 1237.5 | 1998-08-21 | 5:30 | 594.5 | NR | NR | NR | NR | NR | NR | 1999-01-07 | 18:00 | 507 | 0.254 | 0.795 | 1.927 | 139.7 | 437.25 | 1059.85 | 1999-03-03 | 3:00 | 519 | 0.272 | 0.779 | 1.737 | 149.6 | 428.45 | 955.35
1998-06-06 | 22:00 | 551.5 | 0.204 | 0.716 | 2.06 | 112.2 | 393.8 | 1133 | 1998-08-21 | 9:00 | 598 | 0.431 | 0.8 | 2.22 | 237.05 | 440 | 1221 | 1999-01-08 | 1:00 | 514 | 0.255 | 0.797 | 1.937 | 140.25 | 438.35 | 1065.35 | 1999-03-03 | 9:00 | 525 | 0.275 | 0.798 | 1.645 | 151.25 | 438.9 | 904.75
1998-06-07 | 7:00 | 560.5 | NR | NR | NR | NR | NR | NR | 1998-08-21 | 18:00 | 607 | 0.194 | 0.825 | 2.23 | 106.7 | 453.75 | 1226.5 | 1999-01-08 | 10:00 | 523 | 0.184 | 0.779 | 1.823 | 101.2 | 428.45 | 1002.65 | 1999-03-03 | 18:00 | 534 | 0.315 | 0.766 | 1.92 | 173.25 | 421.3 | 1056
1998-06-07 | 11:00 | 564.5 | NR | NR | NR | NR | NR | NR | 1998-08-22 | 6:45 | 619.75 | 0.179 | 0.833 | 2.07 | 98.45 | 458.15 | 1138.5 | 1999-01-08 | 17:30 | 530.5 | 0.265 | 0.753 | 1.824 | 145.75 | 414.15 | 1003.2 | 1999-03-04 | 3:00 | 543 | 0.283 | 0.763 | 1.878 | 155.65 | 419.65 | 1032.9
1998-06-07 | 18:00 | 571.5 | NR | NR | NR | NR | NR | NR | 1998-08-22 | 14:00 | 627 | 0.17 | 0.824 | 2.04 | 93.5 | 453.2 | 1122 | 1999-01-09 | 1:00 | 538 | 0.263 | 0.768 | 1.827 | 144.65 | 422.4 | 1004.85 | 1999-03-04 | 9:00 | 549 | 0.29 | 0.873 | 1.68 | 159.5 | 480.15 | 924
1998-06-08 | 0:25 | 577.9167 | NR | NR | NR | NR | NR | NR | 1998-08-22 | 20:30 | 633.5 | 0.196 | 0.848 | 2.3 | 107.8 | 466.4 | 1265 | 1999-01-09 | 13:00 | 550 | 0.205 | 0.763 | 1.459 | 112.75 | 419.65 | 802.45 | 1999-03-04 | 18:00 | 558 | 0.276 | 0.767 | 1.838 | 151.8 | 421.85 | 1010.9
1998-06-08 | 10:00 | 587.5 | 0.177 | 0.725 | 2.16 | 97.35 | 398.75 | 1188 | 1998-08-23 | 2:30 | 639.5 | 0.221 | 0.845 | 2.5 | 121.55 | 464.75 | 1375 | 1999-01-09 | 16:15 | 553.25 | 0.241 | 0.764 | 1.807 | 132.55 | 420.2 | 993.85 | 1999-03-05 | 3:00 | 567 | 0.318 | 0.784 | 2.02 | 174.9 | 431.2 | 1111
1998-06-08 | 18:00 | 595.5 | 0.227 | 0.778 | 2.3 | 124.85 | 427.9 | 1265 | 1998-08-23 | 13:45 | 650.75 | 0.206 | 0.852 | 2.14 | 113.3 | 468.6 | 1177 | 1999-01-10 | 3:00 | 564 | 0.238 | 0.763 | 1.812 | 130.9 | 419.65 | 996.6 | 1999-03-05 | 13:00 | 577 | 0.256 | 0.788 | 1.874 | 140.8 | 433.4 | 1030.7
1998-06-09 | 2:15 | 603.75 | 0.21 | 0.724 | 2.41 | 115.5 | 398.2 | 1325.5 | 1998-08-23 | 18:00 | 655 | 0.234 | 0.838 | 2.21 | 128.7 | 460.9 | 1215.5 | 1999-01-10 | 12:30 | 573.5 | 0.202 | 0.748 | 1.847 | 111.1 | 411.4 | 1015.85 | 1999-03-05 | 23:00 | 587 | 0.233 | 0.768 | 1.497 | 128.15 | 422.4 | 823.35
1998-06-09 | 9:10 | 610.6667 | 0.2 | 0.728 | 2.3 | 110 | 400.4 | 1265 | 1998-08-24 | 2:30 | 663.5 | 0.232 | 0.836 | 2.2 | 127.6 | 459.8 | 1210 | 1999-01-10 | 18:00 | 579 | 0.252 | 0.762 | 1.762 | 138.6 | 419.1 | 969.1 | 1999-03-06 | 3:00 | 591 | 0.274 | 0.774 | 1.832 | 150.7 | 425.7 | 1007.6
1998-06-09 | 18:00 | 619.5 | 0.25 | 0.781 | 2.28 | 137.5 | 429.55 | 1254 | 1998-08-24 | 9:00 | 670 | 0.192 | 0.85 | 2.16 | 105.6 | 467.5 | 1188 | 1999-01-11 | 3:00 | 588 | 0.248 | 0.76 | 1.746 | 136.4 | 418 | 960.3 | 1999-03-06 | 13:00 | 601 | 0.268 | 0.785 | 1.829 | 147.4 | 431.75 | 1005.95
1998-06-10 | 3:30 | 629 | 0.226 | 0.767 | 2.4 | 124.3 | 421.85 | 1320 | 1998-08-24 | 18:00 | 679 | 0.243 | 0.847 | 2.21 | 133.65 | 465.85 | 1215.5 | 1999-01-11 | 9:00 | 594 | 0.217 | 0.748 | 1.761 | 119.35 | 411.4 | 968.55 | 1999-03-06 | 16:45 | 604.75 | 0.194 | 0.774 | 1.32 | 106.7 | 425.7 | 726
1998-06-10 | 11:00 | 636.5 | 0.188 | 0.751 | 2.06 | 103.4 | 413.05 | 1133 | 1998-08-25 | 3:45 | 688.75 | 0.234 | 0.837 | 2.18 | 128.7 | 460.35 | 1199 | 1999-01-11 | 18:00 | 603 | 0.254 | 0.764 | 1.815 | 139.7 | 420.2 | 998.25 | 1999-03-07 | 1:00 | 613 | 0.27 | 0.772 | 1.806 | 148.5 | 424.6 | 993.3
1998-06-10 | 18:00 | 643.5 | 0.262 | 0.759 | 2.27 | 144.1 | 417.45 | 1248.5 | 1998-08-25 | 9:00 | 694 | 0.239 | 0.826 | 2.04 | 131.45 | 454.3 | 1122 | 1999-01-12 | 3:00 | 612 | 0.253 | 0.763 | 1.806 | 139.15 | 419.65 | 993.3 | 1999-03-07 | 9:00 | 621 | 0.195 | 0.763 | 1.367 | 107.25 | 419.65 | 751.85
1998-06-11 | 4:45 | 654.25 | 0.263 | 0.734 | 2.38 | 144.65 | 403.7 | 1309 | 1998-08-25 | 18:00 | 703 | 0.234 | 0.836 | 2.12 | 128.7 | 459.8 | 1166 | 1999-01-12 | 9:00 | 618 | 0.294 | 0.714 | 1.778 | 161.7 | 392.7 | 977.9 | 1999-03-07 | 18:00 | 630 | 0.285 | 0.78 | 1.784 | 156.75 | 429 | 981.2
[9 empty] | 1998-08-26 | 5:15 | 714.25 | 0.223 | 0.852 | 2.07 | 122.65 | 468.6 | 1138.5 | [9 empty] | 1999-03-08 | 3:00 | 639 | 0.276 | 0.771 | 1.756 | 151.8 | 424.05 | 965.8
[9 empty] | 1998-08-26 | 9:00 | 718 | NR | NR | NR | NR | NR | NR | [9 empty] | 1999-03-08 | 9:00 | 645 | 0.272 | 0.844 | 1.594 | 149.6 | 464.2 | 876.7
[9 empty] | 1998-08-26 | 18:00 | 727 | 0.173 | 0.83 | 2.04 | 95.15 | 456.5 | 1122
[9 empty] | 1998-08-27 | 3:30 | 736.5 | 0.208 | 0.847 | 2.33 | 114.4 | 465.85 | 1281.5
[9 empty] | 1998-08-27 | 9:00 | 742 | 0.277 | 0.813 | 2.29 | 152.35 | 447.15 | 1259.5
[9 empty] | 1998-08-27 | 18:00 | 751 | 0.236 | 0.858 | 2.39 | 129.8 | 471.9 | 1314.5
[9 empty] | 1998-08-28 | 6:30 | 763.5 | 0.246 | 0.86 | 2.31 | 135.3 | 473 | 1270.5
[9 empty] | 1998-08-28 | 15:00 | 772 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-08-28 | 15:30 | 772.5 | 0.318 | 0.95 | 1.694 | 174.9 | 522.5 | 931.7
[9 empty] | 1998-08-28 | 22:30 | 779.5 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-08-29 | 6:00 | 787 | 0.263 | 0.874 | 2.31 | 144.65 | 480.7 | 1270.5
[9 empty] | 1998-08-29 | 14:45 | 795.75 | 0.257 | 0.908 | 2.36 | 141.35 | 499.4 | 1298
[9 empty] | 1998-08-29 | 18:10 | 799.1667 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-08-30 | 2:30 | 807.5 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-08-30 | 15:30 | 820.5 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-08-30 | 18:00 | 823 | 0.264 | 0.861 | 2.28 | 145.2 | 473.55 | 1254
[9 empty] | 1998-08-31 | 3:00 | 832 | 0.202 | 0.868 | 1.864 | 111.1 | 477.4 | 1025.2
[9 empty] | 1998-08-31 | 9:00 | 838 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-08-31 | 18:00 | 847 | 0.252 | 0.878 | 2.34 | 138.6 | 482.9 | 1287
[9 empty] | 1998-09-01 | 4:45 | 857.75 | 0.249 | 0.882 | 2.31 | 136.95 | 485.1 | 1270.5
[9 empty] | 1998-09-01 | 9:00 | 862 | NR | NR | NR | NR | NR | NR
[9 empty] | 1998-09-01 | 18:00 | 871 | 0.265 | 0.904 | 2.6 | 145.75 | 497.2 | 1430
[9 empty] | 1998-09-02 | 6:30 | 883.5 | 0.272 | 0.905 | 2.54 | 149.6 | 497.75 | 1397
[9 empty] | 1998-09-02 | 11:45 | 888.75 | NR | NR | NR | NR | NR | NR
1998-05-01 | 16:00 | 862000
1998-05-02 | 0:30 | 862008.5
1998-05-02 | 9:00 | 862017
1998-05-02 | 16:30 | 862024.5
1998-05-03 | 2:00 | 862034
1998-05-03 | 9:30 | 862041.5
1998-05-03 | 18:00 | 862050
1998-05-04 | 0:45 | 862056.75
1998-05-04 | 9:00 | 862065
1998-05-04 | 17:00 | 862073
1998-05-05 | 2:00 | 862082
1998-05-05 | 9:00 | 862089
1998-05-05 | 18:00 | 862098
1998-05-06 | 1:30 | 862105.5
1998-05-06 | 9:00 | 862113
1998-05-06 | 9:20 | 862113.3333
1998-05-07 | 3:00 | 862131
1998-05-18 | 13:30 | 862405.5
1998-05-18 | 18:00 | 862410
1998-05-19 | 3:30 | 862419.5
1998-05-19 | 9:00 | 862425
1998-05-19 | 18:00 | 862434
1998-05-20 | 5:45 | 862445.75
1998-05-20 | 11:00 | 862451
1998-05-20 | 3:00 | 862443
1998-05-21 | 3:30 | 862467.5
1998-05-21 | 11:00 | 862475
1998-05-21 | 18:00 | 862482
1998-05-22 | 3:00 | 862491
1998-05-22 | 9:00 | 862497
1998-05-22 | 19:30 | 862507.5
1998-05-23 | 1:30 | 862513.5
1998-05-23 | 11:45 | 862523.75
1998-05-23 | 21:00 | 862533
1998-05-24 | 4:00 | 862540
1998-05-24 | 11:30 | 862547.5
1998-05-24 | 18:00 | 862554
1998-05-25 | 1:45 | 862561.75
1998-05-25 | 13:00 | 862573
1998-05-25 | 18:00 | 862578
1998-05-26 | 3:45 | 862587.75
1998-05-26 | 9:00 | 862593
1998-05-26 | 18:00 | 862602
1998-05-27 | 3:45 | 862611.75
1998-05-27 | 9:00 | 862617
1998-05-27 | 18:00 | 862626
1998-05-28 | 2:30 | 862634.5
1998-05-28 | 9:00 | 862641
1998-05-28 | 18:00 | 862650
1998-05-29 | 6:30 | 862662.5
1998-05-29 | 9:45 | 862665.75
1998-05-29 | 19:15 | 862675.25
1998-05-30 | 6:00 | 862686
1998-05-30 | 13:00 | 862693
1998-05-30 | 19:30 | 862699.5
1998-05-31 | 2:00 | 862706
1998-05-31 | 12:00 | 862716
1998-05-31 | 19:00 | 862723
1998-06-01 | 1:00 | 862729
1998-06-01 | 9:00 | 862737
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0

## FldSys. 1st Quarter
FIELD-SET 1: 1st QUARTER SEBST RESULTS (FILE: Fluid Sys.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: SEBST Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 1-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 1-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 1-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 1-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week NA | [9 empty] | Field 1-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [18 empty] | 0.7237 |  | 14.0873 | 12.1359 | [30 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH |  | TDS (mg/L) | [11 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.76 | [8 empty] | Recovery during sample collection (decimal) | 0.74 | [8 empty] | Recovery during sample collection (decimal) | NA | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL5360313 | Membrane trade name | Spiral-Wound Reverse Osmosis Element | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.25077 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.05 | [8 empty] | Feed flow rate during sample collection (gpm) | 0.95 | [8 empty] | Feed flow rate during sample collection (gpm) | NA | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | TFCS 4921S |  |  | LSI | 0.14 | Hydrochloric acid addition | pH = 6.7 | Pilot-scale | 1998-05-03 | 18:00 | 0 | 26.3 | 46 | 44 | 9 | 4.6 | 0.8 | 0.3 |  | 1.1 | 5.7 | 0.34519 | 0.72727 | 4.1818 | 14.7692 | 13.2001 | 2.3252 | 33.6748 | 0.39199 | 7.3 | 7.3 | 7.5 | 332.2 | 400.4 | 570.9 | 582.2667 | -1.991 | 17.033 | 564.7181 | 41.1742 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.35 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.35 | [8 empty] | Influent flow rate during sample collection (gpm) | NA | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.26 |  |  |  | 1998-05-04 | 0:45 | 6.75 | 26.9 | 60 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.968 | 10.2289 | 49.2711 | 0.2632 | 6.3 | 7 | 7.4 | 99.55 | 400.4 | 1193.5 | 1202.6667 | -0.76805 | 75.1374 | 1122.44 | 91.1309 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.35 |  |  |  | 1998-05-04 | 17:00 | 23 | 28.2 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.9193 | 9.4812 | 49.5188 | 0.22051 | 6.6 | 7.3 | 7.6 | 101.2 | 405.35 | 1008.7 | 1115.0333 | -10.5416 | 75.0339 | 1049.3219 | 90.3557 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 1998-05-05 | 2:00 | 32 | 24.5 | 62 | 61 | 0 | 4.4 | 0.6 | 0.3 |  | 0.9 | 5.3 | 0.32565 | 0.66667 | 4.8889 | 11.0769 | 10.4411 | 7.5495 | 53.9505 | 0.19353 | 6.8 | 7.3 | 7.6 | 134.2 | 400.95 | 996.6 | 934.45 | 6.2362 | 66.5295 | 889.1528 | 84.907 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophyllic | Permeate flow rate, Qp (gpm) | 0.8125 | Total aluminum (mg/L) | 0.11 |  |  |  | 1998-05-05 | 9:00 | 39 | 26.4 | 60 | 59 | 0 | 4.4 | 0.6 | 0.3 |  | 0.9 | 5.3 | 0.32565 | 0.66667 | 4.8889 | 11.0769 | 9.8708 | 6.6 | 52.9 | 0.18659 | 6.9 | 7.3 | 7.6 | 132 | 365.2 | 866.8 | 831.6 | 4.0609 | 63.8554 | 792 | 83.3333 | [16 empty] | Sampling date | MM/DD/YY | 1998-05-21 | 1998-05-21 | 1998-05-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-28 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-04 | 1998-06-04 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-11 | 1998-06-11 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | NA | NA | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.0833 | Fluoride (mg/L) | 0.41 |  |  |  | 1998-05-05 | 18:00 | 48 | 28.4 | 90 | 88 | 0 | 4.5 | 0.65 | 0.25 |  | 0.9 | 5.4 | 0.33053 | 0.72222 | 5 | 12 | 10.0796 | 10.4393 | 78.5607 | 0.1283 | 6.6 | 7.3 | 7.6 | 114.95 | 423.5 | 1018.6 | 1225.73 | -20.3348 | 72.8571 | 1158.8775 | 90.0809 | [16 empty] | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 4:45 | 4:45 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | NA | NA | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27083 | (Ortho) Phosphate (mg/L) | 0.098 |  |  |  | 1998-05-06 | 1:30 | 55.5 | 24.3 | 90 | 88 | 0 | 4.4 | 0.55 | 0.3 |  | 0.85 | 5.25 | 0.32402 | 0.64706 | 5.1765 | 10.1538 | 9.6277 | 8.4025 | 80.5975 | 0.11945 | 6.7 | 7.4 | 7.6 | 108.9 | 421.85 | 952.05 | 995.5917 | -4.5735 | 74.1851 | 949.1459 | 88.5265 | [16 empty] | Operation time | hh.hh | 156.5 | 156.5 | 156.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 322.5 | 322.5 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 490.5 | 490.5 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 654.3 | 654.3 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | NA | NA | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 31 |  |  |  | 1998-05-06 | 9:00 | 63 | 27.5 | 100 | 100 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 10.8014 | 89.1986 | 0.12497 | 6.4 | 7.3 | 7.4 | 130.9 | 477.4 | 959.75 | 1285.9 | -33.9828 | 72.5806 | 1211.0389 | 89.1911 | [16 empty] | pH | --- | NA | NA | NA | --- | --- | --- | --- | --- | pH | --- | 3.28 | 7.32 | NA | --- | --- | --- | --- | --- | pH | --- | 5.91 | 7.33 | NA | --- | --- | --- | --- | --- | pH | --- | 5.84 | 7.17 | NA | --- | --- | --- | --- | --- | pH | --- | NA | NA | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 10 | Calcium (mg/L) | 83 |  |  |  | 1998-05-18 | 18:00 | 91.5 | 28.2 | 56 | 54 | 0 | 4.4 | 0.75 | 0.3 | X | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.6992 | 8.1919 | 46.8081 | 0.24994 | 5.7 | 7.3 | 6.3 | 160.6 | 411.95 | 1226.5 | 1040.325 | 15.1794 | 61.0147 | 979.7935 | 83.6088 | [16 empty] | Temperature | oC | 27.2 | 27.2 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.2 | 27.2 | NA | --- | --- | --- | --- | --- | Temperature | oC | 28.5 | 28.5 | NA | --- | --- | --- | --- | --- | Temperature | oC | 26.2 | 26.2 | NA | --- | --- | --- | --- | --- | Temperature | oC | NA | NA | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.016 |  |  |  | 1998-05-19 | 3:30 | 101 | 26.4 | 57 | 56 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.3385 | 7.3494 | 49.1506 | 0.25104 | 5.3 | 7.3 | 5.4 | 200.75 | 426.25 | 1254 | 990 | 21.0526 | 52.9032 | 935.6938 | 78.5453 | [16 empty] | Total Alkalinity | mg/L as CaCO3 | 34 | 250 | 300 | 898 | -199.3333 | 86.4 | 833.2 | 95.9193 | Alkalinity | mg/L as CaCO3 | BMRL | 260 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 36 | 260 | NA | 969.3333 | #VALUE! | 86.1538 | 899.7259 | 95.9988 | Alkalinity | mg/L as CaCO3 | 26 | 240 | NA | 849.0769 | #VALUE! | 89.1667 | 795 | 96.7296 | Alkalinity | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Design recycle flow rate, QR (gpm) | 4.4167 | Strontium (mg/L) | 0.13 |  |  |  | 1998-05-19 | 9:00 | 106.5 | 27.4 | 58 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.9792 | 8.4787 | 49.5213 | 0.2419 | 5.7 | 7.3 | 6.3 | 166.1 | 426.25 | 1226.5 | 1076.625 | 12.2197 | 61.0323 | 1013.9742 | 83.6189 | [16 empty] | Total dissolved solids | mg/L | 120 | 440 | 1700 | 1400 | 17.6471 | 72.7273 | 1304 | 90.7975 | Total dissolved solids | mg/L | 180 | 490 | NA | 1328.1481 | #VALUE! | 63.2653 | 1244.3333 | 85.5344 | Total dissolved solids | mg/L | 100 | 460 | NA | 1600 | #VALUE! | 78.2609 | 1488.1308 | 93.2802 | Total dissolved solids | mg/L | 110 | 390 | NA | 1186.9231 | #VALUE! | 71.7949 | 1116.1682 | 90.1449 | Total dissolved solids | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Recycle ratio, r | 4.0769 | Reactive silica (mg/L as SiO2) | 34 |  |  |  | 1998-05-19 | 18:00 | 115.5 | 27.6 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1147 | 7.4067 | 46.5933 | 0.23855 | 5.5 | 7.3 | 5.7 | 167.75 | 405.35 | 1265 | 959.75 | 24.1304 | 58.616 | 908.4167 | 81.5338 | [16 empty] | Total hardness | mg/L as CaCO3 | 42 | 260 | 710 | 914 | -28.7324 | 83.8462 | 848.6 | 95.0507 | Total hardness | mg/L as CaCO3 | 31 | 270 | NA | 916.1852 | #VALUE! | 88.5185 | 851.5667 | 96.3597 | Total hardness | mg/L as CaCO3 | 33 | 270 | NA | 1020.5 | #VALUE! | 87.7778 | 946.8528 | 96.5148 | Total hardness | mg/L as CaCO3 | 39 | 260 | NA | 889 | #VALUE! | 85 | 833.1542 | 95.319 | Total hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | NR |  |  |  | 1998-05-20 | 5:45 | 127.25 | 25.6 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.7915 | 8.3325 | 47.6675 | 0.24737 | 5.2 | 7.2 | 5.1 | 149.05 | 416.35 | 1265 | 1040.05 | 17.7826 | 64.2008 | 982.3 | 84.8264 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 34 | 200 | 540 | 698 | -29.2593 | 83 | 648.2 | 94.7547 | Calcium hardness | mg/L as CaCO3 | 26 | 200 | NA | 670.4444 | #VALUE! | 87 | 623.4 | 95.8293 | Calcium hardness | mg/L as CaCO3 | 24 | 210 | NA | 799 | #VALUE! | 88.5714 | 741.2009 | 96.762 | Calcium hardness | mg/L as CaCO3 | 30 | 210 | NA | 722.3077 | #VALUE! | 85.7143 | 676.8224 | 95.5675 | Calcium hardness | mg/L as CaCO3 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 3.2 |  |  |  | 1998-05-20 | 3:00 | 124.5 | 28.4 | 55 | 54 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.6303 | 8.5325 | 45.9675 | 0.25301 | 5.2 | 7.3 | 4.7 | 182.05 | 443.85 | 1287 | 1098.35 | 14.6581 | 58.9839 | 1035.3018 | 82.4158 | [16 empty] | Turbidity | ntu | BMRL | 13 | 23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.1 | 12 | NA | 44.1741 | #VALUE! | 99.1667 | 40.9567 | 99.7558 | Turbidity | ntu | BMRL | 1.3 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.4 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 1998-05-21 | 11:00 | 156.5 | 26.5 | 60 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.1223 | 7.48 | 52.02 | 0.25225 | 6 | 7.2 | 7.4 | 236.5 | 456.5 | 962.5 | 1043.1667 | -8.381 | 48.1928 | 984.5 | 75.9777 | [16 empty] | Nitrogen - Ammonia | mg NH3-N / L | 0.39 | 0.62 | 1 | 1.31 | -31 | 37.0968 | 1.241 | 68.5737 | Ammonia | mg NH3-N / L | 0.41 | 0.56 | NA | 0.96556 | #VALUE! | 26.7857 | 0.925 | 55.6757 | Ammonia | mg NH3-N / L | 0.3 | 0.5 | NA | 1.1333 | #VALUE! | 40 | 1.0712 | 71.9936 | Ammonia | mg NH3-N / L | 0.21 | 0.39 | NA | 0.90231 | #VALUE! | 46.1538 | 0.85682 | 75.4908 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-05-21 | 18:00 | 163.5 | 29 | 58 | 57 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.1875 | 9.2004 | 48.2996 | 0.25233 | 5.8 | 7.3 | 6.6 | 138.05 | 408.65 | 1199 | 1130.25 | 5.7339 | 66.218 | 1058.09 | 86.9529 | [16 empty] | Total organic carbon | mg/L | 0.70 | 5.9 | 18 | 21.5 | -19.4444 | 88.1356 | 19.94 | 96.4895 | Total organic carbon | mg/L | 0.7 | 5.5 | NA | 18.4778 | #VALUE! | 87.2727 | 17.18 | 95.9255 | Total organic carbon | mg/L | BMRL | 5.4 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.7 | 5.4 | NA | 18.7769 | #VALUE! | 87.037 | 17.5893 | 96.0203 | Total organic carbon | mg/L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 12.67 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-05-22 | 3:00 | 172.5 | 26.5 | 56 | 55 | 0 | 4.4 | 0.82 | 0.3 |  | 1.12 | 5.52 | 0.33281 | 0.73214 | 3.9286 | 15.1385 | 13.4503 | 9.5421 | 45.9579 | 0.29267 | 5.9 | 7.3 | 6.4 | 136.4 | 412.5 | 1210 | 1167.1733 | 3.5394 | 66.9333 | 1090.6123 | 87.4933 | [16 empty] | UV254 | cm-1 | 0.01 | 0.23 | 0.66 | 0.89 | -34.8485 | 95.6522 | 0.824 | 98.7864 | UV254 | cm-1 | 0.009 | 0.2 | NA | 0.71641 | #VALUE! | 95.5 | 0.66477 | 98.6461 | UV254 | cm-1 | BMRL | 0.22 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.016 | 0.26 | NA | 0.95446 | #VALUE! | 93.8462 | 0.8928 | 98.2079 | UV254 | cm-1 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0027 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-05-22 | 9:00 | 178.5 | 26.5 | 59 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.1223 | 8.228 | 51.272 | 0.25593 | 5.6 | 7 | 6.4 | 217.25 | 459.25 | 1171.5 | 1104.5833 | 5.7121 | 52.6946 | 1040.05 | 79.1116 | [16 empty] | SUVA | L/(mg*m) | 1.4286 | 3.8983 | 3.6667 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.2857 | 3.6364 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.0741 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.2857 | 4.8148 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NA | NA | NA | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 1998-05-22 | 19:30 | 189 | 27.9 | 59 | 57 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.5903 | 9.3126 | 48.6874 | 0.2586 | 5.5 | 7 | 6.3 | 122.65 | 396.55 | 1155 | 1126.95 | 2.4286 | 69.0707 | 1053.91 | 88.3624 | [16 empty] | Bromide | mg/L | NR | NR | 0.52 | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 120 | 370 | NA | 1045.9259 | --- | 67.5676 | 978.3333 | 87.7342 | Bromide | mg/L | 66 | 460 | NA | 1707.6667 | --- | 85.6522 | 1585.2321 | 95.8366 | Bromide | mg/L | 56 | 200 | NA | 609.8462 | --- | 72 | 573.4579 | 90.2347 | Bromide | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 1998-05-23 | 1:30 | 195 | 26.9 | 60 | 58 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.31751 | 0.71429 | 4 | 13.8462 | 12.1575 | 9.7061 | 49.2939 | 0.24663 | 5.6 | 7.2 | 6.3 | 124.3 | 422.95 | 1094.5 | 1169.575 | -6.8593 | 70.6112 | 1094.9125 | 88.6475 | [16 empty] | SDS-Cl2 dose | mg/L | NA | NA | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 11 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 10 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 8.3 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | NA | NA | NA | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1152.638 | [5 empty] | 1998-05-23 | 11:45 | 205.25 | 27.9 | 60 | 58 | 0 | 4.3 | 0.77 | 0.3 |  | 1.07 | 5.37 | 0.32467 | 0.71963 | 4.0187 | 14.2154 | 12.1182 | 8.5224 | 50.4776 | 0.24007 | 5.5 | 7 | 6.2 | 126.5 | 383.9 | 1166 | 1044.56 | 10.4151 | 67.0487 | 978.7401 | 87.0752 | [16 empty] | SDS-Free Cl2 residual | mg/L | NA | NA | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.2 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.1 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | NA | NA | NA | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 202.454 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-05-23 | 21:00 | 214.5 | 26.7 | 60 | 58 | 0 | 4.2 | 0.76 | 0.3 |  | 1.06 | 5.26 | 0.31783 | 0.71698 | 3.9623 | 14.0308 | 12.3927 | 8.7262 | 50.2738 | 0.2465 | 5.6 | 7 | 6.3 | 125.4 | 391.6 | 1100 | 1065.9733 | 3.0933 | 67.9775 | 998.0232 | 87.4352 | [16 empty] | SDS-Cl2 demand | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 9.8 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 8.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 7.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | 1 | Influent TDS, TDSI (mg/L) | 1012.2699 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-05-24 | 4:00 | 221.5 | 26.2 | 60 | 58 | 0 | 4.3 | 0.75 | 0.3 |  | 1.05 | 5.35 | 0.32402 | 0.71429 | 4.0952 | 13.8462 | 12.4117 | 8.5207 | 50.4793 | 0.24588 | 5.4 | 7 | 6.2 | 127.05 | 388.85 | 1160.5 | 1043.35 | 10.0948 | 67.3267 | 979.1234 | 87.0241 | [16 empty] | SDS-Chlorination temp. | oC | NA | NA | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | NA | NA | NA | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 1998-05-24 | 11:30 | 229 | 28.5 | 58 | 57 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.369 | 7.7605 | 49.7395 | 0.24868 | 5.6 | 7.2 | 6.3 | 151.25 | 379.5 | 1111 | 988.1667 | 11.0561 | 60.1449 | 927.3 | 83.6892 | [16 empty] | SDS-Chlorination pH | --- | NA | NA | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.87 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.01 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | NA | NA | NA | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 10 | [7 empty] | 1998-05-24 | 18:00 | 235.5 | 28.1 | 55 | 53 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.31751 | 0.71429 | 4 | 13.8462 | 11.7339 | 7.9186 | 46.0814 | 0.25463 | 5.5 | 7.3 | 6.3 | 141.9 | 385.55 | 1160.5 | 994.675 | 14.2891 | 63.1954 | 933.7625 | 84.8034 | [16 empty] | SDS-Incubation time | hours | NA | NA | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | NA | NA | NA | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 1998-05-25 | 1:45 | 243.25 | 26.9 | 55 | 53 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.1575 | 8.5146 | 45.4854 | 0.26728 | 5.4 | 7 | 6.2 | 119.35 | 380.6 | 1072.5 | 1033.725 | 3.6154 | 68.6416 | 970.8093 | 87.7061 | [16 empty] | SDS-TOX | mg Cl- /L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 100 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 42 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 36 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | NaCl 500 mg/L | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 1998-05-25 | 13:00 | 254.5 | 28.5 | 55 | 53 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.5959 | 7.5645 | 46.4355 | 0.24972 | 5.5 | 7 | 6.3 | 147.4 | 379.5 | 1116.5 | 959.75 | 14.0394 | 61.1594 | 903.8544 | 83.6921 | [16 empty] | SDS-CHCl3 | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 4.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 3.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) | 85 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-05-25 | 18:00 | 259.5 | 28.5 | 54 | 52 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.31751 | 0.71429 | 4 | 13.8462 | 11.5959 | 8.008 | 44.992 | 0.25773 | 5.7 | 7.3 | 6.4 | 140.25 | 386.65 | 1122 | 1002.65 | 10.6373 | 63.7269 | 941.05 | 85.0964 | [16 empty] | SDS-BDCM | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 7.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 4.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | +/-15.0 | Required influent pressure, PI (psi) | 70.6164 | [5 empty] | 1998-05-26 | 3:45 | 269.25 | 27.1 | 52 | 51 | 0 | 4 | 0.675 | 0.3 |  | 0.975 | 4.975 | 0.30204 | 0.69231 | 4.1026 | 12.4615 | 10.8773 | 7.6647 | 43.8353 | 0.24814 | 5.5 | 7.2 | 6.2 | 134.75 | 387.75 | 1105.5 | 957 | 13.4328 | 65.2482 | 901.2192 | 85.048 | [16 empty] | SDS-DBCM | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 8.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 2.8 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 6.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [7 empty] | 1998-05-26 | 9:00 | 274.5 | 26.4 | 50 | 50 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.31751 | 0.71429 | 4 | 13.8462 | 12.3385 | 7.9365 | 42.0635 | 0.29333 | 5.5 | 7 | 5.9 | 203.5 | 447.7 | 1127.5 | 1058.2 | 6.1463 | 54.5455 | 997.15 | 79.5918 | [16 empty] | SDS-CHBr3 | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 0.79 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 1.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7.5 | [7 empty] | 1998-05-26 | 18:00 | 283.5 | 27.8 | 63 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.6276 | 9.35 | 52.65 | 0.23984 | 5.5 | 7.2 | 6.1 | 148.5 | 423.5 | 1254 | 1156.8333 | 7.7485 | 64.9351 | 1083.5 | 86.2944 | [16 empty] | SDS-THM4 | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 20.99 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 7.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 15 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0-350 | [7 empty] | 1998-05-27 | 3:45 | 293.25 | 27.1 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.8916 | 11.2574 | 51.7426 | 0.24915 | 6.3 | 7.2 | 7.5 | 86.9 | 418 | 1122 | 1300.9333 | -15.9477 | 79.2105 | 1212.64 | 92.8338 | [16 empty] | SDS-MCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 1998-05-27 | 9:00 | 298.5 | 27.8 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.6276 | 7.3117 | 55.6883 | 0.22675 | 6.3 | 7 | 7.4 | 188.1 | 403.15 | 1111 | 976.6167 | 12.0957 | 53.3424 | 919.27 | 79.5381 | [16 empty] | SDS-DCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 1.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 3 | [7 empty] | 1998-05-27 | 18:00 | 307.5 | 28.1 | 60 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.7339 | 9.5005 | 49.4995 | 0.23705 | 5.4 | 7.3 | 5.7 | 158.4 | 449.9 | 1320 | 1178.65 | 10.7083 | 64.7922 | 1108.4493 | 85.7098 | [16 empty] | SDS-TCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-05-28 | 2:30 | 316 | 27.5 | 61 | 59 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.9438 | 10.5581 | 49.4419 | 0.24157 | 6.3 | 7.3 | 7.6 | 100.65 | 424.6 | 1111 | 1234.475 | -11.1139 | 76.2953 | 1156.4595 | 91.2967 | [16 empty] | SDS-MBAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 0 | [7 empty] | 1998-05-28 | 18:00 | 331.5 | 27.8 | 64 | 62 | 0 | 4.4 | 0.75 | 0.25 |  | 1 | 5.4 | 0.32727 | 0.75 | 4.4 | 13.8462 | 11.8384 | 12.877 | 50.123 | 0.23619 | 6.1 | 7.4 | 7.1 | 138.05 | 484 | 1309 | 1521.85 | -16.2605 | 71.4773 | 1425.7528 | 90.3174 | [16 empty] | SDS-DBAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 1998-05-29 | 6:30 | 344 | 26.4 | 64 | 62 | 0 | 4.4 | 0.75 | 0.25 |  | 1 | 5.4 | 0.32727 | 0.75 | 4.4 | 13.8462 | 12.3385 | 10.3385 | 52.6615 | 0.2343 | 6 | 7.3 | 7 | 138.6 | 416.35 | 1309 | 1249.6 | 4.5378 | 66.7107 | 1172.4472 | 88.1786 | [16 empty] | SDS-BCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-05-29 | 9:45 | 347.25 | 28 | 64 | 63 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.5532 | 9.7053 | 53.7947 | 0.23335 | 5.9 | 7.1 | 6.9 | 104.5 | 389.95 | 1199 | 1151.15 | 3.9908 | 73.2017 | 1075.03 | 90.2793 | [16 empty] | SDS-TBAA | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-05-29 | 19:15 | 356.75 | 27.6 | 65 | 63.5 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7025 | 4.9929 | 59.2571 | 0.21436 | 5.7 | 7.1 | 6.8 | 58.85 | 205.7 | 635.8 | 597.3 | 6.0554 | 71.3904 | 558.14 | 89.4561 | [16 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-05-30 | 6:00 | 367.5 | 26.9 | 65 | 63 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.968 | 9.5557 | 54.4443 | 0.23819 | 5.8 | 7.3 | 6.9 | 128.7 | 409.75 | 1254 | 1159.2167 | 7.5585 | 68.5906 | 1084.27 | 88.1303 | [16 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-05-30 | 13:00 | 374.5 | 27.6 | 64 | 62 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.32565 | 0.72727 | 3.9091 | 14.7692 | 12.7025 | 10.2887 | 52.7113 | 0.24098 | 5.7 | 7 | 6.7 | 118.25 | 421.3 | 1199 | 1229.4333 | -2.5382 | 71.9321 | 1147.1235 | 89.6916 | [16 empty] | SDS-HAA5 | mg/L | NA | NA | N/A | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 2.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-05-30 | 19:30 | 381 | 27.6 | 63.5 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7025 | 10.1728 | 52.5772 | 0.2416 | 5.8 | 7.1 | 6.7 | 105.6 | 404.8 | 1204.5 | 1202.6667 | 0.15221 | 73.913 | 1122.88 | 90.5956 | [16 empty] | SDS-HAA6 | mg/L | NA | NA | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 3.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-05-31 | 2:00 | 387.5 | 26.9 | 63.5 | 62 | 0 | 4.2 | 0.77 | 0.3 |  | 1.07 | 5.27 | 0.31816 | 0.71963 | 3.9252 | 14.2154 | 12.4817 | 9.9828 | 52.7672 | 0.23654 | 5.6 | 7 | 6.7 | 121 | 422.95 | 1035.65 | 1197.955 | -15.6718 | 71.3914 | 1119.278 | 89.1895 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 1998-05-31 | 12:00 | 397.5 | 27.3 | 63.5 | 62 | 0 | 4.3 | 0.78 | 0.3 |  | 1.08 | 5.38 | 0.325 | 0.72222 | 3.9815 | 14.4 | 12.4952 | 10.2108 | 52.5392 | 0.23783 | 5.7 | 7.1 | 6.7 | 111.1 | 416.9 | 1098.9 | 1211.98 | -10.2903 | 73.3509 | 1132.1764 | 90.187 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 1998-05-31 | 19:00 | 404.5 | 27.3 | 59 | 58 | 0 | 4 | 0.75 | 0.3 |  | 1.05 | 5.05 | 0.30448 | 0.71429 | 3.8095 | 13.8462 | 12.0146 | 9.7478 | 48.7522 | 0.24644 | 5.8 | 7.3 | 6.7 | 131.45 | 432.3 | 1204.5 | 1184.425 | 1.6667 | 69.5929 | 1106.2338 | 88.1173
[11 empty] | 1998-06-01 | 1:00 | 410.5 | 26.8 | 58 | 56.5 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.0064 | 11.2948 | 45.9552 | 0.28302 | 5.6 | 7 | 6.6 | 109.45 | 441.65 | 1075.8 | 1327.5167 | -23.3981 | 75.2179 | 1238.93 | 91.1658 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 1998-06-01 | 9:00 | 418.5 | 28.3 | 62 | 58 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.4423 | 7.6109 | 52.3891 | 0.2375 | 5.7 | 7.1 | 6.6 | 149.6 | 373.45 | 1166 | 970.3833 | 16.7767 | 59.9411 | 910.69 | 83.5729 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 1998-06-01 | 18:00 | 427.5 | 28.5 | 56 | 55 | 0 | 4.2 | 0.7 | 0.2 |  | 0.9 | 5.1 | 0.30936 | 0.77778 | 4.6667 | 12.9231 | 10.8229 | 12.7014 | 42.7986 | 0.25288 | 5.9 | 7.4 | 6.7 | 163.35 | 466.4 | 1314.5 | 1527.075 | -16.1715 | 64.9764 | 1433.486 | 88.6047 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 1998-06-02 | 18:00 | 451.5 | 29.2 | 68 | 66 | 0 | 4.4 | 0.8 | 0.25 |  | 1.05 | 5.45 | 0.3289 | 0.7619 | 4.1905 | 14.7692 | 12.1157 | 11.3016 | 55.6984 | 0.21752 | 5.9 | 7.3 | 6.8 | 136.4 | 426.8 | 1375 | 1356.08 | 1.376 | 68.0412 | 1266.5622 | 89.2307 | [16 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
[11 empty] | 1998-06-03 | 18:00 | 475.5 | 28.7 | 67 | 65 | 0 | 4.2 | 0.85 | 0.3 |  | 1.15 | 5.35 | 0.32076 | 0.73913 | 3.6522 | 15.6923 | 13.0646 | 13.1784 | 52.8216 | 0.24733 | 5.9 | 7.3 | 6.8 | 128.15 | 501.6 | 1237.5 | 1559.7083 | -26.037 | 74.4518 | 1445.9864 | 91.1375 | [16 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-06-04 | 6:30 | 488 | 26.8 | 69 | 67 | 0 | 4.4 | 0.8 | 0.25 |  | 1.05 | 5.45 | 0.3289 | 0.7619 | 4.1905 | 14.7692 | 13.0064 | 10.9163 | 57.0837 | 0.22785 | 5.8 | 7.3 | 6.8 | 134.75 | 415.25 | 1369.5 | 1312.85 | 4.1365 | 67.5497 | 1226.3839 | 89.0124 | [16 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-06-04 | 9:00 | 490.5 | 28.5 | 68 | 67 | 0 | 4.3 | 0.8 | 0.25 |  | 1.05 | 5.35 | 0.32239 | 0.7619 | 4.0952 | 14.7692 | 12.369 | 11.3704 | 56.1296 | 0.22036 | 5.9 | 7.2 | 6.7 | 122.1 | 414.7 | 1292.5 | 1351.02 | -4.5277 | 70.557 | 1259.1381 | 90.3029 | [16 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
[11 empty] | 1998-06-04 | 18:00 | 499.5 | 28.2 | 65 | 63 | 0 | 4.2 | 0.8 | 0.3 |  | 1.1 | 5.3 | 0.31913 | 0.72727 | 3.8182 | 14.7692 | 12.4792 | 10.8139 | 53.1861 | 0.23463 | 5.8 | 7.3 | 6.8 | 137.5 | 456.5 | 1298 | 1307.1667 | -0.70621 | 69.8795 | 1218.8899 | 88.7192 | [16 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-06-05 | 5:45 | 511.25 | 27.4 | 64 | 62 | 0 | 4 | 0.75 | 0.3 |  | 1.05 | 5.05 | 0.30448 | 0.71429 | 3.8095 | 13.8462 | 11.9792 | 10.0151 | 52.9849 | 0.22609 | 5.9 | 7.3 | 6.8 | 117.15 | 426.25 | 1276 | 1199 | 6.0345 | 72.5161 | 1118.6646 | 89.5277 | [16 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-06-05 | 19:30 | 525 | 28.8 | 63 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.2598 | 9.3687 | 52.6313 | 0.23294 | 5.7 | 7.1 | 6.6 | 114.4 | 389.95 | 1171.5 | 1124.75 | 3.9906 | 70.6629 | 1051.27 | 89.1179 | [16 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[11 empty] | 1998-06-06 | 6:45 | 536.25 | 27.9 | 60 | 58 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.31751 | 0.71429 | 4 | 13.8462 | 11.8034 | 9.2056 | 49.7944 | 0.23704 | 5.8 | 7.3 | 6.7 | 113.3 | 396.55 | 1171.5 | 1104.675 | 5.7042 | 71.4286 | 1033.8625 | 89.0411 | [16 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-06-06 | 11:30 | 541 | 29.2 | 58 | 56 | 0 | 4.4 | 0.8 | 0.28 |  | 1.08 | 5.48 | 0.33086 | 0.74074 | 4.0741 | 14.7692 | 12.1157 | 10.6982 | 46.3018 | 0.26167 | 5.8 | 7.2 | 6.6 | 114.4 | 413.6 | 1237.5 | 1268.4571 | -2.5016 | 72.3404 | 1184.2194 | 90.3396 | [16 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 1998-06-06 | 22:00 | 551.5 | 27.9 | 63 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.5903 | 9.5744 | 52.4256 | 0.24016 | 5.6 | 7.1 | 6.5 | 112.2 | 393.8 | 1133 | 1144.7333 | -1.0356 | 71.5084 | 1069.64 | 89.5105 | [16 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 1998-06-08 | 10:00 | 587.5 | 28.2 | 73 | 72 | 0 | 4.2 | 0.85 | 0.3 |  | 1.15 | 5.35 | 0.32076 | 0.73913 | 3.6522 | 15.6923 | 13.2591 | 10.6359 | 61.8641 | 0.21433 | 5.8 | 7 | 6.9 | 97.35 | 398.75 | 1188 | 1252.7167 | -5.4475 | 75.5862 | 1160.9352 | 91.6145 | [16 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 1998-06-08 | 18:00 | 595.5 | 27.9 | 68 | 65 | 0 | 4.5 | 0.85 | 0.3 |  | 1.15 | 5.65 | 0.3403 | 0.73913 | 3.913 | 15.6923 | 13.3772 | 10.7431 | 55.7569 | 0.23992 | 5.7 | 7.3 | 6.6 | 124.85 | 427.9 | 1265 | 1286.5417 | -1.7029 | 70.8226 | 1199.1578 | 89.5885 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 1998-06-09 | 2:15 | 603.75 | 27.6 | 68 | 66 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7025 | 9.6118 | 57.3882 | 0.22134 | 5.6 | 7.2 | 6.5 | 115.5 | 398.2 | 1325.5 | 1152.0667 | 13.0844 | 70.9945 | 1076.68 | 89.2726 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 1998-06-09 | 9:10 | 610.6667 | 28.4 | 69 | 67 | 0 | 4.4 | 0.8 | 0.24 |  | 1.04 | 5.44 | 0.32825 | 0.76923 | 4.2308 | 14.7692 | 12.4056 | 11.6587 | 56.3413 | 0.22019 | 5.7 | 7.2 | 6.5 | 110 | 400.4 | 1265 | 1368.4 | -8.1739 | 72.5275 | 1275.8706 | 91.3784 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1998-06-09 | 18:00 | 619.5 | 28.5 | 65 | 63 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.369 | 9.9297 | 54.0703 | 0.22876 | 5.7 | 7.3 | 6.5 | 137.5 | 429.55 | 1254 | 1208.35 | 3.6404 | 67.9898 | 1130.47 | 87.8369 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1998-06-10 | 3:30 | 629 | 27.5 | 66 | 64 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7401 | 10.1167 | 54.8833 | 0.23213 | 5.5 | 7.2 | 6.5 | 124.3 | 421.85 | 1320 | 1215.3167 | 7.9306 | 70.5346 | 1135.97 | 89.0578 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1998-06-10 | 11:00 | 636.5 | 28.7 | 66 | 63 | 0 | 4.3 | 0.8 | 0.25 |  | 1.05 | 5.35 | 0.32239 | 0.7619 | 4.0952 | 14.7692 | 12.2961 | 12.0329 | 52.4671 | 0.23436 | 5.6 | 7.2 | 6.5 | 103.4 | 413.05 | 1133 | 1403.93 | -23.9126 | 74.9667 | 1306.6941 | 92.0869 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1998-06-10 | 18:00 | 643.5 | 29 | 59 | 57 | 0 | 4.4 | 0.7 | 0.25 |  | 0.95 | 5.35 | 0.32565 | 0.73684 | 4.6316 | 12.9231 | 10.6641 | 9.7078 | 48.2922 | 0.22082 | 5.5 | 7.3 | 6.4 | 144.1 | 417.45 | 1248.5 | 1182.83 | 5.2599 | 65.4809 | 1114.8757 | 87.0748 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1998-06-11 | 4:45 | 654.25 | 26.2 | 57 | 55 | 0 | 4.4 | 0.7 | 0.25 | X | 0.95 | 5.35 | 0.32565 | 0.73684 | 4.6316 | 12.9231 | 11.5843 | 9.1999 | 46.8001 | 0.24753 | 5.5 | 7.3 | 6.3 | 144.65 | 403.7 | 1309 | 1129.04 | 13.7479 | 64.1689 | 1064.6407 | 86.4133 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[59 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[31 empty] | 0.11945 | [27 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[31 empty] | 0.39199 | [27 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
0.23811
0.39199
0.24753
[11 empty] | 1998-05-01 | 16:00 | 862000 | 27.9 | 58 | 55 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-02 | 0:30 | 862008.5 | 25.3 | 54 | 52 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-02 | 9:00 | 862017 | 26 | 50 | 48 | 10 | 4.3 | 0.7 | 0.25
[11 empty] | 1998-05-02 | 16:30 | 862024.5 | 29.2 | 48 | 47 | 8 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-03 | 2:00 | 862034 | 26.2 | 50 | 48 | 9.5 | 4.6 | 0.8 | 0.3
[11 empty] | 1998-05-03 | 9:30 | 862041.5 | 26.4 | 52 | 48 | 9 | 4.6 | 0.8 | 0.3
[11 empty] | 1998-05-03 | 18:00 | 862050 | 26.3 | 46 | 44 | 9 | 4.6 | 0.8 | 0.3
[11 empty] | 1998-05-04 | 0:45 | 862056.75 | 26.9 | 60 | 59 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-04 | 9:00 | 862065 | 25.6 | 62 | 61 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-04 | 17:00 | 862073 | 28.2 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3
[11 empty] | 1998-05-05 | 2:00 | 862082 | 24.5 | 62 | 61 | 0 | 4.4 | 0.6 | 0.3
[11 empty] | 1998-05-05 | 9:00 | 862089 | 26.4 | 60 | 59 | 0 | 4.4 | 0.6 | 0.3
[11 empty] | 1998-05-05 | 18:00 | 862098 | 28.4 | 90 | 88 | 0 | 4.5 | 0.65 | 0.25
[11 empty] | 1998-05-06 | 1:30 | 862105.5 | 24.3 | 90 | 88 | 0 | 4.4 | 0.55 | 0.3
[11 empty] | 1998-05-06 | 9:00 | 862113 | 27.5 | 100+ | 100+ | 0 | 4.4 | 0.7 | 0.3
[11 empty] | 1998-05-06 | 9:20 | 862113.3333 |  | 100+ | 100+ | 0 | 4.4 | 0.55 | 0.3
[11 empty] | 1998-05-07 | 3:00 | 862131 |  | Off line
[11 empty] | 1998-05-18 | 13:30 | 862405.5 | 28.5 | 59 | 58 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-18 | 18:00 | 862410 | 28.2 | 56 | 54 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-19 | 3:30 | 862419.5 | 26.4 | 57 | 56 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-19 | 9:00 | 862425 | 27.4 | 58 | 58 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-19 | 18:00 | 862434 | 27.6 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3
[11 empty] | 1998-05-20 | 5:45 | 862445.75 | 25.6 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3
[11 empty] | 1998-05-20 | 11:00 | 862451 | 28.7 | 56 | 56 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-20 | 3:00 | 862443 | 28.4 | 55 | 54 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-21 | 3:30 | 862467.5 | 26.3 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3
[11 empty] | 1998-05-21 | 11:00 | 862475 | 26.5 | 60 | 59 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-21 | 18:00 | 862482 | 29 | 58 | 57 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-22 | 3:00 | 862491 | 26.5 | 56 | 55 | 0 | 4.4 | 0.82 | 0.3
[11 empty] | 1998-05-22 | 9:00 | 862497 | 26.5 | 59 | 60 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-22 | 19:30 | 862507.5 | 27.9 | 59 | 57 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-23 | 1:30 | 862513.5 | 26.9 | 60 | 58 | 0 | 4.2 | 0.75 | 0.3
[11 empty] | 1998-05-23 | 11:45 | 862523.75 | 27.9 | 60 | 58 | 0 | 4.3 | 0.77 | 0.3
[11 empty] | 1998-05-23 | 21:00 | 862533 | 26.7 | 60 | 58 | 0 | 4.2 | 0.76 | 0.3
[11 empty] | 1998-05-24 | 4:00 | 862540 | 26.2 | 60 | 58 | 0 | 4.3 | 0.75 | 0.3
[11 empty] | 1998-05-24 | 11:30 | 862547.5 | 28.5 | 58 | 57 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-24 | 18:00 | 862554 | 28.1 | 55 | 53 | 0 | 4.2 | 0.75 | 0.3
[11 empty] | 1998-05-25 | 1:45 | 862561.75 | 26.9 | 55 | 53 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-25 | 13:00 | 862573 | 28.5 | 55 | 53 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-25 | 18:00 | 862578 | 28.5 | 54 | 52 | 0 | 4.2 | 0.75 | 0.3
[11 empty] | 1998-05-26 | 3:45 | 862587.75 | 27.1 | 52 | 51 | 0 | 4 | 0.675 | 0.3
[11 empty] | 1998-05-26 | 9:00 | 862593 | 26.4 | 50 | 50 | 0 | 4.2 | 0.75 | 0.3
[11 empty] | 1998-05-26 | 18:00 | 862602 | 27.8 | 63 | 61 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-27 | 3:45 | 862611.75 | 27.1 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-27 | 9:00 | 862617 | 27.8 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-27 | 18:00 | 862626 | 28.1 | 60 | 58 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-28 | 2:30 | 862634.5 | 27.5 | 61 | 59 | 0 | 4.4 | 0.75 | 0.3
[11 empty] | 1998-05-28 | 9:00 | 862641 | 27.2 | 61 | 60 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-28 | 18:00 | 862650 | 27.8 | 64 | 62 | 0 | 4.4 | 0.75 | 0.25
[11 empty] | 1998-05-29 | 6:30 | 862662.5 | 26.4 | 64 | 62 | 0 | 4.4 | 0.75 | 0.25
[11 empty] | 1998-05-29 | 9:45 | 862665.75 | 28 | 64 | 63 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-29 | 19:15 | 862675.25 | 27.6 | 65 | 63.5 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-30 | 6:00 | 862686 | 26.9 | 65 | 63 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-30 | 13:00 | 862693 | 27.6 | 64 | 62 | 0 | 4.3 | 0.8 | 0.3
[11 empty] | 1998-05-30 | 19:30 | 862699.5 | 27.6 | 63.5 | 62 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-05-31 | 2:00 | 862706 | 26.9 | 63.5 | 62 | 0 | 4.2 | 0.77 | 0.3
[11 empty] | 1998-05-31 | 12:00 | 862716 | 27.3 | 63.5 | 62 | 0 | 4.3 | 0.78 | 0.3
[11 empty] | 1998-05-31 | 19:00 | 862723 | 27.3 | 59 | 58 | 0 | 4 | 0.75 | 0.3
[11 empty] | 1998-06-01 | 1:00 | 862729 | 26.8 | 58 | 56.5 | 0 | 4.4 | 0.8 | 0.3
[11 empty] | 1998-06-01 | 9:00 | 862737 | 28.3 | 62 | 58 | 0 | 4.4 | 0.8 | 0.3
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Note on A2: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis.
Note on AA15: TSC_ADM: Membrane cleaned due to carbonate scale build-up on the membrane. After this point a more stable acid feed system was used to maintain the influent pH <= 7 to prevent membrane scaling.
Note on AA73: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AK10: C. Hill (9/17/99): The dip in MTCw between 32and 91.5 hrs was explained in the Summary Report. The consultant had problems controlling the acid feed initially, which caused scaling problems. The acid feed was stabilized beyond 91.5 hrs, which reduced scaling and consequently the MTCw was more stable. See page 22 of the Summary Report.
Note on AO45: TSC_ADM: When questioned, consultant did not explain this drop in TDS.
Note on AQ5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN17: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BP25: DPATTON: Lab error suspected, changing values to NR
Note on BQ25: DPATTON: Lab error suspected, changing values to NR
Note on BR17: C. Hill (9/17/99): Reviewer verified this with the analytical data provided in the Summary Report (Exhibit 3).
Note on BT16: C. Hill (9/17/99): Reviewer verified reported feed, permeate and concentrate values for alkalinity, calcium/total hardness and UV during Week 1 (Summary Report - Exhibit 3). No changes were made.
Note on BT18: C. Hill (9/17/99): Reviewer verified reported feed, permeate and concentrate values for alkalinity, calcium/total hardness and UV during Week 1 (Summary Report - Exhibit 3). No changes were made.
Note on BT19: C. Hill (9/17/99): Reviewer verified reported feed, permeate and concentrate values for alkalinity, calcium/total hardness and UV during Week 1 (Summary Report - Exhibit 3). No changes were made.
Note on BT23: C. Hill (9/17/99): Reviewer verified reported feed, permeate and concentrate values for alkalinity, calcium/total hardness and UV during Week 1 (Summary Report - Exhibit 3). No changes were made.
Note on BY17: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on CA29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CA31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CB26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.7'.
Note on CB27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CB29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CB30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.97'.
Note on CB31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CB32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '256'.
Note on CB33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.1'.
Note on CB34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.1'.
Note on CB38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.5'.
Note on CB40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.5'.
Note on CB48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.5'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CJ17: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on CL29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CL31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CM26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.8'.
Note on CM27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CM29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CM30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.06'.
Note on CM31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CM32: C. Hill (9/15/99): Fee SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '296'.
Note on CM33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23'.
Note on CM34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.2'.
Note on CM35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '26.2'.
Note on CM38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.7'.
Note on CM40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.1'.
Note on CM41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.8'.
Note on CM48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.8'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CU17: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on CW29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CW31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CX26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.3'.
Note on CX27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CX30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.06'.
Note on CX31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CX32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '309'.
Note on CX33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '26'.
Note on CX34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.4'.
Note on CX35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '28.4'.
Note on CX38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on CX48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DF17: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on DR5: C. Hill (9/15/99): This data was copied by the reviewer from field 4-12 of the NF70 data collection spreadsheet.

## FldSys. 2nd Quarter
FIELD-SET 2: 2nd QUARTER SEBST RESULTS (FILE: Fluid Sys.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: SEBST Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 2-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 2-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 2-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 2-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [18 empty] | 0.71182 |  | 13.7008 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | ** Sample were received by lab out of holding time, for analysis of | [7 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL5360313 | Membrane trade name | Spiral-Wound Reverse Osmosis Element | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.25077 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | pH and UV254. | [7 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | TFCS 4921S |  |  | LSI | 0.14 | Hydrochloric acid addition | pH = 6.7 | Pilot-scale | 1998-07-27 | 18:00 | 7 | 32.8 | 61 | 59 | 0 | 4.3 | 0.75 | 0.25 |  | 1 | 5.3 | 0.32076 | 0.75 | 4.3 | 13.8462 | 10.2119 | 11.8367 | 48.1633 | 0.21203 | 6.4 | 7.3 | 7.4 | 106.15 | 424.6 | 1149.5 | 1379.95 | -20.0478 | 75 | 1289.8226 | 91.7702 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.26 |  |  |  | 1998-07-30 | 18:00 | 79 | 32.2 | 53 | 50 | 0 | 4.6 | 0.65 | 0.3 |  | 0.95 | 5.55 | 0.3403 | 0.68421 | 4.8421 | 12 | 9.0087 | 10.412 | 41.088 | 0.21925 | 5.7 | 6.4 | 6.1 | 135.85 | 485.1 | 1127.5 | 1241.8083 | -10.1382 | 71.9955 | 1177.045 | 88.4584 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.35 |  |  |  | 1998-07-31 | 9:30 | 94.5 | 31.8 | 64 | 64 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.2195 | 14.4738 | 49.5262 | 0.22654 | 5.5 | 5.9 | 6.2 | 169.4 | 595.1 | 1501.5 | 1730.3 | -15.2381 | 71.5342 | 1616.78 | 89.5224 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 1998-07-31 | 20:00 | 105 | 31.4 | 62 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.3529 | 12.4355 | 48.5645 | 0.23377 | 6.1 | 6.3 | 6.5 | 127.6 | 493.35 | 1364 | 1468.6833 | -7.6747 | 74.136 | 1371.15 | 90.6939 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 (dup) | CF-4 (dup) | CC-4 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophyllic | Permeate flow rate, Qp (gpm) | 0.8125 | Total aluminum (mg/L) | 0.11 |  |  |  | 1998-08-01 | 6:45 | 115.75 | 27.4 | 65 | 63 | 0 | 4.6 | 0.65 | 0.3 |  | 0.95 | 5.55 | 0.3403 | 0.68421 | 4.8421 | 12 | 10.3819 | 9.92 | 54.08 | 0.19197 | 5.7 | 6.1 | 6.4 | 165 | 497.75 | 1677.5 | 1218.7083 | 27.3497 | 66.8508 | 1157.0047 | 85.739 | [16 empty] | Sampling date | MM/DD/YY | 1998-08-05 | 1998-08-05 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-12 | 1998-08-12 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-19 | 1998-08-19 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-26 | 1998-08-26 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-26 | 1998-08-26 | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.0833 | Fluoride (mg/L) | 0.41 |  |  |  | 1998-08-01 | 14:00 | 123 | 32.2 | 59 | 57 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.0876 | 11.7623 | 46.2377 | 0.2398 | 5.7 | 6.1 | 6.5 | 133.65 | 479.6 | 1287 | 1402.1333 | -8.9459 | 72.133 | 1309.88 | 89.7968 | [16 empty] | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27083 | Phosphate (mg/L) | 0.098 |  |  |  | 1998-08-01 | 20:15 | 129.25 | 26.8 | 62 | 62 | 0 | 4.6 | 0.6 | 0.3 |  | 0.9 | 5.5 | 0.33867 | 0.66667 | 5.1111 | 11.0769 | 9.7548 | 9.7032 | 52.2968 | 0.18653 | 5.8 | 6.3 | 6.5 | 154 | 496.1 | 1325.5 | 1180.3 | 10.9544 | 68.9579 | 1124.32 | 86.3028 | [16 empty] | Operation time | hh.hh | 214 | 214 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 382 | 382 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 550 | 550 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 718 | 718 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 718 | 718 | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 31 |  |  |  | 1998-08-02 | 5:00 | 138 | 32 | 64 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.1533 | 11.781 | 52.719 | 0.21156 | 5.7 | 6.1 | 6.5 | 134.75 | 481.25 | 1287 | 1405.25 | -9.188 | 72 | 1312.85 | 89.7361 | [16 empty] | pH | --- | 6.01 | 6.31 | NA | --- | --- | --- | --- | --- | pH | --- | 5.97 | 5.92 | NA | --- | --- | --- | --- | --- | pH | --- | NR | NR | NA | --- | --- | --- | --- | --- | pH | --- | 5.79 | 6.3 | NA | --- | --- | --- | --- | --- | pH | --- | 5.81 | 6.31 | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 10 | Calcium (mg/L) | 83 |  |  |  | 1998-08-02 | 13:30 | 146.5 | 34.6 | 58 | 56 | 0 | 4.3 | 0.73 | 0.3 |  | 1.03 | 5.33 | 0.32337 | 0.70874 | 4.1748 | 13.4769 | 9.4245 | 11.9086 | 45.0914 | 0.20901 | 5.8 | 6.1 | 6.6 | 138.6 | 510.95 | 1232 | 1417.0017 | -15.0164 | 72.8741 | 1329.4563 | 89.5747 | [16 empty] | Temperature | oC | 29 | 29 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.9 | 27.9 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.9 | 27.9 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.8 | 27.8 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.8 | 27.8 | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.016 |  |  |  | 1998-08-02 | 18:00 | 151 | 31.6 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 9.8752 | 11.3157 | 44.6843 | 0.221 | 5.8 | 6.3 | 6.5 | 139.15 | 502.15 | 1221 | 1349.15 | -10.4955 | 72.2892 | 1270.7241 | 89.0496 | [16 empty] | Alkalinity | mg/L as CaCO3 | 43 | 140 | NA | 402.2593 | #VALUE! | 69.2857 | 376.0333 | 88.5648 | Alkalinity | mg/L as CaCO3 | 32 | 130 | NA | 358.6667 | #VALUE! | 75.3846 | 337.4938 | 90.5183 | Alkalinity | mg/L as CaCO3 | 32 | 140 | NA | 432 | #VALUE! | 77.1429 | 402.8 | 92.0556 | Alkalinity | mg/L as CaCO3 | 34 | 150 | NA | 463.6296 | #VALUE! | 77.3333 | 432.2667 | 92.1345 | Alkalinity | mg/L as CaCO3 | 37 | 140 | NA | 418.4815 | #VALUE! | 73.5714 | 390.6333 | 90.5282 | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Design recycle flow rate, QR (gpm) | 4.4167 | Strontium (mg/L) | 0.13 |  |  |  | 1998-08-03 | 1:00 | 158 | 32.4 | 58 | 56 | 0 | 4.4 | 0.72 | 0.3 |  | 1.02 | 5.42 | 0.32955 | 0.70588 | 4.3137 | 13.2923 | 9.92 | 11.6794 | 45.3206 | 0.21888 | 5.8 | 6.2 | 6.5 | 137.5 | 505.45 | 1226.5 | 1388.53 | -13.2108 | 72.7965 | 1305.4358 | 89.4671 | [16 empty] | Total dissolved solids | mg/L | 110 | 610 | NA | 1961.8519 | #VALUE! | 81.9672 | 1826.6667 | 93.9781 | Total dissolved solids | mg/L | 100 | 600 | NA | 1766.6667 | #VALUE! | 83.3333 | 1658.642 | 93.971 | Total dissolved solids | mg/L | 120 | 530 | NA | 1638.5185 | #VALUE! | 77.3585 | 1527.6667 | 92.1449 | Total dissolved solids | mg/L | 95 | 560 | NA | 1817.2222 | #VALUE! | 83.0357 | 1691.5 | 94.3837 | Total dissolved solids | mg/L | 98 | 590 | NA | 1920.2222 | #VALUE! | 83.3898 | 1787.2 | 94.5166 | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Recycle ratio, r | 4.0769 | Reactive silica (mg/L as SiO2) | 34 |  |  |  | 1998-08-03 | 18:00 | 175 | 30.9 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.0817 | 10.9043 | 47.0957 | 0.21407 | 5.8 | 6.3 | 6.6 | 157.85 | 507.65 | 1325.5 | 1323.85 | 0.12448 | 68.9057 | 1248.2759 | 87.3546 | [16 empty] | Total hardness | mg/L as CaCO3 | 39 | 290 | NA | 968.6296 | #VALUE! | 86.5517 | 900.7667 | 95.6704 | Total hardness | mg/L as CaCO3 | 32 | 270 | NA | 825.3333 | #VALUE! | 88.1481 | 773.9136 | 95.8652 | Total hardness | mg/L as CaCO3 | 41 | 270 | NA | 889.1481 | #VALUE! | 84.8148 | 827.2333 | 95.0437 | Total hardness | mg/L as CaCO3 | 35 | 280 | NA | 942.4074 | #VALUE! | 87.5 | 876.1667 | 96.0053 | Total hardness | mg/L as CaCO3 | 37 | 290 | NA | 974.037 | #VALUE! | 87.2414 | 905.6333 | 95.9145 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | NR |  |  |  | 1998-08-04 | 6:15 | 187.25 | 27 | 62 | 60 | 0 | 4.4 | 0.65 | 0.35 |  | 1 | 5.4 | 0.33053 | 0.65 | 4.4 | 12 | 10.5054 | 10.4561 | 50.5439 | 0.20785 | 5.8 | 6.2 | 6.5 | 119.35 | 508.75 | 1199 | 1231.9214 | -2.7457 | 76.5405 | 1164.9611 | 89.755 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 29 | 220 | NA | 736.4074 | #VALUE! | 86.8182 | 684.7667 | 95.765 | Calcium hardness | mg/L as CaCO3 | 28 | 210 | NA | 634.6667 | #VALUE! | 86.6667 | 595.3457 | 95.2969 | Calcium hardness | mg/L as CaCO3 | 34 | 220 | NA | 722.8889 | #VALUE! | 84.5455 | 672.6 | 94.945 | Calcium hardness | mg/L as CaCO3 | 27 | 220 | NA | 741.8148 | #VALUE! | 87.7273 | 689.6333 | 96.0849 | Calcium hardness | mg/L as CaCO3 | 29 | 230 | NA | 773.4444 | #VALUE! | 87.3913 | 719.1 | 95.9672 | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 3.2 |  |  |  | 1998-08-04 | 18:00 | 199 | 30.5 | 61 | 59 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.31751 | 0.71429 | 4 | 13.8462 | 10.9303 | 12.012 | 47.988 | 0.22777 | 5.8 | 6.3 | 6.6 | 133.1 | 502.7 | 1276 | 1426.7 | -11.8103 | 73.523 | 1334.3 | 90.0247 | [16 empty] | Turbidity | ntu | BMRL | 3 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.1 | 0.33 | NA | 0.86667 | #VALUE! | 69.697 | 0.81698 | 87.7597 | Turbidity | ntu | BMRL | 1.1 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.3 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 1998-08-05 | 6:00 | 211 | 27 | 64 | 62 | 0 | 3 | 0.65 | 0.35 |  | 1 | 4 | 0.23935 | 0.65 | 3 | 12 | 10.5054 | 10.6837 | 52.3162 | 0.20081 | 5.7 | 6.2 | 6.5 | 93.5 | 500.5 | 1188 | 1256.3571 | -5.754 | 81.3187 | 1161.875 | 91.9527 | [16 empty] | Ammonia | mg NH3-N / L | 0.31 | 0.59 | NA | 1.347 | #VALUE! | 47.4576 | 1.2713 | 75.6162 | Ammonia | mg NH3-N / L | 0.53 | 0.26 | NA | -0.37 | #VALUE! | -103.8462 | -0.31167 | 270.0535 | Ammonia | mg NH3-N / L | 0.36 | 0.46 | NA | 0.73037 | #VALUE! | 21.7391 | 0.70333 | 48.8152 | Ammonia | mg NH3-N / L | 0.24 | 0.47 | NA | 1.0919 | #VALUE! | 48.9362 | 1.0297 | 76.6915 | Ammonia | mg NH3-N / L | 0.25 | 0.48 | NA | 1.1019 | #VALUE! | 47.9167 | 1.0397 | 75.9538
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-08-05 | 18:00 | 223 | 31.3 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 9.9632 | 10.8871 | 46.1129 | 0.21606 | 5.8 | 6.3 | 6.6 | 147.4 | 496.65 | 1259.5 | 1311.5667 | -4.1339 | 70.3212 | 1236.1114 | 88.0755 | [16 empty] | Total organic carbon | mg/L | BMRL | 5.7 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.1 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 12.67 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-08-06 | 4:45 | 233.75 | 27.1 | 59 | 57 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.32727 | 0.68421 | 4.6316 | 12 | 10.4744 | 11.4674 | 46.5326 | 0.2251 | 5.8 | 6.2 | 6.5 | 126.5 | 512.05 | 1221 | 1347.4083 | -10.3529 | 75.2954 | 1273.241 | 90.0647 | [16 empty] | UV254 | cm-1 | 0.012 | 0.24 | NA | 0.85644 | #VALUE! | 95 | 0.7948 | 98.4902 | UV254 | cm-1 | 0.012 | 0.23 | NA | 0.73867 | #VALUE! | 94.7826 | 0.69157 | 98.2648 | UV254 | cm-1 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.27 | NA | 0.97567 | #VALUE! | 96.6667 | 0.9051 | 99.0056 | UV254 | cm-1 | 0.009 | 0.27 | NA | 0.97567 | #VALUE! | 96.6667 | 0.9051 | 99.0056
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0027 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 1998-08-06 | 10:00 | 239 | 30.3 | 60 | 58 | 0 | 4.4 | 0.69 | 0.3 |  | 0.99 | 5.39 | 0.32858 | 0.69697 | 4.4444 | 12.7385 | 10.1155 | 12.2316 | 46.7684 | 0.21629 | 6.2 | 6.3 | 6.7 | 111.65 | 507.65 | 1111 | 1418.45 | -27.6733 | 78.0065 | 1334.8051 | 91.6355 | [16 empty] | SUVA | L/(mg*m) | NR | 4.2105 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.7705 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | NR | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.3548 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.1538 | NA | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 1998-08-06 | 18:00 | 247 | 29.4 | 58 | 56 | 0 | 4.5 | 0.7 | 0.3 |  | 1 | 5.5 | 0.33542 | 0.7 | 4.5 | 12.9231 | 10.5387 | 10.9695 | 46.0305 | 0.22895 | 5.7 | 6.2 | 6.4 | 138.05 | 489.5 | 1237.5 | 1309.55 | -5.8222 | 71.7978 | 1235 | 88.8219 | [16 empty] | Bromide | mg/L | 97 | 420 | NA | 1293.2963 | --- | 76.9048 | 1205.9667 | 91.9567 | Bromide | mg/L | 59 | 240 | NA | 662.3333 | --- | 75.4167 | 623.2284 | 90.5332 | Bromide | mg/L | BMRL | 300 | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 80 | 390 | NA | 1228.1481 | --- | 79.4872 | 1144.3333 | 93.009 | Bromide | mg/L | 77 | 400 | NA | 1273.2963 | --- | 80.75 | 1185.9667 | 93.5074
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 1998-08-07 | 9:00 | 262 | 30.6 | 60 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.6246 | 14.212 | 45.788 | 0.25388 | 5.7 | 6.1 | 6.3 | 157.3 | 575.3 | 1210 | 1689.9667 | -39.6667 | 72.6577 | 1578.5 | 90.0348 | [16 empty] | SDS-Cl2 dose | mg/L | 12 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 9.7 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 8.8 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.9 | NR | NA | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1152.638 | [5 empty] | 1998-08-07 | 18:05 | 271.0833 | 27 | 62 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 12.053 | 49.447 | 0.2288 | 5.8 | 6.6 | 6.6 | 109.45 | 496.1 | 1116.5 | 1398.2833 | -25.2381 | 77.9379 | 1314.7478 | 91.6752 | [16 empty] | SDS-Free Cl2 residual | mg/L | 0.64 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.4 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.2 | NR | NA | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 202.454 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-08-08 | 5:30 | 282.5 | 25.8 | 67 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.722 | 11.5558 | 54.4442 | 0.2153 | 5.8 | 6.2 | 6.6 | 121.55 | 492.25 | 1298 | 1357.2167 | -4.5621 | 75.3073 | 1277.1272 | 90.4825 | [16 empty] | SDS-Cl2 demand | mg/L | 11.36 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 8.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 7.5 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 2.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | 1 | Influent TDS, TDSI (mg/L) | 1012.2699 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-08-08 | 13:30 | 290.5 | 32.6 | 61 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 10.9573 | 12.2298 | 47.7702 | 0.22937 | 5.8 | 6.2 | 6.6 | 134.2 | 493.9 | 1303.5 | 1453.1 | -11.4768 | 72.8285 | 1357.18 | 90.1118 | [16 empty] | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 1998-08-08 | 16:45 | 293.75 | 30.1 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.3229 | 11.8301 | 49.1699 | 0.20994 | 6.2 | 6.8 | 6.9 | 107.25 | 486.75 | 1098.9 | 1372.25 | -24.8749 | 77.9661 | 1290.2593 | 91.6877 | [16 empty] | SDS-Chlorination pH | --- | 7.93 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.92 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.9 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.91 | NR | NA | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 10 | [7 empty] | 1998-08-09 | 1:00 | 302 | 32.6 | 61 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 10.9573 | 12.4168 | 48.0832 | 0.22788 | 5.8 | 6.2 | 6.6 | 127.6 | 492.8 | 1309 | 1466.6667 | -12.0448 | 74.1071 | 1369.28 | 90.6812 | [16 empty] | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 1998-08-09 | 14:00 | 315 | 35.2 | 50 | 48 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 10.1467 | 10.285 | 38.715 | 0.26209 | 6.4 | 7.2 | 7.4 | 142.45 | 444.95 | 1188 | 1251.6167 | -5.3549 | 67.9852 | 1170.95 | 87.8347 | [16 empty] | SDS-TOX | mg Cl- /L | 40 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 63 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 224 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 140 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | NaCl 500 mg/L | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 1998-08-10 | 18:00 | 343 | 28.7 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.7591 | 10.2527 | 51.7473 | 0.20792 | 5.3 | 5.3 | 5.5 | 162.8 | 491.7 | 1452 | 1259.1333 | 13.2828 | 66.8904 | 1188.0747 | 86.2972 | [16 empty] | SDS-CHCl3 | mg/L | 6.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 6.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 32 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 19 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) | 85 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 1998-08-11 | 2:30 | 351.5 | 23.6 | 66 | 62 | 0 | 3.5 | 0.68 | 0.3 |  | 0.98 | 4.48 | 0.26964 | 0.69388 | 3.5714 | 12.5538 | 12.1522 | 10.0781 | 53.9219 | 0.22537 | 5.7 | 6 | 6.3 | 136.4 | 470.25 | 1369.5 | 1226.9767 | 10.407 | 70.9942 | 1144.2097 | 88.0791 | [16 empty] | SDS-BDCM | mg/L | 2.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 9.5 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 4.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | +/-15.0 | Required influent pressure, PI (psi) | 70.6164 | [5 empty] | 1998-08-11 | 9:00 | 358 | 27.8 | 70 | 70 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.6276 | 14.0811 | 55.9189 | 0.22582 | 5.7 | 6 | 6.4 | 135.85 | 550 | 1314.5 | 1654.4 | -25.8577 | 75.3 | 1543.96 | 91.2012 | [16 empty] | SDS-DBCM | mg/L | 6.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 8.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [7 empty] | 1998-08-11 | 18:00 | 367 | 29.7 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.4457 | 10.5956 | 41.4044 | 0.25229 | 5.8 | 6.3 | 6.6 | 119.9 | 459.8 | 1003.2 | 1252.9 | -24.8904 | 73.9234 | 1179.4648 | 89.8344 | [16 empty] | SDS-CHBr3 | mg/L | 3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7.5 | [7 empty] | 1998-08-12 | 1:00 | 374 | 24 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 10.5614 | 42.4386 | 0.29131 | 6 | 6.3 | 6.5 | 122.1 | 460.9 | 1090.1 | 1251.4333 | -14.7999 | 73.5084 | 1178.2358 | 89.637 | [16 empty] | SDS-THM4 | mg/L | 17.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 24.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 36.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 20.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0-350 | [7 empty] | 1998-08-12 | 19:30 | 392.5 | 28.5 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.8229 | 9.7898 | 50.2102 | 0.21555 | 5.8 | 6.2 | 6.5 | 156.75 | 470.8 | 1369.5 | 1203.5833 | 12.1151 | 66.7056 | 1135.733 | 86.1983 | [16 empty] | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 1998-08-13 | 1:00 | 398 | 27.4 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1806 | 9.7727 | 49.7273 | 0.22484 | 5.8 | 6.2 | 6.5 | 161.15 | 474.65 | 1375 | 1206.15 | 12.28 | 66.0487 | 1138.4185 | 85.8444 | [16 empty] | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 6.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 13 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 7.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 3 | [7 empty] | 1998-08-13 | 13:00 | 410 | 26.6 | 75 | 73 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.0835 | 11.6688 | 62.3312 | 0.2099 | 5.7 | 5.8 | 6.2 | 223.85 | 567.05 | 1545.5 | 1482.25 | 4.0925 | 60.5238 | 1390.73 | 83.9041 | [16 empty] | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 4.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 4.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-08-14 | 2:30 | 423.5 | 25.6 | 76 | 74 | 0 | 4.5 | 0.7 | 0.3 |  | 1 | 5.5 | 0.33542 | 0.7 | 4.5 | 12.9231 | 11.7915 | 11.1583 | 63.8417 | 0.1847 | 5.2 | 5.5 | 5.8 | 136.4 | 493.9 | 1160.5 | 1328.0667 | -14.4392 | 72.3831 | 1252.2333 | 89.1075 | [16 empty] | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 0 | [7 empty] | 1998-08-14 | 18:00 | 439 | 29.5 | 68 | 66 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.0087 | 11.6314 | 55.3686 | 0.21689 | 5.6 | 6.1 | 6.4 | 132 | 474.1 | 1298 | 1386.3667 | -6.8079 | 72.1578 | 1295.14 | 89.8081 | [16 empty] | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 2.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 1998-08-15 | 1:30 | 446.5 | 26.4 | 70 | 71 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.1611 | 11.8745 | 58.6255 | 0.22449 | 5.6 | 6.1 | 6.4 | 130.9 | 480.15 | 1408 | 1411.4833 | -0.2474 | 72.7377 | 1318.35 | 90.0709 | [16 empty] | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 3.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 4.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-08-15 | 13:30 | 458.5 | 28.4 | 67 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.4056 | 11.7997 | 54.2003 | 0.22888 | 5.4 | 5.9 | 6.1 | 118.25 | 465.3 | 1210 | 1390.7667 | -14.9394 | 74.5863 | 1298.22 | 90.8914 | [16 empty] | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-08-15 | 19:30 | 464.5 | 28 | 66 | 64 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.5532 | 11.7436 | 53.2564 | 0.23571 | 5.1 | 5.8 | 6 | 121 | 466.4 | 1265 | 1387.4667 | -9.6812 | 74.0566 | 1295.36 | 90.659 | [16 empty] | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-08-16 | 2:30 | 471.5 | 27.8 | 67 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.6276 | 11.8558 | 54.1442 | 0.23322 | 5.5 | 6.1 | 6.4 | 125.4 | 474.1 | 1331 | 1403.9667 | -5.4821 | 73.5499 | 1310.98 | 90.4346 | [16 empty] | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-08-16 | 18:00 | 487 | 28.1 | 63 | 61 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.7339 | 9.9307 | 52.0693 | 0.22535 | 5.5 | 5.9 | 6 | 149.6 | 454.3 | 1122 | 1216.05 | -8.3824 | 67.0702 | 1142.6704 | 86.9079 | [16 empty] | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 11.5 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 16 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 14.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-08-17 | 2:30 | 495.5 | 28.2 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.4792 | 11.7249 | 51.2751 | 0.24338 | 5.4 | 5.8 | 6.2 | 119.35 | 464.2 | 1226.5 | 1383.8 | -12.8251 | 74.2891 | 1291.84 | 90.7612 | [16 empty] | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 17.5 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 19.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 19.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 1998-08-17 | 21:00 | 514 | 27.4 | 67 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1806 | 10.047 | 55.953 | 0.19982 | 5.6 | 6.2 | 6.6 | 119.9 | 442.2 | 1320 | 1194.2333 | 9.5278 | 72.8856 | 1124.6006 | 89.3384 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 1998-08-18 | 4:45 | 521.75 | 26.8 | 66 | 64 | 0 | 4.2 | 0.7 | 0.25 |  | 0.95 | 5.15 | 0.31262 | 0.73684 | 4.4211 | 12.9231 | 11.3806 | 11.3371 | 53.6629 | 0.21208 | 5.7 | 6.4 | 6.7 | 124.3 | 444.4 | 1292.5 | 1340.68 | -3.7277 | 72.0297 | 1258.0134 | 90.1193 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 1998-08-18 | 9:00 | 526 | 27.5 | 66 | 63 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7401 | 8.9386 | 55.5614 | 0.2293 | 5.7 | 6.1 | 6.5 | 178.2 | 441.1 | 1265 | 1142.1667 | 9.7101 | 59.601 | 1072.06 | 83.3778
[11 empty] | 1998-08-18 | 18:00 | 535 | 29.8 | 67 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.9027 | 10.8273 | 55.1727 | 0.21574 | 5.7 | 6.3 | 6.6 | 129.25 | 447.7 | 1320 | 1296.9 | 1.75 | 71.1302 | 1211.98 | 89.3356 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 1998-08-19 | 4:00 | 545 | 26.9 | 65 | 63 | 0 | 4.2 | 0.7 | 0.25 |  | 0.95 | 5.15 | 0.31262 | 0.73684 | 4.4211 | 12.9231 | 11.347 | 11.0449 | 52.9551 | 0.21428 | 5.7 | 6.2 | 6.6 | 134.75 | 446.6 | 1292.5 | 1319.78 | -2.1106 | 69.8276 | 1239.244 | 89.1264 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 1998-08-19 | 9:00 | 550 | 27.6 | 66 | 64 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7025 | 7.9288 | 57.0712 | 0.22257 | 5.6 | 6.3 | 6.3 | 206.25 | 439.45 | 1232 | 1061.3167 | 13.8542 | 53.0663 | 999.13 | 79.357 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 1998-08-19 | 18:00 | 559 | 27.3 | 70 | 68 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.0146 | 10.8091 | 58.1909 | 0.20647 | 5.8 | 6.3 | 6.7 | 116.6 | 448.25 | 1353 | 1277.375 | 5.5894 | 73.9877 | 1197.5052 | 90.2631 | [16 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
[11 empty] | 1998-08-20 | 6:00 | 571 | 26.9 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.347 | 10.0299 | 52.9701 | 0.21422 | 5.7 | 6.3 | 6.7 | 124.3 | 446.05 | 1265 | 1196.8 | 5.3913 | 72.1332 | 1127.2861 | 88.9735 | [16 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-08-20 | 9:00 | 574 | 28.2 | 72 | 70 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.4792 | 13.7071 | 57.2929 | 0.21781 | 5.7 | 6.2 | 6.5 | 160.6 | 563.75 | 1595 | 1638.8167 | -2.7471 | 71.5122 | 1531.31 | 89.5122 | [16 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-08-21 | 9:00 | 598 | 27.5 | 64 | 62 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.9438 | 6.6145 | 56.3855 | 0.21182 | 5.7 | 6 | 6.5 | 237.05 | 440 | 1221 | 947.375 | 22.4099 | 46.125 | 898.4994 | 73.6171 | [16 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
[11 empty] | 1998-08-21 | 18:00 | 607 | 27.5 | 72 | 70 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.7401 | 11.7997 | 59.2003 | 0.2152 | 5.6 | 6.4 | 6.6 | 106.7 | 453.75 | 1226.5 | 1379.2167 | -12.4514 | 76.4848 | 1286.67 | 91.7073 | [16 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-08-22 | 6:45 | 619.75 | 26.9 | 71 | 69 | 0 | 4.2 | 0.8 | 0.3 |  | 1.1 | 5.3 | 0.31913 | 0.72727 | 3.8182 | 14.7692 | 12.968 | 12.1936 | 57.8064 | 0.22434 | 5.9 | 6.4 | 6.8 | 98.45 | 458.15 | 1138.5 | 1417.35 | -24.4928 | 78.5114 | 1317.8104 | 92.5293 | [16 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-08-22 | 14:00 | 627 | 29 | 68 | 66 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.1875 | 12.2298 | 54.7702 | 0.22252 | 5.7 | 6.2 | 6.6 | 93.5 | 453.2 | 1122 | 1412.4 | -25.8824 | 79.3689 | 1316.48 | 92.8977 | [16 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[11 empty] | 1998-08-22 | 20:30 | 633.5 | 26.9 | 68 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.968 | 12.1924 | 54.3076 | 0.23879 | 5.8 | 6.3 | 6.7 | 107.8 | 466.4 | 1265 | 1422.6667 | -12.4638 | 76.8868 | 1327.04 | 91.8767 | [16 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[11 empty] | 1998-08-23 | 2:30 | 639.5 | 26.3 | 68 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.2001 | 11.6688 | 54.8312 | 0.24074 | 5.8 | 6.4 | 6.6 | 121.55 | 464.75 | 1375 | 1379.95 | -0.36 | 73.8462 | 1288.43 | 90.566 | [16 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 1998-08-23 | 13:45 | 650.75 | 29.7 | 62 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.938 | 12.0802 | 48.9198 | 0.24403 | 5.6 | 6.2 | 6.4 | 113.3 | 468.6 | 1177 | 1416.0667 | -20.3115 | 75.8216 | 1321.32 | 91.4252 | [16 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 1998-08-23 | 18:00 | 655 | 29.8 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.4149 | 10.3556 | 50.6444 | 0.20565 | 5.6 | 6.3 | 6.6 | 128.7 | 460.9 | 1215.5 | 1236.0333 | -1.6893 | 72.0764 | 1164.2617 | 88.9458 | [16 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 1998-08-24 | 2:30 | 663.5 | 29.6 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.4766 | 10.3556 | 50.6444 | 0.20687 | 5.6 | 6.3 | 6.6 | 127.6 | 459.8 | 1210 | 1234.9333 | -2.0606 | 72.2488 | 1163.1617 | 89.0299 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 1998-08-24 | 9:00 | 670 | 27.2 | 62 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.8535 | 12.3046 | 48.6954 | 0.26396 | 5.6 | 6 | 6.4 | 105.6 | 467.5 | 1188 | 1432.5667 | -20.5864 | 77.4118 | 1336.06 | 92.0962 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 1998-08-24 | 18:00 | 679 | 29.7 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.4457 | 10.3556 | 48.6444 | 0.21474 | 5.7 | 6.3 | 6.6 | 133.65 | 465.85 | 1215.5 | 1240.9833 | -2.0965 | 71.3105 | 1169.2117 | 88.5692 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 1998-08-25 | 3:45 | 688.75 | 27.2 | 60 | 58 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.31588 | 0.7 | 4.2 | 12.9231 | 11.2469 | 10.3109 | 48.6891 | 0.23099 | 5.7 | 6.2 | 6.5 | 128.7 | 460.35 | 1199 | 1234.2 | -2.9358 | 72.043 | 1159.7913 | 88.9032 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 1998-08-25 | 9:00 | 694 | 28 | 62 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.5532 | 10.9769 | 50.0231 | 0.25095 | 5.7 | 6.1 | 6.4 | 131.45 | 454.3 | 1122 | 1315.2333 | -17.2222 | 71.0654 | 1229.14 | 89.3055 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 1998-08-25 | 18:00 | 703 | 29.8 | 60 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.1588 | 10.7911 | 48.2089 | 0.23147 | 5.6 | 6.4 | 6.5 | 128.7 | 459.8 | 1166 | 1287.55 | -10.4245 | 72.0096 | 1207.8126 | 89.3444 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 1998-08-26 | 5:15 | 714.25 | 27.5 | 60 | 57 | 0 | 3.8 | 0.65 | 0.3 |  | 0.95 | 4.75 | 0.2882 | 0.68421 | 4 | 12 | 10.3513 | 10.2055 | 48.2945 | 0.21434 | 5.7 | 6.2 | 6.5 | 122.65 | 468.6 | 1138.5 | 1218.1583 | -6.9968 | 73.8263 | 1143.2025 | 89.2714 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 1998-08-26 | 18:00 | 727 | 28.5 | 74 | 71 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.369 | 12.2859 | 60.2141 | 0.20542 | 5.6 | 6.4 | 6.6 | 95.15 | 456.5 | 1122 | 1420.1 | -26.5686 | 79.1566 | 1323.74 | 92.812 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 1998-08-27 | 3:30 | 736.5 | 27.6 | 72 | 70 | 0 | 4.2 | 0.8 | 0.3 |  | 1.1 | 5.3 | 0.31913 | 0.72727 | 3.8182 | 14.7692 | 12.7025 | 11.9139 | 59.0861 | 0.21498 | 5.7 | 6.2 | 6.7 | 114.4 | 465.85 | 1281.5 | 1403.05 | -9.485 | 75.4427 | 1305.7934 | 91.239 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1998-08-27 | 9:00 | 742 | 27 | 70 | 68 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.9298 | 10.0232 | 58.9768 | 0.21923 | 5.7 | 6 | 6.4 | 152.35 | 447.15 | 1259.5 | 1233.2833 | 2.0815 | 65.9287 | 1154.67 | 86.8058 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 1998-08-27 | 18:00 | 751 | 29.6 | 68 | 64 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.9733 | 11.6314 | 54.3686 | 0.22022 | 5.6 | 6.3 | 6.6 | 129.8 | 471.9 | 1314.5 | 1384.1667 | -5.2999 | 72.4942 | 1292.94 | 89.9609 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 1998-08-28 | 6:30 | 763.5 | 27.2 | 65 | 62 | 0 | 4 | 0.7 | 0.3 |  | 1 | 5 | 0.30285 | 0.7 | 4 | 12.9231 | 11.2469 | 10.4687 | 53.0313 | 0.21208 | 5.7 | 6.3 | 6.7 | 135.3 | 473 | 1270.5 | 1260.9667 | 0.75036 | 71.3953 | 1182.17 | 88.5549
[11 empty] | 1998-08-28 | 15:30 | 772.5 | 27.4 | 60 | 56 | 0 | 4.3 | 0.75 | 0.3 |  | 1.05 | 5.35 | 0.32402 | 0.71429 | 4.0952 | 13.8462 | 11.9792 | 11.3132 | 46.6868 | 0.25659 | 5.4 | 6 | 6 | 174.9 | 522.5 | 931.7 | 1391.5 | -49.3506 | 66.5263 | 1306.2243 | 86.6103
[11 empty] | 1998-08-29 | 6:00 | 787 | 27.5 | 63 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 10.4756 | 51.0244 | 0.21848 | 5.4 | 5.8 | 5.9 | 144.65 | 480.7 | 1270.5 | 1264.8167 | 0.44733 | 69.9085 | 1192.2133 | 87.8671
[11 empty] | 1998-08-29 | 14:45 | 795.75 | 30.3 | 59 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.2621 | 11.1614 | 45.8386 | 0.22387 | 5.4 | 5.4 | 5.8 | 141.35 | 499.4 | 1298 | 1334.85 | -2.839 | 71.696 | 1257.4935 | 88.7594
[11 empty] | 1998-08-30 | 18:00 | 823 | 30.1 | 57 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.3229 | 10.2356 | 45.2644 | 0.22806 | 5.5 | 5.9 | 6.2 | 145.2 | 473.55 | 1254 | 1239.7 | 1.1404 | 69.338 | 1168.7602 | 87.5766
[11 empty] | 1998-08-31 | 3:00 | 832 | 28.8 | 58 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.7273 | 11.4186 | 44.5814 | 0.24062 | 5.7 | 6 | 6.3 | 111.1 | 477.4 | 1025.2 | 1332.1 | -29.9356 | 76.7281 | 1252.9611 | 91.133
[11 empty] | 1998-08-31 | 18:00 | 847 | 29.5 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 12.0087 | 11.7062 | 51.2938 | 0.23412 | 5.4 | 5.9 | 6.1 | 138.6 | 482.9 | 1287 | 1401.0333 | -8.8604 | 71.2984 | 1309.22 | 89.4135
[11 empty] | 1998-09-01 | 4:45 | 857.75 | 27.6 | 64 | 61 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.31588 | 0.7 | 4.2 | 12.9231 | 11.1147 | 10.8239 | 51.6761 | 0.21508 | 5.4 | 5.7 | 6.1 | 136.95 | 485.1 | 1270.5 | 1297.45 | -2.1212 | 71.7687 | 1219.3394 | 88.7685
[11 empty] | 1998-09-01 | 18:00 | 871 | 29.7 | 69 | 66 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 11.938 | 11.9493 | 55.5507 | 0.2149 | 5.5 | 6 | 6.4 | 145.75 | 497.2 | 1430 | 1434.4 | -0.30769 | 70.6858 | 1340.68 | 89.1287
[11 empty] | 1998-09-02 | 6:30 | 883.5 | 27.5 | 67 | 64 | 0 | 4.4 | 0.7 | 0.3 | X | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 10.8528 | 54.6472 | 0.20399 | 5.6 | 5.9 | 6.4 | 149.6 | 497.75 | 1397 | 1310.1 | 6.2205 | 69.9448 | 1234.8824 | 87.8855
0.1847
0.29131
0.22296
0.21203
0.20399
Note on A2: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis.
Note on Q3: TSC_ADM: Consultant noted that water treatment plant staff measured the influent temperature and the membrane operating parameters, and attributed the wide temperature fluctuations and erratic operational data to measurement error.
Note on AA86: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN17: C. Hill (9/17/99): Reviewer verified feed and permeate TDS values (which differ significantly from those reported in operational data) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity with an average TDS conversion factor.
Note on BN38: C. Hill (9/17/99): Reviewer verified all reported HAA permeate values using analytical reports contained in the Summary Report (Exhibit 3).
Note on BP29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on BP31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on BQ26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.1'.
Note on BQ27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on BQ30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.9'.
Note on BQ31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on BQ32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '276'.
Note on BQ33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17'.
Note on BQ34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17'.
Note on BQ38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.8'.
Note on BQ40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.8'.
Note on BQ48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.8'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on BY17: C. Hill (9/17/99): Reviewer verified feed and permeate TDS values (which differ significantly from those reported in operational data) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity with an average TDS conversion factor.
Note on BY38: C. Hill (9/17/99): Reviewer verified all reported HAA permeate values using analytical reports contained in the Summary Report (Exhibit 3).
Note on CA29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CA31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CB25: C. Hill (9/17/99): This value was reported incorrectly. Changed from 200 to 240 by the reviewer based on analytical report contained in Summary Report (Exhibit 3).
Note on CB26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.6'.
Note on CB27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CB30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.96'.
Note on CB31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CB32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '303'.
Note on CB33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '24'.
Note on CB34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.1'.
Note on CB35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '28.1'.
Note on CB38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.1'.
Note on CB40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.3'.
Note on CB41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.1'.
Note on CB44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '14.4'.
Note on CB48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17.5'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CJ17: C. Hill (9/17/99): Reviewer verified feed and permeate TDS values (which differ significantly from those reported in operational data) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity with an average TDS conversion factor.
Note on CJ38: C. Hill (9/17/99): Reviewer verified all reported HAA permeate values using analytical reports contained in the Summary Report (Exhibit 3).
Note on CL26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.7'.
Note on CL27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CL28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CL29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CL30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.93'.
Note on CL31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CL32: C. Hill (9/15/99): Permeate SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '228'.
Note on CL33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '19'.
Note on CL34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.7'.
Note on CL35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on CL36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CL37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '28.5'.
Note on CL38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CL39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.7'.
Note on CL40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.1'.
Note on CL41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CL42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.1'.
Note on CL43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.4'.
Note on CL44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CL45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CL46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CL47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.9'.
Note on CL48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '13.3'.
Note on CM26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.2'.
Note on CM27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CM30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.93'.
Note on CM31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CM32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '316'.
Note on CM33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '37'.
Note on CM34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '10'.
Note on CM35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on CM36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '51'.
Note on CM38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '12'.
Note on CM40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.4'.
Note on CM41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.6'.
Note on CM43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5'.
Note on CM44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CM48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CU17: C. Hill (9/17/99): Reviewer verified feed and permeate TDS values (which differ significantly from those reported in operational data) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity with an average TDS conversion factor.
Note on CU33: C. Hill (9/17/99): Reviewer verified permeate CHCl3 values for Week 4 using Summary Report (Exhibit 3).
Note on CU38: C. Hill (9/17/99): Reviewer verified all reported HAA permeate values using analytical reports contained in the Summary Report (Exhibit 3).
Note on CW29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CW31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CX26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.1'.
Note on CX27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CX30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.88'.
Note on CX31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CX32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '353'.
Note on CX33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '27'.
Note on CX34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '21'.
Note on CX35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '14'.
Note on CX36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '62'.
Note on CX38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '12'.
Note on CX40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.9'.
Note on CX41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '15.9'.
Note on CX48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '15.9'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DF17: C. Hill (9/17/99): Reviewer verified feed and permeate TDS values (which differ significantly from those reported in operational data) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity with an average TDS conversion factor.
Note on DF33: C. Hill (9/17/99): Reviewer verified permeate CHCl3 values for Week 4 using Summary Report (Exhibit 3).
Note on DF38: C. Hill (9/17/99): Reviewer verified all reported HAA permeate values using analytical reports contained in the Summary Report (Exhibit 3).
Note on DH29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on DH31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on DI26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.2'.
Note on DI27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI29: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on DI30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.94'.
Note on DI31: DPATTON: This value is measured by lab. It was initially given as target value to achieve. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on DI32: C. Hill (9/15/99): Feed SDS-DBPs were evaluated under a combined chlorine-chloramine residual. This data is invalid for use with the ICR base analysis. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '322'.
Note on DI33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '31'.
Note on DI34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8'.
Note on DI35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.3'.
Note on DI36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '16'.
Note on DI37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '60.3'.
Note on DI38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '18'.
Note on DI40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.5'.
Note on DI41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on DI44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23.5'.
Note on DI48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25.3'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR5: C. Hill (9/15/99): This data was copied by the reviewer from field 4-12 of the NF70 data collection spreadsheet.

## FldSys. 3rd Quarter
FIELD-SET 3: 3rd QUARTER SEBST RESULTS (FILE: Fluid Sys.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: SEBST Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 3-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 3-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 3-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 3-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [19 empty] | 0.70222 |  | 13.0385 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale |  | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 70 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL5360313 | Membrane trade name | Spiral-Wound Reverse Osmosis Element | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.25077 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale | DAYS | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | TFCS 4921S |  |  | LSI | 0.14 | Hydrochloric acid addition | pH = 6.7 | Pilot-scale | 1 | 1998-12-17 | 15:00 | 0 | 26 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.1555 | 53.8445 | 0.21642 | 5.8 | 6.5 | 6.7 | 159.5 | 453.2 | 1171.5 | 1138.5 | 2.8169 | 64.8058 | 1075.0463 | 85.1634 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.26 |  |  |  | 1 | 1998-12-17 | 21:00 | 6 | 25.4 | 63 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8615 | 10.0299 | 52.4701 | 0.22606 | 5.9 | 6.5 | 6.8 | 130.9 | 452.65 | 1199 | 1203.4 | -0.36697 | 71.0814 | 1133.8861 | 88.4556 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.35 |  |  |  | 2 | 1998-12-18 | 3:00 | 12 | 24.8 | 63 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0737 | 10.3213 | 52.1787 | 0.23139 | 5.9 | 6.5 | 6.8 | 130.9 | 462 | 1193.5 | 1234.5667 | -3.4409 | 71.6667 | 1163.0327 | 88.7449 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 2 | 1998-12-18 | 9:30 | 18.5 | 26 | 64 | 62 | 0 | 4.4 | 0.7 | 0.25 |  | 0.95 | 5.35 | 0.32565 | 0.73684 | 4.6316 | 12.9231 | 11.6529 | 8.5163 | 54.4837 | 0.21388 | 5.9 | 6.5 | 6.8 | 205.15 | 444.95 | 1925 | 1116.39 | 42.0057 | 53.8937 | 1056.7762 | 80.5872 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-1 (dup) | CF-1 (dup) | CC-1 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophyllic | Permeate flow rate, Qp (gpm) | 0.8125 | Total aluminum (mg/L) | 0.11 |  |  |  | 2 | 1998-12-18 | 15:00 | 24 | 27 | 65 | 63 | 0 | 4.4 | 0.75 | 0.29 |  | 1.04 | 5.44 | 0.32988 | 0.72115 | 4.2308 | 13.8462 | 12.1216 | 11.3125 | 52.6875 | 0.23007 | 6 | 6.4 | 6.8 | 134.75 | 473.55 | 1193.5 | 1349.7569 | -13.0923 | 71.5447 | 1266.0018 | 89.3563 | [16 empty] | Sampling date | MM/DD/YY | 1998-12-22 | 1998-12-22 | 1998-12-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-30 | 1998-12-30 | 1998-12-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-06 | 1999-01-06 | 1999-01-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-12 | 1999-01-12 | 1999-01-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-12 | 1999-01-12 | 1999-01-12 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.0833 | Fluoride (mg/L) | 0.41 |  |  |  | 2 | 1998-12-18 | 21:00 | 30 | 25.5 | 64 | 62 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.1216 | 10.5402 | 52.4598 | 0.23107 | 6 | 6.5 | 6.9 | 117.15 | 440.55 | 1116.5 | 1249.05 | -11.8719 | 73.4082 | 1171.167 | 89.9972 | [16 empty] | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27083 | Phosphate (mg/L) | 0.098 |  |  |  | 3 | 1998-12-19 | 3:00 | 36 | 24.9 | 64 | 62 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.6712 | 10.7732 | 52.2268 | 0.24262 | 6 | 6.5 | 6.8 | 129.25 | 459.8 | 1199 | 1286.175 | -7.2706 | 71.89 | 1206.5701 | 89.2878 | [16 empty] | Operation time | hh.hh | 116 | 116 | 116 | --- | --- | --- | --- | --- | Operation time | hh.hh | 308 | 308 | 308 | --- | --- | --- | --- | --- | Operation time | hh.hh | 478 | 478 | 478 | --- | --- | --- | --- | --- | Operation time | hh.hh | 618 | 618 | 618 | --- | --- | --- | --- | --- | Operation time | hh.hh | 618 | 618 | 618 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 31 |  |  |  | 3 | 1998-12-19 | 9:00 | 42 | 26.2 | 64 | 63 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.8979 | 10.2354 | 53.2646 | 0.24215 | 5.9 | 6.4 | 6.9 | 114.95 | 429 | 932.25 | 1214.125 | -30.236 | 73.2051 | 1138.4937 | 89.9033 | [16 empty] | pH | --- | 6.41 | 7.02 | 7.3 | --- | --- | --- | --- | --- | pH | --- | 6.43 | 6.94 | 7.14 | --- | --- | --- | --- | --- | pH | --- | 6.19 | 6.63 | 6.95 | --- | --- | --- | --- | --- | pH | --- | 6.61 | 7.06 | 7.31 | --- | --- | --- | --- | --- | pH | --- | 6.57 | 7.01 | 7.28 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 10 | Calcium (mg/L) | 83 |  |  |  | 3 | 1998-12-19 | 21:00 | 54 | 26 | 63 | 61 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.4117 | 10.1817 | 51.8183 | 0.23952 | 6 | 6.6 | 6.9 | 125.95 | 438.35 | 1144 | 1219.35 | -6.5865 | 71.2673 | 1144.1161 | 88.9915 | [16 empty] | Temperature | oC | 27 | 27 | 27 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 27 | 27 | 27 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | 24 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.016 |  |  |  | 4 | 1998-12-20 | 3:00 | 60 | 25.7 | 64 | 61 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.4853 | 10.5043 | 51.9957 | 0.24012 | 6 | 6.5 | 6.9 | 119.35 | 441.65 | 1098.9 | 1247.4 | -13.5135 | 72.9763 | 1169.7819 | 89.7972 | [16 empty] | Alkalinity | mg/L as CaCO3 | 54 | 200 | 530 | 540.6667 | -2.0126 | 73 | 509.1235 | 89.3935 | Alkalinity | mg/L as CaCO3 | 47 | 210 | 570 | 590.3333 | -3.5673 | 77.619 | 555.1173 | 91.5333 | Alkalinity | mg/L as CaCO3 | 54 | 200 | 460 | 51.8841 | 88.7209 | 73 | 65.5985 | 17.681 | Alkalinity | mg/L as CaCO3 | 55 | 230 | 580 | 638.3333 | -10.0575 | 76.087 | 600.5247 | 90.8413 | Alkalinity | mg/L as CaCO3 | 52 | 220 | 560 | 612 | -9.2857 | 76.3636 | 575.7037 | 90.9676 | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Design recycle flow rate, QR (gpm) | 4.4167 | Strontium (mg/L) | 0.13 |  |  |  | 4 | 1998-12-20 | 8:40 | 65.6667 | 26.1 | 63 | 61 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.5965 | 10.2892 | 51.7108 | 0.2436 | 6 | 6.5 | 6.8 | 116.05 | 431.75 | 1090.1 | 1221 | -12.0081 | 73.121 | 1144.9713 | 89.8644 | [16 empty] | Total dissolved solids | mg/L | 100 | 410 | 1200 | 1133.3333 | 5.5556 | 75.6098 | 1066.358 | 90.6223 | Total dissolved solids | mg/L | 97 | 470 | 1200 | 1340.3333 | -11.6944 | 79.3617 | 1259.7469 | 92.3 | Total dissolved solids | mg/L | 120 | 500 | 1300 | 114.4928 | 91.1929 | 76 | 150.1879 | 20.1001 | Total dissolved solids | mg/L | 100 | 460 | 1200 | 1300 | -8.3333 | 78.2609 | 1222.2222 | 91.8182 | Total dissolved solids | mg/L | 100 | 450 | 1100 | 1266.6667 | -15.1515 | 77.7778 | 1191.0494 | 91.604 | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Recycle ratio, r | 4.0769 | Reactive silica (mg/L as SiO2) | 34 |  |  |  | 4 | 1998-12-20 | 21:00 | 78 | 26 | 62 | 60 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.4484 | 10.0562 | 50.9438 | 0.24436 | 6 | 6.5 | 6.9 | 134.2 | 442.75 | 1138.5 | 1214.125 | -6.6425 | 69.6894 | 1139.8182 | 88.2262 | [16 empty] | Total hardness | mg/L as CaCO3 | 44 | 290 | 820 | 864 | -5.3659 | 84.8276 | 810.8519 | 94.5736 | Total hardness | mg/L as CaCO3 | 40 | 290 | 770 | 873.3333 | -13.4199 | 86.2069 | 819.321 | 95.1179 | Total hardness | mg/L as CaCO3 | 46 | 290 | 900 | 42.4638 | 95.2818 | 84.1379 | 65.3838 | 29.6462 | Total hardness | mg/L as CaCO3 | 48 | 290 | 780 | 854.6667 | -9.5726 | 83.4483 | 802.3827 | 94.0178 | Total hardness | mg/L as CaCO3 | 47 | 290 | 780 | 857 | -9.8718 | 83.7931 | 804.5 | 94.1579 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | NR |  |  |  | 5 | 1998-12-21 | 3:00 | 84 | 25.8 | 62 | 60 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.4853 | 10.3788 | 50.6212 | 0.24664 | 6 | 6.5 | 6.9 | 122.1 | 440.55 | 1144 | 1236.675 | -8.101 | 72.2846 | 1159.9841 | 89.474 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 35 | 230 | 640 | 685 | -7.0312 | 84.7826 | 642.8704 | 94.5557 | Calcium hardness | mg/L as CaCO3 | 32 | 230 | 630 | 692 | -9.8413 | 86.087 | 649.2222 | 95.071 | Calcium hardness | mg/L as CaCO3 | 34 | 220 | 720 | 31.3043 | 95.6522 | 84.5455 | 48.7762 | 30.2938 | Calcium hardness | mg/L as CaCO3 | 37 | 230 | 620 | 680.3333 | -9.7312 | 83.913 | 638.6358 | 94.2064 | Calcium hardness | mg/L as CaCO3 | 36 | 220 | 610 | 649.3333 | -6.4481 | 83.6364 | 609.5802 | 94.0943 | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 3.2 |  |  |  | 5 | 1998-12-21 | 9:00 | 90 | 26 | 62 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.3966 | 12.7908 | 48.2092 | 0.27789 | 5.8 | 6.3 | 6.9 | 145.2 | 521.4 | 1105.5 | 1524.6 | -37.9104 | 72.1519 | 1424.28 | 89.8054 | [16 empty] | Turbidity | ntu | BMRL | 15 | 1.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 23 | 21 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.6 | 1.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 24 | 0.48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 28 | 0.57 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 5 | 1998-12-21 | 21:00 | 102 | 26.5 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.5669 | 45.4331 | 0.25649 | 6 | 6.5 | 6.9 | 128.15 | 435.05 | 1076.35 | 1151.15 | -6.9494 | 70.5436 | 1084.8444 | 88.1872 | [16 empty] | Ammonia | mg NH3-N / L | 0.21 | 0.41 | 0.79 | 0.87667 | -10.9705 | 48.7805 | 0.83346 | 74.8037 | Ammonia | mg NH3-N / L | 0.23 | 0.39 | 0.77 | 0.76333 | 0.8658 | 41.0256 | 0.72877 | 68.4398 | Ammonia | mg NH3-N / L | 0.28 | 0.54 | 1 | 0.27623 | 72.3768 | 48.1481 | 0.30065 | 6.87 | Ammonia | mg NH3-N / L | 0.21 | 0.52 | 1.1 | 1.2433 | -13.0303 | 59.6154 | 1.1764 | 82.1483 | Ammonia | mg NH3-N / L | 0.26 | 0.52 | 1 | 1.1267 | -12.6667 | 50 | 1.0705 | 75.7121
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 6 | 1998-12-22 | 1:00 | 106 | 25.5 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.482 | 9.4641 | 44.5359 | 0.25781 | 6.2 | 6.7 | 6.9 | 137.5 | 441.1 | 1081.85 | 1149.5 | -6.2532 | 68.8279 | 1083.9074 | 87.3144 | [16 empty] | Total organic carbon | mg/L | BMRL | 6 | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.5 | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.4 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.9 | 6.2 | 17 | 16.2333 | 4.5098 | 69.3548 | 15.3043 | 87.5852 | Total organic carbon | mg/L | BMRL | 6.2 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 12.67 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 6 | 1998-12-22 | 11:00 | 116 | 27 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8264 | 9.4469 | 44.5531 | 0.26545 | 6.1 | 6.5 | 6.8 | 134.2 | 437.25 | 1036.2 | 1144.3667 | -10.4388 | 69.3082 | 1078.8929 | 87.5613 | [16 empty] | UV254 | cm-1 | 0.022 | 0.21 | 0.6 | 0.64867 | -8.1111 | 89.5238 | 0.60805 | 96.3819 | UV254 | cm-1 | 0.02 | 0.24 | 0.64 | 0.75333 | -17.7083 | 91.6667 | 0.7058 | 97.1663 | UV254 | cm-1 | 0.029 | 0.21 | 0.57 | 0.026377 | 95.3725 | 86.1905 | 0.043379 | 33.1473 | UV254 | cm-1 | 0.043 | 0.26 | 0.66 | 0.76633 | -16.1111 | 83.4615 | 0.71945 | 94.0232 | UV254 | cm-1 | 0.043 | 0.26 | 0.64 | 0.76633 | -19.7396 | 83.4615 | 0.71945 | 94.0232
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0027 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 6 | 1998-12-22 | 21:00 | 126 | 25.7 | 54 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.7384 | 43.7616 | 0.25853 | 6 | 6.6 | 6.9 | 124.3 | 436.7 | 1005.4 | 1165.6333 | -15.9373 | 71.5365 | 1098.1395 | 88.6809 | [16 empty] | SUVA | L/(mg*m) | NR | 3.5 | 3.5294 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.6923 | 3.7647 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.2812 | 3.5625 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.2632 | 4.1935 | 3.8824 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.1935 | 4 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 7 | 1998-12-23 | 3:00 | 132 | 24.9 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.7567 | 9.4812 | 42.5188 | 0.27651 | 6.2 | 6.5 | 6.9 | 134.75 | 438.9 | 1031.25 | 1148.5833 | -11.3778 | 69.2982 | 1082.8719 | 87.5562 | [16 empty] | Bromide | mg/L | 82 | 250 | 0.61 | 642 | --- | 67.2 | 605.7037 | 86.462 | Bromide | mg/L | 64 | 220 | 0.56 | 584 | --- | 70.9091 | 550.2963 | 88.3699 | Bromide | mg/L | 79 | 260 | 640 | 76.3768 | --- | 69.6154 | 93.379 | 15.3985 | Bromide | mg/L | 73 | 240 | 620 | 629.6667 | --- | 69.5833 | 593.5864 | 87.7019 | Bromide | mg/L | 78 | 230 | 600 | 584.6667 | --- | 66.087 | 551.8272 | 85.8651
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 7 | 1998-12-23 | 8:30 | 137.5 | 27 | 54 | 51 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.32727 | 0.68421 | 4.6316 | 12 | 11.1782 | 9.2754 | 43.2246 | 0.25861 | 6 | 6.4 | 6.8 | 121 | 432.85 | 1016.95 | 1108.525 | -9.0049 | 72.0457 | 1048.5352 | 88.4601 | [16 empty] | SDS-Cl2 dose | mg/L | 16 | 14 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 12 | 14 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 19 | 28 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 14 | 12 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 14 | 13 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1152.638 | [5 empty] | 7 | 1998-12-23 | 21:00 | 150 | 26.2 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.7212 | 42.2788 | 0.26759 | 6 | 6.5 | 6.9 | 123.2 | 435.05 | 987.25 | 1162.7 | -17.7716 | 71.6814 | 1095.325 | 88.7522 | [16 empty] | SDS-Free Cl2 residual | mg/L | 1.2 | 0.75 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | 0.66 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.4 | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.2 | 0.83 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.4 | 0.73 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 202.454 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 8 | 1998-12-24 | 3:00 | 156 | 25.4 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.5843 | 9.6184 | 42.3816 | 0.27333 | 6.1 | 6.5 | 6.9 | 133.65 | 442.2 | 1035.1 | 1162.15 | -12.2742 | 69.7761 | 1095.488 | 87.8 | [16 empty] | SDS-Cl2 demand | mg/L | 14.8 | 13.25 | --- | 9.6333 | --- | -11.6981 | 9.9682 | -48.472 | SDS-Cl2 demand | mg/L | 10.7 | 13.34 | --- | 19.5 | --- | 19.7901 | 18.9296 | 43.4749 | SDS-Cl2 demand | mg/L | 17.6 | 27 | --- | 17.4638 | --- | 34.8148 | 18.3468 | 4.0702 | SDS-Cl2 demand | mg/L | 12.8 | 11.17 | --- | 7.3667 | --- | -14.5927 | 7.7188 | -65.8283 | SDS-Cl2 demand | mg/L | 12.6 | 12.27 | --- | 11.5 | --- | -2.6895 | 11.5713 | -8.8901
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | 1 | Influent TDS, TDSI (mg/L) | 1012.2699 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 8 | 1998-12-24 | 9:00 | 162 | 26 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8615 | 8.6411 | 42.3589 | 0.28002 | 5.9 | 6.5 | 6.8 | 156.2 | 433.4 | 980.65 | 1080.2 | -10.1514 | 63.9594 | 1020.3111 | 84.6909 | [16 empty] | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 8 | 1998-12-24 | 18:00 | 171 | 27.5 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.0697 | 46.9303 | 0.2483 | 6.1 | 6.6 | 7 | 139.15 | 430.1 | 1068.65 | 1108.9833 | -3.7742 | 67.6471 | 1046.1238 | 86.6985 | [16 empty] | SDS-Chlorination pH | --- | 8.07 | 8.18 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.14 | 7.99 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.08 | 7.99 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.14 | 8.12 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.18 | 8.15 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 10 | [7 empty] | 9 | 1998-12-25 | 5:00 | 182 | 26.1 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 9.104 | 46.896 | 0.23771 | 6.1 | 6.5 | 6.9 | 140.8 | 432.85 | 1078.55 | 1114.3 | -3.3146 | 67.4714 | 1051.2028 | 86.6058 | [16 empty] | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 9 | 1998-12-25 | 9:00 | 186 | 27 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6185 | 9.6184 | 46.3816 | 0.2505 | 5.8 | 6.5 | 6.9 | 133.65 | 442.2 | 1068.65 | 1162.15 | -8.7494 | 69.7761 | 1095.488 | 87.8 | [16 empty] | SDS-TOX | mg Cl- /L | 52 | 625 | --- | 1962 | --- | 91.68 | 1838.2037 | 97.1712 | SDS-TOX | mg Cl- /L | 38 | 648 | --- | 2071.3333 | --- | 94.1358 | 1939.5432 | 98.0408 | SDS-TOX | mg Cl- /L | 105 | 1020 | --- | 91.7391 | --- | 89.7059 | 177.6892 | 40.9081 | SDS-TOX | mg Cl- /L | 98 | 599 | --- | 1768 | --- | 83.6394 | 1659.7593 | 94.0955 | SDS-TOX | mg Cl- /L | 94 | 656 | --- | 1967.3333 | --- | 85.6707 | 1845.9136 | 94.9077
|  | Rejection of reference solute and conditions of test | NaCl 500 mg/L | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 9 | 1998-12-25 | 21:00 | 198 | 25.8 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.7898 | 46.2102 | 0.24483 | 6 | 6.5 | 6.8 | 123.2 | 437.25 | 1024.65 | 1170.0333 | -14.1886 | 71.8239 | 1102.183 | 88.8222 | [16 empty] | SDS-CHCl3 | mg/L | 5.2 | 110 | --- | 354.5333 | --- | 95.2727 | 331.8914 | 98.4332 | SDS-CHCl3 | mg/L | 3.6 | 160 | --- | 524.9333 | --- | 97.75 | 491.1432 | 99.267 | SDS-CHCl3 | mg/L | 8.1 | 140 | --- | 6.1884 | --- | 94.2143 | 18.5784 | 56.4009 | SDS-CHCl3 | mg/L | 16 | 140 | --- | 429.3333 | --- | 88.5714 | 402.5432 | 96.0253 | SDS-CHCl3 | mg/L | 17 | 130 | --- | 393.6667 | --- | 86.9231 | 369.2531 | 95.3961
|  | (e.g., solute type and concentration) | 85 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 10 | 1998-12-26 | 3:00 | 204 | 25.4 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.722 | 9.6184 | 46.3816 | 0.25273 | 6 | 6.4 | 6.9 | 130.9 | 439.45 | 1076.9 | 1159.4 | -7.6609 | 70.2128 | 1092.738 | 88.0209 | [16 empty] | SDS-BDCM | mg/L | 6.3 | 80 | --- | 251.9667 | --- | 92.125 | 236.0438 | 97.331 | SDS-BDCM | mg/L | 5.4 | 68 | --- | 214.0667 | --- | 92.0588 | 200.542 | 97.3073 | SDS-BDCM | mg/L | 12 | 70 | --- | 11.1594 | --- | 82.8571 | 16.6076 | 27.744 | SDS-BDCM | mg/L | 15 | 63 | --- | 175 | --- | 76.1905 | 164.6296 | 90.8886 | SDS-BDCM | mg/L | 15 | 59 | --- | 161.6667 | --- | 74.5763 | 152.1605 | 90.142
|  | Variability of rejection of reference solute (%) | +/-15.0 | Required influent pressure, PI (psi) | 70.6164 | [5 empty] | 10 | 1998-12-26 | 8:45 | 209.75 | 26.1 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8615 | 9.8241 | 46.1759 | 0.25688 | 6 | 6.6 | 6.8 | 105.6 | 420.75 | 1085.7 | 1156.1 | -6.4843 | 74.902 | 1088.012 | 90.2942 | [16 empty] | SDS-DBCM | mg/L | 8.3 | 32 | --- | 87.3 | --- | 74.0625 | 82.1796 | 89.9002 | SDS-DBCM | mg/L | 7.1 | 21 | --- | 53.4333 | --- | 66.1905 | 50.4302 | 85.9211 | SDS-DBCM | mg/L | 14 | 30 | --- | 13.7681 | --- | 53.3333 | 15.2711 | 8.3234 | SDS-DBCM | mg/L | 14 | 20 | --- | 34 | --- | 30 | 32.7037 | 57.1914 | SDS-DBCM | mg/L | 15 | 19 | --- | 28.3333 | --- | 21.0526 | 27.4691 | 45.3933
|  | Standard testing recovery (%) | 10 | [7 empty] | 10 | 1998-12-26 | 21:00 | 222 | 25.6 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6185 | 9.4812 | 43.5188 | 0.26698 | 6 | 6.5 | 6.8 | 128.15 | 432.3 | 1007.6 | 1141.9833 | -13.337 | 70.3562 | 1076.2719 | 88.0932 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 1.4 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 2.5 | 2.4 | --- | 2.5014 | --- | -4.1667 | 2.4921 | -0.31878 | SDS-CHBr3 | mg/L | 6.2 | 1.1 | --- | -10.8 | --- | -463.6364 | -9.6981 | 163.9297 | SDS-CHBr3 | mg/L | 7.7 | 2.9 | --- | -8.3 | --- | -165.5172 | -7.263 | 206.0173
|  | Standard testing pH | 7.5 | [7 empty] | 11 | 1998-12-27 | 3:00 | 228 | 25.3 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.7915 | 9.3612 | 43.6388 | 0.27021 | 5.9 | 6.6 | 6.8 | 130.9 | 431.2 | 1068.65 | 1131.9 | -5.9187 | 69.6429 | 1067.0204 | 87.7322 | [16 empty] | SDS-THM4 | mg/L | 19.8 | 222 | --- | 693.8 | --- | 91.0811 | 650.1148 | 96.9544 | SDS-THM4 | mg/L | 17.5 | 249 | --- | 789.1667 | --- | 92.9719 | 739.1512 | 97.6324 | SDS-THM4 | mg/L | 36.6 | 242.4 | --- | 33.6174 | --- | 84.901 | 52.9491 | 30.877 | SDS-THM4 | mg/L | 51.2 | 224.1 | --- | 627.5333 | --- | 77.1531 | 590.1784 | 91.3247 | SDS-THM4 | mg/L | 54.7 | 210.9 | --- | 575.3667 | --- | 74.0635 | 541.6198 | 89.9007
|  | Acceptable range of operating pressures | 0-350 | [7 empty] | 11 | 1998-12-27 | 10:00 | 235 | 26.9 | 53 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8966 | 10.2527 | 42.2473 | 0.28159 | 5.9 | 6.6 | 6.8 | 103.95 | 432.85 | 1030.7 | 1200.2833 | -16.4532 | 75.9848 | 1129.2247 | 90.7946 | [16 empty] | SDS-MCAA* | mg/L | BMRL | 3.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 11 | 1998-12-27 | 18:00 | 243 | 27.8 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.347 | 8.7954 | 44.2046 | 0.25669 | 6.1 | 6.6 | 6.9 | 145.2 | 427.35 | 1041.7 | 1085.7 | -4.2239 | 66.0232 | 1024.7417 | 85.8306 | [16 empty] | SDS-DCAA* | mg/L | 2.1 | 20 | --- | 61.7667 | --- | 89.5 | 57.8994 | 96.373 | SDS-DCAA* | mg/L | 1.3 | 5.9 | --- | 16.6333 | --- | 77.9661 | 15.6395 | 91.6877 | SDS-DCAA* | mg/L | 1.9 | 60 | --- | 1.058 | --- | 96.8333 | 6.5156 | 70.8391 | SDS-DCAA* | mg/L | NR | 79 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | 81 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 3 | [7 empty] | 12 | 1998-12-28 | 3:00 | 252 | 25.8 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.0491 | 8.864 | 44.136 | 0.25034 | 6 | 6.6 | 6.7 | 145.2 | 429.55 | 1042.8 | 1093.0333 | -4.8172 | 66.1972 | 1031.5997 | 85.9248 | [16 empty] | SDS-TCAA* | mg/L | 1.8 | 8.9 | --- | 25.4667 | --- | 79.7753 | 23.9327 | 92.4789 | SDS-TCAA* | mg/L | 2 | 7 | --- | 18.6667 | --- | 71.4286 | 17.5864 | 88.6276 | SDS-TCAA* | mg/L | 1.6 | 48 | --- | 0.92754 | --- | 96.6667 | 5.2861 | 69.7319 | SDS-TCAA* | mg/L | NR | 88 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | 92 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 12 | 1998-12-28 | 9:00 | 258 | 25 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.722 | 8.624 | 48.376 | 0.24231 | 6 | 6.5 | 6.8 | 141.9 | 418.55 | 1001 | 1064.0667 | -6.3004 | 66.0972 | 1004.2966 | 85.8707 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 0 | [7 empty] | 12 | 1998-12-28 | 18:00 | 267 | 27.1 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 8.504 | 45.496 | 0.26381 | 6.1 | 6.5 | 6.9 | 141.35 | 414.15 | 1065.35 | 1050.6833 | 1.3767 | 65.8699 | 991.7451 | 85.7473 | [16 empty] | SDS-DBAA* | mg/L | 8.4 | 13 | --- | 23.7333 | --- | 35.3846 | 22.7395 | 63.0599 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 3.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 8.7 | 11 | --- | 16.3667 | --- | 20.9091 | 15.8698 | 45.1787 | SDS-DBAA* | mg/L | 9.5 | 7.8 | --- | 3.8333 | --- | -21.7949 | 4.2006 | -126.1572
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 13 | 1998-12-29 | 3:00 | 276 | 25.2 | 54 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.2801 | 8.0067 | 45.4933 | 0.24795 | 6.2 | 6.5 | 6.9 | 154.55 | 411.4 | 1078 | 1010.7167 | 6.2415 | 62.4332 | 955.2244 | 83.8206 | [16 empty] | SDS-BCAA* | mg/L | 4.6 | 18 | --- | 49.2667 | --- | 74.4444 | 46.3716 | 90.0801 | SDS-BCAA* | mg/L | BMRL | 3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 3.1 | 19 | --- | 2.8696 | --- | 83.6842 | 4.3631 | 28.95 | SDS-BCAA* | mg/L | 11 | 30 | --- | 74.3333 | --- | 63.3333 | 70.2284 | 84.3368 | SDS-BCAA* | mg/L | 12 | 26 | --- | 58.6667 | --- | 53.8462 | 55.642 | 78.4335
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 13 | 1998-12-29 | 11:00 | 284 | 26 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.9318 | 7.8867 | 45.1133 | 0.26449 | 6 | 6.5 | 6.9 | 133.65 | 386.65 | 981.75 | 976.9833 | 0.48553 | 65.4339 | 922.3228 | 85.5094 | [16 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 13 | 1998-12-29 | 18:00 | 291 | 26.8 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.5669 | 44.4331 | 0.26226 | 6.1 | 6.6 | 7 | 104.5 | 411.4 | 915.2 | 1127.5 | -23.1971 | 74.5989 | 1061.1944 | 90.1526 | [16 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 14 | 1998-12-30 | 5:00 | 302 | 24.9 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3806 | 8.5725 | 45.4275 | 0.25052 | 6.1 | 6.6 | 6.9 | 143 | 418 | 1111 | 1059.6667 | 4.6205 | 65.7895 | 1000.2531 | 85.7036 | [16 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 14 | 1998-12-30 | 11:00 | 308 | 26 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0381 | 7.2352 | 46.7648 | 0.25742 | 6 | 6.5 | 6.9 | 141.9 | 374 | 975.7 | 915.5667 | 6.1631 | 62.0588 | 865.4216 | 83.6034 | [16 empty] | SDS-HAA5 | mg/L | 12.3 | 45.7 | --- | 123.6333 | --- | 73.0853 | 116.4173 | 89.4346 | SDS-HAA5 | mg/L | 3.3 | 12.9 | --- | 35.3 | --- | 74.4186 | 33.2259 | 90.068 | SDS-HAA5 | mg/L | 3.5 | 111.8 | --- | 1.9304 | --- | 96.8694 | 12.1035 | 71.0828 | SDS-HAA5 | mg/L | 8.7 | 178 | --- | 573.0333 | --- | 95.1124 | 536.4562 | 98.3782 | SDS-HAA5 | mg/L | 9.5 | 180.8 | --- | 580.5 | --- | 94.7456 | 543.4907 | 98.252
[11 empty] | 14 | 1998-12-30 | 18:00 | 315 | 26.4 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 8.744 | 46.256 | 0.25192 | 6.1 | 6.7 | 7.1 | 123.2 | 403.7 | 994.4 | 1058.2 | -6.4159 | 69.4823 | 997.5981 | 87.6503 | [16 empty] | SDS-HAA6 | mg/L | 16.9 | 63.7 | --- | 172.9 | --- | 73.4694 | 162.7889 | 89.6185 | SDS-HAA6 | mg/L | 3.3 | 15.9 | --- | 45.3 | --- | 79.2453 | 42.5778 | 92.2495 | SDS-HAA6 | mg/L | 6.6 | 130.8 | --- | 4.8 | --- | 94.9541 | 16.4667 | 59.919 | SDS-HAA6 | mg/L | 19.7 | 208 | --- | 647.3667 | --- | 90.5288 | 606.6846 | 96.7528 | SDS-HAA6 | mg/L | 21.5 | 206.8 | --- | 639.1667 | --- | 89.6035 | 599.1327 | 96.4115
[11 empty] | 15 | 1998-12-31 | 3:00 | 324 | 20.8 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.516 | 8.8811 | 45.1189 | 0.25524 | 6.1 | 6.4 | 7 | 122.65 | 407.55 | 993.85 | 1072.3167 | -7.8952 | 69.9055 | 1010.7642 | 87.8656 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 15 | 1998-12-31 | 10:00 | 331 | 25 | 58 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 13.5891 | 10.1499 | 46.3501 | 0.29318 | 5.9 | 6.4 | 6.9 | 121 | 446.6 | 907.5 | 1206.3333 | -32.9293 | 72.9064 | 1135.9877 | 89.3485 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 15 | 1998-12-31 | 18:00 | 339 | 26.8 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 8.8983 | 49.1017 | 0.24444 | 6 | 6.5 | 6.9 | 129.25 | 414.7 | 1060.4 | 1080.75 | -1.9191 | 68.8329 | 1019.0787 | 87.317
[11 empty] | 16 | 1999-01-01 | 7:00 | 352 | 23.7 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3806 | 8.8811 | 49.1189 | 0.2317 | 6 | 6.5 | 7 | 131.45 | 416.35 | 1067.55 | 1081.1167 | -1.2708 | 68.428 | 1019.5642 | 87.1072 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 16 | 1999-01-01 | 13:00 | 358 | 25.7 | 58 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.4727 | 9.807 | 47.693 | 0.26152 | 6 | 6.6 | 7 | 124.85 | 439.45 | 1018.6 | 1173.5167 | -15.2088 | 71.5895 | 1105.5475 | 88.707 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 16 | 1999-01-01 | 16:00 | 361 | 27 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.7567 | 9.0526 | 48.9474 | 0.24019 | 5.9 | 6.6 | 6.8 | 119.9 | 410.3 | 1020.8 | 1087.9 | -6.5733 | 70.7775 | 1025.1593 | 88.3043 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 17 | 1999-01-02 | 1:00 | 370 | 25 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.4126 | 47.5874 | 0.23774 | 6.1 | 6.4 | 7 | 110.55 | 412.5 | 901.45 | 1117.05 | -23.917 | 73.2 | 1051.8139 | 89.4896 | [16 empty] | Qp/QT (THM4), % | 74.184 | 91.9881 |  | Qp/QT (HAA5), % | -24.8503 | 55.988 |  |  |  | Qp/QT (THM4), % | 76.4579 | 92.0086 |  | Qp/QT (HAA5), % | -428.125 | -146.875 |  |  |  | Qp/QT (THM4), % | 82.7988 | 100.2915 |  | Qp/QT (HAA5), % | 53.3703 | 78.301 |  |  |  | Qp/QT (THM4), % | 87.9699 | 108.7912 |  | Qp/QT (HAA5), % | 73.2428 | 89.1908 |  |  |  | Qp/QT (THM4), % | 88.9245 | 111.9718 |  | Qp/QT (HAA5), % | 74.0222 | 89.784
[11 empty] | 17 | 1999-01-02 | 11:00 | 380 | 26.5 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 9.7555 | 46.2445 | 0.25955 | 5.9 | 6.5 | 6.9 | 93.5 | 406.45 | 898.7 | 1136.6667 | -26.479 | 76.9959 | 1069.054 | 91.2539 | [16 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 108.7922 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 132.564 | 81.2565 |  |  |  | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 97.4633 | 69.8891 |  |  |  | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 95.2773 | 70.6574
[11 empty] | 17 | 1999-01-02 | 17:30 | 386.5 | 27 | 56 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.482 | 8.9669 | 45.5331 | 0.25217 | 5.9 | 6.5 | 6.8 | 119.9 | 407.55 | 928.95 | 1078.7333 | -16.1239 | 70.5803 | 1016.5867 | 88.2056 | [16 empty] | SDS-HAA5b, mg/L | 20.9226 | 14.976 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | 5.56 | 4.0672 |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | 22.1289 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 29.0669 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 28.4724 | NA |  | SDS-HAA5b, mg/L | 54 | 27
[11 empty] | 18 | 1999-01-03 | 3:00 | 396 | 26.8 | 56 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.2926 | 45.2074 | 0.25026 | 6.1 | 6.5 | 6.9 | 110 | 408.1 | 899.25 | 1103.6667 | -22.7319 | 73.0458 | 1039.2623 | 89.4156 | [16 empty] | SDS-TOXb, mg Cl- /L | 199.9258 | 97.908 |  | SDS-TOXb, mg Cl- /L | NA | 304.1886 |  |  |  | SDS-TOXb, mg Cl- /L | 181.6069 | 86.7473 |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | 262.3907 | NA |  | SDS-TOXb, mg Cl- /L | 531.662 | 303.5457 |  |  |  | SDS-TOXb, mg Cl- /L | 158.2707 | NA |  | SDS-TOXb, mg Cl- /L | 232.0538 | 152.1542 |  |  |  | SDS-TOXb, mg Cl- /L | 156.2446 | NA |  | SDS-TOXb, mg Cl- /L | 239.9953 | 151.4139
[11 empty] | 18 | 1999-01-03 | 9:00 | 402 | 26 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3806 | 9.5498 | 45.4502 | 0.2504 | 5.9 | 6.5 | 6.9 | 110 | 416.35 | 917.95 | 1131.1667 | -23.2275 | 73.5799 | 1064.9799 | 89.6712 | [16 empty] | SDS-CDb, mg/L | 14.3999 | 14.6758 |  | SDS-CDb, mg/L | NA | 14.1178 |  |  |  | SDS-CDb, mg/L | 11.3215 | 10.911 |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | 19.2169 | NA |  | SDS-CDb, mg/L | 21.9832 | 19.6397 |  |  |  | SDS-CDb, mg/L | 12.6039 | NA |  | SDS-CDb, mg/L | 12.3639 | 12.6238 |  |  |  | SDS-CDb, mg/L | 12.5635 | NA |  | SDS-CDb, mg/L | 12.5143 | 12.5663
[11 empty] | 18 | 1999-01-03 | 18:00 | 411 | 27.1 | 55 | 54 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.33216 | 0.72727 | 4 | 14.7692 | 13.3176 | 9.6305 | 44.8695 | 0.29681 | 6 | 6.4 | 6.9 | 154.55 | 437.8 | 1090.65 | 1193.1333 | -9.3965 | 64.6985 | 1117.6 | 86.1713 | [16 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | 2.4173 | NA |  | TOCb, mg/L | 3.0506 | 2.3648 |  |  |  | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 19 | 1999-01-04 | 3:00 | 420 | 26.5 | 50 | 48 | 0 | 4.4 | 0.6 | 0.3 |  | 0.9 | 5.3 | 0.32565 | 0.66667 | 4.8889 | 11.0769 | 9.6687 | 8.1099 | 40.8901 | 0.23646 | 6.1 | 6.6 | 6.9 | 154 | 440.55 | 1091.75 | 1013.65 | 7.1537 | 65.0437 | 964.9906 | 84.0413 | [16 empty] | UV254 b, cm-1 | 0.070534 | 0.037062 |  | UV254 b, cm-1 | NA | 0.10474 |  |  |  | UV254 b, cm-1 | 0.071793 | 0.037581 |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | 0.060134 | NA |  | UV254 b, cm-1 | 0.1134 | 0.068275 |  |  |  | UV254 b, cm-1 | 0.069105 | NA |  | UV254 b, cm-1 | 0.10106 | 0.066456 |  |  |  | UV254 b, cm-1 | 0.067034 | NA |  | UV254 b, cm-1 | 0.099372 | 0.065169
[11 empty] | 19 | 1999-01-04 | 10:30 | 427.5 | 24 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.482 | 8.8983 | 44.1017 | 0.26035 | 6.1 | 6.6 | 7 | 142.45 | 427.9 | 1042.25 | 1093.95 | -4.9604 | 66.7095 | 1032.2787 | 86.2004 | [16 empty] | Bromideb, mg/L | 125.3709 | 95.4599 |  | Bromideb, mg/L | NA | 155.9401 |  |  |  | Bromideb, mg/L | 100.7257 | 76.4665 |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | 110.1341 | NA |  | Bromideb, mg/L | 163.3998 | 118.2752 |  |  |  | Bromideb, mg/L | 93.0902 | NA |  | Bromideb, mg/L | 117.6846 | 91.0514 |  |  |  | Bromideb, mg/L | 94.8348 | NA |  | Bromideb, mg/L | 117.4863 | 93.5283
[11 empty] | 19 | 1999-01-04 | 18:00 | 435 | 25.6 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 9.5155 | 48.4845 | 0.25498 | 6.1 | 6.5 | 7 | 123.75 | 429 | 1070.3 | 1141.25 | -6.629 | 71.1538 | 1075.3009 | 88.4916 | [16 empty] | Alkb, mg/L CaCO3 | 91.6914 | 65.6973 |  | Alkb, mg/L CaCO3 | NA | 118.2575 |  |  |  | Alkb, mg/L CaCO3 | 85.3737 | 60.0259 |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | 79.1137 | NA |  | Alkb, mg/L CaCO3 | 122.0794 | 85.6805 |  |  |  | Alkb, mg/L CaCO3 | 76.0526 | NA |  | Alkb, mg/L CaCO3 | 101.8252 | 73.9161 |  |  |  | Alkb, mg/L CaCO3 | 70.6069 | NA |  | Alkb, mg/L CaCO3 | 95.6427 | 69.1629
[11 empty] | 20 | 1999-01-05 | 3:00 | 444 | 21.7 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.7915 | 9.2069 | 48.7931 | 0.24166 | 6.1 | 6.7 | 7 | 138.05 | 433.4 | 1081.3 | 1122.55 | -3.8149 | 68.1472 | 1058.7398 | 86.9609 | [16 empty] | T-Hdb, mg/L CaCO3 | 107.5074 | 63.7092 |  | T-Hdb, mg/L CaCO3 | NA | 152.2695 |  |  |  | T-Hdb, mg/L CaCO3 | 98.8553 | 59.9784 |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | 87.9708 | NA |  | T-Hdb, mg/L CaCO3 | 159.7765 | 98.9455 |  |  |  | T-Hdb, mg/L CaCO3 | 77.1128 | NA |  | T-Hdb, mg/L CaCO3 | 112.7525 | 74.1583 |  |  |  | T-Hdb, mg/L CaCO3 | 73.9136 | NA |  | T-Hdb, mg/L CaCO3 | 110.1261 | 71.8249
[11 empty] | 20 | 1999-01-05 | 13:00 | 454 | 24 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 13.2323 | 10.0299 | 47.9701 | 0.27584 | 6 | 6.5 | 6.8 | 128.15 | 449.9 | 1078.55 | 1200.65 | -11.3208 | 71.5159 | 1131.1361 | 88.6707 | [16 empty] | Ca-Hdb, mg/L CaCO3 | 85.3412 | 50.6231 |  | Ca-Hdb, mg/L CaCO3 | NA | 120.8234 |  |  |  | Ca-Hdb, mg/L CaCO3 | 78.6134 | 47.8229 |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | 65.9942 | NA |  | Ca-Hdb, mg/L CaCO3 | 120.7313 | 74.3601 |  |  |  | Ca-Hdb, mg/L CaCO3 | 60.218 | NA |  | Ca-Hdb, mg/L CaCO3 | 88.6415 | 57.8618 |  |  |  | Ca-Hdb, mg/L CaCO3 | 56.379 | NA |  | Ca-Hdb, mg/L CaCO3 | 83.7992 | 54.7974
[11 empty] | 20 | 1999-01-05 | 18:00 | 459 | 25 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 9.6527 | 48.3473 | 0.2557 | 6.1 | 6.4 | 6.9 | 141.35 | 451 | 1086.8 | 1173.5167 | -7.9791 | 68.6585 | 1106.617 | 87.2268 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 21 | 1999-01-06 | 1:00 | 466 | 20.7 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 9.4984 | 49.5016 | 0.24247 | 6.1 | 6.6 | 6.9 | 146.3 | 451 | 1111 | 1161.9667 | -4.5875 | 67.561 | 1096.1364 | 86.6531 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 21 | 1999-01-06 | 13:00 | 478 | 25.4 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 13.6293 | 9.807 | 47.193 | 0.2888 | 6 | 6.4 | 6.8 | 140.25 | 454.85 | 1105.5 | 1188.9167 | -7.5456 | 69.1657 | 1120.9475 | 87.4883 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 21 | 1999-01-06 | 18:00 | 483 | 26.1 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8615 | 9.1212 | 47.8788 | 0.24774 | 6.1 | 6.4 | 6.8 | 159.5 | 452.1 | 1127.5 | 1134.8333 | -0.65041 | 64.7202 | 1071.6173 | 85.116 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 22 | 1999-01-07 | 1:00 | 490 | 25.7 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6185 | 9.2583 | 47.7417 | 0.24336 | 6 | 6.5 | 6.8 | 153.45 | 450.45 | 1116.5 | 1143.45 | -2.4138 | 65.9341 | 1079.2833 | 85.7822 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 22 | 1999-01-07 | 9:50 | 498.8333 | 24.4 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.7567 | 9.9784 | 47.0216 | 0.25003 | 6 | 6.4 | 6.8 | 102.85 | 422.95 | 1020.8 | 1169.85 | -14.6013 | 75.6827 | 1100.6926 | 90.6559 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 22 | 1999-01-07 | 18:00 | 507 | 27.4 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.2173 | 9.2755 | 47.7245 | 0.256 | 6 | 6.3 | 6.8 | 139.7 | 437.25 | 1059.85 | 1131.5333 | -6.7635 | 68.0503 | 1067.2478 | 86.9103 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 23 | 1999-01-08 | 1:00 | 514 | 22.7 | 58 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1806 | 9.2926 | 47.7074 | 0.23436 | 5.9 | 6.5 | 6.8 | 140.25 | 438.35 | 1065.35 | 1133.9167 | -6.4361 | 68.005 | 1069.5123 | 86.8865 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 23 | 1999-01-08 | 10:00 | 523 | 25.2 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.8469 | 10.2013 | 45.7987 | 0.28051 | 6.1 | 6.6 | 6.8 | 101.2 | 428.45 | 1002.65 | 1192.0333 | -18.8883 | 76.38 | 1121.3312 | 90.975 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 23 | 1999-01-08 | 17:30 | 530.5 | 26.2 | 56 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.9318 | 8.3668 | 46.1332 | 0.25864 | 6.2 | 6.6 | 6.9 | 145.75 | 414.15 | 1003.2 | 1040.4167 | -3.7098 | 64.8074 | 982.429 | 85.1643 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 24 | 1999-01-09 | 1:00 | 538 | 23.8 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.5843 | 8.6583 | 46.3417 | 0.24997 | 6 | 6.6 | 7 | 144.65 | 422.4 | 1004.85 | 1070.4833 | -6.5317 | 65.7552 | 1010.4756 | 85.685 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 24 | 1999-01-09 | 13:00 | 550 | 26.8 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.4359 | 9.5669 | 44.4331 | 0.27988 | 6 | 6.5 | 6.9 | 112.75 | 419.65 | 802.45 | 1135.75 | -41.5353 | 73.1324 | 1069.4444 | 89.4571
[11 empty] | 24 | 1999-01-09 | 16:15 | 553.25 | 26.5 | 54 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3806 | 8.9669 | 45.0331 | 0.25272 | 6 | 6.6 | 6.8 | 132.55 | 420.2 | 993.85 | 1091.3833 | -9.8137 | 68.4555 | 1029.2367 | 87.1215
[11 empty] | 25 | 1999-01-10 | 3:00 | 564 | 23.6 | 54 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.482 | 9.0012 | 44.4988 | 0.25803 | 6.1 | 6.6 | 6..8 | 130.9 | 419.65 | 996.6 | 1093.4 | -9.713 | 68.8073 | 1031.0157 | 87.3038
[11 empty] | 25 | 1999-01-10 | 12:30 | 573.5 | 25.8 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.5096 | 9.3612 | 45.6388 | 0.2741 | 6.1 | 6.6 | 7 | 111.1 | 411.4 | 1015.85 | 1112.1 | -9.4748 | 72.9947 | 1047.2204 | 89.391
[11 empty] | 25 | 1999-01-10 | 18:00 | 579 | 26.4 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.722 | 8.744 | 46.256 | 0.25342 | 6.1 | 6.6 | 7 | 138.6 | 419.1 | 969.1 | 1073.6 | -10.7832 | 66.9291 | 1012.9981 | 86.3178
[11 empty] | 26 | 1999-01-11 | 3:00 | 588 | 22.8 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.516 | 8.7783 | 46.2217 | 0.24915 | 6.1 | 6.6 | 7 | 136.4 | 418 | 960.3 | 1075.0667 | -11.9511 | 67.3684 | 1014.2272 | 86.5513
[11 empty] | 26 | 1999-01-11 | 9:00 | 594 | 23 | 58 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.809 | 9.104 | 48.396 | 0.26467 | 6.1 | 6.4 | 6.8 | 119.35 | 411.4 | 968.55 | 1092.85 | -12.8336 | 70.9893 | 1029.7528 | 88.4098
[11 empty] | 26 | 1999-01-11 | 18:00 | 603 | 26.6 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.7335 | 8.744 | 49.256 | 0.25852 | 6.1 | 6.6 | 7 | 139.7 | 420.2 | 998.25 | 1074.7 | -7.6584 | 66.7539 | 1014.0981 | 86.2242
[11 empty] | 27 | 1999-01-12 | 3:00 | 612 | 24.5 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.4481 | 8.744 | 49.256 | 0.23242 | 6.2 | 6.6 | 7 | 139.15 | 419.65 | 993.3 | 1074.15 | -8.1395 | 66.8414 | 1013.5481 | 86.271
[11 empty] | 27 | 1999-01-12 | 9:00 | 618 | 24 | 58 | 57 | 0 | 4.4 | 0.7 | 0.3 | X | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.1812 | 7.2009 | 50.2991 | 0.24218 | 6.1 | 6.5 | 6.8 | 161.7 | 392.7 | 977.9 | 931.7 | 4.7244 | 58.8235 | 881.7926 | 81.6624
0.21388
0.29681
0.25366
[31 empty] | initial | 0.21642
[31 empty] | final | 0.24218
[31 empty] | after cleaning | 0.23228
Note on Q3: TSC_ADM: Consultant noted that water treatment plant staff measured the influent temperature and the membrane operating parameters, and attributed the wide temperature fluctuations and erratic operational data to measurement error.
Note on AA86: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on BN17: C. Hill (9/21/99): All weekly TOC data was verified by reviewer using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on BP26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on BP29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on BP31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on BQ26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on BQ29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on BQ31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on BQ39: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3.
Note on BQ40: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3.
Note on BY15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on BY17: C. Hill (9/21/99): All weekly TOC data was verified by reviewer using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on CA26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CA29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CA31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CB26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CB29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CB31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CB39: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3. DPATTON: Lab error suspected, due to low chlorine residual maintained, could contribute to low DCAA & TCAA values.
Note on CB40: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3. DPATTON: Lab error suspected, due to low chlorine residual maintained, could contribute to low DCAA & TCAA values.
Note on CJ15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on CJ16: C. Hill (9/21/99): All feed, permeate and concentrate values were verified by reviewer using Summary Report - Exhibit 3. Values were reported correctly, and the summary report provides no possible explanation for the high mass balance closure errors for this week.
Note on CJ17: C. Hill (9/21/99): All weekly TOC data was verified by reviewer using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on CL29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CL31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CM29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CM31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CM32: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3.
Note on CU15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on CU17: C. Hill (9/21/99): All weekly TOC data was verified by reviewer using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on CW26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CW29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CW31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CW39: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3. Lab error suspected. Lab reported values are final, reporting values as NR as instructed.
Note on CW40: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3. Lab error suspected. Lab reported values are final, reporting values as NR as instructed.
Note on CX26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CX29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CX31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on CX39: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3.
Note on CX40: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3.
Note on DF15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on DF17: C. Hill (9/21/99): All weekly TOC data was verified by reviewer using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on DH26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on DH29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on DH31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on DH39: TSC_ADM: Reviewer changed reported value of 14 to NR, as was done by the consultant for the primary Week 4 water quality sample with the following justification "Lab error suspected. Lab reported values are final, reporting values as NR as instructed."
Note on DH40: TSC_ADM: Reviewer changed reported value of 13 to NR, as was done by the consultant for the primary Week 4 water quality sample with the following justification "Lab error suspected. Lab reported values are final, reporting values as NR as instructed."
Note on DI26: DPATTON: Lab results reported are final. Lab error suspected. One explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on DI29: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on DI31: DPATTON: This value is measured by lab. It was initially given as target value to achieve.
Note on DR5: C. Hill (9/15/99): This data was copied by the reviewer from field 4-12 of the NF70 data collection spreadsheet.

## FldSys. 4th Quarter
FIELD-SET 4: 4th QUARTER SEBST RESULTS (FILE: Fluid Sys.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: SEBST Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 4-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 4-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 4-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 4-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 4-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [19 empty] | 0.69947 |  | 12.8938 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 260 | Process | Description | Scale |  | Date | Time | Operation time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL5360313 | Membrane trade name | Spiral-Wound Reverse Osmosis Element | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.25077 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale |  | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | TFCS 4921S |  |  | LSI | 0.29 | Hydrochloric acid addition | pH = 6.7 | Pilot-scale | 0 | 1999-02-09 | 12:00 | 0 | 27 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.2926 | 48.7074 | 0.23228 | 5.9 | 6.4 | 6.9 | 138.05 | 436.15 | 1056.55 | 1131.7167 | -7.1144 | 68.348 | 1067.3123 | 87.0656 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.052 |  |  |  | 0.25 | 1999-02-09 | 18:00 | 6 | 28.3 | 59 | 57 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 11.6647 | 8.2278 | 49.7722 | 0.23436 | 6 | 6.4 | 6.8 | 174.9 | 427.35 | 1111 | 1058.475 | 4.7277 | 59.0734 | 997.6786 | 82.4693 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.052 |  |  |  | 0.5 | 1999-02-10 | 0:00 | 12 | 25.3 | 59 | 57 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.33053 | 0.71429 | 4.1905 | 13.8462 | 12.7463 | 8.0485 | 49.9515 | 0.25517 | 6 | 6.3 | 6.9 | 179.3 | 426.25 | 1149.5 | 1043.625 | 9.2105 | 57.9355 | 984.1531 | 81.7813 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | BMRL |  |  |  | 0.875 | 1999-02-10 | 9:00 | 21 | 26 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 8.9154 | 50.0846 | 0.23267 | 5.8 | 6.4 | 6.9 | 143 | 429 | 1056.55 | 1096.3333 | -3.7654 | 66.6667 | 1034.5432 | 86.1775 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 (dup) | CF-3 (dup) | CC-3 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophyllic | Permeate flow rate, Qp (gpm) | 0.8125 | Total aluminum (mg/L) | BMRL |  |  |  | 1.25 | 1999-02-10 | 18:00 | 30 | 28.4 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.8549 | 7.3552 | 41.6448 | 0.26065 | 6.1 | 6.4 | 6.8 | 193.6 | 429.55 | 1057.65 | 980.1 | 7.3323 | 54.9296 | 929.1231 | 79.1631 | [16 empty] | Sampling date | MM/DD/YY | 1999-02-17 | 1999-02-17 | 1999-02-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-02 | 1999-03-02 | 1999-03-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-08 | 1999-03-08 | 1999-03-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-02 | 1999-03-02 | 1999-03-02 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.0833 | Fluoride (mg/L) | 0.41 |  |  |  | 1.5417 | 1999-02-11 | 1:00 | 37 | 25.1 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.9671 | 8.1439 | 40.8561 | 0.29291 | 6 | 6.3 | 6.8 | 163.35 | 424.6 | 973.5 | 1034.1833 | -6.2335 | 61.5285 | 977.7404 | 83.2931 | [16 empty] | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27083 | Phosphate (mg/L) | BMRL |  |  |  | 1.875 | 1999-02-11 | 9:00 | 45 | 26 | 50 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 8.3325 | 41.1675 | 0.28306 | 5.8 | 6.3 | 6.9 | 162.25 | 429.55 | 1069.75 | 1053.25 | 1.5424 | 62.2279 | 995.5 | 83.7017 | [16 empty] | Operation time | hh.hh | 190 | 190 | 190 | --- | --- | --- | --- | --- | Operation time | hh.hh | 356 | 356 | 356 | --- | --- | --- | --- | --- | Operation time | hh.hh | 505 | 505 | 505 | --- | --- | --- | --- | --- | Operation time | hh.hh | 645 | 645 | 645 | --- | --- | --- | --- | --- | Operation time | hh.hh | 505 | 505 | 505 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 4 | Sulfate (mg/L) | 36 |  |  |  | 2.25 | 1999-02-11 | 18:00 | 54 | 29 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.6641 | 8.3496 | 42.6504 | 0.25004 | 6.1 | 6.5 | 6.9 | 172.15 | 440 | 1042.8 | 1064.9833 | -2.1273 | 60.875 | 1007.1145 | 82.9066 | [16 empty] | pH | --- | 6.45 | 6.61 | 7.04 | --- | --- | --- | --- | --- | pH | --- | 6.53 | 6.85 | 7.16 | --- | --- | --- | --- | --- | pH | --- | 6.53 | 6.68 | 7.13 | --- | --- | --- | --- | --- | pH | --- | 6.39 | 6.88 | 7.3 | --- | --- | --- | --- | --- | pH | --- | 6.37 | 6.71 | 7.26 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 10 | Calcium (mg/L) | 82 |  |  |  | 2.5417 | 1999-02-12 | 1:00 | 61 | 24.9 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0381 | 8.5725 | 42.4275 | 0.28373 | 6.6 | 6.8 | 7.4 | 144.1 | 419.1 | 986.7 | 1060.7667 | -7.5065 | 65.6168 | 1001.3531 | 85.6095 | [16 empty] | Temperature | oC | 27 | 27 | 27 | --- | --- | --- | --- | --- | Temperature | oC | 22 | 22 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 16 |  |  |  | 3.0417 | 1999-02-12 | 13:00 | 73 | 26.2 | 48 | 46 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.32727 | 0.68421 | 4.6316 | 12 | 10.7568 | 8.4738 | 38.5262 | 0.27921 | 6 | 6.5 | 6.8 | 159.5 | 444.4 | 966.9 | 1061.6833 | -9.8028 | 64.1089 | 1006.8778 | 84.159 | [16 empty] | Alkalinity | mg/L as CaCO3 | 61 | 190 | 460 | 491 | -6.7391 | 67.8947 | 463.1296 | 86.8287 | Alkalinity | mg/L as CaCO3 | 58 | 190 | 510 | 498 | 2.3529 | 69.4737 | 469.4815 | 87.6459 | Alkalinity | mg/L as CaCO3 | 100 | 200 | 450 | 433.3333 | 3.7037 | 50 | 411.7284 | 75.7121 | Alkalinity | mg/L as CaCO3 | 76 | 200 | 500 | 489.3333 | 2.1333 | 62 | 462.5432 | 83.5691 | Alkalinity | mg/L as CaCO3 | 130 | 200 | 410 | 363.3333 | 11.3821 | 35 | 348.2099 | 62.6662 | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Design recycle flow rate, QR (gpm) | 4.4167 | Strontium (mg/L) | 0.4 |  |  |  | 3.25 | 1999-02-12 | 18:00 | 78 | 25.7 | 48 | 46 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.32727 | 0.68421 | 4.6316 | 12 | 10.917 | 8.9809 | 38.0191 | 0.28714 | 6 | 6.7 | 6.9 | 130.9 | 432.85 | 798.05 | 1087.075 | -36.2164 | 69.7586 | 1028.9896 | 87.2788 | [16 empty] | Total dissolved solids | mg/L | 140 | 500 | 1200 | 1340 | -11.6667 | 72 | 1262.2222 | 88.9085 | Total dissolved solids | mg/L | 150 | 520 | 1200 | 1383.3333 | -15.2778 | 71.1538 | 1303.3951 | 88.4916 | Total dissolved solids | mg/L | 130 | 550 | 1200 | 1530 | -27.5 | 76.3636 | 1439.2593 | 90.9676 | Total dissolved solids | mg/L | 130 | 460 | 1200 | 1230 | -2.5 | 71.7391 | 1158.7037 | 88.7806 | Total dissolved solids | mg/L | 140 | 480 | 1000 | 1273.3333 | -27.3333 | 70.8333 | 1199.8765 | 88.3321 | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Recycle ratio, r | 4.0769 | Reactive silica (mg/L as SiO2) | 0.0033 |  |  |  | 3.5417 | 1999-02-13 | 1:00 | 85 | 24.8 | 48 | 46 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.32727 | 0.68421 | 4.6316 | 12 | 11.2113 | 7.9667 | 39.0333 | 0.28722 | 6.2 | 6.4 | 6.9 | 166.65 | 434.5 | 971.85 | 1014.8417 | -4.4237 | 61.6456 | 963.316 | 82.7004 | [16 empty] | Total hardness | mg/L as CaCO3 | 62 | 270 | 670 | 755.3333 | -12.7363 | 77.037 | 710.3951 | 91.2725 | Total hardness | mg/L as CaCO3 | 59 | 270 | 720 | 762.3333 | -5.8796 | 78.1481 | 716.7469 | 91.7684 | Total hardness | mg/L as CaCO3 | 58 | 270 | 630 | 764.6667 | -21.3757 | 78.5185 | 718.8642 | 91.9317 | Total hardness | mg/L as CaCO3 | 59 | 280 | 710 | 795.6667 | -12.0657 | 78.9286 | 747.9198 | 92.1115 | Total hardness | mg/L as CaCO3 | 55 | 270 | 600 | 771.6667 | -28.6111 | 79.6296 | 725.216 | 92.4161 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | 0.4 |  |  |  | 4.0417 | 1999-02-13 | 13:00 | 97 | 25.4 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8615 | 8.744 | 41.256 | 0.28751 | 6 | 6.4 | 6.8 | 153.45 | 433.95 | 987.8 | 1088.45 | -10.1893 | 64.6388 | 1027.8481 | 85.0708 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 48 | 200 | 520 | 554.6667 | -6.6667 | 76 | 521.8272 | 90.8016 | Calcium hardness | mg/L as CaCO3 | 46 | 210 | 570 | 592.6667 | -3.9766 | 78.0952 | 557.2346 | 91.7449 | Calcium hardness | mg/L as CaCO3 | 46 | 210 | 500 | 592.6667 | -18.5333 | 78.0952 | 557.2346 | 91.7449 | Calcium hardness | mg/L as CaCO3 | 45 | 210 | 550 | 595 | -8.1818 | 78.5714 | 559.3519 | 91.955 | Calcium hardness | mg/L as CaCO3 | 43 | 210 | 470 | 599.6667 | -27.5887 | 79.5238 | 563.5864 | 92.3703 | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 2.5 |  |  |  | 4.2083 | 1999-02-13 | 17:00 | 101 | 26.4 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.516 | 9.1383 | 40.8617 | 0.28183 | 6 | 6.6 | 6.8 | 132.55 | 425.7 | 783.75 | 1109.7167 | -41.5906 | 68.863 | 1046.3818 | 87.3325 | [16 empty] | Turbidity | ntu | 0.31 | 10 | 3.6 | 32.61 | -805.8333 | 96.9 | 30.5165 | 98.9842 | Turbidity | ntu | BMRL | 12 | 3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 5.1 | 0.95 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 24 | 0.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 7.5 | 0.98 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 4.625 | 1999-02-14 | 3:00 | 111 | 24 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 8.3325 | 41.6675 | 0.2967 | 6 | 6.6 | 7 | 158.95 | 426.25 | 982.85 | 1049.95 | -6.8271 | 62.7097 | 992.2 | 83.98 | [16 empty] | Ammonia | mg NH3-N / L | 0.33 | 0.58 | 0.96 | 1.1633 | -21.1806 | 43.1034 | 1.1093 | 70.2521 | Ammonia | mg NH3-N / L | 0.28 | 0.5 | 0.92 | 1.0133 | -10.1449 | 44 | 0.9658 | 71.0086 | Ammonia | mg NH3-N / L | 0.29 | 0.51 | 0.88 | 1.0233 | -16.2879 | 43.1373 | 0.9758 | 70.2809 | Ammonia | mg NH3-N / L | 0.28 | 0.44 | 0.83 | 0.81333 | 2.008 | 36.3636 | 0.77877 | 64.0457 | Ammonia | mg NH3-N / L | 0.28 | 0.52 | 0.82 | 1.08 | -31.7073 | 46.1538 | 1.0281 | 72.7666
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 5.0938 | 1999-02-14 | 14:15 | 122.25 | 25.8 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.722 | 9.7041 | 40.2959 | 0.2909 | 6.1 | 6.7 | 7 | 110 | 421.3 | 729.85 | 1147.6667 | -57.2469 | 73.8903 | 1080.4105 | 89.8187 | [16 empty] | Total organic carbon | mg/L | BMRL | 6 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.7 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.4 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.6 | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 12.67 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 5.25 | 1999-02-14 | 18:00 | 126 | 27.5 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 8.3325 | 42.6675 | 0.26127 | 6.1 | 6.6 | 6.9 | 160.6 | 427.9 | 1005.4 | 1051.6 | -4.5952 | 62.4679 | 993.85 | 83.8406 | [16 empty] | UV254 | cm-1 | 0.023 | 0.21 | 0.56 | 0.64633 | -15.4167 | 89.0476 | 0.60593 | 96.2042 | UV254 | cm-1 | 0.02 | 0.24 | 0.6 | 0.75333 | -25.5556 | 91.6667 | 0.7058 | 97.1663 | UV254 | cm-1 | 0.022 | 0.26 | 0.55 | 0.81533 | -48.2424 | 91.5385 | 0.76391 | 97.1201 | UV254 | cm-1 | 0.028 | 0.22 | 0.56 | 0.668 | -19.2857 | 87.2727 | 0.62652 | 95.5309 | UV254 | cm-1 | 0.021 | 0.26 | 0.54 | 0.81767 | -51.4198 | 91.9231 | 0.76603 | 97.2586
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.0027 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 5.625 | 1999-02-15 | 3:00 | 135 | 23.8 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.4359 | 8.5211 | 42.4789 | 0.29275 | 6.1 | 6.6 | 7 | 159.5 | 432.85 | 999.9 | 1070.6667 | -7.0774 | 63.1512 | 1011.6096 | 84.233 | [16 empty] | SUVA | L/(mg*m) | NR | 3.5 | 3.5 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.1169 | 3.3333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.0625 | 3.6667 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.6667 | 3.5 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.9394 | 3.8571 | --- | --- | --- | --- | ---
Process Train Name | NA | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 5.8542 | 1999-02-15 | 8:30 | 140.5 | 23.3 | 51 | 49 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.32793 | 0.69072 | 4.5361 | 12.3692 | 12.0802 | 8.8705 | 41.1295 | 0.29371 | 6.3 | 7 | 7.1 | 127.05 | 419.65 | 796.95 | 1073.1233 | -34.6538 | 69.7248 | 1014.1039 | 87.4717 | [16 empty] | Bromide | mg/L | 90 | 220 | 500 | 523.3333 | --- | 59.0909 | 495.2469 | 81.8272 | Bromide | mg/L | 87 | 230 | 500 | 563.6667 | --- | 62.1739 | 532.7716 | 83.6703 | Bromide | mg/L | 90 | 220 | 460 | 523.3333 | --- | 59.0909 | 495.2469 | 81.8272 | Bromide | mg/L | 85 | 220 | 480 | 535 | --- | 61.3636 | 505.8333 | 83.196 | Bromide | mg/L | 87 | 230 | 450 | 563.6667 | --- | 62.1739 | 532.7716 | 83.6703
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 6.25 | 1999-02-15 | 18:00 | 150 | 27.5 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 8.2296 | 41.7704 | 0.26688 | 6.1 | 6.5 | 6.9 | 166.1 | 430.1 | 1013.65 | 1046.1 | -3.2013 | 61.3811 | 989.063 | 83.2063 | [16 empty] | SDS-Cl2 dose | mg/L | 15 | 9.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 11 | 10 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 10 | 7.8 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 17 | 10 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 11 | 8.1 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1152.638 | [5 empty] | 6.625 | 1999-02-16 | 3:00 | 159 | 22.8 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.809 | 8.3496 | 41.6504 | 0.30754 | 6.5 | 6.8 | 7.3 | 161.15 | 429 | 1003.2 | 1053.9833 | -5.0621 | 62.4359 | 996.1145 | 83.8221 | [16 empty] | SDS-Free Cl2 residual | mg/L | 0.7 | 0.75 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.65 | 0.72 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.89 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.71 | 0.85 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.7 | 0.75 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 202.454 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 6.875 | 1999-02-16 | 9:00 | 165 | 26 | 51 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 10.75 | 39.75 | 0.29316 | 5.9 | 6.2 | 6.9 | 156.75 | 501.6 | 909.15 | 1306.25 | -43.6782 | 68.75 | 1231.7454 | 87.2742 | [16 empty] | SDS-Cl2 demand | mg/L | 14.3 | 8.45 | --- | -5.2 | --- | -69.2308 | -3.9361 | 463.3028 | SDS-Cl2 demand | mg/L | 10.35 | 9.28 | --- | 6.7833 | --- | -11.5302 | 7.0145 | -47.5514 | SDS-Cl2 demand | mg/L | 9.11 | 7.15 | --- | 2.5767 | --- | -27.4126 | 3.0001 | -203.6542 | SDS-Cl2 demand | mg/L | 16.29 | 9.15 | --- | -7.51 | --- | -78.0328 | -5.9674 | 372.9829 | SDS-Cl2 demand | mg/L | 10.3 | 7.35 | --- | 0.46667 | --- | -40.1361 | 1.104 | -832.9606
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | 1 | Influent TDS, TDSI (mg/L) | 1012.2699 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 7.25 | 1999-02-16 | 18:00 | 174 | 28.5 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.8229 | 8.0925 | 41.9075 | 0.25826 | 6.1 | 6.5 | 6.9 | 169.4 | 429 | 1013.1 | 1034.7333 | -2.1354 | 60.5128 | 978.6469 | 82.6904 | [16 empty] | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 7.7083 | 1999-02-17 | 5:00 | 185 | 22.4 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.9613 | 8.2811 | 40.7189 | 0.31831 | 6.1 | 6.4 | 7 | 162.25 | 427.9 | 1000.45 | 1047.75 | -4.7279 | 62.0823 | 990.3565 | 83.617 | [16 empty] | SDS-Chlorination pH | --- | 7.97 | 8.1 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.11 | 8.03 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.19 | 8.09 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.86 | 8.12 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.11 | 8.12 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 10 | [7 empty] | 7.9167 | 1999-02-17 | 10:00 | 190 | 27 | 50 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 7.5953 | 41.9047 | 0.26998 | 6.1 | 6.5 | 6.9 | 157.85 | 401.5 | 976.8 | 970.0167 | 0.69444 | 60.6849 | 917.3762 | 82.7933 | [16 empty] | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 8.25 | 1999-02-17 | 18:00 | 198 | 28.3 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.887 | 8.1096 | 40.8904 | 0.26625 | 6 | 6.5 | 6.9 | 165.55 | 425.7 | 995.5 | 1032.7167 | -3.7385 | 61.1111 | 976.5114 | 83.0468 | [16 empty] | SDS-TOX | mg Cl- /L | 67 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 64 | 628 | --- | 1944 | --- | 89.8089 | 1822.1481 | 96.4877 | SDS-TOX | mg Cl- /L | 47 | 438 | --- | 1350.3333 | --- | 89.2694 | 1265.858 | 96.2871 | SDS-TOX | mg Cl- /L | NR | 567 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 57 | 500 | --- | 1533.6667 | --- | 88.6 | 1437.9568 | 96.036
|  | Rejection of reference solute and conditions of test | NaCl 500 mg/L | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 8.625 | 1999-02-18 | 3:00 | 207 | 24.9 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0381 | 8.2468 | 40.7532 | 0.29539 | 6 | 6.5 | 6.9 | 165.55 | 430.1 | 992.2 | 1047.3833 | -5.5617 | 61.509 | 990.2275 | 83.2816 | [16 empty] | SDS-CHCl3 | mg/L | 5.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 4.8 | 69 | --- | 218.8 | --- | 93.0435 | 204.9296 | 97.6577 | SDS-CHCl3 | mg/L | 3 | 68 | --- | 219.6667 | --- | 95.5882 | 205.6235 | 98.541 | SDS-CHCl3 | mg/L | NR | 82 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 3.4 | 70 | --- | 225.4 | --- | 95.1429 | 211.0111 | 98.3887
|  | (e.g., solute type and concentration) | 85 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 8.875 | 1999-02-18 | 9:00 | 213 | 27 | 50 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.2583 | 40.2417 | 0.28114 | 5.9 | 6.3 | 6.8 | 159.5 | 456.5 | 882.75 | 1149.5 | -30.2181 | 65.0602 | 1085.3333 | 85.3041 | [16 empty] | SDS-BDCM | mg/L | 6.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 7.3 | 49 | --- | 146.3 | --- | 85.102 | 137.2907 | 94.6828 | SDS-BDCM | mg/L | 3.8 | 41 | --- | 127.8 | --- | 90.7317 | 119.763 | 96.8271 | SDS-BDCM | mg/L | NR | 52 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 5 | 50 | --- | 155 | --- | 90 | 145.2778 | 96.5583
|  | Variability of rejection of reference solute (%) | +/-15.0 | Required influent pressure, PI (psi) | 70.6164 | [5 empty] | 9.25 | 1999-02-18 | 18:00 | 222 | 28.3 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.887 | 7.801 | 44.199 | 0.24632 | 6.1 | 6.5 | 6.9 | 172.15 | 422.4 | 1060.4 | 1006.3167 | 5.1003 | 59.2448 | 952.2503 | 81.9218 | [16 empty] | SDS-DBCM | mg/L | 8.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 13 | 18 | --- | 29.6667 | --- | 27.7778 | 28.5864 | 54.5239 | SDS-DBCM | mg/L | 9.4 | 17 | --- | 34.7333 | --- | 44.7059 | 33.0914 | 71.5938 | SDS-DBCM | mg/L | NR | 20 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 9 | 21 | --- | 49 | --- | 57.1429 | 46.4074 | 80.6065
|  | Standard testing recovery (%) | 10 | [7 empty] | 9.5417 | 1999-02-19 | 1:00 | 229 | 24.9 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0381 | 8.0067 | 44.9933 | 0.26755 | 6.1 | 6.7 | 6.9 | 168.85 | 425.7 | 1067 | 1025.0167 | 3.9347 | 60.3359 | 969.5244 | 82.5842 | [16 empty] | SDS-CHBr3 | mg/L | 2.4 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 6.1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 8.4 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 4.2 | 1.2 | --- | -5.8 | --- | -250 | -5.1519 | 181.5241
|  | Standard testing pH | 7.5 | [7 empty] | 10.125 | 1999-02-19 | 15:00 | 243 | 26.9 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.347 | 8.4011 | 42.5989 | 0.26637 | 6 | 6.5 | 6.8 | 162.25 | 431.75 | 994.4 | 1060.5833 | -6.6556 | 62.4204 | 1002.358 | 83.8132 | [16 empty] | SDS-THM4 | mg/L | 23.6 | 0 | --- | -55.0667 | --- | #DIV/0! | -49.9679 | 147.2303 | SDS-THM4 | mg/L | 31.2 | 136 | --- | 380.5333 | --- | 77.0588 | 357.8914 | 91.2823 | SDS-THM4 | mg/L | 24.6 | 126 | --- | 362.6 | --- | 80.4762 | 340.6926 | 92.7794 | SDS-THM4 | mg/L | NR | 154 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 21.6 | 142.2 | --- | 423.6 | --- | 84.8101 | 397.5444 | 94.5666
|  | Acceptable range of operating pressures | 0-350 | [7 empty] | 10.1979 | 1999-02-19 | 16:45 | 244.75 | 26.6 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.4481 | 9.5669 | 41.4331 | 0.2763 | 6.1 | 6.7 | 6.9 | 121.55 | 428.45 | 794.2 | 1144.55 | -44.1136 | 71.6303 | 1078.2444 | 88.727 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 10.7917 | 1999-02-20 | 7:00 | 259 | 24 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 8.4697 | 42.5303 | 0.29068 | 6.1 | 6.4 | 6.9 | 158.95 | 430.65 | 1005.4 | 1064.6167 | -5.8899 | 63.0907 | 1005.916 | 84.1985 | [16 empty] | SDS-DCAA* | mg/L | 3 | 10 | --- | 26.3333 | --- | 70 | 24.821 | 87.9135 | SDS-DCAA* | mg/L | 1.5 | 55 | --- | 179.8333 | --- | 97.2727 | 168.2747 | 99.1086 | SDS-DCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | 34 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | 40 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 3 | [7 empty] | 11.1146 | 1999-02-20 | 14:45 | 266.75 | 27 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 9.3269 | 41.6731 | 0.27148 | 6 | 6.4 | 6.8 | 123.75 | 422.95 | 812.9 | 1121.0833 | -37.9116 | 70.7412 | 1056.4414 | 88.2861 | [16 empty] | SDS-TCAA* | mg/L | 3.7 | 8.2 | --- | 18.7 | --- | 54.878 | 17.7278 | 79.1288 | SDS-TCAA* | mg/L | BMRL | 52 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 18 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | 27 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | 52 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 11.375 | 1999-02-20 | 21:00 | 273 | 24.8 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0737 | 8.6754 | 42.3246 | 0.28526 | 6 | 6.5 | 6.8 | 152.9 | 431.2 | 1020.25 | 1080.5667 | -5.9119 | 64.5408 | 1020.4401 | 85.0163 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 0 | [7 empty] | 11.625 | 1999-02-21 | 3:00 | 279 | 24.2 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.2897 | 8.4697 | 42.5303 | 0.28896 | 6.1 | 6.5 | 6.9 | 158.4 | 430.1 | 1005.4 | 1064.0667 | -5.8352 | 63.1714 | 1005.366 | 84.2445 | [16 empty] | SDS-DBAA* | mg/L | 3.4 | 2.7 | --- | 1.0667 | --- | -25.9259 | 1.2179 | -179.1688 | SDS-DBAA* | mg/L | 3.6 | 6.6 | --- | 13.6 | --- | 45.4545 | 12.9519 | 72.2047 | SDS-DBAA* | mg/L | 3.4 | 2.4 | --- | 0.066667 | --- | -41.6667 | 0.28272 | -1102.6201 | SDS-DBAA* | mg/L | NR | 5.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 2.2 | 6.5 | --- | 16.5333 | --- | 66.1538 | 15.6043 | 85.9013
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 11.9583 | 1999-02-21 | 11:00 | 287 | 26.3 | 52 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.5501 | 8.8811 | 42.6189 | 0.27101 | 6.3 | 6.7 | 7.1 | 143.55 | 428.45 | 993.85 | 1093.2167 | -9.9982 | 66.4955 | 1031.6642 | 86.0856 | [16 empty] | SDS-BCAA* | mg/L | 3.5 | 4.9 | --- | 8.1667 | --- | 28.5714 | 7.8642 | 55.4945 | SDS-BCAA* | mg/L | 2.4 | 22 | --- | 67.7333 | --- | 89.0909 | 63.4988 | 96.2204 | SDS-BCAA* | mg/L | 1.6 | 7.9 | --- | 22.6 | --- | 79.7468 | 21.2389 | 92.4666 | SDS-BCAA* | mg/L | NR | 15 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.4 | 20 | --- | 63.4 | --- | 93 | 59.3815 | 97.6424
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 12.25 | 1999-02-21 | 18:00 | 294 | 26.2 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.5843 | 8.2296 | 42.7704 | 0.27085 | 6.1 | 6.5 | 6.9 | 171.05 | 435.05 | 1047.2 | 1051.05 | -0.36765 | 60.6827 | 994.013 | 82.792 | [16 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 12.625 | 1999-02-22 | 3:00 | 303 | 24.4 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.2173 | 8.504 | 42.496 | 0.28749 | 6 | 6.5 | 6.8 | 157.85 | 430.65 | 1031.8 | 1067.1833 | -3.4293 | 63.3461 | 1008.2451 | 84.3441 | [16 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 12.875 | 1999-02-22 | 9:00 | 309 | 25 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 8.2468 | 42.7532 | 0.28074 | 6 | 6.4 | 6.9 | 156.2 | 420.75 | 1035.1 | 1038.0333 | -0.28339 | 62.8758 | 980.8775 | 84.0755 | [16 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 13.25 | 1999-02-22 | 18:00 | 318 | 27 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3135 | 8.1096 | 42.8904 | 0.26378 | 6.1 | 6.6 | 6.9 | 174.35 | 434.5 | 1048.3 | 1041.5167 | 0.64708 | 59.8734 | 985.3114 | 82.3051 | [16 empty] | SDS-HAA5 | mg/L | 10.1 | 20.9 | --- | 46.1 | --- | 51.6746 | 43.7667 | 76.9231 | SDS-HAA5 | mg/L | 5.1 | 113.6 | --- | 366.7667 | --- | 95.5106 | 343.3253 | 98.5145 | SDS-HAA5 | mg/L | 3.4 | 38.4 | --- | 120.0667 | --- | 91.1458 | 112.5049 | 96.9779 | SDS-HAA5 | mg/L | NR | 66.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 2.2 | 98.5 | --- | 323.2 | --- | 97.7665 | 302.3944 | 99.2725
[11 empty] | 13.5417 | 1999-02-23 | 1:00 | 325 | 20.2 | 52 | 50 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.32727 | 0.68421 | 4.6316 | 12 | 12.8442 | 8.0812 | 42.9188 | 0.29927 | 6.2 | 6.5 | 7.1 | 168.85 | 440.55 | 1055.45 | 1029.2333 | 2.4839 | 61.6729 | 976.9671 | 82.7169 | [16 empty] | SDS-HAA6 | mg/L | 13.6 | 25.8 | --- | 54.2667 | --- | 47.2868 | 51.6309 | 73.6592 | SDS-HAA6 | mg/L | 7.5 | 135.6 | --- | 434.5 | --- | 94.469 | 406.8241 | 98.1565 | SDS-HAA6 | mg/L | 5 | 46.3 | --- | 142.6667 | --- | 89.2009 | 133.7438 | 96.2615 | SDS-HAA6 | mg/L | NR | 81.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 3.6 | 118.5 | --- | 386.6 | --- | 96.962 | 361.7759 | 99.0049
[11 empty] | 13.875 | 1999-02-23 | 9:00 | 333 | 24 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 8.2468 | 42.7532 | 0.28916 | 6 | 6.5 | 7 | 156.2 | 420.75 | 1035.1 | 1038.0333 | -0.28339 | 62.8758 | 980.8775 | 84.0755 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 14.25 | 1999-02-23 | 18:00 | 342 | 27.5 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1476 | 8.0582 | 42.9418 | 0.2596 | 6.1 | 6.5 | 6.9 | 166.1 | 424.6 | 1016.4 | 1027.7667 | -1.1183 | 60.8808 | 971.9179 | 82.9101 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 14.8333 | 1999-02-24 | 8:00 | 356 | 22 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 13.1155 | 8.4868 | 42.5132 | 0.3085 | 6.1 | 6.4 | 6.9 | 155.1 | 427.35 | 1012 | 1062.6 | -5 | 63.7066 | 1003.7806 | 84.5484
[11 empty] | 14.875 | 1999-02-24 | 9:00 | 357 | 25 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 9.3612 | 41.6388 | 0.28825 | 5.9 | 6.2 | 6.8 | 150.7 | 451 | 922.35 | 1151.7 | -24.8658 | 66.5854 | 1086.8204 | 86.1339 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 15.25 | 1999-02-24 | 18:00 | 366 | 28 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.984 | 7.9553 | 44.0447 | 0.24938 | 6 | 6.7 | 6.9 | 153.45 | 408.65 | 995.5 | 1004.1167 | -0.86556 | 62.4495 | 948.9809 | 83.83 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 15.625 | 1999-02-25 | 3:00 | 375 | 22.5 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.9231 | 8.2125 | 43.7875 | 0.29513 | 6.1 | 6.4 | 6.9 | 152.35 | 415.8 | 1002.65 | 1030.5167 | -2.7793 | 63.3598 | 973.5985 | 84.3519 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 15.875 | 1999-02-25 | 9:00 | 381 | 25 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 7.4924 | 43.5076 | 0.27587 | 5.9 | 6.2 | 6.8 | 151.8 | 392.15 | 988.9 | 952.9667 | 3.6337 | 61.2903 | 901.0392 | 83.1528 | [16 empty] | Qp/QT (THM4), % | 305.0847 | 152.5424 |  | Qp/QT (HAA5), % | -306.4815 | -56.4815 |  |  |  | Qp/QT (THM4), % | 61.0687 | 95.4198 |  | Qp/QT (HAA5), % | 54.9309 | 79.8157 |  |  |  | Qp/QT (THM4), % | 53.2544 | 88.7574 |  | Qp/QT (HAA5), % | -44.5714 | 32.5714 |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | 58.209 | 88.0597 |  | Qp/QT (HAA5), % | 46.2098 | 74.2471
[11 empty] | 16.25 | 1999-02-25 | 18:00 | 390 | 27.7 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.0819 | 8.0925 | 43.9075 | 0.25239 | 6.1 | 6.4 | 6.9 | 159.5 | 419.1 | 1016.4 | 1024.8333 | -0.82973 | 61.9423 | 968.7469 | 83.5354 | [16 empty] | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 78.4324 | 52.3532 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 92.9726 |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 86.471 | 52.6579
[11 empty] | 16.625 | 1999-02-26 | 3:00 | 399 | 26.1 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6185 | 8.4525 | 43.5475 | 0.2668 | 6 | 6.3 | 6.9 | 150.7 | 421.85 | 997.15 | 1054.5333 | -5.7547 | 64.2764 | 995.9515 | 84.8687 | [16 empty] | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | SDS-HAA5b, mg/L | 47.3405 | 10.0695 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 19.7609 | 7.3349 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | 42.4448 | 13.6985 |  | SDS-HAA5b, mg/L | 54 | 27
[11 empty] | 17.0417 | 1999-02-26 | 13:00 | 409 | 26.5 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.482 | 8.7954 | 43.2046 | 0.26576 | 5.9 | 6.4 | 6.8 | 144.1 | 426.25 | 993.3 | 1084.6 | -9.1916 | 66.1935 | 1023.6417 | 85.9228 | [16 empty] | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | SDS-TOXb, mg Cl- /L | 283.5725 | 89.8321 |  | SDS-TOXb, mg Cl- /L | 318.1899 | 177.8396 |  |  |  | SDS-TOXb, mg Cl- /L | 229.7751 | 90.9586 |  | SDS-TOXb, mg Cl- /L | NA | 310.6457 |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | 242.1343 | 109.8955 |  | SDS-TOXb, mg Cl- /L | 295.2908 | 171.0852
[11 empty] | 17.375 | 1999-02-26 | 21:00 | 417 | 25 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.0025 | 8.504 | 43.496 | 0.27595 | 5.9 | 6.3 | 6.8 | 149.6 | 422.4 | 996.05 | 1058.9333 | -6.3133 | 64.5833 | 999.9951 | 85.0399 | [16 empty] | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | SDS-CDb, mg/L | 9.9334 | 10.301 |  | SDS-CDb, mg/L | 9.8678 | 10.134 |  |  |  | SDS-CDb, mg/L | 8.1938 | 8.8896 |  | SDS-CDb, mg/L | NA | 7.7884 |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | 9.0672 | 9.9478 |  | SDS-CDb, mg/L | 8.7132 | 9.5403
[11 empty] | 17.5417 | 1999-02-27 | 1:00 | 421 | 22.6 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.8849 | 8.5897 | 43.4103 | 0.29682 | 6 | 6.4 | 6.9 | 150.15 | 425.7 | 994.95 | 1068.65 | -7.4074 | 64.7287 | 1009.1176 | 85.1207 | [16 empty] | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 18.0417 | 1999-02-27 | 13:00 | 433 | 26.5 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.482 | 8.6754 | 43.3246 | 0.26502 | 6.1 | 6.5 | 6.8 | 144.65 | 422.95 | 991.65 | 1072.3167 | -8.1346 | 65.7997 | 1012.1901 | 85.7092 | [16 empty] | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | UV254 b, cm-1 | 0.10565 | 0.030076 |  | UV254 b, cm-1 | 0.11915 | 0.064406 |  |  |  | UV254 b, cm-1 | 0.13325 | 0.048757 |  | UV254 b, cm-1 | NA | 0.18248 |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | 0.12088 | 0.049537 |  | UV254 b, cm-1 | 0.14956 | 0.082549
[11 empty] | 18.2604 | 1999-02-27 | 18:15 | 438.25 | 25.9 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6874 | 9.3269 | 42.6731 | 0.27388 | 6.6 | 5.9 | 6.8 | 113.85 | 413.05 | 827.2 | 1111.1833 | -34.3307 | 72.4368 | 1046.5414 | 89.1213 | [16 empty] | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Bromideb, mg/L | 142.6718 | 93.5496 |  | Bromideb, mg/L | 151.4488 | 115.8636 |  |  |  | Bromideb, mg/L | 150.7692 | 104.6154 |  | Bromideb, mg/L | NA | 177.6571 |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | 146.7612 | 104.0746 |  | Bromideb, mg/L | 163.92 | 123.8266
[11 empty] | 18.625 | 1999-02-28 | 3:00 | 447 | 23 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.7335 | 7.681 | 44.319 | 0.28731 | 6 | 6.5 | 6.8 | 150.7 | 397.1 | 895.4 | 972.0333 | -8.5586 | 62.0499 | 918.7988 | 83.5981 | [16 empty] | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Alkb, mg/L CaCO3 | 109.3893 | 64.0458 |  | Alkb, mg/L CaCO3 | 117.4912 | 84.6433 |  |  |  | Alkb, mg/L CaCO3 | 146.7456 | 111.2426 |  | Alkb, mg/L CaCO3 | NA | 167.4286 |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | 159.2537 | 138.3582 |  | Alkb, mg/L CaCO3 | 167.6532 | 148.027
[11 empty] | 18.8542 | 1999-02-28 | 8:30 | 452.5 | 25.4 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8615 | 9.4812 | 41.5188 | 0.28569 | 6 | 6.5 | 7 | 102.3 | 406.45 | 662.2 | 1116.1333 | -68.5493 | 74.8309 | 1050.4219 | 90.2611 | [16 empty] | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | T-Hdb, mg/L CaCO3 | 141.145 | 68.6641 |  | T-Hdb, mg/L CaCO3 | 154.0959 | 101.5889 |  |  |  | T-Hdb, mg/L CaCO3 | 157.1006 | 81.8343 |  | T-Hdb, mg/L CaCO3 | NA | 200.9486 |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | 144.8507 | 80.6716 |  | T-Hdb, mg/L CaCO3 | 170.649 | 110.3686
[11 empty] | 19.25 | 1999-02-28 | 18:00 | 462 | 27.4 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.1806 | 7.801 | 43.199 | 0.25882 | 6.1 | 6.5 | 7 | 165 | 415.25 | 1074.7 | 999.1667 | 7.0283 | 60.2649 | 945.1003 | 82.5415 | [16 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Ca-Hdb, mg/L CaCO3 | 109.8473 | 53.5115 |  | Ca-Hdb, mg/L CaCO3 | 119.9134 | 79.1023 |  |  |  | Ca-Hdb, mg/L CaCO3 | 122.6627 | 64.4379 |  | Ca-Hdb, mg/L CaCO3 | NA | 156.5829 |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | 112.791 | 62.9403 |  | Ca-Hdb, mg/L CaCO3 | 132.8297 | 86.0073
[11 empty] | 19.625 | 1999-03-01 | 3:00 | 471 | 24.4 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.2173 | 9.1555 | 41.8445 | 0.29197 | 6 | 6.5 | 7 | 157.85 | 451.55 | 1036.75 | 1136.85 | -9.6552 | 65.0426 | 1073.3963 | 85.2943 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 19.875 | 1999-03-01 | 9:00 | 477 | 26 | 52 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.5498 | 41.9502 | 0.27778 | 6 | 6.3 | 6.8 | 151.8 | 458.15 | 935 | 1172.9667 | -25.451 | 66.8667 | 1106.7799 | 86.2845 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 20.25 | 1999-03-01 | 18:00 | 486 | 28 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.984 | 8.4182 | 41.5818 | 0.26415 | 6.1 | 6.7 | 7 | 152.35 | 422.4 | 1004.85 | 1052.5167 | -4.7437 | 63.9323 | 994.1725 | 84.6757 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 20.5417 | 1999-03-02 | 1:00 | 493 | 22.7 | 51 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.8469 | 8.6068 | 41.3932 | 0.31036 | 6.1 | 6.5 | 7 | 149.6 | 425.7 | 994.4 | 1069.9333 | -7.5959 | 64.8579 | 1010.2821 | 85.1923 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 21.0417 | 1999-03-02 | 13:00 | 505 | 26.9 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.347 | 8.984 | 40.016 | 0.28356 | 6.1 | 6.6 | 6.9 | 146.3 | 434.5 | 955.35 | 1106.9667 | -15.8703 | 66.3291 | 1044.7012 | 85.996 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 21.25 | 1999-03-02 | 18:00 | 510 | 28 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.984 | 8.3325 | 40.6675 | 0.27009 | 6 | 6.45 | 6.8 | 156.75 | 424.05 | 981.2 | 1047.75 | -6.7825 | 63.035 | 990 | 84.1667 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 21.625 | 1999-03-03 | 3:00 | 519 | 23.6 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.5096 | 8.6925 | 40.3075 | 0.31036 | 6 | 6.4 | 6.9 | 149.6 | 428.45 | 955.35 | 1079.1 | -12.9534 | 65.0834 | 1018.8546 | 85.3168 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 21.875 | 1999-03-03 | 9:00 | 525 | 24 | 52 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3626 | 8.9669 | 42.5331 | 0.29066 | 6 |  | 6.9 | 151.25 | 438.9 | 904.75 | 1110.0833 | -22.695 | 65.5388 | 1047.9367 | 85.5669 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 22.25 | 1999-03-03 | 18:00 | 534 | 27.7 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.0819 | 7.7324 | 41.2676 | 0.26854 | 6.1 | 6.5 | 6.9 | 173.25 | 421.3 | 1056 | 1000.0833 | 5.2951 | 58.8773 | 946.4923 | 81.6956 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 22.625 | 1999-03-04 | 3:00 | 543 | 26.8 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3806 | 8.2296 | 40.7704 | 0.27914 | 6.1 | 6.5 | 6.9 | 155.65 | 419.65 | 1032.9 | 1035.65 | -0.26624 | 62.9096 | 978.613 | 84.0948 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 22.875 | 1999-03-04 | 9:00 | 549 | 26 | 50 | 49 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.9956 | 39.5044 | 0.29498 | 6 | 6.3 | 6.8 | 159.5 | 480.15 | 924 | 1228.3333 | -32.9365 | 66.7812 | 1159.0571 | 86.2388 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 23.25 | 1999-03-04 | 18:00 | 558 | 28 | 53 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.984 | 8.4182 | 43.5818 | 0.25203 | 6.1 | 6.6 | 7 | 151.8 | 421.85 | 1010.9 | 1051.9667 | -4.0624 | 64.0156 | 993.6225 | 84.7226
[11 empty] | 23.625 | 1999-03-05 | 3:00 | 567 | 21.5 | 53 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 13.3108 | 7.9896 | 43.5104 | 0.30592 | 6.2 | 6.5 | 7 | 174.9 | 431.2 | 1111 | 1029.2333 | 7.3597 | 59.4388 | 973.8599 | 82.0405
[11 empty] | 24.0417 | 1999-03-05 | 13:00 | 577 | 26.4 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.516 | 9.1212 | 46.8788 | 0.24565 | 6.2 | 6.7 | 6.9 | 140.8 | 433.4 | 1030.7 | 1116.1333 | -8.2889 | 67.5127 | 1052.9173 | 86.6276
[11 empty] | 24.4583 | 1999-03-05 | 23:00 | 587 | 25.5 | 57 | 55 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.8264 | 9.1726 | 46.8274 | 0.25255 | 6 | 6.6 | 7 | 128.15 | 422.4 | 823.35 | 1108.9833 | -34.6916 | 69.6615 | 1045.4108 | 87.7417
[11 empty] | 24.625 | 1999-03-06 | 3:00 | 591 | 22.2 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 13.0382 | 8.5725 | 46.4275 | 0.28083 | 6.1 | 6.7 | 7.1 | 150.7 | 425.7 | 1007.6 | 1067.3667 | -5.9316 | 64.5995 | 1007.9531 | 85.0489
[11 empty] | 25.0417 | 1999-03-06 | 13:00 | 601 | 27.3 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.2137 | 8.864 | 46.136 | 0.24306 | 6 | 6.7 | 7 | 147.4 | 431.75 | 1005.95 | 1095.2333 | -8.8755 | 65.8599 | 1033.7997 | 85.7419
[11 empty] | 25.1979 | 1999-03-06 | 16:45 | 604.75 | 26.8 | 56 | 54 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.3806 | 9.9441 | 45.0559 | 0.25259 | 6 | 6.5 | 6.9 | 106.7 | 425.7 | 726 | 1170.0333 | -61.1616 | 74.9354 | 1101.1136 | 90.3098
[11 empty] | 25.5417 | 1999-03-07 | 1:00 | 613 | 23.2 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.6584 | 8.6068 | 45.3932 | 0.27886 | 6 | 6.7 | 7 | 148.5 | 424.6 | 993.3 | 1068.8333 | -7.6043 | 65.0259 | 1009.1821 | 85.2851
[11 empty] | 25.875 | 1999-03-07 | 9:00 | 621 | 25.2 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.9318 | 9.7384 | 43.2616 | 0.27581 | 6 | 6.5 | 6.9 | 107.25 | 419.65 | 751.85 | 1148.5833 | -52.7676 | 74.443 | 1081.0895 | 90.0795
[11 empty] | 26.25 | 1999-03-07 | 18:00 | 630 | 29.2 | 54 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 10.6012 | 8.4868 | 44.5132 | 0.23816 | 6 | 6.6 | 6.9 | 156.75 | 429 | 981.2 | 1064.25 | -8.4641 | 63.4615 | 1005.4306 | 84.4097
[11 empty] | 26.625 | 1999-03-08 | 3:00 | 639 | 23.9 | 54 | 51 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 12.3992 | 8.4868 | 44.0132 | 0.28172 | 6.1 | 6.6 | 6.9 | 151.8 | 424.05 | 965.8 | 1059.3 | -9.6811 | 64.2023 | 1000.4806 | 84.8273
[11 empty] | 26.875 | 1999-03-08 | 9:00 | 645 | 26 | 52 | 51 | 0 | 4.4 | 0.7 | 0.3 | X | 1 | 5.4 | 0.3289 | 0.7 | 4.4 | 12.9231 | 11.6529 | 9.807 | 41.693 | 0.27949 | 6 | 6.3 | 6.8 | 149.6 | 464.2 | 876.7 | 1198.2667 | -36.6792 | 67.7725 | 1130.2975 | 86.7645
0.23228
0.31831
0.27596
[31 empty] | initial | 0.23228
[31 empty] | final | 0.27949
[31 empty] | after cleaning | n/a
Note on A2: C. Hill (9/21/99): Reviewer verified all reported SDS-Cl2 dose and residuals reported. In all four weeks of this data sheet the reported permeate dose is greater than the feed dose, yet feed TOC concentrations are 6-7 mg/l greater than permeate concentrations, and stil similar residuals are achieved. This data is questionable and should be used with caution during the base analysis.
Note on Q3: TSC_ADM: Consultant noted that water treatment plant staff measured the influent temperature and the membrane operating parameters, and attributed the wide temperature fluctuations and erratic operational data to measurement error.
Note on AA88: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AI5: C. Hill (8/5/99): Corrected formula - was referring to the wrong columns.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on BN17: C. Hill (9/21/99): Reviewer verified all weekly TDS data (feed, permeate and concentrate) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on BN26: C. Hill (9/21/99): Reviewer verified all reported SDS-Cl2 dose and residuals reported. In all four weeks of this data sheet the reported permeate dose is greater than the feed dose, yet similar residuals are achieved. This data is questionable and should be used with caution during the base analysis. DPATTON: Lab results reported are final, although lab error could attribute to this. Another explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on BQ26: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports.
Note on BQ27: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports.
Note on BQ32: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ33: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ34: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ35: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ36: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ38: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ39: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ40: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ41: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ42: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BQ43: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. DPATTON: Lab results are final. Reportd as NR, as recommended.
Note on BY15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on BY17: C. Hill (9/21/99): Reviewer verified all weekly TDS data (feed, permeate and concentrate) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on BY26: C. Hill (9/21/99): Reviewer verified all reported SDS-Cl2 dose and residuals reported. In all four weeks of this data sheet the reported permeate dose is greater than the feed dose, yet similar residuals are achieved. This data is questionable and should be used with caution during the base analysis. DPATTON: Lab results reported are final, although lab error could attribute to this. Another explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CJ15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on CJ17: C. Hill (9/21/99): Reviewer verified all weekly TDS data (feed, permeate and concentrate) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on CJ26: C. Hill (9/21/99): Reviewer verified all reported SDS-Cl2 dose and residuals reported. In all four weeks of this data sheet the reported permeate dose is greater than the feed dose, yet similar residuals are achieved. This data is questionable and should be used with caution during the base analysis. DPATTON: Lab results reported are final, although lab error could attribute to this. Another explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CU15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on CU17: C. Hill (9/21/99): Reviewer verified all weekly TDS data (feed, permeate and concentrate) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on CU26: C. Hill (9/21/99): Reviewer verified all reported SDS-Cl2 dose and residuals reported. In all four weeks of this data sheet the reported permeate dose is greater than the feed dose, yet similar residuals are achieved. This data is questionable and should be used with caution during the base analysis. DPATTON: Lab results reported are final, although lab error could attribute to this. Another explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on CW27: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports.
Note on CW32: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '12'.
Note on CW33: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW34: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW35: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW36: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on CW38: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW39: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW40: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW41: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW42: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW43: C. Hill (9/21/99): Verified by reviewer using Summary Report - Exhibit 3, which contains analytical reports. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CW44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CW45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CW46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CW47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'.
Note on CW48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '0'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DF15: DPATTON: Influent temperature shifts, of operational data, could be attributed to operator error in measuring.
Note on DF17: C. Hill (9/21/99): Reviewer verified all weekly TDS data (feed, permeate and concentrate) using Summary Report - Exhibit 3. DPATTON: The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results are experimentally measured and are more accurate.
Note on DF26: C. Hill (9/21/99): Reviewer verified all reported SDS-Cl2 dose and residuals reported. In all four weeks of this data sheet the reported permeate dose is greater than the feed dose, yet similar residuals are achieved. This data is questionable and should be used with caution during the base analysis. DPATTON: Lab results reported are final, although lab error could attribute to this. Another explanation could be the hydogen sulfide concentration in the permeate is usually higher than in the feed, therefore requiring an additional chlorine demand. In membrane treatment it has been observed that approximately 80%-90% of the hydrogen sulfide in the feed stream is transfered into the permeate, while only 10-20% is rejected into the concentrate stream.
Note on DR5: C. Hill (9/15/99): This data was copied by the reviewer from field 4-12 of the NF70 data collection spreadsheet.

## NF70. Additional data
2nd quarter
Field 1-6: Membrane Performance Data During Operation With The Test Water | [17 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water | [8 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water
Date | Time | Operation | Conductivity (mS/cm) |  |  | TDS (mg/L) |  |  | Date | Time | Operation | Conductivity (mS/cm) | [5 empty] | Date | Time | Operation | Conductivity (mS/cm) | [5 empty] | Date | Time | Operation | Conductivity (mS/cm)
MM/DD/YY | hh:mm | Time | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC | MM/DD/YY | hh:mm | Time | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC | MM/DD/YY | hh:mm | Time | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC | MM/DD/YY | hh:mm | Time | CONDp | CONDF | CONDC | TDSp | TDSF | TDSC
1998-06-11 | 14:30 | 0 | 0.291 | 0.718 | 2.02 | 160.05 | 394.9 | 1111 | 1998-09-02 | 18:00 | 0 | 0.252 | 0.882 | 2.67 | 138.6 | 485.1 | 1468.5 | 1998-11-16 | 18:00 | 0 | 0.314 | 0.863 | 2.34 | 172.7 | 474.65 | 1287 | 1999-01-12 | 11:00 | 0 | 0.183 | 0.776 | 2.32 | 100.65 | 426.8 | 1276
1998-06-11 | 18:00 | 3.5 | 0.3 | 0.805 | 2.03 | 165 | 442.75 | 1116.5 | 1998-09-03 | 6:30 | 12.5 | 0.221 | 0.886 | 2.39 | 121.55 | 487.3 | 1314.5 | 1998-11-17 | 2:00 | 8 | 0.338 | 0.859 | 2.68 | 185.9 | 472.45 | 1474 | 1999-01-13 | 18:00 | 31 | 0.191 | 0.782 | 1.97 | 105.05 | 430.1 | 1083.5
1998-06-12 | 6:45 | 16.25 | 0.308 | 0.726 | 2.04 | 169.4 | 399.3 | 1122 | 1998-09-03 | 9:00 | 15 | NR | NR | NR | NR | NR | NR | 1998-11-17 | 9:00 | 15 | 0.328 | 0.858 | 2.48 | 180.4 | 471.9 | 1364 | 1999-01-14 | 1:00 | 38 | 0.201 | 0.78 | 2.04 | 110.55 | 429 | 1122
1998-06-12 | 14:00 | 23.5 | 0.262 | 0.715 | 1.965 | 144.1 | 393.25 | 1080.75 | 1998-09-03 | 18:00 | 24 | 0.22 | 0.884 | 2.45 | 121 | 486.2 | 1347.5 | 1998-11-17 | 18:00 | 24 | NR | NR | NR | NR | NR | NR | 1999-01-14 | 9:00 | 46 | 0.253 | 0.727 | 1.905 | 139.15 | 399.85 | 1047.75
1998-06-12 | 18:00 | 27.5 | 0.294 | 0.713 | 2.08 | 161.7 | 392.15 | 1144 | 1998-09-04 | 0:30 | 30.5 | 0.217 | 0.889 | 2.27 | 119.35 | 488.95 | 1248.5 | 1998-11-18 | 6:00 | 36 | 0.315 | 0.866 | 2.63 | 173.25 | 476.3 | 1446.5 | 1999-01-14 | 18:00 | 55 | 0.187 | 0.768 | 2.09 | 102.85 | 422.4 | 1149.5
1998-06-13 | 5:30 | 39 | 0.171 | 0.728 | 1.966 | 94.05 | 400.4 | 1081.3 | 1998-09-04 | 9:00 | 39 | NR | NR | NR | NR | NR | NR | 1998-11-18 | 9:00 | 39 | 0.314 | 0.864 | 2.4 | 172.7 | 475.2 | 1320 | 1999-01-15 | 3:00 | 64 | 0.192 | 0.768 | 2.13 | 105.6 | 422.4 | 1171.5
1998-06-13 | 8:30 | 42 | 0.155 | 0.713 | 1.837 | 85.25 | 392.15 | 1010.35 | 1998-09-04 | 16:20 | 46.3333 | 0.194 | 0.875 | 2.11 | 106.7 | 481.25 | 1160.5 | 1998-11-18 | 18:00 | 48 | 0.34 | 0.87 | 2.71 | 187 | 478.5 | 1490.5 | 1999-01-15 | 15:00 | 76 | 0.171 | 0.784 | 2.26 | 94.05 | 431.2 | 1243
1998-06-13 | 21:00 | 54.5 | 0.276 | 0.718 | 2.04 | 151.8 | 394.9 | 1122 | 1998-09-05 | 1:00 | 55 | 0.221 | 0.885 | 2.47 | 121.55 | 486.75 | 1358.5 | 1998-11-19 | 1:00 | 55 | 0.284 | 0.873 | 2.52 | 156.2 | 480.15 | 1386 | 1999-01-15 | 18:00 | 79 | 0.147 | 0.772 | 2.04 | 80.85 | 424.6 | 1122
1998-06-14 | 6:30 | 64 | 0.261 | 0.718 | 2.36 | 143.55 | 394.9 | 1298 | 1998-09-05 | 10:00 | 64 | NR | NR | NR | NR | NR | NR | 1998-11-19 | 13:00 | 67 | 0.307 | 0.86 | 2.33 | 168.85 | 473 | 1281.5 | 1999-01-16 | 1:00 | 86 | 0.178 | 0.768 | 2.06 | 97.9 | 422.4 | 1133
1998-06-14 | 14:00 | 71.5 | 0.128 | 0.721 | 1.886 | 70.4 | 396.55 | 1037.3 | 1998-09-05 | 11:15 | 65.25 | NR | NR | NR | NR | NR | NR | 1998-11-19 | 18:00 | 72 | 0.266 | 0.863 | 2.18 | 146.3 | 474.65 | 1199 | 1999-01-16 | 10:40 | 95.6667 | 0.114 | 0.724 | 1.796 | 62.7 | 398.2 | 987.8
1998-06-14 | 18:00 | 75.5 | 0.248 | 0.747 | 2.19 | 136.4 | 410.85 | 1204.5 | 1998-09-05 | 18:10 | 72.1667 | 0.166 | 0.815 | 2.41 | 91.3 | 448.25 | 1325.5 | 1998-11-20 | 1:00 | 79 | 0.278 | 0.854 | 2.33 | 152.9 | 469.7 | 1281.5 | 1999-01-16 | 16:15 | 101.25 | 0.158 | 0.722 | 1.871 | 86.9 | 397.1 | 1029.05
1998-06-15 | 6:30 | 88 | 0.184 | 0.715 | 1.866 | 101.2 | 393.25 | 1026.3 | 1998-09-06 | 0:30 | 78.5 | NR | NR | NR | NR | NR | NR | 1998-11-20 | 9:00 | 87 | 0.195 | 0.805 | 1.919 | 107.25 | 442.75 | 1055.45 | 1999-01-17 | 3:00 | 112 | 0.155 | 0.768 | 1.87 | 85.25 | 422.4 | 1028.5
1998-06-15 | 9:30 | 91 | 0.186 | 0.719 | 1.999 | 102.3 | 395.45 | 1099.45 | 1998-09-06 | 14:30 | 92.5 | 0.156 | 0.84 | 2.15 | 85.8 | 462 | 1182.5 | 1998-11-20 | 21:00 | 99 | 0.213 | 0.859 | 2.12 | 117.15 | 472.45 | 1166 | 1999-01-17 | 8:35 | 117.5833 | 0.104 | 0.733 | 1.294 | 57.2 | 403.15 | 711.7
1998-06-15 | 18:00 | 99.5 | 0.266 | 0.79 | 2.4 | 146.3 | 434.5 | 1320 | 1998-09-06 | 18:00 | 96 | 0.175 | 0.816 | 2.57 | 96.25 | 448.8 | 1413.5 | 1998-11-21 | 1:00 | 103 | 0.246 | 0.87 | 2.19 | 135.3 | 478.5 | 1204.5 | 1999-01-17 | 18:00 | 127 | 0.167 | 0.743 | 2.21 | 91.85 | 408.65 | 1215.5
1998-06-16 | 6:45 | 112.25 | 0.27 | 0.73 | 2.76 | 148.5 | 401.5 | 1518 | 1998-09-07 | 1:00 | 103 | 0.168 | 0.815 | 2.47 | 92.4 | 448.25 | 1358.5 | 1998-11-21 | 8:45 | 110.75 | 0.177 | 0.806 | 1.947 | 97.35 | 443.3 | 1070.85 | 1999-01-18 | 3:00 | 136 | 0.17 | 0.772 | 2.26 | 93.5 | 424.6 | 1243
1998-06-16 | 11:00 | 116.5 | 0.27 | 0.68 | 2.86 | 148.5 | 374 | 1573 | 1998-09-07 | 9:40 | 111.6667 | 0.146 | 0.8 | 2.13 | 80.3 | 440 | 1171.5 | 1998-11-21 | 21:00 | 123 | 0.221 | 0.843 | 2.17 | 121.55 | 463.65 | 1193.5 | 1999-01-18 | 9:00 | 142 | 0.158 | 0.82 | 1.882 | 86.9 | 451 | 1035.1
1998-06-16 | 18:00 | 123.5 | 0.43 | 0.864 | 3.7 | 236.5 | 475.2 | 2035 | 1998-09-07 | 18:00 | 120 | 0.153 | 0.825 | 2.3 | 84.15 | 453.75 | 1265 | 1998-11-22 | 3:00 | 129 | NR | NR | NR | NR | NR | NR | 1999-01-18 | 18:00 | 151 | 0.161 | 0.746 | 2 | 88.55 | 410.3 | 1100
1998-06-17 | 4:45 | 134.25 | 0.407 | 0.709 | 4.31 | 223.85 | 389.95 | 2370.5 | 1998-09-08 | 5:15 | 131.25 | 0.204 | 0.845 | 2.77 | 112.2 | 464.75 | 1523.5 | 1998-11-22 | 8:40 | 134.6667 | NR | NR | NR | NR | NR | NR | 1999-01-19 | 1:00 | 158 | 0.174 | 0.742 | 2 | 95.7 | 408.1 | 1100
1998-06-17 | 9:30 | 139 | 0.276 | 0.69 | 2.85 | 151.8 | 379.5 | 1567.5 | 1998-09-08 | 9:00 | 135 | 0.22 | 0.923 | 2.4 | 121 | 507.65 | 1320 | 1998-11-22 | 18:00 | 144 | 0.245 | 0.828 | 2.25 | 134.75 | 455.4 | 1237.5 | 1999-01-19 | 9:00 | 166 | 0.163 | 0.893 | 1.838 | 89.65 | 491.15 | 1010.9
1998-06-17 | 18:00 | 147.5 | 0.24 | 0.763 | 2.43 | 132 | 419.65 | 1336.5 | 1998-09-08 | 18:00 | 144 | 0.242 | 0.831 | 3.2 | 133.1 | 457.05 | 1760 | 1998-11-23 | 2:30 | 152.5 | 0.233 | 0.856 | 2.27 | 128.15 | 470.8 | 1248.5 | 1999-01-19 | 18:00 | 175 | 0.162 | 0.742 | 1.938 | 89.1 | 408.1 | 1065.9
1998-06-18 | 2:30 | 156 | 0.236 | 0.711 | 2.41 | 129.8 | 391.05 | 1325.5 | 1998-09-09 | 6:00 | 156 | 0.244 | 0.828 | 3.28 | 134.2 | 455.4 | 1804 | 1998-11-23 | 8:30 | 158.5 | 0.284 | 0.837 | 2.18 | 156.2 | 460.35 | 1199 | 1999-01-20 | 5:00 | 186 | 0.167 | 0.752 | 1.962 | 91.85 | 413.6 | 1079.1
1998-06-18 | 15:00 | 168.5 | 0.189 | 0.716 | 1.847 | 103.95 | 393.8 | 1015.85 | 1998-09-09 | 9:00 | 159 | NR | NR | NR | NR | NR | NR | 1998-11-23 | 18:00 | 168 | 0.25 | 0.849 | 2.14 | 137.5 | 466.95 | 1177 | 1999-01-20 | 9:00 | 190 | 0.125 | 0.755 | 1.605 | 68.75 | 415.25 | 882.75
1998-06-18 | 18:00 | 171.5 | 0.233 | 0.725 | 2.16 | 128.15 | 398.75 | 1188 | 1998-09-09 | 18:00 | 168 | 0.232 | 0.834 | 2.96 | 127.6 | 458.7 | 1628 | 1998-11-24 | 1:00 | 175 | 0.232 | 0.834 | 2.13 | 127.6 | 458.7 | 1171.5 | 1999-01-20 | 18:00 | 199 | 0.106 | 0.74 | 1.48 | 58.3 | 407 | 814
1998-06-19 | 5:45 | 183.25 | 0.252 | 0.714 | 2.41 | 138.6 | 392.7 | 1325.5 | 1998-09-10 | 6:00 | 180 | 0.242 | 0.826 | 2.89 | 133.1 | 454.3 | 1589.5 | 1998-11-24 | 9:00 | 183 | 0.276 | 0.811 | 2.12 | 151.8 | 446.05 | 1166 | 1999-01-21 | 1:00 | 206 | 0.156 | 0.748 | 2.05 | 85.8 | 411.4 | 1127.5
1998-06-19 | 10:15 | 187.75 | 0.197 | 0.716 | 2.11 | 108.35 | 393.8 | 1160.5 | 1998-09-10 | 9:00 | 183 | 0.322 | 0.835 | 2.76 | 177.1 | 459.25 | 1518 | 1998-11-24 | 18:00 | 192 | 0.234 | 0.837 | 2.15 | 128.7 | 460.35 | 1182.5 | 1999-01-21 | 9:00 | 214 | 0.237 | 0.726 | 2.03 | 130.35 | 399.3 | 1116.5
1998-06-19 | 19:30 | 197 | 0.211 | 0.718 | 2.26 | 116.05 | 394.9 | 1243 | 1998-09-10 | 18:00 | 192 | 0.243 | 0.839 | 3.06 | 133.65 | 461.45 | 1683 | 1998-11-25 | 1:00 | 199 | 0.243 | 0.836 | 2.13 | 133.65 | 459.8 | 1171.5 | 1999-01-21 | 18:00 | 223 | 0.156 | 0.75 | 2.08 | 85.8 | 412.5 | 1144
1998-06-20 | 5:45 | 207.25 | 0.268 | 0.714 | 2.31 | 147.4 | 392.7 | 1270.5 | 1998-09-11 | 6:15 | 204.25 | 0.262 | 0.844 | 3.06 | 144.1 | 464.2 | 1683 | 1998-11-25 | 11:00 | 209 | 0.264 | 0.798 | 2.12 | 145.2 | 438.9 | 1166 | 1999-01-22 | 3:00 | 232 | 0.152 | 0.751 | 2.03 | 83.6 | 413.05 | 1116.5
1998-06-20 | 8:30 | 210 | 0.191 | 0.713 | 1.942 | 105.05 | 392.15 | 1068.1 | 1998-09-11 | 9:00 | 207 | NR | NR | NR | NR | NR | NR | 1998-11-25 | 18:00 | 216 | 0.216 | 0.82 | 2.04 | 118.8 | 451 | 1122 | 1999-01-22 | 15:00 | 244 | 0.127 | 0.764 | 2.02 | 69.85 | 420.2 | 1111
1998-06-20 | 21:30 | 223 | 0.242 | 0.697 | 2.47 | 133.1 | 383.35 | 1358.5 | 1998-09-11 | 16:40 | 214.6667 | NR | NR | NR | NR | NR | NR | 1998-11-26 | 3:00 | 225 | 0.22 | 0.833 | 2.03 | 121 | 458.15 | 1116.5 | 1999-01-22 | 20:00 | 249 | 0.112 | 0.727 | 1.811 | 61.6 | 399.85 | 996.05
1998-06-21 | 6:45 | 232.25 | 0.296 | 0.699 | 2.85 | 162.8 | 384.45 | 1567.5 | 1998-09-12 | 7:00 | 229 | 0.168 | 0.842 | 2.54 | 92.4 | 463.1 | 1397 | 1998-11-26 | 13:00 | 235 | 0.202 | 0.815 | 2.06 | 111.1 | 448.25 | 1133 | 1999-01-23 | 1:00 | 254 | 0.158 | 0.75 | 2.05 | 86.9 | 412.5 | 1127.5
1998-06-21 | 9:00 | 234.5 | 0.292 | 0.698 | 2.89 | 160.6 | 383.9 | 1589.5 | 1998-09-12 | 12:30 | 234.5 | 0.194 | 0.871 | 3.3 | 106.7 | 479.05 | 1815 | 1998-11-26 | 18:00 | 240 | 0.228 | 0.827 | 2.08 | 125.4 | 454.85 | 1144 | 1999-01-23 | 10:00 | 263 | 0.119 | 0.727 | 1.565 | 65.45 | 399.85 | 860.75
1998-06-21 | 18:00 | 243.5 | 0.436 | 0.795 | 4.05 | 239.8 | 437.25 | 2227.5 | 1998-09-12 | 16:45 | 238.75 | 0.155 | 0.843 | 2.21 | 85.25 | 463.65 | 1215.5 | 1998-11-27 | 1:00 | 247 | 0.226 | 0.841 | 2.11 | 124.3 | 462.55 | 1160.5 | 1999-01-23 | 17:30 | 270.5 | 0.134 | 0.754 | 2.11 | 73.7 | 414.7 | 1160.5
1998-06-22 | 6:30 | 256 | 0.205 | 0.716 | 1.846 | 112.75 | 393.8 | 1015.3 | 1998-09-13 | 3:00 | 249 | 0.158 | 0.88 | 2.62 | 86.9 | 484 | 1441 | 1998-11-27 | 14:30 | 260.5 | 0.212 | 0.807 | 1.857 | 116.6 | 443.85 | 1021.35 | 1999-01-24 | 3:00 | 280 | 0.128 | 0.753 | 2.01 | 70.4 | 414.15 | 1105.5
1998-06-22 | 12:30 | 262 | 0.21 | 0.69 | 2.02 | 115.5 | 379.5 | 1111 | 1998-09-13 | 8:45 | 254.75 | NR | NR | NR | NR | NR | NR | 1998-11-27 | 19:00 | 265 | 0.204 | 0.812 | 2.08 | 112.2 | 446.6 | 1144 | 1999-01-24 | 8:45 | 285.75 | 0.095 | 0.727 | 1.388 | 52.25 | 399.85 | 763.4
1998-06-22 | 18:00 | 267.5 | 0.21 | 0.716 | 2.18 | 115.5 | 393.8 | 1199 | 1998-09-13 | 18:00 | 264 | NR | NR | NR | NR | NR | NR | 1998-11-28 | 1:00 | 271 | 0.229 | 0.852 | 2.12 | 125.95 | 468.6 | 1166 | 1999-01-24 | 18:00 | 295 | 0.142 | 0.754 | 2.05 | 78.1 | 414.7 | 1127.5
1998-06-23 | 6:00 | 279.5 | 0.26 | 0.699 | 2.14 | 143 | 384.45 | 1177 | 1998-09-14 | 1:00 | 271 | 0.256 | 0.88 | 2.85 | 140.8 | 484 | 1567.5 | 1998-11-28 | 11:30 | 281.5 | 0.426 | 0.814 | 1.763 | 234.3 | 447.7 | 969.65 | 1999-01-25 | 3:00 | 304 | 0.133 | 0.754 | 2.09 | 73.15 | 414.7 | 1149.5
1998-06-23 | 12:20 | 285.8333 | 0.255 | 0.751 | 2.04 | 140.25 | 413.05 | 1122 | 1998-09-14 | 6:00 | 276 | NR | NR | NR | NR | NR | NR | 1998-11-28 | 19:00 | 289 | 0.197 | 0.856 | 2.14 | 108.35 | 470.8 | 1177 | 1999-01-25 | 9:00 | 310 | 0.122 | 0.853 | 1.835 | 67.1 | 469.15 | 1009.25
1998-06-24 | 6:15 | 303.75 | 0.201 | 0.739 | 1.618 | 110.55 | 406.45 | 889.9 | 1998-09-14 | 18:00 | 288 | 0.14 | 0.825 | 2.2 | 77 | 453.75 | 1210 | 1998-11-29 | 3:00 | 297 | 0.227 | 0.862 | 2.18 | 124.85 | 474.1 | 1199 | 1999-01-25 | 18:00 | 319 | 0.142 | 0.75 | 2.09 | 78.1 | 412.5 | 1149.5
1998-06-26 | 13:40 | 359.1667 | 0.214 | 0.827 | 2.38 | 117.7 | 454.85 | 1309 | 1998-09-15 | 5:30 | 299.5 | 0.173 | 0.834 | 2.34 | 95.15 | 458.7 | 1287 | 1998-11-29 | 8:45 | 302.75 | 0.18 | 0.809 | 1.837 | 99 | 444.95 | 1010.35 | 1999-01-26 | 3:00 | 328 | 0.139 | 0.777 | 2.09 | 76.45 | 427.35 | 1149.5
1998-06-26 | 22:00 | 367.5 | 0.206 | 0.769 | 2.35 | 113.3 | 422.95 | 1292.5 | 1998-09-15 | 9:00 | 303 | NR | NR | NR | NR | NR | NR | 1998-11-29 | 18:00 | 312 | 0.22 | 0.842 | 2.2 | 121 | 463.1 | 1210 | 1999-01-26 | 9:00 | 334 | 0.133 | 0.85 | 1.809 | 73.15 | 467.5 | 994.95
1998-06-27 | 6:30 | 376 | 0.255 | 0.83 | 2.59 | 140.25 | 456.5 | 1424.5 | 1998-09-15 | 18:00 | 312 | 0.158 | 0.825 | 2.3 | 86.9 | 453.75 | 1265 | 1998-11-30 | 3:00 | 321 | NR | NR | NR | NR | NR | NR | 1999-01-26 | 18:00 | 343 | 0.147 | 0.738 | 2.02 | 80.85 | 405.9 | 1111
1998-06-27 | 12:30 | 382 | 0.191 | 0.779 | 5.17 | 105.05 | 428.45 | 2843.5 | 1998-09-16 | 5:45 | 323.75 | 0.168 | 0.828 | 2.26 | 92.4 | 455.4 | 1243 | 1998-11-30 | 9:00 | 327 | 0.232 | 0.852 | 2 | 127.6 | 468.6 | 1100 | 1999-01-27 | 1:00 | 350 | 0.163 | 0.747 | 2.03 | 89.65 | 410.85 | 1116.5
1998-06-27 | 22:00 | 391.5 | 0.394 | 0.72 | 4.8 | 216.7 | 396 | 2640 | 1998-09-16 | 9:00 | 327 | 0.271 | 0.783 | 2.25 | 149.05 | 430.65 | 1237.5 | 1998-11-30 | 18:00 | 336 | 0.217 | 0.835 | 2.12 | 119.35 | 459.25 | 1166 | 1999-01-27 | 9:00 | 358 | 0.152 | 0.891 | 1.868 | 83.6 | 490.05 | 1027.4
1998-06-28 | 18:00 | 411.5 | 0.282 | 0.825 | 2.9 | 155.1 | 453.75 | 1595 | 1998-09-16 | 18:00 | 336 | 0.182 | 0.842 | 2.33 | 100.1 | 463.1 | 1281.5 | 1998-12-01 | 1:00 | 343 | 0.234 | 0.838 | 2.15 | 128.7 | 460.9 | 1182.5 | 1999-01-27 | 18:00 | 367 | 0.16 | 0.776 | 2.14 | 88 | 426.8 | 1177
1998-06-30 | 6:00 | 447.5 | 0.116 | 0.732 | 2.17 | 63.8 | 402.6 | 1193.5 | 1998-09-17 | 0:30 | 342.5 | 0.178 | 0.845 | 2.44 | 97.9 | 464.75 | 1342 | 1998-12-01 | 11:00 | 353 | 0.264 | 0.815 | 2.08 | 145.2 | 448.25 | 1144 | 1999-01-28 | 3:00 | 376 | 0.168 | 0.785 | 2.09 | 92.4 | 431.75 | 1149.5
1998-06-30 | 9:00 | 450.5 | 0.116 | 0.853 | 1.828 | 63.8 | 469.15 | 1005.4 | 1998-09-17 | 9:30 | 351.5 | 0.155 | 0.83 | 2.44 | 85.25 | 456.5 | 1342 | 1998-12-01 | 18:00 | 360 | 0.224 | 0.848 | 2.08 | 123.2 | 466.4 | 1144 | 1999-01-28 | 9:00 | 382 | 0.162 | 0.874 | 1.857 | 89.1 | 480.7 | 1021.35
1998-06-30 | 18:00 | 459.5 | 0.167 | 0.783 | 1.486 | 91.85 | 430.65 | 817.3 | 1998-09-17 | 18:00 | 360 | 0.122 | 0.844 | 2.1 | 67.1 | 464.2 | 1155 | 1998-12-02 | 1:00 | 367 | 0.222 | 0.842 | 2.06 | 122.1 | 463.1 | 1133 | 1999-01-28 | 18:00 | 391 | 0.179 | 0.782 | 2.11 | 98.45 | 430.1 | 1160.5
1998-07-01 | 5:15 | 470.75 | 0.339 | 0.711 | 2.41 | 186.45 | 391.05 | 1325.5 | 1998-09-18 | 7:00 | 373 | 0.196 | 0.868 | 2.44 | 107.8 | 477.4 | 1342 | 1998-12-02 | 11:00 | 377 | 0.235 | 0.801 | 2.06 | 129.25 | 440.55 | 1133 | 1999-01-29 | 1:00 | 398 | 0.186 | 0.789 | 2.16 | 102.3 | 433.95 | 1188
1998-07-01 | 9:00 | 474.5 | 0.24 | 0.918 | 2.07 | 132 | 504.9 | 1138.5 | 1998-09-18 | 11:00 | 377 | 0.128 | 0.823 | 2.09 | 70.4 | 452.65 | 1149.5 | 1998-12-02 | 18:00 | 384 | 0.207 | 0.819 | 2.11 | 113.85 | 450.45 | 1160.5 | 1999-01-29 | 13:00 | 410 | 0.171 | 0.791 | 2.13 | 94.05 | 435.05 | 1171.5
1998-07-01 | 18:00 | 483.5 | 0.261 | 0.745 | 2.27 | 143.55 | 409.75 | 1248.5 | 1998-09-18 | 18:25 | 384.4167 | NR | NR | NR | NR | NR | NR | 1998-12-03 | 1:00 | 391 | 0.234 | 0.823 | 2.12 | 128.7 | 452.65 | 1166 | 1999-01-29 | 17:30 | 414.5 | 0.145 | 0.778 | 1.954 | 79.75 | 427.9 | 1074.7
1998-07-02 | 5:30 | 495 | 0.135 | 0.712 | 2.11 | 74.25 | 391.6 | 1160.5 | 1998-09-19 | 3:30 | 393.5 | 0.191 | 0.865 | 2.44 | 105.05 | 475.75 | 1342 | 1998-12-03 | 9:00 | 399 | 0.271 | 0.792 | 2.06 | 149.05 | 435.6 | 1133 | 1999-01-30 | 1:30 | 422.5 | 0.168 | 0.781 | 1.976 | 92.4 | 429.55 | 1086.8
1998-07-02 | 9:00 | 498.5 | 0.353 | 1.124 | 1.88 | 194.15 | 618.2 | 1034 | 1998-09-19 | 13:20 | 403.3333 | 0.18 | 0.883 | 2.18 | 99 | 485.65 | 1199 | 1998-12-03 | 18:00 | 408 | 0.195 | 0.823 | 2.05 | 107.25 | 452.65 | 1127.5 | 1999-01-30 | 8:50 | 429.8333 | 0.114 | 0.771 | 1.57 | 62.7 | 424.05 | 863.5
1998-07-02 | 18:00 | 507.5 | 0.288 | 0.76 | 2.43 | 158.4 | 418 | 1336.5 | 1998-09-19 | 16:50 | 406.8333 | 0.17 | 0.845 | 2 | 93.5 | 464.75 | 1100 | 1998-12-04 | 1:00 | 415 | 0.198 | 0.626 | 2.11 | 108.9 | 344.3 | 1160.5 | 1999-01-30 | 21:00 | 442 | 0.14 | 0.746 | 1.974 | 77 | 410.3 | 1085.7
1998-07-03 | 6:00 | 519.5 | 0.233 | 0.713 | 2.36 | 128.15 | 392.15 | 1298 | 1998-09-20 | 0:30 | 414.5 | 0.188 | 0.85 | 2.25 | 103.4 | 467.5 | 1237.5 | 1998-12-04 | 10:45 | 424.75 | 0.137 | 0.768 | 1.822 | 75.35 | 422.4 | 1002.1 | 1999-01-31 | 3:00 | 448 | 0.144 | 0.744 | 1.972 | 79.2 | 409.2 | 1084.6
1998-07-03 | 10:30 | 524 | 0.182 | 0.962 | 1.997 | 100.1 | 529.1 | 1098.35 | 1998-09-20 | 8:15 | 422.25 | NR | NR | NR | NR | NR | NR | 1998-12-04 | 21:00 | 435 | 0.179 | 0.794 | 2.04 | 98.45 | 436.7 | 1122 | 1999-01-31 | 8:50 | 453.8333 | 0.135 | 0.761 | 1.735 | 74.25 | 418.55 | 954.25
1998-07-03 | 22:30 | 536 | 0.132 | 0.691 | 2.19 | 72.6 | 380.05 | 1204.5 | 1998-09-20 | 18:00 | 432 | 0.14 | 0.786 | 2.08 | 77 | 432.3 | 1144 | 1998-12-05 | 1:00 | 439 | 0.205 | 0.816 | 2.05 | 112.75 | 448.8 | 1127.5 | 1999-01-31 | 18:00 | 463 | 0.164 | 0.774 | 2.18 | 90.2 | 425.7 | 1199
1998-07-04 | 5:30 | 543 | 0.226 | 0.694 | 3.47 | 124.3 | 381.7 | 1908.5 | 1998-09-21 | 1:00 | 439 | 0.196 | 0.8 | 2.46 | 107.8 | 440 | 1353 | 1998-12-05 | 8:40 | 446.6667 | 0.165 | 0.77 | 1.897 | 90.75 | 423.5 | 1043.35 | 1999-02-01 | 3:00 | 472 | 0.173 | 0.76 | 2.13 | 95.15 | 418 | 1171.5
1998-07-04 | 14:00 | 551.5 | 0.204 | 0.744 | 2.41 | 112.2 | 409.2 | 1325.5 | 1998-09-21 | 9:00 | 447 | NR | NR | NR | NR | NR | NR | 1998-12-05 | 21:00 | 459 | 0.169 | 0.776 | 2.04 | 92.95 | 426.8 | 1122 | 1999-02-01 | 9:00 | 478 | 0.147 | 0.884 | 1.986 | 80.85 | 486.2 | 1092.3
1998-07-04 | 21:30 | 559 | 0.163 | 0.719 | 2.37 | 89.65 | 395.45 | 1303.5 | 1998-09-21 | 12:00 | 450 | NR | NR | NR | NR | NR | NR | 1998-12-06 | 3:00 | 465 | 0.229 | 0.797 | 2.01 | 125.95 | 438.35 | 1105.5 | 1999-02-02 | 2:00 | 495 | 0.177 | 0.773 | 2.12 | 97.35 | 425.15 | 1166
1998-07-05 | 2:00 | 563.5 | 0.222 | 0.731 | 2.18 | 122.1 | 402.05 | 1199 | 1998-09-21 | 18:00 | 456 | 0.312 | 0.844 | 2.21 | 171.6 | 464.2 | 1215.5 | 1998-12-06 | 8:30 | 470.5 | 0.131 | 0.778 | 1.89 | 72.05 | 427.9 | 1039.5 | 1999-02-02 | 9:00 | 502 | 0.151 | 0.909 | 1.666 | 83.05 | 499.95 | 916.3
1998-07-05 | 9:30 | 571 | 0.179 | 0.725 | 2.23 | 98.45 | 398.75 | 1226.5 | 1998-09-22 | 2:00 | 464 | 0.324 | 0.854 | 2.31 | 178.2 | 469.7 | 1270.5 | 1998-12-06 | 21:00 | 483 | 0.175 | 0.783 | 2.08 | 96.25 | 430.65 | 1144 | 1999-02-02 | 18:00 | 511 | 0.16 | 0.77 | 2.02 | 88 | 423.5 | 1111
1998-07-05 | 19:00 | 580.5 | 0.247 | 0.803 | 2.55 | 135.85 | 441.65 | 1402.5 | 1998-09-22 | 10:30 | 472.5 | NR | NR | NR | NR | NR | NR | 1998-12-07 | 3:00 | 489 | 0.184 | 0.798 | 1.824 | 101.2 | 438.9 | 1003.2 | 1999-02-03 | 1:00 | 518 | 0.17 | 0.773 | 2.05 | 93.5 | 425.15 | 1127.5
1998-07-06 | 2:00 | 587.5 | 0.232 | 0.749 | 2.48 | 127.6 | 411.95 | 1364 | 1998-09-22 | 18:00 | 480 | NR | NR | NR | NR | NR | NR | 1998-12-07 | 9:00 | 495 | 0.266 | 0.739 | 2.06 | 146.3 | 406.45 | 1133 | 1999-02-03 | 9:00 | 526 | 0.15 | 0.704 | 2.01 | 82.5 | 387.2 | 1105.5
1998-07-06 | 9:00 | 594.5 | 0.243 | 0.942 | 2.79 | 133.65 | 518.1 | 1534.5 | 1998-09-23 | 2:00 | 488 | 0.43 | 0.933 | 2.73 | 236.5 | 513.15 | 1501.5 | 1998-12-07 | 23:00 | 509 | 0.187 | 0.801 | 2.07 | 102.85 | 440.55 | 1138.5 | 1999-02-03 | 18:00 | 535 | 0.167 | 0.775 | 2.12 | 91.85 | 426.25 | 1166
1998-07-06 | 20:00 | 605.5 | 0.24 | 0.8 | 2.42 | 132 | 440 | 1331 | 1998-09-23 | 9:00 | 495 | NR | NR | NR | NR | NR | NR | 1998-12-08 | 1:00 | 511 | 0.197 | 0.827 | 2.1 | 108.35 | 454.85 | 1155 | 1999-02-04 | 1:00 | 542 | 0.171 | 0.776 | 2.16 | 94.05 | 426.8 | 1188
1998-07-07 | 5:15 | 614.75 | 0.235 | 0.749 | 2.6 | 129.25 | 411.95 | 1430 | 1998-09-23 | 18:00 | 504 | 0.32 | 0.844 | 2.56 | 176 | 464.2 | 1408 | 1998-12-08 | 9:00 | 519 | 0.248 | 0.79 | 2.07 | 136.4 | 434.5 | 1138.5 | 1999-02-04 | 9:00 | 550 | 0.164 | 0.87 | 1.956 | 90.2 | 478.5 | 1075.8
1998-07-07 | 9:00 | 618.5 | 0.243 | 0.948 | 2.32 | 133.65 | 521.4 | 1276 | 1998-09-24 | 6:00 | 516 | 0.323 | 0.867 | 2.53 | 177.65 | 476.85 | 1391.5 | 1998-12-08 | 21:00 | 531 | 0.178 | 0.806 | 2.01 | 97.9 | 443.3 | 1105.5 | 1999-02-04 | 18:00 | 559 | 0.168 | 0.761 | 2.01 | 92.4 | 418.55 | 1105.5
1998-07-07 | 18:00 | 627.5 | 0.292 | 0.767 | 2.51 | 160.6 | 421.85 | 1380.5 | 1998-09-24 | 11:00 | 521 | 0.559 | 0.843 | 2.21 | 307.45 | 463.65 | 1215.5 | 1998-12-09 | 5:00 | 539 | 0.202 | 0.83 | 2.02 | 111.1 | 456.5 | 1111 | 1999-02-05 | 1:00 | 566 | 0.18 | 0.775 | 2.06 | 99 | 426.25 | 1133
1998-07-08 | 5:45 | 639.25 | 0.255 | 0.748 | 2.35 | 140.25 | 411.4 | 1292.5 | 1998-09-24 | 18:00 | 528 | 0.308 | 0.868 | 2.4 | 169.4 | 477.4 | 1320 | 1998-12-09 | 9:00 | 543 | 0.239 | 0.788 | 1.98 | 131.45 | 433.4 | 1089 | 1999-02-05 | 13:00 | 578 | 0.149 | 0.783 | 2.02 | 81.95 | 430.65 | 1111
1998-07-08 | 9:00 | 642.5 | 0.243 | 0.762 | 2.32 | 133.65 | 419.1 | 1276 | 1998-09-25 | 0:45 | 534.75 | 0.298 | 0.877 | 2.36 | 163.9 | 482.35 | 1298 | 1998-12-09 | 21:00 | 555 | 0.185 | 0.807 | 2.06 | 101.75 | 443.85 | 1133 | 1999-02-05 | 16:45 | 581.75 | 0.12 | 0.775 | 1.433 | 66 | 426.25 | 788.15
1998-07-08 | 18:00 | 651.5 | 0.235 | 0.772 | 2.25 | 129.25 | 424.6 | 1237.5 | 1998-09-25 | 14:15 | 548.25 | 0.263 | 0.905 | 2.34 | 144.65 | 497.75 | 1287 | 1998-12-10 | 1:00 | 559 | 0.202 | 0.831 | 2.09 | 111.1 | 457.05 | 1149.5 | 1999-02-06 | 1:00 | 590 | 0.183 | 0.77 | 2.02 | 100.65 | 423.5 | 1111
1998-07-09 | 6:30 | 664 | 0.256 | 0.765 | 2.39 | 140.8 | 420.75 | 1314.5 | 1998-09-25 | 22:00 | 556 | 0.26 | 0.912 | 2.31 | 143 | 501.6 | 1270.5 | 1998-12-10 | 9:00 | 567 | 0.218 | 0.8 | 2.04 | 119.9 | 440 | 1122 | 1999-02-06 | 13:00 | 602 | 0.15 | 0.801 | 2.05 | 82.5 | 440.55 | 1127.5
1998-07-09 | 10:00 | 667.5 | 0.213 | 1.004 | 2.32 | 117.15 | 552.2 | 1276 | 1998-09-26 | 6:45 | 564.75 | 0.278 | 0.878 | 2.36 | 152.9 | 482.9 | 1298 | 1998-12-10 | 21:00 | 579 | 0.179 | 0.808 | 2.07 | 98.45 | 444.4 | 1138.5 | 1999-02-06 | 16:50 | 605.8333 | 0.121 | 0.776 | 1.437 | 66.55 | 426.8 | 790.35
1998-07-09 | 18:00 | 675.5 | 0.23 | 0.781 | 2.13 | 126.5 | 429.55 | 1171.5 | 1998-09-26 | 11:00 | 569 | NR | NR | NR | NR | NR | NR | 1998-12-11 | 1:00 | 583 | 0.21 | 0.831 | 2.08 | 115.5 | 457.05 | 1144 | 1999-02-07 | 3:00 | 616 | 0.143 | 0.782 | 2..07 | 78.65 | 430.1 | #VALUE!
1998-07-10 | 6:30 | 688 | 0.244 | 0.764 | 2.36 | 134.2 | 420.2 | 1298 | 1998-09-26 | 22:30 | 580.5 | 0.254 | 0.927 | 2.29 | 139.7 | 509.85 | 1259.5 | 1998-12-11 | 9:00 | 591 | 0.256 | 0.812 | 2.09 | 140.8 | 446.6 | 1149.5 | 1999-02-07 | 8:40 | 621.6667 | 0.124 | 0.766 | 1.58 | 68.2 | 421.3 | 869
1998-07-10 | 9:00 | 690.5 | 0.239 | 0.555 | 1.734 | 131.45 | 305.25 | 953.7 | 1998-09-27 | 3:00 | 585 | 0.263 | 0.912 | 2.32 | 144.65 | 501.6 | 1276 | 1998-12-11 | 21:00 | 603 | 0.169 | 0.778 | 2.03 | 92.95 | 427.9 | 1116.5 | 1999-02-07 | 18:00 | 631 | 0.166 | 0.772 | 2.08 | 91.3 | 424.6 | 1144
1998-07-10 | 22:00 | 703.5 | 0.14 | 0.767 | 1.931 | 77 | 421.85 | 1062.05 | 1998-09-27 | 11:45 | 593.75 | NR | NR | NR | NR | NR | NR | 1998-12-12 | 3:00 | 609 | 0.279 | 0.838 | 2.08 | 153.45 | 460.9 | 1144 | 1999-02-08 | 3:00 | 640 | 0.183 | 0.768 | 2.08 | 100.65 | 422.4 | 1144
1998-07-11 | 6:00 | 711.5 | 0.206 | 0.769 | 2.58 | 113.3 | 422.95 | 1419 | 1998-09-27 | 22:30 | 604.5 | 0.246 | 0.917 | 2.27 | 135.3 | 504.35 | 1248.5 | 1998-12-12 | 8:45 | 614.75 | 0.159 | 0.784 | 1.993 | 87.45 | 431.2 | 1096.15 | 1999-02-08 | 8:30 | 645.5 | 0.123 | 0.786 | 1.932 | 67.65 | 432.3 | 1062.6
1998-07-11 | 12:15 | 717.75 | 0.221 | 0.803 | 2.2 | 121.55 | 441.65 | 1210 | 1998-09-28 | 1:30 | 607.5 | 0.252 | 0.905 | 2.29 | 138.6 | 497.75 | 1259.5 | 1998-12-12 | 21:00 | 627 | 0.167 | 0.781 | 2.2 | 91.85 | 429.55 | 1210 | 1999-02-08 | 18:00 | 655 | 0.17 | 0.78 | 2.13 | 93.5 | 429 | 1171.5
1998-07-11 | 21:30 | 727 | 0.184 | 0.779 | 2.43 | 101.2 | 428.45 | 1336.5 | 1998-09-28 | 11:00 | 617 | 0.445 | 0.879 | 2.13 | 244.75 | 483.45 | 1171.5 | 1998-12-13 | 3:00 | 633 | 0.179 | 0.788 | 2.23 | 98.45 | 433.4 | 1226.5 | 1999-02-09 | 3:00 | 664 | 0.182 | 0.782 | 2.11 | 100.1 | 430.1 | 1160.5
1998-07-12 | 1:00 | 730.5 | 0.196 | 0.78 | 2.38 | 107.8 | 429 | 1309 | 1998-09-28 | 22:30 | 628.5 | 0.265 | 0.923 | 2.93 | 145.75 | 507.65 | 1611.5 | 1998-12-13 | 10:25 | 640.4167 | 0.17 | 0.783 | 1.995 | 93.5 | 430.65 | 1097.25
1998-07-12 | 10:30 | 740 | 0.292 | 0.782 | 3.53 | 160.6 | 430.1 | 1941.5 | 1998-09-29 | 5:30 | 635.5 | 0.276 | 0.931 | 2.7 | 151.8 | 512.05 | 1485 | 1998-12-13 | 21:00 | 651 | 0.178 | 0.816 | 2.27 | 97.9 | 448.8 | 1248.5
1998-07-12 | 18:00 | 747.5 | 0.45 | 0.82 | 5.13 | 247.5 | 451 | 2821.5 | 1998-09-29 | 9:00 | 639 | 0.265 | 0.923 | 2.24 | 145.75 | 507.65 | 1232 | 1998-12-14 | 3:00 | 657 | 0.158 | 0.781 | 1.984 | 86.9 | 429.55 | 1091.2
1998-07-13 | 1:00 | 754.5 | 0.399 | 0.818 | 5.23 | 219.45 | 449.9 | 2876.5 | 1998-09-29 | 22:30 | 652.5 | 0.251 | 0.886 | 2.65 | 138.05 | 487.3 | 1457.5 | 1998-12-14 | 11:00 | 665 | 0.234 | 0.867 | 2.1 | 128.7 | 476.85 | 1155
1998-07-13 | 9:00 | 762.5 | 0.166 | 0.997 | 1.79 | 91.3 | 548.35 | 984.5 | 1998-09-30 | 5:00 | 659 | 0.27 | 0.915 | 2.6 | 148.5 | 503.25 | 1430 | 1998-12-14 | 21:00 | 675 | 0.18 | 0.833 | 2.07 | 99 | 458.15 | 1138.5
1998-07-13 | 18:00 | 771.5 | 0.17 | 0.788 | 2.13 | 93.5 | 433.4 | 1171.5 | 1998-09-30 | 5:00 | 659 | 0.27 | 0.915 | 2.6 | 148.5 | 503.25 | 1430 | 1998-12-15 | 3:00 | 681 | 0.2 | 0.871 | 2.12 | 110 | 479.05 | 1166
1998-07-14 | 9:00 | 786.5 | 0.168 | 0.776 | 2.25 | 92.4 | 426.8 | 1237.5 | [9 empty] | 1998-12-15 | 10:00 | 688 | 0.205 | 0.98 | 1.985 | 112.75 | 539 | 1091.75
[18 empty] | 1998-12-15 | 21:00 | 699 | 0.179 | 0.839 | 2.11 | 98.45 | 461.45 | 1160.5
[18 empty] | 1998-12-16 | 1:00 | 703 | 0.201 | 0.86 | 2.12 | 110.55 | 473 | 1166
[18 empty] | 1998-12-16 | 9:00 | 711 | 0.276 | 0.805 | 2.09 | 151.8 | 442.75 | 1149.5

## NF70. 1st Quarter
FIELD-SET 1: 1st QUARTER SEBST RESULTS (FILE: Film Tec.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: SEBST Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 1-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 1-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 1-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 1-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 1-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [19 empty] | 0.72266 |  | 13.7338 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | FilmTec Corp. | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale |  | Date | Time | Operation | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH |  | TDS (mg/L) | [11 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.71 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | 0.73 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL 5360313 | Membrane trade name | FILMTEC | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.38079 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale | DAYS | MM/DD/YY | hh:mm | Time | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 0.98 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | NF70-4040 |  |  | LSI | 0.14 | Hydrochloric acid addition | pH = 6.4 | Pilot-scale | 1 | 1998-06-11 | 14:30 | 0 | 29.4 | 45 | 43 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.7432 | 7.9849 | 36.0151 | 0.32606 | 5.4 | 7 | 6.1 | 160.05 | 394.9 | 1111 | 1021.1667 | 8.0858 | 59.4708 | 958.54 | 83.3027 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.18 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.26 |  |  |  | 1 | 1998-06-11 | 18:00 | 3.5 | 29.1 | 45 | 43 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.8478 | 9.4435 | 34.5565 | 0.34285 | 5.5 | 7.3 | 6.3 | 165 | 442.75 | 1116.5 | 1183.4167 | -5.9934 | 62.7329 | 1109.35 | 85.1264 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | discriminating | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.35 |  |  |  | 2 | 1998-06-12 | 6:45 | 16.25 | 26.6 | 43 | 41 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.27287 | 0.7 | 4.2 | 12.6 | 11.1619 | 7.1475 | 34.8525 | 0.32026 | 5.4 | 7.2 | 6.1 | 169.4 | 399.3 | 1122 | 935.7333 | 16.6013 | 57.5758 | 884.1532 | 80.8404 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 2 | 1998-06-12 | 14:00 | 23.5 | 29.5 | 40 | 38 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 11.7085 | 8.4588 | 30.5412 | 0.38337 | 5.5 | 7.2 | 6.2 | 144.1 | 393.25 | 1080.75 | 1057.65 | 2.1374 | 63.3566 | 989.9796 | 85.4441 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 (dup) | CF-4 (dup) | CC-4 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Permeate flow rate, Qp (gpm) | 0.83333 | Total aluminum (mg/L) | 0.11 |  |  |  | 2 | 1998-06-12 | 18:00 | 27.5 | 28.8 | 44 | 42 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.9533 | 7.8353 | 35.1647 | 0.33992 | 5.5 | 7.3 | 6.2 | 161.7 | 392.15 | 1144 | 1006.6833 | 12.0032 | 58.7658 | 945.23 | 82.8931 | [16 empty] | Sampling date | MM/DD/YY | 1998-06-22 | 1998-06-22 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-30 | 1998-06-30 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-06 | 1998-07-06 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.1111 | Fluoride (mg/L) | 0.41 |  |  |  | 3 | 1998-06-13 | 5:30 | 39 | 26.5 | 46 | 44 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.9946 | 9.9845 | 35.0155 | 0.34255 | 6.4 | 7.3 | 7.6 | 94.05 | 400.4 | 1081.3 | 1166.275 | -7.8586 | 76.511 | 1092.4981 | 91.3913 | [16 empty] | Sampling time | hh:mm | 12:30 | 12:30 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27778 | (Ortho) Phosphate (mg/L) | 0.098 |  |  |  | 3 | 1998-06-13 | 8:30 | 42 | 28.6 | 49 | 47 | 0 | 4.5 | 0.7 | 0.3 |  | 1 | 5.5 | 0.28975 | 0.7 | 4.5 | 12.6 | 10.5212 | 9.579 | 38.421 | 0.27384 | 6.4 | 7.2 | 7.5 | 85.25 | 392.15 | 1010.35 | 1108.25 | -9.6897 | 78.2609 | 1043.15 | 91.8276 | [16 empty] | Operation time | hh.hh | 262 | 262 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 450.5 | 450.5 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 594.5 | 594.5 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 762.5 | 762.5 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 762.5 | 762.5 | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
|  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 3 | Sulfate (mg/L) | 31 |  |  |  | 3 | 1998-06-13 | 21:00 | 54.5 | 28.2 | 48 | 46 | 0 | 4.5 | 0.72 | 0.3 |  | 1.02 | 5.52 | 0.29032 | 0.70588 | 4.4118 | 12.96 | 10.9505 | 7.7264 | 39.2736 | 0.27882 | 5.6 | 7.3 | 6.3 | 151.8 | 394.9 | 1122 | 978.34 | 12.8039 | 61.5599 | 924.4352 | 83.5792 | [16 empty] | pH | --- | 5.22 | 7.05 | NA | --- | --- | --- | --- | --- | pH | --- | 5 | 7.37 | NA | --- | --- | --- | --- | --- | pH | --- | 5.36 | 7.57 | NA | --- | --- | --- | --- | --- | pH | --- | 5.75 | 7.15 | NA | --- | --- | --- | --- | --- | pH | --- | 5.72 | 7.19 | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 83 |  |  |  | 4 | 1998-06-14 | 6:30 | 64 | 27.9 | 53 | 51 | 0 | 4.5 | 0.62 | 0.3 |  | 0.92 | 5.42 | 0.2875 | 0.67391 | 4.8913 | 11.16 | 9.5136 | 7.2672 | 44.7328 | 0.21268 | 4.3 | 7.2 | 4.6 | 143.55 | 394.9 | 1298 | 914.3567 | 29.5565 | 63.649 | 870.2699 | 83.5051 | [16 empty] | Temperature | oC | 26.7 | 26.7 | NA | --- | --- | --- | --- | --- | Temperature | oC | 28.2 | 28.2 | NA | --- | --- | --- | --- | --- | Temperature | oC | 28 | 28 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.2 | 27.2 | NA | --- | --- | --- | --- | --- | Temperature | oC | 27.2 | 27.2 | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.016 |  |  |  | 4 | 1998-06-14 | 14:00 | 71.5 | 29.3 | 52 | 50 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.7779 | 11.0891 | 39.9109 | 0.29511 | 6.2 | 7.1 | 7.5 | 70.4 | 396.55 | 1037.3 | 1266.2833 | -22.0749 | 82.2469 | 1179.31 | 94.0304 | [16 empty] | Total Alkalinity | mg/L as CaCO3 | 12 | 240 | NA | 798.2069 | #VALUE! | 95 | 745.4035 | 98.3901 | Alkalinity | mg/L as CaCO3 | 28 | 240 | NA | 813.1852 | #VALUE! | 88.3333 | 755.8667 | 96.2956 | Alkalinity | mg/L as CaCO3 | 14 | 250 | NA | 888.0741 | #VALUE! | 94.4 | 824.2667 | 98.3015 | Alkalinity | mg/L as CaCO3 | 23 | 250 | NA | 863.7407 | #VALUE! | 90.8 | 802.3667 | 97.1335 | Alkalinity | mg/L as CaCO3 | 24 | 250 | NA | 861.037 | #VALUE! | 90.4 | 799.9333 | 96.9997 | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 28.7 | Design recycle flow rate, QR (gpm) | 4.3889 | Strontium (mg/L) | 0.13 |  |  |  | 4 | 1998-06-14 | 18:00 | 75.5 | 28.9 | 51 | 49 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.918 | 9.3313 | 40.6687 | 0.29305 | 5.6 | 7.4 | 6.6 | 136.4 | 410.85 | 1204.5 | 1142.7167 | 5.1294 | 66.8005 | 1069.53 | 87.2467 | [16 empty] | Total dissolved solids | mg/L | 210 | 430 | NA | 968.6207 | #VALUE! | 51.1628 | 917.6701 | 77.116 | Total dissolved solids | mg/L | 66 | 450 | NA | 1488.2222 | #VALUE! | 85.3333 | 1384.4 | 95.2326 | Total dissolved solids | mg/L | 140 | 440 | NA | 1251.1111 | #VALUE! | 68.1818 | 1170 | 88.0342 | Total dissolved solids | mg/L | 81 | 490 | NA | 1595.8148 | #VALUE! | 83.4694 | 1485.2333 | 94.5463 | Total dissolved solids | mg/L | 84 | 510 | NA | 1661.7778 | #VALUE! | 83.5294 | 1546.6 | 94.5687 | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Recycle ratio, r | 3.95 | Reactive silica (mg/L as SiO2) | 34 |  |  |  | 5 | 1998-06-15 | 6:30 | 88 | 27.3 | 47 | 46 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.4952 | 9.9297 | 36.5703 | 0.34168 | 5.7 | 7.3 | 6.6 | 101.2 | 393.25 | 1026.3 | 1172.05 | -14.2015 | 74.2657 | 1094.17 | 90.751 | [16 empty] | Total hardness | mg/L as CaCO3 | 44 | 270 | NA | 823.3103 | #VALUE! | 83.7037 | 770.9702 | 94.2929 | Total hardness | mg/L as CaCO3 | 13 | 270 | NA | 964.8519 | #VALUE! | 95.1852 | 895.3667 | 98.5481 | Total hardness | mg/L as CaCO3 | 34 | 280 | NA | 945.1111 | #VALUE! | 87.8571 | 878.6 | 96.1302 | Total hardness | mg/L as CaCO3 | 17 | 270 | NA | 954.037 | #VALUE! | 93.7037 | 885.6333 | 98.0805 | Total hardness | mg/L as CaCO3 | 16 | 280 | NA | 993.7778 | #VALUE! | 94.2857 | 922.4 | 98.2654 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.41 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | NR |  |  |  | 5 | 1998-06-15 | 9:30 | 91 | 27.5 | 47 | 45 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.4216 | 9.9671 | 36.0329 | 0.34473 | 5.7 | 7.2 | 6.6 | 102.3 | 395.45 | 1099.45 | 1177.1833 | -7.0702 | 74.1307 | 1099.01 | 90.6916 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 36 | 210 | NA | 636 | #VALUE! | 82.8571 | 595.7027 | 93.9567 | Calcium hardness | mg/L as CaCO3 | 9.6 | 220 | NA | 788.8593 | #VALUE! | 95.6364 | 731.9733 | 98.6885 | Calcium hardness | mg/L as CaCO3 | 22 | 220 | NA | 755.3333 | #VALUE! | 90 | 701.8 | 96.8652 | Calcium hardness | mg/L as CaCO3 | 12 | 210 | NA | 745.3333 | #VALUE! | 94.2857 | 691.8 | 98.2654 | Calcium hardness | mg/L as CaCO3 | 13 | 210 | NA | 742.6296 | #VALUE! | 93.8095 | 689.3667 | 98.1142 | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 3.2 |  |  |  | 5 | 1998-06-15 | 18:00 | 99.5 | 29.2 | 53 | 50 | 0 | 4.4 | 0.8 | 0.25 |  | 1.05 | 5.45 | 0.28413 | 0.7619 | 4.1905 | 14.4 | 11.8128 | 11.216 | 40.284 | 0.29324 | 5.5 | 7.3 | 6.5 | 146.3 | 434.5 | 1320 | 1356.74 | -2.7833 | 66.3291 | 1267.9004 | 88.4612 | [16 empty] | Turbidity | ntu | BMRL | 7 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.1 | 3 | NA | 10.8407 | #VALUE! | 96.6667 | 10.0567 | 99.0056 | Turbidity | ntu | 0.1 | 11 | NA | 40.4704 | #VALUE! | 99.0909 | 37.5233 | 99.7335 | Turbidity | ntu | 0.1 | 0.8 | NA | 2.6926 | #VALUE! | 87.5 | 2.5033 | 96.0053 | Turbidity | ntu | 0.1 | 0.87 | NA | 2.9519 | #VALUE! | 88.5057 | 2.7437 | 96.3552 | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 6 | 1998-06-16 | 6:45 | 112.25 | 27.6 | 55 | 53 | 0 | 4.4 | 0.8 | 0.2 |  | 1 | 5.4 | 0.28131 | 0.8 | 4.4 | 14.4 | 12.3849 | 11.713 | 42.287 | 0.29288 | 5.6 | 7.3 | 6.5 | 148.5 | 401.5 | 1518 | 1413.5 | 6.8841 | 63.0137 | 1319.7963 | 88.7483 | [16 empty] | Nitrogen - Ammonia | mg NH3-N / L | 0.37 | 0.4 | NA | 0.47345 | #VALUE! | 7.5 | 0.4665 | 20.686 | Ammonia | mg NH3-N / L | 0.31 | 0.64 | NA | 1.5322 | #VALUE! | 51.5625 | 1.443 | 78.517 | Ammonia | mg NH3-N / L | 0.54 | 0.52 | NA | 0.46593 | #VALUE! | -3.8462 | 0.47133 | -14.5686 | Ammonia | mg NH3-N / L | 0.25 | 0.48 | NA | 1.1019 | #VALUE! | 47.9167 | 1.0397 | 75.9538 | Ammonia | mg NH3-N / L | 0.25 | 0.49 | NA | 1.1389 | #VALUE! | 48.9796 | 1.074 | 76.7225
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 6 | 1998-06-16 | 11:00 | 116.5 | 28.8 | 56 | 54 | 0 | 4.6 | 0.75 | 0.3 |  | 1.05 | 5.65 | 0.29679 | 0.71429 | 4.381 | 13.5 | 11.2062 | 7.3687 | 47.6313 | 0.23527 | 5.5 | 7.3 | 6.5 | 148.5 | 374 | 1573 | 937.75 | 40.3846 | 60.2941 | 885.3662 | 83.2273 | [16 empty] | Total organic carbon | mg/L | 0.7 | 5 | NA | 15.5276 | #VALUE! | 86 | 14.5317 | 95.183 | Total organic carbon | mg/L | 0.7 | 5.9 | NA | 19.9593 | #VALUE! | 88.1356 | 18.5533 | 96.2271 | Total organic carbon | mg/L | 0.7 | 5.9 | NA | 19.9593 | #VALUE! | 88.1356 | 18.5533 | 96.2271 | Total organic carbon | mg/L | 0.7 | 5.7 | NA | 19.2185 | #VALUE! | 87.7193 | 17.8667 | 96.0821 | Total organic carbon | mg/L | 0.7 | 5.7 | NA | 19.2185 | #VALUE! | 87.7193 | 17.8667 | 96.0821
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 6 | 1998-06-16 | 18:00 | 123.5 | 29.3 | 54 | 51 | 0 | 4.5 | 0.75 | 0.3 |  | 1.05 | 5.55 | 0.29116 | 0.71429 | 4.2857 | 13.5 | 11.0418 | 7.79 | 44.71 | 0.24697 | 5.5 | 7.3 | 6.4 | 236.5 | 475.2 | 2035 | 1071.95 | 47.3243 | 50.2315 | 1015.5007 | 76.711 | [16 empty] | UV254 | cm-1 | 0.009 | 0.24 | NA | 0.80555 | #VALUE! | 96.25 | 0.75205 | 98.8033 | UV254 | cm-1 | 0.016 | 0.26 | NA | 0.9197 | #VALUE! | 93.8462 | 0.85373 | 98.1259 | UV254 | cm-1 | 0.009 | 0.26 | NA | 0.93863 | #VALUE! | 96.5385 | 0.87077 | 98.9664 | UV254 | cm-1 | 0.009 | 0.23 | NA | 0.82752 | #VALUE! | 96.087 | 0.76777 | 98.8278 | UV254 | cm-1 | 0.007 | 0.22 | NA | 0.79589 | #VALUE! | 96.8182 | 0.7383 | 99.0519
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.003 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 7 | 1998-06-17 | 4:45 | 134.25 | 28.1 | 57 | 55 | 0 | 4.6 | 0.7 | 0.3 |  | 1 | 5.6 | 0.29538 | 0.7 | 4.6 | 12.6 | 10.6778 | 5.1906 | 50.8094 | 0.21015 | 5.5 | 7.3 | 6.2 | 223.85 | 389.95 | 2370.5 | 777.5167 | 67.2003 | 42.5952 | 742.9125 | 69.8686 | [16 empty] | SUVA | L/(mg*m) | 1.2857 | 4.8 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.2857 | 4.4068 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.2857 | 4.4068 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.2857 | 4.0351 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1 | 3.8596 | NA | --- | --- | --- | --- | ---
Process Train Name | SEBST | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 7 | 1998-06-17 | 9:30 | 139 | 28.2 | 53 | 50 | 0 | 4.5 | 0.75 | 0.3 |  | 1.05 | 5.55 | 0.29116 | 0.71429 | 4.2857 | 13.5 | 11.4067 | 7.431 | 44.069 | 0.25884 | 5.6 | 7.3 | 6.4 | 151.8 | 379.5 | 1567.5 | 948.75 | 39.4737 | 60 | 894.902 | 83.0372 | [16 empty] | Bromide | mg/L | 80 | 200 | NA | 493.7931 | --- | 60 | 466.0019 | 82.8327 | Bromide | mg/L | 54 | 200 | NA | 594.7407 | --- | 73 | 555.2667 | 90.2749 | Bromide | mg/L | 67 | 220 | NA | 633.6667 | --- | 69.5455 | 592.3 | 88.6882 | Bromide | mg/L | 200 | 200 | NA | 200 | --- | 0 | 200 | 0 | Bromide | mg/L | 33 | 200 | NA | 651.5185 | --- | 83.5 | 606.3667 | 94.5577
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 7 | 1998-06-17 | 18:00 | 147.5 | 28.8 | 54 | 51 | 0 | 4.4 | 0.8 | 0.25 |  | 1.05 | 5.45 | 0.28413 | 0.7619 | 4.1905 | 14.4 | 11.9533 | 11.1946 | 41.3054 | 0.28939 | 5.6 | 7.3 | 6.5 | 132 | 419.65 | 1336.5 | 1340.13 | -0.2716 | 68.5452 | 1251.4599 | 89.4523 | [16 empty] | SDS-Cl2 dose | mg/L | 10 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 11 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 11 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 10 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 10 | NR | NA | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1154.0984 | [5 empty] | 8 | 1998-06-18 | 2:30 | 156 | 26.3 | 53 | 51 | 0 | 4.2 | 0.75 | 0.25 |  | 1 | 5.2 | 0.27147 | 0.75 | 4.2 | 13.5 | 12.0657 | 9.6964 | 42.3036 | 0.28522 | 5.7 | 7.3 | 6.6 | 129.8 | 391.05 | 1325.5 | 1174.8 | 11.3693 | 66.8073 | 1099.4394 | 88.194 | [16 empty] | SDS-Free Cl2 residual | mg/L | 0.91 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.2 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.65 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.65 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.8 | NR | NA | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 201.9672 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 8 | 1998-06-18 | 15:00 | 168.5 | 28.6 | 48 | 46 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 12.0242 | 9.8406 | 37.1594 | 0.32358 | 5.7 | 7.3 | 6.6 | 103.95 | 393.8 | 1015.85 | 1166.7333 | -14.8529 | 73.6034 | 1088.0086 | 90.4458 | [16 empty] | SDS-Cl2 demand | mg/L | 9.09 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 9.8 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 10.35 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 9.35 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 9.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | see guidelines | Influent TDS, TDSI (mg/L) | 1009.8361 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 8 | 1998-06-18 | 18:00 | 171.5 | 28 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7094 | 8.4354 | 49.5646 | 0.21607 | 5.6 | 7.3 | 6.5 | 128.15 | 398.75 | 1188 | 1030.15 | 13.287 | 67.8621 | 971.687 | 86.8116 | [16 empty] | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | see guidelines | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 9 | 1998-06-19 | 5:45 | 183.25 | 27 | 52 | 50 | 0 | 4.6 | 0.75 | 0.25 |  | 1 | 5.6 | 0.29397 | 0.75 | 4.6 | 13.5 | 11.8186 | 9.4834 | 41.5166 | 0.28467 | 5.7 | 7.4 | 6.5 | 138.6 | 392.7 | 1325.5 | 1155 | 12.8631 | 64.7059 | 1086.9375 | 87.2486 | [16 empty] | SDS-Chlorination pH | --- | 8 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.01 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.98 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.99 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.02 | NR | NA | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 9 | 1998-06-19 | 10:15 | 187.75 | 28.6 | 52 | 49 | 0 | 4.4 | 0.75 | 0.23 |  | 0.98 | 5.38 | 0.2816 | 0.76531 | 4.4898 | 13.5 | 11.2727 | 11.3149 | 39.1851 | 0.28768 | 5.7 | 7.3 | 6.6 | 108.35 | 393.8 | 1160.5 | 1324.6152 | -14.1418 | 72.486 | 1239.8384 | 91.261 | [16 empty] | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 9 | 1998-06-19 | 19:30 | 197 | 29 | 52 | 50 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.8828 | 9.4809 | 41.5191 | 0.2862 | 5.5 | 7.2 | 6.5 | 116.05 | 394.9 | 1243 | 1138.5 | 8.4071 | 70.6128 | 1064.14 | 89.0945 | [16 empty] | SDS-TOX | mg Cl- /L | 112 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 23 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 51 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 30 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | MgSO4 2000 mg/l | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 10 | 1998-06-20 | 5:45 | 207.25 | 27.8 | 52 | 50 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3119 | 8.3402 | 42.6598 | 0.28861 | 5.6 | 7.3 | 6.5 | 147.4 | 392.7 | 1270.5 | 1046.8333 | 17.6046 | 62.465 | 981.42 | 84.9809 | [16 empty] | SDS-CHCl3 | mg/L | 15 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 74 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 3.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) | >90 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 10 | 1998-06-20 | 8:30 | 210 | 27.9 | 52 | 50 | 0 | 4.4 | 0.8 | 0.27 |  | 1.07 | 5.47 | 0.28525 | 0.74766 | 4.1121 | 14.4 | 12.2756 | 10.5457 | 40.4543 | 0.30344 | 5.7 | 7.3 | 6.6 | 105.05 | 392.15 | 1068.1 | 1242.8167 | -16.3577 | 73.2118 | 1159.6162 | 90.941 | [16 empty] | SDS-BDCM | mg/L | 7.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 5.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 3.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 1.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | n/a | Required influent pressure, PI (psi) | 50.1913 | [5 empty] | 10 | 1998-06-20 | 21:30 | 223 | 28 | 51 | 49 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2393 | 8.5085 | 41.4915 | 0.29498 | 5.5 | 7.2 | 6.3 | 133.1 | 383.35 | 1358.5 | 1050.6833 | 22.6586 | 65.2798 | 983.95 | 86.4729 | [16 empty] | SDS-DBCM | mg/L | 17 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 6.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 4.8 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 1.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 20 | [7 empty] | 11 | 1998-06-21 | 6:45 | 232.25 | 27.6 | 54 | 52 | 0 | 4.6 | 0.7 | 0.3 |  | 1 | 5.6 | 0.29538 | 0.7 | 4.6 | 12.6 | 10.8368 | 6.9266 | 46.0734 | 0.23521 | 5.7 | 7.3 | 6.5 | 162.8 | 384.45 | 1567.5 | 901.6333 | 42.4795 | 57.6538 | 855.4562 | 80.9692 | [16 empty] | SDS-CHBr3 | mg/L | 11 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 0.64 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7 | [7 empty] | 11 | 1998-06-21 | 9:00 | 234.5 | 27 | 54 | 52 | 0 | 4.5 | 0.7 | 0.3 |  | 1 | 5.5 | 0.28975 | 0.7 | 4.5 | 12.6 | 11.0307 | 6.9697 | 46.0303 | 0.23964 | 5.6 | 7.3 | 6.4 | 160.6 | 383.9 | 1589.5 | 904.9333 | 43.0681 | 58.1662 | 857.5667 | 81.2726 | [16 empty] | SDS-THM4 | mg/L | 50.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 86.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 12.24 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 3.8 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 6.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 50-250 | [7 empty] | 11 | 1998-06-21 | 18:00 | 243.5 | 29.9 | 51 | 49 | 0 | 4.4 | 0.6 | 0.3 |  | 0.9 | 5.3 | 0.28131 | 0.66667 | 4.8889 | 10.8 | 8.6782 | 5.5882 | 44.4118 | 0.1954 | 5.6 | 7.3 | 6.6 | 239.8 | 437.25 | 2227.5 | 832.15 | 62.642 | 45.1572 | 798.6208 | 69.9732 | [16 empty] | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | 2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [7 empty] | 12 | 1998-06-22 | 6:30 | 256 | 27.2 | 50 | 48 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.28328 | 0.69072 | 4.5361 | 12.06 | 10.4957 | 8.5204 | 40.4796 | 0.25928 | 5.7 | 7.3 | 6.6 | 112.75 | 393.8 | 1015.3 | 1021.4783 | -0.60852 | 71.3687 | 964.7886 | 88.3135 | [16 empty] | SDS-DCAA* | mg/L | 2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 4 | [7 empty] | 12 | 1998-06-22 | 12:30 | 262 | 26.7 | 44 | 42 | 0 | 4.2 | 0.7 | 0.28 |  | 0.98 | 5.18 | 0.27175 | 0.71429 | 4.2857 | 12.6 | 11.129 | 8.6157 | 34.3843 | 0.32366 | 5.8 | 7.1 | 6.1 | 115.5 | 379.5 | 1111 | 1039.5 | 6.4356 | 69.5652 | 977.0676 | 88.1789 | [16 empty] | SDS-TCAA* | mg/L | 1.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 12 | 1998-06-22 | 18:00 | 267.5 | 29.6 | 51 | 49 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.674 | 9.4622 | 40.5378 | 0.28798 | 5.7 | 7.3 | 6.7 | 115.5 | 393.8 | 1199 | 1135.9333 | 5.2599 | 70.6704 | 1061.72 | 89.1214 | [16 empty] | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 13 | 1998-06-23 | 6:00 | 279.5 | 26.8 | 44 | 41 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.3035 | 7.1814 | 35.3186 | 0.29173 | 5.7 | 7.3 | 6.5 | 143 | 384.45 | 1177 | 907.5917 | 22.8894 | 62.804 | 861.1445 | 83.3942 | [16 empty] | SDS-DBAA* | mg/L | 4.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 13 | 1998-06-23 | 12:20 | 285.8333 | 27.6 | 50 | 49 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 9.2752 | 40.2248 | 0.30789 | 5.4 | 7.2 | 6.2 | 140.25 | 413.05 | 1122 | 1140.5167 | -1.6503 | 66.0453 | 1067.77 | 86.8651 | [16 empty] | SDS-BCAA* | mg/L | 2.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 14 | 1998-06-24 | 6:15 | 303.75 | 26.7 | 50 | 48 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.129 | 9.224 | 39.776 | 0.27979 | 5.6 | 7.3 | 6.3 | 110.55 | 406.45 | 889.9 | 1096.8833 | -23.2592 | 72.8011 | 1032.9543 | 89.2977 | [16 empty] | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 16 | 1998-06-26 | 13:40 | 359.1667 | 28.7 | 57 | 55 | 0 | 4.4 | 0.78 | 0.3 |  | 1.08 | 5.48 | 0.28638 | 0.72222 | 4.0741 | 14.04 | 11.689 | 11.2736 | 44.7264 | 0.26134 | 5.7 | 7.3 | 6.5 | 117.7 | 454.85 | 1309 | 1331.44 | -1.7143 | 74.1233 | 1245.0607 | 90.5466 | [16 empty] | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 16 | 1998-06-26 | 22:00 | 367.5 | 29 | 56 | 54 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.8828 | 10.5281 | 44.4719 | 0.2672 | 5.1 | 7.2 | 6.2 | 113.3 | 422.95 | 1292.5 | 1248.6833 | 3.3901 | 73.212 | 1166.11 | 90.2839 | [16 empty] | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 17 | 1998-06-27 | 6:30 | 376 | 26.9 | 55 | 53 | 0 | 4.5 | 0.75 | 0.3 |  | 1.05 | 5.55 | 0.29116 | 0.71429 | 4.2857 | 13.5 | 11.8536 | 10.3209 | 43.6791 | 0.27138 | 5.6 | 7.3 | 6.4 | 140.25 | 456.5 | 1424.5 | 1247.125 | 12.4517 | 69.2771 | 1172.3361 | 88.0367 | [16 empty] | SDS-HAA5 | mg/L | 8 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 17 | 1998-06-27 | 12:30 | 382 | 28.8 | 54 | 52 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 11.9533 | 10.9796 | 42.0204 | 0.28446 | 5.6 | 7.3 | 6.4 | 105.05 | 428.45 | 2843.5 | 1290.85 | 54.6035 | 75.4814 | 1203.013 | 91.2678 | [16 empty] | SDS-HAA6 | mg/L | 10.6 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 17 | 1998-06-27 | 22:00 | 391.5 | 28.2 | 86 | 84 | 14 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 12.1672 | 6.0873 | 64.9127 | 0.18744 | 5.2 | 7.2 | 5.6 | 216.7 | 396 | 2640 | 874.1333 | 66.8889 | 45.2778 | 825.4346 | 73.7472 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 18 | 1998-06-28 | 18:00 | 411.5 | 27.8 | 57 | 55 | 0 | 4.4 | 0.75 | 0.2 |  | 0.95 | 5.35 | 0.27991 | 0.78947 | 4.6316 | 13.5 | 11.5424 | 13.1915 | 42.8085 | 0.26963 | 5.4 | 7.2 | 6.2 | 155.1 | 453.75 | 1595 | 1573.6875 | 1.3362 | 65.8182 | 1474.2538 | 89.4794 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 20 | 1998-06-30 | 6:00 | 447.5 | 26.6 | 60 | 57 | 0 | 4.4 | 1.05 | 0.3 |  | 1.35 | 5.75 | 0.29397 | 0.77778 | 3.2593 | 18.9 | 16.7428 | 13.854 | 44.646 | 0.37501 | 6.2 | 7.3 | 6.6 | 63.8 | 402.6 | 1193.5 | 1588.4 | -33.0876 | 84.153 | 1449.1974 | 95.5976
[11 empty] | 20 | 1998-06-30 | 9:00 | 450.5 | 28.2 | 58 | 56 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1672 | 13.7819 | 43.2181 | 0.28153 | 5.9 | 7.2 | 7.2 | 63.8 | 469.15 | 1005.4 | 1550.0833 | -54.1758 | 86.4009 | 1441.99 | 95.5756 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 20 | 1998-06-30 | 18:00 | 459.5 | 28 | 59 | 56 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2393 | 11.5192 | 45.9808 | 0.26618 | 6.2 | 7.3 | 7.5 | 91.85 | 430.65 | 817.3 | 1334.1167 | -63.2346 | 78.6718 | 1243.77 | 92.6152 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 21 | 1998-07-01 | 5:15 | 470.75 | 26.8 | 79 | 77 | 7 | 4.2 | 1 | 0.35 |  | 1.35 | 5.55 | 0.28413 | 0.74074 | 3.1111 | 18 | 15.8516 | 7.1807 | 63.8193 | 0.24838 | 3.6 | 7.2 | 6.6 | 186.45 | 391.05 | 1325.5 | 975.6214 | 26.396 | 52.3207 | 904.5249 | 79.387 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 21 | 1998-07-01 | 9:00 | 474.5 | 28.1 | 55 | 52 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 12.6786 | 40.8214 | 0.29894 | 5 | 7 | 6 | 132 | 504.9 | 1138.5 | 1499.3 | -31.6908 | 73.8562 | 1399.86 | 90.5705 | [16 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE!
[11 empty] | 21 | 1998-07-01 | 18:00 | 483.5 | 28.9 | 54 | 51 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.1731 | 8.6759 | 43.8241 | 0.25495 | 5.4 | 7.2 | 6 | 143.55 | 409.75 | 1248.5 | 1075.25 | 13.8767 | 64.9664 | 1011.1422 | 85.8032 | [16 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE!
[11 empty] | 22 | 1998-07-02 | 5:30 | 495 | 28.1 | 55 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6778 | 9.8927 | 43.6073 | 0.24486 | 6.4 | 7.3 | 7.6 | 74.25 | 391.6 | 1160.5 | 1132.0833 | 2.4487 | 81.0393 | 1063.5201 | 93.0185 | [16 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE!
[11 empty] | 22 | 1998-07-02 | 9:00 | 498.5 | 28.3 | 52 | 52 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1313 | 14.4177 | 37.5823 | 0.32279 | 5.8 | 7 | 5.3 | 194.15 | 618.2 | 1034 | 1749 | -69.1489 | 68.5943 | 1635.92 | 88.1321 | [16 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE!
[11 empty] | 22 | 1998-07-02 | 18:00 | 507.5 | 28.9 | 56 | 53 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.918 | 8.8264 | 45.6736 | 0.26094 | 5.2 | 7.2 | 5.6 | 158.4 | 418 | 1336.5 | 1110.2667 | 16.9273 | 62.1053 | 1041.04 | 84.7844 | [16 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE!
[11 empty] | 23 | 1998-07-03 | 6:00 | 519.5 | 26.8 | 57 | 55 | 0 | 4.6 | 0.8 | 0.3 |  | 1.1 | 5.7 | 0.29819 | 0.72727 | 4.1818 | 14.4 | 12.6813 | 9.0007 | 46.9993 | 0.26982 | 5.5 | 7.3 | 6.2 | 128.15 | 392.15 | 1298 | 1096.15 | 15.5508 | 67.3212 | 1028.2202 | 87.5367 | [16 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 23 | 1998-07-03 | 10:30 | 524 | 29.2 | 57 | 54 | 0 | 4.4 | 0.78 | 0.27 |  | 1.05 | 5.45 | 0.28469 | 0.74286 | 4.1905 | 14.04 | 11.5175 | 15.4895 | 40.0105 | 0.28786 | 6 | 7.9 | 6.8 | 100.1 | 529.1 | 1098.35 | 1768.4333 | -61.0082 | 81.0811 | 1649.048 | 93.9298 | [16 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[11 empty] | 23 | 1998-07-03 | 22:30 | 536 | 27.6 | 51 | 49 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 10.4533 | 39.5467 | 0.31317 | 6.8 | 7.4 | 7.7 | 72.6 | 380.05 | 1204.5 | 1199.9167 | 0.38052 | 80.8973 | 1117.93 | 93.5059 | [16 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[11 empty] | 24 | 1998-07-04 | 5:30 | 543 | 28.1 | 68 | 66 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 8.7516 | 58.2484 | 0.2095 | 2.5 | 7.3 | 2.9 | 124.3 | 381.7 | 1908.5 | 1068.1 | 44.0346 | 67.4352 | 999.46 | 87.5633 | [16 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 24 | 1998-07-04 | 14:00 | 551.5 | 28.5 | 65 | 63 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0598 | 10.098 | 53.902 | 0.22374 | 5.2 | 7 | 5.9 | 112.2 | 409.2 | 1325.5 | 1201.2 | 9.3776 | 72.5806 | 1122 | 90 | [16 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 24 | 1998-07-04 | 21:30 | 559 | 26.4 | 66 | 64 | 3 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.8321 | 10.3972 | 51.6028 | 0.24867 | 6.1 | 7 | 7.4 | 89.65 | 395.45 | 1303.5 | 1210.9167 | 7.1027 | 77.3296 | 1129.37 | 92.0619 | [16 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE!
[11 empty] | 25 | 1998-07-05 | 2:00 | 563.5 | 27.3 | 65 | 63 | 3 | 4.4 | 0.83 | 0.3 |  | 1.13 | 5.53 | 0.28778 | 0.73451 | 3.8938 | 14.94 | 12.9638 | 9.7534 | 51.2466 | 0.25297 | 5.1 | 7 | 5.6 | 122.1 | 402.05 | 1199 | 1176.5783 | 1.87 | 69.6306 | 1097.4448 | 88.8742 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 25 | 1998-07-05 | 9:30 | 571 | 27.1 | 65 | 63 | 3 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5693 | 10.2102 | 50.7898 | 0.24748 | 6.6 | 7 | 6 | 98.45 | 398.75 | 1226.5 | 1199.55 | 2.1973 | 75.3103 | 1119.47 | 91.2057 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 25 | 1998-07-05 | 19:00 | 580.5 | 27.8 | 62 | 60 | 0.5 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3119 | 10.3972 | 50.1028 | 0.24573 | 5.1 | 7.1 | 5.6 | 135.85 | 441.65 | 1402.5 | 1257.1167 | 10.366 | 69.2403 | 1175.57 | 88.4439 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 26 | 1998-07-06 | 2:00 | 587.5 | 27.5 | 62 | 60 | 0.5 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.4216 | 9.6679 | 50.8321 | 0.24436 | 5.5 | 7 | 6.3 | 127.6 | 411.95 | 1364 | 1170.2167 | 14.207 | 69.0254 | 1094.39 | 88.3405 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 26 | 1998-07-06 | 9:00 | 594.5 | 28 | 62 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2393 | 13.0713 | 48.9287 | 0.25015 | 4.9 | 7 | 5.7 | 133.65 | 518.1 | 1534.5 | 1543.3 | -0.57348 | 74.2038 | 1440.78 | 90.7238 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 26 | 1998-07-06 | 20:00 | 605.5 | 28.2 | 62 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1672 | 10.472 | 50.028 | 0.24321 | 5.5 | 7.3 | 6.2 | 132 | 440 | 1331 | 1261.3333 | 5.2342 | 70 | 1179.2 | 88.806 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 27 | 1998-07-07 | 5:15 | 614.75 | 27 | 62 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.6065 | 9.6118 | 50.8882 | 0.24773 | 5.5 | 7.3 | 6.2 | 129.25 | 411.95 | 1430 | 1165.8167 | 18.4744 | 68.6248 | 1090.43 | 88.1469 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 27 | 1998-07-07 | 9:00 | 618.5 | 28.2 | 62 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1672 | 13.1835 | 48.8165 | 0.24924 | 5 | 7.2 | 6 | 133.65 | 521.4 | 1276 | 1555.4 | -21.8966 | 74.3671 | 1452 | 90.7955 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 27 | 1998-07-07 | 18:00 | 627.5 | 28 | 55 | 53 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.4744 | 8.5146 | 45.4854 | 0.25226 | 5.2 | 7.2 | 5.8 | 160.6 | 421.85 | 1380.5 | 1074.975 | 22.1315 | 61.9296 | 1012.0593 | 84.1314 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 28 | 1998-07-08 | 5:45 | 639.25 | 26.8 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0961 | 8.4525 | 45.5475 | 0.24362 | 5.3 | 7.3 | 5.8 | 140.25 | 411.4 | 1292.5 | 1044.0833 | 19.2199 | 65.9091 | 985.5015 | 85.7687 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 28 | 1998-07-08 | 9:00 | 642.5 | 28.1 | 58 | 55 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 9.7053 | 46.7947 | 0.26078 | 5.7 | 7.1 | 6 | 133.65 | 419.1 | 1276 | 1180.3 | 7.5 | 68.1102 | 1104.18 | 87.896 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 28 | 1998-07-08 | 18:00 | 651.5 | 28.2 | 55 | 52 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6463 | 9.2069 | 44.2931 | 0.24036 | 5.5 | 7.3 | 6.1 | 129.25 | 424.6 | 1237.5 | 1113.75 | 10 | 69.5596 | 1049.9398 | 87.6898
[11 empty] | 29 | 1998-07-09 | 6:30 | 664 | 26.8 | 55 | 53 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0961 | 8.7268 | 45.2732 | 0.24509 | 5.4 | 7.3 | 6 | 140.8 | 420.75 | 1314.5 | 1073.9667 | 18.2985 | 66.5359 | 1013.4836 | 86.1073
[11 empty] | 29 | 1998-07-09 | 10:00 | 667.5 | 28.2 | 55 | 53 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1672 | 14.7917 | 39.2083 | 0.31032 | 5.5 | 7.1 | 6.3 | 117.15 | 552.2 | 1276 | 1712.3333 | -34.1954 | 78.7849 | 1596.32 | 92.6612
[11 empty] | 29 | 1998-07-09 | 18:00 | 675.5 | 30 | 52 | 50 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.0947 | 9.4469 | 41.5531 | 0.24293 | 5.6 | 7.3 | 6.5 | 126.5 | 429.55 | 1171.5 | 1136.6667 | 2.9734 | 70.5506 | 1071.1929 | 88.1907
[11 empty] | 30 | 1998-07-10 | 6:30 | 688 | 27.5 | 48 | 46 | 0 | 4.4 | 0.6 | 0.3 |  | 0.9 | 5.3 | 0.28131 | 0.66667 | 4.8889 | 10.8 | 9.3162 | 8.0943 | 38.9057 | 0.23946 | 5.6 | 7.3 | 6.3 | 134.2 | 420.2 | 1298 | 992.2 | 23.5593 | 68.0628 | 943.634 | 85.7784
[11 empty] | 30 | 1998-07-10 | 9:00 | 690.5 | 28.8 | 48 | 45 | 0 | 4.7 | 0.7 | 0.3 |  | 1 | 5.7 | 0.30101 | 0.7 | 4.7 | 12.6 | 10.4591 | 5.4376 | 41.0624 | 0.25471 | 5.5 | 7.1 | 6.3 | 131.45 | 305.25 | 953.7 | 710.7833 | 25.471 | 56.9369 | 675.2102 | 80.532
[11 empty] | 30 | 1998-07-10 | 22:00 | 703.5 | 26.6 | 63 | 61 | 1 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.7565 | 11.7249 | 49.2751 | 0.25888 | 5.7 | 7.5 | 6.7 | 77 | 421.85 | 1062.05 | 1341.45 | -26.3076 | 81.7471 | 1249.49 | 93.8375
[11 empty] | 31 | 1998-07-11 | 6:00 | 711.5 | 27.3 | 63 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.4952 | 10.5281 | 51.4719 | 0.24276 | 5.7 | 7.3 | 6.6 | 113.3 | 422.95 | 1419 | 1248.6833 | 12.0026 | 73.212 | 1166.11 | 90.2839
[11 empty] | 31 | 1998-07-11 | 12:15 | 717.75 | 28.8 | 61 | 59 | 0 | 4.4 | 0.78 | 0.3 |  | 1.08 | 5.48 | 0.28638 | 0.72222 | 4.0741 | 14.04 | 11.6545 | 10.7035 | 49.2965 | 0.23642 | 5.7 | 7.2 | 6.6 | 121.55 | 441.65 | 1210 | 1273.91 | -5.2818 | 72.4782 | 1191.899 | 89.802
[11 empty] | 31 | 1998-07-11 | 21:30 | 727 | 27.6 | 61 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 11.1265 | 48.8735 | 0.25341 | 5.7 | 7.4 | 6.6 | 101.2 | 428.45 | 1336.5 | 1301.1167 | 2.6475 | 76.38 | 1213.85 | 91.6629
[11 empty] | 32 | 1998-07-12 | 1:00 | 730.5 | 27.6 | 61 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 10.9208 | 49.0792 | 0.25235 | 5.7 | 7.3 | 6.6 | 107.8 | 429 | 1309 | 1285.5333 | 1.7927 | 74.8718 | 1199.88 | 91.0158
[11 empty] | 32 | 1998-07-12 | 10:30 | 740 | 29.5 | 62 | 60 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 9.5132 | 8.0157 | 52.9843 | 0.17955 | 5.7 | 7.5 | 6.5 | 160.6 | 430.1 | 1941.5 | 1014.0167 | 47.7715 | 62.6598 | 962.1736 | 83.3086
[11 empty] | 32 | 1998-07-12 | 18:00 | 747.5 | 27.9 | 80 | 78 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2756 | 6.919 | 72.081 | 0.1703 | 5.3 | 7.3 | 6.1 | 247.5 | 451 | 2821.5 | 993.6667 | 64.7823 | 45.122 | 939.4 | 73.6534
[11 empty] | 33 | 1998-07-13 | 1:00 | 754.5 | 27.6 | 82 | 79 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 7.8353 | 72.6647 | 0.17044 | 5.3 | 7.4 | 6.2 | 219.45 | 449.9 | 2876.5 | 1064.4333 | 62.9955 | 51.2225 | 1002.98 | 78.1202
[11 empty] | 33 | 1998-07-13 | 9:00 | 762.5 | 27.2 | 60 | 59 | 0 | 4.4 | 0.8 | 0.3 | X | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 15.5397 | 43.9603 | 0.28508 | 5.1 | 7 | 6.5 | 91.3 | 548.35 | 984.5 | 1767.15 | -79.4972 | 83.3501 | 1645.27 | 94.4508
[11 empty] | 33 | 1998-07-13 | 18:00 | 771.5 | 28.8 | 61 | 58 | 0 | NR | 0.8 | NR |  | NR | NR | NR | NR | NR | 14.4 | 11.9533 | NR | NR | NR | 5.7 | 7.3 | 6.6 | 93.5 | 433.4 | 1171.5 | NR | NR | 78.4264 | NR | NR
[11 empty] | 34 | 1998-07-14 | 9:00 | 786.5 | 27 | 62 | 59 | 0 | NR | 0.2 | NR |  | NR | NR | NR | NR | NR | 3.6 | 3.1516 | NR | NR | NR | 5.7 | 7.2 | 6.7 | 92.4 | 426.8 | 1237.5 | NR | NR | 78.3505 | NR | NR
0.1703
0.38337
0.26918
0.32606
0.28508
Note on A2: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field.
Note on E24: C. Hill (9/22/99): Reviewer changed from 0.092 to 0.003.
Note on U49: TSC_ADM: According to the consultant, this pressure spike was caused by operational errors.
Note on U89: TSC_ADM: According to the consultant, this pressure spike was caused by operational errors.
Note on U90: TSC_ADM: According to the consultant, this pressure spike was caused by operational errors.
Note on V49: TSC_ADM: According to the consultant, this pressure spike was caused by operational errors.
Note on V89: TSC_ADM: According to the consultant, this pressure spike was caused by operational errors.
Note on V90: TSC_ADM: According to the consultant, this pressure spike was caused by operational errors.
Note on AA91: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on BP17: C, Hill (9/21/99): High permeate TDS verified by reviewer using analytical reports contained in Exhibit 3 of the Summary Report.
Note on BP37: C. Hill (9/21/99): Reviewer verified permeate THM concentrations for Week 1 using Summary Report - Exhibit 3, which contains copies of analytical reports.
Note on BQ26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.8'.
Note on BQ27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on BQ30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.01'.
Note on BQ31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on BQ32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '166'.
Note on BQ33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '11'.
Note on BQ34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '11'.
Note on BQ38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5'.
Note on BQ40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5'.
Note on BQ48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on BY17: DPATTON(11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported (weekly) results of TDS are experimentally measured and are more accurate.
Note on CB26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.4'.
Note on CB27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CB28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CB30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8'.
Note on CB31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CB32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '321'.
Note on CB33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '52'.
Note on CB34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.6'.
Note on CB35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1'.
Note on CB36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1'.
Note on CB37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '55.6'.
Note on CB38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2'.
Note on CB39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.1'.
Note on CB40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.3'.
Note on CB41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1'.
Note on CB42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1'.
Note on CB43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.2'.
Note on CB44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CB47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '10.4'.
Note on CB48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '11.6'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CJ17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported (weekly) results of TDS are experimentally measured and are more accurate.
Note on CM26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.7'.
Note on CM27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CM30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.01'.
Note on CM31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CM32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '193'.
Note on CM33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.5'.
Note on CM34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.5'.
Note on CM38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.4'.
Note on CM40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.6'.
Note on CM41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6'.
Note on CM48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CU17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported (weekly) results of TDS are experimentally measured and are more accurate.
Note on CX26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.3'.
Note on CX27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CX30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.01'.
Note on CX31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CX32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '313'.
Note on CX33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '19'.
Note on CX34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.4'.
Note on CX35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20.4'.
Note on CX38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.3'.
Note on CX40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on CX41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CX47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.1'.
Note on CX48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.1'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DF17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported (weekly) results of TDS are experimentally measured and are more accurate.
Note on DI26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.4'.
Note on DI27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on DI30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8'.
Note on DI31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on DI32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '276'.
Note on DI33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '21'.
Note on DI34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.9'.
Note on DI35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '22.9'.
Note on DI38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.3'.
Note on DI40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.4'.
Note on DI41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DI44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on DI47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.7'.
Note on DI48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.7'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR6: C. Hill (9/21/99): Reviewer copied values reported for fourth quarter.

## NF70. 2nd Quarter
FIELD-SET 2: 2nd QUARTER SEBST RESULTS (FILE: Film Tec.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: SEBST Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 2-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 2-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 2-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 2-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 2-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [19 empty] | 0.72083 |  | 13.9375 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | FilmTec Corp. | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale |  | Date | Time | Operation | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | NA | ** Sample received by lab after maximum holding time had expired, | [7 empty] | Recovery during sample collection (decimal) | 0.73 | [8 empty] | Recovery during sample collection (decimal) | NR | [8 empty] | Recovery during sample collection (decimal) | NR | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL 5360313 | Membrane trade name | FILMTEC | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.38079 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale | DAYS | MM/DD/YY | hh:mm | Time | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | NA | no anlaysis performed. | [7 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | NR | [8 empty] | Feed flow rate during sample collection (gpm) | NR | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | NF70-4040 |  |  | LSI | 0.14 | Hydrochloric acid addition | pH = 6.4 | Pilot-scale | 1 | 1998-09-02 | 18:00 | 0 | 30.8 | 56 | 53 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.2671 | 11.781 | 42.719 | 0.26375 | 5.6 | 6.2 | 6.6 | 138.6 | 485.1 | 1468.5 | 1409.1 | 4.0449 | 71.4286 | 1316.7 | 89.4737 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | NA | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | NR | [8 empty] | Influent flow rate during sample collection (gpm) | NR | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.26 |  |  |  | 2 | 1998-09-03 | 6:30 | 12.5 | 27.9 | 55 | 52 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.5083 | 11.9204 | 41.5796 | 0.27678 | 5.6 | 6 | 6.6 | 121.55 | 487.3 | 1314.5 | 1401.675 | -6.6318 | 75.0564 | 1313.593 | 90.7468 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | discriminating | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.35 |  |  |  | 2 | 1998-09-03 | 9:00 | 15 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 2 | 1998-09-03 | 18:00 | 24 | 28.6 | 55 | 52 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0242 | 12.4168 | 41.0832 | 0.29268 | 5.5 | 6.2 | 6.6 | 121 | 486.2 | 1347.5 | 1460.0667 | -8.3537 | 75.1131 | 1362.68 | 91.1204 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Permeate flow rate, Qp (gpm) | 0.83333 | Total aluminum (mg/L) | 0.11 |  |  |  | 3 | 1998-09-04 | 0:30 | 30.5 | 28.5 | 55 | 52 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0598 | 12.5664 | 40.9336 | 0.29462 | 5.6 | 6.1 | 6.4 | 119.35 | 488.95 | 1248.5 | 1474.55 | -18.1057 | 75.5906 | 1375.99 | 91.3262 | [16 empty] | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-17 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-23 | 1998-09-23 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-03 | NA | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-03 | NA | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.1111 | Fluoride (mg/L) | 0.41 |  |  |  | 3 | 1998-09-04 | 9:00 | 39 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | 6:00 | 6:00 | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | NA | --- | --- | --- | --- | --- | Sampling time | hh:mm | NR | NR | NA | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27778 | Phosphate (mg/L) | 0.098 |  |  |  | 3 | 1998-09-04 | 16:20 | 46.3333 | 29.4 | 52 | 48 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.7432 | 12.7347 | 37.2653 | 0.31512 | 6.7 | 6.9 | 7.1 | 106.7 | 481.25 | 1160.5 | 1480.05 | -27.5355 | 77.8286 | 1380.17 | 92.2691 | [16 empty] | Operation time | hh.hh | 159 | 159 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | 327 | 327 | NR | --- | --- | --- | --- | --- | Operation time | hh.hh | 276 | 276 | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | NR | NR | NA | --- | --- | --- | --- | --- | Operation time | hh.hh | NR | NR | NA | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 3 | Sulfate (mg/L) | 31 |  |  |  | 4 | 1998-09-05 | 1:00 | 55 | 28.9 | 55 | 52 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.918 | 12.4168 | 41.0832 | 0.29009 | 5.6 | 6 | 6.5 | 121.55 | 486.75 | 1358.5 | 1460.6167 | -7.5169 | 75.0282 | 1363.23 | 91.0837 | [16 empty] | pH | --- | 5.77 | 6.54 | NA | --- | --- | --- | --- | --- | pH | --- | NR | NR | NR | --- | --- | --- | --- | --- | pH | --- | 5.76 | 6.12 | NA | --- | --- | --- | --- | --- | pH | --- | NR | NR | NA | --- | --- | --- | --- | --- | pH | --- | NR | NR | NA | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 83 |  |  |  | 4 | 1998-09-05 | 10:00 | 64 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | Temperature | oC | 28.3 | 28.3 | NA | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | NR | --- | --- | --- | --- | --- | Temperature | oC | 27.1 | 27.1 | NA | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | NA | --- | --- | --- | --- | --- | Temperature | oC | NR | NR | NA | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.016 |  |  |  | 4 | 1998-09-05 | 11:15 | 65.25 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | Alkalinity | mg/L as CaCO3 | 28 | 160 | NA | 516.8889 | #VALUE! | 82.5 | 481.2 | 94.1812 | Alkalinity | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 30 | 71 | NA | 181.8519 | #VALUE! | 57.7465 | 170.7667 | 82.4322 | Alkalinity | mg/L as CaCO3 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 28.7 | Design recycle flow rate, QR (gpm) | 4.3889 | Strontium (mg/L) | 0.13 |  |  |  | 4 | 1998-09-05 | 18:10 | 72.1667 | 28.4 | 64 | 60 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 12.0955 | 12.1187 | 49.8813 | 0.24248 | 5.5 | 6.4 | 6.7 | 91.3 | 448.25 | 1325.5 | 1400.1167 | -5.6293 | 79.6319 | 1303.1673 | 92.994 | [16 empty] | Total dissolved solids | mg/L | 83 | 560 | NA | 1849.6667 | #VALUE! | 85.1786 | 1720.7 | 95.1764 | Total dissolved solids | mg/L | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 220 | 660 | NA | 1849.6296 | #VALUE! | 66.6667 | 1730.6667 | 87.2881 | Total dissolved solids | mg/L | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Recycle ratio, r | 3.95 | Reactive silica (mg/L as SiO2) | 34 |  |  |  | 5 | 1998-09-06 | 0:30 | 78.5 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | Total hardness | mg/L as CaCO3 | 20 | 270 | NA | 945.9259 | #VALUE! | 92.5926 | 878.3333 | 97.723 | Total hardness | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 63 | 280 | NA | 866.7037 | #VALUE! | 77.5 | 808.0333 | 92.2033 | Total hardness | mg/L as CaCO3 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.41 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | NR |  |  |  | 5 | 1998-09-06 | 14:30 | 92.5 | 28.9 | 62 | 58 | 0 | 4.3 | 0.83 | 0.3 |  | 1.13 | 5.43 | 0.28216 | 0.73451 | 3.8053 | 14.94 | 12.3649 | 13.0872 | 46.9128 | 0.26357 | 5.6 | 6.3 | 6.6 | 85.8 | 462 | 1182.5 | 1502.82 | -27.0884 | 81.4286 | 1394.521 | 93.8473 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 15 | 220 | NA | 774.2593 | #VALUE! | 93.1818 | 718.8333 | 97.9133 | Calcium hardness | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 50 | 210 | NA | 642.5926 | #VALUE! | 76.1905 | 599.3333 | 91.6574 | Calcium hardness | mg/L as CaCO3 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 3.2 |  |  |  | 5 | 1998-09-06 | 18:00 | 96 | 27.2 | 64 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 11.9867 | 50.5133 | 0.2481 | 5.5 | 6.4 | 6.7 | 96.25 | 448.8 | 1413.5 | 1388.9333 | 1.738 | 78.5539 | 1294.92 | 92.5671 | [16 empty] | Turbidity | ntu | BMRL | 0.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.1 | 0.24 | NA | 0.61852 | #VALUE! | 58.3333 | 0.58067 | 82.7784 | Turbidity | ntu | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 6 | 1998-09-07 | 1:00 | 103 | 27.1 | 64 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5693 | 12.0989 | 49.9011 | 0.25188 | 5.5 | 6.4 | 6.6 | 92.4 | 448.25 | 1358.5 | 1397.1833 | -2.8475 | 79.3865 | 1302.29 | 92.9048 | [16 empty] | Ammonia | mg NH3-N / L | 0.14 | 0.24 | NA | 0.51037 | #VALUE! | 41.6667 | 0.48333 | 71.0345 | Ammonia | mg NH3-N / L | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.16 | 0.28 | NA | 0.60444 | #VALUE! | 42.8571 | 0.572 | 72.028 | Ammonia | mg NH3-N / L | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 6 | 1998-09-07 | 9:40 | 111.6667 | 27 | 63 | 60 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 12.6065 | 12.212 | 49.288 | 0.25577 | 5.4 | 6.7 | 6.7 | 80.3 | 440 | 1171.5 | 1399.2 | -19.4366 | 81.75 | 1301.5037 | 93.8302 | [16 empty] | Total organic carbon | mg/L | BMRL | 6.5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1 | 5.7 | NA | 18.4074 | #VALUE! | 82.4561 | 17.1367 | 94.1646 | Total organic carbon | mg/L | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 6 | 1998-09-07 | 18:00 | 120 | 27.1 | 64 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5693 | 12.5664 | 49.9336 | 0.25172 | 5.6 | 6.4 | 6.8 | 84.15 | 453.75 | 1265 | 1439.35 | -13.7826 | 81.4545 | 1340.79 | 93.7238 | [16 empty] | UV254 | cm-1 | BMRL | 0.26 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.038 | 0.22 | NA | 0.71207 | #VALUE! | 82.7273 | 0.66287 | 94.2673 | UV254 | cm-1 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | NR | NR | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.003 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 7 | 1998-09-08 | 5:15 | 131.25 | 27.2 | 62 | 59 | 0 | 4.2 | 0.8 | 0.25 |  | 1.05 | 5.25 | 0.27287 | 0.7619 | 4 | 14.4 | 12.5322 | 13.6789 | 46.8211 | 0.26766 | 5.5 | 6.1 | 6.7 | 112.2 | 464.75 | 1523.5 | 1592.91 | -4.556 | 75.858 | 1480.094 | 92.4194 | [16 empty] | SUVA | L/(mg*m) | #VALUE! | 4 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | NR | NR | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.8 | 3.8596 | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | NR | NA | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | NR | NA | --- | --- | --- | --- | ---
Process Train Name | SEBST | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 7 | 1998-09-08 | 9:00 | 135 | 27.8 | 62 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3119 | 13.1461 | 47.8539 | 0.25728 | 5.7 | 6.2 | 6.8 | 121 | 507.65 | 1320 | 1538.7167 | -16.5694 | 76.1647 | 1435.61 | 91.5715 | [16 empty] | Bromide | mg/L | 64 | 280 | NA | 864 | --- | 77.1429 | 805.6 | 92.0556 | Bromide | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | 140 | 370 | NA | 991.8519 | --- | 62.1622 | 929.6667 | 84.9408 | Bromide | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 7 | 1998-09-08 | 18:00 | 144 | 28.5 | 66 | 63 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0598 | 11.0143 | 53.4857 | 0.22548 | 5.5 | 6.2 | 6.6 | 133.1 | 457.05 | 1760 | 1320.9167 | 24.9479 | 70.8785 | 1234.53 | 89.2186 | [16 empty] | SDS-Cl2 dose | mg/L | 6.9 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | NR | NR | NR | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 9.3 | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | NR | NR | NA | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1154.0984 | [5 empty] | 8 | 1998-09-09 | 6:00 | 156 | 27.6 | 62 | 59 | 0 | 4.2 | 0.8 | 0.3 |  | 1.1 | 5.3 | 0.27569 | 0.72727 | 3.8182 | 14.4 | 12.3849 | 10.8885 | 49.6115 | 0.24964 | 5.5 | 6.2 | 6.6 | 134.2 | 455.4 | 1804 | 1311.9333 | 27.2764 | 70.5314 | 1223.0478 | 89.0274 | [16 empty] | SDS-Free Cl2 residual | mg/L | 0.67 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | NR | NR | NR | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.69 | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | NR | NR | NA | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 201.9672 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 8 | 1998-09-09 | 9:00 | 159 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-Cl2 demand | mg/L | 6.23 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | 8.61 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-Cl2 demand | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | see guidelines | Influent TDS, TDSI (mg/L) | 1009.8361 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 8 | 1998-09-09 | 18:00 | 168 | 28.8 | 61 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.2062 | 10.7911 | 48.7089 | 0.23007 | 5.5 | 6.2 | 6.7 | 127.6 | 458.7 | 1628 | 1286.45 | 20.9797 | 72.1823 | 1206.7126 | 89.4258 | [16 empty] | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | NR | NR | NR | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | NR | NR | NA | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | see guidelines | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 9 | 1998-09-10 | 6:00 | 180 | 27.4 | 62 | 59 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.6797 | 10.4685 | 50.0315 | 0.23345 | 5.5 | 6.2 | 6.6 | 133.1 | 454.3 | 1589.5 | 1257.3 | 20.8997 | 70.7022 | 1179.9468 | 88.7198 | [16 empty] | SDS-Chlorination pH | --- | 7.95 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | NR | NR | NR | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.05 | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | NR | NR | NA | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 9 | 1998-09-10 | 9:00 | 183 | 28 | 62 | 59 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2393 | 9.5931 | 50.9069 | 0.24043 | 5.6 | 6 | 6.5 | 177.1 | 459.25 | 1518 | 1211.65 | 20.1812 | 61.4371 | 1136.41 | 84.4158 | [16 empty] | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | NR | NR | NR | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | NR | NR | NA | --- | --- | --- | --- | --- | SDS-Incubation time | hours | NR | NR | NA | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 9 | 1998-09-10 | 18:00 | 192 | 27.4 | 59 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.901 | 10.2185 | 47.2815 | 0.23056 | 5.5 | 6.1 | 6.6 | 133.65 | 461.45 | 1683 | 1226.3167 | 27.1351 | 71.0369 | 1155.4957 | 88.4335 | [16 empty] | SDS-TOX | mg Cl- /L | 28 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 129 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Rejection of reference solute and conditions of test | MgSO4 2000 mg/l | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 10 | 1998-09-11 | 6:15 | 204.25 | 27.2 | 58 | 55 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.27287 | 0.7 | 4.2 | 12.6 | 10.9657 | 9.9518 | 46.5482 | 0.23558 | 5.5 | 6.1 | 6.7 | 144.1 | 464.2 | 1683 | 1211.1 | 28.0392 | 68.9573 | 1139.2827 | 87.3517 | [16 empty] | SDS-CHCl3 | mg/L | 4.5 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 16 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | (e.g., solute type and concentration) | >90 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 10 | 1998-09-11 | 9:00 | 207 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-BDCM | mg/L | 2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | 25 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Variability of rejection of reference solute (%) | n/a | Required influent pressure, PI (psi) | 50.1913 | [5 empty] | 10 | 1998-09-11 | 16:40 | 214.6667 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-DBCM | mg/L | 3.5 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | 22 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 20 | [7 empty] | 11 | 1998-09-12 | 7:00 | 229 | 25.8 | 73 | 70 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 13.0617 | 12.6038 | 58.8962 | 0.22177 | 5.6 | 6.5 | 6.9 | 92.4 | 463.1 | 1397 | 1451.6333 | -3.9108 | 80.0475 | 1352.78 | 93.1696 | [16 empty] | SDS-CHBr3 | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 4.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7 | [7 empty] | 11 | 1998-09-12 | 12:30 | 234.5 | 28.7 | 64 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.9887 | 12.6599 | 49.8401 | 0.24054 | 5.4 | 6.1 | 6.6 | 106.7 | 479.05 | 1815 | 1471.9833 | 18.899 | 77.7268 | 1372.69 | 92.2269 | [16 empty] | SDS-THM4 | mg/L | 10 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | 67.9 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 50-250 | [7 empty] | 11 | 1998-09-12 | 16:45 | 238.75 | 27.6 | 64 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 12.8656 | 49.1344 | 0.25206 | 5.5 | 6.2 | 6.6 | 85.25 | 463.65 | 1215.5 | 1472.7167 | -21.1614 | 81.6133 | 1371.81 | 93.7856 | [16 empty] | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [7 empty] | 12 | 1998-09-13 | 3:00 | 249 | 26.5 | 64 | 60 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.7942 | 13.5014 | 48.4986 | 0.26381 | 5.5 | 6.1 | 6.6 | 86.9 | 484 | 1441 | 1542.9333 | -7.0738 | 82.0455 | 1437.04 | 93.9528 | [16 empty] | SDS-DCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 5.3 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 4 | [7 empty] | 12 | 1998-09-13 | 8:45 | 254.75 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-TCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 3.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | [7 empty] | 12 | 1998-09-13 | 18:00 | 264 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 13 | 1998-09-14 | 1:00 | 271 | 27.2 | 64 | 61 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 11.6688 | 50.8312 | 0.24655 | 5.4 | 6.1 | 6.6 | 140.8 | 484 | 1567.5 | 1399.2 | 10.7368 | 70.9091 | 1307.68 | 89.2328 | [16 empty] | SDS-DBAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 4.2 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 13 | 1998-09-14 | 6:00 | 276 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-BCAA* | mg/L | BMRL | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 4.4 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 13 | 1998-09-14 | 18:00 | 288 | 27.2 | 61 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.7489 | 12.2789 | 47.2211 | 0.24881 | 5.7 | 6.6 | 7.1 | 77 | 453.75 | 1210 | 1395.625 | -15.3409 | 83.0303 | 1304.8939 | 94.0991 | [16 empty] | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 14 | 1998-09-15 | 5:30 | 299.5 | 24 | 59 | 56 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.27287 | 0.7 | 4.2 | 12.6 | 12.0535 | 11.3027 | 46.1973 | 0.26091 | 5.9 | 6.6 | 7.1 | 95.15 | 458.7 | 1287 | 1306.9833 | -1.5527 | 79.2566 | 1225.4176 | 92.2353 | [16 empty] | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 14 | 1998-09-15 | 9:00 | 303 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 14 | 1998-09-15 | 18:00 | 312 | 27.4 | 60 | 57 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.6797 | 11.9563 | 46.5437 | 0.25094 | 5.7 | 6.6 | 7 | 86.9 | 453.75 | 1265 | 1370.875 | -8.3696 | 80.8485 | 1282.5281 | 93.2243 | [16 empty] | SDS-HAA5 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | NR | NR | NR | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 12.7 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | 0 | NA | #VALUE! | --- | #DIV/0! | #VALUE! | #VALUE! | SDS-HAA5 | mg/L | 0 | 0 | NA | #VALUE! | --- | #DIV/0! | #VALUE! | #VALUE!
[11 empty] | 15 | 1998-09-16 | 5:45 | 323.75 | 27 | 58 | 55 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.27287 | 0.7 | 4.2 | 12.6 | 11.0307 | 11.2856 | 45.2144 | 0.24396 | 5.7 | 6.5 | 7 | 92.4 | 455.4 | 1243 | 1302.4 | -4.7788 | 79.7101 | 1220.9577 | 92.4322 | [16 empty] | SDS-HAA6 | mg/L | 0 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | NR | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 17.1 | NR | NA | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | 0 | NA | #VALUE! | --- | #DIV/0! | #VALUE! | #VALUE! | SDS-HAA6 | mg/L | 0 | 0 | NA | #VALUE! | --- | #DIV/0! | #VALUE! | #VALUE!
[11 empty] | 15 | 1998-09-16 | 9:00 | 327 | 27.3 | 58 | 56 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.4952 | 9.5744 | 47.4256 | 0.26347 | 5.5 | 6.2 | 6.6 | 149.05 | 430.65 | 1237.5 | 1181.5833 | 4.5185 | 65.3895 | 1106.49 | 86.5295 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 15 | 1998-09-16 | 18:00 | 336 | 27.8 | 61 | 58 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3119 | 12.342 | 47.158 | 0.26108 | 5.7 | 6.5 | 6.9 | 100.1 | 463.1 | 1281.5 | 1431.1 | -11.6738 | 78.3848 | 1334.3 | 92.4979 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 16 | 1998-09-17 | 0:30 | 342.5 | 27.1 | 61 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.7837 | 11.9563 | 47.5437 | 0.24785 | 5.7 | 6.5 | 6.9 | 97.9 | 464.75 | 1342 | 1381.875 | -2.9713 | 78.9349 | 1293.5281 | 92.4316
[11 empty] | 16 | 1998-09-17 | 9:30 | 351.5 | 27.5 | 61 | 59 | 0 | 4.2 | 0.75 | 0.3 |  | 1.05 | 5.25 | 0.27428 | 0.71429 | 4 | 13.5 | 11.6452 | 12.0656 | 47.9344 | 0.24294 | 5.6 | 6.2 | 6.8 | 85.25 | 456.5 | 1342 | 1384.625 | -3.1762 | 81.3253 | 1291.8125 | 93.4007 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 16 | 1998-09-17 | 18:00 | 360 | 26.1 | 59 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3281 | 12.3787 | 45.1213 | 0.25106 | 6.2 | 6.5 | 7.1 | 67.1 | 464.2 | 1155 | 1390.7667 | -20.4127 | 85.545 | 1304.9735 | 94.8581 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 17 | 1998-09-18 | 7:00 | 373 | 26.6 | 55 | 52 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.27287 | 0.7 | 4.2 | 12.6 | 11.1619 | 11.4908 | 42.0092 | 0.2657 | 5.8 | 6.3 | 6.8 | 107.8 | 477.4 | 1342 | 1339.8 | 0.16393 | 77.4194 | 1256.8769 | 91.4232 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 17 | 1998-09-18 | 11:00 | 377 | 27.2 | 55 | 52 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 12.9965 | 40.5035 | 0.30941 | 6 | 6.1 | 6.5 | 70.4 | 452.65 | 1149.5 | 1471.9833 | -28.0542 | 84.4471 | 1370.05 | 94.8615 | [16 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0!
[11 empty] | 17 | 1998-09-18 | 18:25 | 384.4167 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0!
[11 empty] | 18 | 1998-09-19 | 3:30 | 393.5 | 26.7 | 62 | 59 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.9239 | 12.0818 | 48.4182 | 0.24627 | 5.9 | 6.6 | 6.9 | 105.05 | 475.75 | 1342 | 1402.5 | -4.5082 | 77.9191 | 1313.2259 | 92.0006 | [16 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0!
[11 empty] | 18 | 1998-09-19 | 13:20 | 403.3333 | 27.5 | 61 | 58 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.4216 | 13.1461 | 46.3539 | 0.26797 | 5.7 | 6.4 | 6.7 | 99 | 485.65 | 1199 | 1516.7167 | -26.4985 | 79.6149 | 1413.61 | 92.9967 | [16 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0!
[11 empty] | 18 | 1998-09-19 | 16:50 | 406.8333 | 27.3 | 61 | 57 | 0 | 4.3 | 0.75 | 0.3 |  | 1.05 | 5.35 | 0.27991 | 0.71429 | 4.0952 | 13.5 | 11.7143 | 12.083 | 46.917 | 0.24968 | 5.9 | 6.6 | 6.8 | 93.5 | 464.75 | 1100 | 1392.875 | -26.625 | 79.8817 | 1301.7973 | 92.8176 | [16 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0!
[11 empty] | 19 | 1998-09-20 | 0:30 | 414.5 | 26.8 | 61 | 57 | 0 | 4.3 | 0.8 | 0.3 |  | 1.1 | 5.4 | 0.28131 | 0.72727 | 3.9091 | 14.4 | 12.6813 | 12.3614 | 46.6386 | 0.2719 | 5.6 | 6.6 | 6.6 | 103.4 | 467.5 | 1237.5 | 1438.4333 | -16.237 | 77.8824 | 1339.542 | 92.2809 | [16 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #DIV/0! | #DIV/0!
[11 empty] | 19 | 1998-09-20 | 8:15 | 422.25 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0!
[11 empty] | 19 | 1998-09-20 | 18:00 | 432 | 28.3 | 62 | 59 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.3731 | 11.5798 | 48.9202 | 0.23248 | 6.5 | 7.2 | 7.6 | 77 | 432.3 | 1144 | 1320.55 | -15.4327 | 82.1883 | 1234.9846 | 93.7651 | [16 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #DIV/0! | #DIV/0!
[11 empty] | 20 | 1998-09-21 | 1:00 | 439 | 27.4 | 65 | 62 | 0 | 4.5 | 0.6 | 0.3 |  | 0.9 | 5.4 | 0.28694 | 0.66667 | 5 | 10.8 | 9.3438 | 9.4123 | 54.0877 | 0.17275 | 6 | 6.6 | 6.9 | 107.8 | 440 | 1353 | 1104.4 | 18.374 | 75.5 | 1049.0333 | 89.7239 | [16 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0!
[11 empty] | 20 | 1998-09-21 | 9:00 | 447 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
[11 empty] | 20 | 1998-09-21 | 12:00 | 450 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0!
[11 empty] | 20 | 1998-09-21 | 18:00 | 456 | 28.5 | 76 | 73 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0598 | 9.9484 | 64.5516 | 0.18682 | 5.8 | 6.3 | 6.6 | 171.6 | 464.2 | 1215.5 | 1244.4667 | -2.3831 | 63.0332 | 1166.44 | 85.2886 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 21 | 1998-09-22 | 2:00 | 464 | 27.4 | 74 | 71 | 0 | 4.2 | 0.8 | 0.3 |  | 1.1 | 5.3 | 0.27569 | 0.72727 | 3.8182 | 14.4 | 12.4583 | 9.8817 | 62.6183 | 0.19896 | 5.8 | 6.3 | 6.6 | 178.2 | 469.7 | 1270.5 | 1247.0333 | 1.847 | 62.0609 | 1166.3667 | 84.7218 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 21 | 1998-09-22 | 10:30 | 472.5 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 21 | 1998-09-22 | 18:00 | 480 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 22 | 1998-09-23 | 2:00 | 488 | 27.4 | 61 | 58 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.6797 | 9.0165 | 50.4835 | 0.23136 | 5.4 | 5.6 | 5.8 | 236.5 | 513.15 | 1501.5 | 1204.775 | 19.7619 | 53.9121 | 1138.1506 | 79.2207 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 22 | 1998-09-23 | 9:00 | 495 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 22 | 1998-09-23 | 18:00 | 504 | 29.4 | 60 | 56 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.7432 | 9.7988 | 48.2012 | 0.24363 | 5.7 | 6.3 | 6.4 | 176 | 464.2 | 1408 | 1232.7333 | 12.4479 | 62.0853 | 1155.88 | 84.7735 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 23 | 1998-09-24 | 6:00 | 516 | 27.5 | 59 | 56 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.6452 | 9.7514 | 47.7486 | 0.24389 | 5.7 | 6.2 | 6.5 | 177.65 | 476.85 | 1391.5 | 1224.85 | 11.9763 | 62.7451 | 1152.795 | 84.5896 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 23 | 1998-09-24 | 11:00 | 521 | 28.6 | 60 | 58 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0242 | 5.3108 | 53.6892 | 0.22396 | 5.6 | 5.8 | 6.3 | 307.45 | 463.65 | 1215.5 | 880.1833 | 27.5867 | 33.6892 | 838.53 | 63.3346 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 23 | 1998-09-24 | 18:00 | 528 | 30.5 | 57 | 53 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 10.657 | 10.0383 | 44.9617 | 0.23702 | 5.7 | 6.3 | 6.5 | 169.4 | 477.4 | 1320 | 1247.4 | 5.5 | 64.5161 | 1173.2257 | 85.5612 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 24 | 1998-09-25 | 0:45 | 534.75 | 28.1 | 58 | 55 | 0 | 4.2 | 0.7 | 0.3 |  | 1 | 5.2 | 0.27287 | 0.7 | 4.2 | 12.6 | 10.6778 | 9.9005 | 46.5995 | 0.22914 | 5.8 | 6.2 | 6.5 | 163.9 | 482.35 | 1298 | 1225.4 | 5.5932 | 66.0205 | 1153.9529 | 85.7966 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 24 | 1998-09-25 | 14:15 | 548.25 | 28.1 | 59 | 56 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 12.0054 | 45.4946 | 0.26823 | 5.6 | 6.1 | 6.4 | 144.65 | 497.75 | 1287 | 1439.35 | -11.8376 | 70.9392 | 1345.19 | 89.2469
[11 empty] | 24 | 1998-09-25 | 22:00 | 556 | 27.2 | 59 | 56 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 12.1924 | 45.3076 | 0.2766 | 5.6 | 6.1 | 6.3 | 143 | 501.6 | 1270.5 | 1457.8667 | -14.7475 | 71.4912 | 1362.24 | 89.5026
[11 empty] | 25 | 1998-09-26 | 6:45 | 564.75 | 26.9 | 60 | 57 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.8536 | 10.7553 | 47.7447 | 0.24827 | 5.7 | 6.2 | 6.4 | 152.9 | 482.9 | 1298 | 1307.9 | -0.76271 | 68.3371 | 1228.4275 | 87.5532
[11 empty] | 25 | 1998-09-26 | 11:00 | 569 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR
[11 empty] | 25 | 1998-09-26 | 22:30 | 580.5 | 28.5 | 57 | 54 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.0598 | 12.5851 | 42.9149 | 0.28102 | 5.7 | 6.1 | 6.5 | 139.7 | 509.85 | 1259.5 | 1496.9167 | -18.8501 | 72.5998 | 1398.21 | 90.0087
[11 empty] | 26 | 1998-09-27 | 3:00 | 585 | 28.1 | 57 | 55 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 12.1363 | 43.8637 | 0.27821 | 5.6 | 6.1 | 6.5 | 144.65 | 501.6 | 1276 | 1453.4667 | -13.908 | 71.1623 | 1358.28 | 89.3505
[11 empty] | 26 | 1998-09-27 | 11:45 | 593.75 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR
[11 empty] | 26 | 1998-09-27 | 22:30 | 604.5 | 28.1 | 56 | 53 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 12.5477 | 41.9523 | 0.29088 | 5.8 | 6.3 | 6.5 | 135.3 | 504.35 | 1248.5 | 1488.4833 | -19.2217 | 73.1734 | 1390.07 | 90.2667
[11 empty] | 27 | 1998-09-28 | 1:30 | 607.5 | 28.1 | 57 | 54 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.2032 | 12.2111 | 43.2889 | 0.2819 | 5.7 | 6.4 | 6.5 | 138.6 | 497.75 | 1259.5 | 1455.4833 | -15.5604 | 72.1547 | 1359.71 | 89.8066
[11 empty] | 27 | 1998-09-28 | 11:00 | 617 | 28.9 | 57 | 54 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.918 | 8.1158 | 47.3842 | 0.25152 | 6.3 | 6.6 | 7.3 | 244.75 | 483.45 | 1171.5 | 1119.9833 | 4.3975 | 49.3743 | 1056.33 | 76.8302
[11 empty] | 27 | 1998-09-28 | 22:30 | 628.5 | 28.2 | 74 | 71 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1672 | 12.3046 | 60.1954 | 0.20213 | 5.6 | 6.1 | 6.5 | 145.75 | 507.65 | 1611.5 | 1472.7167 | 8.6121 | 71.2893 | 1376.21 | 89.4093
[11 empty] | 28 | 1998-09-29 | 5:30 | 635.5 | 26.7 | 71 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.129 | 11.23 | 58.27 | 0.19099 | 5.8 | 6.2 | 6.7 | 151.8 | 512.05 | 1485 | 1352.6333 | 8.9136 | 70.3545 | 1274.8015 | 88.0923
[11 empty] | 28 | 1998-09-29 | 9:00 | 639 | 28.2 | 70 | 68 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.1672 | 12.3046 | 56.6954 | 0.21461 | 5.6 | 6.3 | 6.5 | 145.75 | 507.65 | 1232 | 1472.7167 | -19.5387 | 71.2893 | 1376.21 | 89.4093
[11 empty] | 28 | 1998-09-29 | 22:30 | 652.5 | 27.8 | 69 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3119 | 11.8745 | 55.1255 | 0.22334 | 5.8 | 6.3 | 6.6 | 138.05 | 487.3 | 1457.5 | 1418.6333 | 2.6667 | 71.6704 | 1325.5 | 89.5851
[11 empty] | 29 | 1998-09-30 | 5:00 | 659 | 26.9 | 68 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.6438 | 12.0615 | 54.4385 | 0.23226 | 5.8 | 6.3 | 6.7 | 148.5 | 503.25 | 1430 | 1449.25 | -1.3462 | 70.4918 | 1354.65 | 89.0378
[11 empty] | 29 | 1998-09-30 | 5:00 | 659 | 26.9 | 68 | 65 | 0 | 4.4 | 0.8 | 0.3 | X | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.6438 | 12.0615 | 54.4385 | 0.23226 | 5.8 | 6.3 | 6.7 | 148.5 | 503.25 | 1430 | 1449.25 | -1.3462 | 70.4918 | 1354.65 | 89.0378
0.17275
0.31512
0.24916
0.26375
0.23226
Note on A2: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field.
Note on E24: C. Hill (9/22/99): Reviewer changed from 0.092 to 0.003.
Note on AA92: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on BQ26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.6'.
Note on BQ27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on BQ30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.97'.
Note on BQ31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on BQ32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '208'.
Note on BQ33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '32'.
Note on BQ34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.7'.
Note on BQ35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '36.7'.
Note on BQ38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '16'.
Note on BQ40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on BQ41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on BQ43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.5'.
Note on BQ44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on BQ47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on BQ48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '21.5'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on BY17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CA11: C. Hill (8/5/99): Reviewer inserted these dates and times for review purposes.
Note on CJ17: DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CJ30: C. Hill (9/21/99): Reviewer corrected feed and permeate SDS-pH using Summary Report - Exhibit 3. Both were initially reported as 2.0
Note on CL37: C. Hill (9/21/99): Reviewer verified permeate HAA and THM values using Exhibit 3 of the Summary Report which contains copies of analytical reports.
Note on CL47: C. Hill (9/21/99): Reviewer verified permeate HAA and THM values using Exhibit 3 of the Summary Report which contains copies of analytical reports.
Note on CL48: C. Hill (9/21/99): Reviewer verified permeate HAA and THM values using Exhibit 3 of the Summary Report which contains copies of analytical reports.
Note on CM16: C. Hill (9/21/99): Verified by reviewer using Exhibit 3 of Summary Report.
Note on CM26: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3'.
Note on CM27: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM28: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM29: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20'.
Note on CM30: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.04'.
Note on CM31: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '83'.
Note on CM32: C. Hill (9/21/99): Consultant measured "total chlorine residual," or combine chlorine-chloramine residual, as opposed to the free chlorine residual. As a result feed SDS-DBP data for this quarter is invalid. Reviewer changed the reported "total chlorine residual" to BMRL in the SDS-free chlorine residual field. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '317'.
Note on CM33: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '26'.
Note on CM34: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.6'.
Note on CM35: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM36: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM37: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '30.6'.
Note on CM38: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM39: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.9'.
Note on CM40: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.9'.
Note on CM41: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM42: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CM43: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.4'.
Note on CM44: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM45: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM46: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NA'.
Note on CM47: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '12.8'.
Note on CM48: 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17.2'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR6: C. Hill (9/21/99): Reviewer copied values reported for fourth quarter.

## NF70. 3rd Quarter
FIELD-SET 3: 3rd QUARTER SEBST RESULTS (FILE: Film Tec.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: SEBST Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 3-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 3-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 3-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 3-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 3-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [19 empty] | 0.70208 |  | 12.7465 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | FilmTec Corp. | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 250 | Process | Description | Scale |  | Date | Time | Operation | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL 5360313 | Membrane trade name | FILMTEC | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.38079 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale | DAYS | MM/DD/YY | hh:mm | Time | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | NF70-4040 |  |  | LSI | 0.14 | Hydrochloric acid addition | pH = 6.4 | Pilot-scale | 1 | 1998-11-16 | 18:00 | 0 | 27.6 | 74 | 71 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.3849 | 10.2663 | 62.2337 | 0.19901 | 5.8 | 6.3 | 6.6 | 172.7 | 474.65 | 1287 | 1279.85 | 0.55556 | 63.6153 | 1199.33 | 85.6003 | [17 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.26 |  |  |  | 2 | 1998-11-17 | 2:00 | 8 | 26.4 | 74 | 72 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.8321 | 9.7427 | 63.2573 | 0.20286 | 5.8 | 6.2 | 6.6 | 185.9 | 472.45 | 1474 | 1236.5833 | 16.107 | 60.6519 | 1160.17 | 83.9765 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | discriminating | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.35 |  |  |  | 2 | 1998-11-17 | 9:00 | 15 | 27.2 | 74 | 72 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 9.911 | 63.089 | 0.19864 | 5.6 | 6 | 6.4 | 180.4 | 471.9 | 1364 | 1249.2333 | 8.414 | 61.7716 | 1171.5 | 84.6009 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | <0.10 |  |  |  | 3 | 1998-11-18 | 6:00 | 36 | 25.4 | 72 | 70 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 13.2171 | 10.3037 | 60.6963 | 0.21776 | 5.8 | 6.3 | 6.6 | 173.25 | 476.3 | 1446.5 | 1284.4333 | 11.2041 | 63.6259 | 1203.62 | 85.6059 | [16 empty] | 85 | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 (dup) | CF-4 (dup) | CC-4 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Permeate flow rate, Qp (gpm) | 0.83333 | Total aluminum (mg/L) | 0.11 |  |  |  | 3 | 1998-11-18 | 9:00 | 39 | 26.9 | 73 | 70 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.6438 | 10.285 | 61.215 | 0.20655 | 5.6 | 6 | 6.5 | 172.7 | 475.2 | 1320 | 1281.8667 | 2.8889 | 63.6574 | 1201.2 | 85.6227 | [16 empty] | Sampling date | MM/DD/YY | 1998-11-23 | 1998-11-23 | 1998-11-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-02 | 1998-12-02 | 1998-12-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-09 | 1998-12-09 | 1998-12-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-16 | 1998-12-16 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.1111 | Fluoride (mg/L) | 0.41 |  |  |  | 3 | 1998-11-18 | 18:00 | 48 | 28 | 71 | 68 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.4744 | 9.5005 | 59.9995 | 0.19124 | 5.8 | 6.2 | 6.5 | 187 | 478.5 | 1490.5 | 1207.25 | 19.0037 | 60.9195 | 1137.0493 | 83.5539 | [16 empty] | Sampling time | hh:mm | 8:30 | 8:30 | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27778 | Phosphate (mg/L) | 0.098 |  |  |  | 4 | 1998-11-19 | 1:00 | 55 | 26.1 | 69 | 67 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.1372 | 10.5581 | 57.4419 | 0.2113 | 5.9 | 6.1 | 6.7 | 156.2 | 480.15 | 1386 | 1290.025 | 6.9246 | 67.4685 | 1212.0095 | 87.1123 | [16 empty] | Operation time | hh.hh | 158.5 | 158.5 | 158.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 377 | 377 | 377 | --- | --- | --- | --- | --- | Operation time | hh.hh | 543 | 543 | 543 | --- | --- | --- | --- | --- | Operation time | hh.hh | 711 | 711 | 711 | --- | --- | --- | --- | --- | Operation time | hh.hh | 711 | 711 | 711 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 3 | Sulfate (mg/L) | 31 |  |  |  | 4 | 1998-11-19 | 13:00 | 67 | 29.5 | 66 | 65 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 11.7085 | 10.3411 | 55.1589 | 0.21227 | 5.8 | 6.1 | 6.6 | 168.85 | 473 | 1281.5 | 1284.0667 | -0.20029 | 64.3023 | 1202.96 | 85.9638 | [16 empty] | pH | --- | 5.99 | 6.47 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 5.84 | 6.4 | 6.64 | --- | --- | --- | --- | --- | pH | --- | 5.97 | 6.76 | 6.82 | --- | --- | --- | --- | --- | pH | --- | 5.91 | 6.62 | 6.93 | --- | --- | --- | --- | --- | pH | --- | 5.77 | 6.58 | 6.87 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 83 |  |  |  | 4 | 1998-11-19 | 18:00 | 72 | 28.3 | 60 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6149 | 10.2356 | 47.7644 | 0.22223 | 5.9 | 6.3 | 6.7 | 146.3 | 474.65 | 1199 | 1240.8 | -3.4862 | 69.1773 | 1169.8602 | 87.4942 | [16 empty] | Temperature | oC | 28.6 | 28.6 | 28.6 | --- | --- | --- | --- | --- | Temperature | oC | 27.5 | 27.5 | 27.5 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | 24 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.016 |  |  |  | 5 | 1998-11-20 | 1:00 | 79 | 26.3 | 60 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2613 | 9.8756 | 48.6244 | 0.2316 | 5.9 | 6.3 | 6.7 | 152.9 | 469.7 | 1281.5 | 1208.9 | 5.6652 | 67.4473 | 1140.4556 | 86.5931 | [16 empty] | Alkalinity | mg/L as CaCO3 | 33 | 180 | 340 | 523 | -53.8235 | 81.6667 | 491.2407 | 93.2823 | Alkalinity | mg/L as CaCO3 | 32 | 150 | 390 | 425.3333 | -9.0598 | 78.6667 | 399.8395 | 91.9968 | Alkalinity | mg/L as CaCO3 | 32 | 180 | 380 | 525.3333 | -38.2456 | 82.2222 | 493.358 | 93.5138 | Alkalinity | mg/L as CaCO3 | 32 | 160 | 460 | 458.6667 | 0.28986 | 80 | 431.0123 | 92.5756 | Alkalinity | mg/L as CaCO3 | 32 | 160 | 420 | 458.6667 | -9.2063 | 80 | 431.0123 | 92.5756 | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 28.7 | Design recycle flow rate, QR (gpm) | 4.3889 | Strontium (mg/L) | 0.13 |  |  |  | 5 | 1998-11-20 | 9:00 | 87 | 27.1 | 58 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9981 | 10.4585 | 47.5415 | 0.23134 | 5.8 | 6.5 | 6.6 | 107.25 | 442.75 | 1055.45 | 1225.5833 | -16.1195 | 75.7764 | 1153.0988 | 90.699 | [16 empty] | Total dissolved solids | mg/L | 100 | 620 | 1500 | 1833.3333 | -22.2222 | 83.871 | 1720.9877 | 94.1894 | Total dissolved solids | mg/L | 82 | 540 | 1400 | 1608.6667 | -14.9048 | 84.8148 | 1509.716 | 94.5685 | Total dissolved solids | mg/L | 79 | 520 | 1100 | 1549 | -40.8182 | 84.8077 | 1453.7222 | 94.5657 | Total dissolved solids | mg/L | 110 | 670 | 1800 | 1976.6667 | -9.8148 | 83.5821 | 1855.679 | 94.0723 | Total dissolved solids | mg/L | 85 | 480 | 1700 | 1401.6667 | 17.549 | 82.2917 | 1316.3272 | 93.5426 | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Recycle ratio, r | 3.95 | Reactive silica (mg/L as SiO2) | 34 |  |  |  | 5 | 1998-11-20 | 21:00 | 99 | 28 | 60 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7094 | 11.0757 | 47.4243 | 0.22582 | 5.8 | 6.3 | 6.7 | 117.15 | 472.45 | 1166 | 1301.4833 | -11.6195 | 75.2037 | 1224.721 | 90.4346 | [16 empty] | Total hardness | mg/L as CaCO3 | 38 | 270 | 660 | 811.3333 | -22.9293 | 85.9259 | 761.2099 | 95.0079 | Total hardness | mg/L as CaCO3 | 38 | 280 | 710 | 844.6667 | -18.9671 | 86.4286 | 792.3827 | 95.2043 | Total hardness | mg/L as CaCO3 | 34 | 280 | 660 | 854 | -29.3939 | 87.8571 | 800.8519 | 95.7545 | Total hardness | mg/L as CaCO3 | 31 | 290 | 820 | 894.3333 | -9.065 | 89.3103 | 838.3765 | 96.3024 | Total hardness | mg/L as CaCO3 | 31 | 300 | 780 | 927.6667 | -18.9316 | 89.6667 | 869.5494 | 96.4349 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.41 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | NR |  |  |  | 6 | 1998-11-21 | 1:00 | 103 | 28.3 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6149 | 10.6985 | 48.3015 | 0.21976 | 6 | 6.2 | 6.8 | 135.3 | 478.5 | 1204.5 | 1279.3 | -6.21 | 71.7241 | 1205.1519 | 88.7732 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 26 | 200 | 550 | 606 | -10.1818 | 87 | 568.4074 | 95.4258 | Calcium hardness | mg/L as CaCO3 | 28 | 210 | 550 | 634.6667 | -15.3939 | 86.6667 | 595.3457 | 95.2969 | Calcium hardness | mg/L as CaCO3 | 22 | 220 | 520 | 682 | -31.1538 | 90 | 639.2222 | 96.5583 | Calcium hardness | mg/L as CaCO3 | 24 | 220 | 640 | 677.3333 | -5.8333 | 89.0909 | 634.9877 | 96.2204 | Calcium hardness | mg/L as CaCO3 | 24 | 230 | 610 | 710.6667 | -16.5027 | 89.5652 | 666.1605 | 96.3973 | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 3.2 |  |  |  | 6 | 1998-11-21 | 8:45 | 110.75 | 26.9 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0634 | 10.7842 | 48.7158 | 0.2271 | 5.6 | 6.5 | 6.6 | 97.35 | 443.3 | 1070.85 | 1250.5167 | -16.7779 | 78.0397 | 1175.7744 | 91.7204 | [16 empty] | Turbidity | ntu | BMRL | 12 | 9.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 17 | 15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 12 | 78 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 28 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 28 | 17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 6 | 1998-11-21 | 21:00 | 123 | 27.8 | 63 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7729 | 10.6642 | 50.8358 | 0.21192 | 5.8 | 6.4 | 6.6 | 121.55 | 463.65 | 1193.5 | 1261.8833 | -5.7296 | 73.7841 | 1187.9728 | 89.7683 | [16 empty] | Ammonia | mg NH3-N / L | 0.2 | 0.42 | 0.8 | 0.93333 | -16.6667 | 52.381 | 0.8858 | 77.4216 | Ammonia | mg NH3-N / L | BMRL | 0.46 | 1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.25 | 0.58 | 0.67 | 1.35 | -101.4925 | 56.8966 | 1.2787 | 80.449 | Ammonia | mg NH3-N / L | 0.26 | 0.44 | 0.85 | 0.86 | -1.1765 | 40.9091 | 0.82111 | 68.3356 | Ammonia | mg NH3-N / L | 0.23 | 0.43 | 0.89 | 0.89667 | -0.74906 | 46.5116 | 0.85346 | 73.0508
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 7 | 1998-11-22 | 18:00 | 144 | 28.1 | 63 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6778 | 9.9956 | 51.5044 | 0.20732 | 5.8 | 6.4 | 6.6 | 134.75 | 455.4 | 1237.5 | 1203.5833 | 2.7407 | 70.4106 | 1134.3071 | 88.1205 | [16 empty] | Total organic carbon | mg/L | BMRL | 5.3 | 16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.89 | 6 | 20 | 17.9233 | 10.3833 | 85.1667 | 16.8193 | 94.7085 | Total organic carbon | mg/L | 0.7 | NR | 23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.7 | 19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.7 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 8 | 1998-11-23 | 2:30 | 152.5 | 28.1 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6778 | 10.6814 | 50.3186 | 0.2122 | 5.8 | 6.2 | 6.6 | 128.15 | 470.8 | 1248.5 | 1270.3167 | -1.7474 | 72.7804 | 1196.2873 | 89.2877 | [16 empty] | UV254 | cm-1 | 0.017 | 0.22 | 0.54 | 0.69367 | -28.4568 | 92.2727 | 0.64981 | 97.3838 | UV254 | cm-1 | 0.019 | 0.26 | 0.65 | 0.82233 | -26.5128 | 92.6923 | 0.77027 | 97.5333 | UV254 | cm-1 | 0.018 | 0.31 | 0.57 | 0.99133 | -73.9181 | 94.1935 | 0.92825 | 98.0609 | UV254 | cm-1 | 0.017 | 0.24 | 0.62 | 0.76033 | -22.6344 | 92.9167 | 0.71215 | 97.6129 | UV254 | cm-1 | 0.016 | 0.24 | 0.59 | 0.76267 | -29.2655 | 93.3333 | 0.71427 | 97.76
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.003 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 8 | 1998-11-23 | 8:30 | 158.5 | 28.6 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.5212 | 9.4812 | 52.5188 | 0.20033 | 5.6 | 6.4 | 6.4 | 156.2 | 460.35 | 1199 | 1170.0333 | 2.4159 | 66.0693 | 1104.3219 | 85.8556 | [16 empty] | SUVA | L/(mg*m) | #VALUE! | 4.1509 | 3.375 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.1348 | 4.3333 | 3.25 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.5714 | #VALUE! | 2.4783 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.2105 | 3.2632 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.2105 | 3.2778 | --- | --- | --- | --- | ---
Process Train Name | SEBST | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 8 | 1998-11-23 | 18:00 | 168 | 28 | 60 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7094 | 10.2699 | 48.2301 | 0.22205 | 5.8 | 6.3 | 6.6 | 137.5 | 466.95 | 1177 | 1235.6667 | -4.9844 | 70.5536 | 1164.4892 | 88.1922 | [16 empty] | Bromide | mg/L | 64 | 230 | 570 | 617.3333 | --- | 72.1739 | 581.4691 | 88.9934 | Bromide | mg/L | 58 | 240 | 560 | 664.6667 | --- | 75.8333 | 625.3457 | 90.7251 | Bromide | mg/L | 52 | 240 | 490 | 678.6667 | --- | 78.3333 | 638.0494 | 91.8502 | Bromide | mg/L | 66 | 240 | 630 | 646 | --- | 72.5 | 608.4074 | 89.152 | Bromide | mg/L | 66 | 250 | 620 | 679.3333 | --- | 73.6 | 639.5802 | 89.6807
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 9 | 1998-11-24 | 1:00 | 175 | 28.3 | 60 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6149 | 10.3213 | 48.1787 | 0.22032 | 5.9 | 6.4 | 6.6 | 127.6 | 458.7 | 1171.5 | 1231.2667 | -5.1017 | 72.1823 | 1159.7327 | 88.9975 | [16 empty] | SDS-Cl2 dose | mg/L | 20 | 18 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 12 | 15 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.6 | 14 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 12 | 16 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 12 | 16 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1154.0984 | [5 empty] | 9 | 1998-11-24 | 9:00 | 183 | 27.2 | 60 | 58 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.5322 | 10.0045 | 48.9955 | 0.25578 | 5.7 | 6 | 6.4 | 151.8 | 446.05 | 1166 | 1230.7167 | -5.5503 | 65.9679 | 1152.25 | 86.8258 | [16 empty] | SDS-Free Cl2 residual | mg/L | 9.8 | 1.4 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | 0.94 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.4 | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.5 | 1.2 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 201.9672 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 9 | 1998-11-24 | 18:00 | 192 | 27.1 | 59 | 56 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.2126 | 9.8643 | 47.6357 | 0.21439 | 5.7 | 6.3 | 6.5 | 128.7 | 460.35 | 1182.5 | 1178.925 | 0.30233 | 72.043 | 1115.1263 | 88.4587 | [16 empty] | SDS-Cl2 demand | mg/L | 10.2 | 16.6 | --- | 31.5333 | --- | 38.5542 | 30.1506 | 66.1698 | SDS-Cl2 demand | mg/L | 10.7 | 14 | --- | 21.7 | --- | 23.5714 | 20.987 | 49.0161 | SDS-Cl2 demand | mg/L | 4.3 | 13.06 | --- | 33.5 | --- | 67.075 | 31.6074 | 86.3956 | SDS-Cl2 demand | mg/L | 10.6 | 15 | --- | 25.2667 | --- | 29.3333 | 24.316 | 56.4074 | SDS-Cl2 demand | mg/L | 10.5 | 14.8 | --- | 24.8333 | --- | 29.0541 | 23.9043 | 56.0749
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | see guidelines | Influent TDS, TDSI (mg/L) | 1009.8361 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 10 | 1998-11-25 | 1:00 | 199 | 24.9 | 59 | 57 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.8987 | 9.7007 | 48.2993 | 0.22565 | 5.8 | 6.2 | 6.6 | 133.65 | 459.8 | 1171.5 | 1166.4583 | 0.43036 | 70.933 | 1103.7176 | 87.8909 | [16 empty] | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | see guidelines | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 10 | 1998-11-25 | 11:00 | 209 | 26.6 | 59 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.1619 | 9.1555 | 48.8445 | 0.22852 | 5.8 | 6.1 | 6.5 | 145.2 | 438.9 | 1166 | 1124.2 | 3.5849 | 66.9173 | 1060.7463 | 86.3115 | [16 empty] | SDS-Chlorination pH | --- | 8.2 | 8.17 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.18 | 8.06 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.19 | 8.1 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.18 | 8.13 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.16 | 8.19 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 10 | 1998-11-25 | 18:00 | 216 | 27.1 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9981 | 10.3556 | 49.1444 | 0.22379 | 5.8 | 6.3 | 6.6 | 118.8 | 451 | 1122 | 1226.1333 | -9.281 | 73.6585 | 1154.3617 | 89.7086 | [16 empty] | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 11 | 1998-11-26 | 3:00 | 225 | 25.5 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5308 | 10.5099 | 48.4901 | 0.2378 | 5.8 | 6.3 | 6.6 | 121 | 458.15 | 1116.5 | 1244.8333 | -11.4943 | 73.5894 | 1171.9923 | 89.6757 | [16 empty] | SDS-TOX | mg Cl- /L | 123 | 972 | --- | 2953 | --- | 87.3457 | 2769.5741 | 95.5589 | SDS-TOX | mg Cl- /L | 73 | 934 | --- | 2943 | --- | 92.1842 | 2756.9815 | 97.3522 | SDS-TOX | mg Cl- /L | 62 | 816 | --- | 2575.3333 | --- | 92.402 | 2412.4321 | 97.43 | SDS-TOX | mg Cl- /L | 69 | 830 | --- | 2605.6667 | --- | 91.6867 | 2441.2531 | 97.1736 | SDS-TOX | mg Cl- /L | 67 | 758 | --- | 2370.3333 | --- | 91.1609 | 2221.0432 | 96.9834
|  | Rejection of reference solute and conditions of test | MgSO4 2000 mg/l | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 11 | 1998-11-26 | 13:00 | 235 | 28.2 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6463 | 10.5099 | 48.4901 | 0.21956 | 5.8 | 6.5 | 6.6 | 111.1 | 448.25 | 1133 | 1234.9333 | -8.9968 | 75.2147 | 1162.0923 | 90.4397 | [16 empty] | SDS-CHCl3 | mg/L | 12 | 190 | --- | 605.3333 | --- | 93.6842 | 566.8765 | 97.8831 | SDS-CHCl3 | mg/L | 8.2 | 110 | --- | 347.5333 | --- | 92.5455 | 325.5395 | 97.4811 | SDS-CHCl3 | mg/L | 7.9 | 120 | --- | 381.5667 | --- | 93.4167 | 357.3475 | 97.7893 | SDS-CHCl3 | mg/L | 7.1 | 120 | --- | 383.4333 | --- | 94.0833 | 359.0414 | 98.0225 | SDS-CHCl3 | mg/L | 8.3 | 130 | --- | 413.9667 | --- | 93.6154 | 387.6735 | 97.859
|  | (e.g., solute type and concentration) | >90 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 11 | 1998-11-26 | 18:00 | 240 | 27.8 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7729 | 10.2699 | 49.2301 | 0.21883 | 5.7 | 6.3 | 6.6 | 125.4 | 454.85 | 1144 | 1223.5667 | -6.9551 | 72.4305 | 1152.3892 | 89.1183 | [16 empty] | SDS-BDCM | mg/L | 11 | 82 | --- | 247.6667 | --- | 86.5854 | 232.3272 | 95.2653 | SDS-BDCM | mg/L | 8.6 | 65 | --- | 196.6 | --- | 86.7692 | 184.4148 | 95.3366 | SDS-BDCM | mg/L | 7.8 | 100 | --- | 315.1333 | --- | 92.2 | 295.2136 | 97.3578 | SDS-BDCM | mg/L | 11 | 87 | --- | 264.3333 | --- | 87.3563 | 247.9136 | 95.563 | SDS-BDCM | mg/L | 13 | 73 | --- | 213 | --- | 82.1918 | 200.037 | 93.5012
|  | Variability of rejection of reference solute (%) | n/a | Required influent pressure, PI (psi) | 50.1913 | [5 empty] | 12 | 1998-11-27 | 1:00 | 247 | 25.5 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5308 | 10.5442 | 48.4558 | 0.23797 | 5.9 | 6.3 | 6.7 | 124.3 | 462.55 | 1160.5 | 1251.8 | -7.8673 | 73.1272 | 1178.7213 | 89.4547 | [16 empty] | SDS-DBCM | mg/L | 8 | 28 | --- | 74.6667 | --- | 71.4286 | 70.3457 | 88.6276 | SDS-DBCM | mg/L | 8.1 | 20 | --- | 47.7667 | --- | 59.5 | 45.1957 | 82.0779 | SDS-DBCM | mg/L | 6.2 | 23 | --- | 62.2 | --- | 73.0435 | 58.5704 | 89.4144 | SDS-DBCM | mg/L | 9.8 | 31 | --- | 80.4667 | --- | 68.3871 | 75.8864 | 87.086 | SDS-DBCM | mg/L | 12 | 31 | --- | 75.3333 | --- | 61.2903 | 71.2284 | 83.1528
|  | Standard testing recovery (%) | 20 | [7 empty] | 12 | 1998-11-27 | 14:30 | 260.5 | 27.8 | 59 | 56 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7729 | 10.2013 | 47.2987 | 0.22776 | 5.8 | 6.4 | 6.7 | 116.6 | 443.85 | 1021.35 | 1207.4333 | -18.2194 | 73.7299 | 1136.7312 | 89.7425 | [16 empty] | SDS-CHBr3 | mg/L | 1.6 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 2.5 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 1.2 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 1.4 | 1 | --- | 0.066667 | --- | -40 | 0.15309 | -814.5161 | SDS-CHBr3 | mg/L | 3 | 1.7 | --- | -1.3333 | --- | -76.4706 | -1.0525 | 385.044
|  | Standard testing pH | 7 | [7 empty] | 12 | 1998-11-27 | 19:00 | 265 | 27.4 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.901 | 10.4242 | 49.5758 | 0.21989 | 5.8 | 6.4 | 6.6 | 112.2 | 446.6 | 1144 | 1226.8667 | -7.2436 | 74.8768 | 1154.6198 | 90.2825 | [16 empty] | SDS-THM4 | mg/L | 32.6 | 300 | --- | 923.9333 | --- | 89.1333 | 866.1617 | 96.2363 | SDS-THM4 | mg/L | 27.4 | 195 | --- | 586.0667 | --- | 85.9487 | 549.8568 | 95.0169 | SDS-THM4 | mg/L | 23.1 | 243 | --- | 756.1 | --- | 90.4938 | 708.5907 | 96.74 | SDS-THM4 | mg/L | 29.3 | 239 | --- | 728.3 | --- | 87.7406 | 682.9944 | 95.7101 | SDS-THM4 | mg/L | 36.3 | 235.7 | --- | 700.9667 | --- | 84.5991 | 657.8864 | 94.4823
|  | Acceptable range of operating pressures | 50-250 | [7 empty] | 13 | 1998-11-28 | 1:00 | 271 | 24.2 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.9825 | 10.6814 | 49.3186 | 0.24296 | 5.8 | 6.4 | 6.7 | 125.95 | 468.6 | 1166 | 1268.1167 | -8.7579 | 73.1221 | 1194.0873 | 89.4522 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 3.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | 3.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [7 empty] | 13 | 1998-11-28 | 11:30 | 281.5 | 27 | 62 | 59 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.28328 | 0.69072 | 4.5361 | 12.06 | 10.558 | 6.4695 | 54.0305 | 0.19541 | 6 | 6.4 | 6.7 | 234.3 | 447.7 | 969.65 | 924.2933 | 4.6776 | 47.6658 | 881.2491 | 73.4127 | [16 empty] | SDS-DCAA* | mg/L | 5.4 | 74 | --- | 234.0667 | --- | 92.7027 | 219.2457 | 97.537 | SDS-DCAA* | mg/L | 2.5 | 44 | --- | 140.8333 | --- | 94.3182 | 131.8673 | 98.1042 | SDS-DCAA* | mg/L | 2.2 | 34 | --- | 108.2 | --- | 93.5294 | 101.3296 | 97.8289 | SDS-DCAA* | mg/L | 3 | 81 | --- | 263 | --- | 96.2963 | 246.1481 | 98.7812 | SDS-DCAA* | mg/L | 2.2 | 53 | --- | 171.5333 | --- | 95.8491 | 160.558 | 98.6298
|  | Typical pressure drop across a single element (psi) | 4 | [7 empty] | 13 | 1998-11-28 | 19:00 | 289 | 26.8 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0961 | 11.2986 | 50.7014 | 0.21885 | 5.6 | 6.3 | 6.6 | 108.35 | 470.8 | 1177 | 1316.5167 | -11.8536 | 76.986 | 1238.2096 | 91.2495 | [16 empty] | SDS-TCAA* | mg/L | 4.5 | 99 | --- | 319.5 | --- | 95.4545 | 299.0833 | 98.4954 | SDS-TCAA* | mg/L | 1.9 | 57 | --- | 185.5667 | --- | 96.6667 | 173.6623 | 98.9059 | SDS-TCAA* | mg/L | 1.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | 2.6 | 72 | --- | 233.9333 | --- | 96.3889 | 218.9395 | 98.8125 | SDS-TCAA* | mg/L | 1.7 | 29 | --- | 92.7 | --- | 94.1379 | 86.8019 | 98.0415
|  | Maximum permissible SDI | 5 | [7 empty] | 14 | 1998-11-29 | 3:00 | 297 | 24.9 | 62 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7371 | 10.8871 | 50.6129 | 0.2319 | 5.7 | 6.4 | 6.6 | 124.85 | 474.1 | 1199 | 1289.0167 | -7.5076 | 73.6659 | 1213.5614 | 89.7121 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 14 | 1998-11-29 | 8:45 | 302.75 | 26.1 | 63 | 61 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.28328 | 0.69072 | 4.5361 | 12.06 | 10.8426 | 10.4879 | 51.5121 | 0.21049 | 5.6 | 6.6 | 6.6 | 99 | 444.95 | 1010.35 | 1217.5717 | -20.5099 | 77.7503 | 1147.7911 | 91.3747 | [16 empty] | SDS-DBAA* | mg/L | 3.3 | 10 | --- | 25.6333 | --- | 67 | 24.1858 | 86.3556 | SDS-DBAA* | mg/L | BMRL | 7.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | 8.7 | 16 | --- | 33.0333 | --- | 45.625 | 31.4562 | 72.3425 | SDS-DBAA* | mg/L | 10 | 12 | --- | 16.6667 | --- | 16.6667 | 16.2346 | 38.403 | SDS-DBAA* | mg/L | 5.3 | 18 | --- | 47.6333 | --- | 70.5556 | 44.8895 | 88.1932
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 14 | 1998-11-29 | 18:00 | 312 | 27.7 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8048 | 10.6642 | 51.3358 | 0.21047 | 5.7 | 6.3 | 6.6 | 121 | 463.1 | 1210 | 1261.3333 | -4.2424 | 73.8717 | 1187.4228 | 89.8099 | [16 empty] | SDS-BCAA* | mg/L | 2.4 | 27 | --- | 84.4 | --- | 91.1111 | 79.0852 | 96.9653 | SDS-BCAA* | mg/L | BMRL | 22 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 5.2 | 20 | --- | 54.5333 | --- | 74 | 51.3358 | 89.8706 | SDS-BCAA* | mg/L | 7 | 23 | --- | 60.3333 | --- | 69.5652 | 56.8765 | 87.6926 | SDS-BCAA* | mg/L | 4.5 | 27 | --- | 79.5 | --- | 83.3333 | 74.6389 | 93.971
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 15 | 1998-11-30 | 3:00 | 321 | NR | NR | NR | NR | NR | NR | NR |  | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | [16 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 15 | 1998-11-30 | 9:00 | 327 | 26.2 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2947 | 10.6299 | 50.3701 | 0.22423 | 5.8 | 6.3 | 6.7 | 127.6 | 468.6 | 1100 | 1264.2667 | -14.9333 | 72.77 | 1190.5938 | 89.2827 | [16 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 15 | 1998-11-30 | 18:00 | 336 | 27.8 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7729 | 10.5956 | 48.9044 | 0.22029 | 5.9 | 6.4 | 6.7 | 119.35 | 459.25 | 1166 | 1252.35 | -7.4057 | 74.012 | 1178.9148 | 89.8763 | [16 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 16 | 1998-12-01 | 1:00 | 343 | 24.6 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8417 | 10.3556 | 48.6444 | 0.24343 | 6 | 6.3 | 6.8 | 128.7 | 460.9 | 1182.5 | 1236.0333 | -4.5271 | 72.0764 | 1164.2617 | 88.9458 | [16 empty] | SDS-HAA5 | mg/L | 13.2 | 183 | --- | 579.2 | --- | 92.7869 | 542.5148 | 97.5669 | SDS-HAA5 | mg/L | 4.4 | 108.2 | --- | 350.4 | --- | 95.9335 | 327.9741 | 98.6584 | SDS-HAA5 | mg/L | 12.7 | 53.4 | --- | 148.3667 | --- | 76.2172 | 139.5735 | 90.9008 | SDS-HAA5 | mg/L | 15.6 | 165 | --- | 513.6 | --- | 90.5455 | 481.3222 | 96.7589 | SDS-HAA5 | mg/L | 9.2 | 103.1 | --- | 322.2 | --- | 91.0766 | 301.913 | 96.9528
[11 empty] | 16 | 1998-12-01 | 11:00 | 353 | 28 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7094 | 9.4469 | 49.5531 | 0.21612 | 5.7 | 6.2 | 6.7 | 145.2 | 448.25 | 1144 | 1155.3667 | -0.99359 | 67.6074 | 1089.8929 | 86.6776 | [16 empty] | SDS-HAA6 | mg/L | 15.6 | 210 | --- | 663.6 | --- | 92.5714 | 621.6 | 97.4903 | SDS-HAA6 | mg/L | 4.4 | 130.2 | --- | 423.7333 | --- | 96.6206 | 396.5543 | 98.8904 | SDS-HAA6 | mg/L | 17.9 | 73.4 | --- | 202.9 | --- | 75.6131 | 190.9093 | 90.6238 | SDS-HAA6 | mg/L | 22.6 | 188 | --- | 573.9333 | --- | 87.9787 | 538.1988 | 95.8008 | SDS-HAA6 | mg/L | 13.7 | 130.1 | --- | 401.7 | --- | 89.4696 | 376.5519 | 96.3617
[11 empty] | 16 | 1998-12-01 | 18:00 | 360 | 27.8 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7729 | 10.6985 | 48.3015 | 0.22303 | 5.8 | 6.3 | 6.7 | 123.2 | 466.4 | 1144 | 1267.2 | -10.7692 | 73.5849 | 1193.0519 | 89.6735 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 17 | 1998-12-02 | 1:00 | 367 | 24.4 | 60 | 57 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.9119 | 10.6299 | 47.8701 | 0.24884 | 5.9 | 6.4 | 6.7 | 122.1 | 463.1 | 1133 | 1258.7667 | -11.1003 | 73.6342 | 1185.0938 | 89.697 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 17 | 1998-12-02 | 11:00 | 377 | 27.5 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8689 | 9.7041 | 51.2959 | 0.21189 | 5.8 | 6.2 | 6.6 | 129.25 | 440.55 | 1133 | 1166.9167 | -2.9935 | 70.6617 | 1099.6605 | 88.2464
[11 empty] | 17 | 1998-12-02 | 18:00 | 384 | 27.2 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9657 | 10.4928 | 51.5072 | 0.2129 | 5.8 | 6.4 | 6.8 | 113.85 | 450.45 | 1160.5 | 1235.85 | -6.4929 | 74.7253 | 1163.1278 | 90.2117 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 18 | 1998-12-03 | 1:00 | 391 | 25 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7025 | 10.0984 | 52.9016 | 0.22121 | 5.9 | 6.4 | 6.8 | 128.7 | 452.65 | 1166 | 1208.5333 | -3.6478 | 71.5674 | 1138.5441 | 88.6961 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 18 | 1998-12-03 | 9:00 | 399 | 26.5 | 64 | 62 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.7942 | 9.7427 | 53.2573 | 0.24023 | 5.7 | 6.2 | 6.8 | 149.05 | 435.6 | 1133 | 1199.7333 | -5.89 | 65.7828 | 1123.32 | 86.7313 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 18 | 1998-12-03 | 18:00 | 408 | 27.5 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8689 | 10.7671 | 53.2329 | 0.20418 | 5.8 | 6.4 | 6.7 | 107.25 | 452.65 | 1127.5 | 1258.5833 | -11.626 | 76.3062 | 1183.9599 | 90.9414 | [16 empty] | Qp/QT (THM4), % | 85.2655 | 98.7285 |  | Qp/QT (HAA5), % | 75.9717 | 91.8728 |  |  |  | Qp/QT (THM4), % | 73.389 | 94.8687 |  | Qp/QT (HAA5), % | 52.2158 | 78.2274 |  |  |  | Qp/QT (THM4), % | 77.7626 | 94.1337 |  | Qp/QT (HAA5), % | -1.4742 | 64.8649 |  |  |  | Qp/QT (THM4), % | 79.6376 | 96.805 |  | Qp/QT (HAA5), % | 74.2972 | 92.3695 |  |  |  | Qp/QT (THM4), % | 82.0963 | 100.1505 |  | Qp/QT (HAA5), % | 52.2897 | 81.0437
[11 empty] | 19 | 1998-12-04 | 1:00 | 415 | 25.4 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5649 | 7.3381 | 56.6619 | 0.2041 | 5.8 | 6.4 | 6.7 | 108.9 | 344.3 | 1160.5 | 893.5667 | 23.0016 | 68.3706 | 842.7086 | 87.0774 | [16 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 96.8516 | 54.3322 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 107.4863 | 63.8909 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 100.3622 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 83.1988 | 45.3012 |  |  |  | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 131.4344 | 74.0989
[11 empty] | 19 | 1998-12-04 | 10:45 | 424.75 | 26.7 | 62 | 60 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.28328 | 0.69072 | 4.5361 | 12.06 | 10.652 | 10.5213 | 50.4787 | 0.21102 | 5.6 | 6.5 | 6.7 | 75.35 | 422.4 | 1002.1 | 1197.4783 | -19.4969 | 82.1615 | 1127.4759 | 93.3169 | [16 empty] | SDS-HAA5b, mg/L | 38.2191 | 15.359 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 32.0222 | 9.7263 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 21.7506 | 15.0876 |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | SDS-HAA5b, mg/L | 46.0215 | 20.3734 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 26.0116 | NA |  | SDS-HAA5b, mg/L | 54 | 27
[11 empty] | 19 | 1998-12-04 | 21:00 | 435 | 27 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0307 | 10.5442 | 50.4558 | 0.21862 | 5.6 | 6.4 | 6.6 | 98.45 | 436.7 | 1122 | 1225.95 | -9.2647 | 77.4559 | 1152.8713 | 91.4605 | [16 empty] | SDS-TOXb, mg Cl- /L | 248.0957 | 133.7951 |  | SDS-TOXb, mg Cl- /L | 327 | 192 |  |  |  | SDS-TOXb, mg Cl- /L | 302.1205 | 117.1802 |  | SDS-TOXb, mg Cl- /L | 484.422 | 260.4624 |  |  |  | SDS-TOXb, mg Cl- /L | 229.6698 | 106.2319 |  | SDS-TOXb, mg Cl- /L | NA | 326.9189 |  |  |  | SDS-TOXb, mg Cl- /L | 223.958 | 93.3143 |  | SDS-TOXb, mg Cl- /L | 264.5984 | 127.0683 |  |  |  | SDS-TOXb, mg Cl- /L | 190.7146 | NA |  | SDS-TOXb, mg Cl- /L | 396.6784 | 197.9883
[11 empty] | 20 | 1998-12-05 | 1:00 | 439 | 25.4 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5649 | 10.4756 | 50.5244 | 0.2289 | 5.8 | 6.4 | 6.8 | 112.75 | 448.8 | 1127.5 | 1232.9167 | -9.3496 | 74.8775 | 1160.3133 | 90.2828 | [16 empty] | SDS-CDb, mg/L | 11.143 | 10.2814 |  | SDS-CDb, mg/L | 11.7378 | 10.7201 |  |  |  | SDS-CDb, mg/L | 11.5782 | 10.8693 |  | SDS-CDb, mg/L | 12.2769 | 11.4185 |  |  |  | SDS-CDb, mg/L | 6.248 | 4.8139 |  | SDS-CDb, mg/L | NA | 7.3778 |  |  |  | SDS-CDb, mg/L | 11.4959 | 10.7406 |  | SDS-CDb, mg/L | 11.7309 | 10.9357 |  |  |  | SDS-CDb, mg/L | 11.2699 | NA |  | SDS-CDb, mg/L | 12.5515 | 11.3151
[11 empty] | 20 | 1998-12-05 | 8:40 | 446.6667 | 25.9 | 62 | 60 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.28328 | 0.69072 | 4.5361 | 12.06 | 10.9069 | 10.0877 | 50.9123 | 0.21423 | 5.6 | 6.5 | 6.8 | 90.75 | 423.5 | 1043.35 | 1166.6417 | -11.8169 | 78.5714 | 1099.5237 | 91.7464 | [16 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | 2.2498 | 1.1522 |  | TOCb, mg/L | 3.3318 | 2.0026 |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 20 | 1998-12-05 | 21:00 | 459 | 27 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0307 | 10.4071 | 50.5929 | 0.21803 | 5.8 | 6.5 | 6.8 | 92.95 | 426.8 | 1122 | 1205.7833 | -7.4673 | 78.2216 | 1133.6552 | 91.8009 | [16 empty] | UV254 b, cm-1 | 0.046911 | 0.019581 |  | UV254 b, cm-1 | 0.065777 | 0.033498 |  |  |  | UV254 b, cm-1 | 0.083132 | 0.031366 |  | UV254 b, cm-1 | 0.13416 | 0.071472 |  |  |  | UV254 b, cm-1 | 0.082933 | 0.03513 |  | UV254 b, cm-1 | NA | 0.12059 |  |  |  | UV254 b, cm-1 | 0.062408 | 0.024125 |  | UV254 b, cm-1 | 0.074317 | 0.034016 |  |  |  | UV254 b, cm-1 | 0.056104 | NA |  | UV254 b, cm-1 | 0.12287 | 0.058462
[11 empty] | 21 | 1998-12-06 | 3:00 | 465 | 25.8 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.429 | 9.7384 | 51.2616 | 0.22295 | 5.7 | 6.4 | 6.8 | 125.95 | 438.35 | 1105.5 | 1167.2833 | -5.5887 | 71.2673 | 1099.7895 | 88.5478 | [16 empty] | Bromideb, mg/L | 88.4592 | 66.1107 |  | Bromideb, mg/L | 103.8869 | 77.4912 |  |  |  | Bromideb, mg/L | 106.432 | 67.3389 |  | Bromideb, mg/L | 144.9672 | 97.6262 |  |  |  | Bromideb, mg/L | 93.8063 | 63.0286 |  | Bromideb, mg/L | NA | 118.0541 |  |  |  | Bromideb, mg/L | 101.4306 | 71.5594 |  | Bromideb, mg/L | 110.7229 | 79.2771 |  |  |  | Bromideb, mg/L | 98.9428 | NA |  | Bromideb, mg/L | 153.787 | 100.8797
[11 empty] | 21 | 1998-12-06 | 8:30 | 470.5 | 25.7 | 62 | 60 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.644 | 10.584 | 50.416 | 0.21112 | 5.6 | 6.6 | 6.8 | 72.05 | 427.9 | 1039.5 | 1198.9083 | -15.3351 | 83.162 | 1130.4543 | 93.6265 | [16 empty] | Alkb, mg/L CaCO3 | 54.6597 | 34.8691 |  | Alkb, mg/L CaCO3 | 68.3216 | 44.947 |  |  |  | Alkb, mg/L CaCO3 | 63.401 | 38.0549 |  | Alkb, mg/L CaCO3 | 88.3854 | 57.6917 |  |  |  | Alkb, mg/L CaCO3 | 64.9113 | 40.6821 |  | Alkb, mg/L CaCO3 | NA | 84 |  |  |  | Alkb, mg/L CaCO3 | 58.0639 | 36.0897 |  | Alkb, mg/L CaCO3 | 64.8996 | 41.7671 |  |  |  | Alkb, mg/L CaCO3 | 54.9168 | NA |  | Alkb, mg/L CaCO3 | 93.0692 | 56.2641
[11 empty] | 21 | 1998-12-06 | 21:00 | 483 | 26.8 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0961 | 10.4242 | 51.5758 | 0.21514 | 5.8 | 6.8 | 6.8 | 96.25 | 430.65 | 1144 | 1210.9167 | -5.8494 | 77.6501 | 1138.6698 | 91.5472 | [16 empty] | T-Hdb, mg/L CaCO3 | 72.184 | 40.9499 |  | T-Hdb, mg/L CaCO3 | 93.7456 | 56.8551 |  |  |  | T-Hdb, mg/L CaCO3 | 102.3986 | 50.4177 |  | T-Hdb, mg/L CaCO3 | 153.6378 | 90.6898 |  |  |  | T-Hdb, mg/L CaCO3 | 88.704 | 48.4311 |  | T-Hdb, mg/L CaCO3 | NA | 120.4324 |  |  |  | T-Hdb, mg/L CaCO3 | 83.7387 | 39.2752 |  | T-Hdb, mg/L CaCO3 | 97.5703 | 50.7631 |  |  |  | T-Hdb, mg/L CaCO3 | 79.161 | NA |  | T-Hdb, mg/L CaCO3 | 159.3408 | 81.9925
[11 empty] | 22 | 1998-12-07 | 3:00 | 489 | 23.5 | 62 | 61 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 11.3592 | 10.0442 | 51.4558 | 0.22076 | 5.6 | 6.4 | 6.762 | 101.2 | 438.9 | 1003.2 | 1170.5833 | -16.6849 | 76.9424 | 1105.6208 | 90.8468 | [16 empty] | Ca-Hdb, mg/L CaCO3 | 51.638 | 28.2124 |  | Ca-Hdb, mg/L CaCO3 | 67.8092 | 40.1413 |  |  |  | Ca-Hdb, mg/L CaCO3 | 76.432 | 37.3389 |  | Ca-Hdb, mg/L CaCO3 | 114.9672 | 67.6262 |  |  |  | Ca-Hdb, mg/L CaCO3 | 66.03 | 33.6153 |  | Ca-Hdb, mg/L CaCO3 | NA | 91.5676 |  |  |  | Ca-Hdb, mg/L CaCO3 | 63.9103 | 30.2623 |  | Ca-Hdb, mg/L CaCO3 | 74.3775 | 38.9558 |  |  |  | Ca-Hdb, mg/L CaCO3 | 60.8816 | NA |  | Ca-Hdb, mg/L CaCO3 | 122.2833 | 63.0501
[10 empty] | 3 | 22 | 1998-12-07 | 9:00 | 495 | 26 | 63 | 61 | 0 | 4.5 | 0.7 | 0.3 |  | 1 | 5.5 | 0.28975 | 0.7 | 4.5 | 12.6 | 11.3616 | 8.1198 | 53.8802 | 0.21087 | 5.6 | 6.2 | 6.6 | 146.3 | 406.45 | 1133 | 1013.4667 | 10.5502 | 64.0054 | 958.2833 | 84.7331 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 22 | 1998-12-07 | 23:00 | 509 | 26.1 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3281 | 10.5271 | 53.4729 | 0.21185 | 5.6 | 6.4 | 6.6 | 102.85 | 440.55 | 1138.5 | 1228.5167 | -7.9066 | 76.6542 | 1155.5568 | 91.0995 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 23 | 1998-12-08 | 1:00 | 511 | 24.1 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 12.018 | 10.8014 | 53.1986 | 0.22591 | 5.8 | 6.2 | 6.8 | 108.35 | 454.85 | 1155 | 1263.35 | -9.381 | 76.179 | 1188.4889 | 90.8834 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 23 | 1998-12-08 | 9:00 | 519 | 26.8 | 66 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0961 | 9.2926 | 55.7074 | 0.19919 | 5.8 | 6.2 | 6.6 | 136.4 | 434.5 | 1138.5 | 1130.0667 | 0.74074 | 68.6076 | 1065.6623 | 87.2004 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 23 | 1998-12-08 | 21:00 | 531 | 26.4 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2281 | 10.7671 | 48.7329 | 0.2304 | 5.6 | 6.5 | 6.6 | 97.9 | 443.3 | 1105.5 | 1249.2333 | -13.0017 | 77.9156 | 1174.6099 | 91.6653 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 24 | 1998-12-09 | 5:00 | 539 | 25.1 | 60 | 58 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.8345 | 10.2732 | 48.7268 | 0.22235 | 5.7 | 6.3 | 6.7 | 111.1 | 456.5 | 1111 | 1204.8667 | -8.4488 | 75.6627 | 1138.4229 | 90.2409 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 24 | 1998-12-09 | 9:00 | 543 | 26 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 9.4126 | 49.5874 | 0.22912 | 5.7 | 6.3 | 6.6 | 131.45 | 433.4 | 1089 | 1137.95 | -4.4949 | 69.6701 | 1072.7139 | 87.746 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 24 | 1998-12-09 | 21:00 | 555 | 26 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 10.6642 | 51.3358 | 0.22132 | 5.7 | 6.5 | 6.6 | 101.75 | 443.85 | 1133 | 1242.0833 | -9.6278 | 77.0756 | 1168.1728 | 91.2898 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 25 | 1998-12-10 | 1:00 | 559 | 25.4 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5649 | 10.7842 | 51.2158 | 0.22581 | 5.8 | 6.4 | 6.7 | 111.1 | 457.05 | 1149.5 | 1264.2667 | -9.9841 | 75.6919 | 1189.5244 | 90.6601 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[10 empty] | 3 | 25 | 1998-12-10 | 9:00 | 567 | 26 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 9.9784 | 52.0216 | 0.2184 | 5.6 | 6.1 | 6.6 | 119.9 | 440 | 1122 | 1186.9 | -5.7843 | 72.75 | 1117.7426 | 89.273 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 25 | 1998-12-10 | 21:00 | 579 | 25.9 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3953 | 10.7842 | 51.2158 | 0.2225 | 5.7 | 6.4 | 6.6 | 98.45 | 444.4 | 1138.5 | 1251.6167 | -9.9356 | 77.8465 | 1176.8744 | 91.6346 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 26 | 1998-12-11 | 1:00 | 583 | 24.9 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7371 | 10.6471 | 51.3529 | 0.22856 | 5.8 | 6.4 | 6.7 | 115.5 | 457.05 | 1144 | 1254 | -9.6154 | 74.7292 | 1180.2083 | 90.2136
[11 empty] | 26 | 1998-12-11 | 9:00 | 591 | 26 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 9.5327 | 52.4673 | 0.21655 | 5.7 | 6.4 | 6.6 | 140.8 | 446.6 | 1149.5 | 1160.1333 | -0.92504 | 68.4729 | 1094.0654 | 87.1306
[11 empty] | 26 | 1998-12-11 | 21:00 | 603 | 26.3 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2613 | 10.4413 | 53.5587 | 0.21026 | 5.8 | 6.7 | 6.7 | 92.95 | 427.9 | 1116.5 | 1209.45 | -8.3251 | 78.2776 | 1137.0843 | 91.8256
[11 empty] | 27 | 1998-12-12 | 3:00 | 609 | 24.7 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8067 | 9.5841 | 54.4159 | 0.21697 | 5.8 | 6.6 | 6.7 | 153.45 | 460.9 | 1144 | 1178.2833 | -2.9968 | 66.7064 | 1111.859 | 86.1988
[11 empty] | 27 | 1998-12-12 | 8:45 | 614.75 | 26.1 | 65 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3281 | 10.7157 | 52.7843 | 0.21461 | 5.7 | 6.5 | 6.7 | 87.45 | 431.2 | 1096.15 | 1233.2833 | -12.5105 | 79.7194 | 1159.0164 | 92.4548
[11 empty] | 27 | 1998-12-12 | 21:00 | 627 | 26.2 | 72 | 70 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.1014 | 11.0062 | 59.9938 | 0.20171 | 5.7 | 6.7 | 6.7 | 91.85 | 429.55 | 1210 | 1273.8 | -5.2727 | 78.6172 | 1192.4732 | 92.2975
[11 empty] | 28 | 1998-12-13 | 3:00 | 633 | 25.3 | 73 | 70 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5992 | 10.4413 | 61.0587 | 0.18997 | 5.7 | 6.7 | 6.7 | 98.45 | 433.4 | 1226.5 | 1214.95 | 0.9417 | 77.2843 | 1142.5843 | 91.3836
[11 empty] | 28 | 1998-12-13 | 10:25 | 640.4167 | 27.1 | 72 | 70 | 0 | 4.4 | 0.77 | 0.3 |  | 1.07 | 5.47 | 0.2861 | 0.71963 | 4.1121 | 13.86 | 12.098 | 11.1786 | 59.8214 | 0.20223 | 5.7 | 6.5 | 6.7 | 93.5 | 430.65 | 1097.25 | 1296.0017 | -18.1136 | 78.2886 | 1211.3649 | 92.2814
[11 empty] | 28 | 1998-12-13 | 21:00 | 651 | 26.3 | 72 | 70 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.0657 | 11.4364 | 59.5636 | 0.20257 | 5.8 | 6.8 | 6.8 | 97.9 | 448.8 | 1248.5 | 1326.05 | -6.2115 | 78.1863 | 1241.5443 | 92.1147
[11 empty] | 29 | 1998-12-14 | 3:00 | 657 | 24.5 | 73 | 71 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8767 | 10.6814 | 61.3186 | 0.19369 | 5.7 | 6.5 | 6.7 | 86.9 | 429.55 | 1091.2 | 1229.0667 | -12.6344 | 79.7695 | 1155.0373 | 92.4764
[11 empty] | 29 | 1998-12-14 | 11:00 | 665 | 26 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 10.8528 | 51.1472 | 0.22214 | 5.6 | 6.7 | 6.5 | 128.7 | 476.85 | 1155 | 1289.2 | -11.619 | 73.0104 | 1213.9824 | 89.3985
[11 empty] | 29 | 1998-12-14 | 21:00 | 675 | 24.7 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8067 | 11.1957 | 52.8043 | 0.22359 | 5.7 | 6.5 | 6.6 | 99 | 458.15 | 1138.5 | 1296.1667 | -13.8486 | 78.3914 | 1218.5725 | 91.8757
[11 empty] | 30 | 1998-12-15 | 3:00 | 681 | 24.6 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8417 | 11.5043 | 52.4957 | 0.22557 | 5.7 | 6.3 | 6.7 | 110 | 479.05 | 1166 | 1340.1667 | -14.9371 | 77.0379 | 1260.4336 | 91.2728
[11 empty] | 30 | 1998-12-15 | 10:00 | 688 | 25 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7025 | 13.2874 | 50.7126 | 0.23076 | 5.6 | 6.2 | 6.6 | 112.75 | 539 | 1091.75 | 1533.5833 | -40.4702 | 79.0816 | 1441.4923 | 92.1782
[11 empty] | 30 | 1998-12-15 | 21:00 | 699 | 24.8 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7719 | 11.3157 | 52.6843 | 0.22344 | 5.7 | 6.5 | 6.7 | 98.45 | 461.45 | 1160.5 | 1308.45 | -12.7488 | 78.6651 | 1230.0241 | 91.9961
[11 empty] | 31 | 1998-12-16 | 1:00 | 703 | 21.8 | 66 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 12.8634 | 11.2986 | 53.2014 | 0.24179 | 5.8 | 6.3 | 6.7 | 110.55 | 473 | 1166 | 1318.7167 | -13.0975 | 76.6279 | 1240.4096 | 91.0876
[11 empty] | 31 | 1998-12-16 | 9:00 | 711 | 24 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 | X | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 12.0535 | 9.0697 | 54.9303 | 0.21943 | 5.7 | 6.2 | 6.6 | 151.8 | 442.75 | 1149.5 | 1121.6333 | 2.4242 | 65.7143 | 1058.7738 | 85.6627
0.18997
0.25578
[10 empty] | 4 | [21 empty] | 0.21866
0.19901
0.21943
Note on E24: C. Hill (9/22/99): Reviewer changed from 0.092 to 0.003.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN17: C. Hill (9/22/99): Reviewer verified all weekly TDS values using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on BN42: C. Hill (9/22/99): Reviewer verified all values reported for DBAA and BCAA using analytical reports found in Exhibit 3 of the Summary Report.
Note on BP23: C. Hill (9/22/99): Reviewer corrected from 0.17 to 0.017 using Summary Report - Exhibit 3 which contains copies of analytical reports.
Note on BP26: C. Hill (9/22/99): Reviewer verified Cl2 dose and residual using analytical reports in Exhibit 3 of Summary Report. NOTE: THE DBP DATA IS CONSISTENT WITH THE REST OF THE STUDY. HOWEVER, THE RESIDUAL DOES EXCEED THE TYPICAL SDS-Cl2 RESIDUAL TOLERANCE. DPATTON(11/09/99): LAB RESULTS ARE FINAL, NO EXPLANATION FOR HIGH RESIDUAL.
Note on BR25: C. Hill (9/22/99): Reviewer corrected bromide using analytical reports in Summary Report - Exhibit 3.
Note on BY17: C. Hill (9/22/99): Reviewer verified all weekly TDS values using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on BY42: C. Hill (9/22/99): Reviewer verified all values reported for DBAA and BCAA using analytical reports found in Exhibit 3 of the Summary Report.
Note on CA23: C. Hill (9/22/99): Reviewer corrected from 0.19 to 0.019 using Summary Report - Exhibit 3 which contains copies of analytical reports.
Note on CC25: C. Hill (9/22/99): Reviewer corrected bromide using analytical reports in Summary Report - Exhibit 3.
Note on CJ17: C. Hill (9/22/99): Reviewer verified all weekly TDS values using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CJ42: C. Hill (9/22/99): Reviewer verified all values reported for DBAA and BCAA using analytical reports found in Exhibit 3 of the Summary Report.
Note on CM22: C. Hill (9/22/99): Verified by reviewer using analytical reports in Summary Report - Exhibit 3. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.3'. 12/08/1999: Data changed to NR. Original value was '9.3 mg/L'.
Note on CM40: C. Hill (9/22/99): Verified by reviewer using analytical reports in Summary Report - Exhibit 3. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17'. 12/08/1999: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CU17: C. Hill (9/22/99): Reviewer verified all weekly TDS values using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CU42: C. Hill (9/22/99): Reviewer verified all values reported for DBAA and BCAA using analytical reports found in Exhibit 3 of the Summary Report.
Note on CY25: C. Hill (9/22/99): Reviewer corrected bromide using analytical reports in Summary Report - Exhibit 3.
Note on DF17: C. Hill (9/22/99): Reviewer verified all weekly TDS values using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on DF42: C. Hill (9/22/99): Reviewer verified all values reported for DBAA and BCAA using analytical reports found in Exhibit 3 of the Summary Report.
Note on DH25: C. Hill (9/22/99): Reviewer corrected bromide using analytical reports in Summary Report - Exhibit 3.
Note on DI25: C. Hill (9/22/99): Reviewer corrected bromide using analytical reports in Summary Report - Exhibit 3.
Note on DJ25: C. Hill (9/22/99): Reviewer corrected bromide using analytical reports in Summary Report - Exhibit 3.
Note on DR6: C. Hill (9/21/99): Reviewer copied values reported for fourth quarter.

## NF70. 4th Quarter
FIELD-SET 4: 4th QUARTER SEBST RESULTS (FILE: Film Tec.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: SEBST Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [20 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [26 empty] | Field 4-7: Permeate, Feed, Concentrate And Blended Water Quality For Week 1 | [9 empty] | Field 4-8: Permeate, Feed, Concentrate And Blended Water Quality For Week 2 | [9 empty] | Field 4-9: Permeate, Feed, Concentrate And Blended Water Quality For Week 3 | [9 empty] | Field 4-10: Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-11: Duplicate Analysis Of Permeate, Feed, Concentrate And Blended Water Quality For Week 4 | [9 empty] | Field 4-12: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment | [19 empty] | 0.70108 |  | 12.672 | [31 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | Operating Parameters During Sample Collection | [9 empty] | General Cost Parameters
PWS Name | Green Meadows WTP | Membrane manufacturer | FilmTec Corp. | Average yearly temperature of feed water, TavgoC (oC) | 22.5 | Alkalinity (mg/L as CaCO3) | 240 | Process | Description | Scale |  | Date | Time | Operation | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1), Optional | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.7 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [8 empty] | Recovery during sample collection (decimal) | 0.75 | [7 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL 5360313 | Membrane trade name | FILMTEC | Temperature normalized MTCW, MTCW(TavgoC) (gfd/psi) | 0.38079 | Calcium Hardness (mg/L as CaCO3) | 210 | Cartridge Filtration | 1mm exclusion size | Pilot-scale |  | MM/DD/YY | hh:mm | Time | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | "X" | (gpm) | (gpm) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) |  | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [8 empty] | Feed flow rate during sample collection (gpm) | 1.1 | [7 empty] | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | N/A | Membrane element model number | NF70-4040 |  |  | LSI | 0.29 | Hydrochloric acid addition | pH = 6.4 | Pilot-scale | 0 | 1999-01-12 | 11:00 | 0 | 26.5 | 75.5 | 74 | 0 | 4.4 | 0.8 | 0.3 |  | 1.1 | 5.5 | 0.28694 | 0.72727 | 4 | 14.4 | 12.7942 | 11.0891 | 63.6609 | 0.20097 | NR | NR | NR | 100.65 | 426.8 | 1276 | 1296.5333 | -1.6092 | 76.4175 | 1209.56 | 91.6788 | [17 empty] | Influent flow rate during sample collection (gpm) | 4.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.4 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [8 empty] | Influent flow rate during sample collection (gpm) | 5.5 | [7 empty] | Capital Recovery Period (years) | 20
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Flow Rates1 |  | Dissolved iron (mg/L) | 0.45 |  |  |  | 1.2917 | 1999-01-13 | 18:00 | 31 | 27.9 | 61 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7411 | 10.1327 | 49.3673 | 0.21758 | 5.8 | 6.4 | 6.9 | 105.05 | 430.1 | 1083.5 | 1188.55 | -9.6954 | 75.5754 | 1118.3231 | 90.6065 | [66 empty] | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | discriminating | Design recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0.45 |  |  |  | 1.5833 | 1999-01-14 | 1:00 | 38 | 24.6 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8417 | 9.927 | 49.073 | 0.24131 | 6 | 6.5 | 6.9 | 110.55 | 429 | 1122 | 1172.05 | -4.4608 | 74.2308 | 1103.2491 | 89.9796 | [16 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Permeate, Feed and Concentrate Water Quality | [9 empty] | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane construction (e.g., thin-film composite) | Thin-Film Composite | Design flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | BMRL |  |  |  | 1.9167 | 1999-01-14 | 9:00 | 46 | 26 | 60 | 58 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 8.1268 | 50.8732 | 0.22333 | 6 | 6.3 | 7 | 139.15 | 399.85 | 1047.75 | 1008.15 | 3.7795 | 65.1994 | 951.8259 | 85.3807 | [16 empty] | Parameter | Units | Cp-1 | CF-1 | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CF-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CF-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CF-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 (dup) | CF-4 (dup) | CC-4 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 10
|  | Membrane hydrophobicity | Hydrophobic | Permeate flow rate, Qp (gpm) | 0.83333 | Total aluminum (mg/L) | BMRL |  |  |  | 2.2917 | 1999-01-14 | 18:00 | 55 | 27.8 | 63 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7729 | 9.9613 | 51.5387 | 0.20903 | 5.8 | 6.6 | 6.9 | 102.85 | 422.4 | 1149.5 | 1168.0167 | -1.6108 | 75.651 | 1098.9781 | 90.6413 | [16 empty] | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-26 | 1999-01-26 | 1999-01-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-02 | 1999-02-02 | 1999-02-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-09 | 1999-02-09 | 1999-02-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-09 | 1999-02-09 | 1999-02-09 | --- | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negatively Charged | Feed flow rate, QF (gpm) | 1.1111 | Fluoride (mg/L) | 0.41 |  |  |  | 2.6667 | 1999-01-15 | 3:00 | 64 | 24.2 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.9825 | 9.8756 | 51.1244 | 0.23438 | 5.9 | 6.4 | 7 | 105.6 | 422.4 | 1171.5 | 1161.6 | 0.84507 | 75 | 1093.1556 | 90.3399 | [16 empty] | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | 9:00 | --- | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  |  |  | Concentrate-waste flow rate, QW (gpm) | 0.27778 | Phosphate (mg/L) | BMRL |  |  |  | 3.1667 | 1999-01-15 | 15:00 | 76 | 26.4 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2281 | 10.5099 | 52.4901 | 0.21391 | 5.8 | 6.5 | 6.8 | 94.05 | 431.2 | 1243 | 1217.8833 | 2.0206 | 78.1888 | 1145.0423 | 91.7863 | [16 empty] | Operation time | hh.hh | 190 | 190 | 190 | --- | --- | --- | --- | --- | Operation time | hh.hh | 334 | 334 | 334 | --- | --- | --- | --- | --- | Operation time | hh.hh | 502 | 502 | 502 | --- | --- | --- | --- | --- | Operation time | hh.hh | 646 | 646 | 646 | --- | --- | --- | --- | --- | Operation time | hh.hh | 646 | 646 | 646 | --- | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  | Design Parameters |  | Minimum influent flow rate, QI, min (gpm) | 3 | Sulfate (mg/L) | 34 |  |  |  | 3.2917 | 1999-01-15 | 18:00 | 79 | 26.6 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.1619 | 10.7157 | 53.2843 | 0.20948 | 5.8 | 6.5 | 6.9 | 80.85 | 424.6 | 1122 | 1226.6833 | -9.3301 | 80.9585 | 1152.4164 | 92.9843 | [16 empty] | pH | --- | 6 | 6.72 | 6.8 | --- | --- | --- | --- | --- | pH | --- | 6.22 | 7.06 | 7.14 | --- | --- | --- | --- | --- | pH | --- | 5.89 | 6.66 | 7.11 | --- | --- | --- | --- | --- | pH | --- | 6.42 | 6.97 | 7.13 | --- | --- | --- | --- | --- | pH | --- | 6.11 | 6.69 | 7.22 | --- | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 14.95
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Maximum influent flow rate, QI, max (gpm) | 16 | Calcium (mg/L) | 85 |  |  |  | 3.5833 | 1999-01-16 | 1:00 | 86 | 23.6 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 12.1969 | 10.1156 | 52.8844 | 0.23063 | 6 | 6.4 | 6.9 | 97.9 | 422.4 | 1133 | 1179.5667 | -4.11 | 76.8229 | 1109.4586 | 91.1759 | [16 empty] | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 27 | 27 | 27 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Temperature | oC | 26 | 26 | 26 | --- | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 80 | Design influent flow rate2, QI (gpm) | 5.5 | Barium (mg/L) | 0.017 |  |  |  | 3.9861 | 1999-01-16 | 10:40 | 95.6667 | 25.2 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.6335 | 10.4585 | 53.5415 | 0.21728 | 5.9 | 6.7 | 6.9 | 62.7 | 398.2 | 987.8 | 1181.0333 | -19.562 | 84.2541 | 1108.5488 | 94.344 | [16 empty] | Alkalinity | mg/L as CaCO3 | 28 | 200 | 550 | 601.3333 | -9.3333 | 86 | 555.7273 | 94.9616 | Alkalinity | mg/L as CaCO3 | 26 | 200 | 570 | 606 | -6.3158 | 87 | 568.4074 | 95.4258 | Alkalinity | mg/L as CaCO3 | 31 | 210 | 540 | 627.6667 | -16.2346 | 85.2381 | 588.9938 | 94.7368 | Alkalinity | mg/L as CaCO3 | 32 | 36 | 650 | 48 | 92.6154 | 11.1111 | 46.8 | 31.6239 | Alkalinity | mg/L as CaCO3 | 31 | 31 | 610 | 31 | 94.918 | 0 | 31 | 0 | Electric Rate ($/kW-h) | 0.063
Mailing Address |  | Design flux, FW (gfd) | 28.7 | Design recycle flow rate, QR (gpm) | 4.3889 | Strontium (mg/L) | 0.32 |  |  |  | 4.2188 | 1999-01-16 | 16:15 | 101.25 | 27.1 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9981 | 9.6698 | 54.3302 | 0.20243 | 5.7 | 6.5 | 6.9 | 86.9 | 397.1 | 1029.05 | 1120.9 | -8.9257 | 78.1163 | 1053.8815 | 91.7543 | [16 empty] | Total dissolved solids | mg/L | 61 | 470 | 1300 | 1424.3333 | -9.5641 | 87.0213 | 1315.8864 | 95.3643 | Total dissolved solids | mg/L | 61 | 470 | 1300 | 1424.3333 | -9.5641 | 87.0213 | 1335.9691 | 95.434 | Total dissolved solids | mg/L | 71 | 510 | 1400 | 1534.3333 | -9.5952 | 86.0784 | 1439.4877 | 95.0677 | Total dissolved solids | mg/L | 73 | 490 | 1300 | 1741 | -33.9231 | 85.102 | 1615.9 | 95.4824 | Total dissolved solids | mg/L | 72 | 500 | 1200 | 1784 | -48.6667 | 85.6 | 1655.6 | 95.6511 | Fuel Oil Rate ($/gal) | N/A
|  | Net driving pressure at the design flux, NDP (psi) | 70 | Recycle ratio, r | 3.95 | Reactive silica (mg/L as SiO2) | 32 |  |  |  | 4.6667 | 1999-01-17 | 3:00 | 112 | 24.2 | 64 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.9825 | 10.5099 | 52.9901 | 0.22613 | 5.8 | 6.5 | 6.9 | 85.25 | 422.4 | 1028.5 | 1209.0833 | -17.5579 | 79.8177 | 1136.2423 | 92.4972 | [16 empty] | Total hardness | mg/L as CaCO3 | 25 | 280 | 760 | 875 | -15.1316 | 91.0714 | 807.3864 | 96.9036 | Total hardness | mg/L as CaCO3 | 21 | 290 | 870 | 917.6667 | -5.4789 | 92.7586 | 859.5494 | 97.5569 | Total hardness | mg/L as CaCO3 | 27 | 290 | 890 | 903.6667 | -1.5356 | 90.6897 | 846.8457 | 96.8117 | Total hardness | mg/L as CaCO3 | 24 | 280 | 810 | 1048 | -29.3827 | 91.4286 | 971.2 | 97.5288 | Total hardness | mg/L as CaCO3 | 24 | 270 | 780 | 1008 | -29.2308 | 91.1111 | 934.2 | 97.431 | Natural Gas Rate ($/ft3) | N/A
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.41 | 1: Flow rates and pressures may need to be adjusted in order to obtain |  | Turbidity (ntu) | 37 |  |  |  | 4.8993 | 1999-01-17 | 8:35 | 117.5833 | 25.6 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.4968 | 10.7842 | 53.2158 | 0.21604 | 5.8 | 6.6 | 7 | 57.2 | 403.15 | 711.7 | 1210.3667 | -70.067 | 85.8117 | 1135.6244 | 94.9631 | [16 empty] | Calcium hardness | mg/L as CaCO3 | 21 | 230 | 630 | 717.6667 | -13.9153 | 90.8696 | 662.25 | 96.829 | Calcium hardness | mg/L as CaCO3 | 17 | 240 | 700 | 760.3333 | -8.619 | 92.9167 | 712.1543 | 97.6129 | Calcium hardness | mg/L as CaCO3 | 22 | 230 | 720 | 715.3333 | 0.64815 | 90.4348 | 670.3951 | 96.7184 | Calcium hardness | mg/L as CaCO3 | 19 | 210 | 630 | 783 | -24.2857 | 90.9524 | 725.7 | 97.3818 | Calcium hardness | mg/L as CaCO3 | 18 | 210 | 610 | 786 | -28.8525 | 91.4286 | 728.4 | 97.5288 | Current Process Water Rate ($/1000 gal) | 1.38
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | the desired operating conditions. |  | SDI | 2.6 |  |  |  | 5.2917 | 1999-01-17 | 18:00 | 127 | 28.3 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6149 | 9.8756 | 52.1244 | 0.20364 | 5.8 | 6.5 | 7.1 | 91.85 | 408.65 | 1215.5 | 1147.85 | 5.5656 | 77.5236 | 1079.4056 | 91.4907 | [16 empty] | Turbidity | ntu | 0.04 | 0.9 | 5.5 | 2.9067 | 47.1515 | 95.5556 | 2.6786 | 98.5067 | Turbidity | ntu | BMRL | 3.1 | 0.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 2.2 | 1.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 17 | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 3.1 | 4.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | N/A
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | 2: The design influent flow rate must be within the range established by the |  | MFI | NA |  |  |  | 5.6667 | 1999-01-18 | 3:00 | 136 | 24.3 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.9471 | 10.3213 | 51.6787 | 0.23118 | 5.8 | 6.5 | 7 | 93.5 | 424.6 | 1243 | 1197.1667 | 3.6873 | 77.9793 | 1125.6327 | 91.6936 | [16 empty] | Ammonia | mg NH3-N / L | 0.23 | 0.46 | 0.91 | 0.99667 | -9.5238 | 50 | 0.93568 | 75.419 | Ammonia | mg NH3-N / L | 0.19 | 0.45 | 0.97 | 1.0567 | -8.9347 | 57.7778 | 1.0005 | 81.0094 | Ammonia | mg NH3-N / L | 0.25 | 0.56 | 1 | 1.2833 | -28.3333 | 55.3571 | 1.2164 | 79.4468 | Ammonia | mg NH3-N / L | 0.38 | 0.64 | 1.2 | 1.42 | -18.3333 | 40.625 | 1.342 | 71.6841 | Ammonia | mg NH3-N / L | 0.31 | 0.68 | 1.1 | 1.79 | -62.7273 | 54.4118 | 1.679 | 81.5366
|  | Minimum flow rate to the element, QI, min (gpm) | 3 | minimum and maximum influent flow rates (i.e., cells H14 and H15). |  | MPFI | NA | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 5.9167 | 1999-01-18 | 9:00 | 142 | 26 | 62 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 11.35 | 50.15 | 0.22655 | 5.8 | 6.3 | 7 | 86.9 | 451 | 1035.1 | 1300.5667 | -25.6465 | 80.7317 | 1221.9031 | 92.8881 | [16 empty] | Total organic carbon | mg/L | 0.71 | 7.9 | 20 | 24.6767 | -23.3833 | 91.0127 | 22.7702 | 96.8819 | Total organic carbon | mg/L | BMRL | 6.7 | 20 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.6 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.2 | 7.2 | 19 | 25.2 | -32.6316 | 83.3333 | 23.4 | 94.8718 | Total organic carbon | mg/L | BMRL | 6.7 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Green Meadows WTP | Total width of all membrane envelopes in the element, w (ft) | 13.2 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 6.2917 | 1999-01-18 | 18:00 | 151 | 27.5 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8689 | 10.0299 | 49.9701 | 0.21751 | 5.7 | 6.4 | 6.9 | 88.55 | 410.3 | 1100 | 1161.05 | -5.55 | 78.4182 | 1091.5361 | 91.8876 | [16 empty] | UV254 | cm-1 | 0.014 | 0.32 | 0.8 | 1.034 | -29.25 | 95.625 | 0.95286 | 98.5307 | UV254 | cm-1 | 0.013 | 0.27 | 0.63 | 0.86967 | -38.0423 | 95.1852 | 0.81414 | 98.4032 | UV254 | cm-1 | 0.018 | 0.25 | 0.64 | 0.79133 | -23.6458 | 92.8 | 0.74121 | 97.5715 | UV254 | cm-1 | 0.018 | 0.22 | 0.61 | 0.826 | -35.4098 | 91.8182 | 0.7654 | 97.6483 | UV254 | cm-1 | 0.05 | NR | 0.57 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Treatment Plant Category | SOFT | Feed spacer thickness, T (ft) | 0.003 | Estimate the Osmotic Pressure Gradient |  |  |  | is to list the pretreatment processes used in this particular SEBST run. |  |  | 6.5833 | 1999-01-19 | 1:00 | 158 | 25.6 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.4968 | 9.7384 | 50.2616 | 0.22874 | 5.8 | 6.4 | 7 | 95.7 | 408.1 | 1100 | 1137.0333 | -3.3667 | 76.5499 | 1069.5395 | 91.0522 | [16 empty] | SUVA | L/(mg*m) | 1.9718 | 4.0506 | 4 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 4.0299 | 3.15 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.7879 | 3.5556 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.5 | 3.0556 | 3.2105 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | #VALUE! | 3.1667 | --- | --- | --- | --- | ---
Process Train Name | SEBST | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | Manufacturer reported TDS rejection, RejTDS (decimal) | 0.8 | [5 empty] | 6.9167 | 1999-01-19 | 9:00 | 166 | 26 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 12.5159 | 47.4841 | 0.23927 | 5.8 | 6.3 | 6.9 | 89.65 | 491.15 | 1010.9 | 1427.9833 | -41.2586 | 81.7469 | 1341.2395 | 93.3159 | [16 empty] | Bromide | mg/L | 48 | 230 | 590 | 654.6667 | --- | 79.1304 | 606.4091 | 92.0846 | Bromide | mg/L | 46 | 200 | 600 | 559.3333 | --- | 77 | 526.0617 | 91.2558 | Bromide | mg/L | 45 | 230 | 620 | 661.6667 | --- | 80.4348 | 621.6975 | 92.7618 | Bromide | mg/L | 47 | 230 | 640 | 779 | --- | 79.5652 | 724.1 | 93.5092 | Bromide | mg/L | 50 | NR | 600 | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 1093 | Purchase price for an equivalent 8" x 40 " element ($) | 700 | Feed TDS, TDSF (mg/L) | 440 | [5 empty] | 7.2917 | 1999-01-19 | 18:00 | 175 | 29 | 62 | 60 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.3975 | 9.9441 | 51.0559 | 0.20365 | 5.7 | 6.5 | 6.9 | 89.1 | 408.1 | 1065.9 | 1152.4333 | -8.1183 | 78.1671 | 1083.5136 | 91.7768 | [16 empty] | SDS-Cl2 dose | mg/L | 10 | 12 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 11 | 13 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 12 | 12 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 15 | 13 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 16 | 19 | --- | --- | --- | --- | --- | ---
PWSID Number of Plant (if assigned) | FL 5360313 |  |  | Waste TDS, TDSW (mg/L) | 1154.0984 | [5 empty] | 7.75 | 1999-01-20 | 5:00 | 186 | 24.6 | 61 | 59 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.9958 | 9.5698 | 50.4302 | 0.21804 | 5.8 | 6.5 | 6.8 | 91.85 | 413.6 | 1079.1 | 1110.725 | -2.9307 | 77.7926 | 1048.8307 | 91.2426 | [16 empty] | SDS-Free Cl2 residual | mg/L | 1.2 | 0.95 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.6 | 0.65 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | 0.05 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 3.2 | 0.6 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.9 | 0.6 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | N/A | Additional Information |  | Permeate TDS, TDSp (mg/L) | 201.9672 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 7.9167 | 1999-01-20 | 9:00 | 190 | 26 | 61 | 59 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 10.8014 | 49.1986 | 0.23093 | 5.8 | 6.4 | 6.8 | 68.75 | 415.25 | 882.75 | 1223.75 | -38.6293 | 83.4437 | 1148.8889 | 94.016 | [16 empty] | SDS-Cl2 demand | mg/L | 8.8 | 11.05 | --- | 16.3 | --- | 20.362 | 15.7034 | 43.9612 | SDS-Cl2 demand | mg/L | 9.4 | 12.35 | --- | 19.2333 | --- | 23.8866 | 18.596 | 49.4515 | SDS-Cl2 demand | mg/L | 11.1 | 11.95 | --- | 13.9333 | --- | 7.113 | 13.7497 | 19.2709 | SDS-Cl2 demand | mg/L | 11.8 | 12.4 | --- | 14.2 | --- | 4.8387 | 14.02 | 15.8345 | SDS-Cl2 demand | mg/L | 13.1 | 18.4 | --- | 34.3 | --- | 28.8043 | 32.71 | 59.9511
Historical Average Water Temperature (oC) | N/A | Design cross-flow velocity (fps) | see guidelines | Influent TDS, TDSI (mg/L) | 1009.8361 | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 8.2917 | 1999-01-20 | 18:00 | 199 | 27 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0307 | 10.87 | 51.13 | 0.21574 | 5.9 | 6.7 | 7.1 | 58.3 | 407 | 814 | 1220.6333 | -49.955 | 85.6757 | 1145.2969 | 94.9096 | [16 empty] | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | ---
State Approved Plant Capacity (MGD) | 9 | Required influent flow to permeate flow rate ratio, QI:Qp | see guidelines | Osmotic pressure gradient, Dp (psi) | 8.8 | [5 empty] | 8.5833 | 1999-01-21 | 1:00 | 206 | 25.2 | 63 | 61 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.6335 | 10.1499 | 51.8501 | 0.22437 | 5.9 | 6.4 | 7 | 85.8 | 411.4 | 1127.5 | 1171.1333 | -3.8699 | 79.1444 | 1100.7877 | 92.2056 | [16 empty] | SDS-Chlorination pH | --- | 8.2 | 8.15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | 8.09 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.98 | 7.94 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.99 | 8.09 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.09 | 8.07 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | 15 | [7 empty] | 8.9167 | 1999-01-21 | 9:00 | 214 | 25 | 66 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7025 | 8.3839 | 57.1161 | 0.20489 | 5.9 | 6.3 | 6.9 | 130.35 | 399.3 | 1116.5 | 1026.85 | 8.0296 | 67.3554 | 968.7435 | 86.5444 | [16 empty] | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 83 | 83 | --- | --- | --- | --- | --- | ---
|  | Variability of design flux (%) | 15 | Estimate the Required Influent Pressure | [6 empty] | 9.2917 | 1999-01-21 | 18:00 | 223 | 28.7 | 66 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.4901 | 10.1842 | 54.8158 | 0.19137 | 5.8 | 6.5 | 7 | 85.8 | 412.5 | 1144 | 1174.8 | -2.6923 | 79.2 | 1104.2167 | 92.2298 | [16 empty] | SDS-TOX | mg Cl- /L | 32 | 700 | --- | 2258.6667 | --- | 95.4286 | 2081.5455 | 98.4627 | SDS-TOX | mg Cl- /L | 53 | 776 | --- | 2463 | --- | 93.1701 | 2306.7963 | 97.7024 | SDS-TOX | mg Cl- /L | 52 | 649 | --- | 2042 | --- | 91.9877 | 1913.0185 | 97.2818 | SDS-TOX | mg Cl- /L | 57 | 680 | --- | 2549 | --- | 91.6176 | 2362.1 | 97.5869 | SDS-TOX | mg Cl- /L | 49 | 717 | --- | 2721 | --- | 93.166 | 2520.6 | 98.056
|  | Rejection of reference solute and conditions of test | MgSO4 2000 mg/l | Estimated system pressure losses, DPloss (psi) | 2 | [5 empty] | 9.6667 | 1999-01-22 | 3:00 | 232 | 22.1 | 66 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 12.7499 | 10.2699 | 54.7301 | 0.23296 | 5.9 | 6.5 | 7 | 83.6 | 413.05 | 1116.5 | 1181.7667 | -5.8456 | 79.7603 | 1110.5892 | 92.4725 | [16 empty] | SDS-CHCl3 | mg/L | 5.2 | 200 | --- | 654.5333 | --- | 97.4 | 602.8818 | 99.1375 | SDS-CHCl3 | mg/L | 5.5 | 170 | --- | 553.8333 | --- | 96.7647 | 518.2932 | 98.9388 | SDS-CHCl3 | mg/L | 5.3 | 130 | --- | 420.9667 | --- | 95.9231 | 394.0253 | 98.6549 | SDS-CHCl3 | mg/L | 5.8 | 86 | --- | 326.6 | --- | 93.2558 | 302.54 | 98.0829 | SDS-CHCl3 | mg/L | 5.9 | 80 | --- | 302.3 | --- | 92.625 | 280.07 | 97.8934
|  | (e.g., solute type and concentration) | >90 | Design permeate pressure, Pp (psi) | 0 | [5 empty] | 10.1667 | 1999-01-22 | 15:00 | 244 | 27.2 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9657 | 10.9214 | 53.0786 | 0.20659 | 5.7 | 6.5 | 6.9 | 69.85 | 420.2 | 1111 | 1237.6833 | -11.4026 | 83.377 | 1161.9904 | 93.9888 | [16 empty] | SDS-BDCM | mg/L | 5.4 | 71 | --- | 224.0667 | --- | 92.3944 | 206.6727 | 97.3872 | SDS-BDCM | mg/L | 6.4 | 58 | --- | 178.4 | --- | 88.9655 | 167.2519 | 96.1734 | SDS-BDCM | mg/L | 6 | 51 | --- | 156 | --- | 88.2353 | 146.2778 | 95.8982 | SDS-BDCM | mg/L | 5.2 | 56 | --- | 208.4 | --- | 90.7143 | 193.16 | 97.3079 | SDS-BDCM | mg/L | 5.4 | 58 | --- | 215.8 | --- | 90.6897 | 200.02 | 97.3003
|  | Variability of rejection of reference solute (%) | n/a | Required influent pressure, PI (psi) | 50.1913 | [5 empty] | 10.375 | 1999-01-22 | 20:00 | 249 | 26.9 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0634 | 10.5442 | 53.4558 | 0.20696 | 5.8 | 6.5 | 7 | 61.6 | 399.85 | 996.05 | 1189.1 | -19.3816 | 84.5942 | 1116.0213 | 94.4804 | [16 empty] | SDS-DBCM | mg/L | 6.1 | 19 | --- | 49.1 | --- | 67.8947 | 45.6795 | 86.6461 | SDS-DBCM | mg/L | 6.3 | 19 | --- | 48.6333 | --- | 66.8421 | 45.8895 | 86.2714 | SDS-DBCM | mg/L | 6.9 | 17 | --- | 40.5667 | --- | 59.4118 | 38.3846 | 82.024 | SDS-DBCM | mg/L | 4.4 | 24 | --- | 82.8 | --- | 81.6667 | 76.92 | 94.2798 | SDS-DBCM | mg/L | 5.3 | 24 | --- | 80.1 | --- | 77.9167 | 74.49 | 92.885
|  | Standard testing recovery (%) | 20 | [7 empty] | 10.5833 | 1999-01-23 | 1:00 | 254 | 25.7 | 65 | 63 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.4628 | 10.1499 | 53.8501 | 0.21287 | 5.9 | 6.6 | 7 | 86.9 | 412.5 | 1127.5 | 1172.2333 | -3.9675 | 78.9333 | 1101.8877 | 92.1135 | [16 empty] | SDS-CHBr3 | mg/L | 1.7 | 0.63 | --- | -1.8667 | --- | -169.8413 | -1.583 | 207.3941 | SDS-CHBr3 | mg/L | 1.1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | 1.4 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHBr3 | mg/L | BMRL | 1.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing pH | 7 | [7 empty] | 10.9583 | 1999-01-23 | 10:00 | 263 | 26.4 | 66 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2281 | 10.4242 | 54.5758 | 0.20573 | 5.7 | 6.5 | 7 | 65.45 | 399.85 | 860.75 | 1180.1167 | -37.1033 | 83.6314 | 1107.8698 | 94.0923 | [16 empty] | SDS-THM4 | mg/L | 18.4 | 290.63 | --- | 925.8333 | --- | 93.6689 | 853.6511 | 97.8446 | SDS-THM4 | mg/L | 19.3 | 247 | --- | 778.3 | --- | 92.1862 | 729.1056 | 97.3529 | SDS-THM4 | mg/L | 19.6 | 198 | --- | 614.2667 | --- | 90.101 | 575.7235 | 96.5956 | SDS-THM4 | mg/L | 15.4 | 167.1 | --- | 622.2 | --- | 90.784 | 576.69 | 97.3296 | SDS-THM4 | mg/L | 16.6 | 163.1 | --- | 602.6 | --- | 89.8222 | 558.65 | 97.0286
|  | Acceptable range of operating pressures | 50-250 | [7 empty] | 11.2708 | 1999-01-23 | 17:30 | 270.5 | 27.1 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9981 | 10.6299 | 52.3701 | 0.21001 | 5.8 | 6.6 | 7 | 73.7 | 414.7 | 1160.5 | 1210.3667 | -4.297 | 82.2281 | 1136.6938 | 93.5163 | [16 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 3-9 | [7 empty] | 11.6667 | 1999-01-24 | 3:00 | 280 | 26.8 | 64 | 62 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0961 | 10.7157 | 52.2843 | 0.21223 | 5.7 | 6.6 | 7 | 70.4 | 414.15 | 1105.5 | 1216.2333 | -10.0166 | 83.0013 | 1141.9664 | 93.8352 | [16 empty] | SDS-DCAA* | mg/L | 3.3 | 73 | --- | 235.6333 | --- | 95.4795 | 217.1523 | 98.4803 | SDS-DCAA* | mg/L | 2.7 | 55 | --- | 177.0333 | --- | 95.0909 | 165.734 | 98.3709 | SDS-DCAA* | mg/L | 2.2 | 35 | --- | 111.5333 | --- | 93.7143 | 104.4469 | 97.8937 | SDS-DCAA* | mg/L | 3.2 | 40 | --- | 150.4 | --- | 92 | 139.36 | 97.7038 | SDS-DCAA* | mg/L | 2.9 | 49 | --- | 187.3 | --- | 94.0816 | 173.47 | 98.3282
|  | Typical pressure drop across a single element (psi) | 4 | [7 empty] | 11.9062 | 1999-01-24 | 8:45 | 285.75 | 25.1 | 67 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.6679 | 10.8357 | 55.1643 | 0.21151 | 5.8 | 6.7 | 7 | 52.25 | 399.85 | 763.4 | 1210.9167 | -58.6215 | 86.9326 | 1135.8179 | 95.3998 | [16 empty] | SDS-TCAA* | mg/L | 2 | 63 | --- | 205.3333 | --- | 96.8254 | 189.1591 | 98.9427 | SDS-TCAA* | mg/L | 1.7 | 52 | --- | 169.3667 | --- | 96.7308 | 158.4994 | 98.9274 | SDS-TCAA* | mg/L | 2 | 39 | --- | 125.3333 | --- | 94.8718 | 117.3395 | 98.2955 | SDS-TCAA* | mg/L | 1.9 | 31 | --- | 118.3 | --- | 93.871 | 109.57 | 98.2659 | SDS-TCAA* | mg/L | 1.9 | 43 | --- | 166.3 | --- | 95.5814 | 153.97 | 98.766
|  | Maximum permissible SDI | 5 | [7 empty] | 12.2917 | 1999-01-24 | 18:00 | 295 | 28 | 66 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7094 | 10.4928 | 54.5072 | 0.19648 | 5.8 | 6.6 | 7 | 78.1 | 414.7 | 1127.5 | 1200.1 | -6.439 | 81.1671 | 1127.3778 | 93.0724 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [7 empty] | 12.6667 | 1999-01-25 | 3:00 | 304 | 25.9 | 65 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3953 | 10.6471 | 53.8529 | 0.2116 | 5.8 | 6.6 | 7 | 73.15 | 414.7 | 1149.5 | 1211.65 | -5.4067 | 82.3607 | 1137.8583 | 93.5713 | [16 empty] | SDS-DBAA* | mg/L | 2.9 | 5.2 | --- | 10.5667 | --- | 44.2308 | 9.9568 | 70.8742 | SDS-DBAA* | mg/L | 2.7 | 6 | --- | 13.7 | --- | 55 | 12.987 | 79.21 | SDS-DBAA* | mg/L | 1.8 | 5.6 | --- | 14.4667 | --- | 67.8571 | 13.6457 | 86.809 | SDS-DBAA* | mg/L | 1.4 | 6.5 | --- | 21.8 | --- | 78.4615 | 20.27 | 93.0932 | SDS-DBAA* | mg/L | 1.7 | 7.5 | --- | 24.9 | --- | 77.3333 | 23.16 | 92.6598
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [7 empty] | 12.9167 | 1999-01-25 | 9:00 | 310 | 25 | 65 | 64 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.7025 | 12.533 | 51.967 | 0.22519 | 5.8 | 6.4 | 6.9 | 67.1 | 469.15 | 1009.25 | 1407.2667 | -39.4369 | 85.6975 | 1320.404 | 94.9182 | [16 empty] | SDS-BCAA* | mg/L | 2.7 | 20 | --- | 60.3667 | --- | 86.5 | 55.7795 | 95.1595 | SDS-BCAA* | mg/L | 2.5 | 20 | --- | 60.8333 | --- | 87.5 | 57.0525 | 95.6181 | SDS-BCAA* | mg/L | 2 | 14 | --- | 42 | --- | 85.7143 | 39.4074 | 94.9248 | SDS-BCAA* | mg/L | 2.1 | 18 | --- | 65.7 | --- | 88.3333 | 60.93 | 96.5534 | SDS-BCAA* | mg/L | 2.4 | 22 | --- | 80.8 | --- | 89.0909 | 74.92 | 96.7966
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 13.2917 | 1999-01-25 | 18:00 | 319 | 28.2 | 69 | 67 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.6463 | 10.4242 | 57.5758 | 0.18491 | 5.8 | 6.6 | 7.1 | 78.1 | 412.5 | 1149.5 | 1192.7667 | -3.764 | 81.0667 | 1120.5198 | 93.03 | [16 empty] | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 13.6667 | 1999-01-26 | 3:00 | 328 | 26.1 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3281 | 10.9385 | 58.0615 | 0.19511 | 5.8 | 6.6 | 7 | 76.45 | 427.35 | 1149.5 | 1246.1167 | -8.4051 | 82.1107 | 1170.3049 | 93.4675 | [16 empty] | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 13.9167 | 1999-01-26 | 9:00 | 334 | 26 | 70 | 67 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 12.293 | 56.207 | 0.20214 | 5.8 | 6.4 | 6.9 | 73.15 | 467.5 | 994.95 | 1387.65 | -39.4693 | 84.3529 | 1302.4509 | 94.3837 | [16 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
[11 empty] | 14.2917 | 1999-01-26 | 18:00 | 343 | 28.4 | 68 | 66 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.5835 | 10.1327 | 56.8673 | 0.18611 | 5.8 | 6.7 | 7.1 | 80.85 | 405.9 | 1111 | 1164.35 | -4.802 | 80.0813 | 1094.1231 | 92.6105 | [16 empty] | SDS-HAA5 | mg/L | 8.2 | 141.2 | --- | 451.5333 | --- | 94.1926 | 416.2682 | 98.0301 | SDS-HAA5 | mg/L | 7.1 | 113 | --- | 360.1 | --- | 93.7168 | 337.2204 | 97.8946 | SDS-HAA5 | mg/L | 6 | 79.6 | --- | 251.3333 | --- | 92.4623 | 235.4321 | 97.4515 | SDS-HAA5 | mg/L | 6.5 | 77.5 | --- | 290.5 | --- | 91.6129 | 269.2 | 97.5854 | SDS-HAA5 | mg/L | 6.5 | 99.5 | --- | 378.5 | --- | 93.4673 | 350.6 | 98.146
[11 empty] | 14.5833 | 1999-01-27 | 1:00 | 350 | 23.4 | 68 | 66 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 12.2692 | 10.0127 | 56.9873 | 0.2153 | 5.9 | 6.5 | 7 | 89.65 | 410.85 | 1116.5 | 1160.3167 | -3.9245 | 78.1794 | 1090.9216 | 91.7822 | [16 empty] | SDS-HAA6 | mg/L | 10.9 | 161.2 | --- | 511.9 | --- | 93.2382 | 472.0477 | 97.6909 | SDS-HAA6 | mg/L | 9.6 | 133 | --- | 420.9333 | --- | 92.782 | 394.2728 | 97.5651 | SDS-HAA6 | mg/L | 8 | 93.6 | --- | 293.3333 | --- | 91.453 | 274.8395 | 97.0892 | SDS-HAA6 | mg/L | 8.6 | 95.5 | --- | 356.2 | --- | 90.9948 | 330.13 | 97.395 | SDS-HAA6 | mg/L | 8.9 | 121.5 | --- | 459.3 | --- | 92.6749 | 425.52 | 97.9084
[11 empty] | 14.9167 | 1999-01-27 | 9:00 | 358 | 26 | 67 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 12.6702 | 53.3298 | 0.21304 | 5.7 | 6.3 | 7 | 83.6 | 490.05 | 1027.4 | 1438.4333 | -40.0071 | 82.9405 | 1350.6201 | 93.8103 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | 15.2917 | 1999-01-27 | 18:00 | 367 | 28 | 68 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.7094 | 10.5614 | 55.9386 | 0.19145 | 5.7 | 6.6 | 6.9 | 88 | 426.8 | 1177 | 1217.3333 | -3.4268 | 79.3814 | 1144.1358 | 92.3086 | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | 15.6667 | 1999-01-28 | 3:00 | 376 | 25.1 | 67 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.6679 | 10.5785 | 55.4215 | 0.21053 | 5.8 | 6.4 | 6.9 | 92.4 | 431.75 | 1149.5 | 1223.5667 | -6.4434 | 78.5987 | 1150.2503 | 91.967
[11 empty] | 15.9167 | 1999-01-28 | 9:00 | 382 | 26 | 67 | 65 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 12.2073 | 53.7927 | 0.21121 | 5.8 | 6.3 | 6.9 | 89.1 | 480.7 | 1021.35 | 1394.4333 | -36.5285 | 81.4645 | 1309.8284 | 93.1976 | [16 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs | [9 empty] | Blending Calculations For D-DBP MCLs
[11 empty] | 16.2917 | 1999-01-28 | 18:00 | 391 | 27.6 | 68 | 66 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8368 | 10.3385 | 56.6615 | 0.19125 | 5.7 | 6.5 | 6.9 | 98.45 | 430.1 | 1160.5 | 1203.95 | -3.7441 | 77.11 | 1132.2972 | 91.3053 | [17 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls | [5 empty] | THM4 Controls |  |  |  | HAA5 Controls
[11 empty] | 16.5833 | 1999-01-29 | 1:00 | 398 | 24.7 | 68 | 66 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.8067 | 10.3385 | 56.6615 | 0.20837 | 5.8 | 6.3 | 6.9 | 102.3 | 433.95 | 1188 | 1207.8 | -1.6667 | 76.4259 | 1136.1472 | 90.9959 | [17 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2
[11 empty] | 17.0833 | 1999-01-29 | 13:00 | 410 | 27.2 | 70 | 67 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.9657 | 10.6299 | 57.8701 | 0.18949 | 5.8 | 6.6 | 6.9 | 94.05 | 435.05 | 1171.5 | 1230.7167 | -5.0548 | 78.3818 | 1157.0438 | 91.8715 | [16 empty] | Qp/QT (THM4), % | 80.3108 | 93.5349 |  | Qp/QT (HAA5), % | 65.5639 | 85.8647 |  |  |  | Qp/QT (THM4), % | 76.8555 | 92.6658 |  | Qp/QT (HAA5), % | 55.7129 | 81.2087 |  |  |  | Qp/QT (THM4), % | 70.6278 | 90.8072 |  | Qp/QT (HAA5), % | 34.7826 | 71.4674 |  |  |  | Qp/QT (THM4), % | 62.6895 | 86.4206 |  | Qp/QT (HAA5), % | 33.0986 | 71.1268 |  |  |  | Qp/QT (THM4), % | 62.1843 | 86.7577 |  | Qp/QT (HAA5), % | 48.9247 | 77.957
[11 empty] | 17.2708 | 1999-01-29 | 17:30 | 414.5 | 26.6 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.1619 | 10.8528 | 58.1472 | 0.19196 | 5.9 | 6.6 | 7 | 79.75 | 427.9 | 1074.7 | 1240.25 | -15.4043 | 81.3625 | 1165.0324 | 93.1547 | [16 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 112.1454 | 56.8806 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 120.1416 | 62.0878 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 135.9478 | 70.5022 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 116.8894 | 59.2007 |  |  |  | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 91.4253 | 48.893
[11 empty] | 17.6042 | 1999-01-30 | 1:30 | 422.5 | 26.3 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2613 | 10.5099 | 58.4901 | 0.19253 | 5.9 | 6.6 | 7 | 92.4 | 429.55 | 1086.8 | 1216.2333 | -11.9096 | 78.4891 | 1143.3923 | 91.9188 | [16 empty] | SDS-HAA5b, mg/L | 34.3867 | 16.7986 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 31.61 | 14.8669 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 27.6179 | 12.7659 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 32.9904 | 16.1414 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | SDS-HAA5b, mg/L | 41.6686 | 18.8154 |  | SDS-HAA5b, mg/L | 54 | 27
[11 empty] | 17.9097 | 1999-01-30 | 8:50 | 429.8333 | 25.7 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.4628 | 11.2643 | 57.7357 | 0.19854 | 5.8 | 6.7 | 6.9 | 62.7 | 424.05 | 863.5 | 1267.2 | -46.7516 | 85.214 | 1189.1306 | 94.7272 | [16 empty] | SDS-TOXb, mg Cl- /L | 163.5241 | 75.187 |  | SDS-TOXb, mg Cl- /L | 262.0331 | 126.4241 |  |  |  | SDS-TOXb, mg Cl- /L | 220.3347 | 106.0264 |  | SDS-TOXb, mg Cl- /L | 373.1955 | 188.8612 |  |  |  | SDS-TOXb, mg Cl- /L | 227.352 | 106.8812 |  | SDS-TOXb, mg Cl- /L | 441.3478 | 222.3397 |  |  |  | SDS-TOXb, mg Cl- /L | 289.4443 | 141.5999 |  | SDS-TOXb, mg Cl- /L | 473.7958 | 236.8803 |  |  |  | SDS-TOXb, mg Cl- /L | 301.6089 | 137.4587 |  | SDS-TOXb, mg Cl- /L | 390.1828 | 196.2473
[11 empty] | 18.4167 | 1999-01-30 | 21:00 | 442 | 26.6 | 75 | 73 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.9592 | 10.8628 | 63.1372 | 0.18942 | 5.9 | 6.7 | 7 | 77 | 410.3 | 1085.7 | 1243.55 | -14.539 | 81.2332 | 1163.2828 | 93.3808 | [16 empty] | SDS-CDb, mg/L | 9.243 | 8.9455 |  | SDS-CDb, mg/L | 9.5748 | 9.118 |  |  |  | SDS-CDb, mg/L | 10.0828 | 9.6164 |  | SDS-CDb, mg/L | 10.7065 | 9.9543 |  |  |  | SDS-CDb, mg/L | 11.3497 | 11.1781 |  | SDS-CDb, mg/L | 11.6543 | 11.3425 |  |  |  | SDS-CDb, mg/L | 12.0239 | 11.8815 |  | SDS-CDb, mg/L | 12.2014 | 11.9732 |  |  |  | SDS-CDb, mg/L | 15.1042 | 13.8018 |  | SDS-CDb, mg/L | 15.807 | 14.2683
[11 empty] | 18.6667 | 1999-01-31 | 3:00 | 448 | 26.4 | 75 | 72 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.0301 | 10.7553 | 62.7447 | 0.19173 | 5.9 | 6.7 | 7 | 79.2 | 409.2 | 1084.6 | 1234.2 | -13.7931 | 80.6452 | 1154.7275 | 93.1412 | [16 empty] | TOCb, mg/L | 2.1257 | 1.1748 |  | TOCb, mg/L | 3.186 | 1.7263 |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | TOCb, mg/L | 3.4386 | 2.0148 |  | TOCb, mg/L | 5.2141 | 2.9324 |  |  |  | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE!
[11 empty] | 18.9097 | 1999-01-31 | 8:50 | 453.8333 | 25.8 | 74 | 72 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.2453 | 11.2213 | 61.7787 | 0.19821 | 5.9 | 6.6 | 6.9 | 74.25 | 418.55 | 954.25 | 1279.3 | -34.0634 | 82.2602 | 1196.3837 | 93.7938 | [16 empty] | UV254 b, cm-1 | 0.074249 | 0.033783 |  | UV254 b, cm-1 | 0.11937 | 0.057254 |  |  |  | UV254 b, cm-1 | 0.072481 | 0.031849 |  | UV254 b, cm-1 | 0.12682 | 0.061294 |  |  |  | UV254 b, cm-1 | 0.086143 | 0.039327 |  | UV254 b, cm-1 | 0.1693 | 0.084196 |  |  |  | UV254 b, cm-1 | 0.093367 | 0.04543 |  | UV254 b, cm-1 | 0.15314 | 0.076324 |  |  |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE!
[11 empty] | 19.2917 | 1999-01-31 | 18:00 | 463 | 28.3 | 75 | 73 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.3731 | 10.9345 | 63.0655 | 0.18034 | 5.8 | 6.5 | 7 | 90.2 | 425.7 | 1199 | 1264.45 | -5.4587 | 78.8114 | 1183.653 | 92.3795 | [16 empty] | Bromideb, mg/L | 83.8344 | 59.7665 |  | Bromideb, mg/L | 110.6737 | 73.7263 |  |  |  | Bromideb, mg/L | 81.6425 | 57.2947 |  | Bromideb, mg/L | 114.2021 | 74.9386 |  |  |  | Bromideb, mg/L | 99.3386 | 62.0067 |  | Bromideb, mg/L | 165.6522 | 97.7853 |  |  |  | Bromideb, mg/L | 115.2782 | 71.8504 |  | Bromideb, mg/L | 169.4296 | 99.838 |  |  |  | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE!
[11 empty] | 19.6667 | 1999-02-01 | 3:00 | 472 | 26.2 | 75 | 73 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.1014 | 10.5222 | 63.4778 | 0.19064 | 5.8 | 6.6 | 7 | 95.15 | 418 | 1171.5 | 1225.125 | -4.5775 | 77.2368 | 1147.3744 | 91.7072 | [16 empty] | Alkb, mg/L CaCO3 | 61.8655 | 39.12 |  | Alkb, mg/L CaCO3 | 87.2301 | 52.3128 |  |  |  | Alkb, mg/L CaCO3 | 66.2714 | 38.7615 |  | Alkb, mg/L CaCO3 | 103.0595 | 58.6969 |  |  |  | Alkb, mg/L CaCO3 | 83.5762 | 47.4552 |  | Alkb, mg/L CaCO3 | 147.7391 | 82.0734 |  |  |  | Alkb, mg/L CaCO3 | 33.4924 | 32.5432 |  | Alkb, mg/L CaCO3 | 34.6761 | 33.1549 |  |  |  | Alkb, mg/L CaCO3 | 31 | 31 |  | Alkb, mg/L CaCO3 | 31 | 31
[11 empty] | 19.9167 | 1999-02-01 | 9:00 | 478 | 26 | 75 | 73 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 12.6359 | 61.3641 | 0.18515 | 5.8 | 6.4 | 6.9 | 80.85 | 486.2 | 1092.3 | 1432.0167 | -31.101 | 83.371 | 1344.441 | 93.9863 | [16 empty] | T-Hdb, mg/L CaCO3 | 75.2075 | 41.4861 |  | T-Hdb, mg/L CaCO3 | 112.812 | 61.0451 |  |  |  | T-Hdb, mg/L CaCO3 | 83.2587 | 40.729 |  | T-Hdb, mg/L CaCO3 | 140.1322 | 71.5486 |  |  |  | T-Hdb, mg/L CaCO3 | 104.2489 | 51.1771 |  | T-Hdb, mg/L CaCO3 | 198.5217 | 102.0408 |  |  |  | T-Hdb, mg/L CaCO3 | 119.5148 | 58.7633 |  | T-Hdb, mg/L CaCO3 | 195.2676 | 97.9155 |  |  |  | T-Hdb, mg/L CaCO3 | 117.0266 | 56.5761 |  | T-Hdb, mg/L CaCO3 | 149.6452 | 78.2258
[11 empty] | 20.625 | 1999-02-02 | 2:00 | 495 | 25.3 | 73 | 71 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5992 | 10.2185 | 61.7815 | 0.18774 | 5.9 | 6.4 | 6.9 | 97.35 | 425.15 | 1166 | 1190.0167 | -2.0597 | 77.1022 | 1119.1957 | 91.3018 | [16 empty] | Ca-Hdb, mg/L CaCO3 | 62.1505 | 34.5121 |  | Ca-Hdb, mg/L CaCO3 | 92.9714 | 50.5429 |  |  |  | Ca-Hdb, mg/L CaCO3 | 68.6122 | 33.3553 |  | Ca-Hdb, mg/L CaCO3 | 115.7602 | 58.9046 |  |  |  | Ca-Hdb, mg/L CaCO3 | 83.0942 | 41.1211 |  | Ca-Hdb, mg/L CaCO3 | 157.6522 | 81.3478 |  |  |  | Ca-Hdb, mg/L CaCO3 | 90.263 | 44.9367 |  | Ca-Hdb, mg/L CaCO3 | 146.7817 | 74.1479 |  |  |  | Ca-Hdb, mg/L CaCO3 | 90.6061 | 43.4253 |  | Ca-Hdb, mg/L CaCO3 | 116.0645 | 60.3226
[11 empty] | 20.9167 | 1999-02-02 | 9:00 | 502 | 27 | 75 | 73 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0307 | 12.996 | 61.004 | 0.18082 | 5.7 | 6.4 | 6.9 | 83.05 | 499.95 | 916.3 | 1472.7167 | -60.7243 | 83.3883 | 1382.6457 | 93.9934 | [16 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes: | [9 empty] | Notes:
[11 empty] | 21.2917 | 1999-02-02 | 18:00 | 511 | 27.5 | 73 | 70 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8689 | 10.4585 | 61.0415 | 0.17806 | 5.7 | 6.5 | 6.9 | 88 | 423.5 | 1111 | 1206.3333 | -8.5809 | 79.2208 | 1133.8488 | 92.2388 | [16 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be
[11 empty] | 21.5833 | 1999-02-03 | 1:00 | 518 | 25.1 | 72 | 70 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.6679 | 10.3385 | 60.6615 | 0.19234 | 5.8 | 6.4 | 6.9 | 93.5 | 425.15 | 1127.5 | 1199 | -6.3415 | 78.0078 | 1127.3472 | 91.7062 | [16 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [9 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
[11 empty] | 21.9167 | 1999-02-03 | 9:00 | 526 | 27 | 72 | 70 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0307 | 9.4984 | 61.5016 | 0.17936 | 5.8 | 6.3 | 6.9 | 82.5 | 387.2 | 1105.5 | 1098.1667 | 0.66335 | 78.6932 | 1032.3364 | 92.0084 | [16 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [9 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
[11 empty] | 22.2917 | 1999-02-03 | 18:00 | 535 | 28.4 | 77 | 75 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 11.3395 | 10.8987 | 65.1013 | 0.17418 | 5.7 | 6.4 | 6.9 | 91.85 | 426.25 | 1166 | 1262.25 | -8.2547 | 78.4516 | 1181.7179 | 92.2274 | [16 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [9 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
[11 empty] | 22.5833 | 1999-02-04 | 1:00 | 542 | 25.5 | 77 | 75 | 0 | 4.4 | 0.75 | 0.3 |  | 1.05 | 5.45 | 0.28553 | 0.71429 | 4.1905 | 13.5 | 12.3544 | 10.8449 | 65.1551 | 0.18962 | 5.9 | 6.4 | 7 | 94.05 | 426.8 | 1188 | 1258.675 | -5.9491 | 77.9639 | 1178.5403 | 92.0198 | [16 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design. | [9 empty] | The maximum (Qp/QT) ratio controls the design.
[11 empty] | 22.9167 | 1999-02-04 | 9:00 | 550 | 26 | 75 | 71 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3616 | 12.1044 | 60.8956 | 0.18658 | 5.8 | 6.3 | 6.9 | 90.2 | 478.5 | 1075.8 | 1384.5333 | -28.698 | 81.1494 | 1300.6414 | 93.065 | [16 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [9 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[11 empty] | 23.2917 | 1999-02-04 | 18:00 | 559 | 28.4 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.5835 | 10.167 | 58.833 | 0.17989 | 5.7 | 6.5 | 6.9 | 92.4 | 418.55 | 1105.5 | 1179.5667 | -6.6998 | 77.9238 | 1109.1022 | 91.6689 | [16 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [9 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[11 empty] | 23.5833 | 1999-02-05 | 1:00 | 566 | 24.6 | 68 | 66 | 0 | 4.4 | 0.65 | 0.3 |  | 0.95 | 5.35 | 0.28272 | 0.68421 | 4.6316 | 11.7 | 10.9958 | 9.7334 | 57.2666 | 0.19201 | 5.8 | 6.5 | 7 | 99 | 426.25 | 1133 | 1135.2917 | -0.20227 | 76.7742 | 1072.3394 | 90.7678 | [16 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [9 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 24.0833 | 1999-02-05 | 13:00 | 578 | 27.5 | 71 | 69 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8689 | 10.87 | 59.13 | 0.18381 | 5.8 | 6.7 | 7 | 81.95 | 430.65 | 1111 | 1244.2833 | -11.9967 | 80.9706 | 1168.9469 | 92.9894 | [16 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [9 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[11 empty] | 24.2396 | 1999-02-05 | 16:45 | 581.75 | 27.6 | 71 | 69 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.8368 | 11.23 | 58.77 | 0.18439 | 5.8 | 6.7 | 6.9 | 66 | 426.25 | 788.15 | 1266.8333 | -60.7351 | 84.5161 | 1189.0015 | 94.4491 | [16 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [9 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[11 empty] | 24.5833 | 1999-02-06 | 1:00 | 590 | 25.5 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5308 | 10.0642 | 58.9358 | 0.19565 | 5.9 | 6.6 | 6.9 | 100.65 | 423.5 | 1111 | 1176.8167 | -5.9241 | 76.2338 | 1107.0651 | 90.9084
[11 empty] | 25.0833 | 1999-02-06 | 13:00 | 602 | 27.4 | 71 | 69 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.901 | 11.1614 | 58.8386 | 0.18527 | 5.8 | 6.5 | 7 | 82.5 | 440.55 | 1127.5 | 1276 | -13.1707 | 81.2734 | 1198.6435 | 93.1172
[11 empty] | 25.2431 | 1999-02-06 | 16:50 | 605.8333 | 27 | 71 | 69 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.0307 | 11.23 | 58.77 | 0.18769 | 5.8 | 6.7 | 7 | 66.55 | 426.8 | 790.35 | 1267.3833 | -60.3572 | 84.4072 | 1189.5515 | 94.4055
[11 empty] | 25.6667 | 1999-02-07 | 3:00 | 616 | 26.5 | 71 | 69 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.1949 | 10.9557 | 59.0443 | 0.1896 | 5.8 | 6.7 | 6.9 | 78.65 | 430.1 | #VALUE! | 1250.15 | #VALUE! | 81.7136 | 1174.2194 | 93.3019
[11 empty] | 25.9028 | 1999-02-07 | 8:40 | 621.6667 | 25.7 | 71 | 69 | 0 | 4.4 | 0.67 | 0.3 |  | 0.97 | 5.37 | 0.28328 | 0.69072 | 4.5361 | 12.06 | 10.9716 | 10.7047 | 59.2953 | 0.18503 | 5.7 | 6.7 | 6.9 | 68.2 | 421.3 | 869 | 1209.89 | -39.2278 | 83.812 | 1138.6673 | 94.0105
[11 empty] | 26.2917 | 1999-02-07 | 18:00 | 631 | 28.4 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.5835 | 10.3899 | 58.6101 | 0.18058 | 5.7 | 6.5 | 6.9 | 91.3 | 424.6 | 1144 | 1202.3 | -5.0962 | 78.4974 | 1130.2907 | 91.9224
[11 empty] | 26.6667 | 1999-02-08 | 3:00 | 640 | 25.9 | 70 | 68 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.3953 | 10.0299 | 58.9701 | 0.19324 | 5.8 | 6.7 | 7 | 100.65 | 422.4 | 1144 | 1173.15 | -2.5481 | 76.1719 | 1103.6361 | 90.8801
[11 empty] | 26.8958 | 1999-02-08 | 8:30 | 645.5 | 26.2 | 73 | 70 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.2947 | 11.3672 | 60.1328 | 0.18783 | 5.9 | 6.7 | 7 | 67.65 | 432.3 | 1062.6 | 1283.15 | -20.7557 | 84.3511 | 1204.3676 | 94.3829
[11 empty] | 27.2917 | 1999-02-08 | 18:00 | 655 | 28.6 | 72 | 70 | 0 | 4.4 | 0.7 | 0.3 | X | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 10.5212 | 10.4585 | 60.5415 | 0.17378 | 5.8 | 6.6 | 6.9 | 93.5 | 429 | 1171.5 | 1211.8333 | -3.4429 | 78.2051 | 1139.3488 | 91.7936
[11 empty] | 27.6667 | 1999-02-09 | 3:00 | 664 | 25.5 | 72 | 70 | 0 | 4.4 | 0.7 | 0.3 |  | 1 | 5.4 | 0.28413 | 0.7 | 4.4 | 12.6 | 11.5308 | 10.287 | 60.713 | 0.18992 | 5.9 | 6.6 | 7 | 100.1 | 430.1 | 1160.5 | 1200.1 | -3.4123 | 76.7263 | 1128.8037 | 91.1322
0.17378
0.24131
0.20257
0.20097
0.18992
Note on A2: C. Hill (9/22/99): 3rd Week SDS feed free Cl2 residual was BMRL. The corresponding DBP data should be used with caution.
Note on E24: C. Hill (9/22/99): Reviewer changed from 0.092 to 0.003.
Note on AA85: TSC_ADM: Reviewer entered cleaning event based on information in the final report and the consultant's response to comments dated 11/29/99.
Note on AS5: TSC_ADM: Consultant reported that the operational TDS data were measured in the field using a conductivity meter, which uses an average TDS conversion factor; however, a more accurate method was used to measure the TDS of the weekly water quality samples. This explains the large discrepancies between the operational TDS data and the TDS data collected during weekly water quality sampling.
Note on BN17: C. Hill (9/22/99): Reviewer verified weekly feed, permeate and concentrate TDS data using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on BQ37: C. Hill (9/22/99): Reviewer verified decreasing feed THM concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on BQ47: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on BQ48: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on BY17: C. Hill (9/22/99): Reviewer verified weekly feed, permeate and concentrate TDS data using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CB37: C. Hill (9/22/99): Reviewer verified decreasing feed THM concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CB47: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CB48: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CJ17: C. Hill (9/22/99): Reviewer verified weekly feed, permeate and concentrate TDS data using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CM27: S Allgeier (9.29): Low residual present at the end of the SDS test. DBP formation may have been limited during this SDS test.
Note on CM37: C. Hill (9/22/99): Reviewer verified decreasing feed THM concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CM47: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CM48: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CN25: C. Hill (9/22/99): Reviewer corrected (0.62 to 620) using Summary Report - Exhibit 3.
Note on CU17: C. Hill (9/22/99): Reviewer verified weekly feed, permeate and concentrate TDS data using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on CX16: C. Hill (9/22/99): Reviewer verified using Summary Report - Exhibit 3, which contains copies of analytical reports.
Note on CX37: C. Hill (9/22/99): Reviewer verified decreasing feed THM concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CX47: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on CX48: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on DF17: C. Hill (9/22/99): Reviewer verified weekly feed, permeate and concentrate TDS data using Exhibit 3 of the Summary Report. DPATTON (11/09/99): The TDS values reported in the operational data sheets are measured values of conductivity multiplied by an average TDS conversion factor. Lab reported results of TDS (weekly)are experimentally measured and are more accurate.
Note on DI37: C. Hill (9/22/99): Reviewer verified decreasing feed THM concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on DI47: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.
Note on DI48: C. Hill (9/22/99): Reviewer verified decreasing feed HAA concentrations for Weeks 1 to 4 using Summary Report - Exhibit 3.