## NF200. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.3851 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.52 | [7 empty] | Recovery during sample collection (decimal) | 0.31 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-05-13 | 1998-05-20 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.4 | [10 empty] | Feed flow rate during sample collection (mL/min) | 4.89 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.46 | [7 empty] | Feed flow rate during sample collection (mL/min) | 14.74 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 281 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [6 empty] | SDS-THM4F, ug/L | 566.1 | 566.1 | 566.1 | 566.1 | SDS-THM4F, ug/L | 566.1 | 566.1 | 566.1 | 566.1 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 24.25 | 24.25 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 56.75 | 74 | 57.4 | 38.4 | SDS-THM4p, ug/L | 56.75 | 74 | 57.4 | 38.4 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.5 | 8.17 | 8.335 | 3.9592 | 1998-05-05 | 11:00 | 0 | 23 | 65.5 | 64.5 | 281 | 5.54 | 10.4 | 15.94 | 0.2151 | 0.34755 | 16.6286 | 12.6448 | 13.2571 | 0 | 0 | 0 | 0 | 65 | 0.20396 | 1998-05-06 | 9:00 | 0 | 23 | 66 | 65 | 281 | 5.67 | 2.91 |  | 8.58 | 0.2151 | 0.66084 | 31.7506 | 12.9415 | 13.5682 | 399.4285 | 243.6743 | 396.2857 | 1.5418 | 63.9582 | 0.21214 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 219.9 | 219.9 | 219.9 | 219.9 | SDS-HAA5F, ug/L | 219.9 | 219.9 | 219.9 | 219.9 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.28066 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-05-05 | 12:00 | 1 | 23 | 66.5 | 66 | 281 | 5.71 | 2.55 | 8.26 | 0.2151 | 0.69128 | 33.0194 | 13.0328 | 13.664 | 0 | 0 | 0 | 0 | 66.25 | 0.20625 | 1998-05-06 | 9:45 | 0.75 | 23 | 66 | 65 | 281 | 5.11 | 2.4 |  | 7.51 | 0.2151 | 0.68043 | 36.4168 | 11.6633 | 12.2282 | 403.4005 | 246.2923 | 400.5435 | 1.5568 | 63.9432 | 0.19123 |  |  |  | 104 |  |  | 706.3646 |  | 64.9241 | 700.8876 | 85.1617 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 10.35 | 15.9 | 8.6 | 6.6 | SDS-HAA5p, ug/L | 10.35 | 15.9 | 8.6 | 6.6 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | highly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 216 | 166 | 191 | 26.178 | 1998-05-05 | 13:30 | 2.5 | 23 | 66 | 66 | 281 | 5.67 | 2.55 | 8.22 | 0.2151 | 0.68978 | 33.1849 | 12.9415 | 13.5682 | 0 | 0 | 0 | 0 | 66 | 0.20558 | 1998-05-06 | 11:20 | 2.3333 | 23 | 65 | 64 | 281 | 5 | 2.18 |  | 7.18 | 0.2151 | 0.69638 | 38.1365 | 11.4122 | 11.9649 | 406.8026 | 248.408 | 403.9842 | 1.5699 | 62.9301 | 0.19013 | 7.75 | 7.72 | 7.83 | 217 | 289 | 382 | 478.8394 | -25.3506 | 26.8128 | 476.5099 | 54.4605 | 0.015 | 0.624 | 1.143 | 1.6865 | -47.5495 | 97.1292 | 1.6716 | 99.1027 | [8 empty] | Sampling date | MM/DD/YY | 1998-05-06 | 1998-05-07 | --- | --- | 1998-05-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-09 | 1998-05-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-10 | 1998-05-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-11 | 1998-05-11 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1300 | 1300 | 1300 | 1300 | SDS-TOXF, ug Cl- /L | 1300 | 1300 | 1300 | 1300 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 294 | 299 | 296.5 | 1.6863 | 1998-05-05 | 14:20 | 3.3333 | 23 | 66 | 64.5 | 281 | 5.71 | 2.5 | 8.21 | 0.2151 | 0.69549 | 33.2266 | 13.0328 | 13.664 | 0 | 0 | 0 | 0 | 65.25 | 0.20941 | 1998-05-06 | 12:25 | 3.4167 | 23 | 65 | 64 | 281 | 5 | 2.33 |  | 7.33 | 0.2151 | 0.68213 | 37.3356 | 11.4122 | 11.9649 | 403.7291 | 246.5312 | 400.932 | 1.558 | 62.942 | 0.19009 | 7.74 |  |  | 230 |  |  | 439.2039 |  | 22.4283 | 437.3426 | 47.4097 | 0.015 |  |  | 1.6116 |  | 97.1292 | 1.5974 | 99.0609 | [8 empty] | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 18:30 | 18:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 75.5 | 110 | 72 | 49 | SDS-TOXp, ug Cl- /L | 75.5 | 110 | 72 | 49 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 200 | 190 | 195 | 5.1282 | 1998-05-05 | 15:00 | 4 | 23 | 66 | 64.5 | 281 | 5.67 | 2.45 | 8.12 | 0.2151 | 0.69828 | 33.6059 | 12.9415 | 13.5682 | 0 | 0 | 0 | 0 | 65.25 | 0.20794 | 1998-05-06 | 13:30 | 4.5 | 23 | 64 | 63 | 281 | 4.92 | 2.11 |  | 7.03 | 0.2151 | 0.69986 | 38.9716 | 11.2296 | 11.7735 | 407.5331 | 248.8822 | 404.7553 | 1.5726 | 61.9274 | 0.19012 |  |  |  | 233 |  |  | 444.5664 |  | 21.4165 | 442.7142 | 47.3701 | 0.015 |  |  | 1.7059 |  | 97.1292 | 1.6911 | 99.113 | [8 empty] | Operation time | hh.hh | 0 | 24 | --- | --- | 0 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80 | 80 | --- | --- | --- | --- | --- | Operation time | hh.hh | 105.5 | 105.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 126 | 126 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 18.77 | 18.77 | 18.77 | 18.77 | SDS-CDF, mg/L | 18.77 | 18.77 | 18.77 | 18.77 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 164 | 158 | 161 | 3.7267 | 1998-05-05 | 16:25 | 5.4167 | 23 | 66 | 64.5 | 281 | 5.49 | 2.5 | 7.99 | 0.2151 | 0.68711 | 34.169 | 12.5306 | 13.1375 | 0 | 0 | 0 | 0 | 65.25 | 0.20134 | 1998-05-06 | 15:00 | 6 | 23 | 64 | 63 | 281 | 5 | 2.23 |  | 7.23 | 0.2151 | 0.69156 | 37.8658 | 11.4122 | 11.9649 | 405.7587 | 247.7706 | 402.9476 | 1.5658 | 61.9342 | 0.19319 | 7.71 |  |  | 237 |  |  | 429.9081 |  | 20.0675 | 428.1918 | 44.651 | 0.015 |  |  | 1.6604 |  | 97.1292 | 1.6458 | 99.0886 | [8 empty] | pH | --- | 8.3 | 8.33 | 8.315 | 0.36079 | 8.71 | --- | --- | --- | --- | --- | pH | --- | 8.29 | 8.79 | --- | --- | --- | --- | --- | pH | --- | 8.32 | 8.77 | --- | --- | --- | --- | --- | pH | --- | 8.35 | 8.76 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.86 | 1.88 | 1.89 | 1.4 | SDS-CDp, mg/L | 1.86 | 1.88 | 1.89 | 1.4 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 15 | 6.5 | 59.9451 | 283.3154 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.95 | 0.96 | 0.955 | 1.0471 | 1998-05-05 | 16:40 | 5.6667 | 23 | 45 | 44 | 272 | 3.71 | 1.12 | 4.83 | 0.20821 | 0.76812 | 55.3147 | 8.4679 | 8.878 | 0 | 0 | 0 | 0 | 44.5 | 0.19951 | 1998-05-06 | 16:15 | 7.25 | 23 | 64 | 62.5 | 281 | 4.98 | 2.2 |  | 7.18 | 0.2151 | 0.69359 | 38.1365 | 11.3666 | 11.9171 | 406.1915 | 248.0419 | 403.3888 | 1.5675 | 61.6825 | 0.1932 | [5 empty] | 418 |  | #VALUE! | [5 empty] | 1.688 |  | #VALUE! | [11 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 14.4 | 14.4 | 14.4 | 14.4 | TOCF, mg/L | 14.4 | 14.4 | 14.4 | 14.4 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 15 | 16.5 | 69.9451 | 283.3154 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | NA | #DIV/0! | #VALUE! | 1998-05-05 | 17:00 | 6 | 23 | 56 | 54 | 272 | 4.67 | 1.43 | 6.1 | 0.20821 | 0.76557 | 43.5902 | 10.659 | 11.1752 | 0 | 0 | 0 | 0 | 55 | 0.20319 | 1998-05-06 | 17:30 | 8.5 | 23 | 64 | 62.5 | 281 | 4.96 | 2.18 |  | 7.14 | 0.2151 | 0.69468 | 38.3557 | 11.3209 | 11.8692 | 406.42 | 248.1884 | 403.627 | 1.5684 | 61.6816 | 0.19243 | 7.94 | 7.74 | 7.93 | 239 | 294 | 420 | 427.3257 | -1.7442 | 19.3929 | 425.6636 | 43.8524 | 0.016 | 0.624 | 1.779 | 1.6749 | 5.8514 | 96.9378 | 1.6603 | 99.0363 | [8 empty] | Alkalinity | mg/L as CaCO3 | 182 | 171 | 176.5 | 6.2323 | 320 | 223.2742 | 30.2268 | 7.5916 | 222.8492 | 20.7985 | Alkalinity | mg/L as CaCO3 | 188 | 354 | 215.2727 | 39.1885 | 1.5707 | 215.0545 | 12.5803 | Alkalinity | mg/L as CaCO3 | 184 | 284 | 198.5833 | 30.0763 | 3.6649 | 198.4469 | 7.28 | Alkalinity | mg/L as CaCO3 | 160 | 262 | 204.9275 | 21.7834 | 16.2304 | 204.5622 | 21.7842 | TOCp, mg/L | 0.9 | 1.4 | 0.9 | 0.6 | TOCp, mg/L | 0.9 | 1.4 | 0.9 | 0.6 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 57.9451 | 283.3154 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 14.4 | NA | 14.4 | #VALUE! | 1998-05-05 | 17:15 | 6.25 | 23 | 80 | 79 | 281 | 6.8 | 2.97 | 9.77 | 0.2151 | 0.69601 | 27.7615 | 15.5206 | 16.2723 | 0 | 0 | 0 | 0 | 79.5 | 0.20468 | 1998-05-07 | 9:00 | 24 | 23 | 63.5 | 62 | 281 | 4.69 | 2.15 |  | 6.84 | 0.2151 | 0.68567 | 40.0819 | 10.7047 | 11.2231 | 404.3882 | 247.0416 | 401.7621 | 1.5603 | 61.1897 | 0.18342 | [27 empty] | Total dissolved solids | mg/L | 222 | 224 | 223 | 0.89686 | 364 | 460.0968 | -26.4002 | 24.7892 | 457.9427 | 51.3039 | Total dissolved solids | mg/L | 223 | 367 | 891.1818 | -142.8288 | 24.7892 | 885.8362 | 74.826 | Total dissolved solids | mg/L | 223 | 357 | 376.125 | -5.3571 | 24.7892 | 374.693 | 40.4846 | Total dissolved solids | mg/L | 214 | 295 | 333.5652 | -13.073 | 27.8246 | 332.5931 | 35.6571 | UV254 F, cm-1 | 0.5225 | 0.5225 | 0.5225 | 0.5225 | UV254 F, cm-1 | 0.5225 | 0.5225 | 0.5225 | 0.5225 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 3.6429 | 57.0879 | 283.3154 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.57 | 0.475 | 0.5225 | 18.1818 | 1998-05-05 | 17:40 | 6.6667 | 23 | 64 | 62 | 281 | 5.33 | 1.77 | 7.1 | 0.2151 | 0.7507 | 38.5775 | 12.1654 | 12.7546 | 0 | 0 | 0 | 0 | 63 | 0.20245 | 1998-05-07 | 10:00 | 25 | 23 | 64 | 62.5 | 281 | 4.8 | 2.29 |  | 7.09 | 0.2151 | 0.67701 | 38.6333 | 10.9557 | 11.4863 | 402.5728 | 245.8945 | 399.8964 | 1.5534 | 61.6966 | 0.18617 | [27 empty] | Total hardness | mg/L as CaCO3 | 202 | 188 | 195 | 7.1795 | 285 | 195 | 31.5789 | 0 | 195 | 0 | Total hardness | mg/L as CaCO3 | 196 | 390 | 186.9091 | 52.0746 | -0.51282 | 186.9818 | -4.823 | Total hardness | mg/L as CaCO3 | 184 | 292 | 206.9167 | 29.1381 | 5.641 | 206.7023 | 10.9831 | Total hardness | mg/L as CaCO3 | 163 | 244 | 209.3768 | 14.1898 | 16.4103 | 208.9997 | 22.0095 | UV254 p, cm-1 | 0.023 | 0.038 | 0.026 | 0.016 | UV254 p, cm-1 | 0.023 | 0.038 | 0.026 | 0.016 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.9583 | NR | 3.9583 | #VALUE! | 1998-05-05 | 18:20 | 7.3333 | 23 | 66 | 64 | 281 | 5.57 | 2.55 | 8.12 | 0.2151 | 0.68596 | 33.6059 | 12.7132 | 13.3289 | 0 | 0 | 0 | 0 | 65 | 0.20506 | 1998-05-07 | 10:45 | 25.75 | 23 | 64 | 62.5 | 281 | 4.73 | 1.93 |  | 6.66 | 0.2151 | 0.71021 | 41.1922 | 10.796 | 11.3188 | 409.7374 | 250.2953 | 407.0535 | 1.581 | 61.669 | 0.18354 | 7.92 | 7.87 | 7.99 | 246 | 299 | 418 | 420.2642 | -0.54169 | 17.032 | 418.7976 | 41.2604 | 0.019 | 0.62 | 2.225 | 1.7565 | 21.0577 | 96.3636 | 1.7418 | 98.9092 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 190 | 161 | 175.5 | 16.5242 | 262 | 128.7258 | 50.868 | -9.0062 | 129.1508 | -35.8877 | Calcium hardness | mg/L as CaCO3 | 182 | 352 | -8.9091 | 102.531 | -13.0435 | -7.3818 | 2565.529 | Calcium hardness | mg/L as CaCO3 | 154 | 226 | 168.5833 | 25.4056 | 4.3478 | 168.4469 | 8.5766 | Calcium hardness | mg/L as CaCO3 | 144 | 212 | 168.6377 | 20.4539 | 10.559 | 168.4374 | 14.5083 | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | NA | 140 | #VALUE! | 1998-05-06 | 9:00 | 0 | 23 | 66 | 65 | 281 | 5.67 | 2.91 | 8.58 | 0.2151 | 0.66084 | 31.7506 | 12.9415 | 13.5682 | 0 | 0 | 0 | 0 | 65.5 | 0.20715 | 1998-05-07 | 11:40 | 26.6667 | 23 | 64 | 62.5 | 281 | 4.8 | 2.1 |  | 6.9 | 0.2151 | 0.69565 | 39.7246 | 10.9557 | 11.4863 | 406.578 | 248.3409 | 403.875 | 1.5689 | 61.6811 | 0.18622 | 7.89 |  |  | 241 |  |  | 423.3571 |  | 18.7184 | 421.7996 | 42.8639 | 0.017 |  |  | 1.6779 |  | 96.7464 | 1.6637 | 98.9782 | [8 empty] | Turbidity | ntu | 0.158 | 0.132 | 0.145 | 17.931 | 0.42 | 2.7579 | -556.6436 | 84.8168 | 2.7342 | 94.6967 | Turbidity | ntu | 0.129 | 0.522 | 7.6381 | -1363.2358 | 86.4921 | 7.578 | 98.2977 | Turbidity | ntu | 0.12 | 0.422 | 1.8596 | -340.6596 | 87.4346 | 1.8433 | 93.49 | Turbidity | ntu | 0.09 | 0.43 | 1.3436 | -212.4705 | 90.5759 | 1.3334 | 93.2505 | Bromidep, ug/L | 120 | 120 | 120 | 120 | Bromidep, ug/L | 120 | 120 | 120 | 120 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 20 | 20 | 20 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-07 | 12:45 | 27.75 | 23 | 64 | 62 | 281 | 4.7 | 2 |  | 6.7 | 0.2151 | 0.70149 | 40.9403 | 10.7275 | 11.247 | 407.8154 | 249.1318 | 405.1612 | 1.5736 | 61.4264 | 0.1831 | 7.87 |  |  | 247 |  |  | 412.825 |  | 16.6948 | 411.4382 | 39.9667 | 0.016 |  |  | 1.7128 |  | 96.9378 | 1.6986 | 99.058 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.13 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 191 | 191 | 191 | 191 | AlkF, mg/L CaCO3 | 191 | 191 | 191 | 191
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.5467 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.23 | 1.23 | 1.23 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-07 | 13:40 | 28.6667 | 23 | 63.5 | 62 | 281 | 4.93 | 2.05 |  | 6.98 | 0.2151 | 0.7063 | 39.2579 | 11.2525 | 11.7974 | 408.947 | 249.7421 | 406.1538 | 1.5781 | 61.1719 | 0.19286 | [27 empty] | Total organic carbon | mg/L | 0.9 | 0.9 | 0.9 | 0 | 61.5 | 44.4484 | 27.7262 | 93.75 | 44.0527 | 97.957 | Total organic carbon | mg/L | 1.4 | 97.6 | 119.5818 | -22.5224 | 90.2778 | 118.6363 | 98.8199 | Total organic carbon | mg/L | 0.9 | 42.7 | 29.025 | 32.0258 | 93.75 | 28.762 | 96.8709 | Total organic carbon | mg/L | 0.6 | 18.8 | 20.6 | -9.5745 | 95.8333 | 20.4374 | 97.0642 | Alkp, mg/L CaCO3 | 176.5 | 188 | 184 | 160 | Alkp, mg/L CaCO3 | 176.5 | 188 | 184 | 160
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.00233 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 18.77 | 18.77 | 18.77 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-07 | 14:40 | 29.6667 | 23 | 64 | 62 | 281 | 4.7 | 2.04 |  | 6.74 | 0.2151 | 0.69733 | 40.6914 | 10.7275 | 11.247 | 406.9087 | 248.5779 | 404.2605 | 1.5701 | 61.4299 | 0.18309 | 7.85 |  | 7.91 | 244 |  | 408 | 417.4559 | -2.3176 | 17.7066 | 416.0053 | 41.3469 | 0.016 |  | 1.88 | 1.6894 | 10.1364 | 96.9378 | 1.6754 | 99.045 | [8 empty] | UV254 | cm-1 | 0.026 | 0.02 | 0.023 | 26.087 | 2.27 | 1.6343 | 28.0048 | 95.5981 | 1.6197 | 98.5799 | UV254 | cm-1 | 0.038 | 2.6 | 4.4425 | -70.8671 | 92.7273 | 4.4073 | 99.1378 | UV254 | cm-1 | 0.026 | 1.446 | 1.0604 | 26.6684 | 95.0239 | 1.0507 | 97.5255 | UV254 | cm-1 | 0.016 | 0.742 | 0.75006 | -1.086 | 96.9378 | 0.74409 | 97.8497 | T-HdF, mg/L CaCO3 | 195 | 195 | 195 | 195 | T-HdF, mg/L CaCO3 | 195 | 195 | 195 | 195
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-07 | 16:05 | 31.0833 | 23 | 64 | 62 | 281 | 4.62 | 2 |  | 6.62 | 0.2151 | 0.69789 | 41.4471 | 10.5449 | 11.0556 | 407.0027 | 248.6633 | 404.3994 | 1.5704 | 61.4296 | 0.17997 | 7.9 | 7.86 | 8.01 | 244 | 285 | 406 | 417.775 | -2.9002 | 17.7066 | 416.3465 | 41.395 | 0.016 | 0.621 | 1.826 | 1.6925 | 7.3102 | 96.9378 | 1.6787 | 99.0469 | [8 empty] | SUVA | L/(mg*m) | 2.8889 | 2.2222 | 2.5556 | 26.087 | 3.6911 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.7143 | 2.6639 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8889 | 3.3864 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.6667 | 3.9468 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 195 | 196 | 184 | 163 | T-Hdp, mg/L CaCO3 | 195 | 196 | 184 | 163
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.7 | 8.7 | 8.7 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 8:45 | 47.75 | 23 | 64 | 62 | 281 | 4.65 | 1.9 |  | 6.55 | 0.2151 | 0.70992 | 41.9008 | 10.6134 | 11.1274 | 409.6466 | 250.2681 | 407.0092 | 1.5806 | 61.4194 | 0.18117 | [27 empty] | Bromide | mg/L | 120 | 120 | 120 | 0 | --- | 184.5161 | --- | 14.2857 | 183.93 | 34.7578 | Bromide | mg/L | 120 | --- | 301.8182 | --- | 14.2857 | 300.3636 | 60.0484 | Bromide | mg/L | 120 | --- | 161.6667 | --- | 14.2857 | 161.277 | 25.5939 | Bromide | mg/L | 120 | --- | 148.9855 | --- | 14.2857 | 148.7498 | 19.3276 | Ca-HdF, mg/L CaCO3 | 161 | 161 | 161 | 161 | Ca-HdF, mg/L CaCO3 | 161 | 161 | 161 | 161
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 9:30 | 48.5 | 23 | 64 | 63.5 | 281 | 4.69 | 1.8 |  | 6.49 | 0.2151 | 0.72265 | 42.2974 | 10.7047 | 11.2231 | 412.4825 | 251.9865 | 409.8038 | 1.5916 | 62.1584 | 0.18056 | [27 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 175.5 | 182 | 154 | 144 | Ca-Hdp, mg/L CaCO3 | 175.5 | 182 | 154 | 144
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 1300 | NA | 1300 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 10:15 | 49.25 | 23 | 64 | 63.5 | 281 | 4.6 | 2.07 |  | 6.67 | 0.2151 | 0.68966 | 41.1289 | 10.4993 | 11.0077 | 405.2152 | 247.5782 | 402.6346 | 1.5635 | 62.1865 | 0.17701 | 7.99 | 7.93 | 8.01 | 255 | 299 | 412 | 388.7222 | 5.6499 | 13.9966 | 387.6277 | 34.2152 | 0.029 | 0.616 | 2.6 | 1.6192 | 37.7244 | 94.4498 | 1.6062 | 98.1944 | [8 empty] | SDS-Free Cl2 residual | mg/L | 2.52 | 1.76 | 2.14 | 35.514 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 3.12 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.11 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.6 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 19 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 490 | NA | 490 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 11:00 | 50 | 23 | 64 | 62.5 | 281 | 4.6 | 2.01 |  | 6.61 | 0.2151 | 0.69592 | 41.5113 | 10.4993 | 11.0077 | 406.5683 | 248.4049 | 403.9792 | 1.5687 | 61.6813 | 0.17846 | 7.88 |  | 8.02 | 246 |  | 421 | 412.0721 | 2.1206 | 17.032 | 410.7128 | 40.1041 | 0.025 |  | 2.6 | 1.6611 | 36.1132 | 95.2153 | 1.6477 | 98.4827 | [8 empty] | SDS-Cl2 demand | mg/L | 1.48 | 2.24 | 1.86 | 40.8602 | --- | 56.4084 | --- | 90.0906 | 55.9128 | 96.6734 | SDS-Cl2 demand | mg/L | 1.88 | --- | 155.4255 | --- | 89.984 | 154.1971 | 98.7808 | SDS-Cl2 demand | mg/L | 1.89 | --- | 37.0567 | --- | 89.9307 | 36.7278 | 94.854 | SDS-Cl2 demand | mg/L | 1.4 | --- | 26.5739 | --- | 92.5413 | 26.3692 | 94.6908 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | minus 10%, plus 25% | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 69 | NA | 69 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 11:30 | 50.5 | 23 | 64 | 62.5 | 281 | 4.52 | 2.12 |  | 6.64 | 0.2151 | 0.68072 | 41.3193 | 10.3167 | 10.8163 | 403.2742 | 246.4201 | 400.7512 | 1.5559 | 61.6941 | 0.17532 | 7.99 |  |  | 248 |  |  | 399.9057 |  | 16.3575 | 398.6839 | 37.7953 | 0.025 |  |  | 1.5832 |  | 95.2153 | 1.5707 | 98.4083 | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 97.006 | 100.4064 | 97.1299 | 93.6327 | Qp/QT (THM4), % | 104.0738 | 107.722 | 104.2068 | 100.4548
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | >99% 2000 ppm MgSO4 @ 67 psi | [13 empty] | SDS-DBCM | mg/L | 7.1 | NA | 7.1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 13:15 | 52.25 | 23 | 64 | 62.5 | 281 | 4.58 | 1.88 |  | 6.46 | 0.2151 | 0.70898 | 42.4985 | 10.4536 | 10.9599 | 409.4144 | 250.1509 | 406.8186 | 1.5797 | 61.6703 | 0.17772 | [27 empty] | SDS-Chlorination pH | --- | 8.51 | 8.71 | 8.61 | 2.3229 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.45 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.62 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.62 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | NA | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NDP or< 50% 500 ppm CaCl2 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-08 | 16:50 | 55.8333 | 24 | 63.5 | 62.5 | 272 | 4.5 | 2.05 |  | 6.55 | 0.20821 | 0.68702 | 40.5267 | 10.271 | 10.4548 | 404.6648 | 247.2249 | 402.0601 | 1.5614 | 61.4386 | 0.17017 | 7.91 | 7.89 | 7.98 | 244 | 296 | 421 | 411.7439 | 2.1986 | 17.7066 | 410.3563 | 40.5395 | 0.024 | 0.619 | 2.988 | 1.6168 | 45.8913 | 95.4067 | 1.6036 | 98.5034 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 16.624 | NA | 14.6644 | 20.1814 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | unknown | [13 empty] | SDS-THM4 | mg/L | 566.1 | 0 | 566.1 | 100 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 12:30 | 75.5 | 24 | 64 | 62.5 | 272 | 4.5 | 2 |  | 6.5 | 0.20821 | 0.69231 | 40.8462 | 10.271 | 10.4548 | 405.8036 | 247.9206 | 403.1915 | 1.5658 | 61.6842 | 0.16949 | [27 empty] | SDS-TOX | mg Cl- /L | 73 | 78 | 75.5 | 6.6225 | --- | 4025.5 | --- | 94.1923 | 3989.6126 | 98.1076 | SDS-TOX | mg Cl- /L | 110 | --- | 10928.1818 | --- | 91.5385 | 10841.6344 | 98.9854 | SDS-TOX | mg Cl- /L | 72 | --- | 2630.3333 | --- | 94.4615 | 2606.4076 | 97.2376 | SDS-TOX | mg Cl- /L | 49 | --- | 1862.0435 | --- | 96.2308 | 1847.3023 | 97.3475 | SDS-TOXb, ug Cl- /L | 112.1617 | NA | 107.2443 | 128.6543 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 15 | [13 empty] | SDS-MCAA* | mg/L | 8.6 | NA | 8.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 13:30 | 76.5 | 24 | 64 | 62.5 | 272 | 4.5 | 1.9 |  | 6.4 | 0.20821 | 0.70312 | 41.5 | 10.271 | 10.4548 | 408.1546 | 249.3569 | 405.5274 | 1.5748 | 61.6752 | 0.16951 | [27 empty] | SDS-CHCl3 | mg/L | 7 | 5.5 | 6.25 | 24 | --- | 1566.7339 | --- | 98.7245 | 1552.5562 | 99.5974 | SDS-CHCl3 | mg/L | 13 | --- | 4349.3636 | --- | 97.3469 | 4314.6719 | 99.6987 | SDS-CHCl3 | mg/L | 5.4 | --- | 1014.9833 | --- | 98.898 | 1005.5416 | 99.463 | SDS-CHCl3 | mg/L | 3.6 | --- | 708.5275 | --- | 99.2653 | 702.796 | 99.4878 | SDS-CDb, mg/L | 2.3663 | NA | 2.3745 | 2.506 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7.0 + 0.3 | [13 empty] | SDS-DCAA* | mg/L | 120 | NA | 120 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 14:30 | 77.5 | 24 | 64 | 62.5 | 272 | 4.45 | 1.9 |  | 6.35 | 0.20821 | 0.70079 | 41.8346 | 10.1569 | 10.3386 | 407.6268 | 249.0526 | 405.0325 | 1.5728 | 61.6772 | 0.16762 | [27 empty] | SDS-BDCM | mg/L | 13 | 13 | 13 | 0 | --- | 193.6452 | --- | 81.1594 | 192.0039 | 93.2293 | SDS-BDCM | mg/L | 23 | --- | 441.1818 | --- | 66.6667 | 437.8363 | 94.7469 | SDS-BDCM | mg/L | 13 | --- | 129.6667 | --- | 81.1594 | 128.5756 | 89.8892 | SDS-BDCM | mg/L | 7.8 | --- | 96.4957 | --- | 88.6957 | 95.7745 | 91.8559 | TOCb, mg/L | 1.3042 | NA | 1.2875 | 1.4787 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | < 105 psi | [13 empty] | SDS-TCAA* | mg/L | 89 | NA | 89 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 14:45 | 77.75 | 24 | 64 | 62.5 | 272 | 4.44 | 0.77 |  | 5.21 | 0.20821 | 0.85221 | 51.2073 | 10.1341 | 10.3154 | 443.5412 | 270.9996 | 440.7247 | 1.7113 | 61.5387 | 0.16762 | 7.87 | 7.84 | 8.06 | 270 | 298 |  | 449.3052 |  | 8.9376 | 447.8417 | 39.7108 | 0.028 | 0.62 |  | 3.3739 |  | 94.6411 | 3.3466 | 99.1633 | [8 empty] | SDS-DBCM | mg/L | 22 | 24 | 23 | 8.6957 | --- | -28.2903 | --- | -223.9437 | -27.8243 | 182.6615 | SDS-DBCM | mg/L | 28 | --- | -162 | --- | -294.3662 | -160.48 | 117.4477 | SDS-DBCM | mg/L | 23 | --- | -10.125 | --- | -223.9437 | -9.8152 | 334.3301 | SDS-DBCM | mg/L | 15 | --- | 3.5507 | --- | -111.2676 | 3.6438 | -311.6566 | UV254 b, cm-1 | 0.037955 | NA | 0.04025 | 0.04825 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 3-10 (2-11 cleaning) | [13 empty] | SDS-MBAA* | mg/L | 1 | NA | 1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 15:15 | 78.25 | 24 | 64 | 62.5 | 272 | 4.32 | 0.75 |  | 5.07 | 0.20821 | 0.85207 | 52.6489 | 9.8602 | 10.0366 | 443.4458 | 270.9886 | 440.7068 | 1.7109 | 61.5391 | 0.16309 | 7.92 |  |  | 273 |  | 433 | 431.86 | 0.26328 | 7.9258 | 430.5985 | 36.5999 | 0.03 |  |  | 3.3593 |  | 94.2584 | 3.3329 | 99.0999 | [8 empty] | SDS-CHBr3 | mg/L | 13 | 16 | 14.5 | 20.6897 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 10 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 16 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 12 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 120.5988 | NA | 120.574 | 121.2735 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 3 | [13 empty] | SDS-DBAA* | mg/L | 1.3 | NA | 1.3 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 15:45 | 78.75 | 24 | 64 | 62.5 | 272 | 4.32 | 0.75 |  | 5.07 | 0.20821 | 0.85207 | 52.6489 | 9.8602 | 10.0366 | 443.4458 | 270.9886 | 440.7068 | 1.7109 | 61.5391 | 0.16309 | 7.87 |  |  | 274 |  | 435 | 426.1 | 2.046 | 7.5885 | 424.8921 | 35.513 | 0.031 |  | 2.998 | 3.3535 | -11.8592 | 94.067 | 3.3272 | 99.0683 | [8 empty] | SDS-THM4 | mg/L | 55 | 58.5 | 56.75 | 6.1674 | --- | 1699.8145 | --- | 89.9753 | 1684.8866 | 96.6318 | SDS-THM4 | mg/L | 74 | --- | 4547.6364 | --- | 86.9281 | 4511.8465 | 98.3599 | SDS-THM4 | mg/L | 57.4 | --- | 1117.1917 | --- | 89.8604 | 1107.2804 | 94.8161 | SDS-THM4 | mg/L | 38.4 | --- | 803.1826 | --- | 93.2167 | 796.9645 | 95.1817 | Alkb, mg/L CaCO3 | 176.9341 | NA | 184.2009 | 161.9738 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 5 | [13 empty] | SDS-BCAA* | mg/L | 16 | NA | 16 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 16:00 | 79 | 24 | 64 | 62.5 | 272 | 4.32 | 0.74 |  | 5.06 | 0.20821 | 0.85375 | 52.7549 | 9.8602 | 10.0366 | 443.8806 | 271.2543 | 441.1389 | 1.7126 | 61.5374 | 0.1631 |  |  |  | 270 |  | 450 | 451.2027 | -0.26727 | 8.9376 | 449.7637 | 39.9685 | 0.031 |  |  | 3.3918 |  | 94.067 | 3.3651 | 99.0788 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | 2.2 | --- | 60.3818 | --- | 74.4186 | 59.9164 | 96.3282 | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 195 | NA | 184.3157 | 165.0375 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 16:30 | 79.5 | 24 | 64 | 62.5 | 272 | 4.3 | 0.75 |  | 5.05 | 0.20821 | 0.85149 | 52.8614 | 9.8145 | 9.9901 | 443.2847 | 270.898 | 440.5595 | 1.7102 | 61.5398 | 0.16234 | [27 empty] | SDS-DCAA* | mg/L | 3.7 | 2.3 | 3 | 46.6667 | --- | 380.4194 | --- | 97.5 | 376.9903 | 99.2042 | SDS-DCAA* | mg/L | 4.7 | --- | 1052.8818 | --- | 96.0833 | 1044.4962 | 99.55 | SDS-DCAA* | mg/L | 2.3 | --- | 247.5083 | --- | 98.0833 | 245.2151 | 99.062 | SDS-DCAA* | mg/L | 2.2 | --- | 172.9246 | --- | 98.1667 | 171.5365 | 98.7175 | Ca-Hdb, mg/L CaCO3 | 175.0659 | NA | 154.2009 | 145.0824 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hour | [13 empty] | SDS-CDBAA | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 17:00 | 80 | 24 | 64 | 62.5 | 272 | 4.35 | 0.74 |  | 5.09 | 0.20821 | 0.85462 | 52.4381 | 9.9286 | 10.1063 | 444.1186 | 271.3879 | 441.3562 | 1.7135 | 61.5365 | 0.16423 |  |  |  | 273 |  |  | 434.6419 |  | 7.9258 | 433.3494 | 37.0023 | [16 empty] | SDS-TCAA* | mg/L | 1.5 | BMRL | 1.5 | #VALUE! | --- | 283.7581 | --- | 98.3146 | 281.1936 | 99.4666 | SDS-TCAA* | mg/L | 2.7 | --- | 787.2455 | --- | 96.9663 | 780.9689 | 99.6543 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 12 | NA | 12 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-09 | 17:30 | 80.5 | 24 | 64 | 62.5 | 272 | 4.3 | 0.72 |  | 5.02 | 0.20821 | 0.85657 | 53.1833 | 9.8145 | 9.9901 | 444.6001 | 271.7018 | 441.8668 | 1.7153 | 61.5347 | 0.16235 | [27 empty] | SDS-MBAA* | mg/L | 1 | BMRL | 1 | #VALUE! | --- | 1 | --- | 0 | 1 | 0 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 219.9 | 0 | 219.9 | 100 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 14:00 | 101 | 24 | 64 | 62.5 | 272 | 4.33 | 0.45 |  | 4.78 | 0.20821 | 0.90586 | 55.9038 | 9.883 | 10.0598 | 457.7726 | 279.7396 | 454.9385 | 1.7662 | 61.4838 | 0.16362 | 7.92 | 7.9 |  | 280 | 298 | 468 | 455.2667 | 2.7208 | 5.5649 | 453.8716 | 38.3085 | 0.056 | 0.618 | 4.45 | 5.0113 | -12.6127 | 89.2823 | 4.9718 | 98.8737 | [8 empty] | SDS-DBAA* | mg/L | 6.1 | 6.1 | 6.1 | 0 | --- | -9.3839 | --- | -369.2308 | -9.2432 | 165.9945 | SDS-DBAA* | mg/L | 6.3 | --- | -39.1545 | --- | -384.6154 | -38.7909 | 116.2409 | SDS-DBAA* | mg/L | 6.3 | --- | -4.1167 | --- | -384.6154 | -4.0192 | 256.7457 | SDS-DBAA* | mg/L | 4.4 | --- | -0.092754 | --- | -238.4615 | -0.056225 | 7925.7256 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 235.9 | 0 | 235.9 | 100 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 15:00 | 102 | 24 | 64 | 62.5 | 272 | 4.32 | 0.45 |  | 4.77 | 0.20821 | 0.90566 | 56.0231 | 9.8602 | 10.0366 | 457.7127 | 279.707 | 454.8855 | 1.7659 | 61.4841 | 0.16324 |  |  |  | 284 |  |  | 416.5 |  | 4.2159 | 415.4478 | 31.64 | 0.056 |  |  | 5.0009 |  | 89.2823 | 4.9616 | 98.8713 | [8 empty] | SDS-BCAA* | mg/L | 4.1 | 3.7 | 3.9 | 10.2564 | --- | 42.9323 | --- | 75.625 | 42.5776 | 90.8403 | SDS-BCAA* | mg/L | 6.5 | --- | 92.8636 | --- | 59.375 | 92.1727 | 92.948 | SDS-BCAA* | mg/L | 3.7 | --- | 29.325 | --- | 76.875 | 29.0854 | 87.2788 | SDS-BCAA* | mg/L | 2.6 | --- | 22.0203 | --- | 83.75 | 21.8624 | 88.1074 | Qp/QT (HAA5), % | 79.1696 | 81.3235 | 78.514 | 77.7778 | Qp/QT (HAA5), % | 92.0544 | 94.5588 | 91.292 | 90.436
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 16:00 | 103 | 24 | 64 | 62.5 | 272 | 4.36 | 0.44 |  | 4.8 | 0.20821 | 0.90833 | 55.6667 | 9.9515 | 10.1295 | 458.4712 | 280.1543 | 455.6129 | 1.7689 | 61.4811 | 0.16476 |  |  |  | 282 |  |  | 440.1818 |  | 4.8904 | 438.914 | 35.7505 | 0.057 |  |  | 5.1352 |  | 89.0909 | 5.0945 | 98.8811 | [8 empty] | SDS-TBAA | mg/L | 4.5 | BMRL | 4.5 | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 162.8494 | 165.9069 | 166.6995 | 155.6667 | SDS-THM4b, ug/L | 97.2209 | 100.776 | 101.6976 | 88.8692
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 16:30 | 103.5 | 24 | 64 | 62.5 | 263 | 4.43 | 4.64 |  | 9.07 | 0.20132 | 0.48842 | 27.9967 | 10.1112 | 10.2922 | 366.0777 | 223.624 | 363.6782 | 1.4125 | 61.8375 | 0.16644 |  |  |  | 261 | 298 | 392 | 330.3933 | 15.716 | 11.973 | 329.8089 | 20.8633 | 0.042 |  |  | 0.98125 |  | 91.9617 | 0.97334 | 95.685 | [8 empty] | SDS-CDBAA | mg/L | 4.8 | 3.4 | 4.1 | 34.1463 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 5.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 3.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-10 | 17:00 | 104 | 24 | 64 | 63 | 263 | 4.54 | 5.16 |  | 9.7 | 0.20132 | 0.46804 | 26.1134 | 10.3623 | 10.5477 | 362.5486 | 221.4316 | 360.1126 | 1.399 | 62.101 | 0.16985 |  |  |  | 255 |  |  | 333.0136 |  | 13.9966 | 332.3402 | 23.2714 | 0.039 |  |  | 0.94791 |  | 92.5359 | 0.94006 | 95.8513 | [8 empty] | SDS-DCBAA | mg/L | 3.2 | 2 | 2.6 | 46.1538 | --- | 32.9226 | --- | 78.3333 | 32.6471 | 92.036 | SDS-DCBAA | mg/L | 5 | --- | 68.6364 | --- | 58.3333 | 68.1273 | 92.6608 | SDS-DCBAA | mg/L | 2.1 | --- | 22.725 | --- | 82.5 | 22.5321 | 90.68 | SDS-DCBAA | mg/L | 1.6 | --- | 16.6725 | --- | 86.6667 | 16.5499 | 90.3323 | SDS-TOXb, ug Cl- /L | 330.5676 | 332.25 | 335.8486 | 327 | SDS-TOXb, ug Cl- /L | 172.7938 | 174.75 | 178.9342 | 168.6456
[44 empty] | 1998-05-10 | 17:30 | 104.5 | 24 | 64 | 63 | 263 | 4.58 | 4.75 |  | 9.33 | 0.20132 | 0.49089 | 27.1886 | 10.4536 | 10.6407 | 366.5427 | 223.8575 | 364.0579 | 1.4144 | 62.0856 | 0.17139 |  |  |  | 239 |  | 377 | 351.9421 | 6.6467 | 19.3929 | 350.9587 | 31.9008 | 0.035 |  |  | 0.99255 |  | 93.3014 | 0.98422 | 96.4439 | [8 empty] | SDS-HAA5 | mg/L | 12.3 | 8.4 | 10.35 | 37.6812 | --- | 686.3177 | --- | 95.2933 | 680.1763 | 98.4783 | SDS-HAA5 | mg/L | 15.9 | --- | 1870.4455 | --- | 92.7694 | 1855.6088 | 99.1431 | SDS-HAA5 | mg/L | 8.6 | --- | 448.8083 | --- | 96.0891 | 444.6915 | 98.0661 | SDS-HAA5 | mg/L | 6.6 | --- | 315.7304 | --- | 96.9986 | 313.217 | 97.8928 | SDS-CDb, mg/L | 5.3824 | 5.0345 | 5.5168 | 5.26 | SDS-CDb, mg/L | 3.2036 | 2.799 | 3.3599 | 3.0613
[44 empty] | 1998-05-10 | 18:00 | 105 | 24 | 64 | 63 | 263 | 4.7 | 5 |  | 9.7 | 0.20132 | 0.48454 | 26.1134 | 10.7275 | 10.9195 | 365.4495 | 223.1495 | 362.9065 | 1.4103 | 62.0897 | 0.17587 |  |  |  | 241 |  |  | 348.67 |  | 18.7184 | 347.7079 | 30.689 | 0.029 | 0.619 | 1.872 | 0.98639 | 47.3082 | 94.4498 | 0.97784 | 97.0343 | [8 empty] | SDS-HAA6 | mg/L | 16.4 | 12.1 | 14.25 | 30.1754 | --- | 729.25 | --- | 93.9593 | 722.7539 | 98.0284 | SDS-HAA6 | mg/L | 22.4 | --- | 1963.3091 | --- | 90.5045 | 1947.7815 | 98.85 | SDS-HAA6 | mg/L | 12.3 | --- | 478.1333 | --- | 94.7859 | 473.7768 | 97.4038 | SDS-HAA6 | mg/L | 9.2 | --- | 337.7507 | --- | 96.1 | 335.0794 | 97.2544 | TOCb, mg/L | 3.7121 | 3.8279 | 3.8006 | 3.6667 | TOCb, mg/L | 1.9727 | 2.1074 | 2.0756 | 1.9198
[44 empty] | 1998-05-10 | 18:30 | 105.5 | 24 | 64 | 63 | 263 | 4.75 | 5 |  | 9.75 | 0.20132 | 0.48718 | 25.9744 | 10.8416 | 11.0356 | 365.9238 | 223.4223 | 363.3501 | 1.4121 | 62.0879 | 0.17774 |  |  |  | 241 |  |  | 349.225 |  | 18.7184 | 348.2477 | 30.7964 | 0.028 |  |  | 0.99228 |  | 94.6411 | 0.98357 | 97.1532 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.12705 | 0.12849 | 0.13268 | 0.12856 | UV254 b, cm-1 | 0.062688 | 0.064362 | 0.069235 | 0.064442
[44 empty] | 1998-05-11 | 7:00 | 118 | 24 | 64 | 62.5 | 263 | 4.75 | 3.5 |  | 8.25 | 0.20132 | 0.57576 | 30.8788 | 10.8416 | 11.0356 | 382.1945 | 233.3567 | 379.5063 | 1.4749 | 61.7751 | 0.17864 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 124.1661 | 123.7353 | 124.2972 | 124.4444 | Bromideb, ug/L | 121.5891 | 121.0882 | 121.7416 | 121.9128
[44 empty] | 1998-05-11 | 7:30 | 118.5 | 24 | 64 | 62.5 | 263 | 4.7 | 5 |  | 9.7 | 0.20132 | 0.48454 | 26.1134 | 10.7275 | 10.9195 | 365.4495 | 223.1495 | 362.9065 | 1.4103 | 61.8397 | 0.17658 | [66 empty] | Alkb, mg/L CaCO3 | 179.5204 | 188.5603 | 185.504 | 166.8889 | Alkb, mg/L CaCO3 | 177.6521 | 188.1632 | 184.6096 | 162.9648
[44 empty] | 1998-05-11 | 8:30 | 119.5 | 24 | 64 | 62.5 | 263 | 5.22 | 4.93 |  | 10.15 | 0.20132 | 0.51429 | 24.9113 | 11.9144 | 12.1276 | 370.8571 | 226.2738 | 367.9875 | 1.4315 | 61.8185 | 0.19618 | [66 empty] | T-Hdb, mg/L CaCO3 | 195 | 195.8132 | 186.3635 | 170.1111 | T-Hdb, mg/L CaCO3 | 195 | 195.9456 | 184.9579 | 166.0605
[44 empty] | 1998-05-11 | 9:30 | 120.5 | 23 | 64 | 62 | 281 | 4.48 | 11 |  | 15.48 | 0.2151 | 0.28941 | 17.1525 | 10.2254 | 10.7206 | 334.1052 | 204.1659 | 332.0335 | 1.289 | 61.711 | 0.17372 | [66 empty] | Ca-Hdb, mg/L CaCO3 | 172.4796 | 178.0779 | 155.504 | 147.7778 | Ca-Hdb, mg/L CaCO3 | 174.3479 | 180.8574 | 154.6096 | 145.6259
[44 empty] | 1998-05-11 | 9:40 | 120.6667 | 23 | 64 | 62 | 281 | 4.47 | 11.1 |  | 15.57 | 0.2151 | 0.28709 | 17.0475 | 10.2025 | 10.6966 | 333.7656 | 203.9613 | 331.7007 | 1.2877 | 61.7123 | 0.17333 | 7.93 |  | 8.01 | 233 |  | 333 | 322.0716 | 3.2818 | 21.4165 | 321.3632 | 27.4964 | 0.019 |  | 1.036 | 0.72526 | 29.9941 | 96.3636 | 0.71964 | 97.3598 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-05-11 | 10:40 | 121.6667 | 23 | 64 | 62 | 281 | 4.48 | 11.5 |  | 15.98 | 0.2151 | 0.28035 | 16.5845 | 10.2254 | 10.7206 | 332.7845 | 203.3589 | 330.7211 | 1.2839 | 61.7161 | 0.17371 | 7.93 |  |  | 222 |  |  | 325.5226 |  | 25.1265 | 324.6974 | 31.6286 | 0.015 |  |  | 0.7202 |  | 97.1292 | 0.71458 | 97.9009 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-05-11 | 11:15 | 122.25 | 23 | 64 | 62 | 281 | 4.49 | 10.44 |  | 14.93 | 0.2151 | 0.30074 | 17.8212 | 10.2482 | 10.7445 | 335.7735 | 205.1825 | 333.6869 | 1.2955 | 61.7045 | 0.17413 |  |  |  | 221 |  |  | 328.9708 |  | 25.4637 | 328.1082 | 32.6442 | 0.014 |  |  | 0.74119 |  | 97.3206 | 0.73538 | 98.0962 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-05-11 | 12:00 | 123 | 23 | 64 | 62.5 | 281 | 4.46 | 10.36 |  | 14.82 | 0.2151 | 0.30094 | 17.9609 | 10.1797 | 10.6727 | 335.8013 | 205.2082 | 333.7286 | 1.2956 | 61.9544 | 0.17227 |  | 7.85 |  | 222 | 289 |  | 328.5724 |  | 25.1265 | 327.7266 | 32.2606 | 0.015 | 0.609 |  | 0.74098 |  | 97.1292 | 0.73522 | 97.9598 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-05-11 | 13:30 | 124.5 | 23 | 64 | 62.5 | 281 | 4.49 | 10.25 |  | 14.74 | 0.2151 | 0.30461 | 18.0638 | 10.2482 | 10.7445 | 336.3478 | 205.5334 | 334.2576 | 1.2977 | 61.9523 | 0.17343 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-05-11 | 14:30 | 125.5 | 23 | 64 | 62.5 | 281 | 4.5 | 10.22 |  | 14.72 | 0.2151 | 0.30571 | 18.0897 | 10.271 | 10.7684 | 336.5111 | 205.6303 | 334.4151 | 1.2983 | 61.9517 | 0.17382 | 7.99 | 8.02 | 8.04 | 222 | 288 | 322 | 329.3033 | -2.2681 | 25.1265 | 328.4441 | 32.4086 | 0.014 | 0.597 | 0.853 | 0.7464 | 12.4972 | 97.3206 | 0.74053 | 98.1095 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-05-11 | 15:00 | 126 | 23 | 64 | 62.5 | 281 | 4.5 | 10.23 |  | 14.73 | 0.2151 | 0.3055 | 18.0767 | 10.271 | 10.7684 | 336.4803 | 205.6115 | 334.3845 | 1.2982 | 61.9518 | 0.17382 | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-05-12 | 9:00 | 144 | 23 | 65.5 | 64.5 | 281 | 4.49 | 10.25 | X | 14.74 | 0.2151 | 0.30461 | 18.0638 | 10.2482 | 10.7445 | 336.3478 | 205.5334 | 334.2576 | 1.2977 | 63.7023 | 0.16867 | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-05-12 | 10:00 |  | 23 | 75.5 | 75 | 281 | 9.28 | 0.6 |  | 9.88 | 0.2151 | 0.93927 | 27.4413 | 21.1811 | 22.2069 | 470.0494 | 285.2791 | 463.9474 | 1.8172 | 73.4328 | 0.30241 | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-05-12 | 10:15 |  | 23 | 74.5 | 74 | 281 | 8.88 | 2.78 |  | 11.66 | 0.2151 | 0.76158 | 23.0995 | 20.2681 | 21.2497 | 423.027 | 256.8891 | 417.7768 | 1.6351 | 72.6149 | 0.29264 | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-05-12 | 10:30 |  | 23 | 65.5 | 64 | 281 | 7.6 | 1.52 |  | 9.12 | 0.2151 | 0.83333 | 29.8114 | 17.3466 | 18.1867 | 440.1381 | 267.7724 | 435.4763 | 1.7003 | 63.0497 | 0.28845 | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-05-12 | 11:00 |  | 23 | 55 | 54 | 281 | 6.32 | 0.93 |  | 7.25 | 0.2151 | 0.87172 | 37.7586 | 14.4251 | 15.1237 | 449.5236 | 273.9823 | 445.5754 | 1.7357 | 52.7643 | 0.28663 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-05-13 | 9:00 |  | 23 | 54.5 | 54 | 281 | 5.8 | 1.1 |  | 6.9 | 0.2151 | 0.84058 | 39.7246 | 13.2382 | 13.8793 | 441.1365 | 269.0689 | 437.5849 | 1.7029 | 52.5471 | 0.26413
[44 empty] | 1998-05-13 | 9:30 |  | 23 | 64 | 63.5 | 281 | 6.48 | 2.07 |  | 8.55 | 0.2151 | 0.75789 | 31.8655 | 14.7903 | 15.5065 | 421.2048 | 256.6637 | 417.4104 | 1.6264 | 62.1236 | 0.24961
[44 empty] | 1998-05-13 | 10:00 |  | 23 | 74 | 73.5 | 281 | 7.68 | 2.57 |  | 10.25 | 0.2151 | 0.74927 | 26.4146 | 17.5292 | 18.3781 | 419.6618 | 255.2857 | 415.1693 | 1.6213 | 72.1287 | 0.2548
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: C. Hill (7/30/99): NF200 was used during quarters 1, 2 and 3. NTR7450 was used during a second 3rd quarter and quarter 4.
Note on Q3: C. Rice 7/13/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Gary Puetz: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X11: Alison Gusses: Feed alkalinity verified by consultant
Note on X12: Alison Gusses: TDS verified by consultant
Note on X13: Alison Gusses: Total hardness verified by consultant
Note on X14: Alison Gusses: Calcium Hardness verified by consultant
Note on X20: Alison Gusses: All bromide data verified by consultant
Note on BV7: Alison Gusses: Consultant verified MTCw values but did not explain why the values were higher during the 2nd Quarter, compared to the 1st Quarter
Note on CY3: Alison Gusses: No explanation was given as to why the permeate TOC, UV, TOX and THM4 concentrations were all lower during Quarter 1, relative to Quarter 2.
Note on DB25: Alison Gusses: All bromide data verified by consultant
Note on DG10: Alison Gusses: Consultant verified alkalinity, TDS, total hardness and calcium hardness concentrations due to their consistently high mass balance errors
Note on DL3: Alison Gusses: No explanation was given as to why the permeate TOC, UV, TOX and THM4 concentrations were all lower during Quarter 1, relative to Quarter 2.
Note on DN25: C. Rice 7/13/99: Consultant verified value.
Note on DQ10: Alison Gusses: Consultant verified alkalinity, TDS, total hardness and calcium hardness concentrations due to their consistently high mass balance errors
Note on DV3: Alison Gusses: No explanation was given as to why the permeate TOC, UV, TOX and THM4 concentrations were all lower during Quarter 1, relative to Quarter 2.
Note on DX25: C. Rice 7/13/99: Consultant verified value.
Note on EA10: Alison Gusses: Consultant verified alkalinity, TDS, total hardness and calcium hardness concentrations due to their consistently high mass balance errors
Note on EF3: Alison Gusses: No explanation was given as to why the permeate TOC, UV, TOX and THM4 concentrations were all lower during Quarter 1, relative to Quarter 2.
Note on EH25: C. Rice 7/13/99: Consultant verified value.
Note on EK10: Alison Gusses: Consultant verified alkalinity, TDS, total hardness and calcium hardness concentrations due to their consistently high mass balance errors

## NF200. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.39367 | [45 empty] | Recovery during sample collection (decimal) | 0.67 | [10 empty] | Recovery during sample collection (decimal) | 0.91 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 11.01 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.79 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.66 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:00 | 8:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 321 | [10 empty] | Influent flow rate during sample collection (mL/min) | 321 | [7 empty] | Influent flow rate during sample collection (mL/min) | 321 | [7 empty] | Influent flow rate during sample collection (mL/min) | 321 | [6 empty] | SDS-THM4F, ug/L | 538.9 | 538.9 | 538.9 | 538.9 | SDS-THM4F, ug/L | 538.9 | 538.9 | 538.9 | 538.9 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 50.5 | 117.6 | 77 | 68 | SDS-THM4p, ug/L | 50.5 | 117.6 | 77 | 68 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.54 | 8.16 | 7.85 | 7.8981 | 1998-07-15 | 8:30 | 0 | 24 | [5 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-16 | 8:30 | 0 | 24 | 60 | 58 | 302 | 7.82 | 3.93 |  | 11.75 | 0.23118 | 0.66553 | 24.7021 | 17.8487 | 18.1681 | 431.9873 | 259.2123 | 427.5134 | 1.7054 | 57.2946 | 0.3171 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 244.9 | 244.9 | 244.9 | 244.9 | SDS-HAA5F, ug/L | 244.9 | 244.9 | 244.9 | 244.9 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.28066 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-07-15 | 9:15 | 0.75 | 24 | 60 | 59 | 302 | 8.33 | 2.63 | 10.96 | 0.23118 | 0.76004 | 26.5547 | 19.0128 | 19.353 | 0 | 0 | 0 | 0 | 59.5 | 0.32526 | 1998-07-16 | 9:30 | 1 | 24 | 60 | 58 | 302 | 7.82 | 3.93 |  | 11.75 | 0.23118 | 0.66553 | 24.7021 | 17.8487 | 18.1681 | 431.9873 | 259.2123 | 427.5134 | 1.7054 | 57.2946 | 0.3171 | 7.81 | 7.65 | 7.72 | 158 | 316 | 253 | 633.3817 | -150.3485 | 50.1577 | 627.2269 | 74.8098 | BMRL | 0.661 | 0.536 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 7.7 | 24.2 | 17.6 | 11.6 | SDS-HAA5p, ug/L | 7.7 | 24.2 | 17.6 | 11.6 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | highly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 206 | 203 | 204.5 | 1.467 | 1998-07-15 | 10:00 | 1.5 | 24 | 60 | 59 | 302 | 8.9 | 3.4 | 12.3 | 0.23118 | 0.72358 | 23.5528 | 20.3138 | 20.6773 | 0 | 0 | 0 | 0 | 59.5 | 0.34752 | 1998-07-16 | 10:30 | 2 | 24 | 60 | 58 | 302 | 7.8 | 3.86 |  | 11.66 | 0.23118 | 0.66895 | 24.9005 | 17.8031 | 18.1216 | 432.788 | 259.6998 | 428.3175 | 1.7085 | 57.2915 | 0.31631 | 7.68 | 7.63 | 7.83 | 233 | 317 | 391 | 486.7409 | -24.4862 | 26.4984 | 483.4641 | 51.8061 | 0.013 | 0.661 | 1.174 | 1.8919 | -61.1492 | 97.9528 | 1.8676 | 99.3039 | [8 empty] | Sampling date | MM/DD/YY | 1998-07-17 | 1998-07-18 | --- | --- | 1998-07-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-19 | 1998-07-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-20 | 1998-07-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-21 | 1998-07-21 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1435 | 1435 | 1435 | 1435 | SDS-TOXF, ug Cl- /L | 1435 | 1435 | 1435 | 1435 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 319 | 315 | 317 | 1.2618 | 1998-07-15 | 10:45 | 2.25 | 24 | 60 | 59 | 302 | 8.9 | 3.5 | 12.4 | 0.23118 | 0.71774 | 23.3548 | 20.3138 | 20.6773 | 0 | 0 | 0 | 0 | 59.5 | 0.34752 | 1998-07-16 | 11:30 | 3 | 24 | 60 | 58 | 302 | 7.72 | 4.09 |  | 11.81 | 0.23118 | 0.65368 | 24.5715 | 17.6205 | 17.9358 | 429.1845 | 257.5655 | 424.7974 | 1.6943 | 57.3057 | 0.31298 | 7.68 | 7.65 | 7.75 | 243 | 316 | 411 | 456.6773 | -11.1137 | 23.3438 | 453.9462 | 46.4694 | 0.015 | 0.66 | 1.413 | 1.8053 | -27.7614 | 97.6378 | 1.7824 | 99.1584 | [8 empty] | Sampling time | hh:mm | 8:30 | 9:30 | --- | --- | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:45 | 19:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 67.5 | 235 | 115 | 88 | SDS-TOXp, ug Cl- /L | 67.5 | 235 | 115 | 88 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 308 | 290 | 299 | 6.0201 | 1998-07-15 | 11:15 | 2.75 | 24 | 46 | 44 | 302 | 6.55 | 2.75 | 9.3 | 0.23118 | 0.7043 | 31.4731 | 14.95 | 15.2175 | 0 | 0 | 0 | 0 | 45 | 0.33817 | 1998-07-16 | 12:00 | 3.5 | 24 | 60 | 58 | 302 | 7.72 | 3.64 |  | 11.36 | 0.23118 | 0.67958 | 25.5845 | 17.6205 | 17.9358 | 435.2866 | 261.2276 | 430.8372 | 1.7183 | 57.2817 | 0.31312 | [27 empty] | Operation time | hh.hh | 24 | 49 | --- | --- | 24 | --- | --- | --- | --- | --- | Operation time | hh.hh | 83.25 | 83.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 104 | 104 | --- | --- | --- | --- | --- | Cumulative time | hr | 123.5 | 123.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 16.52 | 16.52 | 16.52 | 16.52 | SDS-CDF, mg/L | 16.52 | 16.52 | 16.52 | 16.52 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 252 | 260 | 256 | 3.125 | 1998-07-15 | 11:30 | 3 | 24 | 75 | 74 | 302 | 11.33 | 3.11 | 14.44 | 0.23118 | 0.78463 | 19.9141 | 25.8601 | 26.3228 | 0 | 0 | 0 | 0 | 74.5 | 0.35333 | 1998-07-16 | 13:30 | 5 | 24 | 60 | 58 | 302 | 7.63 | 3.79 |  | 11.42 | 0.23118 | 0.66813 | 25.4448 | 17.4151 | 17.7267 | 432.5378 | 259.6097 | 428.1688 | 1.7074 | 57.2926 | 0.30941 | 7.8 | 7.68 | 7.78 | 248 | 314 | 411 | 455.9103 | -10.9271 | 21.7666 | 453.2839 | 45.2881 | 0.026 | 0.661 | 1.525 | 1.861 | -22.035 | 95.9055 | 1.8379 | 98.5853 | [8 empty] | pH | --- | 7.45 | 7.91 | 7.68 | 5.9896 | 8.35 | --- | --- | --- | --- | --- | pH | --- | 7.49 | 8.46 | --- | --- | --- | --- | --- | pH | --- | 7.98 | 8.34 | --- | --- | --- | --- | --- | pH | --- | 8.32 | 8.32 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.105 | 2.41 | 1.43 | 1.28 | SDS-CDp, mg/L | 1.105 | 2.41 | 1.43 | 1.28 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 15 | 6.5 | 59.9451 | 283.3154 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 1.111 | 1.4 | 1.2555 | 23.0187 | 1998-07-15 | 11:55 | 3.4167 | 24 | 60 | 59 | 302 | 9.15 | 2.85 | 12 | 0.23118 | 0.7625 | 24.1667 | 20.8844 | 21.2581 | 0 | 0 | 0 | 0 | 59.5 | 0.35728 | 1998-07-16 | 14:30 | 6 | 24 | 60 | 58 | 302 | 7.8 | 3.68 |  | 11.48 | 0.23118 | 0.67944 | 25.3066 | 17.8031 | 18.1216 | 435.2809 | 261.1957 | 430.7846 | 1.7184 | 57.2816 | 0.31636 | 7.65 | 7.6 | 7.8 | 250 | 314 | 413 | 459.0109 | -11.1406 | 21.1356 | 456.3117 | 45.2129 | 0.018 | 0.661 | 1.535 | 1.9428 | -26.5649 | 97.1654 | 1.9179 | 99.0615 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 13.3 | 13.3 | 13.3 | 13.3 | TOCF, mg/L | 13.3 | 13.3 | 13.3 | 13.3 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 15 | 16.5 | 69.9451 | 283.3154 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.47 | 0.14 | 0.305 | 108.1967 | 1998-07-15 | 13:30 | 5 | 24 | 60 | 59 | 302 | 9.25 | 3.6 | 12.85 | 0.23118 | 0.71984 | 22.5019 | 21.1126 | 21.4904 | 0 | 0 | 0 | 0 | 59.5 | 0.36118 | 1998-07-16 | 15:30 | 7 | 24 | 60 | 58 | 302 | 7.6 | 3.73 |  | 11.33 | 0.23118 | 0.67079 | 25.6549 | 17.3466 | 17.657 | 433.1565 | 259.9916 | 428.7987 | 1.7099 | 57.2901 | 0.3082 | 7.71 | 7.62 | 7.89 | 248 | 310 | 418 | 457.5898 | -9.4712 | 21.7666 | 454.9526 | 45.4888 | 0.022 | 0.66 | 1.601 | 1.884 | -17.677 | 96.5354 | 1.8606 | 98.8176 | [8 empty] | Alkalinity | mg/L as CaCO3 | 113 | 115 | 114 | 1.7544 | 185 | 388.2424 | -109.8608 | 44.2543 | 385.0913 | 70.3966 | Alkalinity | mg/L as CaCO3 | 132 | 199 | 937.5556 | -371.1334 | 35.4523 | 929.8025 | 85.8034 | Alkalinity | mg/L as CaCO3 | 118 | 161 | 291 | -80.7453 | 42.2983 | 289.3967 | 59.2255 | Alkalinity | mg/L as CaCO3 | 114 | 151 | 243.2857 | -61.1164 | 44.2543 | 242.098 | 52.9116 | TOCp, mg/L | 1.05 | 2.8 | 1.6 | 1.2 | TOCp, mg/L | 1.05 | 2.8 | 1.6 | 1.2 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 57.9451 | 283.3154 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 13.8 | 12.8 | 13.3 | 7.5188 | 1998-07-15 | 15:00 | 6.5 | 24 | 60 | 59 | 302 | 9.27 | 2.76 | 12.03 | 0.23118 | 0.77057 | 24.1039 | 21.1583 | 21.5369 | 0 | 0 | 0 | 0 | 59.5 | 0.36196 | 1998-07-16 | 16:30 | 8 | 24 | 60 | 58 | 302 | 7.8 | 3.75 |  | 11.55 | 0.23118 | 0.67532 | 25.1472 | 17.8031 | 18.1216 | 434.2988 | 260.6064 | 429.8127 | 1.7145 | 57.2855 | 0.31634 | 7.68 | 7.58 | 7.9 | 248 | 311 | 411 | 460.52 | -12.0487 | 21.7666 | 457.7755 | 45.825 | 0.018 | 0.661 | 1.573 | 1.9184 | -21.9555 | 97.1654 | 1.8938 | 99.0495 | [8 empty] | Total dissolved solids | mg/L | 252 | 263 | 257.5 | 4.2718 | 381 | 437.803 | -14.9089 | 18.7697 | 435.7313 | 40.9039 | Total dissolved solids | mg/L | 288 | 422 | 610.2222 | -44.6024 | 9.1483 | 607.121 | 52.563 | Total dissolved solids | mg/L | 260 | 338 | 374 | -10.6509 | 17.9811 | 372.9435 | 30.2843 | Total dissolved solids | mg/L | 250 | 332 | 345.7143 | -4.1308 | 21.1356 | 344.835 | 27.5016 | UV254 F, cm-1 | 0.635 | 0.635 | 0.635 | 0.635 | UV254 F, cm-1 | 0.635 | 0.635 | 0.635 | 0.635 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 3.6429 | 57.0879 | 283.3154 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.665 | 0.605 | 0.635 | 9.4488 | 1998-07-15 | 15:30 | 7 | 24 | 60 | 59 | 302 | 9.6 | 3.89 | 13.49 | 0.23118 | 0.71164 | 21.387 | 21.9115 | 22.3036 | 0 | 0 | 0 | 0 | 59.5 | 0.37485 | 1998-07-17 | 8:30 | 24 | 24 | 60 | 58 | 302 | 7.42 | 3.83 |  | 11.25 | 0.23118 | 0.65956 | 25.8444 | 16.9358 | 17.2388 | 430.459 | 258.4356 | 426.2324 | 1.6991 | 57.3009 | 0.30085 | [27 empty] | Total hardness | mg/L as CaCO3 | 200 | 208 | 204 | 3.9216 | 349 | 491.8788 | -40.9395 | 31.7726 | 488.571 | 58.2456 | Total hardness | mg/L as CaCO3 | 230 | 430 | 996.6667 | -131.7829 | 23.0769 | 989.2879 | 76.751 | Total hardness | mg/L as CaCO3 | 208 | 310 | 390 | -25.8065 | 30.4348 | 388.3132 | 46.435 | Total hardness | mg/L as CaCO3 | 186 | 314 | 347.4286 | -10.646 | 37.7926 | 345.9455 | 46.2343 | UV254 p, cm-1 | 0.0235 | 0.106 | 0.051 | 0.042 | UV254 p, cm-1 | 0.0235 | 0.106 | 0.051 | 0.042 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.8188 | 4.7266 | 4.7727 | 1.9335 | 1998-07-15 | 16:30 | 8 | 24 | 60 | 59 | 302 | 9.47 | 3.6 | 13.07 | 0.23118 | 0.72456 | 22.1064 | 21.6148 | 22.0015 | 0 | 0 | 0 | 0 | 59.5 | 0.36977 | 1998-07-17 | 9:30 | 25 | 24 | 60 | 58 | 302 | 7.44 | 3.53 |  | 10.97 | 0.23118 | 0.67821 | 26.5296 | 16.9814 | 17.2853 | 434.8685 | 261.0758 | 430.587 | 1.7165 | 57.2835 | 0.30175 | 7.73 | 7.64 | 7.84 | 259 | 312 | 397 | 439.2436 | -10.6407 | 18.2965 | 437.0234 | 40.7354 | 0.018 | 0.663 | 1.716 | 1.9354 | -12.7867 | 97.1654 | 1.9118 | 99.0585 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 184 | 198 | 191 | 7.3298 | 329 | 387.9697 | -17.9239 | 25.3906 | 385.7065 | 50.4805 | Calcium hardness | mg/L as CaCO3 | 216 | 406 | 660.4444 | -62.671 | 15.625 | 656.1669 | 67.0815 | Calcium hardness | mg/L as CaCO3 | 196 | 302 | 316 | -4.6358 | 23.4375 | 314.8879 | 37.7556 | Calcium hardness | mg/L as CaCO3 | 172 | 282 | 292 | -3.5461 | 32.8125 | 290.8976 | 40.8727 | BromideF, ug/L | 150 | 150 | 150 | 150 | BromideF, ug/L | 150 | 150 | 150 | 150 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 150 | 150 | 150 | 0 | 1998-07-16 | 8:15 | 23.75 | 24 | 60 | 59 | 302 | 8.95 | 3.9 | 12.85 | 0.23118 | 0.6965 | 22.5019 | 20.4279 | 20.7934 | 0 | 0 | 0 | 0 | 59.5 | 0.34947 | 1998-07-17 | 10:30 | 26 | 24 | 60 | 58 | 302 | 7.4 | 3.6 |  | 11 | 0.23118 | 0.67273 | 26.4545 | 16.8901 | 17.1923 | 433.5515 | 260.2993 | 429.3062 | 1.7113 | 57.2887 | 0.3001 | 7.73 | 7.61 | 7.84 | 261 | 318 | 712 | 432.1111 | 39.3102 | 17.6656 | 430.0147 | 39.3044 | 0.018 | 0.662 | 1.674 | 1.9033 | -13.6964 | 97.1654 | 1.8802 | 99.0426 | [8 empty] | Turbidity | ntu | 0.084 | 0.088 | 0.086 | 4.6512 | 0.64 | 3.6299 | -467.178 | 93.1501 | 3.5892 | 97.6039 | Turbidity | ntu | 0.076 | 1.83 | 13.1816 | -620.3036 | 93.9466 | 13.0554 | 99.4179 | Turbidity | ntu | 0.07 | 1.71 | 2.441 | -42.7485 | 94.4245 | 2.419 | 97.1063 | Turbidity | ntu | 0.109 | 1.51 | 1.7469 | -15.6859 | 91.3182 | 1.7318 | 93.706 | Bromidep, ug/L | 150 | 150 | 150 | 140 | Bromidep, ug/L | 150 | 150 | 150 | 140 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 18 | 18 | 18 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 11:30 | 27 | 24 | 60 | 58 | 302 | 7.2 | 3.71 |  | 10.91 | 0.23118 | 0.65995 | 26.681 | 16.4336 | 16.7277 | 430.4809 | 258.5258 | 426.3813 | 1.6991 | 57.3009 | 0.29193 | 7.82 | 7.7 | 7.85 | 257 | 316 | 394 | 433.442 | -10.0107 | 18.9274 | 431.3388 | 40.4181 | 0.019 | 0.646 | 1.643 | 1.8305 | -11.4103 | 97.0079 | 1.8089 | 98.9496 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 204.5 | 204.5 | 204.5 | 204.5 | AlkF, mg/L CaCO3 | 204.5 | 204.5 | 204.5 | 204.5
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.5467 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.16 | 1.8 | 1.48 | 43.2432 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 13:00 | 28.5 | 24 | 60 | 58 | 302 | 7.32 | 3.6 |  | 10.92 | 0.23118 | 0.67033 | 26.6557 | 16.7075 | 17.0065 | 432.9583 | 259.9713 | 428.7653 | 1.7089 | 57.2911 | 0.29684 | 7.78 | 7.65 | 7.86 | 255 | 312 | 405 | 443.0667 | -9.3992 | 19.5584 | 440.7874 | 42.149 | 0.02 | 0.658 | 1.616 | 1.8855 | -16.677 | 96.8504 | 1.8629 | 98.9264 | [8 empty] | Total organic carbon | mg/L | 1 | 1.1 | 1.05 | 9.5238 | 41.3 | 38.1712 | 7.5758 | 92.1053 | 37.7447 | 97.2182 | Total organic carbon | mg/L | 2.8 | 116.6 | 119.4667 | -2.4585 | 78.9474 | 118.3438 | 97.634 | Total organic carbon | mg/L | 1.6 | 27 | 25 | 7.4074 | 87.9699 | 24.7831 | 93.544 | Total organic carbon | mg/L | 1.2 | 18.1 | 18.4857 | -2.131 | 90.9774 | 18.3269 | 93.4523 | Alkp, mg/L CaCO3 | 114 | 132 | 118 | 114 | Alkp, mg/L CaCO3 | 114 | 132 | 118 | 114
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.00233 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 16.84 | 16.2 | 16.52 | 3.8741 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 14:00 | 29.5 | 24 | 60 | 58 | 302 | 7.29 | 3.57 |  | 10.86 | 0.23118 | 0.67127 | 26.8085 | 16.639 | 16.9368 | 433.171 | 260.1097 | 428.9935 | 1.7097 | 57.2903 | 0.29563 | 7.79 | 7.68 | 7.84 | 263 | 314 | 406 | 427.2689 | -5.2386 | 17.0347 | 425.2863 | 38.1593 | 0.021 | 0.66 | 1.589 | 1.8888 | -18.8671 | 96.6929 | 1.8663 | 98.8748 | [8 empty] | UV254 | cm-1 | 0.019 | 0.028 | 0.0235 | 38.2979 | 1.52 | 1.8765 | -23.4559 | 96.2992 | 1.8552 | 98.7333 | UV254 | cm-1 | 0.106 | 4.1 | 5.9838 | -45.9458 | 83.3071 | 5.9272 | 98.2116 | UV254 | cm-1 | 0.051 | 1.172 | 1.219 | -4.0102 | 91.9685 | 1.2082 | 95.7788 | UV254 | cm-1 | 0.042 | 0.837 | 0.88914 | -6.2297 | 93.3858 | 0.88136 | 95.2346 | T-HdF, mg/L CaCO3 | 299 | 299 | 299 | 299 | T-HdF, mg/L CaCO3 | 299 | 299 | 299 | 299
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 15:00 | 30.5 | 24 | 60 | 58 | 302 | 7.56 | 3.7 |  | 11.26 | 0.23118 | 0.6714 | 25.8206 | 17.2553 | 17.5641 | 433.2898 | 260.0857 | 428.9539 | 1.7104 | 57.2896 | 0.30658 | 7.89 | 7.68 | 7.9 | 259 | 314 | 397 | 435.5081 | -9.6998 | 18.2965 | 433.2988 | 40.226 | 0.022 | 0.659 | 1.573 | 1.8875 | -19.9942 | 96.5354 | 1.8642 | 98.8198 | [8 empty] | SUVA | L/(mg*m) | 1.9 | 2.5455 | 2.2227 | 29.0389 | 3.6804 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.7857 | 3.5163 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.1875 | 4.3407 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.5 | 4.6243 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 204 | 230 | 208 | 186 | T-Hdp, mg/L CaCO3 | 204 | 230 | 208 | 186
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.91 | 9.14 | 9.025 | 2.5485 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 16:00 | 31.5 | 24 | 60 | 58 | 302 | 7.23 | 3.7 |  | 10.93 | 0.23118 | 0.66148 | 26.6304 | 16.5021 | 16.7974 | 430.8496 | 258.7367 | 426.7291 | 1.7005 | 57.2995 | 0.29315 | 7.75 | 7.58 | 7.82 | 260 | 315 | 397 | 428.3811 | -7.9046 | 17.9811 | 426.3655 | 39.0195 | 0.02 | 0.66 | 1.601 | 1.8367 | -14.7247 | 96.8504 | 1.815 | 98.8981 | [8 empty] | Bromide | mg/L | 150 | 150 | 150 | 0 | --- | 150 | --- | 0 | 150 | 0 | Bromide | mg/L | 150 | --- | 150 | --- | 0 | 150 | 0 | Bromide | mg/L | 150 | --- | 150 | --- | 0 | 150 | 0 | Bromide | mg/L | 140 | --- | 154.2857 | --- | 6.6667 | 154.1545 | 9.182 | Ca-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256 | Ca-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 9:30 | 49 | 24 | 60 | 58 | 302 | 7.17 | 3.38 |  | 10.55 | 0.23118 | 0.67962 | 27.6256 | 16.3651 | 16.658 | 435.1151 | 261.3195 | 430.9889 | 1.7173 | 57.2827 | 0.2908 | [27 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 191 | 216 | 196 | 172 | Ca-Hdp, mg/L CaCO3 | 191 | 216 | 196 | 172
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 1440 | 1430 | 1435 | 0.69686 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 10:30 | 50 | 24 | 60 | 58 | 302 | 7.2 | 3.38 |  | 10.58 | 0.23118 | 0.68053 | 27.5444 | 16.4336 | 16.7277 | 435.3418 | 261.4451 | 431.1959 | 1.7182 | 57.2818 | 0.29202 | 7.69 | 7.57 | 7.79 | 264 | 311 | 391 | 429.8994 | -9.9487 | 16.7192 | 427.9218 | 38.3065 | 0.029 | 0.662 | 1.728 | 1.9259 | -11.4518 | 95.4331 | 1.9033 | 98.4763 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.38 | 1.41 | 1.395 | 2.1505 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.59 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.07 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.22 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 19 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 480 | 480 | 480 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 11:30 | 51 | 24 | 60 | 58 | 302 | 7.23 | 3.28 |  | 10.51 | 0.23118 | 0.68792 | 27.7345 | 16.5021 | 16.7974 | 437.1232 | 262.5043 | 432.9428 | 1.7253 | 57.2747 | 0.29328 | 7.83 | 7.8 | 7.82 | 262 | 312 | 396 | 438.2348 | -10.6653 | 17.3502 | 436.1252 | 39.9255 | 0.029 | 0.66 | 1.66 | 1.9708 | -18.7221 | 95.4331 | 1.9475 | 98.5109 | [8 empty] | SDS-Cl2 demand | mg/L | 1.12 | 1.09 | 1.105 | 2.7149 | --- | 47.8171 | --- | 93.3111 | 47.2804 | 97.6629 | SDS-Cl2 demand | mg/L | 2.41 | --- | 159.1878 | --- | 85.4116 | 157.6789 | 98.4716 | SDS-Cl2 demand | mg/L | 1.43 | --- | 31.61 | --- | 91.3438 | 31.3303 | 95.4357 | SDS-Cl2 demand | mg/L | 1.28 | --- | 23.0514 | --- | 92.2518 | 22.8514 | 94.3986 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | minus 10%, plus 25% | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 59 | 48 | 53.5 | 20.5607 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 12:30 | 52 | 24 | 59 | 58 | 302 | 6.97 | 3.31 |  | 10.28 | 0.23118 | 0.67802 | 28.3774 | 15.9087 | 16.1933 | 434.6667 | 261.121 | 430.6614 | 1.7154 | 56.7846 | 0.28517 | 7.77 | 7.58 | 7.89 | 266 | 312 | 393 | 424.3927 | -7.988 | 16.0883 | 422.5649 | 37.0511 | 0.032 | 0.658 | 1.646 | 1.9048 | -15.7206 | 94.9606 | 1.8832 | 98.3007 | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 95.5979 | 110.8236 | 101.0825 | 99.1506 | Qp/QT (THM4), % | 102.9689 | 119.3686 | 108.8764 | 106.7955
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | >99% 2000 ppm MgSO4 @ 67 psi | [13 empty] | SDS-DBCM | mg/L | 5.4 | 5.4 | 5.4 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 13:30 | 53 | 24 | 60 | 58 | 302 | 6.93 | 3.24 |  | 10.17 | 0.23118 | 0.68142 | 28.6952 | 15.8174 | 16.1004 | 435.4641 | 261.6142 | 431.4748 | 1.7186 | 57.2814 | 0.28107 | 7.78 | 7.65 | 7.91 | 266 | 313 | 385 | 426.0833 | -10.671 | 16.0883 | 424.2466 | 37.3006 | 0.029 | 0.66 | 0.1645 | 1.9312 | -1073.9615 | 95.4331 | 1.9093 | 98.4812 | [8 empty] | SDS-Chlorination pH | --- | 9.09 | 9.3 | 9.195 | 2.2838 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.08 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.15 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.27 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | NA | NA | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NDP or< 50% 500 ppm CaCl2 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 14:30 | 54 | 24 | 60 | 58 | 302 | 6.87 | 3.34 |  | 10.21 | 0.23118 | 0.67287 | 28.5788 | 15.6804 | 15.961 | 433.4132 | 260.4032 | 429.4775 | 1.7104 | 57.2896 | 0.2786 | 7.77 | 7.59 | 7.88 | 262 | 311 | 392 | 430.1287 | -9.7267 | 17.3502 | 428.2164 | 38.816 | 0.03 | 0.66 | 1.632 | 1.8794 | -15.1603 | 95.2756 | 1.8584 | 98.3857 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 18.1419 | NA | NA | 13.5817 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | unknown | [13 empty] | SDS-THM4 | mg/L | 544.4 | 533.4 | 538.9 | 2.0412 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 15:30 | 55 | 24 | 60 | 58 | 302 | 6.91 | 3.31 |  | 10.22 | 0.23118 | 0.67613 | 28.5499 | 15.7717 | 16.0539 | 434.1977 | 260.8604 | 430.2317 | 1.7135 | 57.2865 | 0.28024 | 7.79 | 7.6 | 7.89 | 264 | 311 | 390 | 427.6435 | -9.6522 | 16.7192 | 425.7714 | 37.9949 | 0.029 | 0.661 | 1.641 | 1.9001 | -15.7888 | 95.4331 | 1.8787 | 98.4564 | [8 empty] | SDS-TOX | mg Cl- /L | 63 | 72 | 67.5 | 13.3333 | --- | 4211.4394 | --- | 95.2962 | 4163.8248 | 98.3789 | SDS-TOX | mg Cl- /L | 235 | --- | 13568.3333 | --- | 83.6237 | 13440.0073 | 98.2515 | SDS-TOX | mg Cl- /L | 115 | --- | 2755 | --- | 91.9861 | 2730.5327 | 95.7884 | SDS-TOX | mg Cl- /L | 88 | --- | 2012.2857 | --- | 93.8676 | 1994.6075 | 95.5881 | SDS-TOXb, ug Cl- /L | 127.6991 | NA | NA | 99.4419 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 15 | [13 empty] | SDS-MCAA* | mg/L | 9.8 | 11 | 10.4 | 11.5385 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 16:30 | 56 | 24 | 60 | 58 | 302 | 6.98 | 3.33 |  | 10.31 | 0.23118 | 0.67701 | 28.2919 | 15.9315 | 16.2165 | 434.4315 | 260.9761 | 430.4225 | 1.7145 | 57.2855 | 0.28308 | 7.7 | 7.64 | 7.9 | 267 | 312 | 388 | 421.8048 | -8.7126 | 15.7729 | 420.0158 | 36.431 | 0.031 | 0.66 | 1.645 | 1.901 | -15.5649 | 95.1181 | 1.8794 | 98.3506 | [8 empty] | SDS-CHCl3 | mg/L | 4.2 | 7.6 | 5.9 | 57.6271 | --- | 1442.5667 | --- | 98.7708 | 1426.0591 | 99.5863 | SDS-CHCl3 | mg/L | 67 | --- | 4655.8889 | --- | 86.0417 | 4611.7233 | 98.5472 | SDS-CHCl3 | mg/L | 18 | --- | 942 | --- | 96.25 | 933.4364 | 98.0716 | SDS-CHCl3 | mg/L | 11 | --- | 681 | --- | 97.7083 | 674.8448 | 98.37 | SDS-CDb, mg/L | 1.7836 | NA | NA | 1.4095 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7.0 + 0.3 | [13 empty] | SDS-DCAA* | mg/L | 130 | 130 | 130 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 14:30 | 78 | 24 | 60 | 58 | 302 | 6.58 | 2 |  | 8.58 | 0.23118 | 0.7669 | 34.1981 | 15.0185 | 15.2872 | 456.7399 | 274.5259 | 452.7698 | 1.8023 | 57.1977 | 0.26727 | [27 empty] | SDS-BDCM | mg/L | 8.2 | 12 | 10.1 | 37.6238 | --- | 141.6152 | --- | 81.1215 | 140.104 | 92.7911 | SDS-BDCM | mg/L | 30 | --- | 291.1111 | --- | 43.9252 | 288.5981 | 89.6049 | SDS-BDCM | mg/L | 21 | --- | 86 | --- | 60.7477 | 85.3976 | 75.4091 | SDS-BDCM | mg/L | 16 | --- | 69.5714 | --- | 70.0935 | 69.0793 | 76.8382 | TOCb, mg/L | 1.5893 | NA | NA | 1.3028 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | < 105 psi | [13 empty] | SDS-TCAA* | mg/L | 110 | 96 | 103 | 13.5922 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 15:15 | 78.75 | 24 | 60 | 58 | 302 | 6.51 | 1.42 |  | 7.93 | 0.23118 | 0.82093 | 37.0832 | 14.8587 | 15.1246 | 471.3477 | 283.3328 | 467.2948 | 1.8599 | 57.1401 | 0.26469 | [27 empty] | SDS-DBCM | mg/L | 16 | 22 | 19 | 31.5789 | --- | -22.2121 | --- | -251.8519 | -21.7386 | 187.4022 | SDS-DBCM | mg/L | 18 | --- | -122 | --- | -233.3333 | -120.6526 | 114.9189 | SDS-DBCM | mg/L | 27 | --- | -16.2 | --- | -400 | -15.7996 | 270.8901 | SDS-DBCM | mg/L | 25 | --- | -3 | --- | -362.963 | -2.7428 | 1011.4885 | UV254 b, cm-1 | 0.050419 | NA | NA | 0.047037 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 3-10 (2-11 cleaning) | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 16:00 | 79.5 | 24 | 60 | 58 | 302 | 6.51 | 0.5 |  | 7.01 | 0.23118 | 0.92867 | 42.0813 | 14.8587 | 15.1246 | 503.5236 | 302.6741 | 499.194 | 1.9868 | 57.0132 | 0.26528 | 7.94 | 7.89 | 8 | 285 | 325 | 411 | 733.64 | -78.5012 | 10.0946 | 728.8045 | 60.8949 | 0.054 | 0.632 | 2.072 | 8.1996 | -295.7346 | 91.4961 | 8.1118 | 99.3343 | [8 empty] | SDS-CHBr3 | mg/L | 14 | 17 | 15.5 | 19.3548 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 11 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 16 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 150 | NA | NA | 140.0849 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 3 | [13 empty] | SDS-DBAA* | mg/L | 1.5 | 1.5 | 1.5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 18:15 | 81.75 | 24 | 60 | 58 | 302 | 6.59 | 0.52 |  | 7.11 | 0.23118 | 0.92686 | 41.4754 | 15.0413 | 15.3105 | 502.9949 | 302.3236 | 498.616 | 1.9848 | 57.0152 | 0.26853 | 8.06 | 7.96 | 8.09 | 293 | 307 | 421 | 621.1538 | -47.5425 | 7.571 | 617.5735 | 52.5563 | 0.067 | 0.644 | 2.444 | 7.8333 | -220.5118 | 89.4488 | 7.7486 | 99.1353 | [8 empty] | SDS-THM4 | mg/L | 42.4 | 58.6 | 50.5 | 32.0792 | --- | 1530.5 | --- | 90.6291 | 1513.4945 | 96.6634 | SDS-THM4 | mg/L | 117.6 | --- | 4798.7111 | --- | 78.1778 | 4753.658 | 97.5261 | SDS-THM4 | mg/L | 77 | --- | 1000.8 | --- | 85.7116 | 992.2383 | 92.2398 | SDS-THM4 | mg/L | 68 | --- | 740.7143 | --- | 87.3817 | 734.5341 | 90.7424 | Alkb, mg/L CaCO3 | 117.9839 | NA | NA | 114.7687 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 5 | [13 empty] | SDS-BCAA* | mg/L | 17 | 15 | 16 | 12.5 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 19:00 | 82.5 | 24 | 60 | 58 | 302 | 6.8 | 0.85 |  | 7.65 | 0.23118 | 0.88889 | 38.4771 | 15.5206 | 15.7984 | 491.3026 | 295.2122 | 486.8873 | 1.9388 | 57.0612 | 0.27687 | 8.03 | 7.9 | 8.1 | 289 |  | 421 | 541 | -28.5036 | 8.8328 | 538.1629 | 46.2988 | 0.066 | 0.649 |  | 5.187 |  | 89.6063 | 5.1293 | 98.7133 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 208.182 | NA | NA | 186.9599 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 19:45 | 83.25 | 24 | 60 | 58 | 302 | 6.63 | 0.73 |  | 7.36 | 0.23118 | 0.90082 | 40.0326 | 15.1326 | 15.4034 | 494.858 | 297.4168 | 490.5234 | 1.9527 | 57.0473 | 0.27001 | [27 empty] | SDS-DCAA* | mg/L | 1.7 | 2.9 | 2.3 | 52.1739 | --- | 389.2697 | --- | 98.2308 | 384.8233 | 99.4023 | SDS-DCAA* | mg/L | 16 | --- | 1282.6667 | --- | 87.6923 | 1270.4757 | 98.7406 | SDS-DCAA* | mg/L | 8.3 | --- | 251.7 | --- | 93.6154 | 249.4442 | 96.6726 | SDS-DCAA* | mg/L | 4.1 | --- | 183.9571 | --- | 96.8462 | 182.3048 | 97.751 | Ca-Hdb, mg/L CaCO3 | 193.8614 | NA | NA | 172.7135 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hour | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 20:30 | 84 | 24 | 60 | 58 | 302 | 6.61 | 0.63 |  | 7.24 | 0.23118 | 0.91298 | 40.7127 | 15.087 | 15.3569 | 498.6254 | 299.6893 | 494.2713 | 1.9676 | 57.0324 | 0.26927 | [27 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 3.9 | --- | 1105.0111 | --- | 96.2136 | 1094.4135 | 99.6436 | SDS-TCAA* | mg/L | 2.9 | --- | 203.1 | --- | 97.1845 | 201.2446 | 98.559 | SDS-TCAA* | mg/L | 1.1 | --- | 146.6714 | --- | 98.932 | 145.3341 | 99.2431
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 14 | 11 | 12.5 | 24 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 23:30 | 87 | 24 | 59 | 58 | 302 | 6.47 | 0.54 |  | 7.01 | 0.23118 | 0.92297 | 42.0813 | 14.7674 | 15.0317 | 501.686 | 301.5857 | 497.399 | 1.9796 | 56.5204 | 0.26595 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 251.3 | 238.5 | 244.9 | 5.2266 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 8:45 | 96.25 | 24 | 60 | 59 | 302 | 5.83 | 0.5 |  | 6.33 | 0.23118 | 0.92101 | 46.7093 | 13.3067 | 13.5448 | 500.6893 | 301.2462 | 496.8391 | 1.9752 | 57.5248 | 0.23546 | 7.9 | 7.86 | 8.08 | 282 | 317 | 436 | 725.1 | -66.3073 | 11.041 | 720.8231 | 60.8781 | 0.108 | 0.649 | 5 | 6.7798 | -35.5964 | 82.9921 | 6.7154 | 98.3918 | [8 empty] | SDS-DBAA* | mg/L | 5.2 | 5.6 | 5.4 | 7.4074 | --- | -6.4182 | --- | -260 | -6.2824 | 185.9546 | SDS-DBAA* | mg/L | 4.3 | --- | -26.8111 | --- | -186.6667 | -26.5117 | 116.2193 | SDS-DBAA* | mg/L | 6.4 | --- | -3.4 | --- | -326.6667 | -3.3092 | 293.4017 | SDS-DBAA* | mg/L | 6.4 | --- | -0.6 | --- | -326.6667 | -0.53569 | 1294.7173 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 268.3 | 253.5 | 260.9 | 5.6727 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 9:30 | 97 | 24 | 60 | 58 | 302 | 6.75 | 0.79 |  | 7.54 | 0.23118 | 0.89523 | 39.0531 | 15.4065 | 15.6822 | 493.208 | 296.3771 | 488.8086 | 1.9463 | 57.0537 | 0.27487 | 8.26 | 8.11 | 8.19 | 293 | 320 | 426 | 522.0633 | -22.5501 | 7.571 | 519.5034 | 43.6 | 0.099 | 0.64 | 4.932 | 5.2147 | -5.7329 | 84.4094 | 5.1576 | 98.0805 | [8 empty] | SDS-BCAA* | mg/L | 2.4 | 3.1 | 2.75 | 25.4545 | --- | 42.9015 | --- | 82.8125 | 42.4402 | 93.5203 | SDS-BCAA* | mg/L | 8.3 | --- | 93.8556 | --- | 48.125 | 93.0321 | 91.0784 | SDS-BCAA* | mg/L | 5.5 | --- | 26.5 | --- | 65.625 | 26.3054 | 79.0917 | SDS-BCAA* | mg/L | 3.9 | --- | 21.1857 | --- | 75.625 | 21.0269 | 81.4523 | Qp/QT (HAA5), % | 80.4806 | 86.4975 | 83.9859 | 81.826 | Qp/QT (HAA5), % | 91.8634 | 98.7313 | 95.8645 | 93.3991
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 10:15 | 97.75 | 24 | 60 | 58 | 302 | 5.8 | 0.76 |  | 6.56 | 0.23118 | 0.88415 | 45.0366 | 13.2382 | 13.4751 | 489.3234 | 294.4197 | 485.5803 | 1.9303 | 57.0697 | 0.23612 | 8.19 | 8.07 | 8.1 | 289 | 319 | 446 | 530.6842 | -18.9875 | 8.8328 | 528.3634 | 45.3028 | 0.095 | 0.64 | 4.92 | 4.7561 | 3.3323 | 85.0394 | 4.7113 | 97.9836 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 145.8327 | 174.486 | 150.969 | 153.5815 | SDS-THM4b, ug/L | 90.2391 | 122.945 | 96.1019 | 99.0838
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 12:00 | 99.5 | 24 | 60 | 58 | 302 | 5.7 | 0.73 |  | 6.43 | 0.23118 | 0.88647 | 45.9673 | 13.0099 | 13.2427 | 489.9691 | 294.8478 | 486.2864 | 1.9328 | 57.0672 | 0.23206 | 8.13 | 8.04 | 8.02 | 285 | 313 | 439 | 566.863 | -29.126 | 10.0946 | 564.203 | 49.4863 | 0.1 | 0.639 | 4.912 | 4.8124 | 2.0277 | 84.252 | 4.7679 | 97.9027 | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 13:00 | 100.5 | 24 | 60 | 58 | 302 | 5.6 | 0.27 |  | 5.87 | 0.23118 | 0.954 | 50.448 | 12.7817 | 13.0104 | 511.1563 | 307.6389 | 507.3824 | 2.0163 | 56.9837 | 0.22832 | [27 empty] | SDS-DCBAA | mg/L | BMRL | 1.2 | 1.2 | #VALUE! | --- | 35.4424 | --- | 90.4 | 35.049 | 96.5762 | SDS-DCBAA | mg/L | 2.3 | --- | 115.6333 | --- | 81.6 | 114.5426 | 97.992 | SDS-DCBAA | mg/L | 1.7 | --- | 23.3 | --- | 86.4 | 23.0998 | 92.6406 | SDS-DCBAA | mg/L | 1.2 | --- | 17.3429 | --- | 90.4 | 17.1946 | 93.021 | SDS-TOXb, ug Cl- /L | 334.4277 | 397.0299 | 326.3858 | 332.8041 | SDS-TOXb, ug Cl- /L | 178.7679 | 250.2243 | 169.5886 | 176.9147
[44 empty] | 1998-07-20 | 13:30 | 101 | 24 | 60 | 58 | 302 | 5.66 | 4.51 |  | 10.17 | 0.23118 | 0.55654 | 28.6952 | 12.9186 | 13.1498 | 407.2527 | 245.0849 | 404.2134 | 1.6065 | 57.3935 | 0.22912 | [27 empty] | SDS-HAA5 | mg/L | 6.9 | 8.5 | 7.7 | 20.7792 | --- | 726.4879 | --- | 96.8559 | 718.2289 | 98.9279 | SDS-HAA5 | mg/L | 24.2 | --- | 2476.4222 | --- | 90.1184 | 2452.8209 | 99.0134 | SDS-HAA5 | mg/L | 17.6 | --- | 472.2 | --- | 92.8134 | 467.9868 | 96.2392 | SDS-HAA5 | mg/L | 11.6 | --- | 344.8857 | --- | 95.2634 | 341.8238 | 96.6064 | SDS-CDb, mg/L | 4.1139 | 4.3152 | 3.8465 | 4.0497 | SDS-CDb, mg/L | 2.3593 | 2.589 | 2.054 | 2.286
[44 empty] | 1998-07-20 | 14:00 | 101.5 | 24 | 60 | 58 | 302 | 5.66 | 4.51 |  | 10.17 | 0.23118 | 0.55654 | 28.6952 | 12.9186 | 13.1498 | 407.2527 | 245.0849 | 404.2134 | 1.6065 | 57.3935 | 0.22912 | [27 empty] | SDS-HAA6 | mg/L | 9.3 | 11.6 | 10.45 | 22.0096 | --- | 769.3894 | --- | 95.9946 | 760.669 | 98.6262 | SDS-HAA6 | mg/L | 32.5 | --- | 2570.2778 | --- | 87.5431 | 2545.8531 | 98.7234 | SDS-HAA6 | mg/L | 23.1 | --- | 498.7 | --- | 91.146 | 494.2922 | 95.3267 | SDS-HAA6 | mg/L | 15.5 | --- | 366.0714 | --- | 94.059 | 362.8508 | 95.7283 | TOCb, mg/L | 3.4411 | 4.2178 | 3.4736 | 3.3991 | TOCb, mg/L | 2.0467 | 2.9332 | 2.0839 | 1.9987
[44 empty] | 1998-07-20 | 14:20 | 101.8333 | 24 | 59 | 58 | 302 | 5.71 | 5.6 |  | 11.31 | 0.23118 | 0.50486 | 25.702 | 13.0328 | 13.266 | 396.774 | 238.7628 | 393.7865 | 1.5652 | 56.9348 | 0.233 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.14286 | 0.17743 | 0.14452 | 0.14977 | UV254 b, cm-1 | 0.073255 | 0.11271 | 0.075151 | 0.081144
[44 empty] | 1998-07-20 | 14:50 | 102.3333 | 24 | 59 | 57 | 302 | 5.75 | 5.93 |  | 11.68 | 0.23118 | 0.49229 | 24.8562 | 13.1241 | 13.3589 | 394.3116 | 237.2682 | 391.3215 | 1.5555 | 56.4445 | 0.23667 | 8.06 | 7.96 | 8.08 | 250 | 310 | 358 | 381.9663 | -6.6945 | 21.1356 | 380.71 | 34.3332 | 0.068 | 0.639 | 1.689 | 1.1848 | 29.8526 | 89.2913 | 1.1742 | 94.2086 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 150 | 150 | 150 | 141.8174 | Bromideb, ug/L | 150 | 150 | 150 | 140.6601
[44 empty] | 1998-07-20 | 16:00 | 103.5 | 24 | 59 | 57 | 302 | 5.8 | 5.18 |  | 10.98 | 0.23118 | 0.52823 | 26.5046 | 13.2382 | 13.4751 | 401.4701 | 241.5595 | 398.399 | 1.5838 | 56.4162 | 0.23885 | 8.01 | 7.91 | 8 | 264 | 318 | 365 | 376.3436 | -3.1078 | 16.7192 | 375.2648 | 29.6497 | 0.055 | 0.639 | 1.325 | 1.2844 | 3.0626 | 91.3386 | 1.2726 | 95.6782 | [47 empty] | Alkb, mg/L CaCO3 | 131.6651 | 141.7893 | 131.8522 | 130.4475 | Alkb, mg/L CaCO3 | 121.3636 | 132.9198 | 121.5772 | 119.9739
[44 empty] | 1998-07-20 | 16:30 | 104 | 24 | 59 | 57 | 302 | 5.86 | 5.89 |  | 11.75 | 0.23118 | 0.49872 | 24.7021 | 13.3751 | 13.6145 | 395.5934 | 238.0043 | 392.5355 | 1.5606 | 56.4394 | 0.24122 | 7.81 | 7.77 | 7.93 | 266 | 326 | 364 | 367.7402 | -1.0275 | 16.0883 | 366.7532 | 27.4717 | 0.051 | 0.637 | 1.234 | 1.216 | 1.4566 | 91.9685 | 1.2047 | 95.7667 | [47 empty] | T-Hdb, mg/L CaCO3 | 222.5434 | 239.3167 | 222.5728 | 206.5366 | T-Hdb, mg/L CaCO3 | 211.7298 | 230.8754 | 211.7633 | 193.4591
[44 empty] | 1998-07-20 | 17:00 | 104.5 | 24 | 59 | 57 | 302 | 5.81 | 5.33 |  | 11.14 | 0.23118 | 0.52154 | 26.1095 | 13.261 | 13.4983 | 400.1221 | 240.7451 | 397.0559 | 1.5784 | 56.4216 | 0.23924 | 7.98 | 7.88 | 7.93 | 258 | 313 | 355 | 381.3133 | -7.4122 | 18.612 | 380.1271 | 32.128 | 0.049 | 0.641 | 1.199 | 1.2738 | -6.2363 | 92.2835 | 1.262 | 96.1172 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 203.6876 | 221.401 | 205.6084 | 187.2662 | Ca-Hdb, mg/L CaCO3 | 196.2888 | 216.5075 | 198.4813 | 177.5448
[44 empty] | 1998-07-20 | 17:30 | 105 | 24 | 59 | 57 | 302 | 5.84 | 6.97 |  | 12.81 | 0.23118 | 0.45589 | 22.5753 | 13.3295 | 13.568 | 387.3426 | 233.0466 | 384.3589 | 1.528 | 56.472 | 0.24026 | 7.93 | 7.87 | 7.95 | 273 | 328 | 362 | 353.8666 | 2.2468 | 13.8801 | 353.0847 | 22.6814 | 0.047 | 0.624 | 1.152 | 1.1277 | 2.1119 | 92.5984 | 1.1172 | 95.7931 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-07-20 | 18:00 | 105.5 | 24 | 59 | 57 | 302 | 5.87 | 7.17 |  | 13.04 | 0.23118 | 0.45015 | 22.1595 | 13.398 | 13.6377 | 386.2685 | 232.391 | 383.2776 | 1.5238 | 56.4762 | 0.24148 | 7.81 | 7.79 | 7.92 | 258 | 310 | 348 | 365.3026 | -4.972 | 18.612 | 364.2598 | 29.1714 | 0.045 | 0.629 | 1.112 | 1.118 | -0.54195 | 92.9134 | 1.1076 | 95.9372 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-07-21 | 8:15 | 119.75 | 24 | 59 | 57 | 302 | 6.13 | 4.63 |  | 10.76 | 0.23118 | 0.5697 | 27.0669 | 13.9914 | 14.2418 | 410.1288 | 246.6597 | 406.8107 | 1.6181 | 56.3819 | 0.25259 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-07-21 | 9:00 | 120.5 | 24 | 53 | 51 | 302 | 5.75 | 24.7 |  | 30.45 | 0.23118 | 0.18883 | 8.9179 | 13.1241 | 13.3589 | 342.7796 | 206.26 | 340.1803 | 1.3522 | 50.6478 | 0.26376 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-07-21 | 9:30 | 121 | 24 | 55 | 54 | 302 | 6.15 | 18.6 |  | 24.75 | 0.23118 | 0.24848 | 11.202 | 14.037 | 14.2882 | 351.8489 | 211.6033 | 348.9929 | 1.3882 | 53.1118 | 0.26902 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-07-21 | 9:45 | 121.25 | 24 | 55 | 54 | 302 | 6.17 | 16.3 |  | 22.47 | 0.23118 | 0.27459 | 12.4401 | 14.0827 | 14.3347 | 355.9615 | 214.0709 | 353.0626 | 1.4044 | 53.0956 | 0.26998 | 7.53 | 7.63 | 7.76 | 248 | 316 | 325 | 343.1184 | -5.5749 | 21.7666 | 342.1467 | 27.5165 | 0.028 | 0.644 | 0.872 | 0.86477 | 0.82956 | 95.5906 | 0.85622 | 96.7298 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-07-21 | 10:00 | 121.5 | 24 | 56 | 54 | 302 | 6.2 | 16.07 |  | 22.27 | 0.23118 | 0.2784 | 12.5608 | 14.1512 | 14.4044 | 356.5728 | 214.4298 | 353.6546 | 1.4068 | 53.5932 | 0.26877 | 7.97 | 7.82 | 7.89 | 244 | 315 | 324 | 345.1643 | -6.5322 | 23.0284 | 344.1258 | 29.0957 | 0.028 | 0.644 | 0.855 | 0.86919 | -1.6594 | 95.5906 | 0.86055 | 96.7463 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-07-21 | 10:30 | 122 | 24 | 56 | 54 | 302 | 5.98 | 15.47 |  | 21.45 | 0.23118 | 0.27879 | 13.0793 | 13.649 | 13.8933 | 356.6147 | 214.5186 | 353.801 | 1.4069 | 53.5931 | 0.25924 | 7.65 | 7.6 | 7.7 | 255 | 316 | 332 | 340.9664 | -2.7007 | 19.5584 | 340.1153 | 25.0254 | 0.027 | 0.641 | 0.866 | 0.87003 | -0.4648 | 95.748 | 0.86168 | 96.8666 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-07-21 | 11:00 | 122.5 | 24 | 56 | 54 | 302 | 6.03 | 15.6 |  | 21.63 | 0.23118 | 0.27878 | 12.9621 | 13.7632 | 14.0094 | 356.6179 | 214.506 | 353.7803 | 1.4069 | 53.5931 | 0.2614 | 7.99 | 7.83 | 7.9 | 246 | 312 | 323 | 344.4442 | -6.6391 | 22.3975 | 343.4614 | 28.3762 | 0.025 | 0.636 | 0.86 | 0.87079 | -1.2545 | 96.063 | 0.86234 | 97.1009 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-07-21 | 12:00 | 123.5 | 24 | 56 | 54 | 302 | 6.06 | 14.27 |  | 20.33 | 0.23118 | 0.29808 | 13.8549 | 13.8316 | 14.0791 | 359.7336 | 216.3714 | 356.8569 | 1.4192 | 53.5808 | 0.26276 | 7.82 | 7.65 | 7.88 | 249 | 312 | 332 | 345.8774 | -4.1799 | 21.4511 | 344.9054 | 27.8063 | 0.025 | 0.636 | 0.864 | 0.89405 | -3.4777 | 96.063 | 0.88533 | 97.1762 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-07-21 | 13:30 | 125 | 24 | 56 | 54 | 302 | 6.03 | 13.93 |  | 19.96 | 0.23118 | 0.3021 | 14.1303 | 13.7632 | 14.0094 | 360.3863 | 216.7727 | 357.5187 | 1.4218 | 53.5782 | 0.26148 | 7.87 | 7.73 | 7.92 | 248 | 314 | 331 | 346.8686 | -4.7941 | 21.7666 | 345.8816 | 28.2992 | 0.027 | 0.631 | 0.865 | 0.89819 | -3.837 | 95.748 | 0.88949 | 96.9646 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-07-21 | 14:45 | 126.25 | 24 | 56 | 55 | 302 | 5.8 | 12.69 |  | 18.49 | 0.23118 | 0.31368 | 15.3332 | 13.2382 | 13.4751 | 362.2625 | 217.9687 | 359.4913 | 1.4291 | 54.0709 | 0.24921 | 8.55 | 8.31 | 8.31 | 252 | 308 | 328 | 346.7084 | -5.7038 | 20.5047 | 345.799 | 27.1253 | 0.031 | 0.632 | 0.865 | 0.91106 | -5.3248 | 95.1181 | 0.90261 | 96.5655 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-07-21 | 15:30 | 127 | 24 | 56 | 55 | 302 | 5.85 | 12.4 |  | 18.25 | 0.23118 | 0.32055 | 15.5479 | 13.3523 | 13.5912 | 363.4035 | 218.6405 | 360.5993 | 1.4336 | 54.0664 | 0.25138 | 8.09 | 8.02 | 8.05 | 258 | 322 | 342 | 344.8347 | -0.82885 | 18.612 | 343.9936 | 24.9986 | 0.031 | 0.632 | 0.864 | 0.91995 | -6.4759 | 95.1181 | 0.91134 | 96.5984
[44 empty] | 1998-07-21 | 16:30 | 128 | 24 | 56 | 55 | 302 | 5.83 | 12.8 |  | 18.63 | 0.23118 | 0.31294 | 15.2104 | 13.3067 | 13.5448 | 362.1425 | 217.8878 | 359.3577 | 1.4286 | 54.0714 | 0.2505
[44 empty] | 1998-07-21 | 17:00 | 128.5 | 24 | 56 | 55 | 302 | 6.09 | 16.2 |  | 22.29 | 0.23118 | 0.27322 | 12.5487 | 13.9001 | 14.1488 | 355.736 | 213.9583 | 352.877 | 1.4035 | 54.0965 | 0.26155
[44 empty] | 1998-07-22 | 8:00 | 143.5 | 24 | 56 | 55 | 302 | 6.09 | 16.2 | X | 22.29 | 0.23118 | 0.27322 | 12.5487 | 13.9001 | 14.1488 | 355.736 | 213.9583 | 352.877 | 1.4035 | 54.0965 | 0.26155
[44 empty] | 1998-07-22 | 14:30 |  | 24 | 60 | 58 | 302 | 8.7 | 5.6 |  | 14.3 | 0.23118 | 0.60839 | 20.1189 | 19.8573 | 20.2126 | 419.1825 | 251.2274 | 414.3441 | 1.6554 | 57.3446 | 0.35248
[44 empty] | 1998-07-22 | 16:15 |  | 24 | 45 | 43 | 302 | 6.56 | 3.04 |  | 9.6 | 0.23118 | 0.68333 | 30.4583 | 14.9728 | 15.2408 | 435.7995 | 261.9466 | 432.0231 | 1.7196 | 42.2804 | 0.36047
[44 empty] | 1998-07-22 | 16:30 |  | 24 | 76 | 75 | 302 | 11.3 | 6.15 |  | 17.45 | 0.23118 | 0.64756 | 16.3066 | 25.7916 | 26.2531 | 428.8695 | 256.1153 | 422.4056 | 1.6952 | 73.8048 | 0.35571
[44 empty] | 1998-07-22 | 16:45 |  | 24 | 60 | 58 | 302 | 8.9 | 4.5 |  | 13.4 | 0.23118 | 0.66418 | 21.5373 | 20.3138 | 20.6773 | 432.014 | 258.8469 | 426.9107 | 1.7062 | 57.2938 | 0.3609
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: C. Hill (7/30/99): NF200 was used during quarters 1, 2 and 3. NTR7450 was used during a second 3rd quarter and quarter 4.
Note on Q3: C. Rice 7/13/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Gary Puetz: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X11: C. Rice 7/19/99: Alkalinity verified by consultant.
Note on X13: C. Rice 7/19/99: Total hardness verified by consultant.
Note on X14: C. Rice 7/19/99: Calcium hardness verified by consultant.
Note on X16: C. Rice 7/19/99: Consultant verified feed ammonia values.
Note on BV7: C. Rice 7/13/99: Consultant stated that all operational parameters were verified and found to be correct. No explanation was given as to why these values are relatively high, compared to the first quarter.
Note on CY3: Alison Gusses: Permeate TOC, UV254, TOX and THM4 concentrations were verified by consultant. No explanation was given as to why these values are higher during the 2nd quarter, compared to the 1st quarter. Also, the consultant did not comment on the possible cause in the decreased concentrations of TOC, UV and DBP during the 70% recovery run.
Note on DG10: C. Rice 7/13/99: Consultant verified alkalinity, total hardness and calcium hardness values due to consistently high mass balance closure errors.
Note on DL3: Alison Gusses: Permeate TOC, UV254, TOX and THM4 concentrations were verified by consultant. No explanation was given as to why these values are higher during the 2nd quarter, compared to the 1st quarter.
Note on DQ10: C. Rice 7/13/99: Consultant verified alkalinity, total hardness and calcium hardness values due to consistently high mass balance closure errors.
Note on DV3: Alison Gusses: Permeate TOC, UV254, TOX and THM4 concentrations were verified by consultant. No explanation was given as to why these values are higher during the 2nd quarter, compared to the 1st quarter.
Note on EA10: C. Rice 7/13/99: Consultant verified alkalinity, total hardness and calcium hardness values due to consistently high mass balance closure errors.
Note on EF3: Alison Gusses: Permeate TOC, UV254, TOX and THM4 concentrations were verified by consultant. No explanation was given as to why these values are higher during the 2nd quarter, compared to the 1st quarter.
Note on EK10: C. Rice 7/13/99: Consultant verified alkalinity, total hardness and calcium hardness values due to consistently high mass balance closure errors.

## NF200. 3rd Quarter
FIELD-SET 3: 3rdQUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.29278 | [45 empty] | Recovery during sample collection (decimal) | 0.73 | [10 empty] | Recovery during sample collection (decimal) | [8 empty] | Recovery during sample collection (decimal) | [8 empty] | Recovery during sample collection (decimal) | [9 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-11-23 | 1998-12-10 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 6.15 | [10 empty] | Feed flow rate during sample collection (mL/min) | [8 empty] | Feed flow rate during sample collection (mL/min) | [8 empty] | Feed flow rate during sample collection (mL/min) | [7 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:45 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | [8 empty] | Influent flow rate during sample collection (mL/min) | [8 empty] | Influent flow rate during sample collection (mL/min) | [7 empty] | SDS-THM4F, ug/L | 462.85 | 462.85 | 462.85 | 462.85 | SDS-THM4F, ug/L | 462.85 | 462.85 | 462.85 | 462.85 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | #DIV/0! | 0 | 0 | 0 | SDS-THM4p, ug/L | #DIV/0! | 0 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.59 | 8.36 | 7.975 | 9.6552 | 1998-11-30 | 8:45 | 0 | 23 | 50 | 51.5 | 272 | 5.2 |  | 5.2 | 0.20821 | 1 | 51.3077 | 11.8687 | 12.4435 | 0 | 0 | 0 | 0 | 50.75 | 0.24519 | 1998-12-01 | 9:30 | 0 | 23 | 50.5 | 51.5 | 272 | 4.44 | 1.99 |  | 6.43 | 0.20821 | 0.69051 | 41.3017 | 10.1341 | 10.6249 | 351.366 | 247.2898 | 349.6671 | 1.0323 | 49.9677 | 0.21263 | 7.89 | 8.27 | 8.17 | 102 | 280 | 179 | 675.5302 | -277.3911 | 63.5063 | 670.8491 | 84.7954 | 0.013 | 0.563 | 0.401 | 1.8111 | -351.6554 | 97.7173 | 1.7965 | 99.2764 | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 208.5 | 208.5 | 208.5 | 208.5 | SDS-HAA5F, ug/L | 208.5 | 208.5 | 208.5 | 208.5 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.28066 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 24 | 23.5 | 4.2553 | 1998-11-30 | 9:45 | 1 | 23 | 51 | 52 | 272 | 5.35 | 8.55 | 13.9 | 0.20821 | 0.38489 | 18.5683 | 12.2111 | 12.8025 | 0 | 0 | 0 | 0 | 51.5 | 0.24859 | 1998-12-01 | 10:30 | 1 | 23 | 52 | 53 | 272 | 4.54 | 1.89 |  | 6.43 | 0.20821 | 0.70607 | 41.3017 | 10.3623 | 10.8642 | 353.4372 | 248.72 | 351.6893 | 1.0384 | 51.4616 | 0.21111 | 8.1 | 8.34 | 8.31 | 202 | 280 | 391 | 465.664 | -19.0957 | 27.7281 | 463.4636 | 56.4151 | 0.026 | 0.568 | 1.062 | 1.8751 | -76.5584 | 95.4346 | 1.8596 | 98.6019 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | #DIV/0! | 0 | 0 | 0 | SDS-HAA5p, ug/L | #DIV/0! | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | highly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 436 | 406 | 421 | 7.1259 | 1998-11-30 | 10:45 | 2 | 23 | 51 | 52 | 272 | 5.6 | 8.24 | 13.84 | 0.20821 | 0.40462 | 18.6532 | 12.7817 | 13.4007 | 0 | 0 | 0 | 0 | 51.5 | 0.26021 | 1998-12-01 | 11:30 | 2 | 23 | 52 | 53 | 272 | 4.56 | 1.75 |  | 6.31 | 0.20821 | 0.72266 | 42.1062 | 10.408 | 10.912 | 355.6538 | 250.2743 | 353.8871 | 1.045 | 51.455 | 0.21207 | 7.95 | 8.21 | 8.14 | 212 | 280 | 393 | 455.3857 | -15.8742 | 24.1503 | 453.3456 | 53.2366 | 0.028 | 0.571 | 1.353 | 1.9805 | -46.378 | 95.0834 | 1.9641 | 98.5744 | [8 empty] | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-02 | --- | --- | 1998-12-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1095 | 1095 | 1095 | 1095 | SDS-TOXF, ug Cl- /L | 1095 | 1095 | 1095 | 1095 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 281 | 278 | 279.5 | 1.0733 | 1998-11-30 | 11:45 | 3 | 23 | 51 | 52.5 | 272 | 5.5 | 8.2 | 13.7 | 0.20821 | 0.40146 | 18.854 | 12.5535 | 13.1614 | 0 | 0 | 0 | 0 | 51.75 | 0.25433 | 1998-12-01 | 12:45 | 3.25 | 23 | 52 | 53 | 272 | 4.62 | 1.58 |  | 6.2 | 0.20821 | 0.74516 | 42.871 | 10.5449 | 11.0556 | 358.7126 | 252.41 | 356.907 | 1.054 | 51.446 | 0.2149 | 9.13 | 8.27 | 8.14 | 220 | 280 | 403 | 453.481 | -12.5263 | 21.288 | 451.4981 | 51.2733 | 0.033 | 0.567 | 1.562 | 2.1383 | -36.892 | 94.2054 | 2.1204 | 98.4437 | [8 empty] | Sampling time | hh:mm | 9:30 | 18:00 | --- | --- | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | 0 | 0 | 0 | SDS-TOXp, ug Cl- /L | #DIV/0! | 0 | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 214 | 220 | 217 | 2.765 | 1998-11-30 | 13:45 | 5 | 23 | 51 | 52.5 | 272 | 5.4 | 2.23 | 7.63 | 0.20821 | 0.70773 | 34.6488 | 12.3252 | 12.9221 | 0 | 0 | 0 | 0 | 51.75 | 0.2497 | 1998-12-01 | 14:45 | 5.25 | 23 | 52 | 53 | 272 | 4.48 | 1.22 |  | 5.7 | 0.20821 | 0.78596 | 46.7193 | 10.2254 | 10.7206 | 364.3264 | 256.4 | 362.5488 | 1.0704 | 51.4296 | 0.20845 | 8.06 | 8.28 | 8.41 | 232 | 280 | 405 | 453.9262 | -12.0806 | 16.9946 | 452.0986 | 48.6838 | 0.048 | 0.567 | 1.799 | 2.4845 | -38.1054 | 91.5716 | 2.4645 | 98.0523 | [8 empty] | Operation time | hh.hh | 30.5 | 32.5 | --- | --- | 27.5 | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | --- | Cumulative time | hr |  |  | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 12.51 | 12.51 | 12.51 | 12.51 | SDS-CDF, mg/L | 12.51 | 12.51 | 12.51 | 12.51 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 204 | 206 | 205 | 0.97561 | 1998-11-30 | 14:45 | 6 | 23 | 51 | 52.5 | 272 | 5.35 | 2.16 | 7.51 | 0.20821 | 0.71238 | 35.2184 | 12.2111 | 12.8025 | 0 | 0 | 0 | 0 | 51.75 | 0.24739 | 1998-12-01 | 15:45 | 6.25 | 23 | 52 | 53.5 | 272 | 4.46 | 1.78 |  | 6.24 | 0.20821 | 0.71474 | 42.5897 | 10.1797 | 10.6727 | 354.5701 | 249.5393 | 352.8479 | 1.0417 | 51.7083 | 0.2064 | 8.07 | 8.19 | 8.44 | 221 | 281 | 397 | 426.0787 | -7.3246 | 20.9302 | 424.3973 | 47.9262 | 0.068 | 0.565 | 1.763 | 1.8261 | -3.5773 | 88.0597 | 1.8117 | 96.2465 | [8 empty] | pH | --- | 8.09 | 7.87 | 7.98 | 2.7569 | 8.229 | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | --- | SDS-CDp, mg/L | #DIV/0! | 0 | 0 | 0 | SDS-CDp, mg/L | #DIV/0! | 0 | 0 | 0 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 15 | 6.5 | 59.9451 | 283.3154 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.888 | 0.359 | 0.6235 | 84.8436 | 1998-11-30 | 15:40 | 6.9167 | 23 | 51 | 52.5 | 272 | 5.4 | 2.15 | 7.55 | 0.20821 | 0.71523 | 35.0265 | 12.3252 | 12.9221 | 0 | 0 | 0 | 0 | 51.75 | 0.2497 | 1998-12-01 | 17:00 | 7.5 | 23 | 52 | 53.5 | 263 | 4.48 | 1.49 |  | 5.97 | 0.20132 | 0.75042 | 43.0536 | 10.2254 | 10.7206 | 359.4349 | 252.9145 | 357.6204 | 1.0561 | 51.6939 | 0.20739 | 8.14 | 8.31 | 8.35 | 230 | 281 | 392 | 428.3322 | -9.2684 | 17.7102 | 426.643 | 46.0908 | 0.097 | 0.573 | 1.727 | 1.9902 | -15.2386 | 82.9675 | 1.974 | 95.0862 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | --- | TOCF, mg/L | 12 | 12 | 12 | 12 | TOCF, mg/L | 12 | 12 | 12 | 12 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 15 | 16.5 | 69.9451 | 283.3154 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-11-30 | 16:05 | 7.3333 | 23 | 61 | 62.5 | 272 | 6.51 | 2.92 | 9.43 | 0.20821 | 0.69035 | 27.8441 | 14.8587 | 15.5783 | 0 | 0 | 0 | 0 | 61.75 | 0.25228 | 1998-12-02 | 9:20 | 23.8333 | 23 | 52 | 53.5 | 272 | 6.1 | 1.67 |  | 7.77 | 0.20821 | 0.78507 | 34.0064 | 13.9229 | 14.5972 | 364.6736 | 256.182 | 362.2406 | 1.0728 | 51.6772 | 0.28247 | 7.96 | 7.93 | 8.18 | 267 | 280 | 332 | 325.1587 | 2.0606 | 4.4723 | 324.5065 | 17.7212 | 0.477 | 0.567 | 0.919 | 0.90737 | 1.265 | 16.2423 | 0.90255 | 47.1496 | [8 empty] | Alkalinity | mg/L as CaCO3 | NA | NA | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | 421 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | 421 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | 421 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | TOCp, mg/L | #DIV/0! | 0 | 0 | 0 | TOCp, mg/L | #DIV/0! | 0 | 0 | 0 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 57.9451 | 283.3154 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 12.3 | 11.7 | 12 | 5 | 1998-11-30 | 16:30 | 7.75 | 23 | 71 | 72.5 | 272 | 7.47 | 3.74 | 11.21 | 0.20821 | 0.66637 | 23.264 | 17.0499 | 17.8756 | 0 | 0 | 0 | 0 | 71.75 | 0.24914 | 1998-12-02 | 10:00 | 24.5 | 23 | 52 | 53.5 | 272 | 6.23 | 1.58 |  | 7.81 | 0.20821 | 0.7977 | 33.8271 | 14.2196 | 14.9083 | 366.5087 | 257.4336 | 364.0104 | 1.0783 | 51.6717 | 0.28852 |  |  |  | 259 |  | 323 | 360.3323 | -11.558 | 7.3345 | 359.1718 | 27.8897 | 0.477 | 0.556 | 0.88 | 0.93423 | -6.1626 | 16.2423 | 0.92899 | 48.6542 | [8 empty] | Total dissolved solids | mg/L | 232.2143 | 255.7778 | 243.996 | 9.6573 | 336.0333 | 375.4922 | -11.7425 | 12.7027 | 374.407 | 34.8313 | Total dissolved solids | mg/L |  |  | 279.5 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | 279.5 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | 279.5 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 F, cm-1 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | UV254 F, cm-1 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 3.6429 | 57.0879 | 283.3154 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.613 | 0.526 | 0.5695 | 15.2766 | 1998-11-30 | 16:55 | 8.1667 | 23 | 41.5 | 43 | 272 | 4.48 | 1.53 | 6.01 | 0.20821 | 0.74542 | 44.2579 | 10.2254 | 10.7206 | 0 | 0 | 0 | 0 | 42.25 | 0.25374 | 1998-12-02 | 11:00 | 25.5 | 23 | 52 | 53.5 | 272 | 6.46 | 1.96 |  | 8.42 | 0.20821 | 0.76722 | 31.304 | 14.7446 | 15.4587 | 362.2663 | 254.3882 | 359.7042 | 1.066 | 51.684 | 0.2991 | 8.08 | 8.18 | 8.15 | 262 | 280 | 316 | 337.1786 | -6.7021 | 6.2612 | 336.2858 | 22.0901 | 0.461 |  | 0.8 | 0.92711 | -15.8884 | 19.0518 | 0.92157 | 49.9768 | [8 empty] | Total hardness | mg/L as CaCO3 | NA | NA | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | 217 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | 217 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | 217 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 p, cm-1 | 0.27298 | 0 | 0 | 0 | UV254 p, cm-1 | 0.27298 | 0 | 0 | 0 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.9837 | 4.4957 | 4.7397 | 10.2962 | 1998-11-30 | 17:15 | 8.5 | 23 | 52 | 53.5 | 272 | 5.65 | 2.05 | 7.7 | 0.20821 | 0.73377 | 34.3247 | 12.8958 | 13.5204 | 0 | 0 | 0 | 0 | 52.75 | 0.25631 | 1998-12-02 | 12:00 | 26.5 | 23 | 52 | 53.5 | 272 | 6.63 | 2.47 |  | 9.1 | 0.20821 | 0.72857 | 28.8901 | 15.1326 | 15.8655 | 356.9862 | 250.6326 | 354.3938 | 1.0506 | 51.6994 | 0.30688 | 8.12 | 8.28 | 8.26 |  | 281 | 312 |  | #VALUE! |  |  |  | 0.455 | 0.557 | 0.757 | 0.87684 | -15.8312 | 20.1054 | 0.8717 | 47.8032 | [8 empty] | Calcium hardness | mg/L as CaCO3 | NA | NA | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | 205 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | 205 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | 205 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | 140 | 140 | 0 | 1998-11-30 | 17:40 | 8.9167 | 23 | 52 | 53.5 | 272 | 5.58 | 2.8 | 8.38 | 0.20821 | 0.66587 | 31.4582 | 12.7361 | 13.3529 | 0 | 0 | 0 | 0 | 52.75 | 0.25313 | 1998-12-02 | 13:00 | 27.5 | 23 | 52 | 53 | 272 | 6.74 | 3.98 |  | 10.72 | 0.20821 | 0.62873 | 24.3731 | 15.3837 | 16.1287 | 343.9435 | 241.4458 | 341.4037 | 1.0123 | 51.4877 | 0.31325 | 7.99 | 8.38 | 8.29 | 260 | 280 | 306 | 312.5226 | -2.1316 | 6.9767 | 311.8719 | 16.6324 | 0.48 | 0.555 | 0.791 | 0.72107 | 8.8413 | 15.7155 | 0.71808 | 33.1549 | [8 empty] | Turbidity | ntu | NA | NA | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | 0.6235 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | 0.6235 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | 0.6235 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Bromidep, ug/L | #DIV/0! | 0 | 0 | 0 | Bromidep, ug/L | #DIV/0! | 0 | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 17 | 11 | 14 | 42.8571 | 1999-12-01 | 9:30 | 24.75 | 23 | 50.5 | 51.5 | 272 | 4.44 | 1.99 | 6.43 | 0.20821 | 0.69051 | 41.3017 | 10.1341 | 10.6249 | 0 | 0 | 0 | 0 | 51 | 0.20833 | 1998-12-02 | 14:00 | 28.5 | 23 | 52 | 53 | 272 | 6.93 | 3.32 |  | 10.25 | 0.20821 | 0.6761 | 25.5366 | 15.8174 | 16.5834 | 350.0679 | 245.6926 | 347.4086 | 1.0305 | 51.4695 | 0.3222 | 8.02 | 8.38 | 8.27 | 258 | 280 | 300 | 324.378 | -8.126 | 7.6923 | 323.5324 | 20.2553 | 0.457 | 0.558 | 0.694 | 0.80433 | -15.8972 | 19.7542 | 0.7999 | 42.868 | [8 empty] | Ammonia | mg NH3-N / L | NA | NA | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 421 | 421 | 421 | 421 | AlkF, mg/L CaCO3 | 421 | 421 | 421 | 421
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.5467 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.01 | 1.97 | 1.49 | 64.4295 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 15:00 | 29.5 | 23 | 52 | 53 | 272 | 7.13 | 2.89 |  | 10.02 | 0.20821 | 0.71158 | 26.1457 | 16.2738 | 17.062 | 354.8189 | 248.971 | 352.0443 | 1.0446 | 51.4554 | 0.33159 | 8.01 | 8.24 | 8.22 | 258 | 281 | 299 | 332.5433 | -11.2185 | 7.6923 | 331.5662 | 22.1875 | 0.463 | 0.559 | 0.683 | 0.83225 | -21.852 | 18.7006 | 0.82741 | 44.0422 | [8 empty] | Total organic carbon | mg/L | NA | NA | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | 12 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | 12 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | 12 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Alkp, mg/L CaCO3 | #DIV/0! | 0 | 0 | 0 | Alkp, mg/L CaCO3 | #DIV/0! | 0 | 0 | 0
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.00233 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 15.99 | 9.03 | 12.51 | 55.6355 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 16:00 | 30.5 | 23 | 52 | 53 | 272 | 7.32 | 2.66 |  | 9.98 | 0.20821 | 0.73347 | 26.2545 | 16.7075 | 17.5167 | 357.8354 | 251.0339 | 354.9612 | 1.0536 | 51.4464 | 0.34048 | 7.68 | 8.25 | 8.3 | 268 | 282 | 299 | 311.1466 | -4.0624 | 4.1145 | 310.566 | 13.706 | 0.473 | 0.552 | 0.688 | 0.83506 | -21.3745 | 16.9447 | 0.83018 | 43.0247 | [8 empty] | UV254 | cm-1 | 0.2704 | 0.27556 | 0.27298 | 1.8886 | 1.0783 | 1.3712 | -27.1661 | 52.0671 | 1.3621 | 79.9597 | UV254 | cm-1 |  |  | 0.5695 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | 0.5695 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | 0.5695 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | T-HdF, mg/L CaCO3 | 217 | 217 | 217 | 217 | T-HdF, mg/L CaCO3 | 217 | 217 | 217 | 217
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 17:00 | 31.5 | Switched to the second NF200 membrane | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | [12 empty] | 0.561 | [14 empty] | SUVA | L/(mg*m) | NA | NA | #DIV/0! | #VALUE! | #VALUE! | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | SUVA | L/(mg*m) |  |  | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | #DIV/0! | 0 | 0 | 0 | T-Hdp, mg/L CaCO3 | #DIV/0! | 0 | 0 | 0
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.79 | 8.98 | 8.885 | 2.1384 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 17:20 | 31.8333 | 23 | 51.5 | 52.5 | 272 | 6.74 | 2.56 |  | 9.3 | 0.20821 | 0.72473 | 28.2473 | 15.3837 | 16.1287 | 356.4938 | 250.256 | 353.8613 | 1.0492 | 50.9508 | 0.31656 |  |  |  | 221 | 281 | 299 | 433.5195 | -44.9898 | 20.9302 | 430.8865 | 48.7104 | 0.034 |  | 0.883 | 1.9794 | -124.1643 | 94.0299 | 1.9553 | 98.2611 | [8 empty] | Bromide | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L |  | --- | 140 | --- | 100 | #DIV/0! | #DIV/0! | Bromide | mg/L |  |  | 140 | --- | 100 | #DIV/0! | #DIV/0! | Bromide | mg/L |  | --- | 140 | --- | 100 | #DIV/0! | #DIV/0! | Ca-HdF, mg/L CaCO3 | 205 | 205 | 205 | 205 | Ca-HdF, mg/L CaCO3 | 205 | 205 | 205 | 205
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 17:40 | 32.1667 | 23 | 51.5 | 52.5 | 272 | 6.6 | 2.33 |  | 8.93 | 0.20821 | 0.73908 | 29.4591 | 15.0641 | 15.7937 | 358.4116 | 251.6418 | 355.8208 | 1.0547 | 50.9453 | 0.31001 | 7.68 | 7.97 | 8.23 | 231 | 281 | 325 | 416.882 | -28.2714 | 17.3524 | 414.6268 | 44.2872 | 0.034 | 0.565 | 1.093 | 2.0864 | -90.8844 | 94.0299 | 2.0615 | 98.3507 | [8 empty] | SDS-Cl2 dose | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | #DIV/0! | 0 | 0 | 0 | Ca-Hdp, mg/L CaCO3 | #DIV/0! | 0 | 0 | 0
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 1120 | 1070 | 1095 | 4.5662 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 18:00 | 32.5 | 23 | 48 | 49 | 272 | 6.11 | 4.38 |  | 10.49 | 0.20821 | 0.58246 | 24.9295 | 13.9457 | 14.6211 | 338.0864 | 237.5019 | 335.827 | 0.99455 | 47.5055 | 0.30778 | 8.11 | 8.24 | 8.34 | 240 | 281 | 333 | 334.6016 | -0.48096 | 14.1324 | 333.5391 | 28.0444 | 0.036 | 0.565 | 1.215 | 1.3137 | -8.1251 | 93.6787 | 1.2994 | 97.2294 | [8 empty] | SDS-Free Cl2 residual | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 19 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 450 | 360 | 405 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 18:20 | 32.8333 | 23 | 48 | 49 | 272 | 6.06 | 2.7 |  | 8.76 | 0.20821 | 0.69178 | 30.0502 | 13.8316 | 14.5015 | 351.92 | 247.2337 | 349.5877 | 1.0352 | 47.4648 | 0.30552 | 8.02 | 8.24 | 8.34 | 237 | 281 | 334 | 374.8889 | -12.2422 | 15.2057 | 373.3528 | 36.5212 | 0.034 | 0.555 | 1.253 | 1.7714 | -41.3727 | 94.0299 | 1.752 | 98.0594 | [8 empty] | SDS-Cl2 demand | mg/L |  | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-Cl2 demand | mg/L | 0 | --- | 12.51 | --- | 100 | #DIV/0! | #DIV/0! | SDS-Cl2 demand | mg/L |  |  | 12.51 | --- | 100 | #DIV/0! | #DIV/0! | SDS-Cl2 demand | mg/L | 0 | --- | 12.51 | --- | 100 | #DIV/0! | #DIV/0! | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | minus 10%, plus 25% | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 59 | 45 | 52 | 26.9231 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 18:40 | 33.1667 | 23 | 48 | 49 | 272 | 6.1 | 2.47 |  | 8.57 | 0.20821 | 0.71179 | 30.7386 | 13.9229 | 14.5972 | 354.5868 | 249.096 | 352.221 | 1.0431 | 47.4569 | 0.30759 | 7.69 | 8.36 | 8.36 | 238 | 281 | 336 | 381.9899 | -13.6875 | 14.8479 | 380.3753 | 37.4302 | 0.041 | 0.558 | 1.363 | 1.8747 | -37.5424 | 92.8007 | 1.8541 | 97.7887 | [8 empty] | SDS-Chlorination temp. | oC | NA | NA | #DIV/0! | #VALUE! | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | 84.4442 | 84.4442 | 84.4442 | Qp/QT (THM4), % | #DIV/0! | 92.2221 | 92.2221 | 92.2221
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | >99% 2000 ppm MgSO4 @ 67 psi | [13 empty] | SDS-DBCM | mg/L | 6.4 | 5.3 | 5.85 | 18.8034 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 8:45 | 47.25 | 23 | 48 | 49 | 272 | 5.22 | 1.13 |  | 6.35 | 0.20821 | 0.82205 | 41.8346 | 11.9144 | 12.4914 | 369.7064 | 259.9726 | 367.6005 | 1.0868 | 47.4132 | 0.26346 | 7.69 | 7.86 | 8.05 | 252 | 281 | 410 | 406.5354 | 0.84502 | 9.839 | 405.0525 | 37.7858 | 0.348 | 0.548 | 1.591 | 1.5927 | -0.10763 | 38.8938 | 1.5808 | 77.9854 | [8 empty] | SDS-Chlorination pH | --- | NA | NA | #DIV/0! | #VALUE! | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | #DIV/0! | 72 | 72 | 72 | SDS-THM4b, ug/L | #DIV/0! | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NDP or< 50% 500 ppm CaCl2 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 9:30 | 48 | 23 | 48 | 49 | 272 | 6.37 | 1.91 |  | 8.28 | 0.20821 | 0.76932 | 31.8502 | 14.5392 | 15.2433 | 362.535 | 254.6025 | 360.0073 | 1.0667 | 47.4333 | 0.32136 |  |  |  | 248 |  | 342 | 384.555 | -12.443 | 11.2701 | 382.956 | 35.2406 | 0.328 |  | 1.368 | 1.3749 | -0.50596 | 42.4056 | 1.3627 | 75.9295 | [8 empty] | SDS-Incubation time | hours | NA | NA | #DIV/0! | #VALUE! | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | #DIV/0! | 32.4338 | 32.4338 | 32.4338 | SDS-HAA5b, ug/L | #DIV/0! | 16.2169 | 16.2169 | 16.2169
|  | Variability of rejection of reference solute (%) | unknown | [13 empty] | SDS-THM4 | mg/L | 515.4 | 410.3 | 462.85 | 22.7071 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 10:15 | 48.75 | 23 | 48 | 49 | 272 | 6.46 | 3.53 |  | 9.99 | 0.20821 | 0.64665 | 26.2272 | 14.7446 | 15.4587 | 346.1569 | 243.076 | 343.7088 | 1.0186 | 47.4814 | 0.32557 | 8.04 | 8.09 | 8.36 | 260 | 281 | 328 | 315.1856 | 3.9068 | 6.9767 | 314.5302 | 17.337 | 0.293 | 0.556 | 1.165 | 1.0755 | 7.6822 | 48.5514 | 1.0662 | 72.5195 | [8 empty] | SDS-TOX | mg Cl- /L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L |  | --- | 1095 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L |  |  | 1095 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L |  | --- | 1095 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | #DIV/0! | 170.336 | 170.336 | 170.336 | SDS-TOXb, ug Cl- /L | #DIV/0! | 85.168 | 85.168 | 85.168
|  | Standard testing recovery (%) | 15 | [13 empty] | SDS-MCAA* | mg/L | 5.4 | 5.5 | 5.45 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 11:15 | 49.75 | 23 | 48 | 49 | 272 | 6.57 | 3.24 |  | 9.81 | 0.20821 | 0.66972 | 26.7268 | 14.9957 | 15.7219 | 349.1538 | 245.1502 | 346.6417 | 1.0275 | 47.4725 | 0.33118 | 8.28 | 8.26 | 8.33 | 253 | 281 | 327 | 333.2361 | -1.9071 | 9.4812 | 332.2671 | 23.8564 | 0.281 | 0.549 | 1.075 | 1.1545 | -7.3966 | 50.6585 | 1.144 | 75.4363 | [8 empty] | SDS-CHCl3 | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L |  | --- | 405 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L |  |  | 405 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L |  | --- | 405 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDb, mg/L | #DIV/0! | 1.946 | 1.946 | 1.946 | SDS-CDb, mg/L | #DIV/0! | 0.97302 | 0.97302 | 0.97302
|  | Standard testing pH | 7.0 + 0.3 | [13 empty] | SDS-DCAA* | mg/L | 100 | 110 | 105 | 9.5238 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 13:15 | 51.75 | 23 | 48 | 49 | 281 | 6.74 | 2.85 |  | 9.59 | 0.2151 | 0.70282 | 28.3014 | 15.3837 | 16.1287 | 353.4952 | 248.2112 | 350.9699 | 1.0402 | 47.4598 | 0.33984 | 7.74 | 8.07 | 8.33 | 268 | 281 | 320 | 306.6965 | 4.1573 | 4.1145 | 306.2324 | 12.4848 | 0.317 | 0.548 | 1.036 | 1.1666 | -12.6101 | 44.3371 | 1.1565 | 72.5885 | [8 empty] | SDS-BDCM | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L |  | --- | 52 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L |  |  | 52 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L |  | --- | 52 | --- | 100 | #DIV/0! | #DIV/0! | TOCb, mg/L | #DIV/0! | 1.8667 | 1.8667 | 1.8667 | TOCb, mg/L | #DIV/0! | 0.93335 | 0.93335 | 0.93335
|  | Acceptable range of operating pressures | < 105 psi | [13 empty] | SDS-TCAA* | mg/L | 83 | 110 | 96.5 | 27.9793 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 14:00 | 52.5 | 23 | 44 | 45 | 272 | 6.29 | 3.2 |  | 9.49 | 0.20821 | 0.6628 | 27.6617 | 14.3566 | 15.0519 | 348.1934 | 244.5526 | 345.7967 | 1.0244 | 43.4756 | 0.34621 | 8.14 | 8.23 | 8.26 | 262 | 281 | 321 | 313.8984 | 2.2123 | 6.2612 | 313.2984 | 16.3736 | 0.308 | 0.543 | 0.994 | 1.0835 | -9.0051 | 45.9175 | 1.0745 | 71.3367 | [8 empty] | SDS-DBCM | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L |  | --- | 5.85 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L |  |  | 5.85 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L |  | --- | 5.85 | --- | 100 | #DIV/0! | #DIV/0! | UV254 b, cm-1 | #DIV/0! | 0.08859 | 0.08859 | 0.08859 | UV254 b, cm-1 | #DIV/0! | 0.044295 | 0.044295 | 0.044295
|  | Acceptable range of operating pH values | 3-10 (2-11 cleaning) | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 15:15 | 53.75 | 23 | 40 | 41 | 272 | 5.83 | 2.44 |  | 8.27 | 0.20821 | 0.70496 | 31.89 | 13.3067 | 13.9511 | 353.6085 | 248.4837 | 351.3553 | 1.04 | 39.46 | 0.35355 | 7.9 | 8 | 7.94 | 266 | 281 | 315 | 311.7561 | 1.0298 | 4.8301 | 311.2658 | 14.5425 | 0.326 | 0.554 | 1.012 | 1.1513 | -13.7653 | 42.7568 | 1.1425 | 71.4651 | [8 empty] | SDS-CHBr3 | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  |  | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | #DIV/0! | 21.7781 | 21.7781 | 21.7781 | Bromideb, ug/L | #DIV/0! | 10.8891 | 10.8891 | 10.8891
|  | Typical pressure drop across a single element (psi) | 3 | [13 empty] | SDS-DBAA* | mg/L | 1.4 | 1.7 | 1.55 | 19.3548 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 16:15 | 54.75 | 23 | 40 | 41 | 272 | 5.91 | 2.11 |  | 8.02 | 0.20821 | 0.73691 | 32.9152 | 13.4893 | 14.1425 | 357.9307 | 251.4985 | 355.6182 | 1.0528 | 39.4472 | 0.35852 | 7.85 | 8.06 | 8.18 | 284 | 281 | 320 | 266.8957 | 16.5951 | -1.61 | 267.0816 | -6.3346 | 0.346 | 0.547 | 1.017 | 1.1955 | -17.5528 | 39.245 | 1.1863 | 70.8333 | [8 empty] | SDS-THM4 | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4 | mg/L | 0 | --- | 462.85 | --- | 100 | #DIV/0! | #DIV/0! | SDS-THM4 | mg/L |  |  | 462.85 | --- | 100 | #DIV/0! | #DIV/0! | SDS-THM4 | mg/L | 0 | --- | 462.85 | --- | 100 | #DIV/0! | #DIV/0! | Alkb, mg/L CaCO3 | #DIV/0! | 65.4899 | 65.4899 | 65.4899 | Alkb, mg/L CaCO3 | #DIV/0! | 32.7449 | 32.7449 | 32.7449
|  | Maximum permissible SDI | 5 | [13 empty] | SDS-BCAA* | mg/L | 14 | 15 | 14.5 | 6.8966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 17:15 | 55.75 | 23 | 38 | 39 | 272 | 5.6 | 2.35 |  | 7.95 | 0.20821 | 0.7044 | 33.2138 | 12.7817 | 13.4007 | 353.4779 | 248.4557 | 351.3157 | 1.0394 | 37.4606 | 0.35773 | 7.9 | 8.06 | 8.11 | 277 | 281 | 314 | 285.4574 | 9.09 | 0.89445 | 285.3704 | 2.9332 | 0.341 | 0.557 | 0.986 | 1.114 | -12.9828 | 40.1229 | 1.1061 | 69.1697 | [8 empty] | SDS-MCAA* | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  | --- | 5.45 | --- | 100 | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  |  | 5.45 | --- | 100 | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L |  | --- | 5.45 | --- | 100 | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | #DIV/0! | 33.7561 | 33.7561 | 33.7561 | T-Hdb, mg/L CaCO3 | #DIV/0! | 16.878 | 16.878 | 16.878
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | NR | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 8:10 | 70.6667 | 23 | 38 | 38.5 | 272 | 6.91 | 0.81 |  | 7.72 | 0.20821 | 0.89508 | 34.2332 | 15.7717 | 16.5355 | 381.2368 | 267.5743 | 378.3492 | 1.1222 | 37.1278 | 0.44537 | 7.37 |  |  | 279 | 280 |  | 283.7654 |  | 0.17889 | 283.7049 | 1.6584 | 0.505 | 0.56 | 0.794 | 1.1197 | -41.0253 | 11.3257 | 1.1119 | 54.5836 | [8 empty] | SDS-DCAA* | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  | --- | 105 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  |  | 105 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L |  | --- | 105 | --- | 100 | #DIV/0! | #DIV/0! | Ca-Hdb, mg/L CaCO3 | #DIV/0! | 31.8894 | 31.8894 | 31.8894 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | 15.9447 | 15.9447 | 15.9447
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hour | [13 empty] | SDS-CDBAA | mg/L | BMRL | 2.2 | 2.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 8:55 | 71.4167 | 23 | 38 | 38.5 | 272 | 6.97 | 2.33 |  | 9.3 | 0.20821 | 0.74946 | 28.2473 | 15.9087 | 16.6791 | 359.9398 | 252.6098 | 357.1895 | 1.0595 | 37.1905 | 0.44848 | 7.74 | 8.02 | 8.01 | 264 | 280 | 295 | 325.867 | -10.4634 | 5.5456 | 325.0743 | 18.7878 | 0.47 | 0.553 | 0.75 | 0.86715 | -15.6195 | 17.4715 | 0.86206 | 45.4793 | [8 empty] | SDS-TCAA* | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  | --- | 96.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  |  | 96.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L |  | --- | 96.5 | --- | 100 | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 12 | 12 | 12 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 10:45 | 73.25 | 23 | 37.5 | 38.5 | 272 | 7.07 | 2.49 |  | 9.56 | 0.20821 | 0.73954 | 27.4519 | 16.1369 | 16.9184 | 358.6004 | 251.6414 | 355.8203 | 1.0557 | 36.9443 | 0.45794 | 7.72 |  | 7.94 | 262 |  |  | 329.1888 |  | 6.2612 | 328.3155 | 20.1987 | 0.459 |  | 0.723 | 0.88325 | -22.1645 | 19.403 | 0.87774 | 47.7063 | [8 empty] | SDS-MBAA* | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  |  | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 189.8 | 227.2 | 208.5 | 17.9376 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 11:45 | 74.25 | 23 | 37.5 | 38.5 | 272 | 7.14 | 3.02 |  | 10.16 | 0.20821 | 0.70276 | 25.7717 | 16.2967 | 17.0859 | 353.6401 | 248.141 | 350.8707 | 1.0411 | 36.9589 | 0.4623 | 8.09 | 8.2 | 8.23 | 262 | 280 | 294 | 320.8742 | -9.1409 | 6.2612 | 320.1014 | 18.1509 | 0.459 | 0.552 | 0.709 | 0.83075 | -17.1718 | 19.403 | 0.82587 | 44.4222 | [8 empty] | SDS-DBAA* | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  | --- | 1.55 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  |  | 1.55 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L |  | --- | 1.55 | --- | 100 | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 203.8 | 242.2 | 223 | 17.2197 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Switched to the NTR7450 membrane on 12/8/98 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | [27 empty] | SDS-BCAA* | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  | --- | 14.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  |  | 14.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L |  | --- | 14.5 | --- | 100 | #DIV/0! | #DIV/0! | Qp/QT (HAA5), % | #DIV/0! | 74.1007 | 74.1007 | 74.1007 | Qp/QT (HAA5), % | #DIV/0! | 87.0504 | 87.0504 | 87.0504
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  |  | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | #DIV/0! | 119.8748 | 119.8748 | 119.8748 | SDS-THM4b, ug/L | #DIV/0! | 59.9374 | 59.9374 | 59.9374
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L |  | --- | 2.2 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L |  |  | 2.2 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L |  | --- | 2.2 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | #DIV/0! | 54 | 54 | 54 | SDS-HAA5b, ug/L | #DIV/0! | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L |  | --- | 12 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L |  |  | 12 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L |  | --- | 12 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | #DIV/0! | 283.5971 | 283.5971 | 283.5971 | SDS-TOXb, ug Cl- /L | #DIV/0! | 141.7986 | 141.7986 | 141.7986
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-HAA5 | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L | 0 | --- | 208.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L |  |  | 208.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L | 0 | --- | 208.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDb, mg/L | #DIV/0! | 3.24 | 3.24 | 3.24 | SDS-CDb, mg/L | #DIV/0! | 1.62 | 1.62 | 1.62
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-HAA6 | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L | 0 | --- | 223 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L |  |  | 223 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L | 0 | --- | 223 | --- | 100 | #DIV/0! | #DIV/0! | TOCb, mg/L | #DIV/0! | 3.1079 | 3.1079 | 3.1079 | TOCb, mg/L | #DIV/0! | 1.554 | 1.554 | 1.554
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.1475 | 0.1475 | 0.1475 | UV254 b, cm-1 | #DIV/0! | 0.073748 | 0.073748 | 0.073748
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | #DIV/0! | 36.259 | 36.259 | 36.259 | Bromideb, ug/L | #DIV/0! | 18.1295 | 18.1295 | 18.1295
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | #DIV/0! | 109.036 | 109.036 | 109.036 | Alkb, mg/L CaCO3 | #DIV/0! | 54.518 | 54.518 | 54.518
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | #DIV/0! | 56.2014 | 56.2014 | 56.2014 | T-Hdb, mg/L CaCO3 | #DIV/0! | 28.1007 | 28.1007 | 28.1007
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | #DIV/0! | 53.0935 | 53.0935 | 53.0935 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | 26.5468 | 26.5468 | 26.5468
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: C. Hill (7/30/99): NF200 was used during quarters 1, 2 and 3. NTR7450 was used during a second 3rd quarter and quarter 4.
Note on Q3: C. Rice 7/13/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Gary Puetz: Consultant verified that cartridge filtration was the only membrane pretreatment employed.

## 7450. 1st Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.15569 | [45 empty] | Recovery during sample collection (decimal) | 0.72 | [10 empty] | Recovery during sample collection (decimal) | [8 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | [9 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-11-23 | 1998-12-10 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 6.31 | [10 empty] | Feed flow rate during sample collection (mL/min) | [8 empty] | Feed flow rate during sample collection (mL/min) | 8.73 | [7 empty] | Feed flow rate during sample collection (mL/min) | [7 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:45 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | [8 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | [7 empty] | SDS-THM4F, ug/L | 462.85 | 462.85 | 462.85 | 462.85 | SDS-THM4F, ug/L | 462.85 | 462.85 | 462.85 | 462.85 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 53.25 | 0 | 77.4 | 0 | SDS-THM4p, ug/L | 53.25 | 0 | 77.4 | 0 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.59 | 8.36 | 7.975 | 9.6552 | 1998-12-07 | 12:30 | 0 | 25 | 63.5 | 64 |  | 2.82 | 3.87 | 6.69 | 0 | 0.42152 | -1 | 6.4365 | 6.3608 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-08 | 12:00 | 0 | 25 | 67 | 68.5 | 272 | 4.71 | 2.13 |  | 6.84 | 0.20791 | 0.6886 | 38.7661 | 10.7503 | 10.624 | 313.6218 | 264.0691 | 312.7637 | 0.49124 | 67.2588 | 0.15796 |  |  |  | 238 | 280 | 232 | 371.2676 | -60.0291 | 14.8479 | 370.1138 | 35.6954 | 0.054 | 0.527 | 0.567 | 1.7094 | -201.483 | 90.518 | 1.6951 | 96.8143 | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 208.5 | 208.5 | 208.5 | 208.5 | SDS-HAA5F, ug/L | 208.5 | 208.5 | 208.5 | 208.5 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 24 | 23.5 | 4.2553 | 1998-12-07 | 12:45 | 0.25 | 25 | 63.5 | 64 | 272 | 2.82 | 3.87 | 6.69 | 0.20791 | 0.42152 | 39.6577 | 6.4365 | 6.3608 | 0 | 0 | 0 | 0 | 63.75 | 0.099778 | 1998-12-08 | 12:30 | 0.5 | 25 | 67 | 68.5 | 272 | 4.68 | 2.01 |  | 6.69 | 0.20791 | 0.69955 | 39.6577 | 10.6818 | 10.5563 | 314.2284 | 264.5846 | 313.3742 | 0.49217 | 67.2578 | 0.15695 |  |  |  | 248 | 280 | 269 | 352.8433 | -31.1685 | 11.2701 | 351.9413 | 29.5337 | 0.081 | 0.531 | 0.794 | 1.7069 | -114.9752 | 85.777 | 1.6929 | 95.2154 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 12.25 | 0 | 13.5 | 0 | SDS-HAA5p, ug/L | 12.25 | 0 | 13.5 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 436 | 406 | 421 | 7.1259 | 1998-12-07 | 13:30 | 1 | 25 | 63 | 64 | 272 | 3 | 3.29 | 6.29 | 0.20791 | 0.47695 | 42.2432 | 6.8473 | 6.7669 | 0 | 0 | 0 | 0 | 63.5 | 0.10656 | 1998-12-08 | 13:30 | 1.5 | 25 | 67 | 68.5 | 272 | 4.72 | 1.93 |  | 6.65 | 0.20791 | 0.70977 | 39.9023 | 10.7731 | 10.6465 | 314.805 | 265.0638 | 313.9418 | 0.4931 | 67.2569 | 0.1583 |  |  |  | 263 | 280 | 285 | 319.8523 | -12.2289 | 5.9034 | 319.3591 | 17.6476 | 0.096 | 0.536 | 1.112 | 1.7275 | -55.3498 | 83.1431 | 1.7133 | 94.3969 | [8 empty] | Sampling date | MM/DD/YY | 1998-12-08 |  | --- | --- | 1998-12-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-09 | 1998-12-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1095 | 1095 | 1095 | 1095 | SDS-TOXF, ug Cl- /L | 1095 | 1095 | 1095 | 1095 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 281 | 278 | 279.5 | 1.0733 | 1998-12-07 | 14:15 | 1.75 | 25 | 71 | 72.5 | 272 | 4 | 3.69 | 7.69 | 0.20791 | 0.52016 | 34.3706 | 9.1298 | 9.0225 | 0 | 0 | 0 | 0 | 71.75 | 0.12575 | 1998-12-08 | 14:00 | 2 | 25 | 67 | 68.5 | 272 | 4.72 | 1.9 |  | 6.62 | 0.20791 | 0.71299 | 40.0876 | 10.7731 | 10.6465 | 314.9853 | 265.2157 | 314.1217 | 0.49338 | 67.2566 | 0.1583 |  |  |  | 265 | 280 | 288 | 315.5211 | -9.5559 | 5.1878 | 315.0827 | 15.8951 | 0.101 | 0.529 | 1.231 | 1.7334 | -40.8085 | 82.2651 | 1.7192 | 94.1251 | [8 empty] | Sampling time | hh:mm | 17:40 |  | --- | --- | 17:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:15 | 13:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 230 | 0 | 135 | 0 | SDS-TOXp, ug Cl- /L | 230 | 0 | 135 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 214 | 220 | 217 | 2.765 | 1998-12-07 | 15:10 | 2.6667 | 25 | 71 | 72.5 | 272 | 4.13 | 2.31 | 6.44 | 0.20791 | 0.6413 | 41.236 | 9.4265 | 9.3157 | 0 | 0 | 0 | 0 | 71.75 | 0.12984 | 1998-12-08 | 14:20 | 2.3333 | 25 | 67 | 68.5 | 272 | 4.72 | 1.87 |  | 6.59 | 0.20791 | 0.71624 | 40.2747 | 10.7731 | 10.6465 | 315.1675 | 265.369 | 314.3033 | 0.49366 | 67.2563 | 0.1583 |  |  |  | 265 | 280 | 289 | 316.0989 | -9.3768 | 5.1878 | 315.6556 | 16.0477 | 0.1 | 0.519 | 1.29 | 1.7545 | -36.0115 | 82.4407 | 1.7402 | 94.2535 | [8 empty] | Operation time | hh.hh | 5.67 |  | --- | --- | 5.67 | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh | 26.25 | 26.25 | --- | --- | --- | --- | --- | Cumulative time | hr |  |  | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 12.51 | 12.51 | 12.51 | 12.51 | SDS-CDF, mg/L | 12.51 | 12.51 | 12.51 | 12.51 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 204 | 206 | 205 | 0.97561 | 1998-12-07 | 16:15 | 3.75 | 25 | 71 | 72 | 272 | 4.24 | 2.18 | 6.42 | 0.20791 | 0.66044 | 41.3676 | 9.6776 | 9.5638 | 0 | 0 | 0 | 0 | 71.5 | 0.13376 | 1998-12-08 | 14:40 | 2.6667 | 25 | 67 | 68.5 | 272 | 4.73 | 1.86 |  | 6.59 | 0.20791 | 0.71775 | 40.2747 | 10.796 | 10.6691 | 315.254 | 265.4403 | 314.3877 | 0.49381 | 67.2562 | 0.15863 |  |  |  | 264 | 280 | 291 | 318.9167 | -9.5934 | 5.5456 | 318.4392 | 17.0956 | 0.102 | 0.54 | 1.338 | 1.7584 | -31.4169 | 82.0896 | 1.744 | 94.1512 | [8 empty] | pH | --- | 8.23 |  | 8.23 | 100 | 8.23 | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | --- | pH | --- | 8.35 | 8.23 | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.93 | 0 | 1.18 | 0 | SDS-CDp, mg/L | 0.93 | 0 | 1.18 | 0 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 53.9325 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.888 | 0.359 | 0.6235 | 84.8436 | 1998-12-07 | 17:05 | 4.5833 | 25 | 71 | 72 | 272 | 4.4 | 2.2 | 6.6 | 0.20791 | 0.66667 | 40.2121 | 10.0428 | 9.9247 | 0 | 0 | 0 | 0 | 71.5 | 0.13881 | 1998-12-08 | 16:00 | 4 | 25 | 68 | 69.5 | 272 | 4.8 | 1.86 |  | 6.66 | 0.20791 | 0.72072 | 39.8408 | 10.9557 | 10.827 | 315.4297 | 265.5773 | 314.5499 | 0.49413 | 68.2559 | 0.15862 |  |  |  | 265 | 280 | 291 | 316.9194 | -8.907 | 5.1878 | 316.4612 | 16.2615 | 0.1 |  | 1.456 | 1.7811 | -22.3292 | 82.4407 | 1.7663 | 94.3384 | [8 empty] | Temperature | oC | 25 |  | 25 | 100 | 25 | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | --- | TOCF, mg/L | 12 | 12 | 12 | 12 | TOCF, mg/L | 12 | 12 | 12 | 12 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 63.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-12-08 | 9:30 | 21 | 25 | 71 | 72 | 272 | 5.03 | 1.65 | 6.68 | 0.20791 | 0.75299 | 39.7186 | 11.4807 | 11.3458 | 0 | 0 | 0 | 0 | 71.5 | 0.15868 | 1998-12-08 | 16:30 | 4.5 | 25 | 68.5 | 70 | 272 | 4.89 | 2.33 |  | 7.22 | 0.20791 | 0.67729 | 36.6731 | 11.1612 | 11.03 | 313.0154 | 263.5305 | 312.1258 | 0.4904 | 68.7596 | 0.16041 | 8.43 | 8.39 | 8.28 | 264 | 280 | 295 | 312.03 | -5.7729 | 5.5456 | 311.5983 | 15.2755 | 0.1 | 0.54 | 1.446 | 1.5548 | -7.5274 | 82.4407 | 1.5418 | 93.5139 | [8 empty] | Alkalinity | mg/L as CaCO3 | 364 |  | 364 | 100 | 440 | 567.5714 | -28.9935 | 13.5392 | 565.8713 | 35.6744 | Alkalinity | mg/L as CaCO3 |  |  | 421 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 | 372 | 424 | 470 | -10.8491 | 11.639 | 469.2137 | 20.7184 | Alkalinity | mg/L as CaCO3 |  |  | 421 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | TOCp, mg/L | 3 | 0 | 1.9 | 0 | TOCp, mg/L | 3 | 0 | 1.9 | 0 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 51.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 12.3 | 11.7 | 12 | 5 | 1998-12-08 | 10:00 | 21.5 | 25 | 71 | 72 | 272 | 5.06 | 1.65 | 6.71 | 0.20791 | 0.7541 | 39.5365 | 11.5492 | 11.4134 | 0 | 0 | 0 | 0 | 71.5 | 0.15963 | 1998-12-08 | 17:40 | 5.6667 | 25 | 68 | 69.5 | 272 | 4.8 | 2.21 |  | 7.01 | 0.20791 | 0.68474 | 37.8017 | 10.9557 | 10.827 | 313.4181 | 263.8836 | 312.5439 | 0.49097 | 68.259 | 0.15862 | 8.38 | 8.35 | 8.28 | 265 | 280 | 291 | 310.9932 | -6.8705 | 5.1878 | 310.5874 | 14.6778 | 0.096 | 0.54 | 1.432 | 1.5979 | -11.5863 | 83.1431 | 1.5847 | 93.9419 | [8 empty] | Total dissolved solids | mg/L | 264 |  | 264 | 100 | 300 | 319.3571 | -6.4524 | 5.5456 | 318.8948 | 17.2141 | Total dissolved solids | mg/L |  |  | 279.5 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L | 262 | 292 | 297 | -1.7123 | 6.2612 | 296.7192 | 11.701 | Total dissolved solids | mg/L |  |  | 279.5 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 F, cm-1 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | UV254 F, cm-1 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 51.0754 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.613 | 0.526 | 0.5695 | 15.2766 | 1998-12-08 | 10:15 | 21.75 | 25 | 59.5 | 60.5 | 272 | 4.22 | 1.52 | 5.74 | 0.20791 | 0.73519 | 46.3868 | 9.6319 | 9.5187 | 0 | 0 | 0 | 0 | 60 | 0.15865 | 1998-12-09 | 8:30 | 20.5 | 25 | 67 | 68.5 | 272 | 4.38 | 1.57 |  | 5.95 | 0.20791 | 0.73613 | 44.7143 | 9.9971 | 9.8796 | 316.2442 | 266.3291 | 315.4404 | 0.49513 | 67.2549 | 0.1469 | 8.25 | 8.23 | 8.35 | 270 | 281 | 296 | 306.0032 | -3.3795 | 3.3989 | 305.7133 | 11.682 | 0.07 | 0.532 | 1.761 | 1.963 | -11.4713 | 87.7085 | 1.9478 | 96.4061 | [8 empty] | Total hardness | mg/L as CaCO3 | 206 |  | 206 | 100 | 264 | 245.2857 | 7.0887 | 5.0691 | 244.9576 | 15.9038 | Total hardness | mg/L as CaCO3 |  |  | 217 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 | 204 | 236 | 230 | 2.5424 | 5.9908 | 229.7914 | 11.2238 | Total hardness | mg/L as CaCO3 |  |  | 217 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 p, cm-1 | 0.081 | 0 | 0.05 | 0 | UV254 p, cm-1 | 0.081 | 0 | 0.05 | 0 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.9837 | 4.4957 | 4.7397 | 10.2962 | 1998-12-08 | 10:40 | 22.1667 | 25 | 49 | 50.5 | 272 | 3.42 | 1.2 | 4.62 | 0.20791 | 0.74026 | 57.8745 | 7.806 | 7.7142 | 0 | 0 | 0 | 0 | 49.75 | 0.15506 | 1998-12-09 | 9:00 | 21 | 23 | 67.5 | 69 | 272 | 4.4 | 1.56 |  | 5.96 | 0.20791 | 0.73826 | 44.6376 | 10.0428 | 10.5291 | 316.3667 | 266.4291 | 315.5588 | 0.49534 | 67.7547 | 0.1554 | 8.46 | 8.49 | 8.38 | 265 | 281 | 295 | 320.3974 | -8.6093 | 5.1878 | 319.9494 | 17.1744 | 0.069 | 0.54 | 1.76 | 1.9812 | -12.5663 | 87.8841 | 1.9657 | 96.4898 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 192 |  | 192 | 100 | 246 | 238.4286 | 3.0778 | 6.3415 | 238.0408 | 19.3416 | Calcium hardness | mg/L as CaCO3 |  |  | 205 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | 174 | 240 | 236 | 1.6667 | 15.122 | 235.5025 | 26.1154 | Calcium hardness | mg/L as CaCO3 |  |  | 205 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | 140 | 140 | 0 | 1998-12-08 | 11:00 | 22.5 | 25 | 78 | 79.5 | 272 | 5.75 | 2.11 | 7.86 | 0.20791 | 0.73155 | 33.6056 | 13.1241 | 12.9698 | 0 | 0 | 0 | 0 | 78.75 | 0.1647 | 1998-12-09 | 9:50 | 21.8333 | 23 | 67.5 | 69 | 272 | 4.42 | 4.86 |  | 9.28 | 0.20791 | 0.47629 | 28.3103 | 10.0884 | 10.577 | 302.223 | 254.515 | 301.4478 | 0.4732 | 67.7768 | 0.15606 | 8.49 | 8.44 | 8.45 | 260 | 280 | 295 | 297.2346 | -0.75748 | 6.9767 | 296.932 | 12.4379 | 0.06 | 0.539 | 1.477 | 1.0329 | 30.0696 | 89.4644 | 1.025 | 94.1462 | [8 empty] | Turbidity | ntu | 0.116 |  | 0.116 | 100 | 0.571 | 1.9285 | -237.7408 | 81.3953 | 1.9134 | 93.9374 | Turbidity | ntu |  |  | 0.6235 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Turbidity | ntu | 0.115 | 0.531 | 1.132 | -113.1827 | 81.5557 | 1.1238 | 89.7672 | Turbidity | ntu |  |  | 0.6235 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Bromidep, ug/L | 140 | 0 | 140 | 0 | Bromidep, ug/L | 140 | 0 | 140 | 0 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 17 | 11 | 14 | 42.8571 | 1998-12-08 | 11:20 | 22.8333 | 25 | 70 | 71 | 272 | 5.2 | 1.82 | 7.02 | 0.20791 | 0.74074 | 37.7464 | 11.8687 | 11.7292 | 0 | 0 | 0 | 0 | 70.5 | 0.16637 | 1998-12-09 | 10:10 | 22.1667 | 23 | 67.5 | 69 | 272 | 4.42 | 4.73 |  | 9.15 | 0.20791 | 0.48306 | 28.7268 | 10.0884 | 10.577 | 302.5725 | 254.8093 | 301.7963 | 0.47375 | 67.7762 | 0.15606 | 8.42 | 8.5 | 8.45 | 259 | 280 | 286 | 298.6564 | -4.4253 | 7.3345 | 298.3342 | 13.1846 | 0.051 | 0.525 | 1.245 | 1.054 | 15.3399 | 91.0448 | 1.0459 | 95.1237 | [8 empty] | Ammonia | mg NH3-N / L | BMRL |  | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 421 | 421 | 421 | 421 | AlkF, mg/L CaCO3 | 421 | 421 | 421 | 421
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.01 | 1.97 | 1.49 | 64.4295 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 10:30 | 22.5 | 23 | 67.5 | 69 | 272 | 4.42 | 4.66 |  | 9.08 | 0.20791 | 0.48678 | 28.9559 | 10.0884 | 10.577 | 302.7652 | 254.9716 | 301.9885 | 0.47405 | 67.7759 | 0.15606 | 8.59 | 8.54 | 8.44 | 257 | 280 | 289 | 300.8412 | -4.0973 | 8.0501 | 300.485 | 14.4716 | 0.051 | 0.534 | 1.144 | 1.0613 | 7.2294 | 91.0448 | 1.0531 | 95.1571 | [8 empty] | Total organic carbon | mg/L | 3 |  | 3 | 100 | 34.9 | 35.1429 | -0.69587 | 75 | 34.8744 | 91.3977 | Total organic carbon | mg/L |  |  | 12 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 1.9 | 23.5 | 22.1 | 5.9574 | 84.1667 | 21.9379 | 91.3392 | Total organic carbon | mg/L |  |  | 12 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | Alkp, mg/L CaCO3 | 364 | 0 | 372 | 0 | Alkp, mg/L CaCO3 | 364 | 0 | 372 | 0
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 15.99 | 9.03 | 12.51 | 55.6355 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 10:50 | 22.8333 | 23 | 67.5 | 69 | 272 | 4.4 | 4.58 |  | 8.98 | 0.20791 | 0.48998 | 29.2895 | 10.0428 | 10.5291 | 302.929 | 255.1125 | 302.1555 | 0.4743 | 67.7757 | 0.15535 | 8.56 | 8.56 | 8.45 | 260 | 280 | 288 | 298.2336 | -3.5533 | 6.9767 | 297.9244 | 12.7295 | 0.049 | 0.525 | 1.071 | 1.0695 | 0.13598 | 91.396 | 1.0613 | 95.383 | [8 empty] | UV254 | cm-1 | 0.081 |  | 0.081 | 100 | 1.574 | 1.8256 | -15.9875 | 85.777 | 1.8111 | 95.5275 | UV254 | cm-1 |  |  | 0.5695 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.05 | 1.008 | 1.089 | -8.0357 | 91.2204 | 1.0807 | 95.3732 | UV254 | cm-1 |  |  | 0.5695 | #DIV/0! | 100 | #DIV/0! | #DIV/0! | T-HdF, mg/L CaCO3 | 217 | 217 | 217 | 217 | T-HdF, mg/L CaCO3 | 217 | 217 | 217 | 217
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 11:10 | 23.1667 | 23 | 67 | 69 | 272 | 4.36 | 4.54 |  | 8.9 | 0.20791 | 0.48989 | 29.5618 | 9.9515 | 10.4334 | 302.9211 | 255.1119 | 302.1548 | 0.47426 | 67.5257 | 0.15451 | 8.58 | 8.55 | 8.54 | 253 | 280 | 286 | 304.9493 | -6.6256 | 9.4812 | 304.533 | 16.922 | 0.049 | 0.526 | 1.026 | 1.0694 | -4.2265 | 91.396 | 1.0612 | 95.3825 | [8 empty] | SUVA | L/(mg*m) | 2.7 | #DIV/0! | #DIV/0! | #DIV/0! | 4.51 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.6316 | 4.2894 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 206 | 0 | 204 | 0 | T-Hdp, mg/L CaCO3 | 206 | 0 | 204 | 0
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.79 | 8.98 | 8.885 | 2.1384 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 11:30 | 23.5 | 23 | 67 | 69 | 272 | 4.36 | 4.54 |  | 8.9 | 0.20791 | 0.48989 | 29.5618 | 9.9515 | 10.4334 | 302.9211 | 255.1119 | 302.1548 | 0.47426 | 67.5257 | 0.15451 | 8.22 | 8.52 | 8.49 | 264 | 281 | 287 | 294.3855 | -2.5733 | 5.5456 | 294.1419 | 10.2474 | 0.047 | 0.526 | 1.012 | 1.0713 | -5.8581 | 91.7471 | 1.0631 | 95.5789 | [8 empty] | Bromide | mg/L | 140 |  | 140 | 100 | --- | 140 | --- | 0 | 140 | 0 | Bromide | mg/L |  | --- | 140 | --- | 100 | #DIV/0! | #DIV/0! | Bromide | mg/L | 140 | --- | 140 | --- | 0 | 140 | 0 | Bromide | mg/L |  | --- | 140 | --- | 100 | #DIV/0! | #DIV/0! | Ca-HdF, mg/L CaCO3 | 205 | 205 | 205 | 205 | Ca-HdF, mg/L CaCO3 | 205 | 205 | 205 | 205
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 12:00 | 24 | 23 | 67.5 | 69 | 272 | 4.4 | 4.44 |  | 8.84 | 0.20791 | 0.49774 | 29.7692 | 10.0428 | 10.5291 | 303.3317 | 255.4517 | 302.5572 | 0.47493 | 67.7751 | 0.15535 | 8.38 | 8.5 | 8.59 | 263 | 282 | 289 | 295.8514 | -2.3707 | 5.9034 | 295.5856 | 11.0241 | 0.047 | 0.537 | 1.008 | 1.0873 | -7.8663 | 91.7471 | 1.0789 | 95.6436 | [8 empty] | SDS-Cl2 dose | mg/L | 3 |  | 3 | 100 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L |  | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 192 | 0 | 174 | 0 | Ca-Hdp, mg/L CaCO3 | 192 | 0 | 174 | 0
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 1120 | 1070 | 1095 | 4.5662 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 13:00 | 25 | 23 | 67.5 | 69 | 272 | 4.36 | 4.36 |  | 8.72 | 0.20791 | 0.5 | 30.1927 | 9.9515 | 10.4334 | 303.446 | 255.554 | 302.6783 | 0.47508 | 67.7749 | 0.15394 | 8.43 | 8.55 | 8.48 | 265 | 282 | 289 | 294 | -1.7301 | 5.1878 | 293.7676 | 9.7926 | 0.047 | 0.529 | 0.996 | 1.092 | -9.6386 | 91.7471 | 1.0836 | 95.6627 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.14 |  | 1.14 | 100 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.82 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L |  | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 450 | 360 | 405 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 14:00 | 26 | 24 | 67.5 | 68.5 | 272 | 4.36 | 4.08 |  | 8.44 | 0.20791 | 0.51659 | 31.2275 | 9.9515 | 10.1295 | 304.311 | 256.2824 | 303.5411 | 0.47644 | 67.5236 | 0.15001 | 8.42 | 8.55 | 8.55 | 259 | 281 | 284 | 301.4069 | -6.1292 | 7.3345 | 301.067 | 13.9726 | 0.046 | 0.531 | 1.012 | 1.1289 | -11.554 | 91.9227 | 1.1202 | 95.8938 | [8 empty] | SDS-Cl2 demand | mg/L | 1.86 | 0 | 0.93 | 200 | --- | 42.2871 | --- | 92.5659 | 41.9417 | 97.7826 | SDS-Cl2 demand | mg/L | 0 | --- | 12.51 | --- | 100 | #DIV/0! | #DIV/0! | SDS-Cl2 demand | mg/L | 1.18 | --- | 23.84 | --- | 90.5675 | 23.6582 | 95.0123 | SDS-Cl2 demand | mg/L | 0 | --- | 12.51 | --- | 100 | #DIV/0! | #DIV/0! | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 59 | 45 | 52 | 26.9231 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 15:00 | 27 | 24 | 67.5 | 68.5 | 272 | 4.4 | 3.96 |  | 8.36 | 0.20791 | 0.52632 | 31.5359 | 10.0428 | 10.2225 | 304.824 | 256.7084 | 304.0457 | 0.47726 | 67.5227 | 0.15139 | 8.57 | 8.41 | 8.48 | 263 | 280 | 285 | 297.8333 | -4.5029 | 5.9034 | 297.5516 | 11.612 | 0.047 | 0.536 | 1.032 | 1.1501 | -11.4395 | 91.7471 | 1.1411 | 95.8813 | [8 empty] | SDS-Chlorination temp. | oC | 25 |  | 25 | 100 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC |  | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 95.4224 | 84.4442 | 101.401 | 84.4442 | Qp/QT (THM4), % | 104.2114 | 92.2221 | 110.7407 | 92.2221
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 6.4 | 5.3 | 5.85 | 18.8034 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 16:00 | 28 | 24 | 68 | 69 | 272 | 4.42 | 5.13 |  | 9.55 | 0.20791 | 0.46283 | 27.4817 | 10.0884 | 10.2689 | 301.5299 | 253.9313 | 300.7565 | 0.47212 | 68.0279 | 0.15095 | [27 empty] | SDS-Chlorination pH | --- | 9.19 |  | 9.19 | 100 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.18 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- |  | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | NA | 72 | SDS-THM4b, ug/L | NA | 36 | NA | 36
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-09 | 17:20 | 29.3333 | 24 | 68 | 69 | 272 | 4.4 | 4.16 |  | 8.56 | 0.20791 | 0.51402 | 30.7757 | 10.0428 | 10.2225 | 304.1801 | 256.1661 | 303.4034 | 0.47626 | 68.0237 | 0.15028 |  |  |  | 256 |  |  | 304.3558 |  | 8.4079 | 303.9647 | 15.7797 | 0.045 |  | 1.017 | 1.1243 | -10.5467 | 92.0983 | 1.1155 | 95.966 | [8 empty] | SDS-Incubation time | hours | 24 |  | 24 | 100 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours |  | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 21.2336 | 32.4338 | NA | 32.4338 | SDS-HAA5b, ug/L | NA | 16.2169 | NA | 16.2169
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 515.4 | 410.3 | 462.85 | 22.7071 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 8:30 | 44.5 | 24 | 67.5 | 69 | 272 | 4.32 | 3.68 |  | 8 | 0.20791 | 0.54 | 33 | 9.8602 | 10.0366 | 305.5366 | 257.3207 | 304.7708 | 0.47833 | 67.7717 | 0.14809 | 8.3 | 8.2 | 8.2 | 264 | 280 | 285 | 297.6957 | -4.4546 | 5.5456 | 297.4281 | 11.239 | 0.045 | 0.542 | 1.077 | 1.1852 | -10.048 | 92.0983 | 1.1762 | 96.174 | [8 empty] | SDS-TOX | mg Cl- /L | 230 |  | 230 | 100 | --- | 3319.2857 | --- | 78.9954 | 3293.4856 | 93.0165 | SDS-TOX | mg Cl- /L |  | --- | 1095 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | 135 | --- | 2055 | --- | 87.6712 | 2039.5941 | 93.381 | SDS-TOX | mg Cl- /L |  | --- | 1095 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 269.5966 | 170.336 | NA | 170.336 | SDS-TOXb, ug Cl- /L | NA | 85.168 | NA | 85.168
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 5.4 | 5.5 | 5.45 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 9:00 | 45 | 24 | 67.5 | 69 | 272 | 4.32 | 3.68 | X | 8 | 0.20791 | 0.54 | 33 | 9.8602 | 10.0366 | 305.5366 | 257.3207 | 304.7708 | 0.47833 | 67.7717 | 0.14809 | 8.36 |  | 8.31 | 261 |  | 288 | 301.2174 | -4.5894 | 6.619 | 300.898 | 13.2596 | 0.043 |  | 1.094 | 1.1876 | -8.5526 | 92.4495 | 1.1785 | 96.3512 | [8 empty] | SDS-CHCl3 | mg/L | 49 |  | 49 | 100 | --- | 1320.4286 | --- | 87.9012 | 1309.8103 | 96.259 | SDS-CHCl3 | mg/L |  | --- | 405 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 21 | --- | 789 | --- | 94.8148 | 782.8376 | 97.3175 | SDS-CHCl3 | mg/L |  | --- | 405 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDb, mg/L | 1.4601 | 1.946 | NA | 1.946 | SDS-CDb, mg/L | NA | 0.97302 | NA | 0.97302
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | 100 | 110 | 105 | 9.5238 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 11:45 |  | 24 | 66.5 | 68 | 263 | 3.95 | 12.2 |  | 16.15 | 0.20103 | 0.24458 | 15.2848 | 9.0157 | 9.177 | 290.7123 | 244.8696 | 290.0238 | 0.45498 | 66.795 | 0.13739 | [27 empty] | SDS-BDCM | mg/L | 32 |  | 32 | 100 | --- | 103.4286 | --- | 38.4615 | 102.832 | 68.8813 | SDS-BDCM | mg/L |  | --- | 52 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | 23 | --- | 81 | --- | 55.7692 | 80.5346 | 71.4409 | SDS-BDCM | mg/L |  | --- | 52 | --- | 100 | #DIV/0! | #DIV/0! | TOCb, mg/L | 3.412 | 1.8667 | NA | 1.8667 | TOCb, mg/L | NA | 0.93335 | NA | 0.93335
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 83 | 110 | 96.5 | 27.9793 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 12:10 |  | 24 | 76.5 | 78 | 263 | 4.69 | 13.83 |  | 18.52 | 0.20103 | 0.25324 | 13.2009 | 10.7047 | 10.8962 | 291.1549 | 245.1317 | 290.3342 | 0.45613 | 76.7939 | 0.14189 | [27 empty] | SDS-DBCM | mg/L | 21 |  | 21 | 100 | --- | -33.1071 | --- | -258.9744 | -32.6553 | 164.3082 | SDS-DBCM | mg/L |  | --- | 5.85 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 24 | --- | -12.3 | --- | -310.2564 | -12.0087 | 299.8546 | SDS-DBCM | mg/L |  | --- | 5.85 | --- | 100 | #DIV/0! | #DIV/0! | UV254 b, cm-1 | 0.10336 | 0.08859 | NA | 0.08859 | UV254 b, cm-1 | NA | 0.044295 | NA | 0.044295
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 12:30 |  | 24 | 56 | 56.5 | 263 | 3.4 | 9.69 |  | 13.09 | 0.20103 | 0.25974 | 19.0917 | 7.7603 | 7.8992 | 291.4146 | 245.5432 | 290.8216 | 0.45575 | 55.7943 | 0.14158 | [27 empty] | SDS-CHBr3 | mg/L | 4.5 |  | 4.5 | 100 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 9.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 140 | 21.7781 | NA | 21.7781 | Bromideb, ug/L | NA | 10.8891 | NA | 10.8891
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 1.4 | 1.7 | 1.55 | 19.3548 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 12:50 |  | 24 | 46 | 47 | 263 | 2.71 | 7.8 |  | 10.51 | 0.20103 | 0.25785 | 24.0238 | 6.1854 | 6.2961 | 291.2967 | 245.5463 | 290.8253 | 0.45515 | 46.0449 | 0.13674 | [27 empty] | SDS-THM4 | mg/L | 106.5 | 0 | 53.25 | 200 | --- | 1516.1071 | --- | 88.4952 | 1503.8901 | 96.4592 | SDS-THM4 | mg/L | 0 | --- | 462.85 | --- | 100 | #DIV/0! | #DIV/0! | SDS-THM4 | mg/L | 77.4 | --- | 848.3 | --- | 83.2775 | 842.1144 | 90.8088 | SDS-THM4 | mg/L | 0 | --- | 462.85 | --- | 100 | #DIV/0! | #DIV/0! | Alkb, mg/L CaCO3 | 366.6093 | 65.4899 | NA | 65.4899 | Alkb, mg/L CaCO3 | NA | 32.7449 | NA | 32.7449
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 14 | 15 | 14.5 | 6.8966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 13:15 |  | 24 | 67 | 68 | 263 | 4.2 | 11.73 |  | 15.93 | 0.20103 | 0.26365 | 15.5097 | 9.5863 | 9.7578 | 291.6348 | 245.6092 | 290.8998 | 0.45658 | 67.0434 | 0.14554 | [27 empty] | SDS-MCAA* | mg/L | 2.1 |  | 2.1 | 100 | --- | 14.0643 | --- | 61.4679 | 13.9644 | 84.9617 | SDS-MCAA* | mg/L |  | --- | 5.45 | --- | 100 | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L |  | --- | 5.45 | --- | 100 | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 206.5035 | 33.7561 | NA | 33.7561 | T-Hdb, mg/L CaCO3 | NA | 16.878 | NA | 16.878
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | NR | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 14:15 |  | 24 | 67 | 68 | 263 | 4.2 | 9.2 |  | 13.4 | 0.20103 | 0.31343 | 18.6269 | 9.5863 | 9.7578 | 294.0452 | 247.6392 | 293.3041 | 0.46035 | 67.0396 | 0.14555 | [27 empty] | SDS-DCAA* | mg/L | 12 |  | 12 | 100 | --- | 344.1429 | --- | 88.5714 | 341.369 | 96.4847 | SDS-DCAA* | mg/L |  | --- | 105 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 5.8 | --- | 204.2 | --- | 94.4762 | 202.6081 | 97.1373 | SDS-DCAA* | mg/L |  | --- | 105 | --- | 100 | #DIV/0! | #DIV/0! | Ca-Hdb, mg/L CaCO3 | 192.5951 | 31.8894 | NA | 31.8894 | Ca-Hdb, mg/L CaCO3 | NA | 15.9447 | NA | 15.9447
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | BMRL | 2.2 | 2.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-10 | 15:15 |  | 24 | 67 | 68 | 263 | 4.25 | 8.9 |  | 13.15 | 0.20103 | 0.32319 | 19 | 9.7004 | 9.874 | 294.525 | 248.0358 | 293.7738 | 0.46114 | 67.0389 | 0.14729 | [27 empty] | SDS-TCAA* | mg/L | 5.3 |  | 5.3 | 100 | --- | 331.0143 | --- | 94.5078 | 328.2941 | 98.3856 | SDS-TCAA* | mg/L |  | --- | 96.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 2 | --- | 191 | --- | 97.9275 | 189.4835 | 98.9445 | SDS-TCAA* | mg/L |  | --- | 96.5 | --- | 100 | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 12 | 12 | 12 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-MBAA* | mg/L | BMRL |  | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 189.8 | 227.2 | 208.5 | 17.9376 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-DBAA* | mg/L | 5.1 |  | 5.1 | 100 | --- | -7.5786 | --- | -229.0323 | -7.4727 | 168.2485 | SDS-DBAA* | mg/L |  | --- | 1.55 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 5.7 | --- | -2.6 | --- | -267.7419 | -2.5334 | 324.9939 | SDS-DBAA* | mg/L |  | --- | 1.55 | --- | 100 | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 203.8 | 242.2 | 223 | 17.2197 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-BCAA* | mg/L | 8.5 |  | 8.5 | 100 | --- | 29.9286 | --- | 41.3793 | 29.7496 | 71.4282 | SDS-BCAA* | mg/L |  | --- | 14.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 5.5 | --- | 23.5 | --- | 62.069 | 23.3556 | 76.451 | SDS-BCAA* | mg/L |  | --- | 14.5 | --- | 100 | #DIV/0! | #DIV/0! | Qp/QT (HAA5), % | 78.7261 | 74.1007 | 79.2308 | 74.1007 | Qp/QT (HAA5), % | 92.4841 | 87.0504 | 93.0769 | 87.0504
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-TBAA | mg/L | NR |  | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L |  | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 140.3878 | 119.8748 | 157.455 | 119.8748 | SDS-THM4b, ug/L | 84.0352 | 59.9374 | 104.085 | 59.9374
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-CDBAA | mg/L | 2.8 |  | 2.8 | 100 | --- | 0.65714 | --- | -27.2727 | 0.67504 | -314.7909 | SDS-CDBAA | mg/L |  | --- | 2.2 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.5 | --- | 1.9 | --- | -13.6364 | 1.9048 | -31.2464 | SDS-CDBAA | mg/L |  | --- | 2.2 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [10 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-DCBAA | mg/L | 4.4 |  | 4.4 | 100 | --- | 31.5429 | --- | 63.3333 | 31.3162 | 85.9498 | SDS-DCBAA | mg/L |  | --- | 12 | --- | 100 | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | 2.7 | --- | 21.3 | --- | 77.5 | 21.1508 | 87.2345 | SDS-DCBAA | mg/L |  | --- | 12 | --- | 100 | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 414.0191 | 283.5971 | 334.3846 | 283.5971 | SDS-TOXb, ug Cl- /L | 295.0127 | 141.7986 | 201.4615 | 141.7986
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-HAA5 | mg/L | 24.5 | 0 | 12.25 | 200 | --- | 713.1429 | --- | 94.1247 | 707.2894 | 98.268 | SDS-HAA5 | mg/L | 0 | --- | 208.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L | 13.5 | --- | 403.5 | --- | 93.5252 | 400.3707 | 96.6281 | SDS-HAA5 | mg/L | 0 | --- | 208.5 | --- | 100 | #DIV/0! | #DIV/0! | SDS-CDb, mg/L | 3.3935 | 3.24 | 3.5332 | 3.24 | SDS-CDb, mg/L | 1.8003 | 1.62 | 1.9644 | 1.62
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-HAA6 | mg/L | 33 | 0 | 16.5 | 200 | --- | 754 | --- | 92.6009 | 747.8408 | 97.7936 | SDS-HAA6 | mg/L | 0 | --- | 223 | --- | 100 | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L | 19 | --- | 427 | --- | 91.4798 | 423.7262 | 95.516 | SDS-HAA6 | mg/L | 0 | --- | 223 | --- | 100 | #DIV/0! | #DIV/0! | TOCb, mg/L | 4.9146 | 3.1079 | 3.9977 | 3.1079 | TOCb, mg/L | 3.6764 | 1.554 | 2.5992 | 1.554
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.18492 | 0.1475 | 0.1579 | 0.1475 | UV254 b, cm-1 | 0.11772 | 0.073748 | 0.085965 | 0.073748
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 140 | 36.259 | 140 | 36.259 | Bromideb, ug/L | 140 | 18.1295 | 140 | 18.1295
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | 376.1261 | 109.036 | 382.1769 | 109.036 | Alkb, mg/L CaCO3 | 368.2841 | 54.518 | 375.3923 | 54.518
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | 208.3401 | 56.2014 | 206.7 | 56.2014 | T-Hdb, mg/L CaCO3 | 206.8268 | 28.1007 | 204.9 | 28.1007
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | 194.7656 | 53.0935 | 180.4385 | 53.0935 | Ca-Hdb, mg/L CaCO3 | 192.9771 | 26.5468 | 176.1462 | 26.5468
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: C. Hill (7/30/99): NF200 was used during quarters 1, 2 and 3. NTR7450 was used during a second 3rd quarter and quarter 4.
Note on Q3: C. Rice 7/13/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Gary Puetz: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X20: C. Rice 7/19/99: All bromide concentrations verified by consultant.
Note on CY3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were lower during this quarter, compared to the 4th quarter.
Note on CY25: C. Rice 7/19/99: All bromide concentrations verified by consultant.
Note on DL3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were lower during this quarter, compared to the 4th quarter.
Note on DL25: Alison Gusses: All bromide concentrations were verified by consultant
Note on DV3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were lower during this quarter, compared to the 4th quarter.
Note on DV25: Alison Gusses: All bromide concentrations were verified by consultant
Note on EF3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were lower during this quarter, compared to the 4th quarter.
Note on EF25: Alison Gusses: All bromide concentrations were verified by consultant

## 7450. 2nd Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.14075 | [45 empty] | Recovery during sample collection (decimal) | 0.69587 | [10 empty] | Recovery during sample collection (decimal) | 0.86563 | [7 empty] | Recovery during sample collection (decimal) | 0.49656 | [7 empty] | Recovery during sample collection (decimal) | 0.30232 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1999-04-01 | 1999-04-09 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.651 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.9029 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.682 | [7 empty] | Feed flow rate during sample collection (mL/min) | 17.1075 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 0:00 | 0:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 276.7143 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [6 empty] | SDS-THM4F, ug/L | 539.45 | 539.45 | 539.45 | 539.45 | SDS-THM4F, ug/L | 539.45 | 539.45 | 539.45 | 539.45 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 154.45 | 207.6 | 138.5 | 133 | SDS-THM4p, ug/L | 154.45 | 207.6 | 138.5 | 133 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.3 | 7.9 | 8.1 | 4.9383 | 1999-04-02 | 10:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 10:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 131.2 | 131.2 | 131.2 | 131.2 | SDS-HAA5F, ug/L | 131.2 | 131.2 | 131.2 | 131.2 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1999-04-02 | 10:30 | 0.5 | 24 | 50 | 51 | 272 | 7.27 | 1.9 | 9.17 | 0.20791 | 0.7928 | 28.6619 | 16.5934 | 16.8903 | 0 | 0 | 0 | 0 | 50.5 | 0.33446 | 1999-04-03 | 11:00 | 1 | 24 | 43 | 44 | 272 | 6.48 | 0.71 |  | 7.19 | 0.20791 | 0.90125 | 36.8303 | 14.7903 | 15.0549 | 336.5892 | 288.224 | 335.437 | 0.47789 | 43.0221 | 0.34993 |  |  |  | 242 | 292 |  | 758.4648 |  | 17.4061 | 752.3128 | 67.8325 | 0.07 | 0.578 |  | 5.3157 |  | 88.0952 | 5.2532 | 98.6675 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 47.2 | 71.5 | 42.5 | 37 | SDS-HAA5p, ug/L | 47.2 | 71.5 | 42.5 | 37 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 350 | 346 | 348 | 1.1494 | 1999-04-02 | 10:45 | 0.75 | 24 | 45 | 46 | 272 | 6.52 | 0.85 | 7.37 | 0.20791 | 0.88467 | 35.9064 | 14.8816 | 15.1478 | 0 | 0 | 0 | 0 | 45.5 | 0.33292 | 1999-04-03 | 12:00 | 2 | 24 | 43 | 44 | 272 | 6.34 | 4.84 |  | 11.18 | 0.20791 | 0.56708 | 23.3292 | 14.4707 | 14.7296 | 318.9805 | 273.1663 | 317.9127 | 0.4528 | 43.0472 | 0.34217 |  |  |  | 260 | 292 | 292 | 336.2273 | -15.1463 | 11.2628 | 335.3389 | 22.4665 | 0.096 | 0.58 | 0.969 | 1.2325 | -27.1909 | 83.6735 | 1.2192 | 92.1262 | [8 empty] | Sampling date | MM/DD/YY | 1999-04-04 | 1999-04-05 | --- | --- | 1999-04-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-06 | 1999-04-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-07 | 1999-04-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-08 | 1999-04-08 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1665 | 1665 | 1665 | 1665 | SDS-TOXF, ug Cl- /L | 1665 | 1665 | 1665 | 1665 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 293 | 293 | 293 | 0 | 1999-04-02 | 11:30 | 1.5 | 24 | 45 | 46 | 272 | 6.53 | 1.29 | 7.82 | 0.20791 | 0.83504 | 33.7826 | 14.9044 | 15.1711 | 0 | 0 | 0 | 0 | 45.5 | 0.33343 | 1999-04-03 | 13:00 | 3 | 24 | 43 | 44 | 272 | 6.53 | 2.84 |  | 9.37 | 0.20791 | 0.69691 | 28.0288 | 14.9044 | 15.1711 | 325.6119 | 278.8166 | 324.4885 | 0.46234 | 43.0377 | 0.35251 |  |  |  | 269 | 292 | 303 | 348.1831 | -14.9119 | 8.1911 | 347.2326 | 22.5303 | 0.091 | 0.578 | 1.106 | 1.7308 | -56.4873 | 84.5238 | 1.7111 | 94.6817 | [8 empty] | Sampling time | hh:mm | 12:00 | 10:00 | --- | --- | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 18:00 | 18:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 352.5 | 530 | 335 | 300 | SDS-TOXp, ug Cl- /L | 352.5 | 530 | 335 | 300 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 298 | 292 | 295 | 2.0339 | 1999-04-02 | 12:00 | 2 | 24 | 45 | 46 | 272 | 6.93 | 3.86 | 10.79 | 0.20791 | 0.64226 | 24.2085 | 15.8174 | 16.1004 | 0 | 0 | 0 | 0 | 45.5 | 0.35385 | 1999-04-03 | 14:00 | 4 | 24 | 43 | 44 | 272 | 6.49 | 2.55 |  | 9.04 | 0.20791 | 0.71792 | 29.0885 | 14.8131 | 15.0781 | 326.7036 | 279.7574 | 325.5835 | 0.46386 | 43.0361 | 0.35036 |  |  |  | 277 | 293 | 307 | 333.7216 | -8.7041 | 5.4608 | 333.0449 | 16.828 | 0.097 | 0.578 | 1.219 | 1.8376 | -50.7501 | 83.5034 | 1.8169 | 94.6612 | [8 empty] | Operation time | hh.hh | 26 | 48 | --- | --- | 26 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80 | 80 | --- | --- | --- | --- | --- | Operation time | hh.hh | 102.5 | 102.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 122 | 122 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 16.045 | 16.045 | 16.045 | 16.045 | SDS-CDF, mg/L | 16.045 | 16.045 | 16.045 | 16.045 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 272 | 268 | 270 | 1.4815 | 1999-04-02 | 13:00 | 3 | 24 | 45 | 46 | 272 | 7 | 3.2 | 10.2 | 0.20791 | 0.68627 | 25.6667 | 15.9771 | 16.263 | 0 | 0 | 0 | 0 | 45.5 | 0.35743 | 1999-04-03 | 15:00 | 5 | 24 | 43 | 44 | 272 | 6.46 | 1.37 |  | 7.83 | 0.20791 | 0.82503 | 33.7382 | 14.7446 | 15.0084 | 332.4041 | 284.6434 | 331.2698 | 0.47194 | 43.0281 | 0.34881 |  |  |  | 275 | 294 | 308 | 377.8759 | -22.687 | 6.1433 | 376.6543 | 26.9887 | 0.108 | 0.579 | 1.455 | 2.8514 | -95.9696 | 81.6327 | 2.8188 | 96.1686 | [8 empty] | pH | --- | 8 | 8 | 8 | 0 | 8 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.2 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 8 | 8.1 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.375 | 5.7 | 3.9 | 3.6 | SDS-CDp, mg/L | 4.375 | 5.7 | 3.9 | 3.6 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 53.9325 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.267 | 0.248 | 0.2575 | 7.3786 | 1999-04-02 | 13:45 | 3.75 | 24 | 45 | 46 | 272 | 6.99 | 2.97 | 9.96 | 0.20791 | 0.70181 | 26.3092 | 15.9543 | 16.2398 | 0 | 0 | 0 | 0 | 45.5 | 0.35692 | 1999-04-03 | 16:00 | 6 | 24 | 43 | 44 | 272 | 6.51 | 3.85 |  | 10.36 | 0.20791 | 0.62838 | 25.2548 | 14.8587 | 15.1246 | 322.0848 | 275.7993 | 320.977 | 0.45732 | 43.0427 | 0.35139 |  |  |  | 271 | 293 | 308 | 330.2 | -7.2078 | 7.5085 | 329.4916 | 17.7521 | 0.098 | 0.6 | 1.408 | 1.4165 | -0.60692 | 83.3333 | 1.4008 | 93.0038 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 12.6 | 12.6 | 12.6 | 12.6 | TOCF, mg/L | 12.6 | 12.6 | 12.6 | 12.6 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 63.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.08 | BMRL | 0.08 | #VALUE! | 1999-04-02 | 14:30 | 4.5 | 24 | 45 | 46 | 272 | 7 | 2.22 | 9.22 | 0.20791 | 0.75922 | 28.5011 | 15.9771 | 16.263 | 0 | 0 | 0 | 0 | 45.5 | 0.35743 | 1999-04-03 | 17:00 | 7 | 24 | 43 | 44 | 272 | 6.66 | 2.43 |  | 9.09 | 0.20791 | 0.73267 | 28.923 | 15.2011 | 15.4731 | 327.4989 | 280.4126 | 326.346 | 0.4651 | 43.0349 | 0.35955 |  |  |  | 271 | 292 | 310 | 353.2963 | -13.9665 | 7.5085 | 352.2888 | 23.0745 | 0.099 | 0.595 | 1.425 | 1.9282 | -35.3138 | 83.1633 | 1.9058 | 94.8054 | [8 empty] | Alkalinity | mg/L as CaCO3 | 326 | 311 | 318.5 | 4.7096 | 399 | 415.4986 | -4.135 | 8.477 | 414.4435 | 23.15 | Alkalinity | mg/L as CaCO3 | 350 | 492 | 335.1162 | 31.8869 | -0.57471 | 335.256 | -4.3978 | Alkalinity | mg/L as CaCO3 | 298 | 376 | 397.316 | -5.6691 | 14.3678 | 396.3786 | 24.8194 | Alkalinity | mg/L as CaCO3 | 284 | 352 | 375.7331 | -6.7424 | 18.3908 | 374.8889 | 24.2442 | TOCp, mg/L | 4.75 | 7.2 | 4.2 | 3.6 | TOCp, mg/L | 4.75 | 7.2 | 4.2 | 3.6 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 51.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 12.7 | 12.5 | 12.6 | 1.5873 | 1999-04-02 | 17:00 | 7 | 24 | 45 | 46 | 263 | 6.8 | 1.9 | 8.7 | 0.20103 | 0.78161 | 29.2299 | 15.5206 | 15.7984 | 0 | 0 | 0 | 0 | 45.5 | 0.34722 | 1999-04-03 | 18:00 | 8 | 24 | 43 | 44 | 272 | 6.63 | 1.92 |  | 8.55 | 0.20791 | 0.77544 | 30.8129 | 15.1326 | 15.4034 | 329.7612 | 282.3542 | 328.6057 | 0.46829 | 43.0317 | 0.35795 |  |  |  | 275 | 292 | 311 | 355.1562 | -14.1982 | 6.1433 | 354.1793 | 22.3557 | 0.101 | 0.595 | 1.424 | 2.2697 | -59.3871 | 82.8231 | 2.2432 | 95.4976 | [8 empty] | Total dissolved solids | mg/L | 286 | 272 | 279 | 5.0179 | 303 | 325.0332 | -7.2717 | 4.7782 | 324.5325 | 14.0302 | Total dissolved solids | mg/L | 293 | 321 | 293 | 8.7227 | 0 | 293 | 0 | Total dissolved solids | mg/L | 270 | 295 | 315.6853 | -7.012 | 7.8498 | 315.2542 | 14.3548 | Total dissolved solids | mg/L | 271 | 287 | 302.5333 | -5.4123 | 7.5085 | 302.2431 | 10.3371 | UV254 F, cm-1 | 0.588 | 0.588 | 0.588 | 0.588 | UV254 F, cm-1 | 0.588 | 0.588 | 0.588 | 0.588 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 51.0754 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.587 | 0.589 | 0.588 | 0.34014 | 1999-04-03 | 9:00 | 23 | 24 | 45 | 46 | 272 | 6.94 | 3.48 | 10.42 | 0.20791 | 0.66603 | 25.1036 | 15.8402 | 16.1236 | 0 | 0 | 0 | 0 | 45.5 | 0.35437 | 1999-04-04 | 10:00 | 24 | 24 | 43 | 44 | 272 | 6.16 | 2.55 |  | 8.71 | 0.20791 | 0.70723 | 30.2285 | 14.0599 | 14.3115 | 326.1059 | 279.2954 | 325.0458 | 0.4628 | 43.0372 | 0.33254 |  |  |  | 273 | 292 | 310 | 341.3137 | -10.1012 | 6.8259 | 340.5402 | 19.8332 | 0.108 | 0.595 | 1.477 | 1.7475 | -18.3161 | 81.6327 | 1.729 | 93.7535 | [8 empty] | Total hardness | mg/L as CaCO3 | 272 | 270 | 271 | 0.73801 | 328 | 349.9141 | -6.6811 | 8.1356 | 349.0557 | 22.362 | Total hardness | mg/L as CaCO3 | 294 | 386 | 301.4419 | 21.9062 | 0.33898 | 301.372 | 2.4461 | Total hardness | mg/L as CaCO3 | 246 | 296 | 343.3296 | -15.9897 | 16.6102 | 342.411 | 28.1565 | Total hardness | mg/L as CaCO3 | 240 | 286 | 318.8331 | -11.4801 | 18.6441 | 318.1076 | 24.5538 | UV254 p, cm-1 | 0.122 | 0.203 | 0.118 | 0.106 | UV254 p, cm-1 | 0.122 | 0.203 | 0.118 | 0.106 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.622 | 4.712 | 4.667 | 1.9274 | 1999-04-03 | 9:20 | 23.3333 | 24 | 36 | 36 | 272 | 5.4 | 2.53 | 7.93 | 0.20791 | 0.68096 | 33.3001 | 12.3252 | 12.5458 | 0 | 0 | 0 | 0 | 36 | 0.34849 | 1999-04-04 | 11:00 | 25 | 24 | 43 | 44 | 281 | 6.19 | 1.26 |  | 7.45 | 0.21479 | 0.83087 | 36.7181 | 14.1283 | 14.3811 | 332.6529 | 284.9285 | 331.6016 | 0.47199 | 43.028 | 0.33423 |  |  |  | 273 | 292 | 309 | 391.254 | -26.6194 | 6.8259 | 389.9515 | 29.9913 | 0.112 | 0.596 | 1.555 | 2.9264 | -88.1958 | 80.9524 | 2.8954 | 96.1319 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 230 | 236 | 233 | 2.5751 | 295 | 354.6592 | -20.2235 | 13.7037 | 353.3359 | 34.0571 | Calcium hardness | mg/L as CaCO3 | 268 | 336 | 282.8838 | 15.8084 | 0.74074 | 282.744 | 5.2146 | Calcium hardness | mg/L as CaCO3 | 218 | 278 | 321.2886 | -15.5714 | 19.2593 | 320.3138 | 31.9417 | Calcium hardness | mg/L as CaCO3 | 212 | 276 | 295.1331 | -6.9323 | 21.4815 | 294.3681 | 27.9813 | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | 140 | 140 | 0 | 1999-04-03 | 9:40 | 23.6667 | 24 | 54 | 56 | 272 | 8.51 | 4.25 | 12.76 | 0.20791 | 0.66693 | 20.3166 | 19.4236 | 19.7712 | 0 | 0 | 0 | 0 | 55 | 0.35948 | 1999-04-04 | 12:00 | 26 | 24 | 43 | 44 | 281 | 6.29 | 5.2 |  | 11.49 | 0.21479 | 0.54743 | 23.456 | 14.3566 | 14.6135 | 317.9814 | 272.3476 | 316.9599 | 0.45123 | 43.0488 | 0.33946 |  |  |  | 271 | 293 | 307 | 319.6115 | -4.108 | 7.5085 | 319.0675 | 15.065 | [16 empty] | Turbidity | ntu | 0.095 | 0.092 | 0.0935 | 3.2086 | 0.389 | 0.63275 | -62.6597 | 63.6893 | 0.62688 | 85.0849 | Turbidity | ntu | 0.12 | 1.18 | 1.1433 | 3.1135 | 53.3981 | 1.1336 | 89.4147 | Turbidity | ntu | 0.087 | 0.299 | 0.42567 | -42.3637 | 66.2136 | 0.42247 | 79.4069 | Turbidity | ntu | 0.083 | 0.276 | 0.33312 | -20.6942 | 67.767 | 0.33081 | 74.9104 | Bromidep, ug/L | 140 | 140 | 140 | 140 | Bromidep, ug/L | 140 | 140 | 140 | 140 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 17.5 | 16.5 | 17 | 5.8824 | 1999-04-03 | 10:00 | 24 | 24 | 46 | 46 | 272 | 7.08 | 3.2 | 10.28 | 0.20791 | 0.68872 | 25.4591 | 16.1597 | 16.4489 | 0 | 0 | 0 | 0 | 46 | 0.35758 | 1999-04-04 | 13:00 | 27 | 24 | 43 | 44 | 281 | 6.37 | 4.03 |  | 10.4 | 0.21479 | 0.6125 | 26.0192 | 14.5392 | 14.7993 | 321.2446 | 275.131 | 320.1992 | 0.45591 | 43.0441 | 0.34382 |  |  |  | 272 | 292 | 306 | 326.1935 | -6.5992 | 7.1672 | 325.5793 | 16.4566 | [16 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 348 | 348 | 348 | 348 | AlkF, mg/L CaCO3 | 348 | 348 | 348 | 348
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.2 | 0.71 | 0.955 | 51.3089 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 14:00 | 28 | 24 | 43 | 44 | 281 | 6.31 | 3.49 |  | 9.8 | 0.21479 | 0.64388 | 27.6735 | 14.4022 | 14.6599 | 322.8327 | 276.4998 | 321.7923 | 0.45813 | 43.0419 | 0.3406 |  |  |  |  | 292 | 300 |  | #VALUE! |  |  |  | 0.103 | 0.597 | 1.34 | 1.4649 | -9.3202 | 82.483 | 1.4496 | 92.8946 | [8 empty] | Total organic carbon | mg/L | 4.7 | 4.8 | 4.75 | 2.1053 | 32.2 | 30.5615 | 5.0886 | 62.3016 | 30.2807 | 84.3134 | Total organic carbon | mg/L | 7.2 | 73.5 | 47.3862 | 35.5289 | 42.8571 | 47.0088 | 84.6837 | Total organic carbon | mg/L | 4.2 | 22.7 | 20.8851 | 7.9952 | 66.6667 | 20.7276 | 79.7372 | Total organic carbon | mg/L | 3.6 | 16.9 | 16.5 | 2.3671 | 71.4286 | 16.3813 | 78.0237 | Alkp, mg/L CaCO3 | 318.5 | 350 | 298 | 284 | Alkp, mg/L CaCO3 | 318.5 | 350 | 298 | 284
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 16.3 | 15.79 | 16.045 | 3.1786 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 15:00 | 29 | 24 | 43 | 44 | 281 | 6.33 | 3.02 |  | 9.35 | 0.21479 | 0.67701 | 29.0535 | 14.4479 | 14.7064 | 324.535 | 277.9549 | 323.4857 | 0.46055 | 43.0394 | 0.3417 |  |  |  | 275 | 293 | 307 | 330.7285 | -7.7291 | 6.1433 | 330.1008 | 16.6921 | [16 empty] | UV254 | cm-1 | 0.12 | 0.124 | 0.122 | 3.2787 | 1.36 | 1.6542 | -21.6359 | 79.2517 | 1.6376 | 92.55 | UV254 | cm-1 | 0.203 | 3.05 | 3.0681 | -0.5944 | 65.4762 | 3.0412 | 93.325 | UV254 | cm-1 | 0.118 | 0.958 | 1.0516 | -9.7672 | 79.932 | 1.0428 | 88.6839 | UV254 | cm-1 | 0.106 | 0.729 | 0.79686 | -9.3093 | 81.9728 | 0.79051 | 86.5909 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 16:00 | 30 | 24 | 43 | 44 | 281 | 6.25 | 2.43 |  | 8.68 | 0.21479 | 0.72005 | 31.3733 | 14.2653 | 14.5205 | 326.7615 | 279.8735 | 325.7186 | 0.46367 | 43.0363 | 0.3374 |  |  |  | 277 | 294 | 308 | 334.1523 | -8.491 | 5.4608 | 333.5167 | 16.9457 | 0.126 | 0.595 | 1.27 | 1.7763 | -39.8639 | 78.5714 | 1.7579 | 92.8324 | [8 empty] | SUVA | L/(mg*m) | 2.5532 | 2.5833 | 2.5683 | 1.1736 | 4.2236 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8194 | 4.1497 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8095 | 4.2203 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.9444 | 4.3136 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 271 | 294 | 246 | 240 | T-Hdp, mg/L CaCO3 | 271 | 294 | 246 | 240
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 17:00 | 31 | 24 | 43 | 44 | 281 | 6.51 | 0.98 |  | 7.49 | 0.21479 | 0.86916 | 36.5167 | 14.8587 | 15.1246 | 334.788 | 286.7093 | 333.6742 | 0.47522 | 43.0248 | 0.35153 |  |  |  | 273 | 292 |  | 425.8571 |  | 6.8259 | 424.0865 | 35.6263 | [16 empty] | Bromide | mg/L | 140 | 140 | 140 | 0 | --- | 140 | --- | 0 | 140 | 0 | Bromide | mg/L | 140 | --- | 140 | --- | 0 | 140 | 0 | Bromide | mg/L | 140 | --- | 140 | --- | 0 | 140 | 0 | Bromide | mg/L | 140 | --- | 140 | --- | 0 | 140 | 0 | Ca-HdF, mg/L CaCO3 | 270 | 270 | 270 | 270 | Ca-HdF, mg/L CaCO3 | 270 | 270 | 270 | 270
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 18:00 | 32 | 24 | 43 | 44 | 281 | 6.45 | 3.42 |  | 9.87 | 0.21479 | 0.6535 | 27.4701 | 14.7218 | 14.9852 | 323.3391 | 276.9132 | 322.2734 | 0.45893 | 43.0411 | 0.34816 |  |  |  | 277 | 292 | 309 | 323.1754 | -4.5875 | 5.4608 | 322.6455 | 14.1473 | [16 empty] | SDS-Cl2 dose | mg/L | 5.25 | 5.25 | 5.25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 6.25 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.75 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 233 | 268 | 218 | 212 | Ca-Hdp, mg/L CaCO3 | 233 | 268 | 218 | 212
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 1930 | 1400 | 1665 | 31.8318 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 19:00 | 33 | 24 | 43 | 44 | 281 | 6.43 | 2.66 |  | 9.09 | 0.21479 | 0.70737 | 29.9131 | 14.6761 | 14.9387 | 326.1207 | 279.2984 | 325.0493 | 0.46287 | 43.0371 | 0.34711 |  |  |  | 274 | 291 | 309 | 338.9286 | -9.6856 | 6.4846 | 338.1857 | 18.9794 | 0.12 | 0.589 | 1.56 | 1.7193 | -10.2111 | 79.5918 | 1.701 | 92.9453 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.9 | 0.85 | 0.875 | 5.7143 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.55 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.85 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.15 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 520 | 430 | 475 | 18.9474 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 20:00 | 34 | 24 | 43 | 44 | 281 | 6.35 | 1.93 |  | 8.28 | 0.21479 | 0.76691 | 32.9372 | 14.4935 | 14.7529 | 329.2432 | 281.9844 | 328.1752 | 0.46725 | 43.0328 | 0.34283 |  |  |  | 273 | 292 | 312 | 358.8031 | -15.001 | 6.8259 | 357.8336 | 23.7076 | 0.134 | 0.591 | 1.531 | 2.0817 | -35.972 | 77.2109 | 2.0597 | 93.4943 | [8 empty] | SDS-Cl2 demand | mg/L | 4.35 | 4.4 | 4.375 | 1.1429 | --- | 42.747 | --- | 72.7329 | 42.3296 | 89.6644 | SDS-Cl2 demand | mg/L | 5.7 | --- | 82.6864 | --- | 64.4749 | 81.9633 | 93.0457 | SDS-Cl2 demand | mg/L | 3.9 | --- | 28.0238 | --- | 75.6934 | 27.7962 | 85.9693 | SDS-Cl2 demand | mg/L | 3.6 | --- | 21.4378 | --- | 77.5631 | 21.2736 | 83.0776 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 61 | 57 | 59 | 6.7797 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 9:00 | 47 | 24 | 44 | 45 | 272 | 5.75 | 1.75 |  | 7.5 | 0.20791 | 0.76667 | 35.2667 | 13.1241 | 13.3589 | 329.1784 | 281.9892 | 328.1808 | 0.4669 | 44.0331 | 0.30338 |  |  |  | 288 | 294 | 315 | 309.4286 | 1.7687 | 1.7065 | 309.2021 | 6.857 | 0.117 | 0.592 | 1.751 | 2.1356 | -21.963 | 80.102 | 2.1142 | 94.4661 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 121.4156 | 140.8618 | 116.5856 | 115.008 | Qp/QT (THM4), % | 130.7662 | 151.7101 | 125.5643 | 123.8652
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 5.6 | 5.3 | 5.45 | 5.5046 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 10:00 | 48 | 24 | 44 | 45 | 281 | 6 | 2.63 |  | 8.63 | 0.21479 | 0.69525 | 31.5608 | 13.6947 | 13.9397 | 325.4419 | 278.7796 | 324.4455 | 0.46164 | 44.0384 | 0.31654 |  |  |  | 281 | 293 | 311 | 320.3764 | -3.0149 | 4.0956 | 319.956 | 12.1754 | 0.115 | 0.593 | 1.501 | 1.6671 | -11.0651 | 80.4422 | 1.6505 | 93.0325 | [8 empty] | SDS-Chlorination pH | --- | 8.9 | 8.9 | 8.9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 11:00 | 49 | 24 | 44 | 45 | 281 | 5.77 | 2.38 |  | 8.15 | 0.21479 | 0.70798 | 33.4785 | 13.1697 | 13.4054 | 326.0764 | 279.3567 | 325.1171 | 0.4624 | 44.0376 | 0.30441 |  |  |  | 288 | 292 | 312 | 305.1218 | 2.2045 | 1.7065 | 304.9461 | 5.5571 | 0.121 | 0.601 | 1.46 | 1.7202 | -17.8206 | 79.4218 | 1.7038 | 92.8981 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 586.6 | 492.3 | 539.45 | 17.4808 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 12:00 | 50 | 24 | 44 | 45 | 272 | 5.94 | 2.04 |  | 7.98 | 0.20791 | 0.74436 | 33.0852 | 13.5577 | 13.8003 | 328.024 | 280.9715 | 326.9965 | 0.46539 | 44.0346 | 0.3134 |  |  |  | 289 | 294 | 315 | 304.6471 | 3.2866 | 1.3652 | 304.4762 | 5.0829 | 0.117 | 0.603 | 1.5 | 1.9594 | -30.6294 | 80.102 | 1.9393 | 93.967 | [8 empty] | SDS-TOX | mg Cl- /L | 345 | 360 | 352.5 | 4.2553 | --- | 4668.1141 | --- | 78.8288 | 4621.1708 | 92.3721 | SDS-TOX | mg Cl- /L | 530 | --- | 8976.5494 | --- | 68.1682 | 8897.2129 | 94.0431 | SDS-TOX | mg Cl- /L | 335 | --- | 2976.8047 | --- | 79.8799 | 2951.8711 | 88.6513 | SDS-TOX | mg Cl- /L | 300 | --- | 2256.4951 | --- | 81.982 | 2238.4897 | 86.5981 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | NR | 11 | 11 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 14:00 | 52 | 24 | 44 | 45 | 272 | 5.65 | 1.99 |  | 7.64 | 0.20791 | 0.73953 | 34.6021 | 12.8958 | 13.1266 | 327.7334 | 280.7665 | 326.7578 | 0.46479 | 44.0352 | 0.29809 |  |  |  | 286 | 295 | 308 | 312.8744 | -1.5826 | 2.3891 | 312.5953 | 8.5079 | 0.118 | 0.601 | 1.491 | 1.9224 | -28.9351 | 79.932 | 1.9037 | 93.8015 | [8 empty] | SDS-CHCl3 | mg/L | 92 | 97 | 94.5 | 5.291 | --- | 1345.6171 | --- | 80.1053 | 1332.008 | 92.9054 | SDS-CHCl3 | mg/L | 150 | --- | 2568.6155 | --- | 68.4211 | 2545.898 | 94.1082 | SDS-CHCl3 | mg/L | 81 | --- | 863.6098 | --- | 82.9474 | 856.2235 | 90.5399 | SDS-CHCl3 | mg/L | 75 | --- | 648.3319 | --- | 84.2105 | 643.0556 | 88.3369 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | NR | 110 | 110 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 15:00 | 53 | 24 | 43 | 44 | 272 | 5.71 | 1.74 |  | 7.45 | 0.20791 | 0.76644 | 35.5101 | 13.0328 | 13.266 | 329.1613 | 281.9806 | 328.1709 | 0.46685 | 43.0331 | 0.30827 |  |  |  | 288 | 296 | 309 | 309.408 | -0.13205 | 1.7065 | 309.1833 | 6.8514 | 0.126 | 0.603 | 1.577 | 2.1041 | -33.4244 | 78.5714 | 2.0833 | 93.952 | [8 empty] | SDS-BDCM | mg/L | 41 | 41 | 41 | 0 | --- | 100.1856 | --- | 30.5085 | 99.5418 | 58.8113 | SDS-BDCM | mg/L | 44 | --- | 155.6284 | --- | 25.4237 | 154.5799 | 71.5358 | SDS-BDCM | mg/L | 38 | --- | 79.7127 | --- | 35.5932 | 79.319 | 52.0922 | SDS-BDCM | mg/L | 37 | --- | 68.5333 | --- | 37.2881 | 68.2431 | 45.782 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | NR | 140 | 140 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 16:00 | 54 | 24 | 44 | 45 | 272 | 5.6 | 3.76 |  | 9.36 | 0.20791 | 0.59829 | 28.0598 | 12.7817 | 13.0104 | 320.473 | 274.5539 | 319.5276 | 0.45446 | 44.0455 | 0.29539 |  |  |  | 286 | 294 | 306 | 303.4255 | 0.84133 | 2.3891 | 303.2462 | 5.6872 | 0.113 | 0.6 | 1.356 | 1.2954 | 4.4656 | 80.7823 | 1.2833 | 91.1944 | [8 empty] | SDS-DBCM | mg/L | 18 | 17 | 17.5 | 5.7143 | --- | -22.1214 | --- | -221.1009 | -21.6905 | 180.6806 | SDS-DBCM | mg/L | 13 | --- | -43.1863 | --- | -138.5321 | -42.6586 | 130.4745 | SDS-DBCM | mg/L | 18 | --- | -6.9283 | --- | -230.2752 | -6.693 | 368.9364 | SDS-DBCM | mg/L | 19 | --- | -0.42162 | --- | -248.6239 | -0.24288 | 7922.6901 | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 17:00 | 55 | 24 | 44 | 45 | 272 | 5.77 | 2.8 |  | 8.57 | 0.20791 | 0.67328 | 30.7386 | 13.1697 | 13.4054 | 324.303 | 277.8097 | 323.3167 | 0.46 | 44.04 | 0.30439 |  |  |  | 287 | 296 | 308 | 305.3643 | 0.85575 | 2.0478 | 305.1695 | 5.9539 | 0.112 | 0.594 | 1.311 | 1.5689 | -19.672 | 80.9524 | 1.5534 | 92.7902 | [8 empty] | SDS-CHBr3 | mg/L | 1.6 | 1.3 | 1.45 | 20.6897 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 0.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | NR | 1.4 | 1.4 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-05 | 18:00 | 56 | 24 | 44 | 45 | 272 | 5.83 | 2.43 |  | 8.26 | 0.20791 | 0.70581 | 31.9298 | 13.3067 | 13.5448 | 325.9928 | 279.2483 | 324.9909 | 0.46244 | 44.0376 | 0.30757 |  |  |  | 261 | 299 | 310 | 369.7737 | -19.2818 | 10.9215 | 368.6079 | 29.1931 | 0.12 | 0.596 | 1.37 | 1.7108 | -24.877 | 79.5918 | 1.6938 | 92.9152 | [8 empty] | SDS-THM4 | mg/L | 152.6 | 156.3 | 154.45 | 2.3956 | --- | 1420.3635 | --- | 71.369 | 1406.5934 | 89.0196 | SDS-THM4 | mg/L | 207.6 | --- | 2677.1924 | --- | 61.5164 | 2653.9961 | 92.1778 | SDS-THM4 | mg/L | 138.5 | --- | 934.9147 | --- | 74.3257 | 927.3981 | 85.0657 | SDS-THM4 | mg/L | 133 | --- | 715.5769 | --- | 75.3453 | 710.2155 | 81.2733 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | NR | 16 | 16 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 9:00 | 71 | 24 | 44 | 45 | 272 | 5.24 | 3.81 |  | 9.05 | 0.20791 | 0.57901 | 29.0552 | 11.96 | 12.174 | 319.4739 | 273.7509 | 318.593 | 0.45283 | 44.0472 | 0.27639 |  |  |  | 277 | 292 | 310 | 315.0052 | -1.6146 | 5.4608 | 314.6392 | 11.9626 | 0.149 | 0.591 | 1.905 | 1.1918 | 37.4399 | 74.6599 | 1.1817 | 87.3913 | [8 empty] | SDS-MCAA* | mg/L | 2.9 | 3.7 | 3.3 | 24.2424 | --- | 28.6183 | --- | 70 | 28.3429 | 88.3569 | SDS-MCAA* | mg/L | 4 | --- | 56.0933 | --- | 63.6364 | 55.604 | 92.8063 | SDS-MCAA* | mg/L | 2.7 | --- | 19.1865 | --- | 75.4545 | 19.0308 | 85.8125 | SDS-MCAA* | mg/L | 3.1 | --- | 14.4233 | --- | 71.8182 | 14.3191 | 78.3506 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 10:00 | 72 | 24 | 44 | 45 | 272 | 5.24 | 2.23 |  | 7.47 | 0.20791 | 0.70147 | 35.4123 | 11.96 | 12.174 | 325.6983 | 279.0845 | 324.8003 | 0.46165 | 44.0384 | 0.27644 |  |  |  | 273 | 292 | 306 | 339.9955 | -11.1096 | 6.8259 | 339.3502 | 19.5521 | 0.133 | 0.593 | 1.639 | 1.6571 | -1.1073 | 77.381 | 1.6425 | 91.9024 | [8 empty] | SDS-DCAA* | mg/L | 23 | 25 | 24 | 8.3333 | --- | 306.7755 | --- | 78.1818 | 303.6996 | 92.0975 | SDS-DCAA* | mg/L | 37 | --- | 580.2582 | --- | 66.3636 | 575.1555 | 93.567 | SDS-DCAA* | mg/L | 21 | --- | 197.7824 | --- | 80.9091 | 196.1139 | 89.2919 | SDS-DCAA* | mg/L | 18 | --- | 149.8663 | --- | 83.6364 | 148.6528 | 87.8912 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | NR | 2.6 | 2.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 11:00 | 73 | 24 | 43 | 44 | 272 | 5.28 | 1.88 |  | 7.16 | 0.20791 | 0.73743 | 36.9888 | 12.0513 | 12.267 | 327.5772 | 280.6884 | 326.667 | 0.46434 | 43.0357 | 0.28504 |  |  |  | 278 | 293 | 305 | 335.1277 | -9.8779 | 5.1195 | 334.5732 | 16.9091 | 0.133 | 0.596 | 1.569 | 1.8659 | -18.9211 | 77.381 | 1.8491 | 92.8071 | [8 empty] | SDS-TCAA* | mg/L | 16 | 17 | 16.5 | 6.0606 | --- | 422.5787 | --- | 88.2143 | 418.1616 | 96.0542 | SDS-TCAA* | mg/L | 28 | --- | 861.4921 | --- | 80 | 853.6633 | 96.72 | SDS-TCAA* | mg/L | 15 | --- | 263.2899 | --- | 89.2857 | 260.9465 | 94.2517 | SDS-TCAA* | mg/L | 12 | --- | 195.4662 | --- | 91.4286 | 193.7778 | 93.8073
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | NR | 19 | 19 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 13:00 | 75 | 24 | 43 | 44 | 272 | 5.37 | 0.9 |  | 6.27 | 0.20791 | 0.85646 | 42.3812 | 12.2567 | 12.4761 | 333.9516 | 286.1366 | 333.0076 | 0.47343 | 43.0266 | 0.28996 |  |  |  | 284 | 294 | 306 | 346.7 | -13.3007 | 3.0717 | 346.0811 | 17.9383 | 0.15 | 0.602 | 1.772 | 3.2014 | -80.6659 | 74.4898 | 3.1713 | 95.27 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 0 | 262.4 | 131.2 | 200 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 14:00 | 76 | 24 | 43 | 44 | 272 | 5.29 | 2.61 |  | 7.9 | 0.20791 | 0.66962 | 33.4304 | 12.0741 | 12.2902 | 324.0617 | 277.6747 | 323.1596 | 0.45936 | 43.0406 | 0.28555 |  |  |  | 288 | 295 | 309 | 303.1341 | 1.8983 | 1.7065 | 302.9869 | 4.9464 | 0.149 | 0.6 | 1.821 | 1.4778 | 18.8482 | 74.6599 | 1.4649 | 89.8283 | [8 empty] | SDS-DBAA* | mg/L | 3.4 | 3.4 | 3.4 | 0 | --- | -3.1762 | --- | -142.8571 | -3.1046 | 209.5135 | SDS-DBAA* | mg/L | 2.5 | --- | -5.6861 | --- | -78.5714 | -5.6092 | 144.5697 | SDS-DBAA* | mg/L | 3.8 | --- | -0.96717 | --- | -171.4286 | -0.92217 | 512.07 | SDS-DBAA* | mg/L | 3.9 | --- | 0.31668 | --- | -178.5714 | 0.34965 | -1015.393 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 0 | 278.4 | 139.2 | 200 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 15:00 | 77 | 24 | 43 | 44 | 272 | 5.36 | 2.25 |  | 7.61 | 0.20791 | 0.70434 | 34.7424 | 12.2339 | 12.4528 | 325.8609 | 279.2058 | 324.9415 | 0.46195 | 43.038 | 0.28934 |  |  |  | 288 | 297 | 306 | 304.9111 | 0.35585 | 1.7065 | 304.7445 | 5.4946 | 0.147 | 0.592 | 1.798 | 1.6386 | 8.8676 | 75 | 1.6239 | 90.9475 | [8 empty] | SDS-BCAA* | mg/L | 11 | 11 | 11 | 0 | --- | 27.4404 | --- | 31.25 | 27.2616 | 59.6502 | SDS-BCAA* | mg/L | 12 | --- | 41.7676 | --- | 25 | 41.488 | 71.076 | SDS-BCAA* | mg/L | 11 | --- | 20.9316 | --- | 31.25 | 20.8379 | 47.2115 | SDS-BCAA* | mg/L | 10 | --- | 18.6 | --- | 37.5 | 18.5208 | 46.0068 | Qp/QT (HAA5), % | 91.9048 | 129.3132 | 87.0349 | 81.9533 | Qp/QT (HAA5), % | 124.0476 | 174.5394 | 117.4746 | 110.6157
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 15:45 | 77.75 | 24 | 43 | 44 | 272 | 5.37 | 0.85 |  | 6.22 | 0.20791 | 0.86334 | 42.7299 | 12.2567 | 12.4761 | 334.3272 | 286.4584 | 333.3822 | 0.47396 | 43.026 | 0.28997 |  |  |  | 290 | 295 | 321 | 311.9529 | 2.8184 | 1.0239 | 311.7362 | 6.9726 | 0.149 | 0.605 | 1.898 | 3.3614 | -77.1047 | 74.6599 | 3.3297 | 95.5252 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 185.6167 | NA | 190.4834 | 206.3508 | SDS-THM4b, ug/L | NA | NA | NA | NA
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 16:30 | 78.5 | 24 | 43 | 44 | 272 | 5.46 | 0.69 |  | 6.15 | 0.20791 | 0.8878 | 43.2276 | 12.4622 | 12.6851 | 335.6828 | 287.606 | 334.7177 | 0.47594 | 43.0241 | 0.29484 |  |  |  | 292 | 293 | 323 | 300.913 | 6.8381 | 0.3413 | 300.8236 | 2.9331 | 0.152 | 0.601 | 1.899 | 4.0381 | -112.6428 | 74.1497 | 3.9991 | 96.1991 | [8 empty] | SDS-CDBAA | mg/L | 3.6 | 3.5 | 3.55 | 2.8169 | --- | 0.42632 | --- | -36.5385 | 0.4603 | -671.2438 | SDS-CDBAA | mg/L | 2.7 | --- | 1.9558 | --- | -3.8462 | 1.9628 | -37.5585 | SDS-CDBAA | mg/L | 3.8 | --- | 1.4164 | --- | -46.1538 | 1.4389 | -164.0882 | SDS-CDBAA | mg/L | 3.8 | --- | 2.08 | --- | -46.1538 | 2.0958 | -81.3121 | SDS-HAA5b, ug/L | 54 | NA | 54 | 54 | SDS-HAA5b, ug/L | NA | NA | NA | NA
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-06 | 17:15 | 79.25 | 24 | 43 | 44 | 272 | 5.44 | 0.71 |  | 6.15 | 0.20791 | 0.88455 | 43.2276 | 12.4165 | 12.6387 | 335.5007 | 287.453 | 334.5397 | 0.47567 | 43.0243 | 0.29376 |  |  |  | 293 | 296 | 325 | 293 | 9.8462 | 0 | 293 | 0 | 0.156 | 0.597 | 1.908 | 3.898 | -104.2962 | 73.4694 | 3.8606 | 95.9591 | [8 empty] | SDS-DCBAA | mg/L | 8.7 | 8.8 | 8.75 | 1.1429 | --- | 42.4529 | --- | 53.9474 | 42.0863 | 79.2094 | SDS-DCBAA | mg/L | 9.2 | --- | 82.1306 | --- | 51.5789 | 81.4455 | 88.7041 | SDS-DCBAA | mg/L | 8.6 | --- | 29.2577 | --- | 54.7368 | 29.0628 | 70.4089 | SDS-DCBAA | mg/L | 7.6 | --- | 23.94 | --- | 60 | 23.7896 | 68.0532 | SDS-TOXb, ug Cl- /L | 458.75 | NA | 507.4352 | 546.3376 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
[44 empty] | 1999-04-06 | 18:00 | 80 | 24 | 43 | 44 | 272 | 5.4 | 0.66 |  | 6.06 | 0.20791 | 0.89109 | 43.8845 | 12.3252 | 12.5458 | 335.8543 | 287.7622 | 334.8996 | 0.47615 | 43.0239 | 0.2916 |  |  |  | 287 | 295 | 327 | 342.0909 | -4.615 | 2.0478 | 341.5441 | 15.9698 | 0.161 | 0.596 | 2.022 | 4.0816 | -101.8613 | 72.619 | 4.0427 | 96.0175 | [8 empty] | SDS-HAA5 | mg/L | 45.3 | 49.1 | 47.2 | 8.0508 | --- | 323.3993 | --- | 64.0244 | 320.3949 | 85.2682 | SDS-HAA5 | mg/L | 71.5 | --- | 515.7811 | --- | 45.503 | 511.608 | 86.0245 | SDS-HAA5 | mg/L | 42.5 | --- | 218.6865 | --- | 67.6067 | 217.0237 | 80.4169 | SDS-HAA5 | mg/L | 37 | --- | 172.0197 | --- | 71.7988 | 170.7771 | 78.3343 | SDS-CDb, mg/L | 5.3197 | NA | 5.4746 | 5.8459 | SDS-CDb, mg/L | NA | NA | NA | NA
[44 empty] | 1999-04-06 | 18:45 | 80.75 | 24 | 43 | 44 | 272 | 5.33 | 1.37 |  | 6.7 | 0.20791 | 0.79552 | 39.597 | 12.1654 | 12.3831 | 330.6579 | 283.3206 | 329.7303 | 0.46874 | 43.0313 | 0.28777 |  |  |  | 289 | 294 | 326 | 308.562 | 5.3491 | 1.3652 | 308.3704 | 6.2815 | 0.16 | 0.598 | 2.11 | 2.2531 | -6.7838 | 72.7891 | 2.2326 | 92.8336 | [8 empty] | SDS-HAA6 | mg/L | 56.3 | 60.1 | 58.2 | 6.5292 | --- | 324.535 | --- | 58.1897 | 321.638 | 81.9051 | SDS-HAA6 | mg/L | 83.5 | --- | 498.0135 | --- | 40.0144 | 494.1201 | 83.1013 | SDS-HAA6 | mg/L | 53.5 | --- | 223.7276 | --- | 61.5661 | 222.1209 | 75.914 | SDS-HAA6 | mg/L | 47 | --- | 179.153 | --- | 66.2356 | 177.9368 | 73.5861 | TOCb, mg/L | 5.3855 | NA | 5.2891 | 5.2242 | TOCb, mg/L | NA | NA | NA | NA
[44 empty] | 1999-04-06 | 19:30 | 81.5 | 24 | 43 | 44 | 272 | 5.26 | 0.97 |  | 6.23 | 0.20791 | 0.8443 | 42.6597 | 12.0057 | 12.2205 | 333.2742 | 285.573 | 332.3517 | 0.4724 | 43.0276 | 0.28402 |  |  |  | 288 | 296 | 323 | 320.1134 | 0.89368 | 1.7065 | 319.8029 | 9.9445 | 0.161 | 0.594 | 2.077 | 2.9035 | -39.7922 | 72.619 | 2.877 | 94.4038 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.15972 | NA | 0.17894 | 0.19299 | UV254 b, cm-1 | NA | NA | NA | NA
[44 empty] | 1999-04-07 | 9:00 | 95 | 24 | 43 | 44 | 272 | 4.9 | 0.25 |  | 5.15 | 0.20791 | 0.95146 | 51.8155 | 11.184 | 11.3841 | 339.1296 | 290.6464 | 338.2562 | 0.48046 | 43.0195 | 0.26463 |  |  |  | 289 | 294 |  | 371.4 |  | 1.3652 | 370.6578 | 22.0305 | 0.214 | 0.601 | 2.89 | 7.9184 | -173.9931 | 63.6054 | 7.849 | 97.2735 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 140 | NA | 140 | 140 | Bromideb, ug/L | NA | NA | NA | NA
[44 empty] | 1999-04-07 | 11:00 | 97 | 24 | 43 | 44 | 272 | 4.93 | 0.95 |  | 5.88 | 0.20791 | 0.83844 | 45.2585 | 11.2525 | 11.4538 | 332.9081 | 285.3098 | 332.0454 | 0.47167 | 43.0283 | 0.26619 |  |  |  | 289 | 293 | 315 | 313.7579 | 0.39432 | 1.3652 | 313.5335 | 7.8248 | 0.188 | 0.603 | 3.112 | 2.6638 | 14.4027 | 68.0272 | 2.6414 | 92.8824 | [47 empty] | Alkb, mg/L CaCO3 | 320.8881 | NA | 304.4825 | 295.5499 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
[44 empty] | 1999-04-07 | 13:15 | 99.25 | 24 | 43 | 44 | 272 | 4.93 | 0.83 |  | 5.76 | 0.20791 | 0.8559 | 46.2222 | 11.2525 | 11.4538 | 333.8555 | 286.1217 | 332.9903 | 0.47301 | 43.027 | 0.2662 | 7.8 | 7.7 | 7.9 | 291 | 294 | 314 | 304.8795 | 2.9046 | 0.68259 | 304.7537 | 4.5131 | 0.189 | 0.596 | 3.56 | 2.958 | 16.9111 | 67.8571 | 2.9329 | 93.5558 | [47 empty] | T-Hdb, mg/L CaCO3 | 272.9429 | NA | 252.3529 | 249.9257 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[44 empty] | 1999-04-07 | 14:00 | 100 | 24 | 43 | 44 | 272 | 4.89 | 0.65 |  | 5.54 | 0.20791 | 0.88267 | 48.0975 | 11.1612 | 11.3609 | 335.3116 | 287.3758 | 334.4498 | 0.47505 | 43.025 | 0.26405 | 7.8 | 7.7 | 7.9 | 292 | 296 | 311 | 300.5231 | 3.3688 | 0.3413 | 300.4465 | 2.8113 | 0.188 | 0.597 | 3.46 | 3.5972 | -3.9662 | 68.0272 | 3.5666 | 94.7289 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 235.9952 | NA | 224.7418 | 222.4671 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
[44 empty] | 1999-04-07 | 14:30 | 100.5 | 24 | 43 | 44 | 281 | 5.14 | 6.03 |  | 11.17 | 0.21479 | 0.46016 | 24.1567 | 11.7318 | 11.9417 | 313.6381 | 268.7884 | 312.8177 | 0.44439 | 43.0556 | 0.27736 | 7.8 | 7.7 | 7.8 | 285 | 300 | 311 | 299.8192 | 3.5951 | 2.7304 | 299.6837 | 4.8997 | 0.143 | 0.595 | 1.893 | 0.96732 | 48.9002 | 75.6803 | 0.95978 | 85.1008 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-04-07 | 15:00 | 101 | 24 | 43 | 44 | 281 | 5.1 | 5 |  | 10.1 | 0.21479 | 0.50495 | 26.8218 | 11.6405 | 11.8488 | 315.8001 | 270.6469 | 314.9806 | 0.44743 | 43.0526 | 0.27522 | 7.8 | 7.7 | 7.9 | 280 | 294 | 313 | 306.26 | 2.1534 | 4.4369 | 306.0217 | 8.5032 | 0.124 | 0.597 | 1.326 | 1.0613 | 19.9638 | 78.9116 | 1.0528 | 88.2216 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-04-07 | 15:30 | 101.5 | 24 | 43 | 44 | 281 | 5.25 | 4.6 |  | 9.85 | 0.21479 | 0.53299 | 27.5279 | 11.9828 | 12.1973 | 317.1831 | 271.811 | 316.3354 | 0.44948 | 43.0505 | 0.28332 | 8 | 7.8 | 8 | 276 | 295 | 310 | 312.4022 | -0.77489 | 5.802 | 312.0621 | 11.5561 | 0.12 | 0.598 | 1.25 | 1.1221 | 10.2296 | 79.5918 | 1.1128 | 89.2161 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-04-07 | 16:00 | 102 | 24 | 43 | 44 | 281 | 5.2 | 3.24 |  | 8.44 | 0.21479 | 0.61611 | 32.2938 | 11.8687 | 12.0811 | 321.314 | 275.3582 | 320.4636 | 0.45531 | 43.0447 | 0.28066 | 8 | 7.8 | 8 | 270 | 293 | 303 | 329.9136 | -8.8824 | 7.8498 | 329.3592 | 18.0226 | 0.118 | 0.594 | 1.245 | 1.3423 | -7.8169 | 79.932 | 1.331 | 91.1344 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-04-07 | 16:30 | 102.5 | 24 | 43 | 44 | 281 | 5.2 | 6.71 |  | 11.91 | 0.21479 | 0.43661 | 22.5936 | 11.8687 | 12.0811 | 312.5153 | 267.8178 | 311.6881 | 0.44284 | 43.0572 | 0.28058 | 8 | 7.7 | 8 | 265 | 294 | 303 | 314.699 | -3.861 | 9.5563 | 314.2391 | 15.6693 | 0.112 | 0.596 | 1.131 | 0.95688 | 15.395 | 80.9524 | 0.94906 | 88.1989 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-04-07 | 17:00 | 103 | 24 | 43 | 44 | 281 | 5.37 | 6.87 |  | 12.24 | 0.21479 | 0.43873 | 21.9575 | 12.2567 | 12.4761 | 312.6273 | 267.8902 | 311.7724 | 0.4431 | 43.0569 | 0.28976 | 8 | 7.7 | 8 | 267 | 294 | 301 | 313.3231 | -4.0941 | 8.8737 | 312.8805 | 14.6639 | 0.105 | 0.596 | 0.999 | 0.96554 | 3.3492 | 82.1429 | 0.95732 | 89.0319 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-04-07 | 17:30 | 103.5 | 24 | 43 | 44 | 281 | 5.25 | 5.31 |  | 10.56 | 0.21479 | 0.49716 | 25.6098 | 11.9828 | 12.1973 | 315.4327 | 270.311 | 314.5896 | 0.447 | 43.053 | 0.28331 | 7.9 | 7.8 | 7.9 | 273 | 294 | 304 | 312.774 | -2.8862 | 6.8259 | 312.4025 | 12.6127 | 0.104 | 0.596 | 0.999 | 1.0665 | -6.7599 | 82.3129 | 1.0575 | 90.1659 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-04-07 | 18:00 | 104 | 24 | 43 | 44 | 281 | 5.33 | 5.4 |  | 10.73 | 0.21479 | 0.49674 | 25.1883 | 12.1654 | 12.3831 | 315.4182 | 270.2874 | 314.5622 | 0.44703 | 43.053 | 0.28763 | 7.9 | 7.7 | 8 | 270 | 294 | 303 | 315.7019 | -4.192 | 7.8498 | 315.2684 | 14.3587 | 0.103 | 0.598 | 0.997 | 1.0667 | -6.9923 | 82.483 | 1.0576 | 90.2607 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-04-08 | 9:30 | 119.5 | 24 | 43 | 44 | 281 | 4.89 | 3.08 |  | 7.97 | 0.21479 | 0.61355 | 34.2572 | 11.1612 | 11.3609 | 321.1552 | 275.2663 | 320.3566 | 0.4549 | 43.0451 | 0.26393 | 7.9 | 7.7 | 7.9 | 281 | 294 | 303 | 312.0519 | -2.9874 | 4.0956 | 311.7818 | 9.8729 | 0.12 | 0.595 | 1.146 | 1.331 | -16.1454 | 79.5918 | 1.3205 | 90.9125 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-04-08 | 10:00 | 120 | 24 | 43 | 44 | 281 | 5.15 | 11.8 |  | 16.95 | 0.21479 | 0.30383 | 15.5782 | 11.7546 | 11.9649 | 306.3089 | 262.5059 | 305.5061 | 0.43402 | 43.066 | 0.27783 | 8.1 | 7.8 | 8 | 281 | 294 | 301 | 298.2373 | 0.91784 | 4.0956 | 298.0793 | 5.7298 | 0.1 | 0.603 | 0.837 | 0.80098 | 4.3031 | 82.9932 | 0.79456 | 87.4144 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-04-08 | 11:00 | 121 | 24 | 43 | 44 | 281 | 5.1 | 11.5 |  | 16.6 | 0.21479 | 0.30723 | 15.9277 | 11.6405 | 11.8488 | 306.4622 | 262.6441 | 305.6669 | 0.4342 | 43.0658 | 0.27513 | 8 | 7.8 | 8 | 269 | 293 | 302 | 303.6435 | -0.5442 | 8.1911 | 303.3291 | 11.3174 | 0.094 | 0.602 | 0.779 | 0.80708 | -3.6044 | 84.0136 | 0.80061 | 88.2589 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-04-08 | 11:30 | 121.5 | 24 | 43 | 44 | 281 | 5.2 | 13.4 |  | 18.6 | 0.21479 | 0.27957 | 14.1075 | 11.8687 | 12.0811 | 305.2037 | 261.552 | 304.3959 | 0.43248 | 43.0675 | 0.28052 | 8 | 7.8 | 8 | 265 | 293 | 300 | 303.8657 | -1.2886 | 9.5563 | 303.5061 | 12.6871 | 0.095 | 0.6 | 0.734 | 0.77931 | -6.1735 | 83.8435 | 0.77298 | 87.7099 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-04-08 | 12:00 | 122 | 24 | 43 | 44 | 281 | 5.25 | 13.14 |  | 18.39 | 0.21479 | 0.28548 | 14.28 | 11.9828 | 12.1973 | 305.4747 | 261.7775 | 304.6583 | 0.43289 | 43.0671 | 0.28322 | 8 | 7.8 | 8.1 | 268 | 294 | 297 | 302.9886 | -2.0164 | 8.5324 | 302.6617 | 11.4523 | 0.094 | 0.595 | 0.766 | 0.78537 | -2.5293 | 84.0136 | 0.77892 | 87.9319
[44 empty] | 1999-04-08 | 13:00 | 123 | 24 | 43 | 44 | 281 | 5.2 | 12.2 |  | 17.4 | 0.21479 | 0.29885 | 15.1494 | 11.8687 | 12.0811 | 306.0829 | 262.3055 | 305.2728 | 0.43372 | 43.0663 | 0.28052 | 8 | 7.8 | 8 | 275 | 295 | 296 | 300.6721 | -1.5784 | 6.1433 | 300.4346 | 8.4659 | 0.096 | 0.597 | 0.775 | 0.7977 | -2.9297 | 83.6735 | 0.79121 | 87.8667
[44 empty] | 1999-04-08 | 14:00 | 124 | 24 | 43 | 44 | 281 | 5.2 | 12 |  | 17.2 | 0.21479 | 0.30233 | 15.3372 | 11.8687 | 12.0811 | 306.2419 | 262.4417 | 305.4314 | 0.43395 | 43.0661 | 0.28052 | 8.1 | 7.8 | 8 | 272 | 295 | 298 | 302.1 | -1.3758 | 7.1672 | 301.8215 | 9.8805 | 0.1 | 0.596 | 0.774 | 0.79947 | -3.2903 | 82.9932 | 0.79299 | 87.3896
[44 empty] | 1999-04-08 | 15:15 | 125.25 | 24 | 43 | 44 | 281 | 5.2 | 11.9 |  | 17.1 | 0.21479 | 0.30409 | 15.4327 | 11.8687 | 12.0811 | 306.3229 | 262.5111 | 305.5121 | 0.43406 | 43.0659 | 0.28053 | 8.1 | 7.8 | 8 | 271 | 294 | 299 | 302.6134 | -1.2085 | 7.5085 | 302.3209 | 10.3602 | 0.096 | 0.597 | 0.771 | 0.80299 | -4.1494 | 83.6735 | 0.79645 | 87.9465
[44 empty] | 1999-04-08 | 16:00 | 126 | 24 | 43 | 44 | 281 | 5.2 | 12 |  | 17.2 | 0.21479 | 0.30233 | 15.3372 | 11.8687 | 12.0811 | 306.2419 | 262.4417 | 305.4314 | 0.43395 | 43.0661 | 0.28052 | 8.1 | 7.8 | 8 | 280 | 296 | 300 | 298.6333 | 0.45556 | 4.4369 | 298.4609 | 6.1854 | 0.096 | 0.598 | 0.779 | 0.8012 | -2.8498 | 83.6735 | 0.79468 | 87.9196
[44 empty] | 1999-04-08 | 17:00 | 127 | 24 | 43 | 44 | 281 | 5.05 | 11.7 |  | 16.75 | 0.21479 | 0.30149 | 15.7761 | 11.5264 | 11.7326 | 306.1974 | 262.4239 | 305.4107 | 0.4338 | 43.0662 | 0.27243 | 8 | 7.7 | 7.9 | 276 | 294 | 301 | 300.3376 | 0.22006 | 5.802 | 300.1189 | 8.0365 | 0.095 | 0.598 | 0.782 | 0.80079 | -2.4029 | 83.8435 | 0.79445 | 88.042
[44 empty] | 1999-04-08 | 18:30 | 128.5 | 24 | 43 | 44 | 281 | 5.14 | 11.38 |  | 16.52 | 0.21479 | 0.31114 | 16.0097 | 11.7318 | 11.9417 | 306.6432 | 262.7938 | 305.8411 | 0.43448 | 43.0655 | 0.27729 | 8.1 | 7.7 | 8 | 269 | 294 | 298 | 303.8401 | -1.9598 | 8.1911 | 303.5214 | 11.3736 | 0.094 | 0.597 | 0.776 | 0.81112 | -4.5264 | 84.0136 | 0.80457 | 88.3167
[44 empty] | 1999-04-09 | 9:30 | 143.5 | 24 | 43 | 44 | 281 | 5.1 | 11.2 | X | 16.3 | 0.21479 | 0.31288 | 16.2393 | 11.6405 | 11.8488 | 306.7216 | 262.8664 | 305.9256 | 0.43457 | 43.0654 | 0.27513 | 8.1 | 7.7 | 8 | 268 | 294 | 297 | 304.3839 | -2.4862 | 8.5324 | 304.0538 | 11.8577 | 0.091 | 0.601 | 0.752 | 0.81431 | -8.2862 | 84.5238 | 0.80775 | 88.7341
[44 empty] | 1999-04-09 | 11:15 |  | 24 | 45 | 46 | 272 | 5.77 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 13.1697 | 13.4054 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 11:30 |  | 24 | 55 | 56 | 272 | 6.9 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 15.7489 | 16.0307 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 11:45 |  | 24 | 35 | 36 | 272 | 4.37 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 9.9743 | 10.1528 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 12:00 |  | 24 | 45 | 46 | 272 | 5.65 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 12.8958 | 13.1266 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 14:00 |  | 24 | 45 | 46 | 272 | 4.25 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 9.7004 | 9.874 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 14:30 |  | 24 | 55 | 56 | 272 | 5.43 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 12.3937 | 12.6155 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 14:45 |  | 24 | 35 | 36 | 272 | 3.35 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 7.6462 | 7.783 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-09 | 15:00 |  | 24 | 45 | 46 | 272 | 4.56 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 10.408 | 10.5942 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: C. Hill (7/30/99): NF200 was used during quarters 1, 2 and 3. NTR7450 was used during a second 3rd quarter and quarter 4.
Note on Q3: C. Rice 7/13/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Gary Puetz: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X20: C. Rice 7/19/99: All bromide concentrations verified by consultant.
Note on Z33: C. Rice 7/13/99: Feed MCAA values were verified and found to be correct.
Note on BX7: C. Rice 7/19/99: The pH meter had malfunctioned during the beginning of these experiments so no pH data was collected initially.
Note on CY3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were higher during this quarter, compared to the previous quarter.
Note on CY25: C. Rice 7/19/99: All bromide concentrations verified by consultant.
Note on DL3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were higher during this quarter, compared to the previous quarter.
Note on DN25: C. Rice 7/13/99: Consultant verified value.
Note on DV3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were higher during this quarter, compared to the previous quarter.
Note on DX25: C. Rice 7/13/99: Consultant verified value.
Note on EF3: Alison Gusses: All permeate TOC, UV, THM4 and HAA concentrations were verified by consultant. No explanation was given as to why these values were higher during this quarter, compared to the previous quarter.
Note on EH25: C. Rice 7/13/99: Consultant verified value.

## SR40. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.37391 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.82 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-05-13 | 1998-05-20 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.09 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.31 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.08 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 254 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [6 empty] | SDS-THM4F, ug/L | 566.1 | 566.1 | 566.1 | 566.1 | SDS-THM4F, ug/L | 566.1 | 566.1 | 566.1 | 566.1 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 24.25 | 24.25 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 5.15 | 48.2 | 49.7 | 38.7 | SDS-THM4p, ug/L | 5.15 | 48.2 | 49.7 | 38.7 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.5 | 8.17 | 8.335 | 3.9592 | 1998-04-28 | 12:00 | 0 | 23 | 51 | 50 | 263 | 6.3 | 3 | 9.3 | 0.18158 | 0.67742 | 27.2796 | 14.3794 | 15.0758 | 0 | 0 | 0 | 0 | 50.5 | 0.29853 | 1998-04-29 | 8:00 | 0 | 23 | 51 | 49 | 254 | 7.75 | 3.1 |  | 10.85 | 0.17537 | 0.71429 | 22.4101 | 17.689 | 18.5456 | 407.4374 | 252.125 | 402.6986 | 1.5294 | 48.4706 | 0.38262 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 219.9 | 219.9 | 219.9 | 219.9 | SDS-HAA5F, ug/L | 219.9 | 219.9 | 219.9 | 219.9 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-04-28 | 13:30 | 1.5 | 23 | 51 | 50 | 263 | 6.3 | 3 | 9.3 | 0.18158 | 0.67742 | 27.2796 | 14.3794 | 15.0758 | 0 | 0 | 0 | 0 | 50.5 | 0.29853 | 1998-04-29 | 9:00 | 1 | 23 | 52 | 50 | 254 | 7 | 2.1 |  | 9.1 | 0.17537 | 0.76923 | 26.9121 | 15.9771 | 16.7509 | 419.1844 | 259.6947 | 414.789 | 1.5729 | 49.4271 | 0.3389 | 7.46 | 7.48 | 7.49 | 156 | 300 | 247 | 764.8333 | -209.6491 | 47.3862 | 756.4439 | 79.3772 | BMRL | 0.641 | 0.658 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 1.9 | 10 | 8.2 | 4.8 | SDS-HAA5p, ug/L | 1.9 | 10 | 8.2 | 4.8 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 216 | 166 | 191 | 26.178 | 1998-04-28 | 14:30 | 2.5 | 23 | 51 | 50 | 263 | 7.14 | 3.87 | 11.01 | 0.18158 | 0.6485 | 22.8874 | 16.2967 | 17.0859 | 0 | 0 | 0 | 0 | 50.5 | 0.33834 | 1998-04-29 | 10:30 | 2.5 | 23 | 52 | 50 | 254 | 6.9 | 2.6 |  | 9.5 | 0.17537 | 0.72632 | 25.7368 | 15.7489 | 16.5116 | 409.6869 | 253.8499 | 405.4535 | 1.5372 | 49.4628 | 0.33382 | 7.49 |  |  | 233 |  |  | 465.0192 |  | 21.4165 | 461.8678 | 49.5527 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-04-30 | 1998-05-01 | --- | --- | 1998-05-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-02 | 1998-05-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-03 | 1998-05-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-04 | 1998-05-04 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1300 | 1300 | 1300 | 1300 | SDS-TOXF, ug Cl- /L | 1300 | 1300 | 1300 | 1300 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 294 | 299 | 296.5 | 1.6863 | 1998-04-28 | 15:30 | 3.5 | 23 | 52 | 51 | 263 | 7.22 | 1.3 | 8.52 | 0.18158 | 0.84742 | 29.8685 | 16.4793 | 17.2774 | 0 | 0 | 0 | 0 | 51.5 | 0.33548 | 1998-04-29 | 11:20 | 3.3333 | 23 | 50 | 49 | 254 | 6.7 | 2.85 |  | 9.55 | 0.17537 | 0.70157 | 25.5969 | 15.2924 | 16.033 | 404.3532 | 250.6221 | 400.2981 | 1.517 | 47.983 | 0.33414 | 7.5 |  |  | 231 |  |  | 450.4825 |  | 22.0911 | 447.5877 | 48.39 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 8:15 | 11:10 | --- | --- | 8:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:00 | 20:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:30 | 11:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | 67 | 59 | 41 | SDS-TOXp, ug Cl- /L | #DIV/0! | 67 | 59 | 41 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 200 | 190 | 195 | 5.1282 | 1998-04-28 | 16:30 | 4.5 | 23 | 51 | 50 | 263 | 7.11 | 4.88 | 11.99 | 0.18158 | 0.59299 | 20.9349 | 16.2282 | 17.0141 | 0 | 0 | 0 | 0 | 50.5 | 0.33691 | 1998-04-29 | 12:15 | 4.25 | 23 | 50 | 49 | 254 | 6.5 | 2.6 |  | 9.1 | 0.17537 | 0.71429 | 26.9121 | 14.8359 | 15.5544 | 406.9606 | 252.3157 | 403.0032 | 1.5267 | 47.9733 | 0.32423 | [11 empty] | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 24.25 | 51.17 | --- | --- | 24.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 84 | 84 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101 | 101 | --- | --- | --- | --- | --- | Cumulative time | hr | 123.5 | 123.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 18.77 | 18.77 | 18.77 | 18.77 | SDS-CDF, mg/L | 18.77 | 18.77 | 18.77 | 18.77 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 164 | 158 | 161 | 3.7267 | 1998-04-28 | 17:30 | 5.5 | 23 | 51 | 50 | 263 | 7.5 | 3.1 | 10.6 | 0.18158 | 0.70755 | 23.8113 | 17.1183 | 17.9474 | 0 | 0 | 0 | 0 | 50.5 | 0.35539 | 1998-04-29 | 13:45 | 5.75 | 23 | 50 | 48 | 254 | 6.6 | 2.6 |  | 9.2 | 0.17537 | 0.71739 | 26.6087 | 15.0641 | 15.7937 | 407.6592 | 252.71 | 403.6329 | 1.5294 | 47.4706 | 0.3327 |  |  |  | 238 |  |  | 445 |  | 19.7302 | 442.3106 | 46.1917 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 8.2 | 8.2 | 8.2 | 0 | 8.4 | --- | --- | --- | --- | --- | pH | --- | 8.2 | 8.6 | --- | --- | --- | --- | --- | pH | --- | 8.3 | 8.5 | --- | --- | --- | --- | --- | pH | --- | 8.4 | 8.5 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.355 | 4.42 | 3.5 | 2.45 | SDS-CDp, mg/L | 4.355 | 4.42 | 3.5 | 2.45 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.95 | 0.96 | 0.955 | 1.0471 | 1998-04-28 | 17:45 | 5.75 | 23 | 62.5 | 62 | 263 | 9.3 | 4.16 | 13.46 | 0.18158 | 0.69094 | 18.5394 | 21.2268 | 22.2548 | 0 | 0 | 0 | 0 | 62.25 | 0.35751 | 1998-04-29 | 15:15 | 7.25 | 23 | 50 | 48 | 254 | 6.5 | 2.85 |  | 9.35 | 0.17537 | 0.69519 | 26.1658 | 14.8359 | 15.5544 | 402.9468 | 249.8272 | 399.0284 | 1.5116 | 47.4884 | 0.32754 | 7.6 | 7.52 | 7.59 | 234 | 290 | 421 | 439.0439 | -4.286 | 21.0793 | 436.4203 | 46.382 | BMRL | 0.597 | 1.756 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 14.4 | 14.4 | 14.4 | 14.4 | TOCF, mg/L | 14.4 | 14.4 | 14.4 | 14.4 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | NA | #DIV/0! | #VALUE! | 1998-04-28 | 18:00 | 6 | 23 | 72 | 72 | 263 | 10.86 | 3.3 | 14.16 | 0.18158 | 0.76695 | 17.5734 | 24.7874 | 25.9878 | 0 | 0 | 0 | 0 | 72 | 0.36094 | 1998-04-29 | 17:00 | 9 | 23 | 50 | 48 | 254 | 6.3 | 3 |  | 9.3 | 0.17537 | 0.67742 | 26.3118 | 14.3794 | 15.0758 | 399.2138 | 247.5887 | 395.453 | 1.4974 | 47.5026 | 0.31737 | [27 empty] | Alkalinity | mg/L as CaCO3 | 152 | 170 | 161 | 11.1801 | 300 | 261 | 13 | 15.7068 | 259.7474 | 38.0167 | Alkalinity | mg/L as CaCO3 | 186 | 330 | 213.7778 | 35.2189 | 2.6178 | 213.492 | 12.8773 | Alkalinity | mg/L as CaCO3 | 190 | 258 | 192 | 25.5814 | 0.52356 | 191.9785 | 1.0306 | Alkalinity | mg/L as CaCO3 | 140 | 242 | 211.831 | 12.4665 | 26.7016 | 211.1238 | 33.6882 | TOCp, mg/L | #DIV/0! | 1 | 0.6 | BMRL | TOCp, mg/L | #DIV/0! | 1 | 0.6 | BMRL | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 14.4 | NA | 14.4 | #VALUE! | 1998-04-28 | 18:15 | 6.25 | 23 | 38 | 36 | 263 | 5.43 | 1.36 | 6.79 | 0.18158 | 0.79971 | 37.7334 | 12.3937 | 12.9939 | 0 | 0 | 0 | 0 | 37 | 0.35119 | 1998-04-30 | 8:15 | 24.25 | 23 | 48 | 48 | 254 | 6.3 | 2.87 |  | 9.17 | 0.17537 | 0.68702 | 26.699 | 14.3794 | 15.0758 | 401.1841 | 248.8106 | 397.4047 | 1.5048 | 46.4952 | 0.32424 | [27 empty] | Total dissolved solids | mg/L | 215 | 234 | 224.5 | 8.4633 | 389 | 464.5 | -19.4087 | 24.2833 | 461.4939 | 51.3536 | Total dissolved solids | mg/L | 260 | 429 | 462.7778 | -7.8736 | 12.3103 | 460.6914 | 43.5631 | Total dissolved solids | mg/L | 247 | 337 | 346 | -2.6706 | 16.6948 | 344.9357 | 28.3924 | Total dissolved solids | mg/L | 204 | 317 | 334.2817 | -5.4516 | 31.1973 | 332.999 | 38.7386 | UV254 F, cm-1 | 0.5225 | 0.5225 | 0.5225 | 0.5225 | UV254 F, cm-1 | 0.5225 | 0.5225 | 0.5225 | 0.5225 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.57 | 0.475 | 0.5225 | 18.1818 | 1998-04-28 | 18:30 | 6.5 | 23 | 50 | 48 | 263 | 7.23 | 2.4 | 9.63 | 0.18158 | 0.75078 | 26.3105 | 16.5021 | 17.3013 | 0 | 0 | 0 | 0 | 49 | 0.35309 | 1998-04-30 | 9:00 | 25 | 23 | 48 | 48 | 254 | 6.3 | 2.7 |  | 9 | 0.17537 | 0.7 | 27.2222 | 14.3794 | 15.0758 | 403.8775 | 250.4811 | 400.0728 | 1.5149 | 46.4851 | 0.32432 | 7.7 | 7.46 | 7.68 | 247 | 301 | 400 | 412 | -3 | 16.6948 | 409.9537 | 39.7493 | BMRL | 0.618 | 1.924 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 138 | 154 | 146 | 10.9589 | 382 | 309.3333 | 19.0227 | 25.1282 | 307.2875 | 52.4875 | Total hardness | mg/L as CaCO3 | 186 | 458 | 236 | 48.4716 | 4.6154 | 235.4856 | 21.0143 | Total hardness | mg/L as CaCO3 | 176 | 318 | 214 | 32.7044 | 9.7436 | 213.5915 | 17.5997 | Total hardness | mg/L as CaCO3 | 118 | 268 | 226.4507 | 15.5035 | 39.4872 | 225.3829 | 47.6447 | UV254 p, cm-1 | #DIV/0! | 0.028 | 0.017 | 0.01 | UV254 p, cm-1 | #DIV/0! | 0.028 | 0.017 | 0.01 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.9583 | NR | 3.9583 | #VALUE! | 1998-04-28 | 19:00 | 7 | 23 | 50 | 48 | 263 | 7.3 | 4.4 | 11.7 | 0.18158 | 0.62393 | 21.4786 | 16.6619 | 17.4688 | 0 | 0 | 0 | 0 | 49 | 0.35651 | 1998-04-30 | 10:00 | 26 | 23 | 50 | 48 | 254 | 6.3 | 2.7 |  | 9 | 0.17537 | 0.7 | 27.2222 | 14.3794 | 15.0758 | 403.8775 | 250.4811 | 400.0728 | 1.5149 | 47.4851 | 0.31749 | 7.59 |  |  | 246 |  |  | 414.3333 |  | 17.032 | 412.2457 | 40.3269 | 0.009 |  |  | 1.7207 |  | 98.2775 | 1.6994 | 99.4704 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 126 | 140 | 133 | 10.5263 | 348 | 226.3333 | 34.9617 | 17.3913 | 225.1643 | 40.932 | Calcium hardness | mg/L as CaCO3 | 158 | 420 | 174.6667 | 58.4127 | 1.8634 | 174.4952 | 9.4531 | Calcium hardness | mg/L as CaCO3 | 156 | 234 | 166 | 29.0598 | 3.1056 | 165.8925 | 5.9632 | Calcium hardness | mg/L as CaCO3 | 106 | 232 | 183.4648 | 20.9203 | 34.1615 | 182.7021 | 41.9821 | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | NA | 140 | #VALUE! | 1998-04-29 | 8:00 | 20 | 23 | 50.5 | 49 | 263 | 7.75 | 4.3 | 12.05 | 0.18158 | 0.64315 | 20.8257 | 17.689 | 18.5456 | 0 | 0 | 0 | 0 | 49.75 | 0.37278 | 1998-04-30 | 11:10 | 27.1667 | 23 | 50 | 48 | 254 | 6.5 | 2.7 |  | 9.2 | 0.17537 | 0.70652 | 26.6087 | 14.8359 | 15.5544 | 405.3193 | 251.2981 | 401.3778 | 1.5205 | 47.4795 | 0.3276 | [27 empty] | Turbidity | ntu | 0.11 | 0.07 | 0.09 | 44.4444 | 1.48 | 2.9733 | -100.9009 | 90.5759 | 2.9372 | 96.9359 | Turbidity | ntu | 0.08 | 1.8 | 4.9411 | -174.5062 | 91.623 | 4.8911 | 98.3644 | Turbidity | ntu | 0.07 | 1.33 | 1.84 | -38.3459 | 92.6702 | 1.821 | 96.1559 | Turbidity | ntu | 0.07 | 1.18 | 1.3165 | -11.566 | 92.6702 | 1.3042 | 94.6328 | Bromidep, ug/L | 130 | 130 | 120 | 110 | Bromidep, ug/L | 130 | 130 | 120 | 110 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 20 | 20 | 20 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-30 | 12:20 | 28.3333 | 23 | 50 | 48 | 254 | 6.3 | 2.85 |  | 9.15 | 0.17537 | 0.68852 | 26.7596 | 14.3794 | 15.0758 | 401.4939 | 249.0028 | 397.7116 | 1.506 | 47.494 | 0.31743 | 7.61 |  |  | 246 |  |  | 408.1316 |  | 17.032 | 406.1209 | 39.4269 | 0.009 |  |  | 1.6576 |  | 98.2775 | 1.6372 | 99.4503 | [8 empty] | Ammonia | mg NH3-N / L | 0.8 | 0.75 | 0.775 | 6.4516 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.39 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.22 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.08 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 191 | 191 | 191 | 191 | AlkF, mg/L CaCO3 | 191 | 191 | 191 | 191
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.23 | 1.23 | 1.23 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-30 | 13:55 | 29.9167 | 23 | 50 | 48 | 254 | 6.3 | 2.75 |  | 9.05 | 0.17537 | 0.69613 | 27.0663 | 14.3794 | 15.0758 | 403.071 | 249.9809 | 399.2739 | 1.5119 | 47.4881 | 0.31747 | 7.63 | 7.49 | 7.69 | 245 | 297 | 403 | 414.4818 | -2.8491 | 17.3693 | 412.38 | 40.5888 | BMRL | 0.635 | 1.742 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 45.5 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 1 | 105.9 | 75.4444 | 28.7588 | 93.0556 | 74.6785 | 98.6609 | Total organic carbon | mg/L | 0.6 | 25.7 | 28.2 | -9.7276 | 95.8333 | 27.9033 | 97.8497 | Total organic carbon | mg/L | BMRL | 19.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 161 | 186 | 190 | 140 | Alkp, mg/L CaCO3 | 161 | 186 | 190 | 140
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 18.77 | 18.77 | 18.77 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-30 | 15:30 | 31.5 | 23 | 49 | 48 | 254 | 6.3 | 2.8 |  | 9.1 | 0.17537 | 0.69231 | 26.9121 | 14.3794 | 15.0758 | 402.2766 | 249.4882 | 398.487 | 1.5089 | 46.9911 | 0.32082 | [27 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 1.748 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.028 | 3.934 | 2.7752 | 29.4555 | 94.6411 | 2.747 | 98.9807 | UV254 | cm-1 | 0.017 | 1.132 | 1.028 | 9.1873 | 96.7464 | 1.0171 | 98.3286 | UV254 | cm-1 | 0.01 | 0.809 | 0.73183 | 9.5388 | 98.0861 | 0.72472 | 98.6202 | T-HdF, mg/L CaCO3 | 195 | 195 | 195 | 195 | T-HdF, mg/L CaCO3 | 195 | 195 | 195 | 195
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-30 | 16:20 | 32.3333 | 23 | 49 | 48 | 254 | 6.3 | 2.75 |  | 9.05 | 0.17537 | 0.69613 | 27.0663 | 14.3794 | 15.0758 | 403.071 | 249.9809 | 399.2739 | 1.5119 | 46.9881 | 0.32084 | [27 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.8418 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8 | 3.7148 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8333 | 4.4047 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.2356 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 146 | 186 | 176 | 118 | T-Hdp, mg/L CaCO3 | 146 | 186 | 176 | 118
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.7 | 8.7 | 8.7 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-30 | 18:15 | 34.25 | 23 | 49 | 48 | 254 | 6.3 | 2.75 |  | 9.05 | 0.17537 | 0.69613 | 27.0663 | 14.3794 | 15.0758 | 403.071 | 249.9809 | 399.2739 | 1.5119 | 46.9881 | 0.32084 | [27 empty] | Bromide | mg/L | 130 | 130 | 130 | 0 | --- | 163.3333 | --- | 7.1429 | 162.9158 | 20.2042 | Bromide | mg/L | 130 | --- | 185.5556 | --- | 7.1429 | 184.9839 | 29.7236 | Bromide | mg/L | 120 | --- | 160 | --- | 14.2857 | 159.57 | 24.7979 | Bromide | mg/L | 110 | --- | 152.2535 | --- | 21.4286 | 151.8375 | 27.5541 | Ca-HdF, mg/L CaCO3 | 161 | 161 | 161 | 161 | Ca-HdF, mg/L CaCO3 | 161 | 161 | 161 | 161
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 8:30 | 48.5 | 23 | 50 | 48 | 254 | 6.13 | 2.65 |  | 8.78 | 0.17537 | 0.69818 | 27.9294 | 13.9914 | 14.669 | 403.4352 | 250.2719 | 399.7387 | 1.5132 | 47.4868 | 0.30891 | 7.71 | 7.73 | 7.7 | 250 | 303 | 395 | 404.0642 | -2.2947 | 15.683 | 402.2051 | 37.8427 | 0.011 | 0.634 | 1.943 | 1.7057 | 12.2128 | 97.8947 | 1.6853 | 99.3473 | [8 empty] | SDS-Cl2 dose | mg/L | 4.5 | 4.5 | 4.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 133 | 158 | 156 | 106 | Ca-Hdp, mg/L CaCO3 | 133 | 158 | 156 | 106
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 1300 | NA | 1300 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 10:20 | 50.3333 | 23 | 50 | 48 | 254 | 6.13 | 2.63 |  | 8.76 | 0.17537 | 0.69977 | 27.9954 | 13.9914 | 14.669 | 403.7676 | 250.4782 | 400.0682 | 1.5144 | 47.4856 | 0.30891 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.16 | 0.13 | 0.145 | 20.6897 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.08 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.05 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 490 | NA | 490 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 11:10 | 51.1667 | 23 | 50 | 48 | 254 | 6.25 | 2.58 |  | 8.83 | 0.17537 | 0.70781 | 27.7656 | 14.2653 | 14.9562 | 405.4983 | 251.5055 | 401.7091 | 1.521 | 47.479 | 0.31501 | 7.69 |  |  | 256 |  |  | 394.6105 |  | 13.6594 | 392.9051 | 34.8443 | 0.01 |  |  | 1.764 |  | 98.0861 | 1.7424 | 99.4261 | [8 empty] | SDS-Cl2 demand | mg/L | 4.34 | 4.37 | 4.355 | 0.68886 | --- | 52.405 | --- | 76.7981 | 51.8031 | 91.5932 | SDS-Cl2 demand | mg/L | 4.42 | --- | 84.1422 | --- | 76.4518 | 83.322 | 94.6953 | SDS-Cl2 demand | mg/L | 3.5 | --- | 34.04 | --- | 81.3532 | 33.7117 | 89.6178 | SDS-Cl2 demand | mg/L | 2.45 | --- | 25.4359 | --- | 86.9473 | 25.2096 | 90.2815 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 69 | NA | 69 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 12:15 | 52.25 | 23 | 50 | 48 | 254 | 6.14 | 2.75 |  | 8.89 | 0.17537 | 0.69066 | 27.5714 | 14.0142 | 14.6929 | 401.8789 | 249.3026 | 398.1906 | 1.5073 | 47.4927 | 0.30937 | [27 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 88.0827 | 95.4045 | 95.6816 | 93.686 | Qp/QT (THM4), % | 94.5004 | 102.3557 | 102.653 | 100.5119
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 7.1 | NA | 7.1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 13:00 | 53 | 23 | 50 | 48 | 254 | 6.05 | 2.6 |  | 8.65 | 0.17537 | 0.69942 | 28.3642 | 13.8088 | 14.4776 | 403.6654 | 250.4454 | 400.0159 | 1.514 | 47.486 | 0.30488 | 7.66 |  |  | 250 |  |  | 404.7019 |  | 15.683 | 402.8595 | 37.9436 | 0.01 |  |  | 1.715 |  | 98.0861 | 1.6947 | 99.4099 | [8 empty] | SDS-Chlorination pH | --- | 8.6 | 8.8 | 8.7 | 2.2989 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.7 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.9 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | NA | NA
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 14:30 | 54.5 | 23 | 50 | 48 | 254 | 6 | 2.8 |  | 8.8 | 0.17537 | 0.68182 | 27.8636 | 13.6947 | 14.3579 | 400.0089 | 248.1958 | 396.4228 | 1.5002 | 47.4998 | 0.30227 | 7.64 | 7.62 | 7.66 | 251 | 297 | 394 | 394 | 0 | 15.3457 | 392.311 | 36.0202 | 0.009 | 0.628 | 1.746 | 1.6229 | 7.0529 | 98.2775 | 1.6038 | 99.4388 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 27.8797 | 19.6459 | 17.342 | 18.3814 | SDS-HAA5b, ug/L | 13.8891 | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 566.1 | NA | 566.1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 16:00 | 56 | 23 | 50 | 48 | 254 | 6 | 2.76 |  | 8.76 | 0.17537 | 0.68493 | 27.9954 | 13.6947 | 14.3579 | 400.6476 | 248.5921 | 397.0557 | 1.5026 | 47.4974 | 0.30229 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | 67 | --- | 6917 | --- | 94.8462 | 6846.5205 | 99.0214 | SDS-TOX | mg Cl- /L | 59 | --- | 2541 | --- | 95.4615 | 2514.3161 | 97.6534 | SDS-TOX | mg Cl- /L | 41 | --- | 1814.2394 | --- | 96.8462 | 1796.7809 | 97.7181 | SDS-TOXb, ug Cl- /L | #DIV/0! | 123.6623 | 112.5908 | 120.4932 | SDS-TOXb, ug Cl- /L | #DIV/0! | NA | NA | NA
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 8.6 | NA | 8.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 17:00 | 57 | 23 | 50 | 48 | 254 | 6 | 2.6 |  | 8.6 | 0.17537 | 0.69767 | 28.5349 | 13.6947 | 14.3579 | 403.2831 | 250.2273 | 399.6676 | 1.5125 | 47.4875 | 0.30235 | [27 empty] | SDS-CHCl3 | mg/L | 2.5 | 3.2 | 2.85 | 24.5614 | --- | 1626.6833 | --- | 99.4184 | 1606.3439 | 99.8226 | SDS-CHCl3 | mg/L | 7.9 | --- | 2686.2333 | --- | 98.3878 | 2658.676 | 99.7029 | SDS-CHCl3 | mg/L | 5.3 | --- | 974.7 | --- | 98.9184 | 964.278 | 99.4504 | SDS-CHCl3 | mg/L | 2.9 | --- | 688.9563 | --- | 99.4082 | 682.2017 | 99.5749 | SDS-CDb, mg/L | 6.0729 | 5.0795 | 4.1594 | 3.4804 | SDS-CDb, mg/L | 5.1478 | NA | NA | NA
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 120 | NA | 120 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-01 | 21:30 | 61.5 | 23 | 50 | 48 | 254 | 6 | 2.6 |  | 8.6 | 0.17537 | 0.69767 | 28.5349 | 13.6947 | 14.3579 | 403.2831 | 250.2273 | 399.6676 | 1.5125 | 47.4875 | 0.30235 | [27 empty] | SDS-BDCM | mg/L | 1.5 | 2 | 1.75 | 28.5714 | --- | 225.9167 | --- | 97.4638 | 223.1088 | 99.2156 | SDS-BDCM | mg/L | 9.3 | --- | 340.9667 | --- | 86.5217 | 337.5542 | 97.2449 | SDS-BDCM | mg/L | 9.4 | --- | 128.6 | --- | 86.3768 | 127.3185 | 92.6169 | SDS-BDCM | mg/L | 5.8 | --- | 94.8141 | --- | 91.5942 | 93.9377 | 93.8257 | TOCb, mg/L | #DIV/0! | 1.6158 | 1.1959 | #VALUE! | TOCb, mg/L | #DIV/0! | NA | NA | NA
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 89 | NA | 89 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 8:00 | 72 | 23 | 50 | 48 | 254 | 6 | 2.5 |  | 8.5 | 0.17537 | 0.70588 | 28.8824 | 13.6947 | 14.3579 | 404.999 | 251.2921 | 401.3682 | 1.5189 | 47.4811 | 0.30239 | [27 empty] | SDS-DBCM | mg/L | BMRL | 1.1 | 1.1 | #VALUE! | --- | 21.1 | --- | 84.507 | 20.8495 | 94.7241 | SDS-DBCM | mg/L | 15 | --- | -28.8889 | --- | -111.2676 | -28.4373 | 152.7476 | SDS-DBCM | mg/L | 18 | --- | -3.8 | --- | -153.5211 | -3.5656 | 604.8197 | SDS-DBCM | mg/L | 14 | --- | 4.2817 | --- | -97.1831 | 4.3774 | -219.8266 | UV254 b, cm-1 | #DIV/0! | 0.050725 | 0.038829 | 0.042359 | UV254 b, cm-1 | #DIV/0! | NA | NA | NA
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | 1 | NA | 1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 9:00 | 73 | 23 | 50 | 48 | 263 | 6.17 | 2.55 |  | 8.72 | 0.18158 | 0.70757 | 29.1606 | 14.0827 | 14.7647 | 405.3381 | 251.5183 | 401.7295 | 1.5202 | 47.4798 | 0.31097 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 16 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 17 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 16 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 131.1917 | 130.4595 | 120.8637 | 111.8942 | Bromideb, ug/L | 130.55 | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.3 | NA | 1.3 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 10:00 | 74 | 23 | 50 | 48 | 263 | 6 | 2.6 |  | 8.6 | 0.18158 | 0.69767 | 29.5814 | 13.6947 | 14.3579 | 403.2085 | 250.2597 | 399.7192 | 1.512 | 47.488 | 0.30235 | [27 empty] | SDS-THM4 | mg/L | 4 | 6.3 | 5.15 | 44.6602 | --- | 1874.9833 | --- | 99.0903 | 1851.5626 | 99.7219 | SDS-THM4 | mg/L | 48.2 | --- | 2925.4222 | --- | 91.4856 | 2895.8186 | 98.3355 | SDS-THM4 | mg/L | 49.7 | --- | 1082.5 | --- | 91.2206 | 1071.3964 | 95.3612 | SDS-THM4 | mg/L | 38.7 | --- | 781.5169 | --- | 93.1638 | 774.2035 | 95.0013 | Alkb, mg/L CaCO3 | 164.5752 | 186.2298 | 190.0432 | 143.2201 | Alkb, mg/L CaCO3 | 162.6499 | NA | NA | NA
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 16 | NA | 16 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 11:00 | 75 | 23 | 50 | 48 | 263 | 6 | 0.86 |  | 6.86 | 0.18158 | 0.87464 | 37.3382 | 13.6947 | 14.3579 | 443.7128 | 275.3995 | 439.873 | 1.6639 | 47.3361 | 0.30332 |  | 7.58 |  | 250 | 303 | 427 | 620.9186 | -45.4142 | 15.683 | 616.6876 | 59.4608 | 0.022 | 0.635 |  | 4.0144 |  | 95.7895 | 3.9688 | 99.4457 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 151.8395 | 186.4136 | 176.8205 | 122.8618 | T-Hdb, mg/L CaCO3 | 148.6948 | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 11:20 | 75.3333 | 23 | 50 | 48 | 263 | 5.65 | 0.86 |  | 6.51 | 0.18158 | 0.8679 | 39.3994 | 12.8958 | 13.5204 | 441.8385 | 274.3777 | 438.2409 | 1.6566 | 47.3434 | 0.28558 | 7.59 |  |  | 251 |  |  | 595.4244 |  | 15.3457 | 591.7248 | 57.5816 | 0.023 |  |  | 3.8041 |  | 95.5981 | 3.7635 | 99.3889 | [8 empty] | SDS-DCAA* | mg/L | 1.7 | 2.1 | 1.9 | 21.0526 | --- | 395.5667 | --- | 98.4167 | 390.6358 | 99.5136 | SDS-DCAA* | mg/L | 3.2 | --- | 652.0889 | --- | 97.3333 | 645.4125 | 99.5042 | SDS-DCAA* | mg/L | 2.2 | --- | 237.8 | --- | 98.1667 | 235.2671 | 99.0649 | SDS-DCAA* | mg/L | 1 | --- | 168.6056 | --- | 99.1667 | 166.9555 | 99.401 | Ca-Hdb, mg/L CaCO3 | 136.3368 | 158.1379 | 156.2159 | 109.4727 | Ca-Hdb, mg/L CaCO3 | 134.5399 | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 11:40 | 75.6667 | 23 | 50 | 48 | 263 | 5.66 | 0.86 |  | 6.52 | 0.18158 | 0.8681 | 39.3374 | 12.9186 | 13.5443 | 441.8943 | 274.4083 | 438.2898 | 1.6568 | 47.3432 | 0.28609 | 7.65 |  |  | 259 |  |  | 543.3023 |  | 12.6476 | 540.2431 | 52.0586 | 0.025 |  |  | 3.7967 |  | 95.2153 | 3.7562 | 99.3344 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.6 | --- | 487.1556 | --- | 98.2022 | 482.1597 | 99.6682 | SDS-TCAA* | mg/L | 1 | --- | 177 | --- | 98.8764 | 175.1078 | 99.4289 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 12 | NA | 12 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 19:00 | 83 | 23 | 49 | 48 | 263 | 5.6 | 0.39 |  | 5.99 | 0.18158 | 0.93489 | 42.9065 | 12.7817 | 13.4007 | 459.1842 | 285.1702 | 455.4789 | 1.7216 | 46.7784 | 0.28647 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 219.9 | NA | 219.9 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 20:00 | 84 | 23 | 49 | 48 | 263 | 5.66 | 1.13 |  | 6.79 | 0.18158 | 0.83358 | 37.7334 | 12.9186 | 13.5443 | 433.4425 | 269.1599 | 429.907 | 1.6251 | 46.8749 | 0.28895 |  |  |  |  | 299 | [22 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 5.2 | --- | -16.4667 | --- | -300 | -16.2437 | 132.0123 | SDS-DBAA* | mg/L | 5 | --- | -2.4 | --- | -284.6154 | -2.3204 | 315.4761 | SDS-DBAA* | mg/L | 3.8 | --- | 0.27887 | --- | -192.3077 | 0.31354 | -1111.964 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 235.9 | NA | 235.9 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-02 | 21:00 | 85 | 23 | 49 | 48 | 263 | 5.5 | 1.2 |  | 6.7 | 0.18158 | 0.8209 | 38.2537 | 12.5535 | 13.1614 | 430.3427 | 267.298 | 426.933 | 1.6134 | 46.8866 | 0.28071 |  |  |  | 264 |  |  | 445.4583 |  | 10.9612 | 443.561 | 40.4817 | [16 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 3 | --- | 75.2222 | --- | 81.25 | 74.4791 | 95.972 | SDS-BCAA* | mg/L | 3.1 | --- | 28.9 | --- | 80.625 | 28.6226 | 89.1694 | SDS-BCAA* | mg/L | 1.8 | --- | 21.8 | --- | 88.75 | 21.6031 | 91.6679 | Qp/QT (HAA5), % | 76.1009 | 79.0376 | 78.3656 | 77.1269 | Qp/QT (HAA5), % | 88.4862 | 91.9009 | 91.1195 | 89.6792
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-03 | 10:00 | 98 | 23 | 49 | 48 | 263 | 5.11 | 1.2 |  | 6.31 | 0.18158 | 0.80983 | 40.6799 | 11.6633 | 12.2282 | 427.5611 | 265.7224 | 424.4166 | 1.6027 | 46.8973 | 0.26074 | 7.59 | 7.54 |  | 264 | 296 |  | 434.8958 |  | 10.9612 | 433.2356 | 39.0632 | 0.036 |  |  | 2.5942 |  | 93.11 | 2.5693 | 98.5989 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 139.2119 | 156.7641 | 161.42 | 159.3326 | SDS-THM4b, ug/L | 69.7364 | 90.1452 | 95.5589 | 93.1318
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-03 | 10:30 | 98.5 | 23 | 50 | 49 | 263 | 5.3 | 6.08 |  | 11.38 | 0.18158 | 0.46573 | 22.1107 | 12.097 | 12.6828 | 359.9903 | 223.6658 | 357.2431 | 1.3495 | 48.1505 | 0.2634 |  |  | 7.65 |  | 300 | 466 |  | #VALUE! | [19 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-03 | 11:00 | 99 | 23 | 50 | 49 | 263 | 5.62 | 6.2 |  | 11.82 | 0.18158 | 0.47547 | 21.2504 | 12.8273 | 13.4486 | 361.6703 | 224.6039 | 358.7414 | 1.356 | 48.144 | 0.27934 | 7.61 |  |  | 259 |  | 410 | 330.4919 | 19.3922 | 12.6476 | 329.7281 | 21.4504 | 0.031 |  |  | 0.96802 |  | 94.067 | 0.95801 | 96.7641 | [8 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | 1.1 | --- | 61.6556 | --- | 90.8333 | 61.0325 | 98.1977 | SDS-DCBAA | mg/L | 1.2 | --- | 22.8 | --- | 90 | 22.5678 | 94.6827 | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | 325.4659 | 327.4828 | 328.9721 | SDS-TOXb, ug Cl- /L | #DIV/0! | 166.8618 | 169.2069 | 170.9386
[44 empty] | 1998-05-03 | 11:30 | 99.5 | 23 | 50.5 | 49.5 | 263 | 5.7 | 6.08 |  | 11.78 | 0.18158 | 0.48387 | 21.326 | 13.0099 | 13.64 | 363.0969 | 225.4633 | 360.114 | 1.3614 | 48.6386 | 0.28044 | 7.6 |  | 7.7 | 249 |  | 373 | 341.0312 | 8.5707 | 16.0202 | 340.034 | 26.772 | 0.025 |  |  | 0.98891 |  | 95.2153 | 0.97846 | 97.445 | [8 empty] | SDS-HAA5 | mg/L | 1.7 | 2.1 | 1.9 | 21.0526 | --- | 728.5667 | --- | 99.136 | 719.4647 | 99.7359 | SDS-HAA5 | mg/L | 10 | --- | 1176.1111 | --- | 95.4525 | 1164.113 | 99.141 | SDS-HAA5 | mg/L | 8.2 | --- | 431.6 | --- | 96.271 | 427.048 | 98.0798 | SDS-HAA5 | mg/L | 4.8 | --- | 307.7577 | --- | 97.8172 | 304.775 | 98.4251 | SDS-CDb, mg/L | 7.8001 | 7.4281 | 6.8036 | 6.1829 | SDS-CDb, mg/L | 6.0147 | 5.5822 | 4.8561 | 4.1344
[44 empty] | 1998-05-03 | 12:00 | 100 | 23 | 50.5 | 49.5 | 263 | 5.75 | 6 |  | 11.75 | 0.18158 | 0.48936 | 21.383 | 13.1241 | 13.7597 | 364.0347 | 226.029 | 361.0175 | 1.365 | 48.635 | 0.28292 |  |  |  | 246 |  | 343 | 344.8958 | -0.55272 | 17.032 | 343.8147 | 28.4498 | 0.022 | 0.63 |  | 1.0021 |  | 95.7895 | 0.99143 | 97.781 | [8 empty] | SDS-HAA6 | mg/L | 1.7 | 2.1 | 1.9 | 21.0526 | --- | 781.9 | --- | 99.1946 | 772.13 | 99.7539 | SDS-HAA6 | mg/L | 13 | --- | 1251.3333 | --- | 94.4892 | 1238.5922 | 98.9504 | SDS-HAA6 | mg/L | 11.3 | --- | 460.5 | --- | 95.2098 | 455.6707 | 97.5201 | SDS-HAA6 | mg/L | 6.6 | --- | 329.5577 | --- | 97.2022 | 326.378 | 97.9778 | TOCb, mg/L | #DIV/0! | 3.809 | 3.5855 | #VALUE! | TOCb, mg/L | #DIV/0! | 2.0853 | 1.8255 | #VALUE!
[44 empty] | 1998-05-03 | 12:30 | 100.5 | 23 | 50.5 | 49.5 | 263 | 5.75 | 6 |  | 11.75 | 0.18158 | 0.48936 | 21.383 | 13.1241 | 13.7597 | 364.0347 | 226.029 | 361.0175 | 1.365 | 48.635 | 0.28292 | 7.61 |  |  | 244 |  |  | 346.8125 |  | 17.7066 | 345.6886 | 29.4162 | 0.02 |  |  | 1.0041 |  | 96.1722 | 0.99331 | 97.9865 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.13166 | 0.12636 | 0.12722 | UV254 b, cm-1 | #DIV/0! | 0.06805 | 0.061891 | 0.062894
[44 empty] | 1998-05-03 | 13:00 | 101 | 23 | 50.5 | 49.5 | 263 | 5.83 | 5.9 |  | 11.73 | 0.18158 | 0.49702 | 21.4211 | 13.3067 | 13.9511 | 365.3527 | 226.8206 | 362.2818 | 1.37 | 48.63 | 0.28688 |  |  |  | 243 |  |  | 349.3653 |  | 18.0438 | 348.1863 | 30.2098 | 0.02 |  | 1.651 | 1.019 | 38.2775 | 96.1722 | 1.008 | 98.0158 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 132.3899 | 132.0962 | 124.3269 | 116.8619 | Bromideb, ug/L | 131.1514 | 130.8099 | 121.7761 | 113.0962
[44 empty] | 1998-05-03 | 13:30 | 101.5 | 23 | 50.5 | 49.5 | 263 | 5.8 | 5.95 |  | 11.75 | 0.18158 | 0.49362 | 21.383 | 13.2382 | 13.8793 | 364.7673 | 226.4671 | 361.7174 | 1.3678 | 48.6322 | 0.28539 |  |  |  | 244 |  |  | 347.6765 |  | 17.7066 | 346.5333 | 29.5883 | 0.019 |  |  | 1.0133 |  | 96.3636 | 1.0023 | 98.1044 | [47 empty] | Alkb, mg/L CaCO3 | 168.1697 | 187.0481 | 190.2163 | 151.6653 | Alkb, mg/L CaCO3 | 164.4541 | 186.405 | 190.0888 | 145.2636
[44 empty] | 1998-05-03 | 14:00 | 102 | 23 | 50.5 | 49.5 | 263 | 5.8 | 5.9 |  | 11.7 | 0.18158 | 0.49573 | 21.4786 | 13.2382 | 13.8793 | 365.1266 | 226.6902 | 362.0736 | 1.3691 | 48.6309 | 0.2854 | [66 empty] | T-Hdb, mg/L CaCO3 | 157.7106 | 187.8866 | 180.1105 | 135.6123 | T-Hdb, mg/L CaCO3 | 151.6417 | 186.7289 | 177.6873 | 125.947
[44 empty] | 1998-05-04 | 7:00 | 119 | 23 | 50.5 | 50 | 263 | 5.57 | 4.31 |  | 9.88 | 0.18158 | 0.56377 | 25.6194 | 12.7132 | 13.3289 | 377.0494 | 234.1718 | 374.0234 | 1.4136 | 48.8364 | 0.27293 | 7.63 | 7.6 | 7.67 | 248 | 301 | 358 | 359.1787 | -0.32923 | 16.3575 | 358.0013 | 30.7265 | 0.018 | 0.63 | 1.307 | 1.1745 | 10.1387 | 96.555 | 1.1622 | 98.4513 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 139.6917 | 158.6289 | 157.0817 | 118.5802 | Ca-Hdb, mg/L CaCO3 | 136.2239 | 158.243 | 156.444 | 111.6764
[44 empty] | 1998-05-04 | 7:30 | 119.5 | 23 | 50 | 49 | 263 | 5.57 | 5.87 |  | 11.44 | 0.18158 | 0.48689 | 21.9895 | 12.7132 | 13.3289 | 363.5804 | 225.8067 | 360.6625 | 1.3631 | 48.1369 | 0.2769 |  |  |  | 249 |  |  | 341.5724 |  | 16.0202 | 340.5921 | 26.892 | 0.019 |  |  | 1.0003 |  | 96.3636 | 0.98988 | 98.0806 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-05-04 | 8:30 | 120.5 | 23 | 50.5 | 50 | 263 | 5.5 | 5.87 |  | 11.37 | 0.18158 | 0.48373 | 22.131 | 12.5535 | 13.1614 | 363.0337 | 225.4904 | 360.1573 | 1.3611 | 48.8889 | 0.26921 | 7.55 |  |  | 247 |  |  | 342.8799 |  | 16.6948 | 341.8774 | 27.7519 | 0.017 |  |  | 0.99614 |  | 96.7464 | 0.9859 | 98.2757 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-05-04 | 9:30 | 121.5 | 23 | 50.5 | 49 | 263 | 5.49 | 14.7 |  | 20.19 | 0.18158 | 0.27192 | 12.0263 | 12.5306 | 13.1375 | 330.5533 | 205.319 | 327.9391 | 1.2393 | 48.5107 | 0.27082 |  |  |  | 245 |  | 334 | 315.7337 | 5.469 | 17.3693 | 314.9954 | 22.2211 | 0.015 |  | 1.006 | 0.71204 | 29.2211 | 97.1292 | 0.70476 | 97.8716 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-05-04 | 10:00 | 122 | 23 | 50.5 | 49.5 | 263 | 5.55 | 14.35 |  | 19.9 | 0.18158 | 0.27889 | 12.2161 | 12.6676 | 13.2811 | 331.5361 | 205.9112 | 328.8851 | 1.243 | 48.757 | 0.27239 | 7.57 |  | 7.62 | 230 |  | 326 | 322.2195 | 1.1597 | 22.4283 | 321.2465 | 28.4039 | 0.014 |  | 0.885 | 0.71917 | 18.7382 | 97.3206 | 0.71173 | 98.033 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-05-04 | 10:30 | 122.5 | 23 | 50.5 | 50 | 281 | 5.64 | 14.31 |  | 19.95 | 0.19401 | 0.28271 | 13.0852 | 12.873 | 13.4964 | 332.0464 | 206.3105 | 329.5227 | 1.2447 | 49.0053 | 0.27541 | 7.59 |  |  | 230 |  |  | 322.7096 |  | 22.4283 | 321.7792 | 28.5224 | 0.014 |  |  | 0.72292 |  | 97.3206 | 0.7158 | 98.0441 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-05-04 | 11:00 | 123 | 23 | 51 | 50 | 281 | 5.6 | 13.6 |  | 19.2 | 0.19401 | 0.29167 | 13.6354 | 12.7817 | 13.4007 | 333.3091 | 207.1064 | 330.7941 | 1.2495 | 49.2505 | 0.27209 | 7.62 |  | 7.61 | 231 |  | 324 | 323.4706 | 0.1634 | 22.0911 | 322.5492 | 28.383 | 0.013 |  | 0.849 | 0.73229 | 13.7463 | 97.512 | 0.72513 | 98.2072 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-05-04 | 11:30 | 123.5 | 23 | 51 | 50 | 281 | 5.6 | 13.52 |  | 19.12 | 0.19401 | 0.29289 | 13.6967 | 12.7817 | 13.4007 | 333.4823 | 207.214 | 330.966 | 1.2501 | 49.2499 | 0.2721 | 7.58 |  |  | 229 |  |  | 324.4586 |  | 22.7656 | 323.5074 | 29.2134 | 0.013 |  |  | 0.73354 |  | 97.512 | 0.72636 | 98.2102 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-05-04 | 12:30 | 124.5 | 23 | 51 | 50 | 281 | 5.56 | 13.25 |  | 18.81 | 0.19401 | 0.29559 | 13.9389 | 12.6904 | 13.305 | 333.8625 | 207.4617 | 331.3615 | 1.2515 | 49.2485 | 0.27016 |  |  |  | 228 |  |  | 325.2442 |  | 23.1029 | 324.2821 | 29.6908 | 0.013 |  |  | 0.7363 |  | 97.512 | 0.72914 | 98.2171 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-05-04 | 13:30 | 125.5 | 23 | 51 | 50 | 281 | 5.67 | 13.5 |  | 19.17 | 0.19401 | 0.29577 | 13.6583 | 12.9415 | 13.5682 | 333.8996 | 207.4533 | 331.3482 | 1.2517 | 49.2483 | 0.27551 | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-05-04 | 14:30 | 126.5 | 23 | 51 | 50 | 281 | 5.56 | 13.64 |  | 19.2 | 0.19401 | 0.28958 | 13.6354 | 12.6904 | 13.305 | 333.0101 | 206.932 | 330.5155 | 1.2483 | 49.2517 | 0.27014 | 7.61 | 7.61 | 7.64 | 231 | 295 | 321 | 323.1994 | -0.68518 | 22.0911 | 322.2873 | 28.3248 | 0.013 | 0.625 | 0.837 | 0.73018 | 12.7617 | 97.512 | 0.72309 | 98.2022 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-05-05 | 8:30 | 144.5 | 23 | 51 | 50 | 281 | 5.56 | 13.64 | X | 19.2 | 0.19401 | 0.28958 | 13.6354 | 12.6904 | 13.305 | 333.0101 | 206.932 | 330.5155 | 1.2483 | 49.2517 | 0.27014 | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-05-05 | 9:30 |  | 23 | 40.5 | 40 | 281 | 6 | 19.35 |  | 25.35 | 0.19401 | 0.23669 | 10.0848 | 13.6947 | 14.3579 | 325.7164 | 202.2772 | 323.0807 | 1.2212 | 39.0288 | 0.36788 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-05-05 | 9:45 |  | 23 | 50 | 49.5 | 281 | 7.73 | 21.78 |  | 29.51 | 0.19401 | 0.26195 | 8.5222 | 17.6433 | 18.4978 | 329.3203 | 204.0258 | 325.8736 | 1.2357 | 48.5143 | 0.38129
[44 empty] | 1998-05-05 | 10:10 |  | 23 | 60 | 59 | 281 | 9.36 | 25 |  | 34.36 | 0.19401 | 0.27241 | 7.1781 | 21.3637 | 22.3983 | 330.925 | 204.5529 | 326.7156 | 1.2427 | 58.2573 | 0.38447
[44 empty] | 1998-05-05 | 10:25 |  | 23 | 70 | 69 | 281 | 11.11 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 25.358 | 26.5861 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: Alison Gusses: Permeate sample during 70% run appeared to have high ammonia demand - DBP data from 70% run is "questionable" and should probably be discarded
Note on Q3: C. Rice 7/9/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used for this study
Note on X11: C. Rice 7/19/99: Alkalinity verified by consultant.
Note on X13: C. Rice 7/19/99: Total hardness verified by consultant.
Note on X14: C. Rice 7/19/99: Calcium hardness verified by consultant.
Note on CZ9: C. Rice 7/9/99: Consultant verified that all water quality parameters for Run 1 were checked and found to be correct. No explanation was given as to why many concentrations appear low relative to concentrations for the other three runs.
Note on DG10: C. Rice 7/19/99: Consultant verified alkalinity, total hardness and calcium hardness due to consistently high mass balance closure errors.
Note on DQ10: C. Rice 7/19/99: Consultant verified alkalinity, total hardness and calcium hardness due to consistently high mass balance closure errors.
Note on EA10: C. Rice 7/19/99: Consultant verified alkalinity, total hardness and calcium hardness due to consistently high mass balance closure errors.
Note on EK10: C. Rice 7/19/99: Consultant verified alkalinity, total hardness and calcium hardness due to consistently high mass balance closure errors.

## SR40. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.45986 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.91 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.57 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.84 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.99 | [7 empty] | Feed flow rate during sample collection (mL/min) | 17.7 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:00 | 8:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 302.38 | [10 empty] | Influent flow rate during sample collection (mL/min) | 321 | [7 empty] | Influent flow rate during sample collection (mL/min) | 321 | [7 empty] | Influent flow rate during sample collection (mL/min) | 321 | [6 empty] | SDS-THM4F, ug/L | 538.9 | 538.9 | 538.9 | 538.9 | SDS-THM4F, ug/L | 538.9 | 538.9 | 538.9 | 538.9 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 3.65 | 59.2 | 39.9 | 33.1 | SDS-THM4p, ug/L | 3.65 | 59.2 | 39.9 | 33.1 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.54 | 8.16 | 7.85 | 7.8981 | 1998-07-07 | 9:30 | 0 | 23.5 | [5 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 9:00 | 0 | 24 | 55 | 54 | 209 | 7.52 | 6.13 |  | 13.65 | 0.1443 | 0.55092 | 14.3114 | 17.164 | 17.4711 | 427.4348 | 226.978 | 420.2222 | 1.9685 | 52.5315 | 0.33258 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 244.9 | 244.9 | 244.9 | 244.9 | SDS-HAA5F, ug/L | 244.9 | 244.9 | 244.9 | 244.9 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-07-07 | 10:30 | 1 | 23.5 | 55 | 54 | 209 | 7.71 | 0.97 | 8.68 | 0.1443 | 0.88825 | 23.0783 | 17.5977 | 18.1792 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 9:40 | 0.66667 | 24 | 54 | 54 | 209 | 7.29 | 6.57 |  | 13.86 | 0.1443 | 0.52597 | 14.0794 | 16.639 | 16.9368 | 420.7145 | 223.5289 | 413.8366 | 1.9375 | 52.0625 | 0.32532 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 3.8 | 9.8 | 6 | 5.5 | SDS-HAA5p, ug/L | 3.8 | 9.8 | 6 | 5.5 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 206 | 203 | 204.5 | 1.467 | 1998-07-07 | 11:15 | 1.75 | 23.5 | 54 | 52 | 209 | 7.71 | 4.11 | 11.82 | 0.1443 | 0.65228 | 16.6819 | 17.5977 | 18.1792 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 10:05 | 1.0833 | 24 | 55 | 54 | 209 | 7.17 | 3.7 |  | 10.87 | 0.1443 | 0.65961 | 18.2272 | 16.3651 | 16.658 | 458.794 | 243.8287 | 451.4194 | 2.1128 | 52.3872 | 0.31798 | 7.52 | 7.3 | 7.63 | 195 | 322 | 436 | 553.4162 | -26.9303 | 38.4858 | 547.2683 | 64.3685 | BMRL | 0.657 | 1.135 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-07-09 | 1998-07-10 | --- | --- | 1998-07-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-11 | 1998-07-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-12 | 1998-07-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1435 | 1435 | 1435 | 1435 | SDS-TOXF, ug Cl- /L | 1435 | 1435 | 1435 | 1435 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 319 | 315 | 317 | 1.2618 | 1998-07-07 | 11:45 | 2.25 | 23.5 | 54 | 52 | 209 | 7.67 | 3.2 | 10.87 | 0.1443 | 0.70561 | 18.2272 | 17.5064 | 18.0849 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 10:45 | 1.75 | 24 | 55 | 54 | 209 | 7.13 | 3.42 |  | 10.55 | 0.1443 | 0.67583 | 18.8104 | 16.2738 | 16.565 | 463.8725 | 246.5506 | 456.4586 | 2.1361 | 52.3639 | 0.31634 | 7.5 | 7.33 | 7.55 | 221 | 321 | 453 | 517.1404 | -14.159 | 30.2839 | 512.089 | 56.8434 | BMRL | 0.638 | 1.319 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 9:00 | 9:10 | --- | --- | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:30 | 15:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:15 | 11:15 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | 78 | 52 | 43 | SDS-TOXp, ug Cl- /L | #DIV/0! | 78 | 52 | 43 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 308 | 290 | 299 | 6.0201 | 1998-07-07 | 13:30 | 4 | 23.5 | 54 | 52 | 209 | 7.83 | 2.43 | 10.26 | 0.1443 | 0.76316 | 19.3704 | 17.8716 | 18.4622 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 11:30 | 2.5 | 24 | 55 | 54 | 209 | 6.8 | 3.24 |  | 10.04 | 0.1443 | 0.67729 | 19.8167 | 15.5206 | 15.7984 | 464.1505 | 246.8871 | 457.0816 | 2.1373 | 52.3627 | 0.30171 | 7.41 | 7.31 | 7.64 | 211 | 323 | 481 | 539.4691 | -12.1557 | 33.4385 | 534.1256 | 60.4962 | BMRL | 0.627 | 1.462 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 24 | 48 | --- | --- | 24 | --- | --- | --- | --- | --- | Operation time | hh.hh | 79.5 | 79.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 102.5 | 102.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 122.25 | 122.25 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 16.52 | 16.52 | 16.52 | 16.52 | SDS-CDF, mg/L | 16.52 | 16.52 | 16.52 | 16.52 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 252 | 260 | 256 | 3.125 | 1998-07-07 | 14:00 | 4.5 | 23.5 | 54 | 52 | 209 | 7.88 | 3.2 | 11.08 | 0.1443 | 0.71119 | 17.8628 | 17.9857 | 18.5801 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 13:45 | 4.75 | 24 | 56 | 55 | 209 | 6.67 | 0.42 |  | 7.09 | 0.1443 | 0.94076 | 28.4781 | 15.2239 | 15.4963 | 566.2826 | 301.303 | 557.8261 | 2.6075 | 52.8925 | 0.29298 | [27 empty] | pH | --- | 7.74 | 7.92 | 7.83 | 2.2989 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 7.65 | 8.29 | --- | --- | --- | --- | --- | pH | --- | 7.7 | 8.3 | --- | --- | --- | --- | --- | pH | --- | 7.69 | 7.71 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.32 | 3.26 | 2.08 | 2.51 | SDS-CDp, mg/L | 4.32 | 3.26 | 2.08 | 2.51 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 1.111 | 1.4 | 1.2555 | 23.0187 | 1998-07-07 | 16:00 | 6.5 | 23.5 | 54 | 52 | 209 | 8.48 | 2.53 | 11.01 | 0.1443 | 0.77021 | 17.9827 | 19.3551 | 19.9948 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 14:30 | 5.5 | 24 | 56 | 55 | 209 | 6.86 | 1.59 |  | 8.45 | 0.1443 | 0.81183 | 23.7337 | 15.6576 | 15.9378 | 511.3481 | 271.9543 | 503.4905 | 2.3546 | 53.1454 | 0.29989 | [27 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 13.3 | 13.3 | 13.3 | 13.3 | TOCF, mg/L | 13.3 | 13.3 | 13.3 | 13.3 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.47 | 0.14 | 0.305 | 108.1967 | 1998-07-07 | 16:15 | 6.75 | 23.5 | 41 | 39 | 209 | 6 | 3.92 | 9.92 | 0.1443 | 0.60484 | 20.0685 | 13.6947 | 14.1473 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 15:00 | 6 | 24 | 56 | 55 | 209 | 6.75 | 3.08 |  | 9.83 | 0.1443 | 0.68667 | 20.2614 | 15.4065 | 15.6822 | 467.1254 | 248.4983 | 460.0645 | 2.151 | 53.349 | 0.29395 | 7.41 | 7.37 | 7.72 | 242 | 321 | 539 | 481.3669 | 10.6926 | 23.6593 | 477.5015 | 49.3195 | BMRL | 0.648 | 2.217 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 193 | 192 | 192.5 | 0.51948 | 270 | 231.2097 | 14.3668 | 5.868 | 230.787 | 16.5898 | Alkalinity | mg/L as CaCO3 | 188 | 265 | 371.3333 | -40.1258 | 8.0685 | 369.8157 | 49.1639 | Alkalinity | mg/L as CaCO3 | 175 | 245 | 235.2041 | 3.9983 | 14.4254 | 234.6785 | 25.4299 | Alkalinity | mg/L as CaCO3 | 157 | 238 | 224.8571 | 5.5222 | 23.2274 | 224.2959 | 30.0032 | TOCp, mg/L | 0.7 | 1.1 | 0.9 | BMRL | TOCp, mg/L | 0.7 | 1.1 | 0.9 | BMRL | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 13.8 | 12.8 | 13.3 | 7.5188 | 1998-07-07 | 16:35 | 7.0833 | 23.5 | 71 | 70 | 209 | 10.67 | 4.53 | 15.2 | 0.1443 | 0.70197 | 12.75 | 24.3537 | 25.1586 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 15:45 | 6.75 | 24 | 56 | 54 | 209 | 6.8 | 3.09 |  | 9.89 | 0.1443 | 0.68756 | 20.1325 | 15.5206 | 15.7984 | 467.4414 | 248.6376 | 460.3225 | 2.1524 | 52.8476 | 0.29894 | 7.52 | 7.24 | 7.68 | 228 | 321 | 492 | 512.8576 | -4.2394 | 28.0757 | 508.2236 | 55.1379 | BMRL | 0.662 | 1.906 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 236 | 240 | 238 | 1.6807 | 453 | 492.8387 | -8.7944 | 24.9211 | 490.0562 | 51.4341 | Total dissolved solids | mg/L | 273 | 486 | 761.8889 | -56.7673 | 13.8801 | 757.8419 | 63.9767 | Total dissolved solids | mg/L | 246 | 352 | 390.898 | -11.0506 | 22.3975 | 389.6329 | 36.8637 | Total dissolved solids | mg/L | 223 | 333 | 357.2857 | -7.293 | 29.653 | 356.175 | 37.3903 | UV254 F, cm-1 | 0.635 | 0.635 | 0.635 | 0.635 | UV254 F, cm-1 | 0.635 | 0.635 | 0.635 | 0.635 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.665 | 0.605 | 0.635 | 9.4488 | 1998-07-07 | 17:00 | 7.5 | 23.5 | 54 | 56 | 209 | 8.17 | 3.63 | 11.8 | 0.1443 | 0.69237 | 16.7119 | 18.6476 | 19.2639 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-08 | 16:30 | 7.5 | 24 | 56 | 54 | 209 | 6.76 | 2.83 |  | 9.59 | 0.1443 | 0.7049 | 20.7935 | 15.4293 | 15.7054 | 473.0786 | 251.6594 | 465.9169 | 2.1784 | 52.8216 | 0.29733 | 7.79 | 7.67 | 7.82 | 237 | 328 | 494 | 508.0954 | -2.8533 | 25.2366 | 503.7112 | 52.9492 | BMRL | 0.666 | 1.843 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 212 | 208 | 210 | 1.9048 | 508 | 497.0968 | 2.1463 | 29.7659 | 493.962 | 57.4866 | Total hardness | mg/L as CaCO3 | 270 | 484 | 592.2222 | -22.36 | 9.699 | 589.5549 | 54.2027 | Total hardness | mg/L as CaCO3 | 182 | 332 | 420.7755 | -26.7396 | 39.1304 | 418.6909 | 56.5312 | Total hardness | mg/L as CaCO3 | 162 | 286 | 357.7143 | -25.0749 | 45.8194 | 356.0955 | 54.5066 | UV254 p, cm-1 | #DIV/0! | 0.024 | 0.016 | 0.02 | UV254 p, cm-1 | #DIV/0! | 0.024 | 0.016 | 0.02 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.8188 | 4.7266 | 4.7727 | 1.9335 | 1998-07-08 | 8:00 | 22.5 | 23.5 | 54 | 52 | 209 | 8.74 | 2 | 10.74 | 0.1443 | 0.81378 | 18.46 | 19.9486 | 20.6079 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 8:00 | 23 | 24 | 56 | 55 | 209 | 6.67 | 2.4 |  | 9.07 | 0.1443 | 0.73539 | 22.043 | 15.2239 | 15.4963 | 483.313 | 257.1572 | 476.0955 | 2.2255 | 53.2745 | 0.29088 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 184 | 176 | 180 | 4.4444 | 478 | 425.1613 | 11.0541 | 29.6875 | 422.4844 | 57.3949 | Calcium hardness | mg/L as CaCO3 | 206 | 462 | 761.5556 | -64.8389 | 19.5312 | 756.9567 | 72.7858 | Calcium hardness | mg/L as CaCO3 | 158 | 324 | 358 | -10.4938 | 38.2812 | 356.2539 | 55.6496 | Calcium hardness | mg/L as CaCO3 | 146 | 280 | 303.1429 | -8.2653 | 42.9688 | 301.8431 | 51.6305 | BromideF, ug/L | 150 | 150 | 150 | 150 | BromideF, ug/L | 150 | 150 | 150 | 150 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 150 | 150 | 150 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 9:00 | 24 | 24 | 55 | 54 | 209 | 6.5 | 3.93 |  | 10.43 | 0.1443 | 0.6232 | 19.0384 | 14.8359 | 15.1014 | 447.4138 | 238.1498 | 440.9056 | 2.0601 | 52.4399 | 0.28797 | 7.54 | 7.4 | 7.63 | 240 | 321 | 461 | 444.3537 | 3.6109 | 24.2902 | 441.1759 | 45.5999 | BMRL | 0.65 | 1.756 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.047 | 0.058 | 0.0525 | 20.9524 | 0.484 | 3.9331 | -712.6333 | 95.8184 | 3.8908 | 98.6507 | Turbidity | ntu | 0.05 | 1.13 | 13.4444 | -1089.7738 | 96.0175 | 13.3336 | 99.625 | Turbidity | ntu | 0.053 | 0.378 | 2.5071 | -563.2491 | 95.7786 | 2.4857 | 97.8678 | Turbidity | ntu | 0.045 | 0.35 | 1.7743 | -406.9388 | 96.4158 | 1.76 | 97.4432 | Bromidep, ug/L | 120 | 140 | 120 | 110 | Bromidep, ug/L | 120 | 140 | 120 | 110 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 18 | 18 | 18 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 10:00 | 25 | 24 | 55 | 54 | 284 | 6.64 | 2.96 |  | 9.6 | 0.19608 | 0.69167 | 28.5833 | 15.1554 | 15.4266 | 467.6478 | 249.8438 | 462.5555 | 2.1526 | 52.3474 | 0.2947 | 7.42 | 7.31 | 7.58 | 228 | 317 | 546 | 516.6486 | 5.3757 | 28.0757 | 513.2743 | 55.5793 | BMRL | 0.663 | 1.643 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 1.1 | 1.1 | 1.1 | 0 | NA | -1.4645 | #VALUE! | -260.6557 | -1.4365 | 176.5742 | Ammonia | mg NH3-N / L | 0.2 | NA | 1.3667 | #VALUE! | 34.4262 | 1.357 | 85.2617 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 204.5 | 204.5 | 204.5 | 204.5 | AlkF, mg/L CaCO3 | 204.5 | 204.5 | 204.5 | 204.5
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.16 | 1.8 | 1.48 | 43.2432 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 11:00 | 26 | 24 | 55 | 54 | 302 | 6.61 | 2.56 |  | 9.17 | 0.2085 | 0.72083 | 31.9335 | 15.087 | 15.3569 | 477.0127 | 255.0283 | 472.1541 | 2.1956 | 52.3044 | 0.29361 | 7.62 | 7.38 | 7.64 | 233 | 315 | 458 | 533.8906 | -16.57 | 26.4984 | 530.5978 | 56.0873 | BMRL | 0.661 | 1.721 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | 0.7 | 0.7 | #VALUE! | 45 | 41.3452 | 8.1219 | 94.7368 | 40.9014 | 98.2886 | Total organic carbon | mg/L | 1.1 | 105 | 136.6556 | -30.1481 | 91.7293 | 135.5334 | 99.1884 | Total organic carbon | mg/L | 0.9 | 27 | 26.2061 | 2.9403 | 93.2331 | 25.9852 | 96.5365 | Total organic carbon | mg/L | BMRL | 19.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 192.5 | 188 | 175 | 157 | Alkp, mg/L CaCO3 | 192.5 | 188 | 175 | 157
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 16.84 | 16.2 | 16.52 | 3.8741 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 12:30 | 27.5 | 24 | 56 | 54 | 302 | 6.57 | 2.58 |  | 9.15 | 0.2085 | 0.71803 | 32.0055 | 14.9957 | 15.264 | 476.0633 | 254.5368 | 471.244 | 2.1912 | 52.8088 | 0.28904 | [27 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 1.66 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.024 | 3.62 | 6.8129 | -88.2014 | 96.2205 | 6.7567 | 99.6448 | UV254 | cm-1 | 0.016 | 1.111 | 1.2793 | -15.1454 | 97.4803 | 1.2682 | 98.7384 | UV254 | cm-1 | 0.02 | 0.877 | 0.89857 | -2.4597 | 96.8504 | 0.8913 | 97.7561 | T-HdF, mg/L CaCO3 | 299 | 299 | 299 | 299 | T-HdF, mg/L CaCO3 | 299 | 299 | 299 | 299
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 14:00 | 29 | 24 | 56 | 54 | 302 | 6.67 | 2.96 |  | 9.63 | 0.2085 | 0.69263 | 30.3603 | 15.2239 | 15.4963 | 467.799 | 250.0787 | 462.9904 | 2.1532 | 52.8468 | 0.29323 | 7.51 | 7.43 | 7.94 | 231 | 312 | 461 | 510.7905 | -10.8006 | 27.1293 | 507.7008 | 54.5008 | BMRL | 0.662 | 1.721 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.6889 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.1818 | 3.4476 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.7778 | 4.1148 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 4.4974 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 210 | 270 | 182 | 162 | T-Hdp, mg/L CaCO3 | 210 | 270 | 182 | 162
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.91 | 9.14 | 9.025 | 2.5485 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 14:45 | 29.75 | 24 | 56 | 54 | 302 | 6.63 | 2.75 |  | 9.38 | 0.2085 | 0.70682 | 31.1962 | 15.1326 | 15.4034 | 472.3881 | 252.5479 | 467.5618 | 2.1743 | 52.8257 | 0.29159 | 7.48 | 7.37 | 7.68 | 237 | 314 | 461 | 509.8727 | -10.6015 | 25.2366 | 506.8775 | 53.2431 | BMRL | 0.66 | 1.74 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 120 | 120 | 120 | 0 | --- | 216.7742 | --- | 20 | 215.7175 | 44.3717 | Bromide | mg/L | 140 | --- | 251.1111 | --- | 6.6667 | 250.1913 | 44.0428 | Bromide | mg/L | 120 | --- | 181.2245 | --- | 20 | 180.69 | 33.5879 | Bromide | mg/L | 110 | --- | 167.1429 | --- | 26.6667 | 166.6702 | 34.0014 | Ca-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256 | Ca-HdF, mg/L CaCO3 | 256 | 256 | 256 | 256
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 15:30 | 30.5 | 24 | 56 | 54 | 302 | 6.64 | 3.03 |  | 9.67 | 0.2085 | 0.68666 | 30.2306 | 15.1554 | 15.4266 | 465.8777 | 249.0634 | 461.1106 | 2.1443 | 52.8557 | 0.29186 | 7.48 | 7.38 | 7.64 | 242 | 316 | 461 | 481.3564 | -4.4157 | 23.6593 | 478.7251 | 49.4491 | BMRL | 0.648 | 1.725 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 180 | 206 | 158 | 146 | Ca-Hdp, mg/L CaCO3 | 180 | 206 | 158 | 146
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 1440 | 1430 | 1435 | 0.69686 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-09 | 16:15 | 31.25 | 24 | 56 | 54 | 302 | 6.62 | 2.88 |  | 9.5 | 0.2085 | 0.69684 | 30.7895 | 15.1098 | 15.3802 | 469.1368 | 250.8136 | 464.351 | 2.1593 | 52.8407 | 0.29107 | 7.53 | 7.58 | 7.62 | 262 | 317 | 466 | 443.4236 | 4.8447 | 17.3502 | 441.4352 | 40.6481 | BMRL | 0.662 | 1.718 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.75 | 0.61 | 0.68 | 20.5882 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.24 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.42 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.99 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 480 | 480 | 480 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 8:00 | 47 | 24 | 57 | 56 | 302 | 6.33 | 2.4 |  | 8.73 | 0.2085 | 0.72509 | 33.5934 | 14.4479 | 14.7064 | 478.3156 | 255.8377 | 473.6524 | 2.2015 | 54.2985 | 0.27084 | [27 empty] | SDS-Cl2 demand | mg/L | 4.25 | 4.39 | 4.32 | 3.2407 | --- | 43.6748 | --- | 73.8499 | 43.2451 | 90.0104 | SDS-Cl2 demand | mg/L | 3.26 | --- | 150.5933 | --- | 80.2663 | 149.3737 | 97.8176 | SDS-Cl2 demand | mg/L | 2.08 | --- | 31.5494 | --- | 87.4092 | 31.2921 | 93.353 | SDS-Cl2 demand | mg/L | 2.51 | --- | 22.5243 | --- | 84.8063 | 22.3587 | 88.774 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 59 | 48 | 53.5 | 20.5607 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 9:00 | 48 | 24 | 55 | 54 | 302 | 6.4 | 3.26 |  | 9.66 | 0.2085 | 0.66253 | 30.2629 | 14.6077 | 14.869 | 458.2238 | 245.0641 | 453.7065 | 2.109 | 52.391 | 0.28381 | [27 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 87.2303 | 97.3317 | 93.5671 | 92.3092 | Qp/QT (THM4), % | 93.9561 | 104.8364 | 100.7816 | 99.4267
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 5.4 | 5.4 | 5.4 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 10:00 | 49 | 24 | 55 | 54 | 302 | 6.5 | 3.2 |  | 9.7 | 0.2085 | 0.6701 | 30.134 | 14.8359 | 15.1014 | 460.6082 | 246.3006 | 455.9956 | 2.12 | 52.38 | 0.2883 | 7.45 | 7.34 | 7.71 | 243 | 313 | 447 | 467.3125 | -4.5442 | 23.3438 | 464.8985 | 47.7305 | 0.01 | 0.641 | 1.888 | 1.9045 | -0.8756 | 98.4252 | 1.8841 | 99.4693 | [8 empty] | SDS-Chlorination pH | --- | 9.4 | 9.29 | 9.345 | 1.1771 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.89 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.38 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.5 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | NA | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 11:00 | 50 | 24 | 55 | 54 | 302 | 6.43 | 3.07 |  | 9.5 | 0.2085 | 0.67684 | 30.7895 | 14.6761 | 14.9387 | 462.6894 | 247.4407 | 458.1064 | 2.1296 | 52.3704 | 0.28525 | 7.6 | 7.46 | 7.8 | 243 | 315 | 442 | 471.9902 | -6.7851 | 23.3438 | 469.5525 | 48.2486 | 0.009 | 0.656 | 1.775 | 1.9461 | -9.6413 | 98.5827 | 1.9255 | 99.5326 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 34.5878 | 16.0733 | 21.3681 | 23.9117 | SDS-HAA5b, ug/L | 18.3719 | NA | NA | 6.8726
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 544.4 | 533.4 | 538.9 | 2.0412 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 13:30 | 52.5 | 24 | 55 | 54 | 302 | 6.34 | 3.05 |  | 9.39 | 0.2085 | 0.67519 | 31.1619 | 14.4707 | 14.7296 | 462.1353 | 247.1794 | 457.6227 | 2.127 | 52.373 | 0.28124 | 7.64 | 7.51 | 7.71 | 244 | 316 | 442 | 468.7443 | -6.0507 | 23.0284 | 466.3852 | 47.6827 | 0.01 | 0.649 | 1.668 | 1.9342 | -15.9581 | 98.4252 | 1.914 | 99.4775 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | 78 | --- | 15155.7778 | --- | 94.5645 | 15030.9657 | 99.4811 | SDS-TOX | mg Cl- /L | 52 | --- | 2874.449 | --- | 96.3763 | 2849.8079 | 98.1753 | SDS-TOX | mg Cl- /L | 43 | --- | 2031.5714 | --- | 97.0035 | 2015.1239 | 97.8661 | SDS-TOXb, ug Cl- /L | #DIV/0! | 114.2093 | 140.9665 | 150.0558 | SDS-TOXb, ug Cl- /L | #DIV/0! | NA | NA | 50.981
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 9.8 | 11 | 10.4 | 11.5385 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 14:30 | 53.5 | 24 | 55 | 54 | 302 | 6.32 | 3.05 |  | 9.37 | 0.2085 | 0.67449 | 31.2305 | 14.4251 | 14.6832 | 461.9105 | 247.0669 | 457.4145 | 2.126 | 52.374 | 0.28035 | 7.52 | 7.43 | 7.75 | 245 | 317 | 440 | 466.1934 | -5.9531 | 22.7129 | 463.879 | 47.1845 | 0.01 | 0.654 | 1.664 | 1.9301 | -15.9905 | 98.4252 | 1.91 | 99.4764 | [8 empty] | SDS-CHCl3 | mg/L | 1.9 | 4.1 | 3 | 73.3333 | --- | 1541.7097 | --- | 99.375 | 1524.9087 | 99.8033 | SDS-CHCl3 | mg/L | 8.2 | --- | 5250.4222 | --- | 98.2917 | 5207.0277 | 99.8425 | SDS-CHCl3 | mg/L | 6 | --- | 973.3469 | --- | 98.75 | 964.9016 | 99.3782 | SDS-CHCl3 | mg/L | 5.1 | --- | 683.5286 | --- | 98.9375 | 677.9173 | 99.2477 | SDS-CDb, mg/L | 5.8779 | 3.6138 | 3.0089 | 3.5875 | SDS-CDb, mg/L | 5.0574 | NA | NA | 2.5903
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 130 | 130 | 130 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 15:30 | 54.5 | 24 | 55 | 54 | 302 | 6.29 | 3 |  | 9.29 | 0.2085 | 0.67707 | 31.5081 | 14.3566 | 14.6135 | 462.7078 | 247.505 | 458.2256 | 2.1296 | 52.3704 | 0.27904 | 7.63 | 7.51 | 7.84 | 243 | 313 | 436 | 472.1533 | -8.292 | 23.3438 | 469.767 | 48.2722 | 0.01 | 0.664 | 1.66 | 1.9454 | -17.1938 | 98.4252 | 1.9253 | 99.4806 | [8 empty] | SDS-BDCM | mg/L | BMRL | 1.3 | 1.3 | #VALUE! | --- | 169.6871 | --- | 97.5701 | 167.8485 | 99.2255 | SDS-BDCM | mg/L | 14 | --- | 452.8889 | --- | 73.8318 | 449.2558 | 96.8837 | SDS-BDCM | mg/L | 9.5 | --- | 99.2959 | --- | 82.243 | 98.512 | 90.3565 | SDS-BDCM | mg/L | 8 | --- | 73 | --- | 85.0467 | 72.4624 | 88.9598 | TOCb, mg/L | 2.309 | 1.4255 | 1.6977 | #VALUE! | TOCb, mg/L | 1.4615 | NA | NA | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 110 | 96 | 103 | 13.5922 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 16:15 | 55.25 | 24 | 55 | 54 | 302 | 6.31 | 2.87 |  | 9.18 | 0.2085 | 0.68736 | 31.8976 | 14.4022 | 14.6599 | 465.9713 | 249.2429 | 461.4429 | 2.1446 | 52.3554 | 0.28001 | 7.63 | 7.53 | 7.78 | 244 | 313 | 440 | 477.4983 | -8.5223 | 23.0284 | 475.0589 | 48.6379 | 0.01 | 0.654 | 1.65 | 2.0091 | -21.7654 | 98.4252 | 1.9882 | 99.497 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 22 | --- | -162.4444 | --- | -307.4074 | -160.9176 | 113.6716 | SDS-DBCM | mg/L | 15 | --- | -4.5918 | --- | -177.7778 | -4.4208 | 439.3057 | SDS-DBCM | mg/L | 12 | --- | 2.5714 | --- | -122.2222 | 2.6494 | -352.9306 | UV254 b, cm-1 | #DIV/0! | 0.040304 | 0.055819 | 0.067298 | UV254 b, cm-1 | #DIV/0! | NA | NA | 0.023526
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-10 | 17:00 | 56 | 24 | 55 | 54 | 302 | 6.27 | 2.91 |  | 9.18 | 0.2085 | 0.68301 | 31.8976 | 14.3109 | 14.567 | 464.5716 | 248.5098 | 460.0858 | 2.1382 | 52.3618 | 0.2782 | 7.62 | 7.49 | 7.75 | 245 | 315 | 437 | 472.134 | -8.0398 | 22.7129 | 469.7762 | 47.8475 | 0.01 | 0.659 | 1.685 | 1.9816 | -17.6053 | 98.4252 | 1.9612 | 99.4901 | [8 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 15 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 9.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 123.8309 | 140.2668 | 121.9299 | 113.0763 | Bromideb, ug/L | 121.8132 | NA | NA | 110.2293
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.5 | 1.5 | 1.5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 11:15 | 74.25 | 24 | 55 | 54 | 302 | 5.69 | 2.04 |  | 7.73 | 0.2085 | 0.73609 | 38.0686 | 12.9871 | 13.2195 | 481.7494 | 257.9334 | 477.5325 | 2.2171 | 52.2829 | 0.25285 | 7.74 | 7.63 | 7.77 | 262 | 325 | 454 | 470.4069 | -3.6138 | 17.3502 | 468.4436 | 44.0701 | 0.013 | 0.652 | 1.932 | 2.3699 | -22.6652 | 97.9528 | 2.3477 | 99.4463 | [8 empty] | SDS-THM4 | mg/L | 1.9 | 5.4 | 3.65 | 95.8904 | --- | 1730.2629 | --- | 99.3227 | 1711.4102 | 99.7867 | SDS-THM4 | mg/L | 59.2 | --- | 5389.2 | --- | 89.0147 | 5345.0789 | 98.8924 | SDS-THM4 | mg/L | 39.9 | --- | 1058.2673 | --- | 92.596 | 1049.3766 | 96.1977 | SDS-THM4 | mg/L | 33.1 | --- | 755.6714 | --- | 93.8579 | 749.695 | 95.5849 | Alkb, mg/L CaCO3 | 194.0324 | 188.4403 | 176.8977 | 160.6531 | Alkb, mg/L CaCO3 | 193.2253 | NA | NA | 157.2723
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 17 | 15 | 16 | 12.5 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 12:00 | 75 | 24 | 55 | 54 | 302 | 5.71 | 3.47 |  | 9.18 | 0.2085 | 0.622 | 31.8976 | 13.0328 | 13.266 | 445.8431 | 238.7013 | 441.9266 | 2.0518 | 52.4482 | 0.25293 | 7.93 | 7.77 | 7.76 | 255 | 322 | 435 | 419.0231 | 3.6729 | 19.5584 | 417.4724 | 38.9181 | 0.013 | 0.651 | 1.726 | 1.6585 | 3.9095 | 97.9528 | 1.643 | 99.2087 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 221.3651 | 270.7738 | 189.5265 | 172.5364 | T-Hdb, mg/L CaCO3 | 215.3791 | NA | NA | 162.7855
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 13:00 | 76 | 24 | 55 | 54 | 302 | 5.69 | 3.68 |  | 9.37 | 0.2085 | 0.60726 | 31.2305 | 12.9871 | 13.2195 | 441.5815 | 236.4271 | 437.7161 | 2.0322 | 52.4678 | 0.25195 | 7.84 | 7.64 | 7.83 | 262 | 330 | 428 | 402.0408 | 6.0652 | 17.3502 | 400.7215 | 34.6179 | 0.013 | 0.65 | 1.558 | 1.5967 | -2.4861 | 97.9528 | 1.5818 | 99.1782 | [8 empty] | SDS-DCAA* | mg/L | 2.3 | 5.3 | 3.8 | 78.9474 | --- | 410.8968 | --- | 97.0769 | 406.4517 | 99.0651 | SDS-DCAA* | mg/L | 3.4 | --- | 1410.0667 | --- | 97.3846 | 1398.4224 | 99.7569 | SDS-DCAA* | mg/L | 2.4 | --- | 262.8082 | --- | 98.1538 | 260.5347 | 99.0788 | SDS-DCAA* | mg/L | 2.5 | --- | 184.6429 | --- | 98.0769 | 183.1363 | 98.6349 | Ca-Hdb, mg/L CaCO3 | 189.705 | 207.3342 | 164.3042 | 154.4599 | Ca-Hdb, mg/L CaCO3 | 184.5934 | NA | NA | 146.6307
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 14:00 | 77 | 24 | 55 | 54 | 302 | 5.85 | 2.22 |  | 8.07 | 0.2085 | 0.72491 | 36.4226 | 13.3523 | 13.5912 | 478.0446 | 255.8856 | 473.7412 | 2.2001 | 52.2999 | 0.25987 | 7.98 | 7.73 | 7.9 | 243 | 315 | 418 | 512 | -22.488 | 23.3438 | 509.3946 | 52.2963 | 0.015 | 0.648 | 1.546 | 2.2688 | -46.7519 | 97.6378 | 2.247 | 99.3324 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.1 | --- | 1133.3222 | --- | 98.932 | 1123.9498 | 99.9021 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 14 | 11 | 12.5 | 24 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 14:15 | 77.25 | 24 | 58 | 56 | 302 | 5.82 | 0.83 |  | 6.65 | 0.2085 | 0.87519 | 44.4135 | 13.2838 | 13.5215 | 534.2989 | 286.0106 | 529.514 | 2.459 | 54.541 | 0.24791 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 251.3 | 238.5 | 244.9 | 5.2266 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 14:30 | 77.5 | 24 | 58 | 56 | 302 | 5.71 | 0.72 |  | 6.43 | 0.2085 | 0.88802 | 45.9673 | 13.0328 | 13.266 | 539.6502 | 288.925 | 534.9097 | 2.4835 | 54.5165 | 0.24334 | 7.71 | 7.62 | 8.01 | 276 | 328 | 439 | 642.1528 | -46.2763 | 12.9338 | 638.6913 | 56.7866 | 0.015 | 0.656 | 1.871 | 5.5519 | -196.7367 | 97.6378 | 5.4996 | 99.7273 | [8 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 5.3 | --- | -36.9222 | --- | -253.3333 | -36.5727 | 114.4917 | SDS-DBAA* | mg/L | 3.6 | --- | -0.68571 | --- | -140 | -0.6483 | 655.2998 | SDS-DBAA* | mg/L | 3 | --- | 0.85714 | --- | -100 | 0.87487 | -242.9095 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 268.3 | 253.5 | 260.9 | 5.6727 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 15:00 | 78 | 24 | 57 | 56 | 302 | 5.57 | 0.65 |  | 6.22 | 0.2085 | 0.8955 | 47.5531 | 12.7132 | 12.9407 | 542.7612 | 290.6544 | 538.1115 | 2.4978 | 54.0022 | 0.23963 | 7.73 | 7.58 | 7.85 | 280 | 326 | 454 | 634.0615 | -39.6611 | 11.6719 | 630.7964 | 55.6117 | 0.016 | 0.655 | 2.062 | 5.9394 | -188.0385 | 97.4803 | 5.8847 | 99.7281 | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 3.5 | --- | 142.3889 | --- | 78.125 | 141.2392 | 97.5219 | SDS-BCAA* | mg/L | 1.9 | --- | 30.6755 | --- | 88.125 | 30.4243 | 93.755 | SDS-BCAA* | mg/L | 1.2 | --- | 22.3429 | --- | 92.5 | 22.168 | 94.5868 | Qp/QT (HAA5), % | 79.1788 | 81.1995 | 79.9079 | 79.741 | Qp/QT (HAA5), % | 90.3774 | 92.684 | 91.2097 | 91.0192
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 15:30 | 78.5 | 24 | 57 | 56 | 302 | 5.5 | 0.63 |  | 6.13 | 0.2085 | 0.89723 | 48.2659 | 12.5535 | 12.7781 | 543.4592 | 291.0601 | 538.8626 | 2.501 | 53.999 | 0.23664 | 7.73 | 7.59 | 7.96 | 283 | 333 | 475 | 613.8254 | -29.2264 | 10.7256 | 610.8129 | 53.6683 | 0.017 | 0.649 | 2.196 | 6.0302 | -174.601 | 97.3228 | 5.9755 | 99.7155 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 115.0957 | 149.386 | 140.1595 | 135.5699 | SDS-THM4b, ug/L | 55.1548 | 94.295 | 83.7635 | 78.5248
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 16:00 | 79 | 24 | 56 | 54 | 302 | 5.5 | 0.55 |  | 6.05 | 0.2085 | 0.90909 | 48.9174 | 12.5535 | 12.7781 | 548.6419 | 293.8358 | 544.0014 | 2.5249 | 52.4751 | 0.24351 | 7.75 | 7.6 | 8 | 287 | 328 | 483 | 617 | -27.7433 | 9.4637 | 613.995 | 53.257 | 0.017 | 0.642 | 2.245 | 6.815 | -203.5635 | 97.3228 | 6.7531 | 99.7483 | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1998-07-11 | 16:30 | 79.5 | 24 | 56 | 54 | 302 | 5.56 | 0.56 |  | 6.12 | 0.2085 | 0.9085 | 48.3464 | 12.6904 | 12.9175 | 548.4234 | 293.6912 | 543.7336 | 2.5239 | 52.4761 | 0.24616 | 7.74 | 7.6 | 7.91 | 293 | 324 | 489 | 555.2857 | -13.5554 | 7.571 | 552.8713 | 47.0039 | 0.018 | 0.653 | 2.456 | 6.7609 | -175.2821 | 97.1654 | 6.6989 | 99.7313 | [8 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | 1.9 | --- | 119.6778 | --- | 84.8 | 118.7028 | 98.3994 | SDS-DCBAA | mg/L | 1.4 | --- | 24.0531 | --- | 88.8 | 23.8553 | 94.1313 | SDS-DCBAA | mg/L | 1.1 | --- | 17.3857 | --- | 91.2 | 17.251 | 93.6236 | SDS-TOXb, ug Cl- /L | #DIV/0! | 333.1229 | 329.8736 | 325.005 | SDS-TOXb, ug Cl- /L | #DIV/0! | 177.2786 | 173.5697 | 168.0125
[44 empty] | 1998-07-11 | 17:15 | 80.25 | 24 | 55 | 54 | 302 | 5.56 | 0.52 |  | 6.08 | 0.2085 | 0.91447 | 48.6711 | 12.6904 | 12.9175 | 551.0701 | 295.1085 | 546.3577 | 2.5361 | 51.9639 | 0.24859 | 7.73 | 7.62 | 7.9 | 290 | 321 | 505 | 605.6923 | -19.9391 | 8.5174 | 602.7863 | 51.8901 | 0.02 | 0.653 | 2.596 | 7.2108 | -177.7646 | 96.8504 | 7.1446 | 99.7201 | [8 empty] | SDS-HAA5 | mg/L | 2.3 | 5.3 | 3.8 | 78.9474 | --- | 781.5419 | --- | 98.4483 | 773.0499 | 99.5084 | SDS-HAA5 | mg/L | 9.8 | --- | 2622.0222 | --- | 95.9984 | 2600.3986 | 99.6231 | SDS-HAA5 | mg/L | 6 | --- | 493.551 | --- | 97.55 | 489.2945 | 98.7737 | SDS-HAA5 | mg/L | 5.5 | --- | 347.5 | --- | 97.7542 | 344.6713 | 98.4043 | SDS-CDb, mg/L | 6.8602 | 5.7529 | 4.9813 | 5.3483 | SDS-CDb, mg/L | 5.494 | 4.2301 | 3.3493 | 3.7682
[44 empty] | 1998-07-11 | 18:00 | 81 | 24 | 55 | 54 | 302 | 5.63 | 0.71 |  | 6.34 | 0.2085 | 0.88801 | 46.6341 | 12.8502 | 13.0801 | 539.5902 | 288.9291 | 534.9173 | 2.4832 | 52.0168 | 0.25146 | 7.68 | 7.6 | 7.84 | 296 | 321 | 514 | 483.5211 | 5.9297 | 6.6246 | 481.7732 | 38.5603 | 0.022 | 0.652 | 2.824 | 5.4958 | -94.6116 | 96.5354 | 5.4448 | 99.5959 | [8 empty] | SDS-HAA6 | mg/L | 2.3 | 5.3 | 3.8 | 78.9474 | --- | 833.1548 | --- | 98.5435 | 824.0992 | 99.5389 | SDS-HAA6 | mg/L | 13.3 | --- | 2764.4111 | --- | 94.9023 | 2741.6377 | 99.5149 | SDS-HAA6 | mg/L | 7.9 | --- | 524.2265 | --- | 96.972 | 519.7188 | 98.4799 | SDS-HAA6 | mg/L | 6.7 | --- | 369.8429 | --- | 97.432 | 366.8393 | 98.1736 | TOCb, mg/L | 3.3235 | 3.3937 | 3.3914 | #VALUE! | TOCb, mg/L | 1.9124 | 1.9926 | 1.99 | #VALUE!
[44 empty] | 1998-07-12 | 11:00 | 98 | 24 | 56 | 54 | 302 | 5.11 | 0.54 |  | 5.65 | 0.2085 | 0.90442 | 52.4513 | 11.6633 | 11.872 | 546.3133 | 292.7673 | 542.0232 | 2.514 | 52.486 | 0.22619 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.13887 | 0.14037 | 0.14459 | UV254 b, cm-1 | #DIV/0! | 0.068701 | 0.070412 | 0.075232
[44 empty] | 1998-07-12 | 12:00 | 99 | 24 | 56 | 54 | 302 | 4.96 | 0.48 |  | 5.44 | 0.2085 | 0.91176 | 54.5147 | 11.3209 | 11.5235 | 549.4304 | 294.5067 | 545.2435 | 2.5283 | 52.4717 | 0.21961 | 7.85 | 7.44 | 7.65 | 283 | 322 | 518 | 668.3333 | -29.0219 | 10.7256 | 665.169 | 57.4544 | 0.028 | 0.653 | 2.798 | 6.9073 | -146.8668 | 95.5906 | 6.8508 | 99.5913 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 126.2464 | 141.8801 | 126.0276 | 118.1036 | Bromideb, ug/L | 122.8868 | 140.7316 | 122.6371 | 113.5923
[44 empty] | 1998-07-12 | 12:30 | 99.5 | 24 | 55 | 54 | 302 | 4.91 | 0.48 |  | 5.39 | 0.2085 | 0.91095 | 55.0297 | 11.2068 | 11.4073 | 549.0327 | 294.3166 | 544.8914 | 2.5265 | 51.9735 | 0.21948 | [66 empty] | Alkb, mg/L CaCO3 | 194.9985 | 191.1021 | 180.9272 | 166.623 | Alkb, mg/L CaCO3 | 193.6547 | 189.2071 | 177.5931 | 161.2659
[44 empty] | 1998-07-12 | 13:00 | 100 | 24 | 54 | 52 | 302 | 5.4 | 8.1 |  | 13.5 | 0.2085 | 0.4 | 21.3704 | 12.3252 | 12.5458 | 389.3099 | 208.5351 | 386.0775 | 1.7916 | 51.2084 | 0.24499 | [66 empty] | T-Hdb, mg/L CaCO3 | 228.5309 | 275.4521 | 205.5077 | 189.7548 | T-Hdb, mg/L CaCO3 | 218.5641 | 272.1217 | 192.2846 | 174.3037
[44 empty] | 1998-07-12 | 13:15 | 100.25 | 24 | 54 | 52 | 302 | 5.63 | 5.17 |  | 10.8 | 0.2085 | 0.5213 | 26.963 | 12.8502 | 13.0801 | 418.2957 | 223.9807 | 414.6732 | 1.925 | 51.075 | 0.2561 | 7.61 | 7.48 | 7.66 | 238 | 323 | 404 | 403.029 | 0.24034 | 24.9211 | 401.4907 | 40.7209 | 0.015 | 0.65 | 2.298 | 1.3102 | 42.9868 | 97.6378 | 1.2981 | 98.8445 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 195.8241 | 215.4003 | 177.6902 | 168.2849 | Ca-Hdb, mg/L CaCO3 | 187.3131 | 209.658 | 166.6145 | 155.8789
[44 empty] | 1998-07-12 | 13:30 | 100.5 | 24 | 54 | 52 | 302 | 5.6 | 6.03 |  | 11.63 | 0.2085 | 0.48151 | 24.9673 | 12.7817 | 13.0104 | 408.3315 | 218.6556 | 404.8143 | 1.8792 | 51.1208 | 0.2545 | 7.72 | 7.49 | 7.69 | 235 | 321 | 392 | 393.1526 | -0.29402 | 25.8675 | 391.6863 | 40.003 | 0.016 | 0.648 | 2.017 | 1.2099 | 40.0169 | 97.4803 | 1.1988 | 98.6653 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-07-12 | 13:45 | 100.75 | 24 | 54 | 52 | 302 | 5.6 | 5.69 |  | 11.29 | 0.2085 | 0.49601 | 25.7493 | 12.7817 | 13.0104 | 411.9054 | 220.5694 | 408.3574 | 1.8956 | 51.1044 | 0.25459 | 7.83 | 7.76 | 7.75 | 248 | 326 | 399 | 384.9086 | 3.5317 | 21.7666 | 383.6393 | 35.3559 | 0.016 | 0.651 | 1.866 | 1.2442 | 33.3221 | 97.4803 | 1.2328 | 98.7022 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-07-12 | 14:00 | 101 | 24 | 54 | 52 | 302 | 5.63 | 5.7 |  | 11.33 | 0.2085 | 0.49691 | 25.6549 | 12.8502 | 13.0801 | 412.1351 | 220.682 | 408.566 | 1.8967 | 51.1033 | 0.25595 | 7.73 | 7.59 | 7.64 | 234 | 324 | 386 | 398.9807 | -3.3629 | 26.183 | 397.4429 | 41.1236 | 0.014 | 0.655 | 1.672 | 1.2484 | 25.3365 | 97.7953 | 1.2369 | 98.8681 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-07-12 | 14:30 | 101.5 | 24 | 54 | 52 | 302 | 5.63 | 5.13 |  | 10.76 | 0.2085 | 0.52323 | 27.0669 | 12.8502 | 13.0801 | 418.7931 | 224.2471 | 415.1663 | 1.9273 | 51.0727 | 0.25611 | 7.7 | 7.55 | 7.65 | 236 | 318 | 382 | 405.8947 | -6.2552 | 25.5521 | 404.3111 | 41.6291 | 0.013 | 0.66 | 1.55 | 1.3176 | 14.992 | 97.9528 | 1.3055 | 99.0042 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-07-12 | 15:00 | 102 | 24 | 54 | 52 | 302 | 5.57 | 5.49 |  | 11.06 | 0.2085 | 0.50362 | 26.3056 | 12.7132 | 12.9407 | 413.7974 | 221.5929 | 410.2524 | 1.9043 | 51.0957 | 0.25326 | 7.67 | 7.58 | 7.58 | 230 | 318 | 378 | 405.2678 | -7.2137 | 27.4448 | 403.6515 | 43.0201 | 0.012 | 0.664 | 1.376 | 1.2671 | 7.9158 | 98.1102 | 1.2555 | 99.0442 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-07-12 | 15:30 | 102.5 | 24 | 54 | 52 | 302 | 5.63 | 4.97 |  | 10.6 | 0.2085 | 0.53113 | 27.4906 | 12.8502 | 13.0801 | 420.8329 | 225.3393 | 417.1885 | 1.9367 | 51.0633 | 0.25615 | 7.65 | 7.58 | 7.69 | 233 | 318 | 375 | 412.1549 | -9.908 | 26.4984 | 410.485 | 43.2379 | 0.01 | 0.66 | 1.291 | 1.343 | -4.0277 | 98.4252 | 1.3306 | 99.2484 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-07-12 | 16:30 | 103.5 | 24 | 54 | 52 | 302 | 5.51 | 5.14 |  | 10.65 | 0.2085 | 0.51737 | 27.3568 | 12.5763 | 12.8013 | 417.263 | 223.4698 | 413.7272 | 1.9203 | 51.0797 | 0.25061 | 7.76 | 7.65 | 7.66 | 233 | 319 | 376 | 407.0467 | -8.2571 | 26.4984 | 405.4589 | 42.5343 | 0.012 | 0.661 | 1.208 | 1.3028 | -7.8515 | 98.1102 | 1.2911 | 99.0705 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-07-12 | 17:30 | 104.5 | 24 | 54 | 52 | 302 | 5.94 | 5.69 |  | 11.63 | 0.2085 | 0.51075 | 24.9673 | 13.5577 | 13.8003 | 415.6809 | 222.4724 | 411.8807 | 1.9131 | 51.0869 | 0.27013 | 7.7 | 7.59 | 7.68 | 236 | 318 | 377 | 401.5589 | -6.5143 | 25.5521 | 399.9307 | 40.9898 | 0.013 | 0.662 | 1.168 | 1.2843 | -9.9596 | 97.9528 | 1.2718 | 98.9778 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-07-12 | 18:30 | 105.5 | 24 | 54 | 52 | 302 | 5.63 | 5.51 |  | 11.14 | 0.2085 | 0.50539 | 26.1095 | 12.8502 | 13.0801 | 414.2555 | 221.8174 | 410.668 | 1.9064 | 51.0936 | 0.256 | 7.71 | 7.6 | 7.76 | 237 | 318 | 378 | 398.7423 | -5.4874 | 25.2366 | 397.2347 | 40.3375 | 0.014 | 0.66 | 1.14 | 1.2695 | -11.3618 | 97.7953 | 1.2578 | 98.887 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-07-12 | 19:30 | 106.5 | 24 | 54 | 52 | 302 | 5.9 | 5.33 |  | 11.23 | 0.2085 | 0.52538 | 25.8923 | 13.4664 | 13.7074 | 419.4111 | 224.4829 | 415.6029 | 1.9302 | 51.0698 | 0.26841 | 7.74 | 7.62 | 7 | 235 | 318 | 377 | 407.7692 | -8.1616 | 25.8675 | 406.0816 | 42.1299 | 0.015 | 0.661 | 1.146 | 1.3213 | -15.297 | 97.6378 | 1.3085 | 98.8537 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-07-13 | 8:20 | 119.3333 | 24 | 55 | 54 | 302 | 5.25 | 5.43 |  | 10.68 | 0.2085 | 0.49157 | 27.2772 | 11.9828 | 12.1973 | 410.7274 | 220.0591 | 407.4128 | 1.8901 | 52.6099 | 0.23184 | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-07-13 | 8:45 | 119.75 | 24 | 52 | 51 | 302 | 5.2 | 16.32 |  | 21.52 | 0.2085 | 0.24164 | 13.0335 | 11.8687 | 12.0811 | 357.0472 | 191.3134 | 354.1935 | 1.6431 | 49.8569 | 0.24232 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-07-13 | 9:00 | 120 | 24 | 52 | 50 | 302 | 5.24 | 16.73 |  | 21.97 | 0.2085 | 0.23851 | 12.746 | 11.96 | 12.174 | 356.4673 | 190.9907 | 353.5962 | 1.6404 | 49.3596 | 0.24664
[44 empty] | 1998-07-13 | 9:45 | 120.75 | 24 | 52 | 51 | 302 | 5.2 | 14.93 |  | 20.13 | 0.2085 | 0.25832 | 14.0025 | 11.8687 | 12.0811 | 360.1893 | 192.997 | 357.3105 | 1.6575 | 49.8425 | 0.24239 | 7.94 | 7.7 | 7.78 | 213 | 316 | 340 | 353.2224 | -3.8889 | 32.8076 | 352.0152 | 39.4912 | 0.01 | 0.653 | 0.885 | 0.85268 | 3.6517 | 98.4252 | 0.84543 | 98.8172
[44 empty] | 1998-07-13 | 10:00 | 121 | 24 | 52 | 51 | 302 | 5.25 | 14.06 |  | 19.31 | 0.2085 | 0.27188 | 14.6396 | 11.9828 | 12.1973 | 362.7884 | 194.3744 | 359.8606 | 1.6695 | 49.8305 | 0.24477 | 7.87 | 7.64 | 7.7 | 218 | 317 | 340 | 353.9666 | -4.1078 | 31.2303 | 352.7847 | 38.2059 | 0.011 | 0.648 | 0.874 | 0.868 | 0.68634 | 98.2677 | 0.86055 | 98.7218
[44 empty] | 1998-07-13 | 10:15 | 121.25 | 24 | 52 | 51 | 302 | 5.29 | 13.83 |  | 19.12 | 0.2085 | 0.27667 | 14.795 | 12.0741 | 12.2902 | 363.7186 | 194.8606 | 360.7607 | 1.6738 | 49.8262 | 0.24666 | 7.81 | 7.6 | 7.7 | 219 | 316 | 340 | 354.4852 | -4.2603 | 30.9148 | 353.2986 | 38.0128 | 0.011 | 0.655 | 0.878 | 0.87368 | 0.4919 | 98.2677 | 0.86613 | 98.73
[44 empty] | 1998-07-13 | 10:30 | 121.5 | 24 | 52 | 51 | 302 | 5.2 | 13.77 |  | 18.97 | 0.2085 | 0.27412 | 14.9199 | 11.8687 | 12.0811 | 363.2153 | 194.6184 | 360.3123 | 1.6715 | 49.8285 | 0.24245 | 7.79 | 7.58 | 7.71 | 219 | 313 | 339 | 354.008 | -4.4271 | 30.9148 | 352.8457 | 37.9332 | 0.011 | 0.635 | 0.874 | 0.87064 | 0.38413 | 98.2677 | 0.86324 | 98.7257
[44 empty] | 1998-07-13 | 11:15 | 122.25 | 24 | 53 | 52 | 302 | 5.24 | 13.04 |  | 18.28 | 0.2085 | 0.28665 | 15.5208 | 11.96 | 12.174 | 365.6571 | 195.9145 | 362.7119 | 1.6827 | 50.8173 | 0.23956 | 7.78 | 7.57 | 7.66 | 219 | 316 | 340 | 356.3804 | -4.8178 | 30.9148 | 355.1885 | 38.3426 | 0.011 | 0.657 | 0.872 | 0.88575 | -1.5767 | 98.2677 | 0.87816 | 98.7474
[44 empty] | 1998-07-13 | 12:00 | 123 | 24 | 53 | 52 | 302 | 5.29 | 12.46 |  | 17.75 | 0.2085 | 0.29803 | 16.0141 | 12.0741 | 12.2902 | 367.9035 | 197.1026 | 364.9116 | 1.693 | 50.807 | 0.2419 | 7.73 | 7.56 | 7.66 | 223 | 315 | 341 | 356.9085 | -4.6653 | 29.653 | 355.7357 | 37.313 | 0.011 | 0.653 | 0.864 | 0.89992 | -4.1579 | 98.2677 | 0.89214 | 98.767
[44 empty] | 1998-07-13 | 13:20 | 124.3333 | 24 | 53 | 52 | 302 | 5.18 | 11.7 |  | 16.88 | 0.2085 | 0.30687 | 16.891 | 11.8231 | 12.0346 | 369.6528 | 198.0739 | 366.7098 | 1.7011 | 50.7989 | 0.23691 | 7.81 | 7.6 | 7.69 | 222 | 314 | 344 | 359.0598 | -4.3779 | 29.9685 | 357.8844 | 37.9688 | 0.011 | 0.648 | 0.887 | 0.91127 | -2.7358 | 98.2677 | 0.90355 | 98.7826
[44 empty] | 1998-07-13 | 14:00 | 125 | 24 | 53 | 52 | 302 | 5.22 | 12.23 |  | 17.45 | 0.2085 | 0.29914 | 16.3066 | 11.9144 | 12.1276 | 368.1166 | 197.2384 | 365.163 | 1.694 | 50.806 | 0.2387 | 7.78 | 7.6 | 7.71 | 219 | 318 | 343 | 358.8283 | -4.6147 | 30.9148 | 357.6198 | 38.7618 | 0.011 | 0.642 | 0.892 | 0.90134 | -1.0466 | 98.2677 | 0.89364 | 98.7691
[44 empty] | 1998-07-13 | 15:00 | 126 | 24 | 53 | 52 | 302 | 5.25 | 11.68 |  | 16.93 | 0.2085 | 0.3101 | 16.8382 | 11.9828 | 12.1973 | 370.3077 | 198.4031 | 367.3193 | 1.7041 | 50.7959 | 0.24012
[44 empty] | 1998-07-13 | 16:00 | 127 | 24 | 53 | 52 | 302 | 5.24 | 11 |  | 16.24 | 0.2085 | 0.32266 | 17.5961 | 11.96 | 12.174 | 372.8459 | 199.7662 | 369.8428 | 1.7158 | 50.7842 | 0.23972 | 7.68 | 7.5 | 7.65 | 225 | 313 | 345 | 360.8255 | -4.5871 | 29.0221 | 359.6471 | 37.4387 | 0.012 | 0.648 | 0.9 | 0.93177 | -3.5305 | 98.1102 | 0.9238 | 98.701
[44 empty] | 1998-07-13 | 17:00 | 128 | 24 | 53 | 51 | 302 | 5.18 | 14.17 |  | 19.35 | 0.2085 | 0.2677 | 14.6072 | 11.8231 | 12.0346 | 361.9781 | 193.9615 | 359.0962 | 1.6658 | 50.3342 | 0.23909 | 7.74 | 7.56 | 7.67 | 220 | 313 | 339 | 352.4594 | -3.9703 | 30.5994 | 351.3234 | 37.3796 | 0.011 | 0.649 | 0.859 | 0.86311 | -0.47847 | 98.2677 | 0.8558 | 98.7147
[44 empty] | 1998-07-13 | 18:00 | 129 | 24 | 53 | 51 | 302 | 5.2 | 13.5 |  | 18.7 | 0.2085 | 0.27807 | 15.1497 | 11.8687 | 12.0811 | 363.9815 | 195.0289 | 361.0723 | 1.675 | 50.325 | 0.24006 | 7.7 | 7.51 |  | 221 | 312 | 339 | 353.9778 | -4.4182 | 30.2839 | 352.8329 | 37.3641 | 0.011 | 0.653 | 0.865 | 0.87536 | -1.1972 | 98.2677 | 0.86791 | 98.7326
[44 empty] | 1998-07-14 | 8:00 | 143 | 24 | 53 | 51 | 302 | 5.2 | 13.5 | X | 18.7 | 0.2085 | 0.27807 | 15.1497 | 11.8687 | 12.0811 | 363.9815 | 195.0289 | 361.0723 | 1.675 | 50.325 | 0.24006
[44 empty] | 1998-07-14 | 1:45 |  | 24 | 54 | 53 | 302 | 9 | 2.35 |  | 11.35 | 0.2085 | 0.79295 | 25.6079 | 20.542 | 20.9096 | 503.6655 | 268.2596 | 496.6501 | 2.319 | 51.181 | 0.40854
[44 empty] | 1998-07-14 | 2:15 |  | 24 | 40 | 38 | 302 | 6.65 | 3.13 |  | 9.78 | 0.2085 | 0.67996 | 29.8793 | 15.1783 | 15.4499 | 463.7562 | 247.9253 | 459.0036 | 2.1345 | 36.8655 | 0.41909
[44 empty] | 1998-07-14 | 2:40 |  | 24 | 70 | 69 | 302 | 12.17 | 8.11 |  | 20.28 | 0.2085 | 0.6001 | 13.8915 | 27.7774 | 28.2744 | 441.5675 | 233.9891 | 433.2025 | 2.034 | 67.466 | 0.41909
[44 empty] | 1998-07-14 | 3:15 |  | 24 | 54 | 52 | 302 | 9 | 5.2 |  | 14.2 | 0.2085 | 0.6338 | 20.2676 | 20.542 | 20.9096 | 450.4314 | 239.9063 | 444.1575 | 2.0739 | 50.9261 | 0.41059
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: Alison Gusses: Permeate sample during 70% run appeared to have high ammonia demand - DBP data from 70% run is "questionable" and should probably be discarded
Note on Q3: C. Rice 7/9/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used for this study
Note on X12: C. Rice 7/19/99: TDS verified by consultant.
Note on X18: C. Rice 7/19/99: UV verified by consultant.
Note on CZ9: C. Rice 7/9/99: Consultant verified that all water quality parameters for Run 1 were found to be correct (including ammonia). No explanation was given as to why many concentrations appear low relative to concentrations for the other three runs. No explanation was given as to why ammonia appears high for the 70% recovery run.
Note on DG10: C. Rice 7/12/99: Consultant verified all TDS and UV concentrations due to consistently high mass balance closure errors.
Note on DQ10: C. Rice 7/12/99: Consultant verified all TDS and UV concentrations due to consistently high mass balance closure errors.
Note on EA10: C. Rice 7/12/99: Consultant verified all TDS and UV concentrations due to consistently high mass balance closure errors.
Note on EK10: C. Rice 7/12/99: Consultant verified all TDS and UV concentrations due to consistently high mass balance closure errors.

## SR40. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.39293 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.54438 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-11-23 | 1998-12-10 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.66 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.54 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.75 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.46 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 8:45 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [6 empty] | SDS-THM4F, ug/L | 462.85 | 462.85 | 462.85 | 462.85 | SDS-THM4F, ug/L | 462.85 | 462.85 | 462.85 | 462.85 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 44.5 | 86.3 | 62 | 48.7 | SDS-THM4p, ug/L | 44.5 | 86.3 | 62 | 48.7 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.59 | 8.36 | 7.975 | 9.6552 | 1998-11-09 | 8:45 | 0 | 23 | 53.5 | 54.5 | 272 | 6.33 | 3.03 | 9.36 | 0.18779 | 0.67628 | 28.0598 | 14.4479 | 15.1476 | 0 | 0 | 0 | 0 | 54 | 0.28051 | 1998-11-10 | 8:45 | 0 | 23 | 48 | 49 | 272 | 6.8 | 2.59 |  | 9.39 | 0.18779 | 0.72417 | 27.967 | 15.5206 | 16.2723 | 393.071 | 236.2428 | 389.1503 | 1.5487 | 46.9513 | 0.34658 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 208.5 | 208.5 | 208.5 | 208.5 | SDS-HAA5F, ug/L | 208.5 | 208.5 | 208.5 | 208.5 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 24 | 23.5 | 4.2553 | 1998-11-09 | 9:00 | 0.25 | 23 | 53.5 | 54.5 | 272 | 6.33 | 3.03 | 9.36 | 0.18779 | 0.67628 | 28.0598 | 14.4479 | 15.1476 | 0 | 0 | 0 | 0 | 54 | 0.28051 | 1998-11-10 | 9:00 | 0.25 | 23 | 48 | 49 | 272 | 6.8 | 2.59 |  | 9.39 | 0.18779 | 0.72417 | 27.967 | 15.5206 | 16.2723 | 393.071 | 236.2428 | 389.1503 | 1.5487 | 46.9513 | 0.34658 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 6.05 | 15 | 8.6 | 6.7 | SDS-HAA5p, ug/L | 6.05 | 15 | 8.6 | 6.7 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 436 | 406 | 421 | 7.1259 | 1998-11-09 | 9:15 | 0.5 | 23 | 54 | 55 | 272 | 7.04 | 3.03 | 10.07 | 0.18779 | 0.69911 | 26.0109 | 16.0684 | 16.8466 | 0 | 0 | 0 | 0 | 54.5 | 0.30911 | 1998-11-10 | 10:00 | 1.25 | 23 | 48 | 49 | 272 | 6.43 | 2.96 |  | 9.39 | 0.18779 | 0.68477 | 27.967 | 14.6761 | 15.3869 | 384.4473 | 231.1883 | 380.8243 | 1.5145 | 46.9855 | 0.32748 | 7.68 | 7.46 | 7.38 | 180 | 263 | 365 | 495.6436 | -35.7928 | 35.5993 | 491.9127 | 63.4081 | 0.012 | 0.596 | 1.281 | 1.7806 | -38.9973 | 97.8929 | 1.7597 | 99.318 | [8 empty] | Sampling date | MM/DD/YY | 1998-11-11 | 1998-11-12 | --- | --- | 1998-11-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-13 | 1998-11-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-14 | 1998-11-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-15 | 1998-11-15 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1095 | 1095 | 1095 | 1095 | SDS-TOXF, ug Cl- /L | 1095 | 1095 | 1095 | 1095 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 281 | 278 | 279.5 | 1.0733 | 1998-11-09 | 10:00 | 1.25 | 23 | 52 | 53 | 272 | 6.9 | 2.29 | 9.19 | 0.18779 | 0.75082 | 28.5974 | 15.7489 | 16.5116 | 0 | 0 | 0 | 0 | 52.5 | 0.31451 | 1998-11-10 | 11:00 | 2.25 | 23 | 47.5 | 48.5 | 272 | 6.13 | 2.04 |  | 8.17 | 0.18779 | 0.75031 | 32.2925 | 13.9914 | 14.669 | 398.6619 | 239.8442 | 395.0826 | 1.5703 | 46.4297 | 0.31594 |  |  |  | 202 | 276 | 390 | 512.3799 | -31.3795 | 27.7281 | 508.8824 | 60.3052 | 0.012 |  | 1.447 | 2.2447 | -55.1301 | 97.8929 | 2.2196 | 99.4594 | [8 empty] | Sampling time | hh:mm | 8:10 | 10:00 | --- | --- | 8:10 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:40 | 17:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:40 | 14:40 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 61.5 | 140 | 85 | 72 | SDS-TOXp, ug Cl- /L | 61.5 | 140 | 85 | 72 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 214 | 220 | 217 | 2.765 | 1998-11-09 | 11:00 | 2.25 | 23 | 52 | 53 | 272 | 7.1 | 1.8 | 8.9 | 0.18779 | 0.79775 | 29.5618 | 16.2054 | 16.9902 | 0 | 0 | 0 | 0 | 52.5 | 0.32362 | 1998-11-10 | 12:00 | 3.25 | 23 | 47.5 | 48.5 | 272 | 6.14 | 3.43 |  | 9.57 | 0.18779 | 0.64159 | 27.4222 | 14.0142 | 14.6929 | 375.4701 | 225.8881 | 372.0935 | 1.4789 | 46.5211 | 0.31583 |  |  |  | 189 |  | 357 | 441.5029 | -23.6703 | 32.3792 | 438.653 | 56.9135 | 0.015 |  | 1.425 | 1.5621 | -9.6213 | 97.3661 | 1.5446 | 99.0289 | [8 empty] | Operation time | hh.hh | 23.42 | 49.25 | --- | --- | 23.42 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80.92 | 80.92 | --- | --- | --- | --- | --- | Operation time | hh.hh | 104.25 | 104.25 | --- | --- | --- | --- | --- | Cumulative time | hr | 125.92 | 125.92 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 12.51 | 12.51 | 12.51 | 12.51 | SDS-CDF, mg/L | 12.51 | 12.51 | 12.51 | 12.51 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 204 | 206 | 205 | 0.97561 | 1998-11-09 | 12:00 | 3.25 | 23 | 50.5 | 51.5 | 272 | 7.13 | 4.74 | 11.87 | 0.18779 | 0.60067 | 21.9149 | 16.2738 | 17.062 | 0 | 0 | 0 | 0 | 51 | 0.33455 | 1998-11-10 | 13:00 | 4.25 | 23 | 47.5 | 48.5 | 272 | 6.13 | 3.2 |  | 9.33 | 0.18779 | 0.65702 | 28.1533 | 13.9914 | 14.669 | 378.5938 | 227.7708 | 375.1947 | 1.4912 | 46.5088 | 0.3154 | 7.42 | 7.4 | 7.47 | 213 | 281 | 391 | 406.8891 | -4.0637 | 23.7925 | 404.7042 | 47.369 | 0.015 | 0.607 | 1.46 | 1.6317 | -11.7612 | 97.3661 | 1.6135 | 99.0703 | [8 empty] | pH | --- | 7.66 | 7.79 | 7.725 | 1.6828 | 7.8 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 8.5 | --- | --- | --- | --- | --- | pH | --- | 7.65 | 7.64 | --- | --- | --- | --- | --- | pH | --- | 7.68 | 8.14 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.815 | 1.99 | 1.8 | 1.8 | SDS-CDp, mg/L | 2.815 | 1.99 | 1.8 | 1.8 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.888 | 0.359 | 0.6235 | 84.8436 | 1998-11-09 | 13:15 | 4.5 | 23 | 50.5 | 51.5 | 272 | 7.32 | 3.67 | 10.99 | 0.18779 | 0.66606 | 23.7498 | 16.7075 | 17.5167 | 0 | 0 | 0 | 0 | 51 | 0.34346 | 1998-11-10 | 14:00 | 5.25 | 23 | 47.5 | 48.5 | 272 | 6.17 | 3.05 |  | 9.22 | 0.18779 | 0.6692 | 28.5011 | 14.0827 | 14.7647 | 381.1105 | 229.2711 | 377.6662 | 1.5012 | 46.4988 | 0.31753 |  |  |  | 214 | 281 | 388 | 412.0033 | -6.1864 | 23.4347 | 409.7575 | 47.774 | 0.011 |  | 1.492 | 1.6993 | -13.8953 | 98.0685 | 1.6802 | 99.3453 | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 12 | 12 | 12 | 12 | TOCF, mg/L | 12 | 12 | 12 | 12 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-11-09 | 14:00 | 5.25 | 23 | 50.5 | 51.5 | 272 | 7.38 | 3.49 | 10.87 | 0.18779 | 0.67893 | 24.023 | 16.8445 | 17.6602 | 0 | 0 | 0 | 0 | 51 | 0.34628 | 1998-11-10 | 15:00 | 6.25 | 23 | 47.5 | 48.5 | 272 | 6.11 | 2.99 |  | 9.1 | 0.18779 | 0.67143 | 28.8901 | 13.9457 | 14.6211 | 381.5541 | 229.5586 | 378.1398 | 1.5029 | 46.4971 | 0.31445 | 7.43 | 7.39 | 7.3 | 219 | 281 | 392 | 403.1304 | -2.8394 | 21.6458 | 401.0624 | 45.395 | 0.012 | 0.59 | 1.56 | 1.7087 | -9.5346 | 97.8929 | 1.6897 | 99.2898 | [8 empty] | Alkalinity | mg/L as CaCO3 | 312 | 330 | 321 | 5.6075 | 581 | 665.8276 | -14.6003 | 23.753 | 661.9301 | 51.5055 | Alkalinity | mg/L as CaCO3 | 384 | 612 | 754 | -23.2026 | 8.7886 | 750.6088 | 48.8415 | Alkalinity | mg/L as CaCO3 | 330 | 506 | 529.7291 | -4.6896 | 21.6152 | 527.7804 | 37.474 | Alkalinity | mg/L as CaCO3 | 312 | 400 | 467.7143 | -16.9286 | 25.8907 | 466.0432 | 33.0534 | TOCp, mg/L | 0.85 | 1.8 | 1 | 0.8 | TOCp, mg/L | 0.85 | 1.8 | 1 | 0.8 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 12.3 | 11.7 | 12 | 5 | 1998-11-09 | 15:00 | 6.25 | 23 | 50.5 | 51.5 | 272 | 7.6 | 3.33 | 10.93 | 0.18779 | 0.69533 | 23.8856 | 17.3466 | 18.1867 | 0 | 0 | 0 | 0 | 51 | 0.3566 | 1998-11-10 | 16:00 | 7.25 | 23 | 47.5 | 48.5 | 272 | 6.11 | 2.99 |  | 9.1 | 0.18779 | 0.67143 | 28.8901 | 13.9457 | 14.6211 | 381.5541 | 229.5586 | 378.1398 | 1.5029 | 46.4971 | 0.31445 |  |  |  | 214 | 281 | 393 | 413.3478 | -5.1776 | 23.4347 | 411.1088 | 47.9457 | 0.014 |  | 1.581 | 1.7047 | -7.8211 | 97.5417 | 1.6857 | 99.1695 | [8 empty] | Total dissolved solids | mg/L | 229 | 234 | 231.5 | 2.1598 | 386 | 397.0172 | -2.8542 | 17.1735 | 395.1465 | 41.4141 | Total dissolved solids | mg/L | 266 | 418 | 401 | 4.067 | 4.8301 | 399.7627 | 33.4605 | Total dissolved solids | mg/L | 247 | 347 | 318.3318 | 8.2617 | 11.6279 | 317.6359 | 22.238 | Total dissolved solids | mg/L | 225 | 301 | 302.8571 | -0.61699 | 19.4991 | 302.0216 | 25.502 | UV254 F, cm-1 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | UV254 F, cm-1 | 0.5695 | 0.5695 | 0.5695 | 0.5695 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.613 | 0.526 | 0.5695 | 15.2766 | 1998-11-09 | 15:25 | 6.6667 | 23 | 60 | 61.5 | 272 | 9.92 | 4.27 | 14.19 | 0.18779 | 0.69908 | 18.1684 | 22.6419 | 23.7384 | 0 | 0 | 0 | 0 | 60.75 | 0.39076 | 1998-11-11 | 8:10 | 23.4167 | 23 | 47 | 48.5 | 272 | 6.3 | 2.43 |  | 8.73 | 0.18779 | 0.72165 | 30.1569 | 14.3794 | 15.0758 | 392.3353 | 235.9778 | 388.7138 | 1.5455 | 46.2045 | 0.32628 |  |  |  | 233 | 281 | 389 | 400.0556 | -2.842 | 16.6369 | 398.1209 | 41.4751 | 0.018 |  | 1.821 | 1.9993 | -9.7921 | 96.8393 | 1.9764 | 99.0892 | [8 empty] | Total hardness | mg/L as CaCO3 | 156 | 160 | 158 | 2.5316 | 364 | 361.4483 | 0.70102 | 27.1889 | 359.1488 | 56.0071 | Total hardness | mg/L as CaCO3 | 196 | 456 | 406 | 10.9649 | 9.6774 | 404.0753 | 51.4942 | Total hardness | mg/L as CaCO3 | 172 | 308 | 270.7672 | 12.0886 | 20.7373 | 269.8035 | 36.2499 | Total hardness | mg/L as CaCO3 | 150 | 240 | 245.7143 | -2.381 | 30.8756 | 244.6871 | 38.6972 | UV254 p, cm-1 | 0.0205 | 0.065 | 0.029 | 0.034 | UV254 p, cm-1 | 0.0205 | 0.065 | 0.029 | 0.034 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.9837 | 4.4957 | 4.7397 | 10.2962 | 1998-11-09 | 15:45 | 7 | 23 | 30 | 31 | 272 | 4.51 | 1.85 | 6.36 | 0.18779 | 0.70912 | 41.7673 | 10.2938 | 10.7924 | 0 | 0 | 0 | 0 | 30.5 | 0.35385 | 1998-11-11 | 9:00 | 24.25 | 23 | 47 | 48.5 | 272 | 6.27 | 2.88 |  | 9.15 | 0.18779 | 0.68525 | 28.7268 | 14.3109 | 15.004 | 384.4951 | 231.2726 | 380.9631 | 1.5146 | 46.2354 | 0.32451 | 7.43 | 7.32 | 7.61 | 226 | 282 | 384 | 395.974 | -3.1182 | 19.1413 | 394.0149 | 42.6418 | 0.018 | 0.609 | 1.72 | 1.7702 | -2.9164 | 96.8393 | 1.75 | 98.9714 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 130 | 140 | 135 | 7.4074 | 345 | 376.3793 | -9.0955 | 34.1463 | 373.6511 | 63.87 | Calcium hardness | mg/L as CaCO3 | 164 | 424 | 574 | -35.3774 | 20 | 570.2422 | 71.2403 | Calcium hardness | mg/L as CaCO3 | 152 | 254 | 268.3258 | -5.6401 | 25.8537 | 267.1908 | 43.1118 | Calcium hardness | mg/L as CaCO3 | 142 | 234 | 232 | 0.8547 | 30.7317 | 231.0342 | 38.5372 | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | 140 | 140 | 0 | 1998-11-09 | 16:05 | 7.3333 | 23 | 40 | 41 | 272 | 5.89 | 2.22 | 8.11 | 0.18779 | 0.72626 | 32.5388 | 13.4436 | 14.0947 | 0 | 0 | 0 | 0 | 40.5 | 0.34802 | 1998-11-11 | 10:00 | 25.25 | 24 | 47 | 48.5 | 272 | 6.24 | 2.73 |  | 8.97 | 0.18779 | 0.69565 | 29.3233 | 14.2425 | 14.4973 | 386.6911 | 232.6039 | 383.1561 | 1.5232 | 46.2268 | 0.31361 |  |  |  | 223 | 280 | 38/0 | 408.6429 | #VALUE! | 20.2147 | 406.5134 | 45.1433 | 0.017 |  | 1.664 | 1.8324 | -10.1176 | 97.0149 | 1.8115 | 99.0616 | [8 empty] | Turbidity | ntu | 0.085 | 0.086 | 0.0855 | 1.1696 | 1 | 1.9407 | -94.0672 | 86.2871 | 1.9197 | 95.5462 | Turbidity | ntu | 0.096 | 4.25 | 5.371 | -26.3765 | 84.603 | 5.3227 | 98.1964 | Turbidity | ntu | 0.074 | 1.15 | 1.2801 | -11.3093 | 88.1315 | 1.2683 | 94.1654 | Turbidity | ntu | 0.078 | 1.11 | 0.85729 | 22.7671 | 87.49 | 0.84892 | 90.8119 | Bromidep, ug/L | 130 | 140 | 130 | 130 | Bromidep, ug/L | 130 | 140 | 130 | 130 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 17 | 11 | 14 | 42.8571 | 1998-11-09 | 16:30 | 7.75 | 23 | 50 | 51.5 | 272 | 7.52 | 2.87 | 10.39 | 0.18779 | 0.72377 | 25.179 | 17.164 | 17.9953 | 0 | 0 | 0 | 0 | 50.75 | 0.35459 | 1998-11-11 | 11:00 | 26.25 | 24 | 47 | 48.5 | 272 | 6.17 | 2.64 |  | 8.81 | 0.18779 | 0.70034 | 29.874 | 14.0827 | 14.3347 | 387.6693 | 233.2168 | 384.1658 | 1.527 | 46.223 | 0.31012 |  |  |  | 225 | 281 | 383 | 406.8731 | -6.2332 | 19.4991 | 404.8103 | 44.4184 | 0.018 |  | 1.672 | 1.8584 | -11.1497 | 96.8393 | 1.8375 | 99.0204 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 421 | 421 | 421 | 421 | AlkF, mg/L CaCO3 | 421 | 421 | 421 | 421
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.01 | 1.97 | 1.49 | 64.4295 | 1998-11-09 | 17:30 | 8.75 | 23 | 60.5 | 51.5 | 272 | 7.64 | 2.53 | 10.17 | 0.18779 | 0.75123 | 25.7453 | 17.4379 | 18.2824 | 0 | 0 | 0 | 0 | 56 | 0.32647 | 1998-11-11 | 12:00 | 27.25 | 24 | 47 | 48.5 | 272 | 6.22 | 2.56 |  | 8.78 | 0.18779 | 0.70843 | 29.9795 | 14.1968 | 14.4508 | 389.4271 | 234.2567 | 385.8787 | 1.534 | 46.216 | 0.31268 |  |  |  | 223 | 282 | 386 | 416.7773 | -7.9734 | 20.2147 | 414.5617 | 46.2083 | 0.017 |  | 1.722 | 1.9119 | -11.028 | 97.0149 | 1.8902 | 99.1006 | [8 empty] | Total organic carbon | mg/L | 0.7 | 1 | 0.85 | 35.2941 | 42.9 | 39.2983 | 8.3956 | 92.9167 | 38.8637 | 97.8129 | Total organic carbon | mg/L | 1.8 | 122.3 | 103.8 | 15.1267 | 85 | 102.8651 | 98.2501 | Total organic carbon | mg/L | 1 | 34.2 | 25.1431 | 26.4822 | 91.6667 | 24.9075 | 95.9851 | Total organic carbon | mg/L | 0.8 | 17.6 | 16.8 | 4.5455 | 93.3333 | 16.6283 | 95.1889 | Alkp, mg/L CaCO3 | 321 | 384 | 330 | 312 | Alkp, mg/L CaCO3 | 321 | 384 | 330 | 312
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 15.99 | 9.03 | 12.51 | 55.6355 | 1998-11-10 | 8:30 | 23.75 | 23 | 49 | 50.5 | 272 | 7.33 | 5.3 | 12.63 | 0.18779 | 0.58036 | 20.536 | 16.7303 | 17.5406 | 0 | 0 | 0 | 0 | 49.75 | 0.35257 | 1998-11-11 | 13:00 | 28.25 | 24 | 47 | 48.5 | 272 | 6.17 | 2.49 |  | 8.66 | 0.18779 | 0.71247 | 30.4088 | 14.0827 | 14.3347 | 390.2856 | 234.7907 | 386.7584 | 1.5373 | 46.2127 | 0.31019 |  |  |  | 226 | 282 | 388 | 412.0683 | -6.2032 | 19.1413 | 409.9579 | 44.8724 | 0.017 |  | 1.762 | 1.9385 | -10.0196 | 97.0149 | 1.9168 | 99.1131 | [8 empty] | UV254 | cm-1 | 0.019 | 0.022 | 0.0205 | 14.6341 | 1.745 | 1.9136 | -9.6621 | 96.4004 | 1.8922 | 98.9166 | UV254 | cm-1 | 0.065 | 4.72 | 5.11 | -8.2627 | 88.5865 | 5.0638 | 98.7164 | UV254 | cm-1 | 0.029 | 1.452 | 1.2153 | 16.3014 | 94.9078 | 1.2037 | 97.5908 | UV254 | cm-1 | 0.034 | 0.797 | 0.799 | -0.25094 | 94.0299 | 0.79079 | 95.7005 | T-HdF, mg/L CaCO3 | 217 | 217 | 217 | 217 | T-HdF, mg/L CaCO3 | 217 | 217 | 217 | 217
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-11 | 14:00 | 29.25 | 24 | 47 | 48.5 | 272 | 6.17 | 2.44 |  | 8.61 | 0.18779 | 0.71661 | 30.5912 | 14.0827 | 14.3347 | 391.186 | 235.3324 | 387.6507 | 1.5409 | 46.2091 | 0.31021 | 7.53 | 7.48 | 7.83 | 229 | 281 | 384 | 407.1988 | -6.0413 | 18.068 | 405.1777 | 43.4816 | 0.018 | 0.6 | 1.784 | 1.9641 | -10.0937 | 96.8393 | 1.942 | 99.0731 | [8 empty] | SUVA | L/(mg*m) | 2.7143 | 2.2 | 2.4571 | 20.9302 | 4.0676 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 3.6111 | 3.8594 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.9 | 4.2456 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 4.25 | 4.5284 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 158 | 196 | 172 | 150 | T-Hdp, mg/L CaCO3 | 158 | 196 | 172 | 150
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.79 | 8.98 | 8.885 | 2.1384 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-11 | 15:00 | 30.25 | 24 | 47 | 48.5 | 272 | 6.17 | 2.4 |  | 8.57 | 0.18779 | 0.71995 | 30.7386 | 14.0827 | 14.3347 | 391.917 | 235.7722 | 388.375 | 1.5437 | 46.2063 | 0.31023 |  |  |  | 230 | 281 |  | 406.7563 |  | 17.7102 | 404.7515 | 43.175 | 0.018 |  | 1.807 | 1.9873 | -9.9787 | 96.8393 | 1.965 | 99.084 | [8 empty] | Bromide | mg/L | 130 | 130 | 130 | 0 | --- | 164.4828 | --- | 7.1429 | 164.093 | 20.7766 | Bromide | mg/L | 140 | --- | 140 | --- | 0 | 140 | 0 | Bromide | mg/L | 130 | --- | 151.9483 | --- | 7.1429 | 151.7341 | 14.3238 | Bromide | mg/L | 130 | --- | 144.2857 | --- | 7.1429 | 144.1324 | 9.8052 | Ca-HdF, mg/L CaCO3 | 205 | 205 | 205 | 205 | Ca-HdF, mg/L CaCO3 | 205 | 205 | 205 | 205
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-11 | 17:00 | 32.25 | 24 | 47 | 48.5 | 272 | 6.17 | 2.37 |  | 8.54 | 0.18779 | 0.72248 | 30.8501 | 14.0827 | 14.3347 | 392.4715 | 236.1058 | 388.9245 | 1.5459 | 46.2041 | 0.31025 | 7.47 | 7.44 | 7.45 | 230 | 283 | 389 | 408.3671 | -4.9787 | 17.7102 | 406.3441 | 43.3977 | 0.019 | 0.607 | 1.818 | 2.0027 | -10.1572 | 96.6637 | 1.9802 | 99.0405 | [8 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 135 | 164 | 152 | 142 | Ca-Hdp, mg/L CaCO3 | 135 | 164 | 152 | 142
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 1120 | 1070 | 1095 | 4.5662 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 8:20 | 47.5833 | 24 | 47 | 48.5 | 272 | 5.92 | 1.87 |  | 7.79 | 0.18779 | 0.75995 | 33.9166 | 13.5121 | 13.7539 | 400.7756 | 241.1917 | 397.3023 | 1.5785 | 46.1715 | 0.29789 |  |  |  | 242 | 281 | 390 | 398.2166 | -2.1068 | 13.4168 | 396.5166 | 38.9685 | 0.023 |  | 1.965 | 2.2996 | -17.0278 | 95.9614 | 2.2748 | 98.9889 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.63 | 1.74 | 1.185 | 93.6709 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.01 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.2 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.2 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 450 | 360 | 405 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 10:00 | 49.25 | 23 | 47 | 48.5 | 272 | 5.92 | 1.98 |  | 7.9 | 0.18779 | 0.74937 | 33.4304 | 13.5121 | 14.1665 | 398.3688 | 239.7432 | 394.9163 | 1.569 | 46.181 | 0.30676 | 7.34 | 7.46 | 7.6 | 235 | 282 | 392 | 412.5505 | -5.2425 | 15.9213 | 410.6183 | 42.7692 | 0.021 | 0.61 | 1.964 | 2.2095 | -12.4979 | 96.3126 | 2.1856 | 99.0392 | [8 empty] | SDS-Cl2 demand | mg/L | 3.37 | 2.26 | 2.815 | 39.4316 | --- | 36.246 | --- | 77.498 | 35.8682 | 92.1518 | SDS-Cl2 demand | mg/L | 1.99 | --- | 107.19 | --- | 84.0927 | 106.2258 | 98.1266 | SDS-Cl2 demand | mg/L | 1.8 | --- | 25.3066 | --- | 85.6115 | 25.0772 | 92.8222 | SDS-Cl2 demand | mg/L | 1.8 | --- | 17.1 | --- | 85.6115 | 16.9358 | 89.3716 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 59 | 45 | 52 | 26.9231 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 11:00 | 50.25 | 23 | 47 | 48.5 | 272 | 5.9 | 2.39 |  | 8.29 | 0.18779 | 0.7117 | 31.8106 | 13.4664 | 14.1186 | 390.0241 | 234.7284 | 386.6556 | 1.5361 | 46.2139 | 0.30551 |  |  |  | 232 | 282 | 384 | 396.7594 | -3.3228 | 16.9946 | 394.9725 | 41.2617 | 0.02 |  | 1.859 | 1.926 | -3.6044 | 96.4881 | 1.9053 | 98.9503 | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 93.4266 | 103.7976 | 97.5053 | 94.374 | Qp/QT (THM4), % | 102.0318 | 113.3581 | 106.4862 | 103.0665
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 6.4 | 5.3 | 5.85 | 18.8034 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 12:00 | 51.25 | 23 | 47 | 48.5 | 272 | 5.92 | 2.75 |  | 8.67 | 0.18779 | 0.68281 | 30.3725 | 13.5121 | 14.1665 | 383.8697 | 231.0175 | 380.5429 | 1.5119 | 46.2381 | 0.30638 |  |  |  | 230 | 282 | 377 | 386.06 | -2.4032 | 17.7102 | 384.3617 | 40.1605 | 0.02 |  | 1.764 | 1.7524 | 0.65626 | 96.4881 | 1.7336 | 98.8463 | [8 empty] | SDS-Chlorination pH | --- | 9.5 | 8.49 | 8.995 | 11.2285 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.43 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.56 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.79 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | NA | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 13:00 | 52.25 | 23 | 47 | 48.5 | 272 | 5.94 | 2.47 |  | 8.41 | 0.18779 | 0.7063 | 31.3424 | 13.5577 | 14.2143 | 388.8715 | 234.0206 | 385.4898 | 1.5316 | 46.2184 | 0.30755 | 7.44 | 7.44 | 7.53 | 240 | 281 | 376 | 374.4919 | 0.40109 | 14.1324 | 373.0234 | 35.6609 | 0.02 | 0.605 | 1.739 | 1.891 | -8.7389 | 96.4881 | 1.8705 | 98.9308 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 19.3579 | NA | 13.5869 | 18.0532 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 515.4 | 410.3 | 462.85 | 22.7071 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 15:30 | 54.75 | 23 | 47 | 48.5 | 272 | 5.97 | 2.47 |  | 8.44 | 0.18779 | 0.70735 | 31.2275 | 13.6262 | 14.2861 | 389.1069 | 234.1518 | 385.7058 | 1.5325 | 46.2175 | 0.30911 |  |  |  | 233 | 282 | 376 | 391.8907 | -4.2262 | 16.6369 | 390.147 | 40.2789 | 0.022 |  | 1.788 | 1.8928 | -5.8618 | 96.137 | 1.8723 | 98.825 | [8 empty] | SDS-TOX | mg Cl- /L | 60 | 63 | 61.5 | 4.878 | --- | 3625.2931 | --- | 94.3836 | 3585.0131 | 98.2845 | SDS-TOX | mg Cl- /L | 140 | --- | 9690 | --- | 87.2146 | 9602.47 | 98.542 | SDS-TOX | mg Cl- /L | 85 | --- | 2301.7739 | --- | 92.2374 | 2280.1452 | 96.2722 | SDS-TOX | mg Cl- /L | 72 | --- | 1533.4286 | --- | 93.4247 | 1517.7451 | 95.2561 | SDS-TOXb, ug Cl- /L | 129.4365 | NA | 110.1965 | 129.5538 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 5.4 | 5.5 | 5.45 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 16:30 | 55.75 | 23 | 47 | 48.5 | 272 | 5.92 | 2.33 |  | 8.25 | 0.18779 | 0.71758 | 31.9697 | 13.5121 | 14.1665 | 391.3085 | 235.4943 | 387.9173 | 1.5412 | 46.2088 | 0.30658 | 7.48 | 7.47 | 7.78 | 238 | 282 | 376 | 384.9421 | -2.3782 | 14.8479 | 383.343 | 37.9146 | 0.02 | 0.598 | 1.752 | 1.9657 | -12.1949 | 96.4881 | 1.9445 | 98.9714 | [8 empty] | SDS-CHCl3 | mg/L | 3.5 | 6.3 | 4.9 | 57.1429 | --- | 1384.5552 | --- | 98.7901 | 1368.9615 | 99.6421 | SDS-CHCl3 | mg/L | 29 | --- | 3789 | --- | 92.8395 | 3754.5379 | 99.2276 | SDS-CHCl3 | mg/L | 12 | --- | 874.5665 | --- | 97.037 | 866.1505 | 98.6146 | SDS-CHCl3 | mg/L | 8.7 | --- | 574.8429 | --- | 97.8519 | 568.7672 | 98.4704 | SDS-CDb, mg/L | 3.4523 | NA | 2.0672 | 2.4025 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 100 | 110 | 105 | 9.5238 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-12 | 17:45 | 57 | 23 | 47 | 48.5 | 272 | 5.89 | 2.25 |  | 8.14 | 0.18779 | 0.72359 | 32.4152 | 13.4436 | 14.0947 | 392.6135 | 236.2903 | 389.2284 | 1.5463 | 46.2037 | 0.30506 |  |  |  | 233 | 282 | 377 | 401.2267 | -6.4262 | 16.6369 | 399.4052 | 41.6633 | 0.02 |  | 1.817 | 2.008 | -10.5101 | 96.4881 | 1.9864 | 98.9932 | [8 empty] | SDS-BDCM | mg/L | 6.1 | 9.1 | 7.6 | 39.4737 | --- | 160.7034 | --- | 85.3846 | 158.973 | 95.2193 | SDS-BDCM | mg/L | 25 | --- | 295 | --- | 51.9231 | 292.5253 | 91.4537 | SDS-BDCM | mg/L | 15 | --- | 96.2085 | --- | 71.1538 | 95.4162 | 84.2794 | SDS-BDCM | mg/L | 11 | --- | 69.5714 | --- | 78.8462 | 68.9429 | 84.0448 | TOCb, mg/L | 1.5829 | NA | 1.2744 | 1.4301 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 83 | 110 | 96.5 | 27.9793 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 8:50 | 72.0833 | 22 | 47 | 48.5 | 272 | 5.65 | 1.42 |  | 7.07 | 0.18779 | 0.79915 | 37.4724 | 12.8958 | 13.926 | 409.8349 | 246.7433 | 406.4471 | 1.614 | 46.136 | 0.30185 | 7.3 | 7.36 | 7.34 | 268 | 282 | 397 | 325.257 | 18.0713 | 4.1145 | 324.6624 | 17.4527 | 0.028 | 0.598 | 2.24 | 2.7241 | -21.6098 | 95.0834 | 2.6961 | 98.9614 | [8 empty] | SDS-DBCM | mg/L | 14 | 17 | 15.5 | 19.3548 | --- | -17.7759 | --- | -164.9573 | -17.3998 | 189.0817 | SDS-DBCM | mg/L | 24 | --- | -157.5 | --- | -310.2564 | -155.8365 | 115.4008 | SDS-DBCM | mg/L | 21 | --- | -12.2516 | --- | -258.9744 | -11.9272 | 276.0685 | SDS-DBCM | mg/L | 16 | --- | 1.5 | --- | -173.5043 | 1.6556 | -866.4121 | UV254 b, cm-1 | 0.056588 | NA | 0.042484 | 0.064127 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 10:00 | 73.25 | 22 | 47 | 48.5 | 272 | 5.7 | 1.9 |  | 7.6 | 0.18779 | 0.75 | 34.7895 | 13.0099 | 14.0492 | 398.4275 | 239.8575 | 395.1046 | 1.5691 | 46.1809 | 0.30422 |  |  |  | 240 | 281 | 377 | 398 | -5.5703 | 14.1324 | 396.3445 | 39.4466 | 0.026 |  | 2.044 | 2.2 | -7.6321 | 95.4346 | 2.1772 | 98.8058 | [8 empty] | SDS-CHBr3 | mg/L | 17 | 16 | 16.5 | 6.0606 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 8.3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 14 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 13 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 130.6573 | NA | 130.2495 | 130.5626 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.4 | 1.7 | 1.55 | 19.3548 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 11:00 | 74.25 | 22 | 47 | 48.5 | 272 | 5.7 | 2.41 |  | 8.11 | 0.18779 | 0.70284 | 32.5388 | 13.0099 | 14.0492 | 388.0443 | 233.6067 | 384.808 | 1.5282 | 46.2218 | 0.30395 |  |  |  | 235 | 282 | 367 | 384.749 | -4.8362 | 15.9213 | 383.1799 | 38.6711 | 0.025 |  | 1.85 | 1.8573 | -0.39576 | 95.6102 | 1.8381 | 98.6399 | [8 empty] | SDS-THM4 | mg/L | 40.6 | 48.4 | 44.5 | 17.5281 | --- | 1487.0862 | --- | 90.3857 | 1470.7813 | 96.9744 | SDS-THM4 | mg/L | 86.3 | --- | 3851.8 | --- | 81.3547 | 3817.2875 | 97.7392 | SDS-THM4 | mg/L | 62 | --- | 941.7959 | --- | 86.6047 | 933.2118 | 93.3563 | SDS-THM4 | mg/L | 48.7 | --- | 640.3429 | --- | 89.4782 | 633.9936 | 92.3185 | Alkb, mg/L CaCO3 | 327.5734 | NA | 332.2702 | 318.1323 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 14 | 15 | 14.5 | 6.8966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 12:00 | 75.25 | 23 | 47 | 48.5 | 272 | 5.7 | 2.18 |  | 7.88 | 0.18779 | 0.72335 | 33.5178 | 13.0099 | 13.64 | 392.4933 | 236.285 | 389.2198 | 1.5457 | 46.2043 | 0.29521 |  |  |  | 237 | 283 | 362 | 390.6239 | -7.9071 | 15.2057 | 389.0142 | 39.0768 | 0.025 |  | 1.838 | 1.9932 | -8.4436 | 95.6102 | 1.9726 | 98.7326 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 161.8783 | NA | 173.1226 | 153.7694 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | NR | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 13:00 | 76.25 | 24 | 47 | 48.5 | 272 | 5.65 | 1.86 |  | 7.51 | 0.18779 | 0.75233 | 35.2184 | 12.8958 | 13.1266 | 398.9357 | 240.1813 | 395.638 | 1.5711 | 46.1789 | 0.28425 | 7.45 | 7.57 | 7.5 | 244 | 282 | 375 | 387.336 | -3.2896 | 12.7013 | 385.8473 | 36.7626 | 0.027 | 0.603 | 1.904 | 2.2174 | -16.461 | 95.259 | 2.1947 | 98.7697 | [8 empty] | SDS-DCAA* | mg/L | 1.4 | 2.4 | 1.9 | 52.6316 | --- | 357.4172 | --- | 98.1905 | 353.399 | 99.4624 | SDS-DCAA* | mg/L | 7 | --- | 987 | --- | 93.3333 | 978.0179 | 99.2843 | SDS-DCAA* | mg/L | 3.8 | --- | 225.9164 | --- | 96.381 | 223.7492 | 98.3017 | SDS-DCAA* | mg/L | 3.1 | --- | 148.6714 | --- | 97.0476 | 147.1092 | 97.8927 | Ca-Hdb, mg/L CaCO3 | 139.6014 | NA | 153.3222 | 145.5444 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | BMRL | 2.2 | 2.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 14:00 | 77.25 | 23 | 47 | 48.5 | 272 | 5.7 | 1.67 |  | 7.37 | 0.18779 | 0.77341 | 35.9064 | 13.0099 | 13.64 | 403.7894 | 243.0854 | 400.4217 | 1.5902 | 46.1598 | 0.2955 |  |  |  | 242 | 281 |  | 407.494 |  | 13.4168 | 405.76 | 40.3588 | 0.029 |  | 1.947 | 2.4143 | -24.0021 | 94.9078 | 2.3893 | 98.7863 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.9 | --- | 947.9 | --- | 98.0311 | 939.2295 | 99.7977 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 12 | 12 | 12 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 15:40 | 78.9167 | 22 | 47 | 48.5 | 272 | 5.65 | 0.56 |  | 6.21 | 0.18779 | 0.90982 | 42.8003 | 12.8958 | 13.926 | 438.1284 | 263.7775 | 434.5068 | 1.7254 | 46.0246 | 0.30258 |  |  |  | 250 | 282 |  | 577.1339 |  | 10.5546 | 573.7363 | 56.426 | 0.034 |  | 2.223 | 5.9723 | -168.66 | 94.0299 | 5.9106 | 99.4248 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 189.8 | 227.2 | 208.5 | 17.9376 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 16:30 | 79.75 | 23 | 47 | 48.5 | 272 | 5.55 | 0.47 |  | 6.02 | 0.18779 | 0.92193 | 44.1827 | 12.6676 | 13.2811 | 441.4038 | 265.7892 | 437.8205 | 1.7382 | 46.0118 | 0.28865 |  |  |  | 254 | 281 |  | 580.617 |  | 9.1234 | 577.2848 | 56.0009 | 0.037 |  | 2.463 | 6.8575 | -178.4219 | 93.5031 | 6.7879 | 99.4549 | [8 empty] | SDS-DBAA* | mg/L | 4 | 4.3 | 4.15 | 7.2289 | --- | -4.8155 | --- | -167.7419 | -4.7142 | 188.0322 | SDS-DBAA* | mg/L | 6.1 | --- | -39.4 | --- | -293.5484 | -38.983 | 115.6479 | SDS-DBAA* | mg/L | 4.8 | --- | -2.3332 | --- | -209.6774 | -2.2636 | 312.0529 | SDS-DBAA* | mg/L | 3.6 | --- | 0.67143 | --- | -132.2581 | 0.70286 | -412.1953 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 203.8 | 242.2 | 223 | 17.2197 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 17:00 | 80.25 | 23 | 47 | 48.5 | 272 | 5.55 | 0.58 |  | 6.13 | 0.18779 | 0.90538 | 43.3719 | 12.6676 | 13.2811 | 436.8628 | 263.0549 | 433.3164 | 1.7203 | 46.0297 | 0.28853 |  |  |  | 257 | 282 |  | 494.8017 |  | 8.0501 | 492.3756 | 47.8041 | 0.04 |  |  | 5.6363 |  | 92.9763 | 5.5792 | 99.283 | [8 empty] | SDS-BCAA* | mg/L | 1.5 | 1.9 | 1.7 | 23.5294 | --- | 45.8379 | --- | 88.2759 | 45.3391 | 96.2505 | SDS-BCAA* | mg/L | 6 | --- | 91 | --- | 58.6207 | 90.2209 | 93.3497 | SDS-BCAA* | mg/L | 2.7 | --- | 28.5989 | --- | 81.3793 | 28.3463 | 90.4749 | SDS-BCAA* | mg/L | 2.4 | --- | 19.6857 | --- | 83.4483 | 19.5002 | 87.6924 | Qp/QT (HAA5), % | 76.3151 | 79.845 | 77.2886 | 76.561 | Qp/QT (HAA5), % | 89.6518 | 93.7984 | 90.7954 | 89.9405
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 17:20 | 80.5833 | 23 | 47 | 48.5 | 272 | 5.55 | 0.65 |  | 6.2 | 0.18779 | 0.89516 | 42.871 | 12.6676 | 13.2811 | 434.1034 | 261.3933 | 430.5793 | 1.7095 | 46.0405 | 0.28846 | 7.41 | 7.5 |  | 255 | 282 |  | 488.6923 |  | 8.7657 | 486.3081 | 47.5641 | 0.038 | 0.611 |  | 5.1077 |  | 93.3275 | 5.056 | 99.2484 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 143.5856 | 162.1938 | 153.0385 | 145.7728 | SDS-THM4b, ug/L | 87.7918 | 109.6519 | 98.8966 | 90.3613
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-13 | 17:40 | 80.9167 | 23 | 47 | 48.5 | 272 | 5.51 | 0.6 |  | 6.11 | 0.18779 | 0.9018 | 43.5172 | 12.5763 | 13.1854 | 435.8696 | 262.4725 | 432.357 | 1.7164 | 46.0336 | 0.28643 |  |  |  | 255 | 282 |  | 504.4917 |  | 8.7657 | 501.9646 | 49.1996 | 0.04 |  |  | 5.4321 |  | 92.9763 | 5.3775 | 99.2562 | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.2 | --- | 2.2 | --- | 0 | 2.2 | 0 | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-11-14 | 12:00 | 99.25 | 22 | 47 | 48 | 272 | 4.8 | 0.19 |  | 4.99 | 0.18779 | 0.96192 | 53.509 | 10.9557 | 11.8309 | 452.3081 | 272.6597 | 449.1379 | 1.7806 | 45.7194 | 0.25877 | 7.58 | 7.53 |  | 272 | 282 | 412 | 468.9737 | -13.8286 | 2.6834 | 467.2357 | 41.7853 | 0.087 | 0.6 |  | 12.759 |  | 84.7234 | 12.6472 | 99.3121 | [8 empty] | SDS-DCBAA | mg/L | 1.2 | 1.5 | 1.35 | 22.2222 | --- | 38.0741 | --- | 88.75 | 37.6591 | 96.4152 | SDS-DCBAA | mg/L | 2.5 | --- | 97.5 | --- | 79.1667 | 96.6293 | 97.4128 | SDS-DCBAA | mg/L | 1.4 | --- | 24.6652 | --- | 88.3333 | 24.4382 | 94.2713 | SDS-DCBAA | mg/L | 1.2 | --- | 16.6286 | --- | 90 | 16.463 | 92.7109 | SDS-TOXb, ug Cl- /L | 306.283 | 332.4806 | 314.3847 | 311.7815 | SDS-TOXb, ug Cl- /L | 168.449 | 199.2248 | 177.9665 | 174.9083
[44 empty] | 1998-11-14 | 12:30 | 99.75 | 22 | 46.5 | 48 | 272 | 4.8 | 0.72 |  | 5.52 | 0.18779 | 0.86957 | 48.2754 | 10.9557 | 11.8309 | 426.9622 | 257.3807 | 423.9696 | 1.6809 | 45.5691 | 0.25963 |  |  |  | 262 | 281 |  | 396.1667 |  | 6.2612 | 394.9828 | 33.668 | 0.088 |  |  | 3.7795 |  | 84.5478 | 3.7469 | 97.6514 | [8 empty] | SDS-HAA5 | mg/L | 5.4 | 6.7 | 6.05 | 21.4876 | --- | 704.1534 | --- | 97.0983 | 696.2631 | 99.1311 | SDS-HAA5 | mg/L | 15 | --- | 1950 | --- | 92.8058 | 1932.2649 | 99.2237 | SDS-HAA5 | mg/L | 8.6 | --- | 447.3456 | --- | 95.8753 | 443.0649 | 98.059 | SDS-HAA5 | mg/L | 6.7 | --- | 294.9857 | --- | 96.7866 | 291.8919 | 97.7046 | SDS-CDb, mg/L | 5.1112 | 4.1103 | 4.2324 | 4.3103 | SDS-CDb, mg/L | 3.8183 | 2.6424 | 2.7858 | 2.8774
[44 empty] | 1998-11-14 | 13:00 | 100.25 | 22 | 46.5 | 48 | 272 | 4.84 | 0.66 |  | 5.5 | 0.18779 | 0.88 | 48.4545 | 11.047 | 11.9295 | 429.7034 | 259.0177 | 426.6662 | 1.6917 | 45.5583 | 0.26185 | 7.61 | 7.66 |  | 261 | 282 |  | 415.1667 |  | 6.619 | 413.795 | 36.9253 | 0.081 | 0.597 |  | 4.1518 |  | 85.777 | 4.1156 | 98.0319 | [8 empty] | SDS-HAA6 | mg/L | 6.9 | 8.6 | 7.75 | 21.9355 | --- | 749.9914 | --- | 96.5247 | 741.6021 | 98.955 | SDS-HAA6 | mg/L | 21 | --- | 2041 | --- | 90.583 | 2022.4858 | 98.9617 | SDS-HAA6 | mg/L | 11.3 | --- | 475.9446 | --- | 94.9327 | 471.4111 | 97.6029 | SDS-HAA6 | mg/L | 9.1 | --- | 314.6714 | --- | 95.9193 | 311.3922 | 97.0776 | TOCb, mg/L | 3.4909 | 3.8558 | 3.4982 | 3.4252 | TOCb, mg/L | 2.0038 | 2.4326 | 2.0125 | 1.9267
[44 empty] | 1998-11-14 | 13:30 | 100.75 | 22 | 48 | 49.5 | 272 | 4.98 | 0.62 |  | 5.6 | 0.18779 | 0.88929 | 47.5714 | 11.3666 | 12.2746 | 432.2286 | 260.4856 | 429.0841 | 1.7017 | 47.0483 | 0.26089 |  |  |  | 258 | 281 |  | 452.1935 |  | 7.6923 | 450.4158 | 42.7196 | 0.083 |  |  | 4.4772 |  | 85.4258 | 4.437 | 98.1294 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.15053 | 0.16668 | 0.15175 | 0.15952 | UV254 b, cm-1 | 0.077312 | 0.096287 | 0.078751 | 0.087868
[44 empty] | 1998-11-14 | 14:30 | 101.75 | 22 | 48.5 | 50.5 | 272 | 5.43 | 3.63 |  | 9.06 | 0.18779 | 0.59934 | 29.0221 | 12.3937 | 13.3837 | 366.9832 | 221.0168 | 364.0692 | 1.4451 | 48.0549 | 0.27851 | 7.57 | 7.59 | 7.47 | 231 | 281 | 349 | 352.0496 | -0.87381 | 17.3524 | 350.8413 | 34.1583 | 0.047 | 0.613 | 2.564 | 1.3511 | 47.3053 | 91.7471 | 1.3381 | 96.4875 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 132.3685 | 140 | 132.2711 | 132.3439 | Bromideb, ug/L | 131.0348 | 140 | 130.9205 | 131.0059
[44 empty] | 1998-11-14 | 15:00 | 102.25 | 22 | 48.5 | 50.5 | 272 | 5.5 | 5.2 |  | 10.7 | 0.18779 | 0.51402 | 24.4206 | 12.5535 | 13.5563 | 351.3433 | 211.5755 | 348.5171 | 1.3835 | 48.1165 | 0.28174 |  |  |  | 228 | 281 | 335 | 333.9712 | 0.30712 | 18.4258 | 332.8998 | 31.5109 | 0.04 |  | 1.994 | 1.1295 | 43.3527 | 92.9763 | 1.1185 | 96.4239 | [47 empty] | Alkb, mg/L CaCO3 | 344.6849 | 391.4574 | 350.6673 | 337.5486 | Alkb, mg/L CaCO3 | 331.3482 | 386.2946 | 338.3762 | 322.9648
[44 empty] | 1998-11-14 | 15:20 | 102.5833 | 23 | 48.5 | 50.5 | 272 | 5.6 | 4.75 |  | 10.35 | 0.18779 | 0.54106 | 25.2802 | 12.7817 | 13.4007 | 356.182 | 214.4573 | 353.2641 | 1.4027 | 48.0973 | 0.27862 |  |  |  | 227 | 281 |  | 341.3947 |  | 18.7835 | 340.2171 | 33.2779 | 0.037 |  | 1.694 | 1.1973 | 29.3218 | 93.5031 | 1.1853 | 96.8785 | [47 empty] | T-Hdb, mg/L CaCO3 | 171.9741 | 200.2326 | 182.2201 | 165.7042 | T-Hdb, mg/L CaCO3 | 164.1055 | 197.3023 | 176.1421 | 156.7398
[44 empty] | 1998-11-14 | 15:40 | 102.9167 | 23 | 48.5 | 50.5 | 272 | 5.6 | 5.05 |  | 10.65 | 0.18779 | 0.52582 | 24.5399 | 12.7817 | 13.4007 | 353.4504 | 212.8126 | 350.5549 | 1.3919 | 48.1081 | 0.27855 |  |  |  | 226 | 281 | 328 | 338.8267 | -3.3008 | 19.1413 | 337.6653 | 33.0698 | 0.034 |  | 1.5 | 1.1633 | 22.4452 | 94.0299 | 1.1517 | 97.0478 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 151.5794 | 172.2636 | 164.037 | 156.7666 | Ca-Hdb, mg/L CaCO3 | 142.2438 | 166.5426 | 156.8784 | 148.3375
[44 empty] | 1998-11-14 | 16:00 | 103.25 | 23 | 48.5 | 50.5 | 272 | 5.15 | 6 |  | 11.15 | 0.18779 | 0.46188 | 23.3946 | 11.7546 | 12.3239 | 342.3552 | 206.2706 | 339.7786 | 1.348 | 48.152 | 0.25594 |  |  |  | 225 | 281 | 324 | 326.2792 | -0.70345 | 19.4991 | 325.3204 | 30.8374 | 0.031 |  | 1.298 | 1.0317 | 20.5152 | 94.5566 | 1.0222 | 96.9674 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-11-14 | 16:20 | 103.5833 | 23 | 48.5 | 50.5 | 272 | 5.68 | 5.83 |  | 11.51 | 0.18779 | 0.49348 | 22.6316 | 12.9643 | 13.5922 | 347.8067 | 209.3895 | 344.9162 | 1.3697 | 48.1303 | 0.2824 |  |  |  | 223 | 281 | 324 | 334.5463 | -3.255 | 20.2147 | 333.3816 | 33.1097 | 0.029 |  | 1.239 | 1.0961 | 11.534 | 94.9078 | 1.085 | 97.3271 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-11-14 | 16:40 | 103.9167 | 23 | 48.5 | 50.5 | 272 | 5.75 | 5.55 |  | 11.3 | 0.18779 | 0.50885 | 23.0708 | 13.1241 | 13.7597 | 350.4877 | 210.9814 | 347.5386 | 1.3803 | 48.1197 | 0.28595 |  |  |  | 224 | 281 | 323 | 337 | -4.3344 | 19.8569 | 335.8056 | 33.2947 | 0.028 |  | 1.203 | 1.1305 | 6.0255 | 95.0834 | 1.1189 | 97.4975 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-11-14 | 17:00 | 104.25 | 23 | 48.5 | 50.5 | 272 | 5.73 | 5.25 |  | 10.98 | 0.18779 | 0.52186 | 23.7723 | 13.0784 | 13.7118 | 352.774 | 212.3641 | 349.8161 | 1.3893 | 48.1107 | 0.28501 | 7.5 |  | 7.5 | 225 | 281 | 325 | 338.9829 | -4.3024 | 19.4991 | 337.7823 | 33.389 | 0.027 | 0.588 | 1.191 | 1.1616 | 2.4685 | 95.259 | 1.1496 | 97.6515 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-11-14 | 17:20 | 104.5833 | 23 | 48.5 | 50.5 | 272 | 5.75 | 5.7 |  | 11.45 | 0.18779 | 0.50218 | 22.7555 | 13.1241 | 13.7597 | 349.3254 | 210.2818 | 346.3861 | 1.3757 | 48.1243 | 0.28592 |  |  |  | 225 |  | 324 | 334.4781 | -3.234 | 19.4991 | 333.3209 | 32.4975 | 0.027 |  | 1.167 | 1.1168 | 4.3052 | 95.259 | 1.1052 | 97.5571 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-11-15 | 11:45 | 123 | 23 | 49 | 50.5 | 272 | 5.28 | 1.53 |  | 6.81 | 0.18779 | 0.77533 | 38.9413 | 12.0513 | 12.635 | 404.0657 | 243.4043 | 400.947 | 1.591 | 48.159 | 0.26236 | 7.42 | 7.48 | 7.8 | 277 | 281 | 357 | 288.1275 | 19.292 | 0.89445 | 288.0194 | 3.8259 | 0.036 | 0.606 | 1.984 | 2.4106 | -21.5019 | 93.6787 | 2.3876 | 98.4922 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-11-15 | 12:30 | 123.75 | 22 | 50 | 52 | 272 | 5.6 | 12.81 |  | 18.41 | 0.18779 | 0.30418 | 13.7746 | 12.7817 | 13.8027 | 317.9873 | 191.4603 | 315.3824 | 1.2522 | 49.7478 | 0.27745 |  |  |  | 220 | 281 | 311 | 305.5109 | 1.765 | 21.288 | 304.6307 | 27.7814 | 0.029 |  | 1.079 | 0.80578 | 25.3212 | 94.9078 | 0.79779 | 96.3649 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-11-15 | 13:00 | 124.25 | 22 | 50 | 52 | 272 | 5.68 | 12.89 |  | 18.57 | 0.18779 | 0.30587 | 13.6473 | 12.9643 | 13.9999 | 318.2383 | 191.5885 | 315.5936 | 1.2533 | 49.7467 | 0.28142 |  |  |  | 215 | 281 | 302 | 307.922 | -1.9609 | 23.0769 | 306.9518 | 29.9564 | 0.024 |  | 0.881 | 0.80988 | 8.0732 | 95.7858 | 0.80167 | 97.0062 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-11-15 | 13:20 | 124.5833 | 23 | 50 | 52 | 272 | 5.72 | 13.49 |  | 19.21 | 0.18779 | 0.29776 | 13.1593 | 13.0556 | 13.6879 | 317.0773 | 190.8781 | 314.4234 | 1.2487 | 49.7513 | 0.27513 |  |  |  | 215 | 282 | 296 | 306.8491 | -3.6653 | 23.0769 | 305.8834 | 29.7118 | 0.021 |  | 0.887 | 0.80207 | 9.5745 | 96.3126 | 0.79386 | 97.3547 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-11-15 | 13:40 | 124.9167 | 22 | 50 | 52 | 272 | 5.73 | 13.2 |  | 18.93 | 0.18779 | 0.30269 | 13.3687 | 13.0784 | 14.1232 | 317.786 | 191.3019 | 315.1215 | 1.2515 | 49.7485 | 0.28389 |  |  |  | 213 | 281 | 296 | 308.367 | -4.1781 | 23.7925 | 307.3625 | 30.7007 | 0.023 |  | 0.834 | 0.80673 | 3.2697 | 95.9614 | 0.79848 | 97.1195 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-11-15 | 14:00 | 125.25 | 22 | 50 | 52 | 272 | 5.76 | 12.91 |  | 18.67 | 0.18779 | 0.30852 | 13.5688 | 13.1469 | 14.1971 | 318.6285 | 191.8005 | 315.9428 | 1.2549 | 49.7451 | 0.2854 |  |  |  | 214 | 281 | 305 | 308.7239 | -1.2209 | 23.4347 | 307.7209 | 30.4565 | 0.024 |  | 0.824 | 0.81288 | 1.3491 | 95.7858 | 0.80453 | 97.0169 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-11-15 | 14:20 | 125.5833 | 22 | 50 | 52 | 272 | 5.79 | 13.71 |  | 19.5 | 0.18779 | 0.29692 | 12.9487 | 13.2154 | 14.2711 | 316.964 | 190.7899 | 314.2782 | 1.2483 | 49.7517 | 0.28685 |  |  |  | 213 | 281 | 301 | 307.5842 | -2.1875 | 23.7925 | 306.5775 | 30.5233 | 0.022 |  | 0.82 | 0.80072 | 2.3512 | 96.137 | 0.79243 | 97.2237 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-11-15 | 14:40 | 125.9167 | 23 | 50 | 52 | 272 | 5.83 | 13.49 |  | 19.32 | 0.18779 | 0.30176 | 13.0787 | 13.3067 | 13.9511 | 317.6615 | 191.1983 | 314.9509 | 1.2511 | 49.7489 | 0.28043 | 7.65 | 7.62 | 7.65 | 216 | 281 | 298 | 306.9429 | -3.001 | 22.7191 | 305.9683 | 29.4044 | 0.023 | 0.593 | 0.817 | 0.80568 | 1.3853 | 95.9614 | 0.79729 | 97.1152
[44 empty] | 1998-11-15 | 15:00 | 126.25 | 23 | 50 | 52 | 272 | 5.84 | 13.14 |  | 18.98 | 0.18779 | 0.30769 | 13.3309 | 13.3295 | 13.975 | 318.5175 | 191.7107 | 315.7949 | 1.2545 | 49.7455 | 0.28093 | 7.59 | 7.59 | 7.53 | 225 | 281 | 299 | 303.7222 | -1.5793 | 19.4991 | 302.8771 | 25.7124 | 0.023 |  | 0.82 | 0.81239 | 0.92818 | 95.9614 | 0.80391 | 97.139
[44 empty] | 1998-11-15 | 15:20 | 126.5833 | 23 | 50 | 52 | 272 | 5.94 | 13.82 |  | 19.76 | 0.18779 | 0.30061 | 12.7652 | 13.5577 | 14.2143 | 317.5067 | 191.0737 | 314.7456 | 1.2505 | 49.7495 | 0.28572
[44 empty] | 1998-11-16 | 9:00 | 144.25 | 23 | 50 | 52 | 272 | 5.94 | 13.82 | X | 19.76 | 0.18779 | 0.30061 | 12.7652 | 13.5577 | 14.2143 | 317.5067 | 191.0737 | 314.7456 | 1.2505 | 49.7495 | 0.28572
[44 empty] | 1998-11-16 | 11:30 |  | 23 | 51.5 | 52.5 | 272 | 8.25 | 10.1 |  | 18.35 | 0.18779 | 0.44959 | 13.8229 | 18.8302 | 19.7421 | 340.8413 | 204.4034 | 336.703 | 1.3437 | 50.6563 | 0.38973
[44 empty] | 1998-11-16 | 13:10 |  | 23 | 52 | 52.5 | 272 | 8.2 | 9.6 |  | 17.8 | 0.18779 | 0.46067 | 14.2809 | 18.7161 | 19.6225 | 342.6865 | 205.5256 | 338.5515 | 1.3509 | 50.8991 | 0.38552
[44 empty] | 1998-11-16 | 13:40 |  | 23 | 60 | 61 | 272 | 9.44 | 11.2 |  | 20.64 | 0.18779 | 0.45736 | 12.1783 | 21.5463 | 22.5898 | 342.3476 | 204.935 | 337.5786 | 1.3503 | 59.1497 | 0.38191
[44 empty] | 1998-11-16 | 13:55 |  | 23 | 29.5 | 30.5 | 272 | 4.72 | 4.88 |  | 9.6 | 0.18779 | 0.49167 | 27.3333 | 10.7731 | 11.2949 | 347.311 | 209.3903 | 344.9176 | 1.3672 | 28.6328 | 0.39447
[44 empty] | 1998-11-16 | 14:15 |  | 23 | 40 | 41.5 | 272 | 6.3 | 6.4 |  | 12.7 | 0.18779 | 0.49606 | 20.4173 | 14.3794 | 15.0758 | 348.3717 | 209.5351 | 345.156 | 1.3723 | 39.3777 | 0.38285
[44 empty] | 1998-11-16 | 14:30 |  | 23 | 50 | 51 | 272 | 7.82 | 7.93 |  | 15.75 | 0.18779 | 0.49651 | 16.2698 | 17.8487 | 18.7132 | 348.7458 | 209.2802 | 344.7361 | 1.3746 | 49.1254 | 0.38093
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/9/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used for this study
Note on X27: C. Rice 7/19/99: Feed TOX verified by consultant. No explanation was given as to why the concentrations are low conpared to the other quarters.
Note on X32: C. Rice 7/19/99: Feed THM4 verified by consultant. No explanation was given as to why the concentrations are low conpared to the other quarters.
Note on CZ9: C. Rice 7/9/99: Consultant verified that all water quality parameters were found to be correct. No explanation was given as to why many concentrations appear low compared to the other three runs.

## SR40. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 1A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.53044 | [45 empty] | Recovery during sample collection (decimal) | 0.71078 | [10 empty] | Recovery during sample collection (decimal) | 0.89827 | [7 empty] | Recovery during sample collection (decimal) | 0.51194 | [7 empty] | Recovery during sample collection (decimal) | 0.31425 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060167 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1999-04-01 | 1999-04-09 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 6.5846 | [10 empty] | Feed flow rate during sample collection (mL/min) | 4.49 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.3801 | [7 empty] | Feed flow rate during sample collection (mL/min) | 15.968 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 0:00 | 0:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [6 empty] | SDS-THM4F, ug/L | 539.45 | 539.45 | 539.45 | 539.45 | SDS-THM4F, ug/L | 539.45 | 539.45 | 539.45 | 539.45 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 38.25 | 70.7 | 41.4 | 33.4 | SDS-THM4p, ug/L | 38.25 | 70.7 | 41.4 | 33.4 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.3 | 7.9 | 8.1 | 4.9383 | 1999-03-24 | 16:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 8:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 131.2 | 131.2 | 131.2 | 131.2 | SDS-HAA5F, ug/L | 131.2 | 131.2 | 131.2 | 131.2 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1999-03-24 | 16:30 | 0.5 | 24 | 58 | 59 | 272 | 6.34 | 2.4 | 8.74 | 0.18779 | 0.7254 | 30.1213 | 14.4707 | 14.7296 | 0 | 0 | 0 | 0 | 58.5 | 0.25179 | 1999-03-26 | 8:30 | 0.5 | 24 | 48 | 49 | 272 | 5.8 | 0.71 |  | 6.51 | 0.18779 | 0.89094 | 40.7819 | 13.2382 | 13.4751 | 560.6246 | 260.2391 | 554.2193 | 2.9718 | 45.5282 | 0.29597 | 7.8 | 7.6 |  | 155 | 299 |  | 1420.3239 |  | 47.099 | 1406.8334 | 88.9823 | BMRL | 0.623 | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 5.8 | 11.7 | 7.6 | 4.4 | SDS-HAA5p, ug/L | 5.8 | 11.7 | 7.6 | 4.4 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 350 | 346 | 348 | 1.1494 | 1999-03-24 | 17:00 | 1 | 24 | 50 | 51 | 272 | 5.93 | 1.07 | 7 | 0.18779 | 0.84714 | 37.8571 | 13.5349 | 13.7771 | 0 | 0 | 0 | 0 | 50.5 | 0.27281 | 1999-03-26 | 8:45 | 0.75 | 24 | 50 | 51 | 272 | 5.94 | 1.47 |  | 7.41 | 0.18779 | 0.80162 | 35.7072 | 13.5577 | 13.8003 | 513.6897 | 238.3849 | 507.6775 | 2.723 | 47.777 | 0.28885 | 7.7 | 7.5 | 7.6 | 131 | 297 | 230 | 947.6122 | -312.0053 | 55.2901 | 938.6956 | 86.0445 | BMRL | 0.62 | 0.554 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1999-03-27 | 1999-03-28 | --- | --- | 1999-03-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-29 | 1999-03-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-30 | 1999-03-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-31 | 1999-03-31 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1665 | 1665 | 1665 | 1665 | SDS-TOXF, ug Cl- /L | 1665 | 1665 | 1665 | 1665 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 293 | 293 | 293 | 0 | 1999-03-24 | 17:30 | 1.5 | 24 | 50 | 51 | 272 | 5.94 | 2.3 | 8.24 | 0.18779 | 0.72087 | 32.0097 | 13.5577 | 13.8003 | 0 | 0 | 0 | 0 | 50.5 | 0.27327 | 1999-03-26 | 9:00 | 1 | 24 | 50 | 51 | 272 | 5.81 | 3.42 |  | 9.23 | 0.18779 | 0.62947 | 28.4691 | 13.261 | 13.4983 | 442.1165 | 205.224 | 437.0564 | 2.3436 | 48.1564 | 0.2803 | 7.8 | 7.5 | 7.7 | 134 | 298 | 273 | 563.114 | -106.2689 | 54.2662 | 558.531 | 76.0085 | BMRL | 0.621 | 0.765 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 10:00 | 10:30 | --- | --- | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:15 | 16:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 18:00 | 18:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:45 | 13:45 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 65 | 110 | 61 | 45 | SDS-TOXp, ug Cl- /L | 65 | 110 | 61 | 45 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 298 | 292 | 295 | 2.0339 | 1999-03-25 | 7:00 | 15 | 24 | 51 | 52 | 272 | 6.16 | 0.51 | 6.67 | 0.18779 | 0.92354 | 39.7796 | 14.0599 | 14.3115 | 0 | 0 | 0 | 0 | 51.5 | 0.27789 | 1999-03-26 | 9:15 | 1.25 | 24 | 50 | 51 | 272 | 5.77 | 2.35 |  | 8.12 | 0.18779 | 0.71059 | 32.4975 | 13.1697 | 13.4054 | 473.1289 | 219.6373 | 467.7516 | 2.508 | 47.992 | 0.27933 | 7.7 | 7.5 | 7.6 | 161 | 299 | 320 | 617.1021 | -92.8444 | 45.0512 | 612.2644 | 73.7042 | BMRL | 0.626 | 0.873 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 26 | 50.5 | --- | --- | 26 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80.25 | 80.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 106 | 106 | --- | --- | --- | --- | --- | Cumulative time | hr | 125.75 | 125.75 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 16.045 | 16.045 | 16.045 | 16.045 | SDS-CDF, mg/L | 16.045 | 16.045 | 16.045 | 16.045 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 272 | 268 | 270 | 1.4815 | 1999-03-25 | 7:45 | 15.75 | 24 | 51 | 52 | 272 | 6.2 | 2.8 | 9 | 0.18779 | 0.68889 | 29.2222 | 14.1512 | 14.4044 | 0 | 0 | 0 | 0 | 51.5 | 0.2797 | 1999-03-26 | 9:45 | 1.75 | 24 | 50 | 51 | 272 | 5.6 | 1.7 |  | 7.3 | 0.18779 | 0.76712 | 36.2603 | 12.7817 | 13.0104 | 497.3565 | 230.9632 | 491.8719 | 2.6365 | 47.8635 | 0.27182 | 7.7 | 7.6 | 7.7 | 156 | 300 | 341 | 744.2941 | -118.2681 | 46.7577 | 738.2381 | 78.8686 | BMRL | 0.624 | 0.829 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.9 | 8 | 7.95 | 1.2579 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8.2 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 8 | 8 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.26 | 1.66 | 1.12 | 1.09 | SDS-CDp, mg/L | 2.26 | 1.66 | 1.12 | 1.09 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.267 | 0.248 | 0.2575 | 7.3786 | 1999-03-25 | 8:45 | 16.75 | 24 | 51 | 52 | 272 | 6.3 | 1.75 | 8.05 | 0.18779 | 0.78261 | 32.7888 | 14.3794 | 14.6367 | 0 | 0 | 0 | 0 | 51.5 | 0.28421 | 1999-03-26 | 10:30 | 2.5 | 24 | 50 | 51 | 272 | 5.5 | 2.08 |  | 7.58 | 0.18779 | 0.72559 | 34.8839 | 12.5535 | 12.7781 | 479.2073 | 222.5798 | 474.0181 | 2.5403 | 47.9597 | 0.26643 | 7.7 | 7.6 | 7.7 | 180 | 300 | 431 | 591.7981 | -37.3081 | 38.5666 | 587.6347 | 69.3687 | BMRL | 0.623 | 1.273 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 12.6 | 12.6 | 12.6 | 12.6 | TOCF, mg/L | 12.6 | 12.6 | 12.6 | 12.6 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.08 | BMRL | 0.08 | #VALUE! | 1999-03-25 | 9:30 | 17.5 | 24 | 51 | 52 | 272 | 6.3 | 2.7 | 9 | 0.18779 | 0.7 | 29.2222 | 14.3794 | 14.6367 | 0 | 0 | 0 | 0 | 51.5 | 0.28421 | 1999-03-26 | 11:15 | 3.25 | 24 | 50 | 51 | 272 | 5.53 | 2.04 |  | 7.57 | 0.18779 | 0.73052 | 34.9313 | 12.6219 | 12.8478 | 481.2981 | 223.5374 | 476.0576 | 2.5514 | 47.9486 | 0.26795 | 7.8 | 7.6 | 7.7 | 183 | 300 | 481 | 591.1863 | -22.9077 | 37.5427 | 587.0369 | 68.8265 | BMRL | 0.623 | 1.48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 152 | 158 | 155 | 3.871 | 435 | 822.3103 | -89.0368 | 55.4598 | 816.5692 | 81.0181 | Alkalinity | mg/L as CaCO3 | 292 | 534 | 842.4974 | -57.7711 | 16.092 | 838.416 | 65.1724 | Alkalinity | mg/L as CaCO3 | 144 | 360 | 561.9815 | -56.106 | 58.6207 | 558.2918 | 74.207 | Alkalinity | mg/L as CaCO3 | 136 | 356 | 445.1509 | -25.0424 | 60.9195 | 442.3905 | 69.2579 | TOCp, mg/L | 0.75 | 1.6 | 1 | 0.7 | TOCp, mg/L | 0.75 | 1.6 | 1 | 0.7 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 12.7 | 12.5 | 12.6 | 1.5873 | 1999-03-25 | 10:30 | 18.5 | 24 | 51 | 52 | 272 | 6.3 | 1.9 | 8.2 | 0.18779 | 0.76829 | 32.1707 | 14.3794 | 14.6367 | 0 | 0 | 0 | 0 | 51.5 | 0.28421 | 1999-03-26 | 14:15 | 6.25 | 24 | 50 | 51 | 272 | 5.07 | 0.65 |  | 5.72 | 0.18779 | 0.88636 | 46.5524 | 11.572 | 11.7791 | 557.3674 | 259.1067 | 551.8079 | 2.9548 | 47.5452 | 0.24774 | 7.8 | 7.6 |  | 191 | 301 |  | 1088.6 |  | 34.8123 | 1080.2345 | 82.3187 | BMRL | 0.623 | 1.852 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 201 | 206 | 203.5 | 2.457 | 420 | 512.9522 | -22.1315 | 30.5461 | 510.2899 | 60.1207 | Total dissolved solids | mg/L | 259 | 443 | 593.2306 | -33.9121 | 11.6041 | 590.7526 | 56.1576 | Total dissolved solids | mg/L | 198 | 375 | 392.6483 | -4.7062 | 32.4232 | 390.93 | 49.3515 | Total dissolved solids | mg/L | 184 | 339 | 342.9502 | -1.1653 | 37.2014 | 341.531 | 46.1249 | UV254 F, cm-1 | 0.588 | 0.588 | 0.588 | 0.588 | UV254 F, cm-1 | 0.588 | 0.588 | 0.588 | 0.588 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.587 | 0.589 | 0.588 | 0.34014 | 1999-03-25 | 11:00 | 19 | 24 | 51 | 52 | 272 | 6.3 | 1.36 | 7.66 | 0.18779 | 0.82245 | 34.5091 | 14.3794 | 14.6367 | 0 | 0 | 0 | 0 | 51.5 | 0.28421 | 1999-03-26 | 15:00 | 7 | 24 | 50 | 51 | 272 | 5.13 | 1.01 |  | 6.14 | 0.18779 | 0.8355 | 43.2997 | 11.709 | 11.9185 | 529.9766 | 246.3438 | 524.6272 | 2.8096 | 47.6904 | 0.24991 | 7.8 | 7.5 | 7.7 | 195 | 301 | 521 | 790.7624 | -51.7778 | 33.4471 | 785.1442 | 75.1638 | BMRL | 0.624 | 1.951 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 154 | 158 | 156 | 2.5641 | 508 | 636.6017 | -25.3153 | 47.1186 | 632.4669 | 75.3347 | Total hardness | mg/L as CaCO3 | 224 | 602 | 921.9521 | -53.1482 | 24.0678 | 916.7775 | 75.5666 | Total hardness | mg/L as CaCO3 | 140 | 378 | 457.584 | -21.054 | 52.5424 | 454.7806 | 69.2159 | Total hardness | mg/L as CaCO3 | 134 | 352 | 368.7797 | -4.767 | 54.5763 | 366.6834 | 63.4562 | UV254 p, cm-1 | 0.02 | 0.045 | 0.018 | 0.014 | UV254 p, cm-1 | 0.02 | 0.045 | 0.018 | 0.014 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.622 | 4.712 | 4.667 | 1.9274 | 1999-03-25 | 11:30 | 19.5 | 24 | 51 | 52 | 272 | 6.47 | 2.95 | 9.42 | 0.18779 | 0.68684 | 27.8747 | 14.7674 | 15.0317 | 0 | 0 | 0 | 0 | 51.5 | 0.29188 | 1999-03-26 | 16:30 | 8.5 | 24 | 49 | 50 | 272 | 5.23 | 1.97 |  | 7.2 | 0.18779 | 0.72639 | 36.7778 | 11.9372 | 12.1508 | 479.3977 | 222.789 | 474.4637 | 2.5414 | 46.9586 | 0.25876 | 7.6 | 7.7 | 7.5 | 198 | 300 | 507 | 545.2081 | -7.5361 | 32.4232 | 541.8701 | 63.4599 | BMRL | 0.623 | 1.891 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 124 | 128 | 126 | 3.1746 | 480 | 623.8895 | -29.977 | 53.3333 | 619.606 | 79.6645 | Calcium hardness | mg/L as CaCO3 | 196 | 566 | 923.443 | -63.1525 | 27.4074 | 918.0497 | 78.6504 | Calcium hardness | mg/L as CaCO3 | 116 | 334 | 431.5351 | -29.2021 | 57.037 | 428.7497 | 72.9446 | Calcium hardness | mg/L as CaCO3 | 102 | 318 | 346.9875 | -9.1156 | 62.2222 | 344.8001 | 70.4176 | BromideF, ug/L | 140 | 140 | 140 | 140 | BromideF, ug/L | 140 | 140 | 140 | 140 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 140 | 140 | 140 | 0 | 1999-03-25 | 12:30 | 20.5 | 24 | 51 | 52 | 272 | 6.6 | 2.56 | 9.16 | 0.18779 | 0.72052 | 28.6943 | 15.0641 | 15.3337 | 0 | 0 | 0 | 0 | 51.5 | 0.29774 | 1999-03-27 | 9:00 | 25 | 24 | 49 | 50 | 272 | 4.51 | 0.78 |  | 5.29 | 0.18779 | 0.85255 | 50.4178 | 10.2938 | 10.478 | 538.3818 | 250.5615 | 533.6094 | 2.8543 | 46.6457 | 0.22463 | 7.6 | 7.7 |  | 280 | 301 |  | 368.1667 |  | 4.4369 | 367.4357 | 23.7962 | 0.036 | 0.625 | 2.508 | 3.7797 | -50.7054 | 93.8776 | 3.7487 | 99.0397 | [8 empty] | Turbidity | ntu | 0.087 | 0.085 | 0.086 | 2.3256 | 0.319 | 0.67897 | -112.8441 | 66.6019 | 0.67387 | 87.2379 | Turbidity | ntu | 0.108 | 0.799 | 1.5776 | -97.4508 | 58.0583 | 1.5667 | 93.1067 | Turbidity | ntu | 0.078 | 0.295 | 0.44578 | -51.1128 | 69.7087 | 0.44254 | 82.3743 | Turbidity | ntu | 0.07 | 0.291 | 0.34342 | -18.015 | 72.8155 | 0.34098 | 79.4711 | Bromidep, ug/L | 100 | 130 | 96 | 83 | Bromidep, ug/L | 100 | 130 | 96 | 83 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 17.5 | 16.5 | 17 | 5.8824 | 1999-03-25 | 13:30 | 21.5 | 24 | 51 | 52 | 272 | 6.55 | 1.76 | 8.31 | 0.18779 | 0.78821 | 31.7316 | 14.95 | 15.2175 | 0 | 0 | 0 | 0 | 51.5 | 0.29549 | 1999-03-27 | 10:00 | 26 | 24 | 49 | 50 | 272 | 4.7 | 2.23 |  | 6.93 | 0.18779 | 0.67821 | 38.2496 | 10.7275 | 10.9195 | 459.7471 | 213.8838 | 455.4987 | 2.4374 | 47.0626 | 0.23202 | 7.6 | 7.7 | 7.7 | 226 | 301 | 631 | 434.2108 | 31.1869 | 22.8669 | 432.4119 | 47.735 | 0.023 | 0.624 | 2.466 | 1.7788 | 27.8667 | 96.0884 | 1.7636 | 98.6959 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 348 | 348 | 348 | 348 | AlkF, mg/L CaCO3 | 348 | 348 | 348 | 348
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.2 | 0.71 | 0.955 | 51.3089 | 1999-03-25 | 14:30 | 22.5 | 24 | 51 | 52 | 272 | 6.47 | 3.87 | 10.34 | 0.18779 | 0.62573 | 25.3056 | 14.7674 | 15.0317 | 0 | 0 | 0 | 0 | 51.5 | 0.29188 | 1999-03-27 | 11:00 | 27 | 24 | 49 | 50 | 272 | 4.71 | 1.72 |  | 6.43 | 0.18779 | 0.7325 | 41.3017 | 10.7503 | 10.9427 | 481.6978 | 224.0913 | 477.237 | 2.5538 | 46.9462 | 0.23309 | 7.6 | 7.7 | 7.8 | 213 | 301 | 532 | 512.0698 | 3.7463 | 27.3038 | 509.4804 | 58.1927 | 0.023 | 0.623 | 2.432 | 2.1352 | 12.2048 | 96.0884 | 2.1169 | 98.9135 | [8 empty] | Total organic carbon | mg/L | 0.8 | 0.7 | 0.75 | 13.3333 | 45.5 | 41.7222 | 8.3029 | 94.0476 | 41.3697 | 98.1871 | Total organic carbon | mg/L | 1.6 | 114.4 | 109.7334 | 4.0792 | 87.3016 | 108.9317 | 98.5312 | Total organic carbon | mg/L | 1 | 27.9 | 24.7676 | 11.2273 | 92.0635 | 24.5578 | 95.928 | Total organic carbon | mg/L | 0.7 | 17.9 | 18.0533 | -0.85631 | 94.4444 | 17.8983 | 96.089 | Alkp, mg/L CaCO3 | 155 | 292 | 144 | 136 | Alkp, mg/L CaCO3 | 155 | 292 | 144 | 136
Plant Name | Broward County District 1A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 16.3 | 15.79 | 16.045 | 3.1786 | 1999-03-25 | 15:30 | 23.5 | 24 | 51 | 52 | 272 | 6.67 | 3.17 | 9.84 | 0.18779 | 0.67785 | 26.6423 | 15.2239 | 15.4963 | 0 | 0 | 0 | 0 | 51.5 | 0.3009 | 1999-03-27 | 12:00 | 28 | 24 | 49 | 50 | 272 | 4.8 | 3.17 |  | 7.97 | 0.18779 | 0.60226 | 33.128 | 10.9557 | 11.1518 | 432.2372 | 201.0454 | 428.1574 | 2.2915 | 47.2085 | 0.23622 | 7.6 | 7.7 | 7.8 | 191 | 301 | 492 | 447.4479 | 9.0553 | 34.8123 | 445.1852 | 57.0965 | 0.021 | 0.623 | 2.002 | 1.4465 | 27.7448 | 96.4286 | 1.434 | 98.5355 | [8 empty] | UV254 | cm-1 | 0.019 | 0.021 | 0.02 | 10 | 1.727 | 1.9839 | -14.8754 | 96.5986 | 1.967 | 98.9832 | UV254 | cm-1 | 0.045 | 3.094 | 5.3829 | -73.9773 | 92.3469 | 5.3433 | 99.1578 | UV254 | cm-1 | 0.018 | 1.099 | 1.1859 | -7.9062 | 96.9388 | 1.1756 | 98.4688 | UV254 | cm-1 | 0.014 | 0.717 | 0.85104 | -18.6946 | 97.619 | 0.84357 | 98.3404 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295 | T-HdF, mg/L CaCO3 | 295 | 295 | 295 | 295
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | 1999-03-25 | 16:30 | 24.5 | 24 | 51 | 52 | 272 | 6.87 | 2.83 | 9.7 | 0.18779 | 0.70825 | 27.0412 | 15.6804 | 15.961 | 0 | 0 | 0 | 0 | 51.5 | 0.30992 | 1999-03-27 | 13:00 | 29 | 24 | 49 | 50 | 272 | 4.88 | 2.29 |  | 7.17 | 0.18779 | 0.68061 | 36.9358 | 11.1383 | 11.3376 | 460.7586 | 214.2772 | 456.3365 | 2.4427 | 47.0573 | 0.24093 | 7.6 | 7.7 | 7.8 | 185 | 300 | 465 | 523.1485 | -12.505 | 36.8601 | 520.1151 | 64.4309 | 0.019 | 0.623 | 1.692 | 1.8005 | -6.415 | 96.7687 | 1.7846 | 98.9353 | [8 empty] | SUVA | L/(mg*m) | 2.375 | 3 | 2.6875 | 23.2558 | 3.7956 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8125 | 2.7045 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8 | 3.9391 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 4.0056 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 156 | 224 | 140 | 134 | T-Hdp, mg/L CaCO3 | 156 | 224 | 140 | 134
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | 1999-03-25 | 17:30 | 25.5 | 24 | 50 | 51 | 272 | 6.51 | 2.78 | 9.29 | 0.18779 | 0.70075 | 28.2788 | 14.8587 | 15.1246 | 0 | 0 | 0 | 0 | 50.5 | 0.2995 | 1999-03-27 | 14:00 | 30 | 24 | 49 | 50 | 272 | 4.9 | 1.58 |  | 6.48 | 0.18779 | 0.75617 | 40.9753 | 11.184 | 11.3841 | 492.0454 | 228.818 | 487.3034 | 2.6086 | 46.8914 | 0.24278 | 7.6 | 7.6 | 7.8 | 271 | 300 | 487 | 361.2278 | 25.8259 | 7.5085 | 360.4151 | 24.8089 | 0.016 | 0.62 | 1.77 | 2.3619 | -33.442 | 97.2789 | 2.3408 | 99.3165 | [8 empty] | Bromide | mg/L | 100 | 100 | 100 | 0 | --- | 238.3026 | --- | 28.5714 | 237.1128 | 57.826 | Bromide | mg/L | 130 | --- | 228.3031 | --- | 7.1429 | 227.5743 | 42.8758 | Bromide | mg/L | 96 | --- | 186.1529 | --- | 31.4286 | 185.3571 | 48.2081 | Bromide | mg/L | 83 | --- | 166.1208 | --- | 40.7143 | 165.3786 | 49.8121 | Ca-HdF, mg/L CaCO3 | 270 | 270 | 270 | 270 | Ca-HdF, mg/L CaCO3 | 270 | 270 | 270 | 270
ICR Treatment Plant Identification Number | 294 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | 1999-03-25 | 18:00 | 26 | 24 | 50 | 51 | 272 | 6.8 | 2.77 | 9.57 | 0.18779 | 0.71055 | 27.4222 | 15.5206 | 15.7984 | 0 | 0 | 0 | 0 | 50.5 | 0.31284 | 1999-03-27 | 15:00 | 31 | 24 | 49 | 50 | 272 | 5.09 | 2.63 |  | 7.72 | 0.18779 | 0.65933 | 34.2332 | 11.6177 | 11.8255 | 452.743 | 210.4609 | 448.2091 | 2.4002 | 47.0998 | 0.25107 | 7.7 | 7.6 | 7.8 | 232 | 300 | 456 | 411.057 | 9.8559 | 20.8191 | 409.3817 | 43.3292 | 0.017 | 0.62 | 1.792 | 1.6931 | 5.5195 | 97.1088 | 1.6774 | 98.9865 | [8 empty] | SDS-Cl2 dose | mg/L | 3.5 | 2.75 | 3.125 | 24 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.75 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 126 | 196 | 116 | 102 | Ca-Hdp, mg/L CaCO3 | 126 | 196 | 116 | 102
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 1930 | 1400 | 1665 | 31.8318 | 1999-03-25 | 18:15 | 26.25 | 24 | 60 | 61 | 272 | 8.12 | 3.48 | 11.6 | 0.18779 | 0.7 | 22.4483 | 18.5335 | 18.8651 | 0 | 0 | 0 | 0 | 60.5 | 0.31182 | 1999-03-27 | 16:00 | 32 | 24 | 49 | 50 | 272 | 5.03 | 2.17 |  | 7.2 | 0.18779 | 0.69861 | 36.7778 | 11.4807 | 11.6861 | 467.9147 | 217.5398 | 463.2846 | 2.4806 | 47.0194 | 0.24854 | 7.7 | 7.6 | 7.8 | 237 | 301 | 469 | 422.8065 | 9.8494 | 19.1126 | 421.0884 | 43.7173 | 0.016 | 0.623 | 1.766 | 1.9139 | -8.3737 | 97.2789 | 1.8963 | 99.1563 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.76 | 0.97 | 0.865 | 24.2775 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.09 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.63 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.66 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 520 | 430 | 475 | 18.9474 | 1999-03-25 | 18:30 | 26.5 | 24 | 41 | 42 | 272 | 5.6 | 2.03 | 7.63 | 0.18779 | 0.73394 | 34.6488 | 12.7817 | 13.0104 | 0 | 0 | 0 | 0 | 41.5 | 0.3135 | 1999-03-27 | 17:00 | 33 | 24 | 49 | 50 | 272 | 4.84 | 1.8 |  | 6.64 | 0.18779 | 0.72892 | 39.9639 | 11.047 | 11.2447 | 480.2523 | 223.3607 | 475.6812 | 2.5461 | 46.9539 | 0.23948 | 7.7 | 7.6 | 7.7 | 209 | 300 | 499 | 518.8667 | -3.9813 | 28.6689 | 516.1098 | 59.5047 | 0.018 | 0.623 | 1.655 | 2.1207 | -28.137 | 96.9388 | 2.102 | 99.1437 | [8 empty] | SDS-Cl2 demand | mg/L | 2.74 | 1.78 | 2.26 | 42.4779 | --- | 49.9225 | --- | 85.9146 | 49.5125 | 95.4355 | SDS-Cl2 demand | mg/L | 1.66 | --- | 143.069 | --- | 89.6541 | 142.0206 | 98.8312 | SDS-Cl2 demand | mg/L | 1.12 | --- | 31.7003 | --- | 93.0196 | 31.4303 | 96.4366 | SDS-Cl2 demand | mg/L | 1.09 | --- | 22.8983 | --- | 93.2066 | 22.7035 | 95.199 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 61 | 57 | 59 | 6.7797 | 1999-03-25 | 19:00 | 27 | 24 | 50 | 51 | 272 | 6.8 | 2.38 | 9.18 | 0.18779 | 0.74074 | 28.6296 | 15.5206 | 15.7984 | 0 | 0 | 0 | 0 | 50.5 | 0.31284 | 1999-03-27 | 18:00 | 34 | 24 | 49 | 50 | 272 | 4.9 | 2.26 |  | 7.16 | 0.18779 | 0.68436 | 36.9888 | 11.184 | 11.3841 | 462.2237 | 214.9499 | 457.7691 | 2.4505 | 47.0495 | 0.24196 | 7.6 | 7.7 | 7.8 | 212 | 299 | 502 | 468.6195 | 6.6495 | 27.6451 | 466.308 | 54.5365 | 0.019 | 0.623 | 1.703 | 1.8217 | -6.9684 | 96.7687 | 1.8054 | 98.9476 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 93.2662 | 99.7227 | 93.856 | 92.3723 | Qp/QT (THM4), % | 100.4489 | 107.4027 | 101.0842 | 99.4862
State Approved Plant Capacity (MGD) | 16 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 5.6 | 5.3 | 5.45 | 5.5046 | 1999-03-26 | 8:00 | 40 | 24 | 50 | 51 | 272 | 6.3 | 2.15 | 8.45 | 0.18779 | 0.74556 | 31.1893 | 14.3794 | 14.6367 | 0 | 0 | 0 | 0 | 50.5 | 0.28984 | 1999-03-27 | 19:00 | 35 | 24 | 49 | 50 | 272 | 4.9 | 2.1 |  | 7 | 0.18779 | 0.7 | 37.8571 | 11.184 | 11.3841 | 468.4072 | 217.8255 | 463.8931 | 2.4832 | 47.0168 | 0.24213 | 7.7 | 7.6 | 7.8 | 208 | 300 | 513 | 491.3333 | 4.2235 | 29.0102 | 488.7812 | 57.4452 | 0.018 | 0.624 | 1.711 | 1.918 | -12.0982 | 96.9388 | 1.9009 | 99.0531 | [8 empty] | SDS-Chlorination pH | --- | 8.9 | 8.9 | 8.9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.9 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 20:00 | 36 | 24 | 49 | 50 | 272 | 4.8 | 1.5 |  | 6.3 | 0.18779 | 0.7619 | 42.1746 | 10.9557 | 11.1518 | 494.533 | 230.0209 | 489.8652 | 2.6218 | 46.8782 | 0.23789 | 7.7 | 7.5 | 7.7 | 226 | 300 | 527 | 507.4 | 3.7192 | 22.8669 | 504.9171 | 55.2402 | 0.018 | 0.621 | 1.766 | 2.412 | -36.5798 | 96.9388 | 2.3909 | 99.2471 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 14.2442 | 12.0314 | 15.1939 | 14.0719 | SDS-HAA5b, ug/L | NA | NA | NA | 5.0515
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 586.6 | 492.3 | 539.45 | 17.4808 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 21:00 | 37 | 24 | 49 | 50 | 272 | 4.8 | 2.32 |  | 7.12 | 0.18779 | 0.67416 | 37.2022 | 10.9557 | 11.1518 | 458.2336 | 213.1371 | 453.9084 | 2.4293 | 47.0707 | 0.23692 | 7.7 | 7.6 | 7.7 | 235 | 301 | 528 | 413 | 21.7803 | 19.7952 | 411.4294 | 42.8821 | 0.019 | 0.623 | 1.812 | 1.7652 | 2.5805 | 96.7687 | 1.7498 | 98.9142 | [8 empty] | SDS-TOX | mg Cl- /L | 62 | 68 | 65 | 9.2308 | --- | 5597.1058 | --- | 96.0961 | 5549.5115 | 98.8287 | SDS-TOX | mg Cl- /L | 110 | --- | 15396.1342 | --- | 93.3934 | 15282.8019 | 99.2802 | SDS-TOX | mg Cl- /L | 61 | --- | 3347.4821 | --- | 96.3363 | 3318.4712 | 98.1618 | SDS-TOX | mg Cl- /L | 45 | --- | 2407.3793 | --- | 97.2973 | 2386.2862 | 98.1142 | SDS-TOXb, ug Cl- /L | 172.7414 | 114.3125 | 159.5491 | 168.5688 | SDS-TOXb, ug Cl- /L | NA | NA | NA | 53.3233
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | NR | 11 | 11 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 10:00 | 50 | 24 | 49 | 50 | 272 | 4.18 | 0.5 |  | 4.68 | 0.18779 | 0.89316 | 57.1197 | 9.5406 | 9.7113 | 560.4576 | 261.0075 | 555.8558 | 2.9715 | 46.5285 | 0.20872 | 7.7 | 7.6 | 7.8 | 284 | 300 |  | 368.24 |  | 3.0717 | 367.5927 | 22.7406 | 0.022 | 0.624 | 2.549 | 5.3198 | -108.6999 | 96.2585 | 5.2791 | 99.5833 | [8 empty] | SDS-CHCl3 | mg/L | 3.6 | 4.9 | 4.25 | 30.5882 | --- | 1631.8992 | --- | 99.1053 | 1617.8961 | 99.7373 | SDS-CHCl3 | mg/L | 15 | --- | 4536.9432 | --- | 96.8421 | 4503.4173 | 99.6669 | SDS-CHCl3 | mg/L | 5.7 | --- | 967.2624 | --- | 98.8 | 958.7743 | 99.4055 | SDS-CHCl3 | mg/L | 4.9 | --- | 690.4275 | --- | 98.9684 | 684.3066 | 99.2839 | SDS-CDb, mg/L | 3.1883 | 1.6999 | 2.037 | 2.2307 | SDS-CDb, mg/L | NA | NA | NA | 1.1668
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | NR | 110 | 110 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 10:30 | 50.5 | 24 | 49 | 50 | 272 | 4.21 | 2.79 |  | 7 | 0.18779 | 0.60143 | 37.8571 | 9.6091 | 9.781 | 431.7443 | 201.0531 | 428.1737 | 2.2891 | 47.2109 | 0.20718 | 7.7 | 7.6 | 7.8 | 264 | 301 | 587 | 336.7599 | 42.6303 | 9.8976 | 336.1968 | 21.4746 | 0.021 | 0.624 | 2.501 | 1.4436 | 42.2799 | 96.4286 | 1.4326 | 98.5341 | [8 empty] | SDS-BDCM | mg/L | 7.4 | 9.5 | 8.45 | 24.8521 | --- | 183.23 | --- | 85.678 | 181.7263 | 95.3501 | SDS-BDCM | mg/L | 21 | --- | 394.5518 | --- | 64.4068 | 391.7823 | 94.6399 | SDS-BDCM | mg/L | 10 | --- | 110.3975 | --- | 83.0508 | 109.5113 | 90.8685 | SDS-BDCM | mg/L | 7.7 | --- | 82.5087 | --- | 86.9492 | 81.8407 | 90.5915 | TOCb, mg/L | 1.548 | 1.6305 | 1.7127 | 1.6077 | TOCb, mg/L | NA | NA | NA | 0.76114
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | NR | 140 | 140 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 12:00 | 52 | 24 | 49 | 50 | 272 | 4.32 | 2.21 |  | 6.53 | 0.18779 | 0.66156 | 40.6539 | 9.8602 | 10.0366 | 453.2488 | 211.0209 | 449.4016 | 2.403 | 47.097 | 0.21311 | 7.8 | 7.5 | 7.8 | 235 | 300 | 466 | 406.3756 | 12.7949 | 19.7952 | 405.0146 | 41.9774 | 0.018 | 0.623 | 2.531 | 1.7022 | 32.7456 | 96.9388 | 1.6888 | 98.9342 | [8 empty] | SDS-DBCM | mg/L | 15 | 16 | 15.5 | 6.4516 | --- | -19.2485 | --- | -184.4037 | -18.9496 | 181.796 | SDS-DBCM | mg/L | 26 | --- | -176.0129 | --- | -377.0642 | -174.5152 | 114.8984 | SDS-DBCM | mg/L | 17 | --- | -6.6651 | --- | -211.9266 | -6.4562 | 363.3116 | SDS-DBCM | mg/L | 13 | --- | 1.9901 | --- | -138.5321 | 2.0885 | -522.4712 | UV254 b, cm-1 | 0.058248 | 0.046506 | 0.053021 | 0.057783 | UV254 b, cm-1 | NA | NA | NA | 0.016949
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 13:00 | 53 | 24 | 49 | 50 | 272 | 4.6 | 2.5 |  | 7.1 | 0.18779 | 0.64789 | 37.3099 | 10.4993 | 10.6871 | 448.2977 | 208.5991 | 444.244 | 2.3767 | 47.1233 | 0.22679 | 7.7 | 7.5 | 7.8 | 232 | 300 | 487 | 405.24 | 16.7885 | 20.8191 | 403.7751 | 42.5423 | 0.018 | 0.622 | 1.836 | 1.6368 | 10.8497 | 96.9388 | 1.6231 | 98.891 | [8 empty] | SDS-CHBr3 | mg/L | 11 | 9.1 | 10.05 | 18.9055 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 8.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 8.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 7.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 102.6935 | 130.0277 | 98.7033 | 87.3478 | Bromideb, ug/L | NA | NA | NA | 83.2929
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | NR | 1.4 | 1.4 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 14:00 | 54 | 24 | 49 | 50 | 272 | 4.62 | 1.98 |  | 6.6 | 0.18779 | 0.7 | 40.2121 | 10.5449 | 10.7336 | 468.2706 | 217.884 | 464.0177 | 2.4826 | 47.0174 | 0.22829 | 7.7 | 7.5 | 7.8 | 210 | 300 | 458 | 486.6667 | -6.2591 | 28.3276 | 484.317 | 56.64 | 0.017 | 0.623 | 1.773 | 1.9203 | -8.3098 | 97.1088 | 1.9042 | 99.1072 | [8 empty] | SDS-THM4 | mg/L | 37 | 39.5 | 38.25 | 6.5359 | --- | 1771.1821 | --- | 92.9094 | 1756.2732 | 97.8221 | SDS-THM4 | mg/L | 70.7 | --- | 4678.6585 | --- | 86.8941 | 4644.4948 | 98.4778 | SDS-THM4 | mg/L | 41.4 | --- | 1061.8691 | --- | 92.3255 | 1052.8611 | 96.0679 | SDS-THM4 | mg/L | 33.4 | --- | 771.3519 | --- | 93.8085 | 764.7629 | 95.6326 | Alkb, mg/L CaCO3 | 167.9963 | 292.1553 | 156.5337 | 152.1707 | Alkb, mg/L CaCO3 | NA | NA | NA | 137.0892
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | NR | 16 | 16 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 20:00 | 60 | 24 | 49 | 50 | 272 | 4.35 | 1.06 |  | 5.41 | 0.18779 | 0.80407 | 49.2773 | 9.9286 | 10.1063 | 513.7975 | 239.1965 | 509.4059 | 2.7241 | 46.7759 | 0.21606 | 7.8 | 7.5 | 7.8 | 216 | 301 | 504 | 608.9906 | -20.8315 | 26.2799 | 605.8481 | 64.3475 | 0.017 | 0.623 | 1.95 | 2.9313 | -50.3208 | 97.1088 | 2.908 | 99.4154 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 165.36 | 224.1969 | 149.5231 | 146.2806 | T-Hdb, mg/L CaCO3 | NA | NA | NA | 134.8272
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 21:00 | 61 | 24 | 50 | 50 | 272 | 4.58 | 2.53 |  | 7.11 | 0.18779 | 0.64416 | 37.256 | 10.4536 | 10.6407 | 446.9279 | 207.97 | 442.9042 | 2.3695 | 47.6305 | 0.2234 | 7.8 | 7.5 | 7.8 | 198 | 301 | 464 | 464.9763 | -0.21041 | 32.4232 | 462.7286 | 57.2103 | 0.018 | 0.624 | 1.637 | 1.6199 | 1.0472 | 96.9388 | 1.6064 | 98.8795 | [8 empty] | SDS-DCAA* | mg/L | 1.1 | 2.5 | 1.8 | 77.7778 | --- | 375.9087 | --- | 98.3636 | 372.6901 | 99.517 | SDS-DCAA* | mg/L | 4 | --- | 1046.013 | --- | 96.3636 | 1038.2875 | 99.6148 | SDS-DCAA* | mg/L | 2.4 | --- | 222.8648 | --- | 97.8182 | 220.9186 | 98.9136 | SDS-DCAA* | mg/L | 1.2 | --- | 159.8586 | --- | 98.9091 | 158.4419 | 99.2426 | Ca-Hdb, mg/L CaCO3 | 135.6967 | 196.2052 | 125.4617 | 114.8145 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | 102.8632
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | NR | 2.6 | 2.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 22:00 | 62 | 24 | 50 | 50 | 272 | 4.68 | 2.18 |  | 6.86 | 0.18779 | 0.68222 | 38.6501 | 10.6818 | 10.873 | 461.2882 | 214.6094 | 457.0438 | 2.4456 | 47.5544 | 0.22864 | 7.7 | 7.5 | 7.8 | 198 | 300 | 455 | 496.945 | -9.2187 | 32.4232 | 494.3731 | 59.9493 | 0.017 | 0.624 | 1.565 | 1.8138 | -15.8988 | 97.1088 | 1.7984 | 99.0547 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.9 | --- | 1359.466 | --- | 98.6429 | 1349.4009 | 99.8592 | SDS-TCAA* | mg/L | 1.4 | --- | 285.3816 | --- | 99 | 282.8748 | 99.5051 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | NR | 19 | 19 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-28 | 23:00 | 63 | 24 | 50 | 50 | 272 | 4.61 | 2.06 |  | 6.67 | 0.18779 | 0.69115 | 39.7796 | 10.5221 | 10.7104 | 464.7527 | 216.2515 | 460.541 | 2.464 | 47.536 | 0.22531 | 7.7 | 7.6 | 7.8 | 209 | 301 | 450 | 480.9806 | -6.8846 | 28.6689 | 478.6757 | 56.3379 | 0.019 | 0.622 | 1.588 | 1.8613 | -17.2131 | 96.7687 | 1.8457 | 98.9706 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 0 | 262.4 | 131.2 | 200 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-29 | 9:00 | 73 | 24 | 50 | 50 | 272 | 4 | 0.48 |  | 4.48 | 0.18779 | 0.89286 | 59.7143 | 9.1298 | 9.2931 | 560.123 | 260.9452 | 555.7233 | 2.9698 | 47.0302 | 0.1976 | 7.9 | 7.5 |  | 240 | 293 |  | 734.6667 |  | 18.0887 | 731.0294 | 67.1696 | 0.021 | 0.6 | 3.055 | 5.313 | -73.9116 | 96.4286 | 5.2741 | 99.6018 | [8 empty] | SDS-DBAA* | mg/L | 3.9 | 4.1 | 4 | 5 | --- | -4.9897 | --- | -185.7143 | -4.9123 | 181.4277 | SDS-DBAA* | mg/L | 5.8 | --- | -37.4534 | --- | -314.2857 | -37.1327 | 115.6197 | SDS-DBAA* | mg/L | 3.8 | --- | -1.1174 | --- | -171.4286 | -1.074 | 453.8103 | SDS-DBAA* | mg/L | 3.2 | --- | 0.57513 | --- | -128.5714 | 0.59857 | -434.6067 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 0 | 278.4 | 139.2 | 200 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-29 | 10:00 | 74 | 24 | 50 | 50 | 272 | 4.1 | 1.16 |  | 5.26 | 0.18779 | 0.77947 | 50.711 | 9.358 | 9.5255 | 502.0634 | 233.8503 | 498.0205 | 2.6619 | 47.3381 | 0.20122 | 7.8 | 7.5 | 7.8 | 236 | 296 | 551 | 494.4655 | 10.2603 | 19.4539 | 492.5175 | 52.0829 | 0.023 | 0.617 | 3.168 | 2.585 | 18.4033 | 96.0884 | 2.5657 | 99.1035 | [8 empty] | SDS-BCAA* | mg/L | 1.9 | 2.5 | 2.2 | 27.2727 | --- | 49.9144 | --- | 86.25 | 49.5039 | 95.5559 | SDS-BCAA* | mg/L | 5.2 | --- | 111.3674 | --- | 67.5 | 110.5802 | 95.2975 | SDS-BCAA* | mg/L | 2.7 | --- | 29.9508 | --- | 83.125 | 29.7102 | 90.9122 | SDS-BCAA* | mg/L | 1.9 | --- | 22.4614 | --- | 88.125 | 22.2779 | 91.4714 | Qp/QT (HAA5), % | 61.563 | 64.6025 | 62.4595 | 60.8833 | Qp/QT (HAA5), % | 83.0941 | 87.1967 | 84.3042 | 82.1767
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-29 | 11:00 | 75 | 24 | 50 | 50 | 272 | 4.37 | 1.84 |  | 6.21 | 0.18779 | 0.7037 | 42.8003 | 9.9743 | 10.1528 | 469.6342 | 218.6277 | 465.6015 | 2.4899 | 47.5101 | 0.2137 | 7.8 | 7.5 | 7.8 | 224 | 298 |  | 456.875 |  | 23.5495 | 455.0043 | 50.7697 | 0.037 | 0.62 | 2.081 | 1.8966 | 8.8599 | 93.7075 | 1.8817 | 98.0337 | [8 empty] | SDS-TBAA | mg/L | NR | NR | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 230.8963 | 236.6257 | 228.3702 | 231.3502 | SDS-THM4b, ug/L | 122.9824 | 130.7157 | 119.5729 | 123.595
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-29 | 12:00 | 76 | 24 | 50 | 50 | 272 | 4.4 | 1.15 |  | 5.55 | 0.18779 | 0.79279 | 48.009 | 10.0428 | 10.2225 | 508.4581 | 236.6871 | 504.0618 | 2.6957 | 47.3043 | 0.2161 | 7.8 | 7.6 | 7.8 | 211 | 296 |  | 606.7391 |  | 27.9863 | 603.5383 | 65.0395 | 0.025 | 0.621 | 1.927 | 2.7421 | -42.2982 | 95.7483 | 2.7201 | 99.0809 | [8 empty] | SDS-CDBAA | mg/L | 2 | 2.7 | 2.35 | 29.7872 | --- | 3.2144 | --- | 9.6154 | 3.207 | 26.7218 | SDS-CDBAA | mg/L | 4.3 | --- | -12.4115 | --- | -65.3846 | -12.2876 | 134.9945 | SDS-CDBAA | mg/L | 2.6 | --- | 2.6 | --- | 0 | 2.6 | 0 | SDS-CDBAA | mg/L | 2.2 | --- | 2.7833 | --- | 15.3846 | 2.7781 | 20.8091 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-29 | 13:30 | 77.5 | 24 | 49 | 50 | 272 | 4.36 | 0.82 |  | 5.18 | 0.18779 | 0.8417 | 51.5097 | 9.9515 | 10.1295 | 532.5888 | 247.9397 | 528.026 | 2.8237 | 46.6763 | 0.21702 | 7.8 | 7.6 | 7.8 | 232 | 298 |  | 617.3415 |  | 20.8191 | 614.2531 | 62.2306 | 0.027 | 0.621 | 2.131 | 3.5709 | -67.5682 | 95.4082 | 3.5425 | 99.2378 | [8 empty] | SDS-DCBAA | mg/L | 1.4 | 1.8 | 1.6 | 25 | --- | 61.7617 | --- | 91.5789 | 61.2441 | 97.3875 | SDS-DCBAA | mg/L | 3.7 | --- | 154.1038 | --- | 80.5263 | 152.9887 | 97.5815 | SDS-DCBAA | mg/L | 1.8 | --- | 37.0416 | --- | 90.5263 | 36.7305 | 95.0994 | SDS-DCBAA | mg/L | 1.3 | --- | 27.1112 | --- | 93.1579 | 26.8807 | 95.1638 | SDS-TOXb, ug Cl- /L | 679.992 | 660.431 | 663.1489 | 678.6909 | SDS-TOXb, ug Cl- /L | 335.4944 | 309.0921 | 312.7605 | 333.7382
[44 empty] | 1999-03-29 | 14:15 | 78.25 | 24 | 49 | 50 | 272 | 4.25 | 0.75 |  | 5 | 0.18779 | 0.85 | 53.4 | 9.7004 | 9.874 | 536.8333 | 249.9706 | 532.3511 | 2.8462 | 46.6538 | 0.21164 | 7.7 | 7.4 | 7.8 | 234 | 300 | 444 | 627.3333 | -41.2913 | 20.1365 | 624.2604 | 62.5156 | 0.023 | 0.623 | 2.173 | 3.7897 | -74.3979 | 96.0884 | 3.7602 | 99.3883 | [8 empty] | SDS-HAA5 | mg/L | 5 | 6.6 | 5.8 | 27.5862 | --- | 439.3788 | --- | 95.5793 | 435.6486 | 98.6687 | SDS-HAA5 | mg/L | 11.7 | --- | 1186.4222 | --- | 91.0823 | 1177.7128 | 99.0065 | SDS-HAA5 | mg/L | 7.6 | --- | 260.8476 | --- | 94.2073 | 258.6121 | 97.0612 | SDS-HAA5 | mg/L | 4.4 | --- | 189.3072 | --- | 96.6463 | 187.6562 | 97.6553 | SDS-CDb, mg/L | 7.5585 | 6.7519 | 6.7229 | 6.9399 | SDS-CDb, mg/L | 4.5905 | 3.5018 | 3.4626 | 3.7555
[44 empty] | 1999-03-29 | 15:00 | 79 | 24 | 49 | 50 | 272 | 4.31 | 0.63 |  | 4.94 | 0.18779 | 0.87247 | 54.0607 | 9.8373 | 10.0134 | 548.9588 | 255.5861 | 544.3101 | 2.9105 | 46.5895 | 0.21493 | 7.7 | 7.5 | 7.8 | 236 | 298 | 462 | 682.9524 | -47.8252 | 19.4539 | 679.4113 | 65.264 | 0.024 | 0.621 | 2.211 | 4.4465 | -101.107 | 95.9184 | 4.4114 | 99.456 | [8 empty] | SDS-HAA6 | mg/L | 6.9 | 9.1 | 8 | 27.5 | --- | 461.6327 | --- | 94.2529 | 457.7299 | 98.2522 | SDS-HAA6 | mg/L | 16.9 | --- | 1219.1471 | --- | 87.8592 | 1210.2336 | 98.6036 | SDS-HAA6 | mg/L | 10.3 | --- | 274.4069 | --- | 92.6006 | 272.0756 | 96.2143 | SDS-HAA6 | mg/L | 6.3 | --- | 200.1026 | --- | 95.4741 | 198.3722 | 96.8242 | TOCb, mg/L | 5.3048 | 5.4937 | 5.3547 | 5.3549 | TOCb, mg/L | 2.7533 | 3.0084 | 2.8207 | 2.821
[44 empty] | 1999-03-29 | 15:45 | 79.75 | 24 | 49 | 50 | 272 | 4.28 | 0.59 |  | 4.87 | 0.18779 | 0.87885 | 54.8522 | 9.7689 | 9.9437 | 552.4629 | 257.2329 | 547.8173 | 2.9291 | 46.5709 | 0.21352 | 7.7 | 7.6 | 7.8 | 241 | 298 | 529 | 670.2203 | -26.6957 | 17.7474 | 666.8434 | 63.8596 | 0.025 | 0.621 | 2.65 | 4.6721 | -76.307 | 95.7483 | 4.6356 | 99.4607 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.23832 | 0.23721 | 0.23198 | 0.23853 | UV254 b, cm-1 | 0.11603 | 0.11452 | 0.10747 | 0.11631
[44 empty] | 1999-03-29 | 16:15 | 80.25 | 24 | 49 | 50 | 272 | 4.22 | 0.58 |  | 4.8 | 0.18779 | 0.87917 | 55.6667 | 9.6319 | 9.8043 | 552.588 | 257.322 | 548.0071 | 2.9298 | 46.5702 | 0.21053 | 7.7 | 7.6 | 7.8 | 258 | 296 | 546 | 547.6552 | -0.30315 | 11.9454 | 545.4082 | 52.696 | 0.026 | 0.622 | 2.377 | 4.677 | -96.7621 | 95.5782 | 4.641 | 99.4398 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 115.3748 | 133.5397 | 112.5178 | 105.2965 | Bromideb, ug/L | 106.7624 | 131.2803 | 102.9061 | 93.1593
[44 empty] | 1999-03-29 | 17:00 | 81 | 24 | 49 | 50 | 272 | 4.25 | 0.53 |  | 4.78 | 0.18779 | 0.88912 | 55.9038 | 9.7004 | 9.874 | 558.214 | 259.9263 | 553.5532 | 2.9596 | 46.5404 | 0.21216 | 7.8 | 7.6 | 7.8 | 269 | 299 | 529 | 485.4528 | 8.232 | 8.1911 | 483.7618 | 44.3941 | 0.028 | 0.622 | 2.483 | 5.0786 | -104.5335 | 95.2381 | 5.0391 | 99.4443 | [47 empty] | Alkb, mg/L CaCO3 | 229.1834 | 311.8226 | 220.5825 | 218.9274 | Alkb, mg/L CaCO3 | 187.6284 | 299.1699 | 176.0194 | 173.7855
[44 empty] | 1999-03-29 | 17:45 | 81.75 | 24 | 49 | 50 | 272 | 4.18 | 0.5 |  | 4.68 | 0.18779 | 0.89316 | 57.1197 | 9.5406 | 9.7113 | 560.4576 | 261.0075 | 555.8558 | 2.9715 | 46.5285 | 0.20872 | 7.8 | 7.6 | 7.8 | 249 | 298 | 551 | 660.84 | -19.9347 | 15.0171 | 657.6755 | 62.1394 | 0.031 | 0.623 | 2.991 | 5.2445 | -75.3434 | 94.7279 | 5.2045 | 99.4044 | [47 empty] | T-Hdb, mg/L CaCO3 | 209.4274 | 249.1322 | 198.1877 | 196.9779 | T-Hdb, mg/L CaCO3 | 179.4992 | 233.0904 | 164.3285 | 162.6956
[44 empty] | 1999-03-29 | 18:30 | 82.5 | 24 | 49 | 50 | 272 | 4.22 | 0.4 |  | 4.62 | 0.18779 | 0.91342 | 57.8745 | 9.6319 | 9.8043 | 572.3443 | 266.5219 | 567.5996 | 3.0345 | 46.4655 | 0.211 | 7.8 | 7.6 | 7.8 | 256 | 299 | 561 | 683.35 | -21.8093 | 12.628 | 680.0349 | 62.3549 | 0.031 | 0.623 | 3.054 | 6.4643 | -111.6683 | 94.7279 | 6.4144 | 99.5167 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 181.3493 | 222.1941 | 173.8123 | 167.7161 | Ca-Hdb, mg/L CaCO3 | 150.3445 | 205.4745 | 140.1715 | 131.9432
[44 empty] | 1999-03-30 | 9:00 | 97 | 24 | 49 | 50 | 272 | 3.57 | 0.06 |  | 3.63 | 0.18779 | 0.98347 | 73.9311 | 8.1483 | 8.2941 | 616.7223 | 287.5593 | 612.402 | 3.27 | 46.23 | 0.17941 | 7.8 | 7.6 |  | 286 | 299 |  | 709.5 |  | 2.3891 | 706.7208 | 59.5314 | 0.034 | 0.623 | 3.178 | 33.551 | -955.7269 | 94.2177 | 33.331 | 99.898 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-03-30 | 11:00 | 99 | 24 | 49 | 50 | 272 | 3.96 | 0.89 |  | 4.85 | 0.18779 | 0.81649 | 55.0825 | 9.0385 | 9.2002 | 519.58 | 242.0767 | 515.5399 | 2.7548 | 46.7452 | 0.19682 | 7.8 | 7.6 | 7.9 | 262 | 298 | 545 | 430.9326 | 20.9298 | 10.5802 | 429.7029 | 39.0276 | 0.032 | 0.622 | 3.265 | 3.0619 | 6.2209 | 94.5578 | 3.0398 | 98.9473 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-03-30 | 13:15 | 101.25 | 24 | 49 | 50 | 272 | 3.84 | 0.34 |  | 4.18 | 0.18779 | 0.91866 | 64.0718 | 8.7646 | 8.9214 | 575.1259 | 268.0201 | 570.7903 | 3.0494 | 46.4506 | 0.19206 | 7.8 | 7.6 |  | 263 | 299 |  | 631.8235 |  | 10.2389 | 629.2201 | 58.2022 | 0.031 | 0.622 | 3.158 | 6.8788 | -117.8222 | 94.7279 | 6.8305 | 99.5462 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-03-30 | 15:15 | 103.25 | 24 | 49 | 50 | 272 | 3.91 | 0.47 |  | 4.38 | 0.18779 | 0.89269 | 61.1005 | 8.9244 | 9.0841 | 559.9499 | 260.9114 | 555.6512 | 2.9689 | 46.5311 | 0.19523 | 7.8 | 7.6 |  | 265 | 296 |  | 525.9362 |  | 9.5563 | 524.0607 | 49.4333 | 0.034 | 0.623 | 3.208 | 5.1968 | -61.9953 | 94.2177 | 5.1597 | 99.341 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-03-30 | 15:45 | 103.75 | 24 | 49 | 50 | 272 | 4.17 | 2.56 |  | 6.73 | 0.18779 | 0.61961 | 39.416 | 9.5178 | 9.6881 | 438.0007 | 203.9828 | 434.413 | 2.3222 | #VALUE! | #VALUE! | 7.8 | 7.6 | 7.8 | 239 | 299 | 445 | 380.9609 | 14.3908 | 18.43 | 379.8727 | 37.0842 | 0.033 | 0.622 | 3.154 | 1.492 | 52.6936 | 94.3878 | 1.4809 | 97.7716 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-03-30 | 16:00 | 104 | 24 | 49 | 50 | 272 | 4.45 | 6.2 |  | 10.65 | 0.18779 | 0.41784 | 24.5399 | 10.1569 | 10.3386 | 377.2639 | 175.5987 | 373.9646 | 2.0002 | 47.4998 | 0.21766 | 7.8 | 7.6 | 7.8 | 229 | 298 | 418 | 338.9355 | 18.915 | 21.843 | 338.0362 | 32.2558 | 0.031 | 0.623 | 2.89 | 0.98778 | 65.8207 | 94.7279 | 0.97996 | 96.8366 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-03-30 | 16:45 | 104.75 | 24 | 49 | 50 | 272 | 4.51 | 5.65 |  | 10.16 | 0.0031759 | 0.4439 | -0.54724 | 10.2938 | 10.478 | 519.8173 | 8.8498 | 18.847 | 2.6048 | 46.8952 | 0.22344 | 7.8 | 7.6 | 7.7 | 212 | 297 | 370 | 357.6566 | 3.336 | 27.6451 | 286.2532 | 25.9397 | 0.03 | 0.623 | 1.565 | 1.0334 | 33.9673 | 94.898 | 0.54152 | 94.4601 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-03-30 | 17:15 | 105.25 | 24 | 49 | 50 | 272 | 4.6 | 5.55 |  | 10.15 | 0.18779 | 0.4532 | 25.798 | 10.4993 | 10.6871 | 386.7072 | 179.9402 | 383.2104 | 2.0502 | 47.4498 | 0.22523 | 7.7 | 7.6 | 7.8 | 208 | 296 | 362 | 363.4505 | -0.40068 | 29.0102 | 362.136 | 42.563 | 0.029 | 0.623 | 1.406 | 1.0513 | 25.2265 | 95.068 | 1.0427 | 97.2187 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-03-30 | 18:00 | 106 | 24 | 49 | 50 | 272 | 4.8 | 4.85 |  | 9.65 | 0.18779 | 0.49741 | 27.1865 | 10.9557 | 11.1518 | 399.2101 | 185.6836 | 395.4419 | 2.1164 | 47.3836 | 0.23535 | 7.7 | 7.5 | 7.7 | 202 | 296 | 335 | 383.0619 | -14.3468 | 31.058 | 381.4643 | 47.0462 | 0.029 | 0.623 | 1.267 | 1.1412 | 9.926 | 95.068 | 1.1314 | 97.4369 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-03-30 | 19:00 | 107 | 24 | 49 | 50 | 272 | 4.721 | 5.24 |  | 9.961 | 0.18779 | 0.47395 | 26.3065 | 10.7754 | 10.9682 | 392.481 | 182.5826 | 388.8379 | 2.0808 | 47.4192 | 0.2313 | 7.7 | 7.5 | 7.8 | 212 | 299 | 369 | 365.9773 | 0.81916 | 27.6451 | 364.641 | 41.8606 | 0.028 | 0.623 | 1.109 | 1.0925 | 1.4847 | 95.2381 | 1.0833 | 97.4153 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-03-30 | 20:00 | 108 | 24 | 49 | 50 | 272 | 4.68 | 5.08 |  | 9.76 | 0.18779 | 0.47951 | 26.8689 | 10.6818 | 10.873 | 394.0408 | 183.3232 | 390.4152 | 2.089 | 47.411 | 0.22933 | 7.7 | 7.5 | 7.8 | 208 | 296 | 348 | 371.3071 | -6.6974 | 29.0102 | 369.9022 | 43.7689 | 0.027 | 0.623 | 1.007 | 1.1048 | -9.7147 | 95.4082 | 1.0956 | 97.5355 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-03-30 | 21:00 | 109 | 24 | 49 | 50 | 272 | 4.76 | 5.2 |  | 9.96 | 0.18779 | 0.47791 | 26.3092 | 10.8644 | 11.0588 | 393.6077 | 183.0924 | 389.9237 | 2.0867 | 47.4133 | 0.23324 | 7.7 | 7.6 | 7.7 | 212 | 297 | 379 | 367.1462 | 3.1277 | 27.6451 | 365.7886 | 42.043 | 0.027 | 0.623 | 1.181 | 1.1015 | 6.729 | 95.4082 | 1.0921 | 97.5278 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-03-31 | 9:00 | 121 | 24 | 49 | 50 | 272 | 4.62 | 2.84 |  | 7.46 | 0.18779 | 0.6193 | 35.4611 | 10.5449 | 10.7336 | 438.0616 | 203.8279 | 434.0831 | 2.3224 | 47.1776 | 0.22751 | 7.7 | 7.5 | 7.7 | 222 | 297 | 421 | 408.5 | 2.9691 | 24.2321 | 406.9161 | 45.4433 | 0.018 | 0.621 | 1.391 | 1.5153 | -8.9327 | 96.9388 | 1.5025 | 98.802
[44 empty] | 1999-03-31 | 9:30 | 121.5 | 24 | 49 | 50 | 272 | 4.85 | 5.5 |  | 10.35 | 0.18779 | 0.4686 | 25.2802 | 11.0699 | 11.2679 | 391.0121 | 181.8523 | 387.2826 | 2.073 | 47.427 | 0.23758 | 7.7 | 7.5 | 7.7 | 208 | 297 | 380 | 367.9545 | 3.1699 | 29.0102 | 366.5285 | 43.2513 | 0.019 | 0.622 | 1.193 | 1.0898 | 8.6543 | 96.7687 | 1.0802 | 98.2411
[44 empty] | 1999-03-31 | 10:30 | 122.5 | 24 | 49 | 50 | 272 | 4.83 | 3.69 |  | 8.52 | 0.18779 | 0.5669 | 30.9249 | 11.0242 | 11.2215 | 420.5153 | 195.5815 | 416.5211 | 2.2294 | 47.2706 | 0.23739 | 7.7 | 7.5 | 7.8 | 210 | 297 | 394 | 401.6423 | -1.9397 | 28.3276 | 399.9407 | 47.4922 | 0.019 | 0.622 | 1.193 | 1.3328 | -11.7174 | 96.7687 | 1.3211 | 98.5618
[44 empty] | 1999-03-31 | 10:45 | 122.75 | 24 | 49 | 50 | 281 | 5 | 12.3 |  | 17.3 | 0.19401 | 0.28902 | 15.2428 | 11.4122 | 11.6164 | 346.5807 | 161.1914 | 343.282 | 1.8374 | 47.6626 | 0.24372 | 7.7 | 7.5 | 7.8 | 188 | 300 | 349 | 335.6829 | 3.8158 | 35.8362 | 334.369 | 43.7747 | 0.014 | 0.623 | 0.951 | 0.82133 | 13.6348 | 97.619 | 0.81415 | 98.2804
[44 empty] | 1999-03-31 | 11:15 | 123.25 | 24 | 49 | 50 | 281 | 5 | 11.8 |  | 16.8 | 0.19401 | 0.29762 | 15.7262 | 11.4122 | 11.6164 | 348.4773 | 162.0735 | 345.1605 | 1.8475 | 47.6525 | 0.24377 | 7.8 | 7.6 | 7.7 | 161 | 298 | 332 | 348.9322 | -5.1001 | 45.0512 | 347.2602 | 53.6371 | 0.014 | 0.623 | 0.847 | 0.83122 | 1.863 | 97.619 | 0.82395 | 98.3009
[44 empty] | 1999-03-31 | 11:45 | 123.75 | 24 | 49 | 50 | 281 | 4.99 | 11.9 |  | 16.89 | 0.19401 | 0.29544 | 15.6371 | 11.3894 | 11.5932 | 347.9941 | 161.8518 | 344.6885 | 1.8449 | 47.6551 | 0.24327 | 7.8 | 7.6 | 7.7 | 176 | 298 | 323 | 342.0613 | -5.9013 | 39.9317 | 340.5869 | 48.3245 | 0.014 | 0.621 | 0.841 | 0.82869 | 1.4632 | 97.619 | 0.82146 | 98.2957
[44 empty] | 1999-03-31 | 13:00 | 125 | 24 | 49 | 50 | 281 | 4.95 | 11.8 |  | 16.75 | 0.19401 | 0.29552 | 15.7761 | 11.2981 | 11.5003 | 348.0076 | 161.8707 | 344.7287 | 1.845 | 47.655 | 0.24132 | 7.8 | 7.6 | 7.7 | 189 | 296 | 340 | 336.6271 | 0.99202 | 35.4949 | 335.3268 | 43.6371 | 0.012 | 0.621 | 0.826 | 0.82963 | -0.43912 | 97.9592 | 0.82243 | 98.5409
[44 empty] | 1999-03-31 | 13:45 | 125.75 | 24 | 49 | 50 | 281 | 5 | 11.7 |  | 16.7 | 0.19401 | 0.2994 | 15.8263 | 11.4122 | 11.6164 | 348.8729 | 162.2574 | 345.5523 | 1.8496 | 47.6504 | 0.24378 | 7.7 | 7.5 | 7.7 | 187 | 296 | 336 | 338.2991 | -0.68427 | 36.1775 | 336.9531 | 44.5027 | 0.012 | 0.622 | 0.856 | 0.83415 | 2.5521 | 97.9592 | 0.82684 | 98.5487
[44 empty] | 1999-03-31 | 15:00 | 127 | 24 | 49 | 50 | 281 | 5 | 11.2 |  | 16.2 | 0.19401 | 0.30864 | 16.3457 | 11.4122 | 11.6164 | 350.9384 | 163.2181 | 347.5981 | 1.8605 | 47.6395 | 0.24384 | 7.7 | 7.5 | 7.7 | 191 | 297 | 328 | 338.5357 | -3.2121 | 34.8123 | 337.2231 | 43.3609 | 0.012 | 0.621 | 0.837 | 0.84514 | -0.97286 | 97.9592 | 0.83773 | 98.5676
[44 empty] | 1999-03-31 | 16:00 | 128 | 24 | 49 | 50 | 281 | 4.95 | 11.2 |  | 16.15 | 0.19401 | 0.3065 | 16.3994 | 11.2981 | 11.5003 | 350.452 | 163.0076 | 347.15 | 1.8579 | 47.6421 | 0.24139 | 7.8 | 7.5 | 7.8 | 181 | 296 | 319 | 342.5 | -7.3668 | 38.2253 | 341.0775 | 46.9329 | 0.013 | 0.622 | 0.845 | 0.84213 | 0.33971 | 97.7891 | 0.83483 | 98.4428
[44 empty] | 1999-03-31 | 17:00 | 129 | 24 | 49 | 50 | 281 | 5.14 | 11.1 |  | 16.24 | 0.19401 | 0.3165 | 16.303 | 11.7318 | 11.9417 | 352.7316 | 164.0076 | 349.2795 | 1.87 | 47.63 | 0.25072 | 7.8 | 7.5 | 7.7 | 178 | 297 | 338 | 346.2523 | -2.4415 | 39.2491 | 344.7134 | 48.3629 | 0.013 | 0.621 | 0.837 | 0.85426 | -2.0623 | 97.7891 | 0.84657 | 98.4644
[44 empty] | 1999-04-01 | 9:00 | 145 | 24 | 50 | 51 | 281 | 4.95 | 9.6 | X | 14.55 | 0.19401 | 0.34021 | 18.3127 | 11.2981 | 11.5003 | 358.175 | 166.5999 | 354.8003 | 1.8989 | 48.6011 | 0.23663 | 7.9 | 7.7 |  | 175 | 294 | 334 | 353.8438 | -5.9412 | 40.273 | 352.2685 | 50.322 | 0.014 | 0.62 | 0.812 | 0.88397 | -8.8631 | 97.619 | 0.87631 | 98.4024
[44 empty] | 1999-04-01 | 11:00 |  | 24 | 50 | 50 | 272 | 6 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 13.6947 | 13.9397 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 11:15 |  | 24 | 60 | 61 | 272 | 7.15 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 16.3195 | 16.6115 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 11:30 |  | 24 | 41 | 42 | 272 | 4.93 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 11.2525 | 11.4538 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 11:45 |  | 24 | 50 | 51 | 272 | 6.2 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 14.1512 | 14.4044 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 15:30 |  | 24 | 50 | 51 | 272 | 6.4 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 14.6077 | 14.869 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 15:45 |  | 24 | 60 | 61 | 272 | 7.63 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 17.4151 | 17.7267 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 16:00 |  | 24 | 40 | 41 | 272 | 5 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 11.4122 | 11.6164 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-01 | 16:30 |  | 24 | 50 | 51 | 272 | 6.36 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 14.5164 | 14.7761 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/9/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used for this study
Note on X11: C. Rice 7/19/99: Alkalinity verified by consultant.
Note on X13: C. Rice 7/19/99: Total hardness verified by consultant.
Note on X14: C. Rice 7/19/99: Calcium hardness verified by consultant.
Note on X18: C. Rice 7/19/99: UV verified by consultant.
Note on X33: C. Rice 7/19/99: MCAA concentrations verified by consultant.
Note on DG10: C. Rice 7/12/99: Consultant verified all values for alkalinity, total hardness, calcium hardness, and UV due to consistently high mass balance closure errors.
Note on DQ10: C. Rice 7/12/99: Consultant verified all values for alkalinity, total hardness, calcium hardness, and UV due to consistently high mass balance closure errors.
Note on EA10: C. Rice 7/12/99: Consultant verified all values for alkalinity, total hardness, calcium hardness, and UV due to consistently high mass balance closure errors.
Note on EK10: C. Rice 7/12/99: Consultant verified all values for alkalinity, total hardness, calcium hardness, and UV due to consistently high mass balance closure errors.