## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Houston, Texas | Carbon manufacturer | Calgon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | Raw pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX1010013 | Carbon trade name | F-300 | mesh size | (mm) | Coagulation | 40 + 20 mg/L alum | Pilot-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 Dose | Free Cl2 Residual | Cl2 Demand | Chlorination Temp. | Chlorination pH | Incubation Time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 | Flocculation | 4-stage | Pilot-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Pilot GAC influent TOC (mg/L) | 4 | 6 | 3.35 | Flocculation Aid | Anionic during flocculation 0.05 + 0.02 mg/L | Pilot-scale | START | N | 1998-04-14 | 14:00 | 0 | 0 | 0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | START | N | 1998-04-14 | 14:00 | 0 | 0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | START | N | 1998-04-14 | 14:00 | 0 | 0 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 101.6 | 8 | 2.36 | Sedimentation | tube settler; settling time ranged between 22 and 27 minutes | Pilot-scale | A1 | N | 1998-04-15 | 14:08 | 24.1333 | 72.4 | 144.8 | 7.11 | 0.08 | 64.8 | 21.7 | 120.8 | 107 | 0.2 | 110 | 3.61 | 0.0543 | 1.5042 | 3 | 0.85 | 2.15 | 21.1 | 8.09 | 18 | 185 | 52.63 | 23.03 | 14.14 | 1.968 | 91.768 | BMRL | 20.84 | 25.68 | BMRL | 5.668 | 10.368 | NA | NA | NA | 52.188 | 62.556 | B1 | N | 1998-04-15 | 14:08 | 24.1333 | 144.8 | 8.75 | 0.07 | 21.7 | 0.179 | 0.19 | 0.008 | 4.2105 | 1.25 | 0.7 | 0.55 | 22 | 8 | 18 | BMRL | 4.251 | 1.617 | 0.332 | 1.818 | 8.018 | BMRL | 0.373 | 6.38 | BMRL | BMRL | BMRL | NA | NA | NA | 6.753 | 6.753 | C1 | N | 1998-04-15 | 14:08 | 24.1333 | 72.4 | 8.65 | 0.06 | 21.7 | 0.156 | 0.12 | 0.006 | 5 | 1.25 | 0.7 | 0.55 | 22 | 8.05 | 18 | BMRL | 2.949 | 0.768 | 0.2608 | 1.669 | 5.6468 | BMRL | BMRL | 5.911 | BMRL | BMRL | BMRL | NA | NA | NA | 5.911 | 5.911 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 479.4 | 10 | 2 | Dual media filtration | sand / anthracite | Pilot-scale | A2 | N | 1998-04-22 | 11:45 | 189.75 | 569.25 | 1138.5 | 7.19 | 0.1 | 79 | 20.6 | 116 | 108 | 0.113 | 110 | 3.29 | 0.0734 | 2.231 | 3 | 0.85 | 2.15 | 22 | 8 | 18 | 290 | NR | 29.19 | 14.12 | 0.884 | 44.194 | BMRL | 29.74 | 41.12 | BMRL | 5.39 | 13.338 | NA | NA | NA | 76.25 | 89.588 | B2 | N | 1998-04-22 | 11:45 | 189.75 | 1138.5 | 7.17 | 0.08 | 20.6 | 0.0973 | 0.27 | 0.0055 | 2.037 | 1.25 | 0.65 | 0.6 | 22 | 8.1 | 18 | BMRL | 2.695 | 1.285 | 0.325 | 1.347 | 5.652 | BMRL | 0.174 | 6.258 | BMRL | 1.558 | BMRL | NA | NA | NA | 7.99 | 7.99 | C2 | N | 1998-04-22 | 11:45 | 189.75 | 569.25 | 7.18 | 0.07 | 20.6 | 0.0751 | 0.25 | 0.0024 | 0.96 | 1.25 | 0.8 | 0.45 | 22 | 8 | 18 | BMRL | 1.06 | 0.349 | 0.269 | 1.376 | 3.054 | BMRL | BMRL | 6.217 | BMRL | BMRL | BMRL | NA | NA | NA | 6.217 | 6.217 | Construction Contingencies (% of construction costs) | 10
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A3 | N | 1998-05-04 | 14:00 | 480 | 1440 | 2880 | 7.13 | 0.11 | 80 | 22.8 | 126 | 117.3 | 0.1 | 117 | 2.81 | 0.0652 | 2.3203 | 3 | 1 | 2 | 23.9 | 7.94 | 18 | 250 | 33.805 | 30.49 | 17.43 | 2.992 | 84.717 | 1.353 | 16.87 | 12.733 | BMRL | 5.68 | 10.637 | NA | NA | NA | 36.636 | 47.273 | B3 | N | 1998-04-29 | 14:00 | 360 | 2160 | 7.13 | 0.1 | 21.7 | 0.141 | 0.5 | 0.0074 | 1.48 | 1.25 | 0.55 | 0.7 | 23.9 | 8.24 | 18 | BMRL | 1.556 | 3.477 | 6.8917 | 6.9267 | 18.8514 | BMRL | 0.299 | BMRL | BMRL | 3.14 | 2.88 | NA | NA | NA | 3.439 | 6.319 | C3 | N | 1998-05-04 | 14:00 | 480 | 1440 | 7.06 | 0.09 | 22.8 | 0.046 | 0.39 | 0.0039 | 1 | 1 | 0.7 | 0.3 | 23.9 | 8.22 | 18 | BMRL | 0.654 | 1.487 | 1.559 | 1.195 | 4.895 | BMRL | BMRL | BMRL | BMRL | 0.282 | BMRL | NA | NA | NA | 0.282 | 0.282 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 |  |  |  | A4 | N | 1998-05-11 | 14:00 | 648 | 1944 | 3888 | 7.15 | 0.11 | 80 | 23.6 | 130 | 117.3 | 0.046 | 123 | 3.12 | 0.0603 | 1.9327 | 3.5 | 0.95 | 2.55 | 25 | 8.1 | 18 | 225 | NR | 20.926 | 13.966 | 8.311 | 43.203 | BMRL | 17.622 | 10.139 | 1.123 | 9.661 | 12.764 | NA | NA | NA | 38.545 | 51.309 | B4 | N | 1998-05-05 | 14:00 | 504 | 3024 | 7.28 | 0.13 | 22.2 | 0.05 | 0.88 | 0.0125 | 1.4205 | 1.25 | 0.7 | 0.55 | 23.9 | 8.06 | 18 | 47 | 2.544 | 6.084 | 13.419 | 12.4679 | 34.5149 | BMRL | 1.353 | 0.621 | BMRL | 5.077 | 5.157 | NA | NA | NA | 7.051 | 12.208 | C4 | N | 1998-05-11 | 13:30 | 647.5 | 1942.5 | 7.07 | 0.08 | 23.6 | 0.029 | 0.53 | 0.0047 | 0.88679 | 1 | 0.7 | 0.3 | 25 | 8.13 | 18 | BMRL | 1.529 | 1.937 | 1.886 | 2.125 | 7.477 | BMRL | 1.197 | 0.787 | BMRL | BMRL | 4.961 | NA | NA | NA | 1.984 | 6.945 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6859
FAX Number |  | Flow rate, Q (L/hr) | 102.2 | 20 | 0.85 |  |  |  | A5 | N | 1998-05-14 | 14:00 | 720 | 2160 | 4320 | 7.37 | 0.1 | 79 | 24.4 | 127 | 114.8 | 0.18 | 135 | 3.08 | 0.0538 | 1.7468 | 3.4 | 0.9 | 2.5 | 26.1 | 8 | 18 | 250 | 43.4 | 35.95 | 22.98 | 3.527 | 105.857 | BMRL | 20.488 | 17.53 | 0.704 | 5.49 | 12.278 | NA | NA | NA | 44.212 | 56.49 | AVG-B5 | Y | 1998-05-07 | 14:00 | 552 | 3312 | 7.29 | 0.1 | 21.7 | 0.032 | 1.06 | 0.0128 | 1.2075 | 1.2 | 0.65 | 0.55 | 23.3333 | 8.08 | 18.5 | 63 | 2.61 | 6.44 | 13.57 | 10.46 | 33.08 | BMRL | 1.81 | 0.44 | BMRL | 5.92 | 4.76 | NA | NA | NA | 8.17 | 12.93 | C5 | N | 1998-05-14 | 14:00 | 720 | 2160 | 7.28 | 0.08 | 24.4 | 0.16 | 0.65 | 0.0041 | 0.63077 | 0.8 | 0.65 | 0.15 | 26.1 | 8.06 | 18 | BMRL | 0.62 | 0.0276 | 0.79 | 1.62 | 3.0576 | BMRL | 0.141 | 0 | BMRL | 4.247 | 1.147 | NA | NA | NA | 4.388 | 5.535 | 1998 Producers Price Index (PPI base year 1967 = 100) | 130.5
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | AVG-A6 | Y | 1998-06-01 | 16:00 | 1154 | 3462 | 6924 | 7.26 | 0.12 | 97.5 | 25.6 | 138 | 122.7 | 0.08 | 110 | 2.97 | 0.068 | 2.2896 | 2.88 | 0.63 | 2.25 | 25.3 | 8.05 | 18 | 250 | 43.89 | 35.41 | 22.02 | 3.67 | 104.99 | BMRL | 18.02 | 14.49 | BMRL | 6.65 | 11.66 | 6.06 | 4.34 | 8.2 | 39.16 | 50.82 | B6 | N | 1998-05-11 | 15:00 | 649 | 3894 | 7.1 | 0.09 | 23.6 | 0.043 | 1.23 | 0.0164 | 1.3333 | 1.85 | 0.95 | 0.9 | 25 | 8.14 | 18 | 56 | 3.31 | 9.57 | 18.48 | 11.5 | 42.86 | BMRL | 2.734 | 0.6009 | BMRL | 6.863 | 3.287 | NA | NA | NA | 10.1979 | 13.4849 | AVG-C6 | Y | 1998-06-01 | 15:00 | 1153 | 3459 | 7.2 | 0.09 | 26.7 | 0.06 | 0.71 | 0.0094 | 1.3239 | 1.1 | 0.6 | 0.5 | 25.3 | 8.12 | 18 | BMRL | 2 | 1.88 | 6.79 | 10.07 | 20.74 | 1.3 | 1.54 | 2.69 | BMRL | 6.08 | BMRL | BMRL | BMRL | BMRL | 11.61 | 11.61 | Labor Rate + Fringe ($/work-hour) | 25
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | N | 1998-06-06 | 14:00 | 1272 | 3816 | 7632 | 7.25 | 0.13 | 106 | 28.9 | 138 | 127.2 | 0.107 | 111 | 3.1 | 0.068 | 2.1935 | 3.2 | 1 | 2.2 | 25.7 | 8.08 | 18 | 260 | 41.3 | 34.4 | 21.8 | 3.91 | 101.41 | BMRL | 12.94 | 12.79 | 2.38 | 3.89 | 9.32 | 6.12 | BMRL | 7.46 | 32 | 41.32 | B7 | N | 1998-05-18 | 14:00 | 816 | 4896 | 7.41 | 0.09 | 26.7 | 0.14 | 1.25 | 0.0195 | 1.56 | 1.65 | 0.85 | 0.8 | 26.1 | 8.02 | 18 | NR | 7.1 | 14.7 | 25.3 | 10.07 | 57.17 | BMRL | 3.364 | 1.769 | BMRL | 6.521 | 4.646 | NA | NA | NA | 11.654 | 16.3 | C7 | N | 1998-06-06 | 14:00 | 1272 | 3816 | 7.27 | 0.08 | 28.9 | 0.043 | 0.89 | 0.0081 | 0.91011 | 1.1 | 1 | 0.1 | 26.7 | 8.02 | 18 | BMRL | 1.3 | 1.57 | 4.21 | 7.29 | 14.37 | BMRL | 2.15 | 0.5 | 1.4 | 4.9 | 3.66 | 4.31 | BMRL | BMRL | 8.95 | 12.61 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 3579.1652 | 50 | 0.3 |  |  |  | AVG-A8 | Y | 1998-06-22 | 15:00 | 1657 | 4971 | 9942 | 7.14 | 0.24 | 84 | 27.8 | 123 | 109.5 | 0.04 | 145 | 3.26 | 0.067 | 2.0552 | 3.35 | 0.73 | 2.62 | 27.8 | 8.14 | 18 | 258 | 39.37 | 27.5 | 16.71 | 10 | 93.58 | BMRL | 17.8 | 16.35 | 1.89 | 5.93 | 13.88 | NR | BMRL | 8.12 | 41.97 | 55.85 | B8 | N | 1998-05-20 | 15:00 | 865 | 5190 | 7.26 | 0.12 | 27.2 | 0.07 | 1.45 | NR | #VALUE! | 1.4 | 0.85 | 0.55 | 25 | 8.2 | 18.5 | 78 | 7.45 | 15.4 | 25.32 | 9.84 | 58.01 | BMRL | 3.53 | 1.93 | BMRL | 3.963 | 5.36 | NA | NA | NA | 9.423 | 14.783 | AVG-C8 | Y | 1998-06-22 | 15:00 | 1657 | 4971 | 7.16 | 0.1 | 26.1 | 0.01 | 0.86 | 0.014 | 1.6279 | 1.05 | 0.68 | 0.37 | 27.8 | 8.19 | 18 | 56 | 2.26 | 4.96 | 11.88 | 12.18 | 31.28 | BMRL | 2.09 | 1.18 | 6.83 | 5.91 | 3.35 | 6.08 | BMRL | BMRL | 16.01 | 19.36 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 7158.3304 | 60 | 0.25 |  |  |  | A9 | N | 1998-07-01 | 14:30 | 1872.5 | 5617.5 | 11235 | 7.31 | 0.11 | 114 | 30 | 134 | 120 | 0.07 | 111 | 3.19 | 0.0625 | 1.9592 | 2.55 | 0.9 | 1.65 | 27.8 | 8.17 | 18 | 240 | 37.68 | 26.3 | 17.71 | 6.59 | 88.28 | BMRL | 24.68 | 13.08 | 3.19 | 9.6 | 15.86 | 6.15 | BMRL | 8.02 | 50.55 | 66.41 | B9 | N | 1998-05-23 | 13:00 | 935 | 5610 | 7.06 | 0.11 | 27.2 | 0.043 | 1.61 | NR | #VALUE! | 1.5 | 0.75 | 0.75 | 25 | 8.25 | 18.5 | 98 | 9.25 | 15.58 | 24.26 | 12.41 | 61.5 | BMRL | 3.06 | 4.036 | BMRL | 8.46 | 6.36 | BMRL | BMRL | 3.18 | 15.556 | 21.916 | C9 | N | 1998-07-01 | 14:30 | 1872.5 | 5617.5 | 7.2 | 0.09 | 30 | 0.0729 | 1.06 | 0.0146 | 1.3774 | 1.2 | 0.6 | 0.6 | 27.8 | 8.14 | 18 | 64 | 3.51 | 8.27 | 17.08 | 20.16 | 49.02 | BMRL | 7.79 | 5.01 | BMRL | 5.82 | 5.34 | NA | NA | NA | 18.62 | 23.96 | Fuel Oil Rate ($/gal) | 0.89
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-07-13 | 15:10 | 2161.1667 | 6483.5 | 12967 | 7.32 | 0.11 | 90 | 30.6 | 129 | 109.8 | 0.095 | 115 | 3.25 | 0.0667 | 2.0523 | 2.4 | 0.75 | 1.65 | 26.1 | 8.11 | 18 | 265 | 41.46 | 34.12 | 21.82 | 2.61 | 100.01 | 2.72 | 39.21 | 33.69 | BMRL | 10.17 | 18.5 | NA | NA | NA | 85.79 | 104.29 | B10 | N | 1998-06-01 | 16:00 | 1154 | 6924 | 7.19 | 0.12 | 26.7 | 0.042 | 1.78 | 0.0322 | 1.809 | 1.6 | 0.7 | 0.9 | 25.3 | 7.97 | 18 | 105 | 9.69 | 16.25 | 23.38 | 11.38 | 60.7 | BMRL | 5.526 | 3.865 | BMRL | 4.66 | 7.37 | 8.788 | 4.43 | 4.417 | 14.051 | 21.421 | C10 | N | 1998-07-13 | 15:10 | 2161.1667 | 6483.5 | 7.15 | 0.08 | 30 | 0.053 | 1.24 | 0.0184 | 1.4839 | 1.25 | 0.6 | 0.65 | 26.1 | 8.17 | 18 | 71 | 2.74 | 10.54 | 21.16 | 12.92 | 47.36 | 1.07 | 10.32 | 6.17 | BMRL | 14.38 | 8.89 | NA | NA | NA | 31.94 | 40.83 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-07-18 | 13:00 | 2279 | 6837 | 13674 | 7.45 | 0.12 | 91 | 30.6 | 123 | 107.3 | 0.108 | 118 | 3.34 | 0.0639 | 1.9132 | 2.5 | 0.65 | 1.85 | 27.8 | 8.05 | 18 | 235 | 36.85 | 31.9 | 20.6 | 2.77 | 92.12 | 3.62 | 38.47 | 36.3 | BMRL | 9.19 | 18.28 | NA | NA | NA | 87.58 | 105.86 | B11 | N | 1998-06-06 | 14:00 | 1272 | 7632 | 7.2 | 0.1 | 28.9 | 0.034 | 1.84 | 0.0313 | 1.7011 | 1.8 | 0.7 | 1.1 | 25.7 | 8.08 | 18 | 110 | 11.33 | 17.94 | 23.73 | 10.94 | 63.94 | BMRL | 6.94 | 3.68 | 0.66 | 6.46 | 4.85 | 6.43 | 7.72 | 5.74 | 17.74 | 22.59 | C11 | N | 1998-07-18 | 13:00 | 2279 | 6837 | 7.4 | 0.09 | 30.6 | 0.047 | 1.41 | 0.022 | 1.5603 | 1.55 | 0.6 | 0.95 | 26.1 | 8.05 | 18 | 60 | 3.02 | 9.6 | 18.24 | 9.2 | 40.06 | 0.93 | 11.24 | 8.68 | BMRL | 12.29 | 9.2 | NA | NA | NA | 33.14 | 42.34 | Current Process Water Rate ($/1000 gal) | 0.08 | for EWPP III
FAX Number |  | Carbon particle diameter, d (mm) | 1.48 | [5 empty] | AVG-A12 | Y | 1998-07-25 | 16:00 | 2450 | 7350 | 14700 | 7.45 | 0.1 | 94 | 31.7 | 127 | 107.7 | 0.08 | 109 | 3.36 | 0.07 | 2.0833 | 3.35 | 0.75 | 2.6 | 30 | 8.19 | 18 | 265 | 38.14 | 33.23 | 22.66 | 3.44 | 97.47 | 4.62 | 35.59 | 23.12 | BMRL | 10.99 | 20.45 | NA | NA | NA | 74.32 | 94.77 | B12 | N | 1998-06-12 | 15:00 | 1417 | 8502 | 7.25 | 0.12 | 28.9 | 0.03 | 1.99 | 0.0339 | 1.7035 | 1.95 | 0.8 | 1.15 | 26.7 | 8.1 | 18 | 145 | 15.67 | 17.99 | 22.52 | 7.31 | 63.49 | BMRL | 4.94 | 2.1 | 0.66 | 7.84 | 8.28 | NA | NA | NA | 15.54 | 23.82 | AVG-C12 | Y | 1998-07-25 | 16:00 | 2450 | 7350 | 7.55 | 0.12 | 31.7 | 0.0433 | 1.54 | 0.024 | 1.5584 | 1.7 | 0.65 | 1.05 | 30 | 8.17 | 18 | 95 | 4.31 | 13.63 | 23.15 | 11.1 | 52.19 | 1.73 | 12.56 | 3.55 | BMRL | 15.05 | 11.32 | NA | NA | NA | 32.89 | 44.21 | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0081073 | [5 empty] | A13 | N | 1998-08-04 | 17:00 | 2691 | 8073 | 16146 | 7.34 | 0.33 | 100 | 30 | 134 | 117.3 | 0.12 | 171 | 3.35 | 0.0608 | 1.8149 | 3.3 | 0.8 | 2.5 | 27.2 | 8.12 | 18 | 260 | 40.5 | 37.52 | 23.82 | 3.41 | 105.25 | 2.04 | 33.03 | 16.67 | BMRL | 10.63 | 19.81 | NA | NA | NA | 62.37 | 82.18 | AVG-B13 | Y | 1998-06-22 | 15:00 | 1657 | 9942 | 7.17 | 0.1 | 26.7 | 0.02 | 2.1 | 0.038 | 1.8095 | 1.7 | 0.8 | 0.9 | 27.8 | 8.09 | 18 | 143 | NR | 16.48 | 20.37 | 10.31 | 47.16 | BMRL | 4.88 | 1.94 | 3.95 | 5.91 | 4.9 | 6.22 | 6.63 | 5.48 | 16.68 | 21.58 | C13 | N | 1998-08-04 | 17:00 | 2691 | 8073 | 7.29 | 0.1 | 30 | 0.099 | 1.77 | 0.0252 | 1.4237 | 1.95 | 0.85 | 1.1 | 27.2 | 8 | 18 | 105 | 6.5 | 16.06 | 24.34 | 9.71 | 56.61 | 1.8 | 15.45 | 5.8 | BMRL | 16.99 | 14.29 | NA | NA | NA | 40.04 | 54.33
|  | Hydraulic loading rate1, v (m/hr) | 12.6059 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1998-08-13 | 14:00 | 2904 | 8712 | 17424 | 7.23 | 0.1 | 86 | 30 | 126 | 107.3 | 0.07 | 171 | 3.52 | 0.0618 | 1.7557 | 3.1 | 0.85 | 2.25 | 26.7 | 8.12 | 18 | 255 | 32.78 | 26.08 | 19.24 | 2.74 | 80.84 | 2.45 | 33.59 | 19.03 | BMRL | 10.54 | 18.07 | NA | NA | NA | 65.61 | 83.68 | B14 | N | 1998-07-02 | 14:30 | 1896.5 | 11379 | 7.02 | 0.11 | 27.8 | 0.07 | 2.23 | 0.0365 | 1.6368 | 2.1 | 0.8 | 1.3 | 27.8 | 8.12 | 18 | 145 | 14.98 | 17.86 | 21.69 | 9.83 | 64.36 | BMRL | 10.85 | 6.62 | 1.92 | 6.52 | 9.74 | 7.12 | 3.22 | 6.05 | 25.91 | 35.65 | C14 | N | 1998-08-13 | 14:00 | 2904 | 8712 | 7.21 | 0.08 | 30 | 0.0567 | 1.92 | 0.0245 | 1.276 | 2.1 | 0.9 | 1.2 | 26.7 | 8.16 | 18 | 115 | 6.87 | 14.4 | 20.32 | 7.48 | 49.07 | 1.49 | 15.62 | 7.12 | BMRL | 14.37 | 12.57 | NA | NA | NA | 38.6 | 51.17
Plant Name | East Water Purification Plant III | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A15 | N | 1998-09-10 | 15:00 | 3577 | 10731 | 21462 | 7.57 | 0.13 | 96 | 27.8 | 132 | 112.2 | 0.13 | 179 | 3.23 | 0.0635 | 1.9659 | 3.4 | 0.9 | 2.5 | 26.7 | 8.01 | 18 | 240 | 33.67 | 24.09 | 18.41 | 4 | 80.17 | 1.94 | 24.53 | 8.83 | BMRL | 5.43 | 7.47 | NA | NA | NA | 40.73 | 48.2 | AVG-B15 | Y | 1998-07-16 | 15:00 | 2233 | 13398 | 7.37 | 0.09 | 27.8 | 0.061 | 2.28 | 0.0522 | 2.2895 | 1.8 | 0.63 | 1.17 | 26.1 | 8.19 | 18 | 138 | 17.1 | 21.34 | 23.82 | 6.57 | 68.83 | 1.71 | 19.42 | 7.84 | BMRL | 15.04 | 13.61 | NA | NA | NA | 44.01 | 57.62 | C15 | N | 1998-09-10 | 15:00 | 3577 | 10731 | 7.49 | 0.08 | 27.8 | 0.081 | 1.84 | 0.0281 | 1.5272 | 2 | 0.95 | 1.05 | 26.7 | 7.98 | 18 | 130 | 8.11 | 12.14 | 10.02 | 3.44 | 33.71 | 3.91 | 15.53 | 6.69 | BMRL | 8.44 | 11.28 | NA | NA | NA | 34.57 | 45.85
Treatment Plant Category | Conventional |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A16 | N | 1998-10-05 | 14:00 | 4176 | 12528 | 25056 | 6.92 | 0.06 | 78 | 27.8 | 148 | 142.8 | 0.11 | 110 | 3.47 | 0.0669 | 1.928 | 3.1 | 0.95 | 2.15 | 25 | 8.04 | 18 | 335 | 34.16 | 23.43 | 19.99 | 5.89 | 83.47 | 2.09 | 24.97 | 28.67 | 0.56 | 4.25 | 15.56 | NA | NA | NA | 60.54 | 76.1 |  |  |  |  | -861614.1333 | -5169684.8 | [30 empty] | C16 | N | 1998-10-05 | 14:00 | 4176 | 12528 | 6.9 | 0.14 | 27.8 | 0.089 | 2.23 | 0.0349 | 1.565 | 2 | 0.95 | 1.05 | 25 | 8.01 | 18 | 165 | 10 | 10.61 | 8.52 | 1.95 | 31.08 | 3.36 | 17.45 | 7.07 | 1.82 | 7.93 | 12.99 | NA | NA | NA | 37.63 | 50.62
Process Train Name | Plant III | 10-Minute EBCT Run | [6 empty] | A17 | N | 1998-10-14 | 15:00 | 4393 | 13179 | 26358 | 6.96 | 0.06 | 66 | 23.9 | 120 | 89.8 | 0.099 | 110 | 3.58 | 0.0687 | 1.919 | 3.4 | 1 | 2.4 | 26.5 | 7.92 | 18 | 355 | 30.35 | 17.87 | 5.46 | 1.75 | 55.43 | 2.56 | 33.97 | 32.01 | 0.32 | 4.74 | 18.82 | NA | NA | NA | 73.6 | 92.42 |  |  |  |  | -861614.1333 | -5169684.8 | [30 empty] | C17 | N | 1998-10-14 | 15:00 | 4393 | 13179 | 6.93 | 0.09 | 23.9 | 0.054 | 2.39 | 0.037 | 1.5481 | 2.3 | 1 | 1.3 | 24 | 7.97 | 18 | 165 | 12.71 | 11.19 | 8.19 | 1.7 | 33.79 | 2.54 | 18.04 | 6.55 | 0.54 | 8.13 | 13.96 | NA | NA | NA | 35.8 | 49.76
ICR Treatment Plant Identification Number | 630 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A18 | N | 1998-10-29 | 9:30 | 4747.5 | 14242.5 | 28485 | 6.93 | 0.07 | 60 | 21.7 | 110 | 97.3 | 0.088 | 120 | 3.46 | 0.0459 | 1.3266 | 2.8 | 0.85 | 1.95 | 23.3 | 8.08 | 18 | 305 | 29.83 | 21.87 | 11.84 | 0.91 | 64.45 | 2.55 | 28.39 | 16.94 | 0.71 | 5.83 | 18.89 | NA | NA | NA | 54.42 | 73.31 |  |  |  |  | -861779.75 | -5170678.5 | [30 empty] | C18 | Y | 1998-10-29 | 9:30 | 4747.5 | 14242.5 | 6.98 | 0.07 | 21.7 | 0.081 | 2.38 | 0.0311 | 1.3067 | 2.2 | 1 | 1.2 | 23.3 | 8.14 | 18 | 150 | 9.58 | 9.45 | 9.28 | 2.09 | 30.4 | 2.44 | 15.51 | 7.31 | 0.17 | 10.56 | 16.88 | NA | NA | NA | 35.99 | 52.87
PWSID Number of Plant (if assigned) | TX1010013 | Estimated run time, t (days) | 49.7106 | [9 empty] | -861614.1333 | -2584842.4 | -5169684.8 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861950 | -5171700 | [34 empty] | -861614.1333 | -2584842.4 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Minimum Water Temperature (oC) | 8.9 | Pilot column bed length, l (m) | 2.101 | [9 empty] | -861590 | -2584770 | -5169540 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -862094 | -5172564 | [34 empty] | -861779.75 | -2585339.25 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Average Water Temperature (oC) | 21 | Mass GAC required, m (kg) | 8.1658 | [9 empty] | -861590 | -2584770 | -5169540 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -862142 | -5172852 | [34 empty] | -861590 | -2584770 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
State Approved Plant Capacity (MGD) | 150 | [11 empty] | -861590 | -2584770 | -5169540 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -862142 | -5172852 | [34 empty] | -861590 | -2584770 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | 20-Minute EBCT Run | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
|  | Estimated run time, t (days) | 99.4213 | [5 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
|  | Pilot column bed length, l (m) | 4.202
|  | Mass GAC required, m (kg) | 16.3316
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A6 | Primary | 1998-06-01 | 16:00 | 1154 | 3462 | 6924 | 7.25 | 0.12 | 98 | 25.6 | 137 | 123 | 0.08 | 111 | 3.03 | 0.0689 | 2.2739 | 2.75 | 0.55 | 2.2 | 25.3 | 8.02 | 18 | 250 | 44.2967 | 36.846 | 22.9616 | 3.904 | 108.0083 | BMRL | 17.44 | 13.745 | BMRL | 7.319 | 10.73 | 5.88 | 4.105 | 8.168 | 38.504 | 49.234 | B5 | Primary | 1998-05-07 | 14:00 | 552 | 3312 | 7.29 | 0.1 | 21.7 | 0.032 | 1.02 | 0.013 | 1.2745 | 1.25 | 0.55 | 0.7 | 23.3 | 8.08 | 18.5 | 66 | 2.648 | 6.629 | 13.75 | 10.512 | 33.539 | BMRL | 1.598 | 0.448 | BMRL | 5.861 | 4.378 | NA | NA | NA | 7.907 | 12.285 | C6 | Primary | 1998-06-01 | 16:00 | 1154 | 3462 | 7.18 | 0.1 | 26.7 | 0.06 | 0.69 | 0.0094 | 1.3623 | 1.1 | 0.65 | 0.45 | 25.3 | 8.01 | 18 | BMRL | 1.81 | 1.71 | 5.935 | 8.42 | 17.875 | 1.16 | 1.24 | 4.233 | BMRL | 6.58 | BMRL | BMRL | BMRL | BMRL | 13.213 | 13.213
[9 empty] | A6-DUP | Duplicate | 1998-06-01 | 16:00 | 1154 | 3462 | 6924 | 7.26 | 0.12 | 97 | 25.6 | 139 | 122.3 | 0.078 | 109 | 2.91 | 0.0668 | 2.2955 | 3 | 0.7 | 2.3 | 25.3 | 8.07 | 18 | 250 | 43.49 | 33.98 | 21.08 | 3.43 | 101.98 | BMRL | 18.6 | 15.23 | BMRL | 5.99 | 12.59 | 6.24 | 4.581 | 8.24 | 39.82 | 52.41 | B5-DUP | Duplicate | 1998-05-07 | 14:00 | 552 | 3312 | 7.29 | 0.1 | 21.7 | 0.035 | 1.09 | 0.0126 | 1.156 | 1.15 | 0.75 | 0.4 | 23.3 | 8.08 | 18.5 | 60 | 2.58 | 6.253 | 13.39 | 10.4 | 32.623 | BMRL | 2.017 | 0.434 | BMRL | 5.98 | 5.141 | NA | NA | NA | 8.431 | 13.572 | C6-DUP | Duplicate | 1998-06-01 | 16:00 | 1154 | 3462 | 7.21 | 0.08 | 26.7 | 0.05 | 0.73 | 0.0095 | 1.3014 | 1.1 | 0.55 | 0.55 | 25.3 | 8.22 | 18 | BMRL | 2.199 | 2.056 | 7.642 | 11.716 | 23.613 | 1.44 | 1.84 | 1.14 | BMRL | 5.58 | BMRL | BMRL | BMRL | BMRL | 10 | 10
[10 empty] | Average | --- | --- | --- | --- | --- | 7.255 | 0.12 | 97.5 | 25.6 | 138 | 122.65 | 0.079 | 110 | 2.97 | 0.06785 | 2.2847 | 2.875 | 0.625 | 2.25 | 25.3 | 8.045 | 18 | 250 | 43.8934 | 35.413 | 22.0208 | 3.667 | 104.9942 | #DIV/0! | 18.02 | 14.4875 | #DIV/0! | 6.6545 | 11.66 | 6.06 | 4.343 | 8.204 | 39.162 | 50.822 |  | Average | --- | --- | --- | --- | 7.29 | 0.1 | 21.7 | 0.0335 | 1.055 | 0.0128 | 1.2152 | 1.2 | 0.65 | 0.55 | 23.3 | 8.08 | 18.5 | 63 | 2.614 | 6.441 | 13.57 | 10.456 | 33.081 | #DIV/0! | 1.8075 | 0.441 | #DIV/0! | 5.9205 | 4.7595 | #DIV/0! | #DIV/0! | #DIV/0! | 8.169 | 12.9285 |  | Average | --- | --- | --- | --- | 7.195 | 0.09 | 26.7 | 0.055 | 0.71 | 0.00945 | 1.3318 | 1.1 | 0.6 | 0.5 | 25.3 | 8.115 | 18 | #DIV/0! | 2.0045 | 1.883 | 6.7885 | 10.068 | 20.744 | 1.3 | 1.54 | 2.6865 | #DIV/0! | 6.08 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 11.6065 | 11.6065
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.13784 | 0 | 1.0256 | 0 | 1.4493 | 0.57073 | 2.5316 | 1.8182 | 4.0404 | 3.0951 | 0.94564 | 8.6957 | 24 | 4.4444 | 0 | 0.6215 | 0 | 0 | 1.8379 | 8.0931 | 8.5446 | 12.9261 | 5.7416 | #VALUE! | 6.4373 | 10.2502 | #VALUE! | 19.9714 | 15.952 | 5.9406 | 10.9602 | 0.87762 | 3.3604 | 6.2493 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 8.9552 | 6.6351 | 3.125 | 9.755 | 8.3333 | 30.7692 | 54.5455 | 0 | 0 | 0 | 9.5238 | 2.6014 | 5.8376 | 2.6529 | 1.0712 | 2.769 | #VALUE! | 23.1812 | 3.1746 | #VALUE! | 2.01 | 16.0311 | #VALUE! | #VALUE! | #VALUE! | 6.4145 | 9.9548 |  | RPD | --- | --- | --- | --- | 0.41696 | 22.2222 | 0 | 18.1818 | 5.6338 | 1.0582 | 4.5763 | 0 | 16.6667 | 20 | 0 | 2.5878 | 0 | #VALUE! | 19.4063 | 18.3749 | 25.1455 | 32.7374 | 27.661 | 21.5385 | 38.961 | 115.1312 | #VALUE! | 16.4474 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 27.6828 | 27.6828
[9 empty] | A8 | Primary | 1998-06-22 | 15:00 | 1657 | 4971 | 9942 | 7.15 | 0.24 | 84 | 27.8 | 122 | 109 | 0.04 | 140 | 3.27 | 0.0657 | 2.0092 | 3.2 | 0.6 | 2.6 | 27.8 | 8.11 | 18 | 255 | 38.3 | 27.49 | 16.85 | 10.46 | 93.1 | BMRL | 18.94 | 16 | 2.15 | 6.35 | 12.84 | NR | BMRL | 8.12 | 43.44 | 56.28 | B13 | Primary | 1998-06-22 | 15:00 | 1657 | 9942 | 7.18 | 0.09 | 26.7 | 0.02 | 2.11 | 0.0391 | 1.8531 | 1.8 | 0.8 | 1 | 27.8 | 8.08 | 18 | 145 | NR | NR | 21.87 | 9.59 | 31.46 | BMRL | 4.72 | 2.1 | 4.19 | 6.04 | 5.18 | 6.42 | 6.7 | 5.75 | 17.05 | 22.23 | C8 | Primary | 1998-06-22 | 15:00 | 1657 | 4971 | 7.15 | 0.1 | 26.1 | 0.01 | 0.86 | 0.0148 | 1.7209 | 1.1 | 0.7 | 0.4 | 27.8 | 8.17 | 18 | 50 | 2.15 | 4.83 | 10.95 | 11.69 | 29.62 | BMRL | 2 | 0.88 | 6.42 | 6.24 | 3.14 | 6.08 | BMRL | BMRL | 15.54 | 18.68
[9 empty] | A8-DUP | Duplicate | 1998-06-22 | 15:00 | 1657 | 4971 | 9942 | 7.13 | 0.24 | 84 | 27.8 | 124 | 110 | 0.04 | 150 | 3.25 | 0.068 | 2.0923 | 3.5 | 0.85 | 2.65 | 27.8 | 8.16 | 18 | 260 | 40.43 | 27.51 | 16.56 | 9.54 | 94.04 | BMRL | 16.66 | 16.7 | 1.62 | 5.51 | 14.91 | NR | BMRL | NR | 40.49 | 55.4 | B13-DUP | Duplicate | 1998-06-22 | 15:00 | 1657 | 9942 | 7.16 | 0.1 | 26.7 | 0.02 | 2.09 | 0.0364 | 1.7416 | 1.6 | 0.8 | 0.8 | 27.8 | 8.1 | 18 | 140 | NR | 16.48 | 18.86 | 11.02 | 46.36 | BMRL | 5.03 | 1.78 | 3.7 | 5.77 | 4.62 | 6.01 | 6.55 | 5.21 | 16.28 | 20.9 | C8-DUP | Duplicate | 1998-06-22 | 15:00 | 1657 | 4971 | 7.16 | 0.1 | 26.1 | 0.01 | 0.86 | 0.0139 | 1.6163 | 1 | 0.65 | 0.35 | 27.8 | 8.2 | 18 | 61 | 2.37 | 5.08 | 12.81 | 12.67 | 32.93 | BMRL | 2.18 | 1.47 | 7.23 | 5.57 | 3.55 | 6.07 | BMRL | BMRL | 16.45 | 20
[10 empty] | Average | --- | --- | --- | --- | --- | 7.14 | 0.24 | 84 | 27.8 | 123 | 109.5 | 0.04 | 145 | 3.26 | 0.06685 | 2.0507 | 3.35 | 0.725 | 2.625 | 27.8 | 8.135 | 18 | 257.5 | 39.365 | 27.5 | 16.705 | 10 | 93.57 | #DIV/0! | 17.8 | 16.35 | 1.885 | 5.93 | 13.875 | #DIV/0! | #DIV/0! | 8.12 | 41.965 | 55.84 |  | Average | --- | --- | --- | --- | 7.17 | 0.095 | 26.7 | 0.02 | 2.1 | 0.03775 | 1.7974 | 1.7 | 0.8 | 0.9 | 27.8 | 8.09 | 18 | 142.5 | #DIV/0! | 16.48 | 20.365 | 10.305 | 38.91 | #DIV/0! | 4.875 | 1.94 | 3.945 | 5.905 | 4.9 | 6.215 | 6.625 | 5.48 | 16.665 | 21.565 |  | Average | --- | --- | --- | --- | 7.155 | 0.1 | 26.1 | 0.01 | 0.86 | 0.01435 | 1.6686 | 1.05 | 0.675 | 0.375 | 27.8 | 8.185 | 18 | 55.5 | 2.26 | 4.955 | 11.88 | 12.18 | 31.275 | #DIV/0! | 2.09 | 1.175 | 6.825 | 5.905 | 3.345 | 6.075 | #DIV/0! | #DIV/0! | 15.995 | 19.34
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.28011 | 0 | 0 | 0 | 1.626 | 0.91324 | 0 | 6.8966 | 0.6135 | 3.4405 | 4.0538 | 8.9552 | 34.4828 | 1.9048 | 0 | 0.61463 | 0 | 1.9417 | 5.4109 | 0.072727 | 1.736 | 9.2 | 1.0046 | #VALUE! | 12.809 | 4.2813 | 28.1167 | 14.1653 | 14.9189 | #VALUE! | #VALUE! | #VALUE! | 7.0297 | 1.5759 |  | RPD | --- | --- | --- | --- | 0.27894 | 10.5263 | 0 | 0 | 0.95238 | 7.1523 | 6.201 | 11.7647 | 0 | 22.2222 | 0 | 0.24722 | 0 | 3.5088 | #VALUE! | #VALUE! | 14.7803 | 13.8768 | 38.2935 | #VALUE! | 6.359 | 16.4948 | 12.4208 | 4.5724 | 11.4286 | 6.5969 | 2.2642 | 9.854 | 4.6205 | 6.1674 |  | RPD | --- | --- | --- | --- | 0.13976 | 0 | 0 | 0 | 0 | 6.2718 | 6.2718 | 9.5238 | 7.4074 | 13.3333 | 0 | 0.36652 | 0 | 19.8198 | 9.7345 | 5.0454 | 15.6566 | 8.046 | 10.5835 | #VALUE! | 8.6124 | 50.2128 | 11.8681 | 11.3463 | 12.2571 | 0.16461 | #VALUE! | #VALUE! | 5.6893 | 6.8252
[9 empty] | A12 | Primary | 1998-07-25 | 16:00 | 2450 | 7350 | 14700 | 7.44 | 0.09 | 94 | 31.7 | 127 | 107.3 | 0.086 | 110 | 3.32 | 0.0689 | 2.0753 | 3.3 | 0.75 | 2.55 | 30 | 8.09 | 18 | 260 | 36.62 | 32.09 | 22.04 | 3.12 | 93.87 | 5.76 | 34.83 | 23.62 | BMRL | 10.16 | 19.7 | NA | NA | NA | 74.37 | 94.07 | B15 | Primary | 1998-07-16 | 16:00 | 2234 | 13404 | 7.39 | 0.09 | 27.8 | 0.061 | 2.27 | 0.0522 | 2.2996 | 1.85 | 0.6 | 1.25 | 26.1 | 8.22 | 18 | 135 | 16.77 | 20.93 | 23.56 | 6.49 | 67.75 | 1.88 | 16.8 | 7 | BMRL | 14.93 | 13.41 | NA | NA | NA | 40.61 | 54.02 | C12 | Primary | 1998-07-25 | 16:00 | 2450 | 7350 | 7.55 | 0.12 | 31.7 | 0.0433 | 1.51 | 0.0226 | 1.4967 | 1.7 | 0.7 | 1 | 30 | 8.14 | 18 | 100 | 4.38 | 14.05 | 23.18 | 11.23 | 52.84 | 1.41 | 12.61 | 3.44 | BMRL | 15.17 | 11.58 | NA | NA | NA | 32.63 | 44.21
[9 empty] | A12-DUP | Duplicate | 1998-07-25 | 16:00 | 2450 | 7350 | 14700 | 7.45 | 0.1 | 94 | 31.7 | 127 | 108.1 | 0.078 | 108 | 3.39 | 0.0713 | 2.1032 | 3.4 | 0.75 | 2.65 | 30 | 8.28 | 18 | 270 | 39.66 | 34.36 | 23.28 | 3.75 | 101.05 | 3.47 | 36.35 | 22.61 | BMRL | 11.82 | 21.2 | NA | NA | NA | 74.25 | 95.45 | B15-DUP | Duplicate | 1998-07-16 | 16:00 | 2234 | 13404 | 7.35 | 0.09 | 27.8 | 0.058 | 2.29 | 0.0511 | 2.2314 | 1.75 | 0.65 | 1.1 | 26.1 | 8.16 | 18 | 140 | 17.42 | 21.74 | 24.08 | 6.64 | 69.88 | 1.53 | 22.04 | 8.67 | BMRL | 15.15 | 13.81 | NA | NA | NA | 47.39 | 61.2 | C12-DUP | Duplicate | 1998-07-25 | 16:00 | 2450 | 7350 | 7.55 | 0.12 | 31.7 | 0.041 | 1.57 | 0.0247 | 1.5732 | 1.7 | 0.6 | 1.1 | 30 | 8.19 | 18 | 90 | 4.23 | 13.2 | 23.11 | 10.97 | 51.51 | 2.05 | 12.51 | 3.66 | BMRL | 14.93 | 11.05 | NA | NA | NA | 33.15 | 44.2
[10 empty] | Average | --- | --- | --- | --- | --- | 7.445 | 0.095 | 94 | 31.7 | 127 | 107.7 | 0.082 | 109 | 3.355 | 0.0701 | 2.0893 | 3.35 | 0.75 | 2.6 | 30 | 8.185 | 18 | 265 | 38.14 | 33.225 | 22.66 | 3.435 | 97.46 | 4.615 | 35.59 | 23.115 | #DIV/0! | 10.99 | 20.45 | #DIV/0! | #DIV/0! | #DIV/0! | 74.31 | 94.76 |  | Average | --- | --- | --- | --- | 7.37 | 0.09 | 27.8 | 0.0595 | 2.28 | 0.05165 | 2.2655 | 1.8 | 0.625 | 1.175 | 26.1 | 8.19 | 18 | 137.5 | 17.095 | 21.335 | 23.82 | 6.565 | 68.815 | 1.705 | 19.42 | 7.835 | #DIV/0! | 15.04 | 13.61 | #DIV/0! | #DIV/0! | #DIV/0! | 44 | 57.61 |  | Average | --- | --- | --- | --- | 7.55 | 0.12 | 31.7 | 0.04215 | 1.54 | 0.02365 | 1.535 | 1.7 | 0.65 | 1.05 | 30 | 8.165 | 18 | 95 | 4.305 | 13.625 | 23.145 | 11.1 | 52.175 | 1.73 | 12.56 | 3.55 | #DIV/0! | 15.05 | 11.315 | #DIV/0! | #DIV/0! | #DIV/0! | 32.89 | 44.205
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.13432 | 10.5263 | 0 | 0 | 0 | 0.7428 | 9.7561 | 1.8349 | 2.0864 | 3.4237 | 1.3375 | 2.9851 | 0 | 3.8462 | 0 | 2.3213 | 0 | 3.7736 | 7.9706 | 6.8322 | 5.4722 | 18.3406 | 7.3671 | 49.6208 | 4.2709 | 4.3695 | #VALUE! | 15.1046 | 7.335 | #VALUE! | #VALUE! | #VALUE! | 0.16149 | 1.4563 |  | RPD | --- | --- | --- | --- | 0.54274 | 0 | 0 | 5.042 | 0.87719 | 2.1297 | 3.0068 | 5.5556 | 8 | 12.766 | 0 | 0.7326 | 0 | 3.6364 | 3.8023 | 3.7966 | 2.183 | 2.2848 | 3.0953 | 20.5279 | 26.9825 | 21.3146 | #VALUE! | 1.4628 | 2.939 | #VALUE! | #VALUE! | #VALUE! | 15.4091 | 12.4631 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 5.4567 | 3.8961 | 8.8795 | 4.9877 | 0 | 15.3846 | 9.5238 | 0 | 0.61237 | 0 | 10.5263 | 3.4843 | 6.2385 | 0.30244 | 2.3423 | 2.5491 | 36.9942 | 0.79618 | 6.1972 | #VALUE! | 1.5947 | 4.684 | #VALUE! | #VALUE! | #VALUE! | 1.581 | 0.022622
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A6-INST | N | 1998-06-01 | 16:00 | 1154 | 3462 | 6924 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BMRL | 2.769 | 1.028 | BMRL | BMRL | 3.797 | BMRL | BMRL | BMRL | BMRL | BMRL | 2.469 | BMRL | BMRL | BMRL | BMRL | 2.469 | B5-INST | N | 1998-05-07 | 14:00 | 552 | 3312 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BMRL | 1.047 | 1.53 | BMRL | BMRL | 2.577 | 0.278 | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0.278 | 0.278 | C6 - INST | N | 1998-06-01 | 15:00 | 1153 | 3459 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | 0.774 | 1.38 | BMRL | 1.17 | BMRL | 1.1 | BMRL | 0.981 | 3.324 | 3.324
[9 empty] | A8-INST | N | 1998-06-22 | 15:00 | 1657 | 4971 | 9942 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 26 | 4.4 | BMRL | BMRL | BMRL | 4.4 | BMRL | BMRL | BMRL | BMRL | BMRL | 1.25 | BMRL | BMRL | BMRL | BMRL | 1.25 | B13-INST | N | 1998-06-22 | 15:00 | 1657 | 9942 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BMRL | 1.28 | BMRL | 1.21 | BMRL | 2.49 | BMRL | 0.46 | BMRL | BMRL | BMRL | 0.66 | 0.72 | BMRL | BMRL | 0.46 | 1.12 | C8-INST | N | 1998-06-22 | 15:00 | 1657 | 4971 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BMRL | 0.89 | BMRL | BMRL | BMRL | 0.89 | BMRL | BMRL | BMRL | BMRL | BMRL | 2.38 | BMRL | BMRL | BMRL | 0 | 2.38
[9 empty] | A12-INST | N | 1998-07-25 | 16:00 | 2450 | 7350 | 14700 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 31 | 0.589 | 0.389 | 0.083 | BMRL | 1.061 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | BMRL | BMRL | B15-INST | N | 1998-07-16 | 16:00 | 2234 | 13404 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 34 | 0.276 | BMRL | BMRL | BMRL | 0.276 | BMRL | 4.66 | 2.28 | BMRL | BMRL | BMRL | NA | NA | NA | 6.94 | 6.94 | C12-INST | N | 1998-07-25 | 16:00 | 2450 | 7350 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | BMRL | 0.19 | BMRL | BMRL | BMRL | 0.19 | 0.42 | 4.7 | 3.58 | BMRL | BMRL | BMRL | NA | NA | NA | 8.7 | 8.7
[11 empty] | Sampling | Sampling | Operation | Bed | Bed
[11 empty] | date | time | time | volumes | volumes
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute)
[11 empty] | 1998-04-14 | 14:00 | 0 | 0 | 0
[11 empty] | 1998-04-15 | 14:08 | 24.1333 | 72.4 | 144.8
[11 empty] | 1998-04-22 | 11:45 | 189.75 | 569.25 | 1138.5
[11 empty] | 1998-05-04 | 14:00 | 480 | 1440 | 2880
[11 empty] | 1998-05-11 | 14:00 | 648 | 1944 | 3888
[11 empty] | 1998-05-14 | 14:00 | 720 | 2160 | 4320
[11 empty] | 1998-06-01 | 16:00 | 1154 | 3462 | 6924
[11 empty] | 1998-06-01 | 16:00 | 1154 | 3462 | 6924
[11 empty] | 1998-06-04 | 14:00 | 1224 | 3672 | 7344
[11 empty] | 1998-06-12 | 12:00 | 1414 | 4242 | 8484
[11 empty] | 1998-10-29 | 9:30 | 4747.5 | 14242.5 | 28485
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
[13 empty] | -861590 | -2584770 | -5169540
Note on E20: Reviewer M.H. (11/13/99): Carbon particle size verified by consultant since it does not match that reported in the summary report. Per consultant: "The average value of the particle diameter was 1.48 mm (8x30). The 1.0 mm particle diameter reported Table 6 was an approximation of the effective diameter."
Note on AK5: Reviewer M.H. (11/13/99): Per Consultant: "The incubation times (start and end) were measured on a few occasions only. The SDS-incubation period was however kept close to the targets of 18C, and on those occasions for which the period was recorded, incubation times ranged between 18 and 18.5 hours. Measured incubation times were added to the data collection sheets: samples B5, B8, and B9 were incubated for 18.5 hours, while samples B7, and B12 were incubated for 18 hours. The remainder of the SDS-incubation times are target values."
Note on AX5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on AY5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on AZ5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on BV5: Reviewer M.H. (11/13/99): Per Consultant: "The incubation times (start and end) were measured on a few occasions only. The SDS-incubation period was however kept close to the targets of 18C, and on those occasions for which the period was recorded, incubation times ranged between 18 and 18.5 hours. Measured incubation times were added to the data collection sheets: samples B5, B8, and B9 were incubated for 18.5 hours, while samples B7, and B12 were incubated for 18 hours. The remainder of the SDS-incubation times are target values."
Note on CD23: Reviewer M.H. (11/13/99): Per consultant, "No change was made to DCAA value for sample B15."
Note on CI5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on CJ5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on CK5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on DG5: Reviewer M.H. (11/13/99): Per Consultant: "The incubation times (start and end) were measured on a few occasions only. The SDS-incubation period was however kept close to the targets of 18C, and on those occasions for which the period was recorded, incubation times ranged between 18 and 18.5 hours. Measured incubation times were added to the data collection sheets: samples B5, B8, and B9 were incubated for 18.5 hours, while samples B7, and B12 were incubated for 18 hours. The remainder of the SDS-incubation times are target values."
Note on DT5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on DU5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."
Note on DV5: Reviewer M.H. (11/13/99): Per Consultant on why most of the results were reported as NA: "In fields 1-4, 1-5, and 1-6, the results are reported as NA because these 3 HAAs (TBAA, CDBAA, and DCBAA) were not analyzed (since they were not required to be analyzed by the EPA)."