## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2a: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 8 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Pompano Beach | Membrane manufacturer | FLUID SYSTEMS CORP. | Average yearly temperature of feed water, TavgoC (oC) | 29 | Alkalinity (mg/L as CaCO3) | 48 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.47731 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.4877 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.48568 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51392 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.48034 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51392 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4131618 | Membrane trade name | FLUID SYSTEMS | Temperature normalized MTCW (gfd/psi) | 0.12621 | Calcium Hardness (mg/L as CaCO3) | 250 | Cartridge filtration | 1 micron | Pilot - scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 18.29 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.73 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.29 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.92 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.56 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.16 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.24 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.86 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.55 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.24 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.86 |  |  |  |  | Capital Recovery Interest Rate (%) | 3
Water Industry Data Base Number (optional) |  | Membrane element model number | 2540 TFCS / 4921 TFCS |  |  | LSI | 0.3 | sulfuric acid addition | pH = 5.7, Dosage= 42 mg/L | Pilot - scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 18.29 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.29 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.29 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.29 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.56 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.86 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.24 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.24 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.24 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.24 |  |  |  |  | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.1 |  |  |  | 1998-05-24 | 9:00 | 0 | 29 | 139.545 | 49.042 | 19.642 | 0 | 15.658 | 4.277 |  | 19.935 | 19.935 | 0.78545 | 0 | 14.2345 | 14.2345 | 6.6646 | 67.9869 | 0.20937 | 8.139 | 5.735 | 45.1435 | 305.9856 | 280.6003 | 1898.1 | 1142.6024 | 39.8028 | 83.9118 | 711.6014 | 93.6561 | 139.545 | 121.35 | 19.642 | 9.336 | 10.776 | 20.112 | 20.112 | 0.41199 | 0.4642 | 14.1813 | 14.1813 | 3.709 | 107.0965 | 0.13242 | 5.735 | 7.505 | 21.8079 | 280.6003 | 540.45 | 504.8102 | 6.5945 | 92.2281 | 392.7053 | 94.4468 | 121.35 | 100.367 | 19.642 | 5.061 | 5.715 | 10.776 | 10.776 | 0.43992 | 0.46965 | 15.3752 | 15.3752 | 7.3224 | 83.8941 | 0.18327 | 5.735 | 7.505 | 32.9303 | 540.45 | 979.65 | 989.8914 | -1.0454 | 88.2644 | 765.1707 | 95.6964 | 100.367 | 49.042 | 19.642 | 1.438 | 4.277 | 5.715 | 5.715 | 0.19991 | 0.25162 | 12.7822 | 12.7822 | 9.546 | 45.5165 | 0.28083 | 7.505 | 7.505 | 162.429 | 979.65 | 1898.1 | 1254.4136 | 33.9121 | 42.1138 | 1117.0318 | 85.4589 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Design system recovery, R (decimal) | 0.82 | Total iron (mg/L) | 0.3 |  |  |  | 1998-05-24 | 17:00 | 8 | 29 | 142.29 | 51.54 | 19.33 | 0 | 13.495 | 4.155 |  | 17.65 | 17.65 | 0.76459 | 0 | 12.2682 | 12.2682 | 6.6847 | 70.9003 | 0.17303 | 8.175 | 5.689 | 39.399 | 301.584 | 294.155 | 1698.6 | 1121.5753 | 33.9706 | 86.606 | 707.8652 | 94.4341 | 142.29 | 124.042 | 19.33 | 9.095 | 10.718 | 19.813 | 19.813 | 0.40723 | 0.45904 | 13.8152 | 13.8152 | 3.9012 | 109.9348 | 0.12567 | 5.689 | 7.471 | 20.2516 | 294.155 | 537.75 | 526.5818 | 2.0768 | 93.1153 | 410.3684 | 95.065 | 124.042 | 100.307 | 19.33 | 5.004 | 5.714 | 10.718 | 10.718 | 0.43835 | 0.46688 | 15.202 | 15.202 | 7.251 | 85.5935 | 0.17761 | 5.689 | 7.471 | 33.465 | 537.75 | 961.2 | 979.3745 | -1.8908 | 88.6233 | 758.5622 | 95.5884 | 100.307 | 51.54 | 19.33 | 1.559 | 4.155 | 5.714 | 5.714 | 0.19745 | 0.27284 | 13.8578 | 13.8578 | 9.7742 | 46.8193 | 0.29598 | 7.471 | 7.471 | 138.185 | 961.2 | 1698.6 | 1270.0039 | 25.2323 | 53.0231 | 1115.602 | 87.6134 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Design average system flux, FW (gfd) | 14 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-05-24 | 21:24 | 12.4078 | 29 | 118.927 | 44.722 | 17.242 | 0 | 14.035 | 4.037 |  | 18.072 | 18.072 | 0.77662 | 0 | 12.7591 | 12.7591 | 6.9073 | 57.6752 | 0.22122 | 7.961 | 5.601 | 42.676 | 302.304 | 294.9258 | 1746.1 | 1171.8955 | 32.885 | 85.5299 | 733.4107 | 94.1812 | 118.927 | 105.225 | 17.242 | 8.074 | 9.458 | 17.532 | 17.532 | 0.36 | 0.46053 | 12.2643 | 12.2643 | 3.8961 | 90.9379 | 0.13486 | 5.601 | 7.365 | 21.867 | 294.9258 | 529.2 | 528.0277 | 0.22153 | 92.5856 | 411.4768 | 94.6857 | 105.225 | 100.255 | 17.242 | 4.282 | 5.176 | 9.458 | 9.458 | 0.39038 | 0.45274 | 13.0086 | 13.0086 | 7.0313 | 78.4667 | 0.16579 | 5.601 | 7.365 | 31.809 | 529.2 | 932.85 | 940.6815 | -0.83952 | 89.2146 | 734.9408 | 95.6719 | 100.255 | 44.722 | 17.242 | 1.139 | 4.037 | 5.176 | 5.176 | 0.18433 | 0.22005 | 10.1244 | 10.1244 | 9.0315 | 46.215 | 0.21907 | 7.365 | 7.365 | 141.3605 | 932.85 | 1746.1 | 1156.161 | 33.7861 | 52.0691 | 1044.5055 | 86.4663 | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 (dup) | CF-sys-8 (dup) | CC-sys-8 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 (dup) | CI-s1-8 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25
|  | Membrane hydrophobicity | HYDRPHILIC | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | 0 |  |  |  | 1998-05-25 | 5:00 | 20 | 29 | 123.022 | 46.155 | 17.638 | 0 | 15.057 | 3.375 |  | 18.432 | 18.432 | 0.81689 | 0 | 13.6882 | 13.6882 | 8.1079 | 58.8426 | 0.23262 | 7.412 | 5.647 | 39.2685 | 293.616 | 290.2363 | 1626.4 | 1409.8874 | 13.3124 | 86.4702 | 850.0619 | 95.3805 | 123.022 | 108.727 | 17.638 | 8.491 | 8.919 | 17.41 | 17.41 | 0.35118 | 0.48771 | 12.8977 | 12.8977 | 3.9786 | 94.2579 | 0.13683 | 5.647 | 7.337 | 20.685 | 290.2363 | 512.1 | 546.8526 | -6.7863 | 92.873 | 418.5444 | 95.0579 | 108.727 | 100.36 | 17.638 | 4.344 | 4.575 | 8.919 | 8.919 | 0.35997 | 0.48705 | 13.197 | 13.197 | 7.1059 | 79.7996 | 0.16538 | 5.647 | 7.337 | 30.2623 | 512.1 | 892.35 | 969.6089 | -8.6579 | 89.5732 | 740.8544 | 95.9152 | 100.36 | 46.155 | 17.638 | 1.2 | 3.375 | 4.575 | 4.575 | 0.15906 | 0.2623 | 10.6667 | 10.6667 | 9.0072 | 46.6123 | 0.22884 | 7.337 | 7.337 | 127.5855 | 892.35 | 1626.4 | 1164.2663 | 28.4145 | 56.0408 | 1028.3081 | 87.5927 | Sampling date | MM/DD/YY | 1998-05-27 | 1998-05-27 | 1998-05-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-27 | 1998-05-27 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | 1998-07-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | 1998-07-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 7
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.1 |  |  |  | 1998-05-25 | 13:00 | 28 | 29 | 134.512 | 51.052 | 18.739 | 0 | 14.994 | 3.247 |  | 18.241 | 18.241 | 0.82199 | 0 | 13.6309 | 13.6309 | 8.4444 | 65.5986 | 0.20779 | 7.336 | 5.685 | 39.0805 | 300.864 | 294.2834 | 1616.9 | 1472.7598 | 8.9146 | 86.7201 | 883.5216 | 95.5767 | 134.512 | 117.975 | 18.739 | 8.977 | 9.327 | 18.304 | 18.304 | 0.36855 | 0.49044 | 13.6359 | 13.6359 | 4.0579 | 103.4466 | 0.13182 | 5.685 | 7.399 | 20.3304 | 294.2834 | 530.55 | 557.9563 | -5.1656 | 93.0916 | 426.1199 | 95.2289 | 117.975 | 100.262 | 18.739 | 4.703 | 4.624 | 9.327 | 9.327 | 0.37216 | 0.50424 | 14.2876 | 14.2876 | 7.5232 | 82.8563 | 0.17244 | 5.685 | 7.399 | 31.8435 | 530.55 | 930.6 | 1037.7768 | -11.517 | 89.1793 | 784.1634 | 95.9392 | 100.262 | 51.052 | 18.739 | 1.377 | 3.247 | 4.624 | 4.624 | 0.15748 | 0.29779 | 12.24 | 12.24 | 9.7153 | 47.2027 | 0.25931 | 7.399 | 7.399 | 129.0355 | 930.6 | 1616.9 | 1270.5305 | 21.4218 | 56.1526 | 1100.5652 | 88.2755 | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 3391
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-05-25 | 21:00 | 36 | 29 | 134.025 | 51.367 | 18.642 | 0 | 14.935 | 3.313 |  | 18.248 | 18.248 | 0.81845 | 0 | 13.5773 | 13.5773 | 8.33 | 65.724 | 0.20658 | 6.887 | 5.722 | 38.5165 | 302.304 | 294.5083 | 1594.1 | 1448.5189 | 9.1325 | 86.9218 | 871.5136 | 95.5805 | 134.025 | 117.795 | 18.642 | 8.975 | 9.332 | 18.307 | 18.307 | 0.36865 | 0.49025 | 13.6329 | 13.6329 | 4.0681 | 103.1999 | 0.1321 | 5.722 | 7.417 | 19.7985 | 294.5083 | 529.2 | 558.7089 | -5.5761 | 93.2774 | 426.6086 | 95.3591 | 117.795 | 100.247 | 18.642 | 4.642 | 4.69 | 9.332 | 9.332 | 0.37406 | 0.49743 | 14.1023 | 14.1023 | 7.4353 | 82.9437 | 0.17002 | 5.722 | 7.417 | 31.8148 | 529.2 | 928.8 | 1021.4947 | -9.9801 | 89.1973 | 775.3474 | 95.8967 | 100.247 | 51.367 | 18.642 | 1.377 | 3.313 | 4.69 | 4.69 | 0.16012 | 0.2936 | 12.24 | 12.24 | 9.6704 | 47.4946 | 0.25771 | 7.417 | 7.417 | 128.151 | 928.8 | 1594.1 | 1261.578 | 20.8595 | 56.4865 | 1095.189 | 88.2987 | Operation time | hh.hh | 72.17 | 72.17 | 72.17 | --- | --- | --- | --- | --- | Operation time | hh.hh | 72.17 | 72.17 | --- | --- | --- | --- | Operation time | hh.hh | 370.42 | 370.42 | 370.42 | --- | --- | --- | --- | --- | Operation time | hh.hh | 370.42 | 370.42 | --- | --- | --- | --- | Operation time | hh.hh | 716.21 | 716.21 | 716.21 | --- | --- | --- | --- | --- | Operation time | hh.hh | 716.21 | 716.21 | --- | --- | --- | --- | Operation time | hh.hh | 1056 | 1056 | 1056 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1056 | 1056 | --- | --- | --- | --- | Operation time | hh.hh | 1416 | 1416 | 1416 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1416 | 1416 | --- | --- | --- | --- | Operation time | hh.hh | 1056 | 1056 | 1056 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1056 | 1056 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 267.13
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 8.9 |  |  |  | 1998-05-26 | 5:00 | 44 | 29 | 133.92 | 51.42 | 18.636 | 0 | 14.994 | 3.198 |  | 18.192 | 18.192 | 0.82421 | 0 | 13.6309 | 13.6309 | 8.5578 | 65.4762 | 0.20818 | 6.83 | 5.697 | 38.4225 | 302.352 | 294.3156 | 1592.2 | 1494.0843 | 6.1623 | 86.9451 | 894.1999 | 95.7031 | 133.92 | 117.577 | 18.636 | 8.973 | 9.16 | 18.133 | 18.133 | 0.36404 | 0.49484 | 13.6299 | 13.6299 | 4.0921 | 103.0204 | 0.1323 | 5.697 | 7.426 | 19.6409 | 294.3156 | 528.3 | 563.3828 | -6.6407 | 93.3266 | 428.8492 | 95.4201 | 117.577 | 100.352 | 18.636 | 4.643 | 4.517 | 9.16 | 9.16 | 0.36485 | 0.50688 | 14.1053 | 14.1053 | 7.5152 | 82.8133 | 0.17033 | 5.697 | 7.426 | 31.901 | 528.3 | 931.95 | 1038.5459 | -11.4379 | 89.161 | 783.4229 | 95.928 | 100.352 | 51.42 | 18.636 | 1.319 | 3.198 | 4.517 | 4.517 | 0.15436 | 0.29201 | 11.7244 | 11.7244 | 9.6981 | 47.5519 | 0.24656 | 7.426 | 7.426 | 127.948 | 931.95 | 1592.2 | 1263.5568 | 20.6408 | 56.5269 | 1097.7534 | 88.3446 | pH | --- | 5.6 | 5.7 | 6.44 | --- | --- | --- | --- | --- | pH | --- | 5.62 | 5.7 | --- | --- | --- | --- | pH | --- | 6.51 | 6.1 | 6.32 | --- | --- | --- | --- | --- | pH | --- | 5.91 | 6.1 | --- | --- | --- | --- | pH | --- | 5.31 | 5.91 | 6.38 | --- | --- | --- | --- | --- | pH | --- | 5.45 | 5.91 | --- | --- | --- | --- | pH | --- | 5.29 | 5.92 | 6.25 | --- | --- | --- | --- | --- | pH | --- | 5.3 | 5.92 | --- | --- | --- | --- | pH | --- | 5.34 | 5.79 | 6.2 | --- | --- | --- | --- | --- | pH | --- | 5.34 | 5.79 | --- | --- | --- | --- | pH | --- | 5.29 | 5.77 | 6.24 | --- | --- | --- | --- | --- | pH | --- | 5.48 | 5.77 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 25
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.76806 | Calcium (mg/L) | 252 |  |  |  | 1998-05-26 | 13:00 | 52 | 29 | 134.032 | 51.855 | 18.688 | 0 | 15.06 | 3.375 |  | 18.435 | 18.435 | 0.81692 | 0 | 13.6909 | 13.6909 | 8.2716 | 65.9839 | 0.20749 | 6.775 | 5.704 | 38.1875 | 301.584 | 294.1871 | 1580.8 | 1436.5141 | 9.1274 | 87.0193 | 865.3506 | 95.587 | 134.032 | 117.555 | 18.688 | 8.974 | 9.395 | 18.369 | 18.369 | 0.37032 | 0.48854 | 13.6314 | 13.6314 | 4.0578 | 103.0477 | 0.13228 | 5.704 | 7.428 | 19.5621 | 294.1871 | 530.1 | 556.5058 | -4.9813 | 93.3505 | 425.3465 | 95.4009 | 117.555 | 100.24 | 18.688 | 4.642 | 4.753 | 9.395 | 9.395 | 0.37742 | 0.49409 | 14.1023 | 14.1023 | 7.4174 | 82.7921 | 0.17033 | 5.704 | 7.428 | 31.7285 | 530.1 | 926.1 | 1016.8327 | -9.7973 | 89.2149 | 773.4663 | 95.8979 | 100.24 | 51.855 | 18.688 | 1.378 | 3.375 | 4.753 | 4.753 | 0.16262 | 0.28992 | 12.2489 | 12.2489 | 9.6289 | 47.7306 | 0.25663 | 7.428 | 7.428 | 126.4545 | 926.1 | 1580.8 | 1252.5923 | 20.7621 | 57.0156 | 1089.3461 | 88.3917 | Temperature | oC | 29 | 29 | 20.7 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 79 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.6083 | Barium (mg/L) | 0.049 |  |  |  | 1998-05-26 | 21:00 | 60 | 29 | 133.612 | 52.072 | 18.717 | 0 | 14.999 | 3.247 |  | 18.246 | 18.246 | 0.82204 | 0 | 13.6355 | 13.6355 | 8.4846 | 65.6404 | 0.20773 | 6.611 | 5.709 | 38.117 | 302.256 | 294.4762 | 1578.9 | 1478.6865 | 6.347 | 87.056 | 886.5813 | 95.7007 | 133.612 | 117.345 | 18.717 | 9.039 | 9.268 | 18.307 | 18.307 | 0.3678 | 0.49375 | 13.7301 | 13.7301 | 4.0918 | 102.6697 | 0.13373 | 5.709 | 7.437 | 19.4242 | 294.4762 | 530.55 | 562.732 | -6.0658 | 93.4038 | 428.6041 | 95.468 | 117.345 | 100.24 | 18.717 | 4.643 | 4.625 | 9.268 | 9.268 | 0.37061 | 0.50097 | 14.1053 | 14.1053 | 7.4908 | 82.5847 | 0.1708 | 5.709 | 7.437 | 31.809 | 530.55 | 932.85 | 1031.232 | -10.5464 | 89.1981 | 780.891 | 95.9266 | 100.24 | 52.072 | 18.717 | 1.378 | 3.247 | 4.625 | 4.625 | 0.1575 | 0.29795 | 12.2489 | 12.2489 | 9.7763 | 47.6627 | 0.25699 | 7.437 | 7.437 | 126.353 | 932.85 | 1578.9 | 1275.1207 | 19.2399 | 57.0923 | 1103.9853 | 88.5548 | Alkalinity | mg/L as CaCO3 | 22 | 70 | 306 | 274.6316 | 10.2511 | 68.5714 | 172.3158 | 87.2327 | Alkalinity | mg/L as CaCO3 | 26 | 70 | 110.1799 | 62.8571 | 90.09 | 71.14 | Alkalinity | mg/L as CaCO3 | 18 | 72 | 316 | 302.2105 | 4.3638 | 75 | 187.1053 | 90.3797 | Alkalinity | mg/L as CaCO3 | 18 | 72 | 123.4066 | 75 | 97.7033 | 81.5769 | Alkalinity | mg/L as CaCO3 | 16 | 64 | 306 | 256 | 16.3399 | 75 | 160 | 90 | Alkalinity | mg/L as CaCO3 | 14 | 64 | 111.2165 | 78.125 | 87.6082 | 84.0198 | Alkalinity | mg/L as CaCO3 | 14 | 58 | 400 | 272.8235 | 31.7941 | 75.8621 | 165.4118 | 91.5363 | Alkalinity | mg/L as CaCO3 | 10 | 58 | 108.7494 | 82.7586 | 83.3747 | 88.006 | Alkalinity | mg/L as CaCO3 | 20 | 52 | 200 | 180 | 10 | 61.5385 | 116 | 82.7586 | Alkalinity | mg/L as CaCO3 | 16 | 52 | 85.2757 | 69.2308 | 68.6378 | 76.6892 | Alkalinity | mg/L as CaCO3 | 16 | 54 | 396 | 239.5294 | 39.5128 | 70.3704 | 146.7647 | 89.0982 | Alkalinity | mg/L as CaCO3 | 10 | 54 | 100.5203 | 81.4815 | 77.2601 | 87.0567 | Electric Rate ($/kW-h) | 0.07
Mailing Address |  | Design flux, FW (gfd) | 17.9 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.2167 | Strontium (mg/L) | 0.4 |  |  |  | 1998-05-27 | 5:00 | 68 | 29 | 134.04 | 52.05 | 18.765 | 0 | 14.697 | 3.307 |  | 18.004 | 18.004 | 0.81632 | 0 | 13.3609 | 13.3609 | 8.259 | 66.021 | 0.20237 | 6.534 | 5.697 | 38.023 | 302.16 | 294.3477 | 1558 | 1433.5082 | 7.9905 | 87.0823 | 863.9279 | 95.5988 | 134.04 | 117.525 | 18.765 | 9.036 | 9.27 | 18.306 | 18.306 | 0.36781 | 0.49361 | 13.7256 | 13.7256 | 4.0903 | 102.9272 | 0.13335 | 5.697 | 7.426 | 19.3454 | 294.3477 | 532.35 | 562.4082 | -5.6463 | 93.4277 | 428.3779 | 95.484 | 117.525 | 100.315 | 18.765 | 4.644 | 4.626 | 9.27 | 9.27 | 0.37069 | 0.50097 | 14.1084 | 14.1084 | 7.5165 | 82.6385 | 0.17072 | 5.697 | 7.426 | 31.901 | 532.35 | 931.95 | 1034.7463 | -11.0302 | 89.1621 | 783.5481 | 95.9286 | 100.315 | 52.05 | 18.765 | 1.319 | 3.307 | 4.626 | 4.626 | 0.15872 | 0.28513 | 11.7244 | 11.7244 | 9.666 | 47.7515 | 0.24553 | 7.426 | 7.426 | 126.063 | 931.95 | 1558 | 1253.3788 | 19.5521 | 57.1721 | 1092.6644 | 88.4628 | Total dissolved solids | mg/L | 38.5 | 294 | 1596 | 1383.2368 | 13.331 | 86.9048 | 838.6184 | 95.4091 | Total dissolved solids | mg/L | 18.4 | 294 | 545.6724 | 93.7415 | 419.8362 | 95.6173 | Total dissolved solids | mg/L | 36 | 293.7 | 1473 | 1392.3158 | 5.4775 | 87.7426 | 843.0079 | 95.7296 | Total dissolved solids | mg/L | 17.8 | 293.7 | 556.3497 | 93.9394 | 425.0249 | 95.812 | Total dissolved solids | mg/L | 33.8 | 285 | 1333 | 1289.8 | 3.2408 | 88.1404 | 787.4 | 95.7074 | Total dissolved solids | mg/L | 17.3 | 285 | 537.7971 | 93.9298 | 411.3986 | 95.7948 | Total dissolved solids | mg/L | 36.7 | 291 | 1452 | 1532.5824 | -5.5497 | 87.3883 | 911.7912 | 95.975 | Total dissolved solids | mg/L | 19 | 291 | 578.58 | 93.4708 | 434.79 | 95.6301 | Total dissolved solids | mg/L | 39.3 | 305.3 | 1306 | 1369.3 | -4.8469 | 87.1274 | 837.3 | 95.3063 | Total dissolved solids | mg/L | 18.9 | 305.3 | 570.0265 | 93.8094 | 437.6632 | 95.6816 | Total dissolved solids | mg/L | 36.7 | 291 | 1452 | 1532.5824 | -5.5497 | 87.3883 | 911.7912 | 95.975 | Total dissolved solids | mg/L | 19 | 291 | 578.58 | 93.4708 | 434.79 | 95.6301 | Fuel Oil Rate ($/gal) | 0.89
|  | Net driving pressure at the design flux, NDP (psi) | 80 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.6083 | Reactive silica (mg/L as SiO2) | 6.29 |  |  |  | 1998-05-27 | 13:00 | 76 | 29 | 132.57 | 52.035 | 18.387 | 0 | 14.819 | 3.672 |  | 18.491 | 18.491 | 0.80142 | 0 | 13.4718 | 13.4718 | 7.7111 | 66.2044 | 0.20349 | 6.441 | 5.713 | 38.54 | 301.44 | 294.0586 | 1596 | 1325.2487 | 16.9644 | 86.8938 | 809.6537 | 95.2399 | 132.57 | 116.235 | 18.387 | 8.734 | 9.635 | 18.369 | 18.369 | 0.37352 | 0.47547 | 13.2668 | 13.2668 | 3.9902 | 102.0253 | 0.13003 | 5.713 | 7.431 | 19.4833 | 294.0586 | 533.25 | 542.9575 | -1.8204 | 93.3743 | 418.508 | 95.3446 | 116.235 | 100.3 | 18.387 | 4.643 | 4.992 | 9.635 | 9.635 | 0.3902 | 0.48189 | 14.1053 | 14.1053 | 7.3448 | 82.5357 | 0.1709 | 5.713 | 7.431 | 31.9125 | 533.25 | 933.3 | 999.5381 | -7.0972 | 89.1476 | 766.394 | 95.836 | 100.3 | 52.035 | 18.387 | 1.32 | 3.672 | 4.992 | 4.992 | 0.17334 | 0.26442 | 11.7333 | 11.7333 | 9.5103 | 48.2702 | 0.24308 | 7.431 | 7.431 | 127.165 | 933.3 | 1596 | 1223.0871 | 23.3655 | 56.7552 | 1078.1935 | 88.2057 | Total hardness | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 14 | 304 | 568.8222 | #VALUE! | 436.4111 | 96.792 | Total hardness | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 16 | 268 | 507.8975 | #VALUE! | 387.9488 | 95.8757 | Total hardness | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 14 | 274 | 519.5258 | #VALUE! | 396.7629 | 96.4714 | Total hardness | mg/L as CaCO3 | NR | NR | NR | 1715.8824 | 29.677 | 96.6667 | 1007.9412 | 99.0079 | Total hardness | mg/L as CaCO3 | 8 | 300 | 608.7255 | 97.3333 | 454.3628 | 98.2393 | Total hardness | mg/L as CaCO3 | NR | NR | NR | 1296 | 17.9747 | 90.7143 | 788 | 96.7005 | Total hardness | mg/L as CaCO3 | 18 | 280 | 522.173 | 93.5714 | 401.0865 | 95.5122 | Total hardness | mg/L as CaCO3 | NR | NR | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 12 | 282 | 567.4654 | #VALUE! | 424.7327 | 97.1747 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.8433 | Turbidity (ntu) | 0.24 |  |  |  | 1998-05-27 | 21:00 | 84 | 29 | 133.267 | 52.11 | 18.415 | 0 | 14.638 | 3.493 |  | 18.131 | 18.131 | 0.80735 | 0 | 13.3073 | 13.3073 | 7.9393 | 66.3342 | 0.20061 | 5.816 | 5.685 | 38.0465 | 302.592 | 294.5404 | 1577 | 1369.4209 | 13.1629 | 87.0828 | 831.9807 | 95.427 | 133.267 | 116.947 | 18.415 | 8.798 | 9.514 | 18.312 | 18.312 | 0.37115 | 0.48045 | 13.3641 | 13.3641 | 4.0241 | 102.6679 | 0.13017 | 5.685 | 7.428 | 19.3651 | 294.5404 | 532.35 | 549.0067 | -3.1289 | 93.4253 | 421.7735 | 95.4086 | 116.947 | 100.33 | 18.415 | 4.644 | 4.87 | 9.514 | 9.514 | 0.38371 | 0.48812 | 14.1084 | 14.1084 | 7.3891 | 82.8344 | 0.17032 | 5.685 | 7.428 | 32.0045 | 532.35 | 936.45 | 1009.4762 | -7.7982 | 89.1341 | 770.9131 | 95.8485 | 100.33 | 52.11 | 18.415 | 1.377 | 3.493 | 4.87 | 4.87 | 0.16732 | 0.28275 | 12.24 | 12.24 | 9.7102 | 48.0948 | 0.2545 | 7.428 | 7.428 | 125.309 | 936.45 | 1577 | 1256.2156 | 20.3414 | 57.4561 | 1096.3328 | 88.5702 | Calcium hardness | mg/L as CaCO3 | 22 | 270 | 1460 | 1327.2632 | 9.0916 | 91.8519 | 798.6316 | 97.2453 | Calcium hardness | mg/L as CaCO3 | 12 | 270 | 505.6004 | 95.5556 | 387.8002 | 96.9056 | Calcium hardness | mg/L as CaCO3 | 18 | 258 | 1500 | 1281.1579 | 14.5895 | 93.0233 | 769.5789 | 97.6611 | Calcium hardness | mg/L as CaCO3 | 12 | 258 | 492.1857 | 95.3488 | 375.0928 | 96.8008 | Calcium hardness | mg/L as CaCO3 | 14 | 254 | 1500 | 1214 | 19.0667 | 94.4882 | 734 | 98.0926 | Calcium hardness | mg/L as CaCO3 | 12 | 254 | 482.5278 | 95.2756 | 368.2639 | 96.7415 | Calcium hardness | mg/L as CaCO3 | 6 | 264 | 2310 | 1523.6471 | 34.0413 | 97.7273 | 893.8235 | 99.3287 | Calcium hardness | mg/L as CaCO3 | 6 | 264 | 536.778 | 97.7273 | 400.389 | 98.5015 | Calcium hardness | mg/L as CaCO3 | 22 | 264 | 1560 | 1232 | 21.0256 | 91.6667 | 748 | 97.0588 | Calcium hardness | mg/L as CaCO3 | 14 | 264 | 495.0811 | 94.697 | 379.5405 | 96.3113 | Calcium hardness | mg/L as CaCO3 | 12 | 256 | 2050 | 1447.2941 | 29.4003 | 95.3125 | 851.6471 | 98.591 | Calcium hardness | mg/L as CaCO3 | 10 | 256 | 516.0907 | 96.0938 | 386.0453 | 97.4096 | Current Process Water Rate ($/1000 gal) | 0.95
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Permeate flow rate from system, Qp-sys (gpm) | 15.6683 | SDI | 2.5 |  |  |  | 1998-05-28 | 5:00 | 92 | 29 | 132.772 | 52.23 | 18.397 | 0 | 15.09 | 3.92 |  | 19.01 | 19.01 | 0.79379 | 0 | 13.7182 | 13.7182 | 7.5231 | 66.5809 | 0.20604 | 6.436 | 5.698 | 37.6705 | 303.072 | 294.8937 | 1559.9 | 1285.0719 | 17.6183 | 87.2257 | 789.9828 | 95.2315 | 132.772 | 116.407 | 18.397 | 8.734 | 9.824 | 18.558 | 18.558 | 0.37856 | 0.47063 | 13.2668 | 13.2668 | 3.9798 | 102.2127 | 0.1298 | 5.698 | 7.416 | 19.3848 | 294.8937 | 532.35 | 539.8342 | -1.4059 | 93.4265 | 417.3639 | 95.3554 | 116.407 | 100.36 | 18.397 | 4.585 | 5.239 | 9.824 | 9.824 | 0.40183 | 0.46671 | 13.9291 | 13.9291 | 7.1943 | 82.7922 | 0.16824 | 5.698 | 7.416 | 31.9067 | 532.35 | 932.4 | 970.3214 | -4.0671 | 89.1803 | 751.3357 | 95.7533 | 100.36 | 52.23 | 18.397 | 1.319 | 3.92 | 5.239 | 5.239 | 0.18325 | 0.25177 | 11.7244 | 11.7244 | 9.4435 | 48.4545 | 0.24197 | 7.416 | 7.416 | 124.0475 | 932.4 | 1559.9 | 1204.3941 | 22.7903 | 57.9348 | 1068.3971 | 88.3894 | Turbidity | ntu | 0.08 | 0.32 | 16.3 | 1.3432 | 91.7598 | 75 | 0.83158 | 90.3797 | Turbidity | ntu | 0.12 | 0.32 | 0.50264 | 62.5 | 0.41132 | 70.8255 | Turbidity | ntu | 0.09 | 0.25 | 18.3 | 0.93211 | 94.9065 | 64 | 0.59105 | 84.7729 | Turbidity | ntu | 0.08 | 0.25 | 0.41184 | 68 | 0.33092 | 75.8248 | Turbidity | ntu | 0.8 | 2.52 | 2.06 | 9.4 | -356.3107 | 68.254 | 5.96 | 86.5772 | Turbidity | ntu | 0.25 | 2.52 | 4.6636 | 90.0794 | 3.5918 | 93.0397 | Turbidity | ntu | 0.3 | 0.89 | 27.5 | 3.7706 | 86.2888 | 66.2921 | 2.3303 | 87.1261 | Turbidity | ntu | 0.19 | 0.89 | 1.6301 | 78.6517 | 1.26 | 84.9212 | Turbidity | ntu | 0.46 | 52 | 10.8 | 258.16 | -2290.3704 | 99.1154 | 155.08 | 99.7034 | Turbidity | ntu | 0.42 | 52 | 99.6766 | 99.1923 | 75.8383 | 99.4462 | Turbidity | ntu | 0.33 | 1.15 | 84.7 | 5.1535 | 93.9155 | 71.3043 | 3.1518 | 89.5297 | Turbidity | ntu | 0.59 | 1.15 | 1.7421 | 48.6957 | 1.446 | 59.1989 | Modifications to Existing Plant (% of construction costs) | 75
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | Feed flow rate to system, QF-sys (gpm) | 19.1077 | MFI | 0 |  |  |  | 1998-05-28 | 11:00 | 98 | 29 | 131 | 56 | 19 | 0 | 15 | NR |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 13.6364 | 13.6364 | #VALUE! | #VALUE! | #VALUE! | 8.41 | 5.78 | 40.185 | 302.544 | 294.2192 | 1381.3 | #VALUE! | #VALUE! | 86.3418 | #VALUE! | #VALUE! | 131 | 115 | 18.1 | 9.06 | 9.48 | 18.54 | 18.54 | 0.37374 | 0.48867 | 13.762 | 13.762 | 4.0349 | 100.8651 | 0.13644 | 5.789 | 7.373 | 21.1972 | 294.2192 | 514.8 | 555.1453 | -7.8371 | 92.7954 | 424.6822 | 95.0087 | 116.5 | 56.252 | 9.957 | 4.67 | 4.82 | 9.49 | 9.49 | 0.38174 | 0.4921 | 14.1873 | 14.1873 | 5.6275 | 70.7915 | 0.20041 | 5.789 | 7.373 | 135.7 | 514.8 | 1348.6 | 882.1023 | 34.5913 | 53.8779 | 698.4511 | 80.5713 | 100.3 | 52 | 9.957 | 1.32 | 3.75 | 5.07 | 5.07 | 0.17646 | 0.26036 | 11.7333 | 11.7333 | 9.0163 | 57.1767 | 0.20521 | 7.373 | 7.373 | 111.708 | 878.4 | 1381.3 | 1148.2756 | 16.8699 | 62.0324 | 1013.3378 | 88.9762 | Ammonia | mg NH3-N / L | 0.24 | 0.65 | 2.1 | 2.3979 | -14.1855 | 63.0769 | 1.5239 | 84.2514 | Total organic carbon | mg/L | 1.76 | 14.6 | 26.3252 | 87.9452 | 20.4626 | 91.3989 | Ammonia | mg NH3-N / L | 0.176 | 0.63 | 2.02 | 2.5655 | -27.0036 | 72.0635 | 1.5977 | 88.9844 | Total organic carbon | mg/L | BMRL | 13.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.12 | 0.69 | 2.34 | 2.97 | -26.9231 | 82.6087 | 1.83 | 93.4426 | Total organic carbon | mg/L | 7.69 | 10.6 | 13.348 | 27.4528 | 11.974 | 35.7775 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1 | 18.4 | 36.7967 | 91.9355 | 27.5983 | 96.3766 | Ammonia | mg NH3-N / L | 0.3 | 0.69 | 2.34 | 2.25 | 3.8462 | 56.5217 | 1.47 | 79.5918 | Total organic carbon | mg/L | 2.41 | 12.4 | 21.634 | 80.5645 | 17.017 | 85.8377 | Ammonia | mg NH3-N / L | NA | NA | 2.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.12 | 18.7 | 37.287 | 94.0107 | 27.9935 | 95.9991
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Concentrate-waste flow rate from system, QW-sys (gpm) | 3.4394 | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-05-28 | 15:30 | 102.5 | 29 | 131 | 56 | 19.5 | 0 | 14.521 | NR |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 13.2009 | 13.2009 | #VALUE! | #VALUE! | #VALUE! | 8.28 | 5.79 | NR | 302.592 | 294.2513 | 1514.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 131 | 115.3 | 18.4 | 9.05 | 9.62 | 18.67 | 18.67 | 0.37734 | 0.48473 | 13.7468 | 13.7468 | 3.9634 | 100.7866 | 0.1364 | 5.802 | 7.361 | 24.7 | 294.2513 | 760 | 547.8313 | 27.9169 | 91.6058 | 421.0413 | 94.1336 | 116.2 | 56.08 | 9.958 | 4.6 | 4.86 | 9.46 | 9.46 | 0.38201 | 0.48626 | 13.9747 | 13.9747 | 9.2903 | 66.8917 | 0.20892 | 5.802 | 7.361 | 139.5 | 770.1 | 1351.8 | 1366.9642 | -1.1218 | 52.5915 | 1068.5321 | 86.9447 | 100.4 | 52.1 | 9.958 | 1.32 | 3.64 | 4.96 | 4.96 | 0.17206 | 0.26613 | 11.7333 | 11.7333 | 6.9296 | 59.3624 | 0.19766 | 7.361 | 7.361 | 158.601 | 745.2 | 1514.3 | 957.9227 | 36.7415 | 46.1002 | 851.5614 | 81.3753 | Total organic carbon | mg/L | BMRL | 14.6 | 88.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.693 | 1.3167 | 98.557 | 1.0049 | 99.0048 | Total organic carbon | mg/L | 3.07 | 13.6 | 64.6 | 58.4911 | 9.4566 | 77.4265 | 36.0455 | 91.483 | UV254 | cm-1 | 0.013 | 0.541 | 1.0436 | 97.597 | 0.79232 | 98.3593 | Total organic carbon | mg/L | BMRL | 10.6 | 64.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.015 | 0.505 | 0.96772 | 97.0297 | 0.73636 | 97.963 | Total organic carbon | mg/L | BMRL | 12.4 | 90.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.538 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 12.4 | 57.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.427 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 5.54 | 18.7 | 97.4 | 82.9518 | 14.8339 | 70.3743 | 50.8259 | 89.1 | UV254 | cm-1 | 0.01 | 0.462 | 0.93989 | 97.8355 | 0.70095 | 98.5734
Plant Name | Pompano Beach WTP | Total width of all membrane envelopes in the element, w (ft) | 14.4 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-05-28 | 17:00 | 104 | 29 | 132.577 | 52.155 | 18.201 | 0 | 14.581 | 4.148 |  | 18.729 | 18.729 | 0.77853 | 0 | 13.2555 | 13.2555 | 7.0822 | 67.0828 | 0.1976 | 6.412 | 5.722 | 38.07 | 303.072 | 294.8937 | 1575.1 | 1197.6774 | 23.9618 | 87.0903 | 746.2856 | 94.8987 | 132.577 | 116.212 | 18.201 | 8.558 | 10.111 | 18.669 | 18.669 | 0.38387 | 0.45841 | 12.9995 | 12.9995 | 3.921 | 102.2725 | 0.12711 | 5.722 | 7.454 | 19.3848 | 294.8937 | 535.95 | 528.0858 | 1.4673 | 93.4265 | 411.4898 | 95.2891 | 116.212 | 100.285 | 18.201 | 4.644 | 5.467 | 10.111 | 10.111 | 0.41556 | 0.4593 | 14.1084 | 14.1084 | 7.1784 | 82.8691 | 0.17025 | 5.722 | 7.454 | 32.108 | 535.95 | 936.45 | 963.9438 | -2.936 | 89.112 | 749.9469 | 95.7186 | 100.285 | 52.155 | 18.201 | 1.319 | 4.148 | 5.467 | 5.467 | 0.19237 | 0.24127 | 11.7244 | 11.7244 | 9.4006 | 48.6184 | 0.24115 | 7.454 | 7.454 | 125.3525 | 936.45 | 1575.1 | 1194.3665 | 24.172 | 57.4923 | 1065.4082 | 88.2343 | UV254 | cm-1 | 0.014 | 0.693 | 2.63 | 3.5877 | -36.4138 | 97.9798 | 2.1403 | 99.3459 | SUVA | L/(mg*m) | 0.56818 | 4.7466 | --- | --- | --- | --- | UV254 | cm-1 | 0.021 | 0.541 | 2.68 | 2.7578 | -2.9046 | 96.1183 | 1.6494 | 98.7268 | SUVA | L/(mg*m) | #VALUE! | 3.9779 | --- | --- | --- | --- | UV254 | cm-1 | 0.051 | 0.505 | 2.68 | 2.321 | 13.3955 | 89.901 | 1.413 | 96.3907 | SUVA | L/(mg*m) | 0.19506 | 4.7642 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.538 | 2.74 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 2.9239 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.427 | 2.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.4435 | --- | --- | --- | --- | UV254 | cm-1 | 0.051 | 0.462 | 2.5 | 2.4686 | 1.2541 | 88.961 | 1.4653 | 96.5195 | SUVA | L/(mg*m) | 0.89286 | 2.4706 | --- | --- | --- | ---
Treatment Plant Category | CONV | Feed spacer thickness, T (ft) | 0.0029 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-05-29 | 1:00 | 112.0003 | 29 | 131.97 | 52.357 | 18.262 | 0 | 14.58 | 3.791 |  | 18.371 | 18.371 | 0.79364 | 0 | 13.2545 | 13.2545 | 7.5198 | 66.3817 | 0.19967 | 6.473 | 5.697 | 38.0465 | 303.84 | 295.3113 | 1575.1 | 1284.739 | 18.4344 | 87.1165 | 790.0251 | 95.1841 | 131.97 | 115.77 | 18.262 | 8.619 | 9.753 | 18.372 | 18.372 | 0.37514 | 0.46914 | 13.0922 | 13.0922 | 3.9788 | 101.6292 | 0.12882 | 5.697 | 7.416 | 19.3651 | 295.3113 | 536.4 | 539.1727 | -0.5169 | 93.4425 | 417.242 | 95.3588 | 115.77 | 100.3 | 18.262 | 4.644 | 5.109 | 9.753 | 9.753 | 0.39646 | 0.47616 | 14.1084 | 14.1084 | 7.3349 | 82.4381 | 0.17114 | 5.697 | 7.416 | 32.108 | 536.4 | 940.5 | 994.7934 | -5.7728 | 89.1274 | 765.5967 | 95.8061 | 100.3 | 52.357 | 18.262 | 1.318 | 3.791 | 5.109 | 5.109 | 0.17806 | 0.25798 | 11.7156 | 11.7156 | 9.5778 | 48.4887 | 0.24161 | 7.416 | 7.416 | 124.555 | 940.5 | 1575.1 | 1224.1759 | 22.2795 | 57.8225 | 1082.338 | 88.492 | SUVA | L/(mg*m) | #VALUE! | 4.7466 | 2.9684 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.68404 | 3.9779 | 4.1486 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 4.7642 | 4.1486 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 4.3387 | 3.031 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 3.4435 | 4.1667 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.92058 | 2.4706 | 2.5667 | --- | --- | --- | --- | ---
Process Train Name | Conventional train | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 11.4272 | [5 empty] | 1998-05-29 | 9:00 | 120 | 29 | 132.502 | 52.897 | 18.205 | 0 | 14.996 | 3.727 |  | 18.723 | 18.723 | 0.80094 | 0 | 13.6327 | 13.6327 | 7.8359 | 66.6586 | 0.20452 | 6.623 | 5.699 | 39.3155 | 312.48 | 299.4869 | 1622.6 | 1346.3154 | 17.0273 | 86.8724 | 822.9012 | 95.2223 | 132.502 | 115.995 | 18.205 | 8.618 | 9.689 | 18.307 | 18.307 | 0.37342 | 0.47075 | 13.0906 | 13.0906 | 4.0419 | 102.0016 | 0.12834 | 5.699 | 7.432 | 19.7197 | 299.4869 | 552.6 | 548.3292 | 0.77285 | 93.4155 | 423.9081 | 95.3481 | 115.995 | 100.375 | 18.205 | 4.643 | 5.046 | 9.689 | 9.689 | 0.39308 | 0.4792 | 14.1053 | 14.1053 | 7.5875 | 82.3925 | 0.1712 | 5.699 | 7.432 | 32.9303 | 552.6 | 964.35 | 1030.7662 | -6.8871 | 89.0044 | 791.6831 | 95.8405 | 100.375 | 52.897 | 18.205 | 1.319 | 3.727 | 5.046 | 5.046 | 0.17552 | 0.2614 | 11.7244 | 11.7244 | 9.8323 | 48.5987 | 0.24125 | 7.432 | 7.432 | 128.9485 | 964.35 | 1622.6 | 1260.0019 | 22.3467 | 56.9435 | 1112.1759 | 88.4057 | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 1080 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 6.0508 | [5 empty] | 1998-05-29 | 17:00 | 128 | 29 | 132.712 | 53.212 | 18.771 | 0 | 14.938 | 3.497 |  | 18.435 | 18.435 | 0.81031 | 0 | 13.58 | 13.58 | 8.1237 | 66.0673 | 0.20555 | 6.149 | 5.674 | 37.6 | 306.384 | 296.6603 | 1540.9 | 1403.2783 | 8.9313 | 87.3256 | 849.9693 | 95.5763 | 132.712 | 116.302 | 18.771 | 9.035 | 9.458 | 18.493 | 18.493 | 0.37282 | 0.48856 | 13.7241 | 13.7241 | 4.0977 | 101.6383 | 0.13503 | 5.674 | 7.416 | 19.3454 | 296.6603 | 540.45 | 561.5726 | -3.9083 | 93.4789 | 429.1165 | 95.4918 | 116.302 | 100.262 | 18.771 | 4.584 | 4.874 | 9.458 | 9.458 | 0.38233 | 0.48467 | 13.9261 | 13.9261 | 7.474 | 82.037 | 0.16975 | 5.674 | 7.416 | 32.1022 | 540.45 | 940.05 | 1018.5514 | -8.3508 | 89.1788 | 779.5007 | 95.8817 | 100.262 | 53.212 | 18.771 | 1.377 | 3.497 | 4.874 | 4.874 | 0.16748 | 0.28252 | 12.24 | 12.24 | 9.8006 | 48.1654 | 0.25412 | 7.416 | 7.416 | 121.2055 | 940.05 | 1540.9 | 1262.4832 | 18.0685 | 59.1433 | 1101.2666 | 88.994 | SDS-Cl2 dose | mg/L | 2.95 | 3.2 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.25 | 3.3 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.5 | 3.45 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 7 | 7 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4131618 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 1.4424 | [5 empty] | 1998-05-30 | 0:00 | 135 | 29 | 132.907 | 53.175 | 18.765 | 0 | 14.939 | 3.621 |  | 18.56 | 18.56 | 0.8049 | 0 | 13.5809 | 13.5809 | 7.9348 | 66.3412 | 0.20471 | 6.819 | 5.661 | 37.6235 | 306.432 | 296.6924 | 1540.9 | 1365.5217 | 11.3815 | 87.319 | 831.1071 | 95.4731 | 132.907 | 116.752 | 18.765 | 9.035 | 9.524 | 18.559 | 18.559 | 0.37458 | 0.48683 | 13.7241 | 13.7241 | 4.089 | 101.9755 | 0.13458 | 5.661 | 7.403 | 19.3454 | 296.6924 | 540 | 559.7994 | -3.6666 | 93.4796 | 428.2459 | 95.4826 | 116.752 | 100.315 | 18.765 | 4.584 | 4.94 | 9.524 | 9.524 | 0.38585 | 0.48131 | 13.9261 | 13.9261 | 7.4369 | 82.3316 | 0.16915 | 5.661 | 7.403 | 32.0045 | 540 | 940.05 | 1011.3869 | -7.5886 | 89.2129 | 775.6935 | 95.8741 | 100.315 | 53.175 | 18.765 | 1.319 | 3.621 | 4.94 | 4.94 | 0.17128 | 0.267 | 11.7244 | 11.7244 | 9.6764 | 48.3036 | 0.24272 | 7.403 | 7.403 | 121.4955 | 940.05 | 1540.9 | 1238.2199 | 19.6431 | 59.05 | 1089.135 | 88.8448 | SDS-Free Cl2 residual | mg/L | 1.3 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.1 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.5 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.86 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-05-30 | 9:00 | 144 | 29 | 132.337 | 52.89 | 18.762 | 0 | 14.938 | 3.556 |  | 18.494 | 18.494 | 0.80772 | 0 | 13.58 | 13.58 | 8.019 | 65.8325 | 0.20628 | 7.004 | 5.66 | 38.0465 | 305.616 | 296.6924 | 1542.8 | 1383.209 | 10.3442 | 87.1765 | 839.9507 | 95.4704 | 132.337 | 116.055 | 18.762 | 9.035 | 9.46 | 18.495 | 18.495 | 0.37287 | 0.48851 | 13.7241 | 13.7241 | 4.093 | 101.341 | 0.13542 | 5.66 | 7.388 | 19.6803 | 296.6924 | 540.45 | 561.2595 | -3.8504 | 93.3668 | 428.976 | 95.4123 | 116.055 | 100.292 | 18.762 | 4.584 | 4.876 | 9.46 | 9.46 | 0.38243 | 0.48457 | 13.9261 | 13.9261 | 7.4744 | 81.9371 | 0.16996 | 5.66 | 7.388 | 32.0102 | 540.45 | 936.45 | 1018.4418 | -8.7556 | 89.211 | 779.4459 | 95.8932 | 100.292 | 52.89 | 18.762 | 1.32 | 3.556 | 4.876 | 4.876 | 0.1687 | 0.27071 | 11.7333 | 11.7333 | 9.6594 | 48.1696 | 0.24358 | 7.388 | 7.388 | 121.7275 | 936.45 | 1542.8 | 1238.8779 | 19.6994 | 58.9718 | 1087.664 | 88.8084 | SDS-Cl2 demand | mg/L | 1.65 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.64 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.15 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.64 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.64 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.5 | NR | --- | 0.32353 | --- | -15.3846 | 0.81176 | -84.7826 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.28 |  |  |  |  | SDS-Cl2 demand | mg/L | 5.6 | NR | --- | 8.6 | --- | 9.6774 | 7.4 | 24.3243 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.4 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.14 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.28
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-05-30 | 17:00 | 152 | 29 | 132.18 | 52.86 | 18.798 | 0 | 14.998 | 3.671 |  | 18.669 | 18.669 | 0.80336 | 0 | 13.6345 | 13.6345 | 7.8568 | 65.8652 | 0.20701 | 7.147 | 5.69 | 37.741 | 304.992 | 295.9537 | 1546.6 | 1350.8907 | 12.6542 | 87.2477 | 823.4222 | 95.4166 | 132.18 | 115.86 | 18.798 | 9.034 | 9.575 | 18.609 | 18.609 | 0.37592 | 0.48546 | 13.7225 | 13.7225 | 4.0687 | 101.1533 | 0.13566 | 5.69 | 7.434 | 19.503 | 295.9537 | 537.3 | 556.7845 | -3.6264 | 93.4101 | 426.3691 | 95.4258 | 115.86 | 100.285 | 18.798 | 4.584 | 4.991 | 9.575 | 9.575 | 0.38857 | 0.47875 | 13.9261 | 13.9261 | 7.3733 | 81.9012 | 0.17004 | 5.69 | 7.434 | 32.0102 | 537.3 | 933.3 | 1001.385 | -7.2951 | 89.184 | 769.3425 | 95.8393 | 100.285 | 52.86 | 18.798 | 1.32 | 3.671 | 4.991 | 4.991 | 0.1733 | 0.26448 | 11.7333 | 11.7333 | 9.5771 | 48.1974 | 0.24344 | 7.434 | 7.434 | 121.539 | 933.3 | 1546.6 | 1225.189 | 20.7818 | 58.9331 | 1079.2445 | 88.7385 | SDS-Chlorination temp. | oC | 23 | 23 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.64 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.65 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.7 |  |  |  |  | SDS-Chlorination temp. | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.38 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.08 |  |  |  |  | SDS-Chlorination temp. | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.38
State Approved Plant Capacity (MGD) | 18 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -3.4272 | [5 empty] | 1998-05-31 | 1:00 | 160 | 29 | 132.795 | 53.167 | 18.751 | 0 | 15.116 | 3.494 |  | 18.61 | 18.61 | 0.81225 | 0 | 13.7418 | 13.7418 | 8.1954 | 66.0346 | 0.2081 | 7.017 | 5.672 | 37.6 | 306.384 | 296.6924 | 1542.8 | 1417.5972 | 8.1153 | 87.3269 | 857.1448 | 95.6133 | 132.795 | 116.557 | 18.751 | 9.095 | 9.397 | 18.492 | 18.492 | 0.37199 | 0.49183 | 13.8152 | 13.8152 | 4.1153 | 101.8097 | 0.1357 | 5.672 | 7.416 | 19.3651 | 296.6924 | 540 | 565.1071 | -4.6495 | 93.473 | 430.8997 | 95.5059 | 116.557 | 100.277 | 18.751 | 4.584 | 4.813 | 9.397 | 9.397 | 0.37907 | 0.48782 | 13.9261 | 13.9261 | 7.4976 | 82.1684 | 0.16948 | 5.672 | 7.416 | 32.108 | 540 | 940.05 | 1023.7268 | -8.9013 | 89.178 | 781.8634 | 95.8934 | 100.277 | 53.167 | 18.751 | 1.319 | 3.494 | 4.813 | 4.813 | 0.1662 | 0.27405 | 11.7244 | 11.7244 | 9.728 | 48.243 | 0.24303 | 7.416 | 7.416 | 121.713 | 940.05 | 1542.8 | 1248.9757 | 19.0449 | 58.9767 | 1094.5129 | 88.8797 | SDS-Chlorination pH | --- | 8.5 | 8.65 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.45 | 8.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.55 | 8.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.7 | 8.48 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.56 | 8.6 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.9 | 8.32 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NA | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -2.0508 | [5 empty] | 1998-05-31 | 7:08 | 166.1336 | 29 | 131.565 | 52.47 | 18.775 | 0 | 15.119 | 3.44 |  | 18.559 | 18.559 | 0.81465 | 0 | 13.7445 | 13.7445 | 7.9926 | 65.2499 | 0.21064 | 5.977 | 5.611 | 33.464 | 280.896 | 283.4269 | 1371.8 | 1382.0283 | -0.74561 | 88.1931 | 832.7276 | 95.9814 | 131.565 | 115.23 | 18.775 | 9.096 | 9.46 | 18.556 | 18.556 | 0.37368 | 0.49019 | 13.8167 | 13.8167 | 3.9311 | 100.6914 | 0.13722 | 5.611 | 7.353 | 17.9467 | 283.4269 | 492.3 | 538.692 | -9.4235 | 93.668 | 411.0594 | 95.634 | 115.23 | 100.382 | 18.775 | 4.643 | 4.817 | 9.46 | 9.46 | 0.38086 | 0.4908 | 14.1053 | 14.1053 | 5.249 | 83.782 | 0.16836 | 5.611 | 7.353 | 138.1 | 492.3 | 853.2 | 833.7056 | 2.2849 | 51.2749 | 663.0028 | 79.1705 | 100.382 | 52.47 | 18.775 | 1.377 | 3.44 | 4.817 | 4.817 | 0.1652 | 0.28586 | 12.24 | 12.24 | 8.9874 | 48.6636 | 0.25152 | 7.353 | 7.353 | 104.342 | 853.2 | 1371.8 | 1152.9609 | 15.9527 | 63.1856 | 1003.0804 | 89.5978 | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | 2.5576 | [5 empty] | 1998-05-31 | 15:00 | 174 | 29 | 131.662 | 52.267 | 18.864 | 0 | 14.938 | 3.311 |  | 18.249 | 18.249 | 0.81857 | 0 | 13.58 | 13.58 | 8.1 | 65.0005 | 0.20892 | 6.541 | 5.672 | 34.1925 | 279.792 | 282.9772 | 1383.2 | 1405.4012 | -1.6051 | 87.9169 | 844.1892 | 95.9497 | 131.662 | 115.252 | 18.864 | 9.1 | 9.33 | 18.43 | 18.43 | 0.37027 | 0.49376 | 13.8228 | 13.8228 | 3.9422 | 100.6508 | 0.13733 | 5.672 | 7.43 | 17.9861 | 282.9772 | 495.45 | 541.4358 | -9.2816 | 93.644 | 412.2065 | 95.6366 | 115.252 | 100.195 | 18.864 | 4.642 | 4.688 | 9.33 | 9.33 | 0.37395 | 0.49753 | 14.1023 | 14.1023 | 5.3352 | 83.5243 | 0.16884 | 5.672 | 7.43 | 138.6 | 495.45 | 852.3 | 848.7985 | 0.41083 | 51.0208 | 672.1242 | 79.3788 | 100.195 | 52.267 | 18.864 | 1.377 | 3.311 | 4.688 | 4.688 | 0.16004 | 0.29373 | 12.24 | 12.24 | 9.041 | 48.326 | 0.25328 | 7.43 | 7.43 | 103.8345 | 852.3 | 1383.2 | 1163.5767 | 15.8779 | 63.3064 | 1007.9383 | 89.6983 | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 (dup) | CI-s2-8 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-05-31 | 23:00 | 182 | 29 | 131.482 | 52.395 | 18.807 | 0 | 15.116 | 3.431 |  | 18.547 | 18.547 | 0.81501 | 0 | 13.7418 | 13.7418 | 8.0075 | 65.124 | 0.21101 | 6.546 | 5.65 | 33.511 | 280.992 | 283.5232 | 1373.7 | 1385.0053 | -0.82298 | 88.1805 | 834.2643 | 95.9832 | 131.482 | 115.08 | 18.807 | 9.035 | 9.334 | 18.369 | 18.369 | 0.36951 | 0.49186 | 13.7241 | 13.7241 | 3.9446 | 100.5294 | 0.13652 | 5.65 | 7.405 | 17.7103 | 283.5232 | 493.2 | 540.8213 | -9.6556 | 93.7535 | 412.1723 | 95.7032 | 115.08 | 100.352 | 18.807 | 4.584 | 4.75 | 9.334 | 9.334 | 0.37571 | 0.49111 | 13.9261 | 13.9261 | 5.3045 | 83.6045 | 0.16657 | 5.65 | 7.405 | 135.4 | 493.2 | 857.7 | 838.4958 | 2.239 | 52.2438 | 665.8479 | 79.665 | 100.352 | 52.395 | 18.807 | 1.319 | 3.431 | 4.75 | 4.75 | 0.16368 | 0.27768 | 11.7244 | 11.7244 | 8.9905 | 48.576 | 0.24136 | 7.405 | 7.405 | 103.6025 | 857.7 | 1373.7 | 1147.6022 | 16.459 | 63.4589 | 1002.6511 | 89.6671 | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-05-27 | 1998-05-27 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 17.08 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-06-09 | 1998-09-09 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | 543.7647 | --- | 73.1092 | 331.3824 | 90.3435 | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | 437.59 | --- | 70.669 | 275.97 | 87.8465 | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 7.83 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-06-01 | 7:00 | 190 | 29 | 131.79 | 52.507 | 18.796 | 0 | 15 | 3.31 |  | 18.31 | 18.31 | 0.81922 | 0 | 13.6364 | 13.6364 | 8.1629 | 65.1896 | 0.20918 | 6.903 | 5.683 | 33.417 | 281.664 | 283.3626 | 1354.7 | 1416.0468 | -4.5284 | 88.207 | 849.7047 | 96.0672 | 131.79 | 115.35 | 18.796 | 9.095 | 9.331 | 18.426 | 18.426 | 0.37023 | 0.4936 | 13.8152 | 13.8152 | 3.9541 | 100.8199 | 0.13703 | 5.683 | 7.426 | 17.5133 | 283.3626 | 491.85 | 542.4881 | -10.2954 | 93.8195 | 412.9254 | 95.7587 | 115.35 | 100.367 | 18.796 | 4.643 | 4.688 | 9.331 | 9.331 | 0.37398 | 0.49759 | 14.1053 | 14.1053 | 5.367 | 83.6955 | 0.16853 | 5.683 | 7.426 | 132.9 | 491.85 | 856.8 | 847.3544 | 1.1024 | 53.099 | 669.6022 | 80.1524 | 100.367 | 52.507 | 18.796 | 1.378 | 3.31 | 4.688 | 4.688 | 0.16002 | 0.29394 | 12.2489 | 12.2489 | 9.1037 | 48.5373 | 0.25236 | 7.426 | 7.426 | 103.2835 | 856.8 | 1354.7 | 1170.4996 | 13.5971 | 63.5508 | 1013.6498 | 89.8107 | SDS-BDCM | mg/L | 7.53 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 7.75 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 3.03 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 5 | NR | --- | 153.8529 | --- | 67.7871 | 94.7765 | 87.8662 | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 11.5 | NR | --- | 146.65 | --- | 84.9985 | 89.99 | 94.4438 | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 0.76 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-06-01 | 15:00 | 198 | 29 | 131.122 | 52.62 | 18.709 | 0 | 14.994 | 3.555 |  | 18.549 | 18.549 | 0.80835 | 0 | 13.6309 | 13.6309 | 7.8837 | 65.2783 | 0.20881 | 7.458 | 5.732 | 35.908 | 292.656 | 289.4976 | 1436.4 | 1359.0677 | 5.3838 | 87.5964 | 824.2826 | 95.6437 | 131.122 | 114.855 | 18.709 | 9.04 | 9.515 | 18.555 | 18.555 | 0.3744 | 0.4872 | 13.7316 | 13.7316 | 4.004 | 100.2755 | 0.13694 | 5.732 | 7.458 | 18.0452 | 289.4976 | 520.2 | 547.3987 | -5.2285 | 93.7667 | 418.4481 | 95.6876 | 114.855 | 100.172 | 18.709 | 4.583 | 4.932 | 9.515 | 9.515 | 0.38539 | 0.48166 | 13.923 | 13.923 | 7.1686 | 81.6359 | 0.17055 | 5.732 | 7.458 | 30.751 | 520.2 | 896.85 | 975.0144 | -8.7154 | 89.3778 | 747.6072 | 95.8867 | 100.172 | 52.62 | 18.709 | 1.377 | 3.555 | 4.932 | 4.932 | 0.1698 | 0.2792 | 12.24 | 12.24 | 9.3897 | 48.2973 | 0.25343 | 7.458 | 7.458 | 110.229 | 896.85 | 1436.4 | 1201.5412 | 16.3505 | 61.924 | 1049.1956 | 89.494 | SDS-DBCM | mg/L | 3.61 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 72.17 | 72.17 | --- | --- | --- | --- | SDS-DBCM | mg/L | 2.71 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 370.42 | 370.42 | --- | --- | --- | --- | SDS-DBCM | mg/L | 3.03 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 716.21 | 716.21 | --- | --- | --- | --- | SDS-DBCM | mg/L | 4.2 | NR | --- | -0.40588 | --- | -22.8571 | 1.5471 | -177.9468 | Operation time | hh.hh | 1056 | 1056 | --- | --- | --- | --- | SDS-DBCM | mg/L | 4.3 | NR | --- | 1.595 | --- | -14.1615 | 2.637 | -59.2719 | Operation time | hh.hh | 1416 | 1416 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1056 | 1056 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-06-01 | 23:00 | 206 | 29 | 131.587 | 53.07 | 18.705 | 0 | 15.007 | 3.313 |  | 18.32 | 18.32 | 0.81916 | 0 | 13.6427 | 13.6427 | 8.3328 | 65.2907 | 0.20895 | 7.937 | 5.711 | 35.203 | 294.672 | 290.429 | 1426.9 | 1446.5344 | -1.376 | 87.879 | 868.4817 | 95.9466 | 131.587 | 115.26 | 18.705 | 9.033 | 9.274 | 18.307 | 18.307 | 0.36788 | 0.49342 | 13.721 | 13.721 | 4.0551 | 100.6634 | 0.13631 | 5.711 | 7.477 | 17.73 | 290.429 | 521.55 | 556.0416 | -6.6133 | 93.8952 | 423.2353 | 95.8108 | 115.26 | 100.3 | 18.705 | 4.642 | 4.632 | 9.274 | 9.274 | 0.37096 | 0.50054 | 14.1023 | 14.1023 | 7.3651 | 81.7099 | 0.17259 | 5.711 | 7.477 | 30.8947 | 521.55 | 905.4 | 1013.2645 | -11.9135 | 89.3624 | 767.4073 | 95.9741 | 100.3 | 53.07 | 18.705 | 1.319 | 3.313 | 4.632 | 4.632 | 0.15896 | 0.28476 | 11.7244 | 11.7244 | 9.5217 | 48.4583 | 0.24195 | 7.477 | 7.477 | 111.302 | 905.4 | 1426.9 | 1221.5531 | 14.3911 | 61.6767 | 1063.4766 | 89.5341 | SDS-CHBr3 | mg/L | 0.77 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.8 | 5.91 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.38 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.84 | 6.3 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.27 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.34 | 6.16 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.489 | NR | --- | -1.7471 | --- | -323.7288 | -0.81453 | 161.3851 | pH | --- | 5.35 | 5.98 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.5 | NR | --- | -1.086 | --- | -181.0345 | -0.456 | 207.2368 | pH | --- | 5.41 | 5.95 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.37 | 5.88 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 12.8923 | [5 empty] | 1998-06-02 | 14:11 | 221.1803 | 29 | 131.25 | 52.545 | 18.616 | 0 | 14.939 | 3.303 |  | 18.242 | 18.242 | 0.81893 | 0 | 13.5809 | 13.5809 | 8.3769 | 64.9046 | 0.20924 | 8.449 | 5.725 | 36.8245 | 299.52 | 293.6732 | 1472.5 | 1455.3632 | 1.1638 | 87.4607 | 874.5182 | 95.7892 | 131.25 | 115.185 | 18.616 | 9.103 | 9.207 | 18.31 | 18.31 | 0.36703 | 0.49716 | 13.8273 | 13.8273 | 4.1127 | 100.4888 | 0.1376 | 5.725 | 7.437 | 18.4589 | 293.6732 | 532.8 | 565.7787 | -6.1897 | 93.7145 | 429.7259 | 95.7045 | 115.185 | 100.112 | 18.616 | 4.584 | 4.623 | 9.207 | 9.207 | 0.36893 | 0.49788 | 13.9261 | 13.9261 | 7.4972 | 81.5353 | 0.1708 | 5.725 | 7.437 | 31.579 | 532.8 | 921.15 | 1029.7927 | -11.7942 | 89.2469 | 781.2963 | 95.9581 | 100.112 | 52.545 | 18.616 | 1.32 | 3.303 | 4.623 | 4.623 | 0.15858 | 0.28553 | 11.7333 | 11.7333 | 9.6798 | 48.0327 | 0.24428 | 7.437 | 7.437 | 114.376 | 921.15 | 1472.5 | 1243.5665 | 15.5473 | 61.0533 | 1082.3582 | 89.4327 | SDS-THM4 | mg/L | 11.91 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 27.92 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 6.33 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 9.689 | NR | --- | 695.4647 | --- | 69.4918 | 426.8914 | 88.6856 | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 16.3 | NR | --- | 584.749 | --- | 71.4722 | 368.141 | 88.2575 | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 8.59 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 80 - 350 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 6.1089 | [5 empty] | 1998-06-02 | 18:46 | 225.7706 | 29 | 132.45 | 53.16 | 18.808 | 0 | 14.936 | 3.431 |  | 18.367 | 18.367 | 0.8132 | 0 | 13.5782 | 13.5782 | 8.1704 | 65.8266 | 0.20627 | 8.313 | 5.727 | 36.566 | 300.816 | 293.7695 | 1464.9 | 1413.4407 | 3.5128 | 87.5528 | 853.6051 | 95.7163 | 132.45 | 115.747 | 18.808 | 9.035 | 9.335 | 18.37 | 18.37 | 0.36953 | 0.49183 | 13.7241 | 13.7241 | 4.0895 | 101.201 | 0.13561 | 5.727 | 7.473 | 18.1831 | 293.7695 | 534.15 | 560.4994 | -4.933 | 93.8104 | 427.1345 | 95.743 | 115.747 | 100.18 | 18.808 | 4.584 | 4.751 | 9.335 | 9.335 | 0.37576 | 0.49106 | 13.9261 | 13.9261 | 7.4479 | 81.7076 | 0.17044 | 5.727 | 7.473 | 31.7342 | 534.15 | 926.1 | 1018.9056 | -10.0211 | 89.1976 | 776.5278 | 95.9133 | 100.18 | 53.16 | 18.808 | 1.32 | 3.431 | 4.751 | 4.751 | 0.1637 | 0.27784 | 11.7333 | 11.7333 | 9.669 | 48.193 | 0.24347 | 7.473 | 7.473 | 115.188 | 926.1 | 1464.9 | 1238.0801 | 15.4836 | 60.7897 | 1082.0901 | 89.355 | SDS-MCAA* | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 124 | 222.368 | 74.2857 | 173.184 | 89.6064 | SDS-MCAA* | mg/L | 9.79 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 222 | 409.0818 | 72.2222 | 315.5409 | 93.6617 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 11.4 | 5.3478 | 71.875 | 8.3739 | -114.9533 | SDS-MCAA* | mg/L | 5.4 | NR | --- | 128.7194 | --- | 90.7595 | 76.2097 | 97.1264 | Alkalinity | mg/L as CaCO3 | 20 | 80 | 142.6341 | 65.5172 | 111.3171 | 82.0333 | SDS-MCAA* | mg/L | 2.19 | NR | --- | 31.4 | --- | 49.0566 | 21 | 74.2857 | Alkalinity | mg/L as CaCO3 | 20 | 92 | 159.6923 | 61.5385 | 125.8462 | 84.1076 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 86 | 156.9854 | 66.6667 | 121.4927 | 85.1843
|  | Acceptable range of operating pH values | 4 - 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 10.7173 | [5 empty] | 1998-06-03 | 2:00 | 233 | 29 | 132.315 | 53.107 | 18.721 | 0 | 15.002 | 3.437 |  | 18.439 | 18.439 | 0.8136 | 0 | 13.6382 | 13.6382 | 8.213 | 65.777 | 0.20734 | 8.285 | 5.711 | 36.4015 | 302.256 | 294.4762 | 1442.1 | 1420.9341 | 1.4677 | 87.6386 | 857.7051 | 95.7559 | 132.315 | 115.777 | 18.721 | 9.033 | 9.34 | 18.373 | 18.373 | 0.36964 | 0.49165 | 13.721 | 13.721 | 4.1019 | 101.2231 | 0.13555 | 5.711 | 7.468 | 17.9861 | 294.4762 | 536.85 | 561.8782 | -4.662 | 93.8922 | 428.1772 | 95.7994 | 115.777 | 100.322 | 18.721 | 4.584 | 4.756 | 9.34 | 9.34 | 0.37603 | 0.49079 | 13.9261 | 13.9261 | 7.4844 | 81.8441 | 0.17015 | 5.711 | 7.468 | 31.8032 | 536.85 | 932.4 | 1023.6318 | -9.7846 | 89.2001 | 780.2409 | 95.9239 | 100.322 | 53.107 | 18.721 | 1.319 | 3.437 | 4.756 | 4.756 | 0.16392 | 0.27733 | 11.7244 | 11.7244 | 9.7352 | 48.2583 | 0.24295 | 7.468 | 7.468 | 115.6085 | 932.4 | 1442.1 | 1245.8559 | 13.6082 | 60.741 | 1089.128 | 89.3852 | SDS-DCAA* | mg/L | 23.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 31.9 | 553 | 1036.5808 | 89.1497 | 794.7904 | 95.9864 | SDS-DCAA* | mg/L | 26.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32 | 534 | 998.9261 | 89.1045 | 766.4631 | 95.825 | SDS-DCAA* | mg/L | 6.18 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 29.1 | 505 | 941.3984 | 89.7895 | 723.1992 | 95.9762 | SDS-DCAA* | mg/L | 15.8 | NR | --- | 857.0824 | --- | 92.7742 | 506.0412 | 97.7867 | Total dissolved solids | mg/L | 31 | 520 | 1030.4683 | 89.3471 | 775.2341 | 96.0012 | SDS-DCAA* | mg/L | 11.2 | NR | --- | 526.8 | --- | 86.6102 | 322.4 | 95.0993 | Total dissolved solids | mg/L | 35.3 | 572 | 1076.5897 | 88.4376 | 824.2949 | 95.7176 | SDS-DCAA* | mg/L | 2.33 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 31 | 520 | 1030.4683 | 89.3471 | 775.2341 | 96.0012
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-06-03 | 10:00 | 241 | 29 | 132.255 | 52.897 | 18.814 | 0 | 15.059 | 3.43 |  | 18.489 | 18.489 | 0.81448 | 0 | 13.69 | 13.69 | 8.126 | 65.636 | 0.20857 | 8.058 | 5.715 | 35.2735 | 293.52 | 289.5939 | 1411.7 | 1406.157 | 0.39265 | 87.8197 | 847.8754 | 95.8398 | 132.255 | 115.687 | 18.814 | 9.099 | 9.333 | 18.432 | 18.432 | 0.37033 | 0.49365 | 13.8213 | 13.8213 | 4.043 | 101.114 | 0.13669 | 5.715 | 7.487 | 17.7891 | 289.5939 | 519.3 | 554.584 | -6.7945 | 93.8572 | 422.0889 | 95.7855 | 115.687 | 100.202 | 18.814 | 4.584 | 4.749 | 9.333 | 9.333 | 0.37566 | 0.49116 | 13.9261 | 13.9261 | 7.2425 | 81.888 | 0.17006 | 5.715 | 7.487 | 30.8085 | 519.3 | 898.65 | 990.8193 | -10.2564 | 89.3615 | 755.0596 | 95.9197 | 100.202 | 52.897 | 18.814 | 1.319 | 3.43 | 4.749 | 4.749 | 0.16364 | 0.27774 | 11.7244 | 11.7244 | 9.4112 | 48.3243 | 0.24262 | 7.487 | 7.487 | 109.301 | 898.65 | 1411.7 | 1202.1927 | 14.8408 | 62.2571 | 1050.4213 | 89.5946 | SDS-TCAA* | mg/L | 5.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 600 | 1134.528 | #VALUE! | 867.264 | 97.2327 | SDS-TCAA* | mg/L | 11.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 18 | 1250 | 2391.014 | #VALUE! | 1820.507 | 99.0113 | SDS-TCAA* | mg/L | 4.38 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 16 | 484 | 913.1542 | #VALUE! | 698.5771 | 97.7096 | SDS-TCAA* | mg/L | NR | NR | --- | 6475.7059 | --- | 99.009 | 3792.8529 | 99.71 | Total hardness | mg/L as CaCO3 | 14 | 550 | 1109.5317 | 95.3333 | 829.7659 | 98.3128 | SDS-TCAA* | mg/L | 1.33 | NR | --- | 1374.4 | --- | 81.7081 | 848.2 | 93.0559 | Total hardness | mg/L as CaCO3 | 28 | 552 | 1044.6496 | 90 | 798.3248 | 96.4927 | SDS-TCAA* | mg/L | 1.33 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 14 | 885 | 1794.239 | #VALUE! | 1339.6195 | 98.9549
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-06-03 | 18:00 | 249 | 29 | 131.82 | 52.792 | 18.81 | 0 | 14.938 | 3.437 |  | 18.375 | 18.375 | 0.81295 | 0 | 13.58 | 13.58 | 8.0551 | 65.4409 | 0.20752 | 8.264 | 5.715 | 35.3205 | 292.272 | 289.1764 | 1413.6 | 1392.4929 | 1.4931 | 87.7858 | 840.8346 | 95.7994 | 131.82 | 115.515 | 18.81 | 9.098 | 9.398 | 18.496 | 18.496 | 0.37206 | 0.49189 | 13.8197 | 13.8197 | 4.0322 | 100.8253 | 0.13707 | 5.715 | 7.472 | 17.4739 | 289.1764 | 518.4 | 552.2056 | -6.5211 | 93.9574 | 420.691 | 95.8464 | 115.515 | 100.217 | 18.81 | 4.642 | 4.756 | 9.398 | 9.398 | 0.37758 | 0.49393 | 14.1023 | 14.1023 | 7.2539 | 81.8021 | 0.1724 | 5.715 | 7.472 | 30.912 | 518.4 | 898.65 | 994.203 | -10.633 | 89.3103 | 756.3015 | 95.9127 | 100.217 | 52.792 | 18.81 | 1.319 | 3.437 | 4.756 | 4.756 | 0.16392 | 0.27733 | 11.7244 | 11.7244 | 9.4112 | 48.2833 | 0.24283 | 7.472 | 7.472 | 109.04 | 898.65 | 1413.6 | 1201.6746 | 14.9919 | 62.2929 | 1050.1623 | 89.6168 | SDS-MBAA* | mg/L | 10.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 500 | 949.152 | 94.0741 | 724.576 | 97.7918 | SDS-MBAA* | mg/L | 5.86 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 14 | 1150 | 2202.1038 | 94.5736 | 1676.0519 | 99.1647 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 14 | 480 | 907.3202 | 94.4882 | 693.6601 | 97.9817 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 12 | 515 | 1040.0829 | 95.4545 | 777.5415 | 98.4567 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 24 | 512 | 970.8034 | 90.9091 | 741.4017 | 96.7629 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 12 | 810 | 1643.0341 | 95.3125 | 1226.5171 | 99.0216
|  | Maximum permissible turbidity (ntu) | less than 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 2.5576 | [5 empty] | 1998-06-04 | 2:00 | 257 | 29 | 131.985 | 52.98 | 18.688 | 0 | 15.003 | 3.497 |  | 18.5 | 18.5 | 0.81097 | 0 | 13.6391 | 13.6391 | 8.0249 | 65.7696 | 0.20738 | 8.133 | 5.698 | 35.1795 | 294.048 | 290.3327 | 1390.8 | 1385.0033 | 0.41679 | 87.883 | 837.668 | 95.8003 | 131.985 | 115.485 | 18.688 | 9.034 | 9.401 | 18.435 | 18.435 | 0.37128 | 0.49005 | 13.7225 | 13.7225 | 4.037 | 101.01 | 0.13585 | 5.698 | 7.455 | 17.6512 | 290.3327 | 521.1 | 552.3691 | -6.0006 | 93.9204 | 421.3509 | 95.8108 | 115.485 | 100.262 | 18.688 | 4.584 | 4.817 | 9.401 | 9.401 | 0.37928 | 0.48761 | 13.9261 | 13.9261 | 7.2332 | 81.9523 | 0.16993 | 5.698 | 7.455 | 30.9868 | 521.1 | 905.85 | 987.5063 | -9.0143 | 89.3272 | 754.3031 | 95.892 | 100.262 | 52.98 | 18.688 | 1.32 | 3.497 | 4.817 | 4.817 | 0.16634 | 0.27403 | 11.7333 | 11.7333 | 9.4649 | 48.4681 | 0.24208 | 7.455 | 7.455 | 109.6345 | 905.85 | 1390.8 | 1206.3946 | 13.2589 | 62.2383 | 1056.1223 | 89.6191 | SDS-DBAA* | mg/L | 4.13 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.09 | 5.07 | 9.6914 | 71.875 | 7.3807 | 98.7806 | SDS-DBAA* | mg/L | 3.68 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 30 | 57.7196 | 72 | 43.8598 | 99.8404 | SDS-DBAA* | mg/L | 1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.13 | 14.3 | 27.2938 | 94.8413 | 20.7969 | 99.3749 | SDS-DBAA* | mg/L | 3.69 | NR | --- | 213.4812 | --- | 93.3854 | 125.9406 | 97.9832 | Turbidity | ntu | 0.14 | 6.08 | 12.2808 | 84.2697 | 9.1804 | 98.475 | SDS-DBAA* | mg/L | 2.54 | NR | --- | -5.46 | --- | -98.3871 | -1.8 | 305 | Turbidity | ntu | 3.37 | 8.84 | 13.9827 | 93.5192 | 11.4114 | 70.468 | SDS-DBAA* | mg/L | 2.55 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.45 | 10.7 | 21.4 | 60.8696 | 16.05 | 97.1963
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 6.1089 | [5 empty] | 1998-06-04 | 10:00 | 265 | 29 | 132.352 | 53.295 | 18.718 | 0 | 14.818 | 3.43 |  | 18.248 | 18.248 | 0.81203 | 0 | 13.4709 | 13.4709 | 8.113 | 65.9925 | 0.20413 | 7.122 | 5.705 | 36.1665 | 299.136 | 292.9023 | 1442.1 | 1402.0308 | 2.7785 | 87.6524 | 847.4665 | 95.7324 | 132.352 | 115.732 | 18.718 | 9.099 | 9.334 | 18.433 | 18.433 | 0.37036 | 0.49363 | 13.8213 | 13.8213 | 4.0915 | 101.2325 | 0.13653 | 5.705 | 7.451 | 17.8285 | 292.9023 | 530.55 | 561.0506 | -5.7489 | 93.9132 | 426.9764 | 95.8245 | 115.732 | 100.285 | 18.718 | 4.584 | 4.75 | 9.334 | 9.334 | 0.37571 | 0.49111 | 13.9261 | 13.9261 | 7.3996 | 81.8909 | 0.17006 | 5.705 | 7.451 | 31.4295 | 530.55 | 922.95 | 1012.2276 | -9.6731 | 89.2696 | 771.3888 | 95.9256 | 100.285 | 53.295 | 18.718 | 1.32 | 3.43 | 4.75 | 4.75 | 0.16366 | 0.27789 | 11.7333 | 11.7333 | 9.6648 | 48.4072 | 0.24239 | 7.451 | 7.451 | 112.433 | 922.95 | 1442.1 | 1234.8691 | 14.3701 | 61.6142 | 1078.9095 | 89.579 | SDS-BCAA* | mg/L | 9.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 6.43 | 28.3 | 48.5954 | 55.9589 | 38.4477 | 83.276 | SDS-BCAA* | mg/L | 17.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 5.54 | 23.7 | 40.5188 | 59.2647 | 32.1094 | 82.7465 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 16.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 2.14 | NR | --- | 104.5118 | --- | 76.8182 | 63.2559 | 91.9375 | Total organic carbon | mg/L | BMRL | 29 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 5.1 | NR | --- | 0.49 | --- | -18.232 | 1.15 | -86.087 | Total organic carbon | mg/L | 5.35 | 20.9 | 35.5197 | 56.8548 | 28.2098 | 81.035 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 14.7 | 33.8 | 53.7385 | 21.3904 | 43.7693 | 66.4148
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-06-05 | 3:30 | 282.5 | 29 | 131.5 | 56 | 20 | 0 | 15.07 | 3.47 |  | 18.54 | 18.54 | 0.81284 | 0 | 13.7 | 13.7 | 8.1808 | 65.5692 | 0.20894 | 8.1 | NR | 37.25 | 295.2 | 295.2 | 1048.3 | 1415.4612 | -35.0244 | 87.3814 | 855.3306 | 95.645 | 131.5 | 115.5 | 20 | 9.12 | 9.42 | 18.54 | 18.54 | 0.37294 | 0.49191 | 13.8532 | 13.8532 | 4.0308 | 99.4692 | 0.13927 | 4.73 | 7.45 | 23.6 | 295.2 | NA | 558.1503 | #VALUE! | 92.0054 | 426.6752 | 94.4689 | 115.5 | 99 | 20 | 4.63 | 4.79 | 9.42 | 9.42 | 0.37907 | 0.49151 | 14.0658 | 14.0658 | #VALUE! | #VALUE! | #VALUE! | 4.73 | 7.45 | 32.8 | NA | 901.5 | #VALUE! | #VALUE! | 88.8889 | #VALUE! | #VALUE! | 99 | 56 | 20 | 1.32 | 4.91 | 6.23 | 6.23 | 0.22288 | 0.21188 | 11.7333 | 11.7333 | 8.0884 | 49.4116 | 0.23746 | 7.45 | 7.45 | 188.5 | 901.5 | 1048.3 | 1093.1823 | -4.2814 | 36.145 | 997.3411 | 81.0997 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 1.12 | 2.1501 | 98.557 | 1.635 | 99.3884 | SDS-TBAA | mg/L | NA | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 1.05 | 2.0113 | 97.7819 | 1.5307 | 99.216 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.017 | 1.06 | 2.0164 | 96.6337 | 1.5382 | 98.8948 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.013 | 1.12 | 2.2756 | 97.5836 | 1.6978 | 99.2343 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.68 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.88 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 19.1077 | [5 empty] | 1998-06-05 | 11:00 | 290 | 29 | 131 | 56 | 19 | 0 | 15 | 3.54 |  | 18.54 | 18.54 | 0.80906 | 0 | 13.6364 | 13.6364 | 7.9058 | 66.5942 | 0.20477 | 8.41 | 5.78 | 37.4 | 290.9 | 290.9 | 1042.5 | 1365.0525 | -30.9403 | 87.1433 | 827.9763 | 95.483 | 131 | 115 | 19 | 9.06 | 9.48 | 18.54 | 18.54 | 0.37374 | 0.48867 | 13.762 | 13.762 | 3.9547 | 100.0453 | 0.13756 | 5.78 | 7.45 | 23.3 | 290.9 | NA | 546.6443 | #VALUE! | 91.9904 | 418.7722 | 94.4361 | 115 | 97 | 19 | 4.68 | 4.8 | 9.48 | 9.48 | 0.38094 | 0.49367 | 14.2177 | 14.2177 | #VALUE! | #VALUE! | #VALUE! | 5.78 | 7.51 | 34.6 | NA | 945.1 | #VALUE! | #VALUE! | 88.1059 | #VALUE! | #VALUE! | 97 | 56 | 19 | 1.32 | 4.85 | 6.17 | 6.17 | 0.22048 | 0.21394 | 11.7333 | 11.7333 | 8.5502 | 48.9498 | 0.2397 | 7.45 | 7.45 | 192.5 | 945.1 | 1042.5 | 1149.9313 | -10.3052 | 33.8261 | 1047.5157 | 81.6232 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.15552 | 3.9576 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.21661 | 4.4304 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 6.3855 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 14.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.8621 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 3.04 | NR | --- | 70.9 | --- | 43.9689 | 48.3 | 70.1863 | SUVA | L/(mg*m) | #VALUE! | 8.0383 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 2.6036 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-06-05 | 19:30 | 298.5 | 29 | 131 | 58 | 19.5 | 0 | 15 | 3.67 |  | 18.67 | 18.67 | 0.80343 | 0 | 13.6364 | 13.6364 | 7.8403 | 67.1597 | 0.20304 | 8.28 | 5.79 | 37.1 | 294.7 | 294.7 | 1048.7 | 1347.561 | -28.4982 | 87.4109 | 821.1305 | 95.4818 | 131 | 115.3 | 19.5 | 9.06 | 9.61 | 18.67 | 18.67 | 0.3772 | 0.48527 | 13.762 | 13.762 | 3.9933 | 99.6567 | 0.13809 | 5.79 | 7.51 | 23.3 | 294.7 | NA | 550.5672 | #VALUE! | 92.0937 | 422.6336 | 94.487 | 115.3 | 98 | 19.5 | 4.62 | 4.99 | 9.61 | 9.61 | 0.38947 | 0.48075 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.79 | 7.49 | 33.3 | NA | 888.2 | #VALUE! | #VALUE! | 88.7004 | #VALUE! | #VALUE! | 98 | 58 | 19.5 | 1.26 | 5.22 | 6.48 | 6.48 | 0.23409 | 0.19444 | 11.2 | 11.2 | 7.7854 | 50.7146 | 0.22084 | 7.51 | 7.51 | 193.5 | 888.2 | 1048.7 | 1055.8862 | -0.68525 | 34.34 | 972.0431 | 80.0935 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 3.12 | NR | --- | 13.4224 | --- | 80.2198 | 8.0762 | 93.3137 | [8 empty] | SDS-DCBAA | mg/L | 0.54 | NR | --- | 47.52 | --- | 74 | 29.76 | 89.5161 | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-06-06 | 3:30 | 306.5 | 29 | 131.6 | 58 | 20 | 0 | 14.96 | 3.58 |  | 18.54 | 18.54 | 0.8069 | 0 | 13.6 | 13.6 | 7.9752 | 66.8248 | 0.20352 | 8.15 | 5.76 | 37.05 | 295.2 | 295.2 | 1049 | 1373.9497 | -30.9771 | 87.4492 | 834.5749 | 95.5606 | 131.6 | 115.6 | 20 | 9.06 | 9.48 | 18.54 | 18.54 | 0.37374 | 0.48867 | 13.762 | 13.762 | 4.0168 | 99.5832 | 0.1382 | 5.76 | 7.49 | 23.4 | 295.2 | NA | 554.9582 | #VALUE! | 92.0732 | 425.0791 | 94.4951 | 115.6 | 99 | 20 | 4.62 | 4.86 | 9.48 | 9.48 | 0.38254 | 0.48734 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.76 | 7.44 | 35.8 | NA | 890.2 | #VALUE! | #VALUE! | 87.8726 | #VALUE! | #VALUE! | 99 | 58 | 20 | 1.32 | 4.79 | 6.11 | 6.11 | 0.21808 | 0.21604 | 11.7333 | 11.7333 | 8.0009 | 50.4991 | 0.23235 | 7.49 | 7.49 | 187 | 890.2 | 1049 | 1083.9837 | -3.335 | 36.6531 | 987.0919 | 81.0555 | SDS-HAA5 | mg/L | 43.93 | 0 | --- | -187.2805 | --- | #DIV/0! | -93.6403 | 146.9136 | [8 empty] | SDS-HAA5 | mg/L | 56.93 | 0 | --- | -242.7016 | --- | #DIV/0! | -121.3508 | 146.9136 | [8 empty] | SDS-HAA5 | mg/L | 11.56 | 0 | --- | -46.24 | --- | #DIV/0! | -23.12 | 150 | [8 empty] | SDS-HAA5 | mg/L | 24.89 | 0 | --- | 7674.9888 | --- | 97.9708 | 4501.0444 | 99.4017 | [8 empty] | SDS-HAA5 | mg/L | 17.26 | 0 | --- | 1927.14 | --- | 81.4812 | 1189.8 | 92.9576 | [8 empty] | SDS-HAA5 | mg/L | 6.21 | 0 | --- | -30.3194 | --- | #DIV/0! | -15.1597 | 140.9639
|  | Field 1-2b: Manufacturer Reported Membrane Characteristics1 |  | maximum system recycle flow rates. | [6 empty] | 1998-06-06 | 11:00 | 314 | 29 | 131.3 | 54 | 18.5 | 0 | 15.06 | 3.3 |  | 18.36 | 18.36 | 0.82026 | 0 | 13.6909 | 13.6909 | 8.2981 | 65.8519 | 0.2079 | 8.3 | 5.82 | 37.15 | 290 | 290 | 1041.7 | 1443.9155 | -38.6114 | 87.1897 | 866.9577 | 95.7149 | 131.3 | 115.4 | 18.5 | 9.06 | 9.3 | 18.36 | 18.36 | 0.36893 | 0.49346 | 13.762 | 13.762 | 3.9705 | 100.8795 | 0.13642 | 5.82 | 7.44 | 23 | 290 | NA | 550.1097 | #VALUE! | 92.069 | 420.0548 | 94.5245 | 115.4 | 98 | 18.5 | 4.68 | 4.62 | 9.3 | 9.3 | 0.37133 | 0.50323 | 14.2177 | 14.2177 | #VALUE! | #VALUE! | #VALUE! | 5.82 | 7.51 | 34.6 | NA | 901.6 | #VALUE! | #VALUE! | 88.069 | #VALUE! | #VALUE! | 98 | 54 | 18.5 | 1.26 | 4.8 | 6.06 | 6.06 | 0.21728 | 0.20792 | 11.2 | 11.2 | 8.0952 | 49.4048 | 0.2267 | 7.44 | 7.44 | 186 | 901.6 | 1041.7 | 1089.445 | -4.5834 | 35.8621 | 995.5225 | 81.3163 | SDS-HAA6 | mg/L | 53.13 | 0 | --- | -226.5016 | --- | #DIV/0! | -113.2508 | 146.9136 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 74.23 | 0 | --- | -316.4542 | --- | #DIV/0! | -158.2271 | 146.9136 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 11.56 | 0 | --- | -46.24 | --- | #DIV/0! | -23.12 | 150 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 27.03 | 0 | --- | 7779.5006 | --- | 97.6258 | 4564.3003 | 99.2982 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 22.36 | 0 | --- | 1927.63 | --- | 81.0839 | 1190.95 | 92.7848 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 6.21 | 0 | --- | -30.3194 | --- | #DIV/0! | -15.1597 | 140.9639 | Stage 3 Operating Parameters During Sample Collection
|  | General Information | [8 empty] | 1998-06-06 | 19:30 | 322.5 | 29 | 132.9 | 58 | 19.5 | 0 | 15 | 3.78 |  | 18.78 | 18.78 | 0.79872 | 0 | 13.6364 | 13.6364 | 7.6558 | 68.2942 | 0.19967 | 7.4 | 5.79 | 37.25 | 293.8 | 293.8 | 1048.32 | 1311.8556 | -25.1388 | 87.3213 | 802.8278 | 95.3602 | 132.9 | 116 | 19.5 | 9.06 | 9.72 | 18.78 | 18.78 | 0.38014 | 0.48243 | 13.762 | 13.762 | 3.9627 | 100.9873 | 0.13627 | 5.79 | 7.51 | 23.5 | 293.8 | NA | 545.7463 | #VALUE! | 92.0014 | 419.7731 | 94.4017 | 116 | 99.5 | 19.5 | 4.62 | 5.1 | 9.72 | 9.72 | 0.39534 | 0.47531 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.79 | 7.45 | 36 | NA | 898.1 | #VALUE! | #VALUE! | 87.7468 | #VALUE! | #VALUE! | 99.5 | 58 | 19.5 | 1.32 | 4.99 | 6.31 | 6.31 | 0.22608 | 0.20919 | 11.7333 | 11.7333 | 8.0572 | 51.1928 | 0.2292 | 7.51 | 7.51 | 186.5 | 898.1 | 1048.32 | 1086.3389 | -3.6266 | 36.5214 | 992.2194 | 81.2038 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.26 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.19 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.25 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.29 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.26 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.29
|  | Membrane manufacturer | FLUID SYSTEMS CORP. | Summary of the Stage and System Flow Rates | [6 empty] | 1998-06-07 | 3:30 | 330.5 | 29 | 132.1 | 56 | 20 | 0 | 15.06 | 3.36 |  | 18.42 | 18.42 | 0.81759 | 0 | 13.6909 | 13.6909 | 8.3668 | 65.6832 | 0.20844 | 7.98 | 5.75 | 37.05 | 295.2 | 295.2 | 1052 | 1452.2652 | -38.048 | 87.4492 | 873.7326 | 95.7596 | 132.1 | 116.1 | 20 | 9.12 | 9.3 | 18.42 | 18.42 | 0.36973 | 0.49511 | 13.8532 | 13.8532 | 4.0477 | 100.0523 | 0.13846 | 5.75 | 7.45 | 23.6 | 295.2 | NA | 561.5432 | #VALUE! | 92.0054 | 428.3716 | 94.4908 | 116.1 | 99 | 20 | 4.62 | 4.68 | 9.3 | 9.3 | 0.37294 | 0.49677 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.75 | 7.48 | 36.4 | NA | 856.6 | #VALUE! | #VALUE! | 87.6694 | #VALUE! | #VALUE! | 99 | 56 | 20 | 1.28 | 4.86 | 6.14 | 6.14 | 0.22008 | 0.20847 | 11.3778 | 11.3778 | 7.5834 | 49.9166 | 0.22794 | 7.45 | 7.45 | 186.5 | 856.6 | 1052 | 1033.0872 | 1.7978 | 36.8225 | 944.8436 | 80.2613 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.32 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.26 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.26 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.2
|  | Membrane trade name | FLUID SYSTEMS | Influent flow rate to stage 1, QI-s(1) (gpm) | 19.1077 | [5 empty] | 1998-06-07 | 1:40 | 328.6667 | 29 | 131.8 | 55 | 19 | 0 | 14.88 | 3.72 |  | 18.6 | 18.6 | 0.8 | 0 | 13.5273 | 13.5273 | 7.662 | 66.738 | 0.20269 | 7.65 | 5.79 | 37.4 | 292.8 | 292.8 | 1045.59 | 1314.4 | -25.7089 | 87.2268 | 803.6 | 95.3459 | 131.8 | 115.3 | 19 | 8.88 | 9.72 | 18.6 | 18.6 | 0.37774 | 0.47742 | 13.4886 | 13.4886 | 3.9282 | 100.6218 | 0.13405 | 5.79 | 7.48 | 23.15 | 292.8 | NA | 539.1469 | #VALUE! | 92.0936 | 415.9735 | 94.4347 | 115.3 | 97 | 19 | 4.68 | 5.04 | 9.72 | 9.72 | 0.39374 | 0.48148 | 14.2177 | 14.2177 | #VALUE! | #VALUE! | #VALUE! | 5.79 | 7.53 | 35.9 | NA | 862.4 | #VALUE! | #VALUE! | 87.7391 | #VALUE! | #VALUE! | 97 | 55 | 19 | 1.32 | 4.62 | 5.94 | 5.94 | 0.21128 | 0.22222 | 11.7333 | 11.7333 | 7.7474 | 49.2526 | 0.23823 | 7.48 | 7.48 | 184.5 | 862.4 | 1045.59 | 1056.0857 | -1.0038 | 36.9877 | 959.2429 | 80.7661 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.99 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.09 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.69 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.09
|  | Membrane element model number | 2540 TFCS / 4921 TFCS | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.2167 | [5 empty] | 1998-06-07 | 19:40 | 346.6667 | 29 | 131.7 | 48 | 20 | 0 | 14.76 | 4.14 |  | 18.9 | 18.9 | 0.78095 | 0 | 13.4182 | 13.4182 | 7.1791 | 62.6709 | 0.21411 | 7.6 | 5.8 | 37.2 | 295.2 | 295.2 | 1055 | 1215.0261 | -15.1683 | 87.3984 | 755.113 | 95.0736 | 131.7 | 115.7 | 20 | 8.88 | 10.02 | 18.9 | 18.9 | 0.38574 | 0.46984 | 13.4886 | 13.4886 | 3.9217 | 99.7783 | 0.13519 | 5.8 | 7.53 | 23.45 | 295.2 | NA | 536.0323 | #VALUE! | 92.0562 | 415.6162 | 94.3578 | 115.7 | 99 | 20 | 4.62 | 5.4 | 10.02 | 10.02 | 0.41135 | 0.46108 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.8 | 7.49 | 34.8 | NA | 854.2 | #VALUE! | #VALUE! | 88.2114 | #VALUE! | #VALUE! | 99 | 48 | 20 | 1.32 | 5.1 | 6.42 | 6.42 | 0.23048 | 0.20561 | 11.7333 | 11.7333 | 7.5411 | 45.9589 | 0.2553 | 7.53 | 7.53 | 186.5 | 854.2 | 1055 | 1027.0165 | 2.6525 | 36.8225 | 940.6082 | 80.1724 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Molecular weight cutoff (Daltons) | 200 | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.8911 | [5 empty] | 1998-06-08 | 3:30 | 354.5 | 29 | 131.7 | 56 | 20.5 | 0 | 14.76 | 4.02 |  | 18.78 | 18.78 | 0.78594 | 0 | 13.4182 | 13.4182 | 7.2285 | 66.1215 | 0.20293 | 7.98 | 5.77 | 37.1 | 292 | 292 | 1057 | 1227.9015 | -16.1685 | 87.2945 | 759.9507 | 95.1181 | 131.7 | 115.9 | 20.5 | 8.88 | 9.9 | 18.78 | 18.78 | 0.38254 | 0.47284 | 13.4886 | 13.4886 | 3.8906 | 99.4094 | 0.13569 | 5.77 | 7.49 | 23.4 | 292 | NA | 532.9261 | #VALUE! | 91.9863 | 412.463 | 94.3268 | 115.9 | 99 | 20.5 | 4.62 | 5.28 | 9.9 | 9.9 | 0.40495 | 0.46667 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.77 | 7.4 | 33.1 | NA | 899.2 | #VALUE! | #VALUE! | 88.6644 | #VALUE! | #VALUE! | 99 | 56 | 20.5 | 1.32 | 4.68 | 6 | 6 | 0.21368 | 0.22 | 11.7333 | 11.7333 | 8.1378 | 48.8622 | 0.24013 | 7.49 | 7.49 | 186 | 899.2 | 1057 | 1100.359 | -4.1021 | 36.3014 | 999.7795 | 81.3959 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.8911 | [5 empty] | 1998-06-08 | 11:30 | 362.5 | 29 | 131.7 | 58 | 18 | 0 | 14.8 | 3.8 |  | 18.6 | 18.6 | 0.7957 | 0 | 13.4545 | 13.4545 | 7.8724 | 68.9776 | 0.19506 | 6.9 | 5.8 | 37.7 | 304.8 | 304.8 | 1068 | 1345.0842 | -25.9442 | 87.6312 | 824.9421 | 95.43 | 131.7 | 115.8 | 18 | 8.9 | 9.7 | 18.6 | 18.6 | 0.37747 | 0.47849 | 13.519 | 13.519 | 4.1071 | 101.6429 | 0.133 | 5.8 | 7.4 | 23.25 | 304.8 | NA | 563.1294 | #VALUE! | 92.372 | 433.9647 | 94.6424 | 115.8 | 98 | 18 | 4.7 | 5 | 9.7 | 9.7 | 0.39214 | 0.48454 | 14.2785 | 14.2785 | #VALUE! | #VALUE! | #VALUE! | 5.8 | 7.43 | 34 | NA | 903.3 | #VALUE! | #VALUE! | 88.8451 | #VALUE! | #VALUE! | 98 | 58 | 18 | 1.32 | 5.04 | 6.36 | 6.36 | 0.22808 | 0.20755 | 11.7333 | 11.7333 | 8.1406 | 51.8594 | 0.22625 | 7.4 | 7.4 | 183.5 | 903.3 | 1068 | 1091.819 | -2.2302 | 39.7966 | 997.5595 | 81.6051 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-2 | CI-s3-2 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-4 | CI-s3-4 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-6 | CI-s3-6 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-8 | CI-s3-8 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-10 | CI-s3-10 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-8 (dup) | CI-s3-8 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.6083 | [5 empty] | 1998-06-08 | 19:00 | 370 | 29 | 132.5 | 58.5 | 20.25 | 0 | 14.88 | 4.26 |  | 19.14 | 19.14 | 0.77743 | 0 | 13.5273 | 13.5273 | 7.237 | 68.013 | 0.19889 | 5.72 | 5.72 | 37.5 | 301 | 301 | 1077 | 1221.3944 | -13.4071 | 87.5415 | 761.1972 | 95.0735 | 132.5 | 116.3 | 20.25 | 8.94 | 10.2 | 19.14 | 19.14 | 0.39134 | 0.46708 | 13.5797 | 13.5797 | 3.9911 | 100.1589 | 0.13558 | 5.72 | 7.43 | 23.5 | 301 | NA | 544.2206 | #VALUE! | 92.1927 | 422.6103 | 94.4393 | 116.3 | 99.5 | 20.25 | 4.62 | 5.58 | 10.2 | 10.2 | 0.42095 | 0.45294 | 14.0354 | 14.0354 | #VALUE! | #VALUE! | #VALUE! | 5.72 | 7.414 | 36.7 | NA | 911.9 | #VALUE! | #VALUE! | 87.8073 | #VALUE! | #VALUE! | 99.5 | 58.5 | 20.25 | 1.26 | 5.4 | 6.66 | 6.66 | 0.24129 | 0.18919 | 11.2 | 11.2 | 8.1148 | 50.6352 | 0.22119 | 7.43 | 7.43 | 185.2 | 911.9 | 1077 | 1081.4633 | -0.41442 | 38.4718 | 996.6817 | 81.4183 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 122.9228 | 61.4614 |  |  |  | Sampling date | MM/DD/YY | 1998-05-27 | 1998-05-27 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 94.8533 | 47.4267 |  |  |  | Sampling date | MM/DD/YY | 1998-06-09 | 1998-06-09 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 467.128 | 233.564 |  |  |  | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | Qp/QT (THM4), % | 78.4581 | 111.18 |  | Qp/QT (HAA5), % | 97.918 | 99.9946 |  |  |  | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | --- | --- | --- | --- | Qp/QT (THM4), % | 73.435 | 106.6747 |  | Qp/QT (HAA5), % | 108.0804 | 115.404 |  |  |  | Sampling date | MM/DD/YY | 1998-07-22 | 1998-07-22 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 869.5652 | 434.7826 |  |  |  | Sampling date | MM/DD/YY | 1998-07-07 | 1998-07-07 | --- | --- | --- | ---
|  | Membrane hydrophobicity | HYDRPHILIC | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 5.2827 | [5 empty] | 1998-06-09 | 14:28 | 389.4656 | 29 | 132.345 | 53.362 | 18.486 | 0 | 14.818 | 3.471 |  | 18.289 | 18.289 | 0.81021 | 0 | 13.4709 | 13.4709 | 8.051 | 66.3165 | 0.20313 | 5.975 | 5.705 | 36.8245 | 299.52 | 293.6732 | 1472.5 | 1390.1824 | 5.5903 | 87.4607 | 841.9278 | 95.6262 | 132.345 | 115.62 | 18.486 | 8.916 | 9.646 | 18.562 | 18.562 | 0.37624 | 0.48034 | 13.5433 | 13.5433 | 4.0216 | 101.4749 | 0.13346 | 5.705 | 7.449 | 17.8285 | 292.8702 | 534.15 | 547.0969 | -2.4238 | 93.9291 | 419.9835 | 95.755 | 115.62 | 100.255 | 18.486 | 4.644 | 5.002 | 9.646 | 9.646 | 0.39076 | 0.48144 | 14.1084 | 14.1084 | 7.3565 | 82.095 | 0.17185 | 5.705 | 7.449 | 31.7285 | 534.15 | 905.85 | 1000.6125 | -10.4612 | 89.196 | 767.3813 | 95.8654 | 100.255 | 53.362 | 18.486 | 1.26 | 5.28 | 6.54 | 6.54 | 0.23649 | 0.19266 | 11.2 | 11.2 | 8.2953 | 50.0272 | 0.22388 | 7.449 | 7.449 | 185 | 926.1 | 1413.6 | 1102.9534 | 21.9756 | 37.0048 | 1014.5267 | 81.7649 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | #VALUE! |  |  |  | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 50.5906 | 48.3059 |  |  |  | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Influent flow rate to stage 3, QI-s(3) (gpm) | 5.2827 | [5 empty] | 1998-06-09 | 22:00 | 397.0003 | 29 | 132.697 | 53.527 | 18.547 | 0 | 14.942 | 3.532 |  | 18.474 | 18.474 | 0.80881 | 0 | 13.5836 | 13.5836 | 8.0125 | 66.5525 | 0.2041 | 6.022 | 5.685 | 36.566 | 300.816 | 293.7695 | 1464.9 | 1381.8598 | 5.6687 | 87.5528 | 837.8147 | 95.6356 | 132.697 | 116.145 | 18.547 | 8.978 | 9.637 | 18.615 | 18.615 | 0.37683 | 0.4823 | 13.6375 | 13.6375 | 4.0441 | 101.8299 | 0.13392 | 5.685 | 7.418 | 17.6512 | 293.5447 | 532.8 | 550.5719 | -3.3356 | 93.9915 | 422.0583 | 95.8178 | 116.145 | 100.292 | 18.547 | 4.645 | 4.992 | 9.637 | 9.637 | 0.39025 | 0.482 | 14.1114 | 14.1114 | 7.3409 | 82.3306 | 0.1714 | 5.685 | 7.418 | 31.7975 | 532.8 | 922.95 | 998.9772 | -8.2374 | 89.176 | 765.8886 | 95.8483 | 100.292 | 53.527 | 18.547 | 1.2 | 5 | 6.2 | 6.2 | 0.22408 | 0.19355 | 10.6667 | 10.6667 | 8.3591 | 50.0034 | 0.21332 | 7.418 | 7.418 | 186.5 | 932.85 | 1407.9 | 1111.974 | 21.019 | 36.5149 | 1022.412 | 81.7588 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 72.17 | 72.17 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 370.42 | 370.42 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 716.21 | 716.21 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 307.0117 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 1056 | 1056 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 181.7273 | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 1416 | 1416 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 1056 | 1056 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 1.8433 | [5 empty] | 1998-06-10 | 6:00 | 405 | 29 | 132.255 | 53.22 | 18.603 | 0 | 14.878 | 3.532 |  | 18.41 | 18.41 | 0.80815 | 0 | 13.5255 | 13.5255 | 8.0162 | 66.1183 | 0.20456 | 6.04 | 5.648 | 36.4015 | 302.256 | 294.4762 | 1442.1 | 1381.5755 | 4.197 | 87.6386 | 838.0258 | 95.6563 | 132.255 | 115.65 | 18.603 | 8.914 | 9.651 | 18.565 | 18.565 | 0.37635 | 0.48015 | 13.5403 | 13.5403 | 3.9359 | 101.4136 | 0.13352 | 5.648 | 7.391 | 16.942 | 286.1892 | 508.95 | 534.8753 | -5.0939 | 94.2467 | 410.5322 | 95.8732 | 115.65 | 100.345 | 18.603 | 4.645 | 5.006 | 9.651 | 9.651 | 0.391 | 0.4813 | 14.1114 | 14.1114 | 7.0091 | 82.3854 | 0.17129 | 5.648 | 7.391 | 30.1702 | 508.95 | 926.1 | 953.2033 | -2.9266 | 89.7546 | 731.0766 | 95.8732 | 100.345 | 53.22 | 18.603 | 1.32 | 5.58 | 6.9 | 6.9 | 0.24969 | 0.1913 | 11.7333 | 11.7333 | 7.762 | 50.4175 | 0.23272 | 7.391 | 7.391 | 187 | 881.1 | 1324.3 | 1045.2957 | 21.0681 | 36.4974 | 963.1978 | 80.5855 | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.83 | 6.4 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.77 | 6.38 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.6 | 6.38 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | NA |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.54 | 6.25 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.53 | 6.16 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.44 | 6.25 | --- | --- | --- | ---
|  | Design Parameters |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 3.4394 | [5 empty] | 1998-06-10 | 12:28 | 411.4625 | 29 | 132.052 | 53.34 | 18.672 | 0 | 14.822 | 3.531 |  | 18.353 | 18.353 | 0.80761 | 0 | 13.4745 | 13.4745 | 7.881 | 66.143 | 0.20372 | 5.981 | 5.708 | 35.2735 | 293.52 | 289.5939 | 1411.7 | 1357.1491 | 3.8642 | 87.8197 | 823.3715 | 95.716 | 132.052 | 115.507 | 18.672 | 8.917 | 9.884 | 18.801 | 18.801 | 0.38261 | 0.47428 | 13.5448 | 13.5448 | 3.9967 | 101.1108 | 0.13396 | 5.708 | 7.442 | 17.6315 | 293.0629 | 535.5 | 541.5475 | -1.1293 | 93.9116 | 417.3052 | 95.7749 | 115.507 | 100.165 | 18.672 | 4.645 | 5.239 | 9.884 | 9.884 | 0.40343 | 0.46995 | 14.1114 | 14.1114 | 7.2707 | 81.8933 | 0.17231 | 5.708 | 7.442 | 31.7515 | 535.5 | 932.85 | 982.1333 | -5.2831 | 89.0359 | 758.8166 | 95.8157 | 100.165 | 53.34 | 18.672 | 1.26 | 3.979 | 5.239 | 5.239 | 0.18443 | 0.2405 | 11.2 | 11.2 | 9.4765 | 48.604 | 0.23043 | 7.442 | 7.442 | 108.8805 | 927 | 1417.4 | 1186.0677 | 16.3209 | 62.4024 | 1056.5339 | 89.6946 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | #VALUE! |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | 1.4569 | NA |  | SDS-CDb, mg/L | 1.4958 | 1.5 |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | 5.7594 | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-06-10 | 12:48 | 411.8022 | 29 | 132.51 | 53.655 | 18.649 | 0 | 14.939 | 3.591 |  | 18.53 | 18.53 | 0.80621 | 0 | 13.5809 | 13.5809 | 7.8189 | 66.6146 | 0.20387 | 5.96 | 5.713 | 35.3205 | 292.272 | 289.1764 | 1413.6 | 1345.2478 | 4.8353 | 87.7858 | 817.2121 | 95.6779 | 132.51 | 115.83 | 18.649 | 8.917 | 9.519 | 18.436 | 18.436 | 0.37287 | 0.48367 | 13.5448 | 13.5448 | 4.0437 | 101.4773 | 0.13348 | 5.713 | 7.441 | 17.6118 | 292.9986 | 535.05 | 550.9695 | -2.9753 | 93.9097 | 421.9841 | 95.8264 | 115.83 | 100.225 | 18.649 | 4.645 | 4.874 | 9.519 | 9.519 | 0.38395 | 0.48797 | 14.1114 | 14.1114 | 7.4312 | 81.9473 | 0.1722 | 5.713 | 7.441 | 31.7515 | 535.05 | 881.1 | 1014.7015 | -15.163 | 89.02 | 774.8758 | 95.9024 | 100.225 | 53.655 | 18.649 | 1.377 | 3.497 | 4.874 | 4.874 | 0.16748 | 0.28252 | 12.24 | 12.24 | 9.7921 | 48.4989 | 0.25238 | 7.441 | 7.441 | 108.866 | 927 | 1415.5 | 1249.1534 | 11.7518 | 62.3531 | 1088.0767 | 89.9946 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 40 | 216 | 279.3025 | 42.8571 | 247.6512 | 83.8483 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | 3.6119 | 8.606 |  |  |  | Alkalinity | mg/L as CaCO3 | 36 | 222 | 284.6631 | 50 | 253.3316 | 85.7894 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 34 | 204 | 261.2727 | 46.875 | 232.6364 | 85.3849 | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | #VALUE! | #VALUE! |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 146 | 194.9965 | 51.7241 | 170.4983 | 83.5775 | TOCb, mg/L | #VALUE! | NA |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 137 | -9.4785 | -163.4615 | 9.2607 | -1379.3626 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 164 | 220.4706 | 48.1481 | 192.2353 | 85.4345
|  | Active membrane area of membrane element used, A (ft2) | 27 | System concentrate waste flow rate, QW-sys (gpm) | 3.4394 | [5 empty] | 1998-06-10 | 20:00 | 419 | 29 | 132.487 | 53.602 | 18.553 | 0 | 14.879 | 3.531 |  | 18.41 | 18.41 | 0.8082 | 0 | 13.5264 | 13.5264 | 7.9274 | 66.5641 | 0.20321 | 6.044 | 5.722 | 35.1795 | 294.048 | 290.3327 | 1390.8 | 1365.5024 | 1.8189 | 87.883 | 827.9175 | 95.7508 | 132.487 | 115.837 | 18.553 | 8.915 | 9.886 | 18.801 | 18.801 | 0.38263 | 0.47418 | 13.5418 | 13.5418 | 3.9959 | 101.6131 | 0.13327 | 5.722 | 7.445 | 17.7497 | 293.1592 | 533.25 | 541.5181 | -1.5505 | 93.8864 | 417.3387 | 95.7469 | 115.837 | 100.225 | 18.553 | 4.645 | 5.241 | 9.886 | 9.886 | 0.40353 | 0.46986 | 14.1114 | 14.1114 | 7.2367 | 82.2413 | 0.17159 | 5.722 | 7.445 | 31.7975 | 533.25 | 927 | 977.6779 | -5.4669 | 89.0479 | 755.464 | 95.791 | 100.225 | 53.602 | 18.553 | 1.319 | 3.922 | 5.241 | 5.241 | 0.18333 | 0.25167 | 11.7244 | 11.7244 | 9.5817 | 48.7788 | 0.24036 | 7.445 | 7.445 | 109.011 | 929.25 | 1409.8 | 1205.1029 | 14.5196 | 62.4531 | 1067.1765 | 89.7851 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | 0.27568 |  |  |  | Total dissolved solids | mg/L | 127 | 933 | 1222.8965 | 56.8027 | 1077.9482 | 88.2184 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | 0.047763 | 0.29438 |  |  |  | Total dissolved solids | mg/L | 185 | 926 | 1175.6417 | 37.0106 | 1050.8209 | 82.3947 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 98.4 | 865 | 1123.2663 | 65.4737 | 994.1332 | 90.1019 | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 104.8 | 892 | 1218.8651 | 63.9863 | 1055.4325 | 90.0704 | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 118.7 | 1009 | 1315.1203 | 61.1202 | 1162.0602 | 89.7854 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 104.8 | 892 | 1218.8651 | 63.9863 | 1055.4325 | 90.0704
|  | Design flux, FW (gfd) | 17.9 | System permeate flow rate, Qp-sys (gpm) | 15.6683 | [5 empty] | 1998-06-11 | 0:00 | 423 | 29 | 132.712 | 53.782 | 18.547 | 0 | 14.816 | 3.532 |  | 18.348 | 18.348 | 0.8075 | 0 | 13.4691 | 13.4691 | 7.9521 | 66.7479 | 0.20179 | 6.013 | 5.698 | 36.1665 | 299.136 | 292.9023 | 1442.1 | 1369.8551 | 5.0097 | 87.6524 | 831.3787 | 95.6498 | 132.712 | 115.777 | 18.547 | 8.914 | 9.701 | 18.615 | 18.615 | 0.37768 | 0.47886 | 13.5403 | 13.5403 | 4.0272 | 101.6703 | 0.13318 | 5.698 | 7.417 | 17.5724 | 293.5126 | 532.8 | 547.0669 | -2.6777 | 94.0006 | 420.2897 | 95.819 | 115.777 | 100.247 | 18.547 | 4.645 | 5.056 | 9.701 | 9.701 | 0.39366 | 0.47882 | 14.1114 | 14.1114 | 7.3113 | 82.1537 | 0.17177 | 5.698 | 7.417 | 31.8032 | 532.8 | 927 | 993.0709 | -7.1274 | 89.142 | 762.9355 | 95.8315 | 100.247 | 53.782 | 18.547 | 1.257 | 3.799 | 5.056 | 5.056 | 0.17716 | 0.24862 | 11.1733 | 11.1733 | 9.5969 | 48.8706 | 0.22863 | 7.417 | 7.417 | 108.9385 | 932.4 | 1407.9 | 1204.8641 | 14.4212 | 62.8072 | 1068.632 | 89.8058 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 86 | 1100 | 1464.7084 | #VALUE! | 1282.3542 | 93.2936 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 74 | 1250 | 1646.1925 | #VALUE! | 1448.0963 | 94.8898 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 66 | 980 | 1287.9251 | #VALUE! | 1133.9626 | 94.1797 | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 64 | 885 | 1225.8997 | 78.6667 | 1055.4498 | 93.9362 | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 70 | 1210 | -321.9771 | -332.1429 | -125.9885 | 1060.4048 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 62 | 940 | 1304.5675 | #VALUE! | 1122.2837 | 94.4756
|  | Net driving pressure at the design flux, NDP (psi) | 109 | System feed flow rate, QF-sys (gpm) | 19.1077 | [5 empty] | 1998-06-11 | 1:52 | 424.8592 | 29 | 133.117 | 53.737 | 18.579 | 0 | 14.876 | 3.532 |  | 18.408 | 18.408 | 0.80813 | 0 | 13.5236 | 13.5236 | 7.9999 | 66.8481 | 0.2023 | 6.028 | 5.71 | 35.297 | 299.136 | 292.8702 | 1413.6 | 1377.7111 | 2.5388 | 87.9479 | 835.2906 | 95.7743 | 133.117 | 116.43 | 18.579 | 8.913 | 9.705 | 18.618 | 18.618 | 0.37778 | 0.47873 | 13.5387 | 13.5387 | 4.0258 | 102.1687 | 0.13251 | 5.71 | 7.443 | 17.6512 | 293.5447 | 536.85 | 546.9232 | -1.8764 | 93.973 | 420.2339 | 95.7997 | 116.43 | 100.337 | 18.579 | 4.645 | 5.06 | 9.705 | 9.705 | 0.39388 | 0.47862 | 14.1114 | 14.1114 | 7.3686 | 82.4359 | 0.17118 | 5.71 | 7.443 | 31.8032 | 536.85 | 929.25 | 1000.4749 | -7.6648 | 89.1408 | 768.6625 | 95.8625 | 100.337 | 53.737 | 18.579 | 1.318 | 3.742 | 5.06 | 5.06 | 0.1761 | 0.26047 | 11.7156 | 11.7156 | 9.6848 | 48.7732 | 0.2402 | 7.443 | 7.443 | 108.9385 | 932.4 | 1407.9 | 1222.438 | 13.173 | 62.8031 | 1077.419 | 89.8889 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | 40.4985 |  |  |  | Calcium hardness | mg/L as CaCO3 | 76 | 1020 | 1359.5313 | 71.8519 | 1189.7657 | 93.6122 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | 20.7792 | 46.3896 |  |  |  | Calcium hardness | mg/L as CaCO3 | 68 | 1150 | 1514.5241 | 73.6434 | 1332.262 | 94.8959 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 54 | 972 | 1281.2727 | 78.7402 | 1126.6364 | 95.207 | Alkb, mg/L CaCO3 | 23.4784 | NA |  | Alkb, mg/L CaCO3 | 14.9161 | 14.0024 |  |  |  | Calcium hardness | mg/L as CaCO3 | 58 | 810 | 1122.2491 | 78.0303 | 966.1246 | 93.9966 | Alkb, mg/L CaCO3 | 28.5008 | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 66 | 1020 | -262.0229 | -286.3636 | -98.0115 | 1140.6946 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 50 | 885 | 1231.7128 | 80.4688 | 1058.3564 | 95.2757
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | [7 empty] | 1998-06-11 | 9:00 | 432.0003 | 29 | 132.795 | 53.505 | 18.664 | 0 | 14.819 | 3.531 |  | 18.35 | 18.35 | 0.80757 | 0 | 13.4718 | 13.4718 | 8.006 | 66.48 | 0.20264 | 6.147 | 5.704 | 35.156 | 299.712 | 293.5447 | 1407.9 | 1377.9576 | 2.1267 | 88.0236 | 835.7511 | 95.7935 | 132.795 | 116.092 | 18.664 | 8.917 | 9.758 | 18.675 | 18.675 | 0.37924 | 0.47748 | 13.5448 | 13.5448 | 3.9654 | 101.8141 | 0.13303 | 5.704 | 7.439 | 17.5133 | 289.6903 | 522.45 | 538.4095 | -3.0547 | 94.0339 | 414.0499 | 95.7702 | 116.092 | 100.202 | 18.664 | 4.645 | 5.113 | 9.758 | 9.758 | 0.3967 | 0.47602 | 14.1114 | 14.1114 | 7.1449 | 82.3381 | 0.17138 | 5.704 | 7.439 | 31.1305 | 522.45 | 932.4 | 968.7983 | -3.9037 | 89.395 | 745.6242 | 95.8249 | 100.202 | 53.505 | 18.664 | 1.257 | 3.856 | 5.113 | 5.113 | 0.17945 | 0.24584 | 11.1733 | 11.1733 | 9.3237 | 48.8658 | 0.22865 | 7.439 | 7.439 | 105.502 | 907.2 | 1379.4 | 1168.5419 | 15.2862 | 64.0593 | 1037.871 | 89.8348 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | #VALUE! |  |  |  | Turbidity | ntu | 0.11 | 11.3 | 15.3247 | 65.625 | 13.3124 | 99.1737 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  |  |  | Turbidity | ntu | 0.14 | 30 | 40.0598 | 44 | 35.0299 | 99.6003 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.15 | 17.3 | 23.0778 | 94.0476 | 20.1889 | 99.257 | T-Hdb, mg/L CaCO3 | 72.4716 | NA |  | T-Hdb, mg/L CaCO3 | 16.0379 | 10.0156 |  |  |  | Turbidity | ntu | 0.29 | 24.8 | 34.9772 | 67.4157 | 29.8886 | 99.0297 | T-Hdb, mg/L CaCO3 | 93.4752 | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 28.2 | 0.52 | -8.9975 | 45.7692 | -4.2387 | 765.2922 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 28 | 61 | 74.7024 | -2334.7826 | 67.8512 | 58.7332
|  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Calculate the Required System Influent Pressure | [6 empty] | 1998-06-11 | 17:00 | 440 | 29 | 132.862 | 53.61 | 18.675 | 0 | 14.94 | 3.531 |  | 18.471 | 18.471 | 0.80884 | 0 | 13.5818 | 13.5818 | 7.8862 | 66.6748 | 0.2037 | 6.48 | 5.712 | 33.0645 | 286.08 | 286.1892 | 1324.3 | 1357.1841 | -2.4831 | 88.4466 | 821.6867 | 95.976 | 132.862 | 116.085 | 18.675 | 8.977 | 9.521 | 18.498 | 18.498 | 0.37372 | 0.4853 | 13.6359 | 13.6359 | 4.0114 | 101.7871 | 0.13397 | 5.712 | 7.447 | 17.4542 | 290.0757 | 525.6 | 547.1205 | -4.0945 | 93.9012 | 418.5981 | 95.8303 | 116.085 | 100.3 | 18.675 | 4.644 | 4.877 | 9.521 | 9.521 | 0.38409 | 0.48776 | 14.1084 | 14.1084 | 7.2992 | 82.2183 | 0.1716 | 5.712 | 7.447 | 31.1133 | 525.6 | 932.4 | 996.4625 | -6.8707 | 89.1284 | 761.0313 | 95.9117 | 100.3 | 53.61 | 18.675 | 1.319 | 3.558 | 4.877 | 4.877 | 0.16876 | 0.27045 | 11.7244 | 11.7244 | 9.5321 | 48.7479 | 0.24051 | 7.447 | 7.447 | 105.7485 | 909.9 | 1379.4 | 1208.0101 | 12.425 | 63.0494 | 1058.9551 | 90.0139 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | 117.5757 |  |  |  | Total organic carbon | mg/L | 3.7 | 43.6 | 57.951 | 74.6575 | 50.7755 | 92.713 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | 30.352 | 144.176 |  |  |  | Total organic carbon | mg/L | 3.68 | 63.8 | 84.0543 | 72.9412 | 73.9272 | 95.0221 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 22.4 | 60.6 | 73.4695 | -111.3208 | 67.0348 | 66.5845 | Ca-Hdb, mg/L CaCO3 | 61.5782 | NA |  | Ca-Hdb, mg/L CaCO3 | 11.3717 | 6.0139 |  |  |  | Total organic carbon | mg/L | 12.7 | 49.8 | 65.2048 | -2.4194 | 57.5024 | 77.914 | Ca-Hdb, mg/L CaCO3 | 86.2874 | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 3.5 | 41.5 | 54.5659 | 71.7742 | 48.033 | 92.7133 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 1.28 | 48.2 | 67.6824 | 93.1551 | 57.9412 | 97.7909
|  | Maximum flow rate to the element, QI, max (gpm) | 8 | Osmotic pressure for stage 13, Dp1 (psi) | 2.8 | [5 empty] | 1998-06-12 | 1:00 | 448 | 29 | 133.192 | 53.797 | 18.774 | 0 | 14.939 | 3.592 |  | 18.531 | 18.531 | 0.80616 | 0 | 13.5809 | 13.5809 | 7.9205 | 66.8 | 0.20331 | 6.064 | 5.7 | 35.861 | 298.416 | 293.0629 | 1417.4 | 1362.7563 | 3.8552 | 87.7634 | 827.9096 | 95.6685 | 133.192 | 116.55 | 18.774 | 8.976 | 9.702 | 18.678 | 18.678 | 0.37854 | 0.48057 | 13.6344 | 13.6344 | 3.9934 | 102.1036 | 0.13354 | 5.7 | 7.433 | 17.3951 | 290.429 | 525.6 | 543.0319 | -3.3166 | 94.0644 | 416.7305 | 95.8258 | 116.55 | 100.285 | 18.774 | 4.644 | 5.058 | 9.702 | 9.702 | 0.39374 | 0.47866 | 14.1084 | 14.1084 | 7.2136 | 82.4299 | 0.17116 | 5.7 | 7.433 | 31.2052 | 525.6 | 907.2 | 979.5283 | -7.9727 | 89.352 | 752.5641 | 95.8535 | 100.285 | 53.797 | 18.774 | 1.319 | 3.739 | 5.058 | 5.058 | 0.176 | 0.26078 | 11.7244 | 11.7244 | 9.5028 | 48.7642 | 0.24043 | 7.433 | 7.433 | 105.705 | 913.5 | 1375.6 | 1198.4643 | 12.877 | 63.9309 | 1055.9822 | 89.9899 | Notes: | [9 empty] | UV254 | cm-1 | 0.051 | 1.95 | 2.633 | 92.6407 | 2.2915 | 97.7744 | Notes: | [9 empty] | UV254 | cm-1 | 0.051 | 2.28 | 3.0309 | 90.573 | 2.6555 | 98.0794 | Notes: | [9 empty] | UV254 | cm-1 | 0.061 | 1.8 | 2.3859 | 87.9208 | 2.0929 | 97.0854 | Notes: | [9 empty] | UV254 | cm-1 | 0.38 | 1.7 | 2.2481 | 29.368 | 1.974 | 80.7502 | Notes: | [9 empty] | UV254 | cm-1 | 0.948 | 1.66 | 1.9048 | -122.0141 | 1.7824 | 46.8135 | Notes: | [9 empty] | UV254 | cm-1 | 0 | 1.66 | 2.3493 | 100 | 2.0046 | 100
|  | Minimum flow rate to the element, QI, min (gpm) | 2 | Osmotic pressure for stage 23, Dp2 (psi) | 5 | [5 empty] | 1998-06-12 | 9:00 | 456 | 29 | 132.307 | 53.265 | 18.661 | 0 | 14.938 | 3.531 |  | 18.469 | 18.469 | 0.80881 | 0 | 13.58 | 13.58 | 8.0244 | 66.1006 | 0.20544 | 4.599 | 5.68 | 35.4145 | 298.416 | 292.9986 | 1415.5 | 1382.716 | 2.3161 | 87.9131 | 837.8573 | 95.7732 | 132.307 | 115.612 | 18.661 | 8.977 | 9.636 | 18.613 | 18.613 | 0.37679 | 0.4823 | 13.6359 | 13.6359 | 3.9838 | 101.3147 | 0.13459 | 5.68 | 7.414 | 17.4936 | 289.2727 | 522.45 | 542.465 | -3.831 | 94.0295 | 415.8689 | 95.7935 | 115.612 | 100.21 | 18.661 | 4.643 | 4.993 | 9.636 | 9.636 | 0.39025 | 0.48184 | 14.1053 | 14.1053 | 7.1991 | 82.0509 | 0.17191 | 5.68 | 7.414 | 31.027 | 522.45 | 909.9 | 979.4252 | -7.641 | 89.4105 | 750.9376 | 95.8682 | 100.21 | 53.265 | 18.661 | 1.318 | 3.675 | 4.993 | 4.993 | 0.17342 | 0.26397 | 11.7156 | 11.7156 | 9.4698 | 48.6067 | 0.24103 | 7.414 | 7.414 | 104.2115 | 907.2 | 1381.3 | 1195.1834 | 13.474 | 64.4328 | 1051.1917 | 90.0863 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.3784 | 4.4725 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.3859 | 3.5737 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.27232 | 2.9703 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 2.9921 | 3.4137 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 27.0857 | 4 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0 | 3.444 | --- | --- | --- | ---
|  | Total width of all membrane envelopes in the element, w (ft) | 19.2 | Osmotic pressure for stage 33, Dp3 (psi) | 9 | [5 empty] | 1998-06-12 | 17:00 | 464 | 29 | 132.757 | 53.437 | 18.54 | 0 | 14.879 | 3.53 |  | 18.409 | 18.409 | 0.80825 | 0 | 13.5264 | 13.5264 | 8.016 | 66.541 | 0.20328 | 5.477 | 5.702 | 35.203 | 299.808 | 293.1592 | 1409.8 | 1380.4484 | 2.082 | 87.9919 | 836.8038 | 95.7932 | 132.757 | 115.965 | 18.54 | 8.916 | 9.646 | 18.562 | 18.562 | 0.37624 | 0.48034 | 13.5433 | 13.5433 | 3.9847 | 101.8363 | 0.13299 | 5.702 | 7.449 | 17.139 | 289.6582 | 526.5 | 541.5533 | -2.8591 | 94.1537 | 415.6057 | 95.8761 | 115.965 | 100.172 | 18.54 | 4.644 | 5.002 | 9.646 | 9.646 | 0.39076 | 0.48144 | 14.1084 | 14.1084 | 7.252 | 82.2765 | 0.17147 | 5.702 | 7.449 | 31.2168 | 526.5 | 913.5 | 986.3351 | -7.9732 | 89.3516 | 756.4176 | 95.8731 | 100.172 | 53.437 | 18.54 | 1.319 | 3.683 | 5.002 | 5.002 | 0.17376 | 0.26369 | 11.7244 | 11.7244 | 9.4931 | 48.7714 | 0.2404 | 7.449 | 7.449 | 105.212 | 910.35 | 1381.3 | 1198.6956 | 13.2197 | 64.111 | 1054.5228 | 90.0228 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Feed spacer thickness, T (ft) | 0.0029 | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1998-06-12 | 17:20 | 464.335 | 29 | 132.435 | 53.437 | 18.54 | 0 | 14.879 | 3.53 |  | 18.409 | 18.409 | 0.80825 | 0 | 13.5264 | 13.5264 | 8.0292 | 66.3668 | 0.20381 | 5.477 | 5.702 | 35.1325 | 300.432 | 293.5126 | 1407.9 | 1382.5882 | 1.7978 | 88.0303 | 838.0504 | 95.8078 | 132.435 | 115.845 | 18.54 | 8.916 | 9.646 | 18.562 | 18.562 | 0.37624 | 0.48034 | 13.5433 | 13.5433 | 3.9847 | 101.6153 | 0.13328 | 5.702 | 7.449 | 17.139 | 289.6582 | 526.5 | 541.5533 | -2.8591 | 94.1607 | 415.6057 | 95.8761 | 115.845 | 100.172 | 18.54 | 4.644 | 5.002 | 9.646 | 9.646 | 0.39076 | 0.48144 | 14.1084 | 14.1084 | 7.252 | 82.2165 | 0.1716 | 5.702 | 7.449 | 31.2168 | 526.5 | 907.2 | 986.3351 | -8.723 | 89.3644 | 756.4176 | 95.8731 | 100.172 | 53.437 | 18.54 | 1.319 | 3.683 | 5.002 | 5.002 | 0.17376 | 0.26369 | 11.7244 | 11.7244 | 9.4931 | 48.7714 | 0.2404 | 7.449 | 7.449 | 105.212 | 910.35 | 1381.3 | 1198.6956 | 13.2197 | 64.1542 | 1054.5228 | 90.0228 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses in a single element, DPe (psi) | 6.7 | [5 empty] | 1998-06-13 | 1:00 | 472.0003 | 29 | 132.277 | 53.37 | 18.697 | 0 | 14.816 | 3.532 |  | 18.348 | 18.348 | 0.8075 | 0 | 13.4691 | 13.4691 | 8.004 | 66.1225 | 0.2037 | 5.636 | 5.713 | 35.1325 | 300.576 | 293.5447 | 1407.9 | 1377.5296 | 2.1571 | 88.0316 | 835.5372 | 95.7952 | 132.277 | 115.537 | 18.697 | 8.914 | 9.701 | 18.615 | 18.615 | 0.37768 | 0.47886 | 13.5403 | 13.5403 | 3.9237 | 101.2863 | 0.13368 | 5.713 | 7.448 | 17.0799 | 285.9322 | 509.85 | 532.9738 | -4.5354 | 94.1815 | 409.453 | 95.8286 | 115.537 | 100.225 | 18.697 | 4.644 | 5.057 | 9.701 | 9.701 | 0.39369 | 0.47871 | 14.1084 | 14.1084 | 6.9976 | 82.1864 | 0.17166 | 5.713 | 7.448 | 30.291 | 509.85 | 910.35 | 950.2439 | -4.3823 | 89.681 | 730.047 | 95.8508 | 100.225 | 53.37 | 18.697 | 1.258 | 3.799 | 5.057 | 5.057 | 0.17718 | 0.24876 | 11.1822 | 11.1822 | 9.1729 | 48.9276 | 0.22855 | 7.448 | 7.448 | 99.5135 | 886.5 | 1328.1 | 1147.1025 | 13.6283 | 66.0994 | 1016.8013 | 90.2131 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Design permeate pressure, Pp (psi) | 15 | [5 empty] | 1998-06-13 | 9:00 | 480 | 29 | 132.27 | 53.437 | 18.741 | 0 | 14.877 | 3.531 |  | 18.408 | 18.408 | 0.80818 | 0 | 13.5245 | 13.5245 | 7.9279 | 66.1846 | 0.20435 | 6.097 | 5.715 | 34.498 | 293.184 | 289.6903 | 1379.4 | 1364.8802 | 1.0526 | 88.0914 | 827.2852 | 95.83 | 132.27 | 115.65 | 18.741 | 8.914 | 9.587 | 18.501 | 18.501 | 0.37464 | 0.48181 | 13.5403 | 13.5403 | 3.9306 | 101.2884 | 0.13368 | 5.715 | 7.451 | 16.745 | 285.065 | 506.25 | 534.5491 | -5.59 | 94.2197 | 409.8071 | 95.9139 | 115.65 | 100.27 | 18.741 | 4.645 | 4.942 | 9.587 | 9.587 | 0.38758 | 0.48451 | 14.1114 | 14.1114 | 6.9977 | 82.2213 | 0.17163 | 5.715 | 7.451 | 30.199 | 506.25 | 910.35 | 953.6917 | -4.761 | 89.5754 | 729.9709 | 95.863 | 100.27 | 53.437 | 18.741 | 1.318 | 3.624 | 4.942 | 4.942 | 0.17138 | 0.26669 | 11.7156 | 11.7156 | 9.2656 | 48.8469 | 0.23984 | 7.451 | 7.451 | 99.354 | 883.35 | 1328.1 | 1168.4788 | 12.0188 | 65.7034 | 1025.9144 | 90.3156 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 45.2 | [5 empty] | 1998-06-13 | 17:00 | 488.0003 | 29 | 132.42 | 53.602 | 18.759 | 0 | 14.94 | 3.531 |  | 18.471 | 18.471 | 0.80884 | 0 | 13.5818 | 13.5818 | 7.9641 | 66.2879 | 0.20489 | 6.358 | 5.715 | 34.451 | 293.136 | 290.0757 | 1379.4 | 1371.6485 | 0.56195 | 88.1234 | 830.8621 | 95.8536 | 132.42 | 115.695 | 18.759 | 8.918 | 9.644 | 18.562 | 18.562 | 0.37622 | 0.48044 | 13.5463 | 13.5463 | 3.9253 | 101.3732 | 0.13363 | 5.715 | 7.436 | 17.1587 | 285.5789 | 506.7 | 533.7925 | -5.3468 | 94.0848 | 409.6857 | 95.8117 | 115.695 | 100.15 | 18.759 | 4.645 | 4.999 | 9.644 | 9.644 | 0.39062 | 0.48165 | 14.1114 | 14.1114 | 6.9788 | 82.1847 | 0.1717 | 5.715 | 7.436 | 30.199 | 506.7 | 886.5 | 949.458 | -7.1019 | 89.5893 | 728.079 | 95.8522 | 100.15 | 53.602 | 18.759 | 1.377 | 3.622 | 4.999 | 4.999 | 0.17248 | 0.27546 | 12.24 | 12.24 | 9.2717 | 48.8453 | 0.25059 | 7.436 | 7.436 | 99.325 | 878.4 | 1330 | 1174.5862 | 11.6853 | 65.7589 | 1026.4931 | 90.3239 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Additional Information |  | Net driving pressure required for permeation, NDP (psi) | 110.9231 | [5 empty] | 1998-06-14 | 1:00 | 496 | 29 | 132.442 | 53.467 | 18.658 | 0 | 14.817 | 3.592 |  | 18.409 | 18.409 | 0.80488 | 0 | 13.47 | 13.47 | 7.8415 | 66.455 | 0.20269 | 6.57 | 5.724 | 34.3805 | 294.72 | 290.429 | 1375.6 | 1346.6293 | 2.106 | 88.1622 | 818.5292 | 95.7997 | 132.442 | 115.71 | 18.658 | 8.914 | 9.653 | 18.567 | 18.567 | 0.3764 | 0.4801 | 13.5403 | 13.5403 | 3.9359 | 101.4821 | 0.13343 | 5.724 | 7.442 | 16.9223 | 286.1892 | 508.95 | 534.842 | -5.0873 | 94.1733 | 410.5156 | 95.8778 | 115.71 | 100.345 | 18.658 | 4.645 | 5.008 | 9.653 | 9.653 | 0.3911 | 0.4812 | 14.1114 | 14.1114 | 7.0067 | 82.3628 | 0.17133 | 5.724 | 7.442 | 30.268 | 508.95 | 883.35 | 952.9352 | -7.8774 | 89.5782 | 730.9426 | 95.859 | 100.345 | 53.467 | 18.658 | 1.258 | 3.75 | 5.008 | 5.008 | 0.17522 | 0.2512 | 11.1822 | 11.1822 | 9.1714 | 49.0766 | 0.22785 | 7.442 | 7.442 | 99.7455 | 885.15 | 1322.4 | 1148.627 | 13.1407 | 65.6558 | 1016.8885 | 90.1911 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 1 | Flow weighted system pressure losses, Lsys (psi) | 50.7059 | [5 empty] | 1998-06-14 | 9:00 | 504 | 29 | 132.262 | 53.415 | 18.75 | 0 | 14.878 | 3.592 |  | 18.47 | 18.47 | 0.80552 | 0 | 13.5255 | 13.5255 | 7.8241 | 66.2644 | 0.20411 | 6.028 | 5.713 | 34.498 | 291.552 | 289.2727 | 1381.3 | 1344.5451 | 2.6609 | 88.0742 | 816.9089 | 95.777 | 132.262 | 115.522 | 18.75 | 8.914 | 9.587 | 18.501 | 18.501 | 0.37464 | 0.48181 | 13.5403 | 13.5403 | 3.9315 | 101.2105 | 0.13378 | 5.713 | 7.423 | 17.0405 | 285.4183 | 509.4 | 534.9562 | -5.0169 | 94.1092 | 410.1873 | 95.8457 | 115.522 | 100.247 | 18.75 | 4.645 | 4.942 | 9.587 | 9.587 | 0.38758 | 0.48451 | 14.1114 | 14.1114 | 7.0428 | 82.0917 | 0.1719 | 5.713 | 7.423 | 30.2853 | 509.4 | 878.4 | 959.7213 | -9.2579 | 89.5306 | 734.5607 | 95.8771 | 100.247 | 53.415 | 18.75 | 1.319 | 3.623 | 4.942 | 4.942 | 0.17136 | 0.2669 | 11.7244 | 11.7244 | 9.2537 | 48.8273 | 0.24012 | 7.423 | 7.423 | 99.586 | 882.45 | 1326.2 | 1167.4618 | 11.9694 | 65.5737 | 1024.9559 | 90.2839 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Required influent pressure to the system, PI (psi) | 176.629 | [5 empty] | 1998-06-14 | 17:00 | 512 | 29 | 131.805 | 53.43 | 18.697 | 0 | 14.879 | 3.531 |  | 18.41 | 18.41 | 0.8082 | 0 | 13.5264 | 13.5264 | 7.9291 | 65.9914 | 0.20497 | 6.655 | 5.703 | 34.451 | 293.088 | 289.6582 | 1381.3 | 1365.0553 | 1.176 | 88.1063 | 827.3567 | 95.836 | 131.805 | 114.99 | 18.697 | 8.915 | 9.524 | 18.439 | 18.439 | 0.37298 | 0.48349 | 13.5418 | 13.5418 | 3.9402 | 100.7603 | 0.1344 | 5.703 | 7.436 | 17.1784 | 285.5789 | 510.75 | 536.8169 | -5.1037 | 94.0694 | 411.1979 | 95.8224 | 114.99 | 100.157 | 18.697 | 4.645 | 4.879 | 9.524 | 9.524 | 0.38422 | 0.48772 | 14.1114 | 14.1114 | 7.093 | 81.7835 | 0.17255 | 5.703 | 7.436 | 30.199 | 510.75 | 885.15 | 968.2535 | -9.3886 | 89.5743 | 739.5017 | 95.9163 | 100.157 | 53.43 | 18.697 | 1.319 | 3.56 | 4.879 | 4.879 | 0.16884 | 0.27034 | 11.7244 | 11.7244 | 9.2393 | 48.8572 | 0.23997 | 7.436 | 7.436 | 99.325 | 878.85 | 1330 | 1167.6684 | 12.2054 | 65.7096 | 1023.2592 | 90.2933 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Maximum element recovery (%) | NA | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-06-15 | 1:00 | 520 | 29 | 132.135 | 53.655 | 18.741 | 0 | 14.938 | 3.8 |  | 18.738 | 18.738 | 0.7972 | 0 | 13.58 | 13.58 | 7.5072 | 66.6468 | 0.20376 | 6.154 | 5.712 | 33.135 | 286.176 | 286.2856 | 1326.2 | 1281.4337 | 3.3755 | 88.4259 | 783.8596 | 95.7728 | 132.135 | 115.425 | 18.741 | 8.975 | 9.763 | 18.738 | 18.738 | 0.38015 | 0.47897 | 13.6329 | 13.6329 | 3.93 | 101.109 | 0.13483 | 5.712 | 7.433 | 17.0405 | 286.2856 | 505.35 | 533.7991 | -5.6296 | 94.0477 | 410.0423 | 95.8442 | 115.425 | 100.225 | 18.741 | 4.644 | 5.119 | 9.763 | 9.763 | 0.397 | 0.47567 | 14.1084 | 14.1084 | 6.9056 | 82.1784 | 0.17168 | 5.712 | 7.433 | 30.2853 | 505.35 | 885.6 | 936.3328 | -5.7286 | 89.4213 | 720.8414 | 95.7986 | 100.225 | 53.655 | 18.741 | 1.319 | 3.8 | 5.119 | 5.119 | 0.17844 | 0.25767 | 11.7244 | 11.7244 | 9.2219 | 48.9771 | 0.23939 | 7.433 | 7.433 | 99.789 | 885.6 | 1326.2 | 1158.3591 | 12.6558 | 65.1435 | 1021.9796 | 90.2357 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Variability of design flux (%) | 15 | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-06-15 | 2:16 | 521.2653 | 29 | 132.645 | 53.722 | 18.828 | 0 | 14.875 | 3.687 |  | 18.562 | 18.562 | 0.80137 | 0 | 13.5227 | 13.5227 | 7.6107 | 66.7448 | 0.2026 | 6.177 | 5.699 | 33.1115 | 284.448 | 285.3541 | 1324.3 | 1303.013 | 1.6074 | 88.3963 | 794.1835 | 95.8307 | 132.645 | 115.74 | 18.828 | 8.913 | 9.649 | 18.562 | 18.562 | 0.37628 | 0.48017 | 13.5387 | 13.5387 | 3.9232 | 101.4413 | 0.13346 | 5.699 | 7.42 | 16.9814 | 285.3541 | 505.35 | 533.256 | -5.5221 | 94.049 | 409.305 | 95.8512 | 115.74 | 100.345 | 18.828 | 4.643 | 5.006 | 9.649 | 9.649 | 0.39094 | 0.48119 | 14.1053 | 14.1053 | 6.9552 | 82.2593 | 0.17147 | 5.699 | 7.42 | 30.1818 | 505.35 | 881.55 | 946.0624 | -7.3181 | 89.4231 | 725.7062 | 95.8411 | 100.345 | 53.722 | 18.828 | 1.319 | 3.687 | 5.006 | 5.006 | 0.17392 | 0.26348 | 11.7244 | 11.7244 | 9.223 | 48.9825 | 0.23936 | 7.42 | 7.42 | 99.1945 | 881.55 | 1324.3 | 1161.4325 | 12.2984 | 65.2381 | 1021.4913 | 90.2892
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | [7 empty] | 1998-06-15 | 10:00 | 529 | 29 | 132.367 | 53.242 | 17.935 | 0 | 14.881 | 3.728 |  | 18.609 | 18.609 | 0.79967 | 0 | 13.5282 | 13.5282 | 7.7178 | 67.1517 | 0.20146 | 6.32 | 5.756 | 35.4145 | 299.328 | 293.0308 | 1417.4 | 1321.3536 | 6.7762 | 87.9144 | 807.1922 | 95.6126 | 132.367 | 115.65 | 17.935 | 8.981 | 9.628 | 18.609 | 18.609 | 0.37663 | 0.48262 | 13.642 | 13.642 | 4.0393 | 102.0342 | 0.1337 | 5.756 | 7.448 | 17.5724 | 293.0308 | 535.5 | 549.9784 | -2.7037 | 94.0032 | 421.5046 | 95.831 | 115.65 | 100.142 | 17.935 | 4.642 | 4.986 | 9.628 | 9.628 | 0.38985 | 0.48214 | 14.1023 | 14.1023 | 7.378 | 82.583 | 0.17076 | 5.756 | 7.448 | 32.0562 | 535.5 | 931.5 | 1004.2096 | -7.8056 | 89.0604 | 769.8548 | 95.8361 | 100.142 | 53.242 | 17.935 | 1.258 | 3.728 | 4.986 | 4.986 | 0.17434 | 0.25231 | 11.1822 | 11.1822 | 9.6262 | 49.1308 | 0.2276 | 7.448 | 7.448 | 107.851 | 931.5 | 1417.4 | 1209.4374 | 14.6721 | 63.1946 | 1070.4687 | 89.9249
|  | (e.g., solute type and concentration) | [8 empty] | 1998-06-15 | 18:00 | 537 | 29 | 132.465 | 53.595 | 18.609 | 0 | 14.821 | 3.858 |  | 18.679 | 18.679 | 0.79346 | 0 | 13.4736 | 13.4736 | 7.5366 | 66.8844 | 0.20145 | 5.597 | 5.752 | 35.3205 | 300 | 293.352 | 1398.4 | 1284.6128 | 8.137 | 87.9597 | 788.9824 | 95.5233 | 132.465 | 115.462 | 18.609 | 8.916 | 9.763 | 18.679 | 18.679 | 0.37936 | 0.47733 | 13.5433 | 13.5433 | 4.0182 | 101.3363 | 0.13365 | 5.752 | 7.475 | 17.4936 | 293.352 | 536.85 | 545.2779 | -1.5699 | 94.0367 | 419.3149 | 95.8281 | 115.462 | 100.157 | 18.609 | 4.586 | 5.177 | 9.763 | 9.763 | 0.39854 | 0.46973 | 13.9322 | 13.9322 | 7.2871 | 81.9134 | 0.17008 | 5.752 | 7.475 | 31.8263 | 536.85 | 930.15 | 984.2209 | -5.8131 | 89.1508 | 760.5354 | 95.8153 | 100.157 | 53.595 | 18.609 | 1.319 | 3.858 | 5.177 | 5.177 | 0.18077 | 0.25478 | 11.7244 | 11.7244 | 9.6237 | 48.6433 | 0.24103 | 7.475 | 7.475 | 108.2715 | 930.15 | 1398.4 | 1211.1396 | 13.391 | 63.0916 | 1070.6448 | 89.8873
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-06-16 | 2:00 | 545 | 29 | 132.532 | 53.715 | 18.844 | 0 | 14.939 | 3.623 |  | 18.562 | 18.562 | 0.80482 | 0 | 13.5809 | 13.5809 | 7.8407 | 66.4388 | 0.20441 | 5.371 | 5.7 | 34.404 | 294 | 290.4933 | 1360.4 | 1346.4463 | 1.0257 | 88.1567 | 818.4698 | 95.7965 | 132.532 | 115.942 | 18.844 | 8.975 | 9.587 | 18.562 | 18.562 | 0.37546 | 0.48351 | 13.6329 | 13.6329 | 4.009 | 101.384 | 0.13447 | 5.7 | 7.421 | 17.4148 | 290.4933 | 525.6 | 546.1394 | -3.9078 | 94.0051 | 418.3163 | 95.8369 | 115.942 | 100.24 | 18.844 | 4.645 | 4.942 | 9.587 | 9.587 | 0.38758 | 0.48451 | 14.1114 | 14.1114 | 7.2673 | 81.9797 | 0.17213 | 5.7 | 7.421 | 31.211 | 525.6 | 913.5 | 990.2776 | -8.4048 | 89.2559 | 757.9388 | 95.8821 | 100.24 | 53.715 | 18.844 | 1.319 | 3.623 | 4.942 | 4.942 | 0.17136 | 0.2669 | 11.7244 | 11.7244 | 9.5633 | 48.5702 | 0.24139 | 7.421 | 7.421 | 104.4435 | 913.5 | 1360.4 | 1208.0475 | 11.1991 | 64.0462 | 1060.7737 | 90.154
|  | Standard testing recovery (%) | 10 | [7 empty] | 1998-06-16 | 11:06 | 554.1081 | 29 | 132.781 | 52.515 | 18.076 | 0 | 14.289 | 4.635 |  | 18.924 | 18.924 | 0.75507 | 0 | 12.99 | 12.99 | 6.467 | 68.105 | 0.19073 | 5.733 | 5.733 | 35.8375 | 293.424 | 290.3006 | 1451.6 | 1074.7715 | 25.9595 | 87.655 | 682.536 | 94.7494 | 132.781 | 114.007 | 18.076 | 8.386 | 10.538 | 18.924 | 18.924 | 0.39297 | 0.44314 | 12.7382 | 12.7382 | 3.8108 | 101.5072 | 0.12549 | 5.733 | 7.417 | 17.6906 | 290.3006 | 527.4 | 507.2399 | 3.8225 | 93.9061 | 398.7702 | 95.5637 | 114.007 | 100.37 | 18.076 | 4.585 | 5.953 | 10.538 | 10.538 | 0.43992 | 0.43509 | 13.9291 | 13.9291 | 6.8794 | 82.2331 | 0.16939 | 5.733 | 7.417 | 30.728 | 527.4 | 892.8 | 909.9367 | -1.9194 | 89.4151 | 718.6684 | 95.7243 | 100.37 | 52.515 | 18.076 | 1.318 | 4.635 | 5.953 | 5.953 | 0.21184 | 0.2214 | 11.7156 | 11.7156 | 8.9539 | 49.4126 | 0.2371 | 7.417 | 7.417 | 108.866 | 892.8 | 1451.6 | 1115.718 | 23.1387 | 62.4989 | 1004.259 | 89.1596
|  | Standard testing pH | 7.5 | [7 empty] | 1998-06-16 | 19:00 | 562 | 29 | 132.352 | 52.807 | 18.097 | 0 | 14.276 | 4.402 |  | 18.678 | 18.678 | 0.76432 | 0 | 12.9782 | 12.9782 | 6.6701 | 67.8124 | 0.19138 | 7.923 | 5.712 | 35.673 | 294 | 290.1078 | 1445.9 | 1115.2582 | 22.8675 | 87.7035 | 702.683 | 94.9233 | 132.352 | 113.745 | 18.097 | 8.434 | 10.244 | 18.678 | 18.678 | 0.38577 | 0.45155 | 12.8111 | 12.8111 | 3.8436 | 101.1079 | 0.12671 | 5.712 | 7.448 | 17.8285 | 290.1078 | 526.05 | 514.2785 | 2.2377 | 93.8545 | 402.1932 | 95.5672 | 113.745 | 100.337 | 18.097 | 4.585 | 5.659 | 10.244 | 10.244 | 0.42423 | 0.44758 | 13.9291 | 13.9291 | 6.9516 | 81.9924 | 0.16988 | 5.712 | 7.448 | 31.3087 | 526.05 | 913.95 | 926.8962 | -1.4165 | 89.2079 | 726.4731 | 95.6903 | 100.337 | 52.807 | 18.097 | 1.257 | 4.402 | 5.659 | 5.659 | 0.20129 | 0.22212 | 11.1733 | 11.1733 | 9.1804 | 49.2946 | 0.22666 | 7.448 | 7.448 | 110.606 | 913.95 | 1445.9 | 1143.3465 | 20.9249 | 61.8742 | 1028.6483 | 89.2474
|  | Acceptable range of operating pressures | 80 - 350 | [7 empty] | 1998-06-17 | 3:00 | 570 | 29 | 133.069 | 53.107 | 18.237 | 0 | 14.276 | 4.288 |  | 18.564 | 18.564 | 0.76902 | 0 | 12.9782 | 12.9782 | 6.8024 | 68.0486 | 0.19072 | 8.035 | 5.7 | 35.626 | 294.72 | 290.9108 | 1444 | 1140.8284 | 20.9953 | 87.7536 | 715.8696 | 95.0234 | 133.069 | 114.24 | 18.237 | 8.432 | 10.132 | 18.564 | 18.564 | 0.38275 | 0.45421 | 12.8081 | 12.8081 | 3.8683 | 101.5492 | 0.12613 | 5.7 | 7.433 | 17.7497 | 290.9108 | 525.6 | 518.2396 | 1.4004 | 93.8986 | 404.5752 | 95.6128 | 114.24 | 100.392 | 18.237 | 4.586 | 5.546 | 10.132 | 10.132 | 0.41823 | 0.45263 | 13.9322 | 13.9322 | 6.9852 | 82.0938 | 0.16971 | 5.7 | 7.433 | 31.4065 | 525.6 | 917.55 | 934.2497 | -1.82 | 89.2041 | 729.9249 | 95.6973 | 100.392 | 53.107 | 18.237 | 1.258 | 4.288 | 5.546 | 5.546 | 0.19675 | 0.22683 | 11.1822 | 11.1822 | 9.2658 | 49.2467 | 0.22707 | 7.433 | 7.433 | 109.504 | 917.55 | 1444 | 1154.612 | 20.0407 | 62.3582 | 1036.081 | 89.4309
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 1998-06-17 | 19:00 | 586.0003 | 29 | 132.6 | 52.65 | 18.118 | 0 | 14.398 | 4.103 |  | 18.501 | 18.501 | 0.77823 | 0 | 13.0891 | 13.0891 | 7.021 | 67.486 | 0.19395 | 8.249 | 5.727 | 35.673 | 294.768 | 290.5575 | 1428.8 | 1184.9829 | 17.0645 | 87.7226 | 737.7702 | 95.1648 | 132.6 | 113.91 | 18.118 | 8.497 | 10.004 | 18.501 | 18.501 | 0.3802 | 0.45927 | 12.9068 | 12.9068 | 3.8858 | 101.2512 | 0.12747 | 5.727 | 7.448 | 17.8088 | 290.5575 | 526.05 | 522.2194 | 0.72817 | 93.8708 | 406.3885 | 95.6178 | 113.91 | 100.98 | 18.118 | 4.644 | 5.36 | 10.004 | 10.004 | 0.40986 | 0.46421 | 14.1084 | 14.1084 | 7.0904 | 82.2366 | 0.17156 | 5.727 | 7.448 | 31.326 | 526.05 | 913.95 | 954.6877 | -4.4573 | 89.2187 | 740.3689 | 95.7689 | 100.98 | 52.65 | 18.118 | 1.257 | 4.103 | 5.36 | 5.36 | 0.18933 | 0.23451 | 11.1733 | 11.1733 | 9.2792 | 49.4178 | 0.2261 | 7.448 | 7.448 | 109.2865 | 913.95 | 1428.8 | 1160.4677 | 18.7803 | 62.3873 | 1037.2088 | 89.4634
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-06-18 | 2:21 | 593.3439 | 29 | NR | 54.757 | 19.81 | 0 | 15.63 | 4.666 |  | 20.296 | 20.296 | 0.7701 | 0 | 14.2091 | 14.2091 | 6.8377 | #VALUE! | #VALUE! | 8.083 | 5.859 | 34.8035 | 294.72 | 290.429 | 1518.1 | 1146.7143 | 24.4638 | 88.0165 | 718.5717 | 95.1566 | NR | 129.36 | 19.81 | 9.066 | 11.23 | 20.296 | 20.296 | 0.4205 | 0.44669 | 13.7711 | 13.7711 | 3.8374 | #VALUE! | #VALUE! | 5.859 | 7.508 | 17.0405 | 290.429 | 533.7 | 511.1361 | 4.2278 | 94.1326 | 400.7826 | 95.7482 | 129.36 | 100.957 | 19.81 | 5.126 | 6.104 | 11.23 | 11.23 | 0.46241 | 0.45646 | 15.5727 | 15.5727 | 7.1103 | 88.2382 | 0.17648 | 5.859 | 7.508 | 32.936 | 533.7 | 956.7 | 954.2302 | 0.25816 | 88.6595 | 743.9651 | 95.5729 | 100.957 | 54.757 | 19.81 | 1.438 | 4.666 | 6.104 | 6.104 | 0.21548 | 0.23558 | 12.7822 | 12.7822 | 9.7312 | 48.3158 | 0.26456 | 7.508 | 7.508 | 113.506 | 956.7 | 1518.1 | 1216.5613 | 19.8629 | 60.9178 | 1086.6307 | 89.5543
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-06-18 | 5:23 | 596.3842 | 29 | 136.874 | NR | 18.561 | 0 | 14.818 | 5.175 |  | 19.993 | 19.993 | 0.74116 | 0 | 13.4709 | 13.4709 | 6.2363 | #VALUE! | #VALUE! | 8.131 | 5.724 | 34.357 | 294.816 | 290.8145 | 1324.3 | 1025.1501 | 22.5893 | 88.1859 | 657.9823 | 94.7784 | 136.874 | 116.67 | 18.561 | 9.214 | 10.779 | 19.993 | 19.993 | 0.41044 | 0.46086 | 13.9959 | 13.9959 | 3.8989 | 104.3121 | 0.13417 | 5.724 | 7.356 | 17.6709 | 290.8145 | 513 | 524.3004 | -2.2028 | 93.9237 | 407.5574 | 95.6642 | 116.67 | 100.984 | 18.561 | 4.644 | 6.135 | 10.779 | 10.779 | 0.4512 | 0.43084 | 14.1084 | 14.1084 | 6.7134 | 83.5526 | 0.16886 | 5.724 | 7.356 | 25.99 | 513 | 841.95 | 881.6511 | -4.7154 | 91.063 | 697.3255 | 96.2729 | 100.984 | 30.225 | 18.561 | 0.96 | 5.175 | 6.135 | 6.135 | 0.22628 | 0.15648 | 8.5333 | 8.5333 | 7.9956 | 39.0479 | 0.21853 | 7.356 | 7.356 | 110.258 | 841.95 | 1324.3 | 977.6842 | 26.1735 | 62.0865 | 909.8171 | 87.8813
|  | Maximum permissible turbidity (ntu) | less than 1 | [7 empty] | 1998-06-18 | 13:00 | 604.0003 | 29 | 138.167 | 48.922 | 19.114 | 0 | 15.18 | 4.456 |  | 19.636 | 19.636 | 0.77307 | 0 | 13.8 | 13.8 | 6.8882 | 67.5423 | 0.20432 | 8.879 | 5.745 | 35.015 | 293.328 | 289.8188 | 1385.1 | 1157.8441 | 16.4072 | 87.9183 | 723.8314 | 95.1625 | 138.167 | 118.762 | 19.114 | 9.218 | 10.418 | 19.636 | 19.636 | 0.40087 | 0.46944 | 14.002 | 14.002 | 3.9263 | 105.4242 | 0.13282 | 5.745 | 7.442 | 17.6118 | 289.8188 | 523.35 | 530.6715 | -1.399 | 93.9232 | 410.2451 | 95.707 | 118.762 | 100.917 | 19.114 | 4.762 | 5.656 | 10.418 | 10.418 | 0.4288 | 0.45709 | 14.4668 | 14.4668 | 7.0133 | 83.7122 | 0.17282 | 5.745 | 7.442 | 29.7907 | 523.35 | 891.9 | 938.8962 | -5.2692 | 89.7209 | 731.1231 | 95.9253 | 100.917 | 48.922 | 19.114 | 1.2 | 4.456 | 5.656 | 5.656 | 0.20231 | 0.21216 | 10.6667 | 10.6667 | 8.8992 | 46.9063 | 0.2274 | 7.442 | 7.442 | 107.59 | 891.9 | 1385.1 | 1103.1145 | 20.3585 | 62.8768 | 997.5073 | 89.2141
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-06-18 | 21:00 | 612 | 29 | 138.784 | 49.125 | 19.113 | 0 | 15.36 | 4.459 |  | 19.819 | 19.819 | 0.77501 | 0 | 13.9636 | 13.9636 | 6.9706 | 67.8709 | 0.20574 | 8.063 | 5.724 | 34.3805 | 294.72 | 290.429 | 1360.4 | 1172.4442 | 13.8162 | 88.1622 | 731.4366 | 95.2996 | 138.784 | 119.392 | 19.113 | 9.216 | 10.603 | 19.819 | 19.819 | 0.40577 | 0.46501 | 13.999 | 13.999 | 3.9178 | 106.0572 | 0.13199 | 5.724 | 7.444 | 17.336 | 290.429 | 525.15 | 527.7982 | -0.50428 | 94.0309 | 409.1136 | 95.7625 | 119.392 | 100.975 | 19.113 | 4.826 | 5.777 | 10.603 | 10.603 | 0.43696 | 0.45515 | 14.6613 | 14.6613 | 7.0214 | 84.0491 | 0.17444 | 5.724 | 7.444 | 29.877 | 525.15 | 901.35 | 938.892 | -4.1651 | 89.7128 | 732.021 | 95.9186 | 100.975 | 49.125 | 19.113 | 1.318 | 4.459 | 5.777 | 5.777 | 0.20479 | 0.22815 | 11.7156 | 11.7156 | 9.1185 | 46.8185 | 0.25023 | 7.444 | 7.444 | 106.9085 | 901.35 | 1360.4 | 1136.1726 | 16.4825 | 63.1895 | 1018.7613 | 89.506
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-06-19 | 13:00 | 628 | 29 | 131.313 | 58.852 | 18.804 | 0 | 14.877 | 3.382 |  | 18.259 | 18.259 | 0.81478 | 0 | 13.5245 | 13.5245 | 8.1775 | 68.101 | 0.1986 | 7.902 | 5.671 | 38.305 | 299.28 | 293.898 | 1523.8 | 1418.22 | 6.9287 | 86.9666 | 856.059 | 95.5254 | 131.313 | 113.092 | 18.804 | 8.978 | 9.281 | 18.259 | 18.259 | 0.36733 | 0.4917 | 13.6375 | 13.6375 | 4.079 | 99.3195 | 0.13731 | 5.671 | 7.412 | 18.9711 | 293.898 | 543.15 | 559.8493 | -3.0745 | 93.545 | 426.8736 | 95.5558 | 113.092 | 100.899 | 18.804 | 4.524 | 4.757 | 9.281 | 9.281 | 0.37448 | 0.48745 | 13.7438 | 13.7438 | 7.5142 | 80.6773 | 0.17036 | 5.671 | 7.412 | 33.8905 | 543.15 | 958.5 | 1027.4657 | -7.1952 | 88.4686 | 785.3079 | 95.6844 | 100.899 | 58.852 | 18.804 | 1.375 | 3.382 | 4.757 | 4.757 | 0.16284 | 0.28905 | 12.2222 | 12.2222 | 10.1434 | 50.9281 | 0.23999 | 7.412 | 7.412 | 115.5215 | 958.5 | 1523.8 | 1301.2248 | 14.6066 | 60.6933 | 1129.8624 | 89.7756
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-06-19 | 21:00 | 636 | 29 | 131.688 | 59.152 | 18.78 | 0 | 14.874 | 3.139 |  | 18.013 | 18.013 | 0.82574 | 0 | 13.5218 | 13.5218 | 8.654 | 67.986 | 0.19889 | 8.236 | 5.662 | 37.7175 | 300.672 | 294.5725 | 1495.3 | 1511.6676 | -1.0946 | 87.1959 | 903.1201 | 95.8236 | 131.688 | 113.632 | 18.78 | 8.974 | 9.039 | 18.013 | 18.013 | 0.36082 | 0.4982 | 13.6314 | 13.6314 | 4.1271 | 99.7529 | 0.13665 | 5.662 | 7.433 | 18.7741 | 294.5725 | 545.4 | 568.3877 | -4.2148 | 93.6267 | 431.4801 | 95.6489 | 113.632 | 100.998 | 18.78 | 4.524 | 4.515 | 9.039 | 9.039 | 0.36157 | 0.5005 | 13.7438 | 13.7438 | 7.6768 | 80.8582 | 0.16997 | 5.662 | 7.433 | 33.9537 | 545.4 | 968.4 | 1057.8657 | -9.2385 | 88.4736 | 801.6329 | 95.7644 | 100.998 | 59.152 | 18.78 | 1.376 | 3.139 | 4.515 | 4.515 | 0.15314 | 0.30476 | 12.2311 | 12.2311 | 10.4089 | 50.8861 | 0.24036 | 7.433 | 7.433 | 114.637 | 968.4 | 1495.3 | 1342.6523 | 10.2085 | 61.0836 | 1155.5261 | 90.0792
[11 empty] | 1998-06-20 | 5:00 | 644 | 29 | 131.534 | 59.032 | 18.687 | 0 | 14.873 | 3.263 |  | 18.136 | 18.136 | 0.82008 | 0 | 13.5209 | 13.5209 | 8.341 | 68.255 | 0.19809 | 7.352 | 5.661 | 36.378 | 294.576 | 290.7502 | 1440.2 | 1450.1981 | -0.69422 | 87.4882 | 870.4742 | 95.8209 | 131.534 | 113.737 | 18.687 | 9.031 | 9.105 | 18.136 | 18.136 | 0.36335 | 0.49796 | 13.718 | 13.718 | 4.0813 | 99.8672 | 0.13736 | 5.661 | 7.392 | 17.927 | 290.7502 | 532.35 | 561.3561 | -5.4487 | 93.8342 | 426.0532 | 95.7923 | 113.737 | 100.953 | 18.687 | 4.585 | 4.52 | 9.105 | 9.105 | 0.36347 | 0.50357 | 13.9291 | 13.9291 | 7.5227 | 81.1353 | 0.17168 | 5.661 | 7.392 | 33.2293 | 532.35 | 947.7 | 1038.6484 | -9.5967 | 88.5712 | 785.4992 | 95.7697 | 100.953 | 59.032 | 18.687 | 1.257 | 3.263 | 4.52 | 4.52 | 0.15572 | 0.2781 | 11.1733 | 11.1733 | 9.9909 | 51.3146 | 0.21774 | 7.392 | 7.392 | 109.968 | 947.7 | 1440.2 | 1270.4181 | 11.7888 | 62.1778 | 1109.059 | 90.0846
[11 empty] | 1998-06-20 | 16:00 | 655 | 29 | 130.596 | 58.17 | 18.168 | 0 | 14.394 | 3.868 |  | 18.262 | 18.262 | 0.78819 | 0 | 13.0855 | 13.0855 | 7.2567 | 68.9583 | 0.18976 | 8.056 | 5.668 | 37.0125 | 293.184 | 290.686 | 1499.1 | 1234.682 | 17.6385 | 87.2672 | 762.684 | 95.1471 | 130.596 | 112.5 | 18.168 | 8.433 | 9.829 | 18.262 | 18.262 | 0.37468 | 0.46178 | 12.8096 | 12.8096 | 3.8935 | 99.4865 | 0.12876 | 5.668 | 7.388 | 18.2225 | 290.686 | 533.7 | 524.4519 | 1.7328 | 93.7312 | 407.5689 | 95.529 | 112.5 | 100.912 | 18.168 | 4.585 | 5.244 | 9.829 | 9.829 | 0.40209 | 0.46648 | 13.9291 | 13.9291 | 7.1906 | 81.3474 | 0.17123 | 5.668 | 7.388 | 33.3672 | 533.7 | 938.25 | 971.1572 | -3.5073 | 88.5212 | 752.4286 | 95.5654 | 100.912 | 58.17 | 18.168 | 1.376 | 3.868 | 5.244 | 5.244 | 0.18231 | 0.2624 | 12.2311 | 12.2311 | 9.7366 | 51.6364 | 0.23687 | 7.388 | 7.388 | 111.621 | 938.25 | 1499.1 | 1232.3145 | 17.7964 | 61.6008 | 1085.2823 | 89.715
[11 empty] | 1998-06-21 | 0:00 | 663 | 29 | 130.891 | 58.402 | 18.102 | 0 | 14.392 | 3.917 |  | 18.309 | 18.309 | 0.78606 | 0 | 13.0836 | 13.0836 | 7.2438 | 69.3007 | 0.1888 | 8.082 | 5.673 | 36.425 | 295.44 | 291.746 | 1476.3 | 1229.8566 | 16.6933 | 87.5148 | 760.8013 | 95.2123 | 130.891 | 112.905 | 18.102 | 8.431 | 9.878 | 18.309 | 18.309 | 0.37596 | 0.46048 | 12.8066 | 12.8066 | 3.9059 | 99.8901 | 0.12821 | 5.673 | 7.432 | 17.9861 | 291.746 | 532.8 | 525.4035 | 1.3882 | 93.835 | 408.5747 | 95.5978 | 112.905 | 100.966 | 18.102 | 4.585 | 5.293 | 9.878 | 9.878 | 0.40471 | 0.46416 | 13.9291 | 13.9291 | 7.1564 | 81.6771 | 0.17054 | 5.673 | 7.432 | 33.442 | 532.8 | 948.6 | 965.3631 | -1.7671 | 88.5373 | 749.0815 | 95.5356 | 100.966 | 58.402 | 18.102 | 1.376 | 3.917 | 5.293 | 5.293 | 0.18427 | 0.25997 | 12.2311 | 12.2311 | 9.8409 | 51.7411 | 0.23639 | 7.432 | 7.432 | 111.534 | 948.6 | 1476.3 | 1242.6523 | 15.8266 | 61.7702 | 1095.6261 | 89.8201
[11 empty] | 1998-06-21 | 8:00 | 671.0006 | 29 | 130.603 | 58.492 | 18.127 | 0 | 14.394 | 3.918 |  | 18.312 | 18.312 | 0.78604 | 0 | 13.0855 | 13.0855 | 7.2182 | 69.2023 | 0.18909 | 8.31 | 5.652 | 36.472 | 294.768 | 290.9108 | 1478.2 | 1225.6716 | 17.0835 | 87.4628 | 758.2912 | 95.1902 | 130.603 | 112.395 | 18.127 | 8.434 | 9.878 | 18.312 | 18.312 | 0.376 | 0.46057 | 12.8111 | 12.8111 | 3.8933 | 99.4787 | 0.12878 | 5.652 | 7.398 | 18.0649 | 290.9108 | 533.25 | 523.8712 | 1.7588 | 93.7902 | 407.391 | 95.5657 | 112.395 | 100.989 | 18.127 | 4.584 | 5.294 | 9.878 | 9.878 | 0.40473 | 0.46406 | 13.9261 | 13.9261 | 7.1618 | 81.4032 | 0.17108 | 5.652 | 7.398 | 33.4535 | 533.25 | 945.45 | 966.0167 | -2.1753 | 88.5004 | 749.6334 | 95.5374 | 100.989 | 58.492 | 18.127 | 1.376 | 3.918 | 5.294 | 5.294 | 0.18431 | 0.25992 | 12.2311 | 12.2311 | 9.8119 | 51.8016 | 0.23611 | 7.398 | 7.398 | 110.8235 | 945.45 | 1478.2 | 1238.5705 | 16.2109 | 61.9047 | 1092.0102 | 89.8514
[11 empty] | 1998-06-21 | 16:00 | 679 | 29 | 130.844 | 58.312 | 18.291 | 0 | 14.392 | 3.743 |  | 18.135 | 18.135 | 0.7936 | 0 | 13.0836 | 13.0836 | 7.4251 | 68.8619 | 0.19 | 8.083 | 5.669 | 36.5895 | 294.096 | 290.6539 | 1483.9 | 1267.5426 | 14.5803 | 87.4113 | 779.0983 | 95.3036 | 130.844 | 112.087 | 18.291 | 8.432 | 9.703 | 18.135 | 18.135 | 0.37131 | 0.46496 | 12.8081 | 12.8081 | 3.908 | 99.2665 | 0.12903 | 5.669 | 7.402 | 18.2225 | 290.6539 | 533.25 | 527.3994 | 1.0972 | 93.7305 | 409.0266 | 95.5449 | 112.087 | 100.881 | 18.291 | 4.584 | 5.119 | 9.703 | 9.703 | 0.3954 | 0.47243 | 13.9261 | 13.9261 | 7.237 | 80.956 | 0.17202 | 5.669 | 7.402 | 33.3672 | 533.25 | 942.3 | 980.8887 | -4.0952 | 88.5199 | 757.0694 | 95.5926 | 100.881 | 58.312 | 18.291 | 1.376 | 3.743 | 5.119 | 5.119 | 0.1773 | 0.2688 | 12.2311 | 12.2311 | 9.8486 | 51.4569 | 0.2377 | 7.402 | 7.402 | 110.3595 | 942.3 | 1483.9 | 1248.1376 | 15.888 | 62.0306 | 1095.2188 | 89.9235
[11 empty] | 1998-06-22 | 8:00 | 695 | 29 | 131.079 | 58.665 | 18.111 | 0 | 14.334 | 3.865 |  | 18.199 | 18.199 | 0.78763 | 0 | 13.0309 | 13.0309 | 7.273 | 69.488 | 0.18753 | 8.105 | 5.662 | 36.425 | 295.44 | 291.232 | 1474.4 | 1236.2266 | 16.1539 | 87.4928 | 763.7293 | 95.2306 | 131.079 | 113.077 | 18.111 | 8.431 | 9.768 | 18.199 | 18.199 | 0.37303 | 0.46327 | 12.8066 | 12.8066 | 3.9117 | 100.0553 | 0.128 | 5.662 | 7.418 | 17.9861 | 291.232 | 532.8 | 527.0773 | 1.0741 | 93.8241 | 409.1547 | 95.6041 | 113.077 | 101.002 | 18.111 | 4.585 | 5.183 | 9.768 | 9.768 | 0.39884 | 0.46939 | 13.9291 | 13.9291 | 7.201 | 81.7275 | 0.17043 | 5.662 | 7.418 | 33.534 | 532.8 | 948.6 | 974.4621 | -2.7263 | 88.4855 | 753.631 | 95.5503 | 101.002 | 58.665 | 18.111 | 1.318 | 3.865 | 5.183 | 5.183 | 0.18103 | 0.25429 | 11.7156 | 11.7156 | 9.8128 | 51.9097 | 0.22569 | 7.418 | 7.418 | 110.258 | 948.6 | 1474.4 | 1234.4822 | 16.2722 | 62.1408 | 1091.5411 | 89.8989
[11 empty] | 1998-06-22 | 22:00 | 709 | 29 | 135.152 | 58.132 | 19.059 | 0 | 15.236 | 3.322 |  | 18.558 | 18.558 | 0.82099 | 0 | 13.8509 | 13.8509 | 8.2803 | 69.3027 | 0.19986 | 8.124 | 5.712 | 33.981 | 284.592 | 285.4183 | 1377.5 | 1438.6089 | -4.4362 | 88.0943 | 862.0136 | 96.058 | 135.152 | 116.587 | 19.059 | 9.213 | 9.345 | 18.558 | 18.558 | 0.37218 | 0.49644 | 13.9944 | 13.9944 | 3.9967 | 102.8138 | 0.13611 | 5.712 | 7.447 | 17.7103 | 285.4183 | 509.85 | 549.3449 | -7.7464 | 93.795 | 417.3816 | 95.7568 | 116.587 | 100.935 | 19.059 | 4.706 | 4.639 | 9.345 | 9.345 | 0.37304 | 0.50358 | 14.2967 | 14.2967 | 7.2127 | 82.4893 | 0.17332 | 5.712 | 7.447 | 31.3087 | 509.85 | 894.15 | 995.3027 | -11.3127 | 89.0306 | 752.5764 | 95.8398 | 100.935 | 58.132 | 19.059 | 1.317 | 3.322 | 4.639 | 4.639 | 0.15928 | 0.2839 | 11.7067 | 11.7067 | 9.4936 | 50.9809 | 0.22963 | 7.447 | 7.447 | 101.848 | 894.15 | 1377.5 | 1208.2565 | 12.2863 | 64.3162 | 1051.2032 | 90.3113
[11 empty] | 1998-06-23 | 0:00 | 711 | 29 | 134.945 | 57.937 | 19.06 | 0 | 15.298 | 3.261 |  | 18.559 | 18.559 | 0.82429 | 0 | 13.9073 | 13.9073 | 8.4129 | 68.9681 | 0.20165 | 8.146 | 5.699 | 33.9575 | 284.4 | 285.4183 | 1360.4 | 1465.0711 | -7.6941 | 88.1026 | 875.2447 | 96.1202 | 134.945 | 116.505 | 19.06 | 9.216 | 9.343 | 18.559 | 18.559 | 0.37216 | 0.49658 | 13.999 | 13.999 | 3.9974 | 102.6676 | 0.13635 | 5.699 | 7.446 | 17.7103 | 285.4183 | 509.4 | 549.4874 | -7.8695 | 93.795 | 417.4528 | 95.7575 | 116.505 | 100.935 | 19.06 | 4.706 | 4.637 | 9.343 | 9.343 | 0.37294 | 0.50369 | 14.2967 | 14.2967 | 7.2056 | 82.4544 | 0.17339 | 5.699 | 7.446 | 31.4007 | 509.4 | 897.75 | 994.512 | -10.7783 | 88.9983 | 751.956 | 95.8241 | 100.935 | 57.937 | 19.06 | 1.376 | 3.261 | 4.637 | 4.637 | 0.15802 | 0.29674 | 12.2311 | 12.2311 | 9.6415 | 50.7345 | 0.24108 | 7.446 | 7.446 | 101.5725 | 897.75 | 1360.4 | 1233.7022 | 9.3133 | 64.4128 | 1065.7261 | 90.4692
[11 empty] | 1998-06-23 | 14:00 | 725 | 29 | 133.913 | 50.122 | 18.841 | 0 | 15.057 | 3.801 |  | 18.858 | 18.858 | 0.79844 | 0 | 13.6882 | 13.6882 | 7.4965 | 65.68 | 0.20841 | 8.403 | 5.77 | 33.8165 | 284.928 | 285.322 | 1333.8 | 1281.6171 | 3.9124 | 88.148 | 783.4695 | 95.6838 | 133.913 | 115.147 | 18.841 | 9.155 | 9.703 | 18.858 | 18.858 | 0.38095 | 0.48547 | 13.9063 | 13.9063 | 3.9447 | 101.7443 | 0.13668 | 5.77 | 7.457 | 17.2966 | 285.322 | 505.35 | 538.21 | -6.5024 | 93.9379 | 411.766 | 95.7994 | 115.147 | 100.926 | 18.841 | 4.644 | 5.059 | 9.703 | 9.703 | 0.3938 | 0.47861 | 14.1084 | 14.1084 | 6.9483 | 82.2472 | 0.17154 | 5.77 | 7.457 | 29.1065 | 505.35 | 864.45 | 942.5263 | -9.0319 | 89.7987 | 723.9381 | 95.9794 | 100.926 | 50.122 | 18.841 | 1.258 | 3.801 | 5.059 | 5.059 | 0.17726 | 0.24867 | 11.1822 | 11.1822 | 8.9279 | 47.7551 | 0.23416 | 7.457 | 7.457 | 98.426 | 864.45 | 1333.8 | 1117.9775 | 16.181 | 65.5035 | 991.2138 | 90.0702
[11 empty] | 1998-06-24 | 3:26 | 738.4367 | 29 | 133.189 | 44.332 | 18.595 | 0 | 14.875 | 3.981 |  | 18.856 | 18.856 | 0.78887 | 0 | 13.5227 | 13.5227 | 7.2397 | 62.9258 | 0.2149 | 8.345 | 5.72 | 34.6155 | 287.616 | 287.0243 | 1345.2 | 1230.1495 | 8.5527 | 87.9399 | 758.5869 | 95.4368 | 133.189 | 114.097 | 18.595 | 9.151 | 9.705 | 18.856 | 18.856 | 0.38095 | 0.48531 | 13.9003 | 13.9003 | 3.9655 | 101.0825 | 0.13751 | 5.72 | 7.527 | 17.533 | 287.0243 | 519.75 | 541.132 | -4.1139 | 93.8915 | 414.0782 | 95.7658 | 114.097 | 101.029 | 18.595 | 4.706 | 4.999 | 9.705 | 9.705 | 0.39225 | 0.4849 | 14.2967 | 14.2967 | 7.1555 | 81.8125 | 0.17475 | 5.72 | 7.527 | 33.212 | 519.75 | 931.5 | 977.7712 | -4.9674 | 88.4289 | 748.7606 | 95.5644 | 101.029 | 44.332 | 18.595 | 1.018 | 3.981 | 4.999 | 4.999 | 0.17967 | 0.20364 | 9.0489 | 9.0489 | 9.3125 | 44.773 | 0.20211 | 7.527 | 7.527 | 105.821 | 931.5 | 1345.2 | 1142.6382 | 15.0581 | 63.1317 | 1037.0691 | 89.7961
[11 empty] | 1998-06-24 | 11:00 | 746.0003 | 29 | 132.72 | 47.647 | 18.735 | 0 | 14.762 | 4.271 |  | 19.033 | 19.033 | 0.7756 | 0 | 13.42 | 13.42 | 6.8506 | 64.5979 | 0.20775 | 8.358 | 5.731 | 34.5685 | 284.832 | 285.6753 | 1366.1 | 1153.584 | 15.5564 | 87.8994 | 719.6297 | 95.1963 | 132.72 | 113.692 | 18.735 | 9.039 | 9.994 | 19.033 | 19.033 | 0.38717 | 0.47491 | 13.7301 | 13.7301 | 3.8883 | 100.5827 | 0.13651 | 5.731 | 7.405 | 17.927 | 285.6753 | 507.15 | 527.8382 | -4.0793 | 93.7247 | 406.7568 | 95.5927 | 113.692 | 100.948 | 18.735 | 4.586 | 5.408 | 9.994 | 9.994 | 0.41087 | 0.45888 | 13.9322 | 13.9322 | 6.8148 | 81.7702 | 0.17038 | 5.731 | 7.405 | 28.5832 | 507.15 | 859.95 | 912.976 | -6.1662 | 89.9945 | 710.063 | 95.9745 | 100.948 | 47.647 | 18.735 | 1.137 | 4.271 | 5.408 | 5.408 | 0.19365 | 0.21024 | 10.1067 | 10.1067 | 8.5977 | 46.9648 | 0.2152 | 7.405 | 7.405 | 101.181 | 859.95 | 1366.1 | 1061.9449 | 22.2645 | 64.5818 | 960.9475 | 89.4707
[11 empty] | 1998-06-24 | 14:06 | 749.0961 | 29 | 132.734 | 47.64 | 18.702 | 0 | 14.698 | 3.974 |  | 18.672 | 18.672 | 0.78717 | 0 | 13.3618 | 13.3618 | 7.1675 | 64.3175 | 0.20775 | 7.555 | 5.754 | 34.5685 | 285.984 | 286.125 | 1362.3 | 1216.5167 | 10.7013 | 87.9184 | 751.3208 | 95.399 | 132.734 | 113.932 | 18.702 | 8.978 | 9.694 | 18.672 | 18.672 | 0.37835 | 0.48083 | 13.6375 | 13.6375 | 3.9236 | 100.7074 | 0.13542 | 5.754 | 7.403 | 17.9467 | 286.125 | 507.15 | 534.4955 | -5.392 | 93.7277 | 410.3103 | 95.6261 | 113.932 | 100.894 | 18.702 | 4.585 | 5.109 | 9.694 | 9.694 | 0.39489 | 0.47297 | 13.9291 | 13.9291 | 6.9331 | 81.7779 | 0.17033 | 5.754 | 7.403 | 28.5832 | 507.15 | 859.95 | 936.633 | -8.9171 | 90.0102 | 721.8915 | 96.0405 | 100.894 | 47.64 | 18.702 | 1.135 | 3.974 | 5.109 | 5.109 | 0.18173 | 0.22216 | 10.0889 | 10.0889 | 8.6741 | 46.8909 | 0.21516 | 7.403 | 7.403 | 100.9345 | 859.95 | 1362.3 | 1076.7297 | 20.9624 | 64.7236 | 968.3399 | 89.5765
[11 empty] | 1998-06-24 | 22:00 | 757.0003 | 29 | 133.075 | 47.737 | 18.723 | 0 | 14.818 | 4.097 |  | 18.915 | 18.915 | 0.7834 | 0 | 13.4709 | 13.4709 | 7.0999 | 64.5831 | 0.20858 | 8.52 | 5.676 | 33.9575 | 287.04 | 286.7674 | 1341.4 | 1201.1282 | 10.4571 | 88.1585 | 743.9478 | 95.4355 | 133.075 | 113.872 | 18.723 | 8.976 | 9.939 | 18.915 | 18.915 | 0.38486 | 0.47454 | 13.6344 | 13.6344 | 3.9055 | 100.845 | 0.1352 | 5.676 | 7.333 | 17.7103 | 286.7674 | 509.4 | 529.7552 | -3.9959 | 93.8242 | 408.2613 | 95.662 | 113.872 | 101.002 | 18.723 | 4.643 | 5.296 | 9.939 | 9.939 | 0.40641 | 0.46715 | 14.1053 | 14.1053 | 6.9134 | 81.8006 | 0.17244 | 5.676 | 7.333 | 28.75 | 509.4 | 866.25 | 930.7856 | -7.45 | 89.9745 | 720.0928 | 96.0075 | 101.002 | 47.737 | 18.723 | 1.199 | 4.097 | 5.296 | 5.296 | 0.18793 | 0.2264 | 10.6578 | 10.6578 | 8.7772 | 46.8693 | 0.22739 | 7.333 | 7.333 | 100.572 | 866.25 | 1341.4 | 1090.3281 | 18.7172 | 64.9291 | 978.289 | 89.7196
[11 empty] | 1998-06-25 | 6:00 | 765.0003 | 29 | 134.121 | 48.135 | 18.565 | 0 | 14.63 | 4.043 |  | 18.673 | 18.673 | 0.78348 | 0 | 13.3 | 13.3 | 7.4219 | 65.1411 | 0.20417 | 8.496 | 5.709 | 38.446 | 316.656 | 302.6346 | 1508.6 | 1258.6277 | 16.5698 | 87.2962 | 780.6312 | 95.075 | 134.121 | 115.14 | 18.565 | 8.97 | 9.703 | 18.673 | 18.673 | 0.37848 | 0.48037 | 13.6253 | 13.6253 | 4.1481 | 101.9174 | 0.13369 | 5.709 | 7.355 | 18.9514 | 302.6346 | 560.25 | 564.8874 | -0.82774 | 93.7379 | 433.761 | 95.6309 | 115.14 | 100.953 | 18.565 | 4.523 | 5.18 | 9.703 | 9.703 | 0.39702 | 0.46614 | 13.7408 | 13.7408 | 7.5917 | 81.8898 | 0.1678 | 5.709 | 7.355 | 31.7975 | 560.25 | 963.9 | 1021.6768 | -5.9941 | 89.4931 | 790.9634 | 95.9799 | 100.953 | 48.135 | 18.565 | 1.137 | 4.043 | 5.18 | 5.18 | 0.18453 | 0.2195 | 10.1067 | 10.1067 | 9.635 | 46.344 | 0.21808 | 7.355 | 7.355 | 119.1755 | 963.9 | 1508.6 | 1201.4592 | 20.3593 | 60.6207 | 1082.6796 | 88.9925
[11 empty] | 1998-06-25 | 10:09 | 769.1517 | 29 | 133.183 | 47.917 | 18.55 | 0 | 14.704 | 4.151 |  | 18.855 | 18.855 | 0.77985 | 0 | 13.3673 | 13.3673 | 7.1677 | 64.8323 | 0.20618 | 8.204 | 5.708 | 37.1065 | 303.6 | 295.761 | 1451.6 | 1211.9872 | 16.5068 | 87.4539 | 753.8741 | 95.0779 | 133.183 | 114.3 | 18.55 | 8.982 | 9.873 | 18.855 | 18.855 | 0.38318 | 0.47637 | 13.6435 | 13.6435 | 4.0321 | 101.1594 | 0.13487 | 5.708 | 7.369 | 18.6165 | 295.761 | 543.6 | 547.8942 | -0.78996 | 93.7056 | 421.8276 | 95.5867 | 114.3 | 100.93 | 18.55 | 4.584 | 5.289 | 9.873 | 9.873 | 0.40447 | 0.4643 | 13.9261 | 13.9261 | 7.3541 | 81.7109 | 0.17043 | 5.708 | 7.369 | 30.5325 | 543.6 | 923.85 | 988.2779 | -6.9738 | 89.6766 | 765.939 | 96.0137 | 100.93 | 47.917 | 18.55 | 1.138 | 4.151 | 5.289 | 5.289 | 0.18887 | 0.21516 | 10.1156 | 10.1156 | 9.2409 | 46.6326 | 0.21692 | 7.369 | 7.369 | 111.157 | 923.85 | 1451.6 | 1146.6504 | 21.0078 | 62.4166 | 1035.2502 | 89.2628
[11 empty] | 1998-06-25 | 13:58 | 772.9628 | 29 | 133.357 | 47.887 | 18.609 | 0 | 14.635 | 4.158 |  | 18.793 | 18.793 | 0.77875 | 0 | 13.3045 | 13.3045 | 7.14 | 64.873 | 0.20509 | 8.751 | 5.729 | 36.989 | 304.272 | 295.6967 | 1430.7 | 1206.2757 | 15.6863 | 87.4909 | 750.9862 | 95.0746 | 133.357 | 114.382 | 18.609 | 8.975 | 9.818 | 18.793 | 18.793 | 0.38162 | 0.47757 | 13.6329 | 13.6329 | 4.0427 | 101.2178 | 0.13469 | 5.729 | 7.398 | 18.2422 | 295.6967 | 542.7 | 549.3282 | -1.2213 | 93.8308 | 422.5125 | 95.6824 | 114.382 | 100.93 | 18.609 | 4.522 | 5.296 | 9.818 | 9.818 | 0.40319 | 0.46058 | 13.7377 | 13.7377 | 7.3071 | 81.7399 | 0.16807 | 5.729 | 7.398 | 30.613 | 542.7 | 922.5 | 979.9465 | -6.2273 | 89.6472 | 761.3232 | 95.979 | 100.93 | 47.887 | 18.609 | 1.138 | 4.158 | 5.296 | 5.296 | 0.18915 | 0.21488 | 10.1156 | 10.1156 | 9.224 | 46.5755 | 0.21719 | 7.398 | 7.398 | 111.128 | 922.5 | 1430.7 | 1144.5638 | 19.9997 | 62.4183 | 1033.5319 | 89.2477
[11 empty] | 1998-06-26 | 1:51 | 784.8531 | 29 | 133.832 | 48.322 | 18.573 | 0 | 14.696 | 4.273 |  | 18.969 | 18.969 | 0.77474 | 0 | 13.36 | 13.36 | 7.0691 | 65.4349 | 0.20417 | 8.977 | 5.71 | 36.378 | 305.664 | 296.307 | 1407.9 | 1190.273 | 15.4576 | 87.7229 | 743.29 | 95.1058 | 133.832 | 115.005 | 18.573 | 8.974 | 9.995 | 18.969 | 18.969 | 0.38633 | 0.47309 | 13.6314 | 13.6314 | 4.0327 | 101.8128 | 0.13389 | 5.71 | 7.359 | 17.9861 | 296.307 | 540.45 | 546.1971 | -1.0634 | 93.9299 | 421.2521 | 95.7303 | 115.005 | 100.966 | 18.573 | 4.585 | 5.41 | 9.995 | 9.995 | 0.41095 | 0.45873 | 13.9291 | 13.9291 | 7.2579 | 82.1546 | 0.16955 | 5.71 | 7.359 | 30.6762 | 540.45 | 928.8 | 972.4856 | -4.7034 | 89.6471 | 756.4678 | 95.9448 | 100.966 | 48.322 | 18.573 | 1.137 | 4.273 | 5.41 | 5.41 | 0.19373 | 0.21017 | 10.1067 | 10.1067 | 9.2738 | 46.7972 | 0.21597 | 7.359 | 7.359 | 110.316 | 928.8 | 1407.9 | 1146.5899 | 18.5603 | 62.7697 | 1037.695 | 89.3691
[11 empty] | 1998-06-26 | 9:00 | 792.0003 | 29 | 133.397 | 48.225 | 18.607 | 0 | 14.756 | 4.096 |  | 18.852 | 18.852 | 0.78273 | 0 | 13.4145 | 13.4145 | 7.2396 | 64.9644 | 0.20649 | 8.738 | 5.713 | 35.6495 | 301.536 | 294.0907 | 1392.7 | 1225.1353 | 12.0316 | 87.8781 | 759.613 | 95.3069 | 133.397 | 114.607 | 18.607 | 8.975 | 9.877 | 18.852 | 18.852 | 0.38319 | 0.47608 | 13.6329 | 13.6329 | 4.0149 | 101.3801 | 0.13447 | 5.713 | 7.372 | 18.0255 | 294.0907 | 533.25 | 544.9448 | -2.1931 | 93.8708 | 419.5177 | 95.7033 | 114.607 | 100.989 | 18.607 | 4.583 | 5.294 | 9.877 | 9.877 | 0.40471 | 0.46401 | 13.923 | 13.923 | 7.2067 | 81.9843 | 0.16983 | 5.713 | 7.372 | 30.2853 | 533.25 | 913.5 | 968.6651 | -6.0389 | 89.7021 | 750.9575 | 95.9671 | 100.989 | 48.225 | 18.607 | 1.198 | 4.096 | 5.294 | 5.294 | 0.18787 | 0.22629 | 10.6489 | 10.6489 | 9.2388 | 46.7612 | 0.22773 | 7.372 | 7.372 | 107.4885 | 913.5 | 1392.7 | 1149.2426 | 17.481 | 63.4506 | 1031.3713 | 89.5781
[11 empty] | 1998-06-26 | 17:00 | 800.0003 | 29 | 133.719 | 48.315 | 18.544 | 0 | 14.693 | 4.04 |  | 18.733 | 18.733 | 0.78434 | 0 | 13.3573 | 13.3573 | 7.3501 | 65.1229 | 0.20511 | 8.845 | 5.732 | 35.908 | 305.472 | 296.6924 | 1406 | 1245.1345 | 11.4414 | 87.8972 | 770.9135 | 95.3421 | 133.719 | 114.982 | 18.544 | 8.972 | 9.761 | 18.733 | 18.733 | 0.38006 | 0.47894 | 13.6284 | 13.6284 | 4.0685 | 101.738 | 0.13396 | 5.732 | 7.372 | 17.9467 | 296.6924 | 540 | 552.9066 | -2.3901 | 93.9511 | 424.7995 | 95.7753 | 114.982 | 101.002 | 18.544 | 4.522 | 5.239 | 9.761 | 9.761 | 0.40015 | 0.46327 | 13.7377 | 13.7377 | 7.2915 | 82.1565 | 0.16721 | 5.732 | 7.372 | 30.6648 | 540 | 927.9 | 979.6286 | -5.5748 | 89.6645 | 759.8143 | 95.9642 | 101.002 | 48.315 | 18.544 | 1.199 | 4.04 | 5.239 | 5.239 | 0.18565 | 0.22886 | 10.6578 | 10.6578 | 9.3937 | 46.7208 | 0.22812 | 7.372 | 7.372 | 109.91 | 927.9 | 1406 | 1170.6649 | 16.7379 | 62.9549 | 1049.2824 | 89.5252
[11 empty] | 1998-06-27 | 1:00 | 808.0003 | 29 | 134.188 | 48.72 | 18.624 | 0 | 14.756 | 3.977 |  | 18.733 | 18.733 | 0.7877 | 0 | 13.4145 | 13.4145 | 7.4454 | 65.3846 | 0.20516 | 9.091 | 5.706 | 36.2135 | 306.192 | 296.9815 | 1419.3 | 1264.5181 | 10.9055 | 87.8061 | 780.7498 | 95.3617 | 134.188 | 115.26 | 18.624 | 8.973 | 9.76 | 18.733 | 18.733 | 0.38004 | 0.47899 | 13.6299 | 13.6299 | 4.0701 | 102.0299 | 0.13359 | 5.706 | 7.332 | 18.1437 | 296.9815 | 539.1 | 553.3352 | -2.6405 | 93.8906 | 425.1584 | 95.7325 | 115.26 | 100.998 | 18.624 | 4.585 | 5.175 | 9.76 | 9.76 | 0.39841 | 0.46977 | 13.9291 | 13.9291 | 7.3355 | 82.1695 | 0.16952 | 5.706 | 7.332 | 30.7452 | 539.1 | 931.05 | 989.4974 | -6.2776 | 89.6474 | 764.2987 | 95.9773 | 100.998 | 48.72 | 18.624 | 1.198 | 3.977 | 5.175 | 5.175 | 0.18311 | 0.2315 | 10.6489 | 10.6489 | 9.4427 | 46.7923 | 0.22758 | 7.332 | 7.332 | 110.3885 | 931.05 | 1419.3 | 1178.2596 | 16.983 | 62.8298 | 1054.6548 | 89.5332
[11 empty] | 1998-06-27 | 9:00 | 816.0003 | 29 | 133.337 | 48.412 | 18.528 | 0 | 14.691 | 4.104 |  | 18.795 | 18.795 | 0.78164 | 0 | 13.3555 | 13.3555 | 7.266 | 65.0805 | 0.20521 | 8.52 | 5.694 | 36.472 | 306.672 | 296.9173 | 1426.9 | 1229.2276 | 13.8533 | 87.7164 | 763.0724 | 95.2204 | 133.337 | 114.562 | 18.528 | 8.971 | 9.824 | 18.795 | 18.795 | 0.38173 | 0.47731 | 13.6268 | 13.6268 | 4.0563 | 101.3652 | 0.13443 | 5.694 | 7.373 | 18.4392 | 296.9173 | 541.8 | 551.2156 | -1.7378 | 93.7898 | 424.0664 | 95.6518 | 114.562 | 100.989 | 18.528 | 4.583 | 5.241 | 9.824 | 9.824 | 0.40188 | 0.46651 | 13.923 | 13.923 | 7.3458 | 81.9017 | 0.17 | 5.694 | 7.373 | 30.6935 | 541.8 | 929.7 | 988.7378 | -6.3502 | 89.6626 | 765.2689 | 95.9892 | 100.989 | 48.412 | 18.528 | 1.137 | 4.104 | 5.241 | 5.241 | 0.18697 | 0.21694 | 10.1067 | 10.1067 | 9.3347 | 46.8378 | 0.21578 | 7.373 | 7.373 | 109.8085 | 929.7 | 1426.9 | 1156.8483 | 18.9258 | 63.0171 | 1043.2742 | 89.4746
[11 empty] | 1998-06-27 | 17:00 | 824 | 29 | 133.437 | 48.465 | 18.451 | 0 | 14.695 | 3.978 |  | 18.673 | 18.673 | 0.78697 | 0 | 13.3591 | 13.3591 | 7.3887 | 65.1113 | 0.20517 | 8.662 | 5.727 | 36.143 | 303.36 | 295.6646 | 1413.6 | 1254.3549 | 11.2652 | 87.7757 | 775.0097 | 95.3364 | 133.437 | 114.75 | 18.451 | 8.975 | 9.698 | 18.673 | 18.673 | 0.37842 | 0.48064 | 13.6329 | 13.6329 | 4.0585 | 101.584 | 0.1342 | 5.727 | 7.386 | 18.2028 | 295.6646 | 542.25 | 552.4412 | -1.8794 | 93.8434 | 424.0529 | 95.7074 | 114.75 | 100.962 | 18.451 | 4.522 | 5.176 | 9.698 | 9.698 | 0.39678 | 0.46628 | 13.7377 | 13.7377 | 7.3529 | 82.0521 | 0.16743 | 5.727 | 7.386 | 30.5038 | 542.25 | 922.05 | 989.3359 | -7.2974 | 89.683 | 765.7929 | 96.0167 | 100.962 | 48.465 | 18.451 | 1.198 | 3.978 | 5.176 | 5.176 | 0.18315 | 0.23145 | 10.6489 | 10.6489 | 9.36 | 46.9025 | 0.22704 | 7.386 | 7.386 | 108.547 | 922.05 | 1413.6 | 1167.0416 | 17.4419 | 63.2871 | 1044.5458 | 89.6082
[11 empty] | 1998-06-28 | 1:00 | 832 | 29 | 133.752 | 48.502 | 18.534 | 0 | 14.757 | 3.85 |  | 18.607 | 18.607 | 0.79309 | 0 | 13.4155 | 13.4155 | 7.5934 | 64.9996 | 0.20639 | 8.841 | 5.71 | 35.9785 | 304.848 | 296.3391 | 1407.9 | 1294.298 | 8.0689 | 87.859 | 795.3186 | 95.4762 | 133.752 | 114.945 | 18.534 | 8.972 | 9.635 | 18.607 | 18.607 | 0.3767 | 0.48218 | 13.6284 | 13.6284 | 4.0789 | 101.7356 | 0.13396 | 5.71 | 7.37 | 18.0255 | 296.3391 | 540.9 | 555.5015 | -2.6995 | 93.9173 | 425.9203 | 95.7679 | 114.945 | 101.016 | 18.534 | 4.586 | 5.049 | 9.635 | 9.635 | 0.39172 | 0.47597 | 13.9322 | 13.9322 | 7.4194 | 82.0271 | 0.16985 | 5.71 | 7.37 | 30.6762 | 540.9 | 928.8 | 1004.3356 | -8.1326 | 89.6483 | 772.6178 | 96.0296 | 101.016 | 48.502 | 18.534 | 1.199 | 3.85 | 5.049 | 5.049 | 0.17804 | 0.23747 | 10.6578 | 10.6578 | 9.4754 | 46.7496 | 0.22798 | 7.37 | 7.37 | 108.924 | 928.8 | 1407.9 | 1184.1328 | 15.8937 | 63.2435 | 1056.4664 | 89.6898
[11 empty] | 1998-06-28 | 9:00 | 840 | 29 | 133.424 | 48.405 | 18.553 | 0 | 14.634 | 4.282 |  | 18.916 | 18.916 | 0.77363 | 0 | 13.3036 | 13.3036 | 7.0387 | 65.3228 | 0.20366 | 9.092 | 5.701 | 36.0725 | 304.368 | 295.9216 | 1409.8 | 1183.9718 | 16.0185 | 87.8101 | 739.9467 | 95.125 | 133.424 | 114.615 | 18.553 | 8.975 | 9.941 | 18.916 | 18.916 | 0.3849 | 0.47447 | 13.6329 | 13.6329 | 4.0328 | 101.4337 | 0.1344 | 5.701 | 7.373 | 18.0649 | 295.9216 | 541.35 | 546.778 | -1.0027 | 93.8954 | 421.3498 | 95.7126 | 114.615 | 100.957 | 18.553 | 4.523 | 5.418 | 9.941 | 9.941 | 0.40972 | 0.45498 | 13.7408 | 13.7408 | 7.2395 | 81.9935 | 0.16758 | 5.701 | 7.373 | 30.5957 | 541.35 | 921.6 | 967.7327 | -5.0057 | 89.6609 | 754.5414 | 95.9451 | 100.957 | 48.405 | 18.553 | 1.136 | 4.282 | 5.418 | 5.418 | 0.19407 | 0.20967 | 10.0978 | 10.0978 | 9.2064 | 46.9216 | 0.21521 | 7.373 | 7.373 | 108.779 | 921.6 | 1409.8 | 1137.2386 | 19.3333 | 63.2406 | 1029.4193 | 89.433
[11 empty] | 1998-06-28 | 17:00 | 848 | 29 | 134.194 | 48.675 | 18.649 | 0 | 14.692 | 4.232 |  | 18.924 | 18.924 | 0.77637 | 0 | 13.3564 | 13.3564 | 7.1232 | 65.6623 | 0.20341 | 8.963 | 5.723 | 36.002 | 304.848 | 296.3712 | 1407.9 | 1200.2807 | 14.7467 | 87.8524 | 748.326 | 95.189 | 134.194 | 115.012 | 18.649 | 9.033 | 9.891 | 18.924 | 18.924 | 0.38434 | 0.47733 | 13.721 | 13.721 | 4.0545 | 101.8995 | 0.13465 | 5.723 | 7.368 | 18.0255 | 296.3712 | 541.35 | 550.5717 | -1.7035 | 93.9179 | 423.4715 | 95.7434 | 115.012 | 101.002 | 18.649 | 4.522 | 5.369 | 9.891 | 9.891 | 0.40708 | 0.45718 | 13.7377 | 13.7377 | 7.2588 | 82.0992 | 0.16733 | 5.723 | 7.368 | 30.5727 | 541.35 | 924.75 | 971.5483 | -5.0606 | 89.6843 | 756.4492 | 95.9584 | 101.002 | 48.675 | 18.649 | 1.137 | 4.232 | 5.369 | 5.369 | 0.19209 | 0.21177 | 10.1067 | 10.1067 | 9.2537 | 46.9358 | 0.21533 | 7.368 | 7.368 | 108.9675 | 924.75 | 1407.9 | 1143.9241 | 18.7496 | 63.2328 | 1034.337 | 89.465
[11 empty] | 1998-06-29 | 1:00 | 856 | 29 | 133.638 | 48.457 | 18.553 | 0 | 14.631 | 3.979 |  | 18.61 | 18.61 | 0.78619 | 0 | 13.3009 | 13.3009 | 7.4018 | 65.0927 | 0.20434 | 8.576 | 5.709 | 35.9315 | 305.664 | 296.6924 | 1406 | 1255.5246 | 10.7024 | 87.8893 | 776.1085 | 95.3703 | 133.638 | 114.75 | 18.553 | 8.971 | 9.639 | 18.61 | 18.61 | 0.37679 | 0.48205 | 13.6268 | 13.6268 | 4.0843 | 101.5567 | 0.13418 | 5.709 | 7.353 | 17.9664 | 296.6924 | 540.9 | 556.1023 | -2.8106 | 93.9444 | 426.3974 | 95.7865 | 114.75 | 101.025 | 18.553 | 4.522 | 5.117 | 9.639 | 9.639 | 0.39364 | 0.46914 | 13.7377 | 13.7377 | 7.3568 | 81.9777 | 0.16758 | 5.709 | 7.353 | 30.6705 | 540.9 | 928.35 | 991.8005 | -6.8348 | 89.6625 | 766.3502 | 95.9978 | 101.025 | 48.457 | 18.553 | 1.138 | 3.979 | 5.117 | 5.117 | 0.18199 | 0.2224 | 10.1156 | 10.1156 | 9.3657 | 46.8223 | 0.21604 | 7.353 | 7.353 | 108.953 | 928.35 | 1406 | 1162.6988 | 17.3045 | 63.2775 | 1045.5244 | 89.5791
[11 empty] | 1998-06-29 | 9:00 | 864 | 29 | 133.672 | 48.052 | 18.579 | 0 | 14.697 | 4.096 |  | 18.793 | 18.793 | 0.78205 | 0 | 13.3609 | 13.3609 | 7.1174 | 65.1656 | 0.20503 | 8.055 | 5.692 | 34.4745 | 292.368 | 289.2085 | 1345.2 | 1203.2283 | 10.5539 | 88.0797 | 746.2184 | 95.3801 | 133.672 | 114.84 | 18.579 | 8.976 | 9.817 | 18.793 | 18.793 | 0.38161 | 0.47762 | 13.6344 | 13.6344 | 3.9562 | 101.7208 | 0.13404 | 5.692 | 7.376 | 17.7103 | 289.2085 | 518.4 | 537.448 | -3.6744 | 93.8763 | 413.3283 | 95.7152 | 114.84 | 100.917 | 18.579 | 4.522 | 5.295 | 9.817 | 9.817 | 0.40313 | 0.46063 | 13.7377 | 13.7377 | 6.9798 | 82.3197 | 0.16688 | 5.692 | 7.376 | 29.279 | 518.4 | 882.9 | 936.1158 | -6.0274 | 89.8762 | 727.2579 | 95.9741 | 100.917 | 48.052 | 18.579 | 1.199 | 4.096 | 5.295 | 5.295 | 0.18789 | 0.22644 | 10.6578 | 10.6578 | 8.9675 | 46.938 | 0.22706 | 7.376 | 7.376 | 100.6445 | 882.9 | 1345.2 | 1111.8854 | 17.3442 | 65.2 | 997.3927 | 89.9092
[11 empty] | 1998-06-29 | 17:00 | 872 | 29 | 133.685 | 48.202 | 18.58 | 0 | 14.7 | 4.269 |  | 18.969 | 18.969 | 0.77495 | 0 | 13.3636 | 13.3636 | 6.9353 | 65.4282 | 0.20425 | 8.782 | 5.718 | 34.5215 | 291.504 | 289.337 | 1347.1 | 1166.776 | 13.3861 | 88.0688 | 728.0565 | 95.2584 | 133.685 | 114.802 | 18.58 | 8.977 | 9.992 | 18.969 | 18.969 | 0.38629 | 0.47325 | 13.6359 | 13.6359 | 3.9384 | 101.7251 | 0.13405 | 5.718 | 7.391 | 17.5724 | 289.337 | 519.3 | 533.4953 | -2.7336 | 93.9267 | 411.4161 | 95.7288 | 114.802 | 100.948 | 18.58 | 4.586 | 5.406 | 9.992 | 9.992 | 0.41076 | 0.45897 | 13.9322 | 13.9322 | 6.9785 | 82.3165 | 0.16925 | 5.718 | 7.391 | 29.2905 | 519.3 | 879.75 | 934.9832 | -6.2783 | 89.8767 | 727.1416 | 95.9718 | 100.948 | 48.202 | 18.58 | 1.137 | 4.269 | 5.406 | 5.406 | 0.19357 | 0.21032 | 10.1067 | 10.1067 | 8.831 | 47.164 | 0.21429 | 7.391 | 7.391 | 100.427 | 879.75 | 1347.1 | 1087.3139 | 19.2848 | 65.2906 | 983.5319 | 89.7891
[11 empty] | 1998-06-30 | 1:00 | 880 | 29 | 133.658 | 48.45 | 18.553 | 0 | 14.757 | 3.976 |  | 18.733 | 18.733 | 0.78775 | 0 | 13.4155 | 13.4155 | 7.3246 | 65.1764 | 0.20583 | 9.07 | 5.698 | 33.9105 | 293.76 | 290.3969 | 1341.4 | 1242.3512 | 7.384 | 88.3227 | 766.374 | 95.5752 | 133.658 | 115.162 | 18.553 | 9.036 | 9.697 | 18.733 | 18.733 | 0.3792 | 0.48236 | 13.7256 | 13.7256 | 3.9979 | 101.8591 | 0.13475 | 5.698 | 7.349 | 17.6709 | 290.3969 | 521.1 | 544.5325 | -4.4967 | 93.9149 | 417.4647 | 95.7671 | 115.162 | 101.002 | 18.553 | 4.584 | 5.113 | 9.697 | 9.697 | 0.39508 | 0.47272 | 13.9261 | 13.9261 | 7.1218 | 82.4072 | 0.16899 | 5.698 | 7.349 | 29.3538 | 521.1 | 886.05 | 961.9693 | -8.5683 | 89.8919 | 741.5347 | 96.0415 | 101.002 | 48.45 | 18.553 | 1.137 | 3.976 | 5.113 | 5.113 | 0.18185 | 0.22237 | 10.1067 | 10.1067 | 8.9784 | 47.1946 | 0.21415 | 7.349 | 7.349 | 100.5285 | 886.05 | 1341.4 | 1110.6823 | 17.1998 | 65.3824 | 998.3661 | 89.9307
[11 empty] | 1998-06-30 | 9:00 | 888 | 29 | 133.109 | 48.082 | 18.58 | 0 | 14.76 | 3.966 |  | 18.726 | 18.726 | 0.78821 | 0 | 13.4182 | 13.4182 | 7.1769 | 64.8386 | 0.20695 | 8.87 | 5.69 | 32.7825 | 282.912 | 283.6517 | 1284.4 | 1217.2951 | 5.2246 | 88.4427 | 750.4734 | 95.6318 | 133.109 | 114.105 | 18.58 | 8.975 | 9.751 | 18.726 | 18.726 | 0.37983 | 0.47928 | 13.6329 | 13.6329 | 3.8919 | 101.1351 | 0.1348 | 5.69 | 7.338 | 17.1193 | 283.6517 | 502.65 | 528.9731 | -5.2369 | 93.9647 | 406.3124 | 95.7867 | 114.105 | 100.953 | 18.58 | 4.586 | 5.165 | 9.751 | 9.751 | 0.3979 | 0.47031 | 13.9322 | 13.9322 | 6.8486 | 82.1004 | 0.1697 | 5.69 | 7.338 | 28.3532 | 502.65 | 852.75 | 923.7778 | -8.3293 | 90.0042 | 713.2139 | 96.0246 | 100.953 | 48.082 | 18.58 | 1.199 | 3.966 | 5.165 | 5.165 | 0.18269 | 0.23214 | 10.6578 | 10.6578 | 8.717 | 47.2205 | 0.2257 | 7.338 | 7.338 | 95.5115 | 852.75 | 1284.4 | 1081.6781 | 15.7834 | 66.3279 | 967.2141 | 90.1251
[11 empty] | 1998-06-30 | 21:00 | 900 | 29 | 134.898 | 55.44 | 18.952 | 0 | 14.933 | 2.903 |  | 17.836 | 17.836 | 0.83724 | 0 | 13.5755 | 13.5755 | 8.9974 | 67.2196 | 0.20196 | 8.933 | 5.653 | 33.6285 | 284.64 | 285.5147 | 1345.2 | 1581.2144 | -17.5449 | 88.2218 | 933.3645 | 96.3971 | 134.898 | 117.442 | 18.952 | 9.274 | 8.562 | 17.836 | 17.836 | 0.3521 | 0.51996 | 14.0871 | 14.0871 | 4.1272 | 103.0908 | 0.13665 | 5.653 | 7.337 | 17.7891 | 285.5147 | 506.25 | 575.5038 | -13.6798 | 93.7695 | 430.5093 | 95.8679 | 117.442 | 101.046 | 18.952 | 4.522 | 4.04 | 8.562 | 8.562 | 0.33618 | 0.52815 | 13.7377 | 13.7377 | 7.42 | 82.872 | 0.16577 | 5.653 | 7.337 | 30.5038 | 506.25 | 890.55 | 1038.7561 | -16.6421 | 89.3162 | 772.503 | 96.0513 | 101.046 | 55.44 | 18.952 | 1.137 | 2.903 | 4.04 | 4.04 | 0.13891 | 0.28144 | 10.1067 | 10.1067 | 9.4279 | 49.8631 | 0.20269 | 7.337 | 7.337 | 102.1525 | 890.55 | 1345.2 | 1199.3368 | 10.8432 | 64.2216 | 1044.9434 | 90.2241
[11 empty] | 1998-07-01 | 5:00 | 908 | 29 | 134.75 | 55.477 | 18.921 | 0 | 14.936 | 2.9 |  | 17.836 | 17.836 | 0.83741 | 0 | 13.5782 | 13.5782 | 9.0265 | 67.166 | 0.20216 | 8.872 | 5.636 | 33.4875 | 284.352 | 285.9644 | 1341.4 | 1586.3072 | -18.2576 | 88.2896 | 936.1358 | 96.4228 | 134.75 | 117.277 | 18.921 | 9.213 | 8.623 | 17.836 | 17.836 | 0.35291 | 0.51654 | 13.9944 | 13.9944 | 4.1174 | 102.9751 | 0.1359 | 5.636 | 7.293 | 17.5921 | 285.9644 | 504.45 | 572.6991 | -13.5294 | 93.8481 | 429.3317 | 95.9024 | 117.277 | 100.951 | 18.921 | 4.586 | 4.037 | 8.623 | 8.623 | 0.33772 | 0.53183 | 13.9322 | 13.9322 | 7.4306 | 82.7624 | 0.16834 | 5.636 | 7.293 | 30.5613 | 504.45 | 892.8 | 1042.7839 | -16.7993 | 89.3129 | 773.6169 | 96.0496 | 100.951 | 55.477 | 18.921 | 1.137 | 2.9 | 4.037 | 4.037 | 0.13879 | 0.28164 | 10.1067 | 10.1067 | 9.4422 | 49.8508 | 0.20274 | 7.293 | 7.293 | 103.3415 | 892.8 | 1341.4 | 1202.3222 | 10.3681 | 63.8621 | 1047.5611 | 90.135
[11 empty] | 1998-07-01 | 13:00 | 916 | 29 | 134.965 | 55.747 | 18.97 | 0 | 14.884 | 2.825 |  | 17.709 | 17.709 | 0.84048 | 0 | 13.5309 | 13.5309 | 9.4206 | 66.9654 | 0.20206 | 9.185 | 5.653 | 36.8715 | 303.072 | 296.0822 | 1474.4 | 1661.7783 | -12.7088 | 87.5469 | 978.9302 | 96.2335 | 134.965 | 117.375 | 18.97 | 9.222 | 8.487 | 17.709 | 17.709 | 0.34941 | 0.52075 | 14.0081 | 14.0081 | 4.2785 | 102.9215 | 0.1361 | 5.653 | 7.313 | 18.8529 | 296.0822 | 541.8 | 597.3203 | -10.2474 | 93.6325 | 446.7012 | 95.7795 | 117.375 | 101.077 | 18.97 | 4.524 | 3.963 | 8.487 | 8.487 | 0.33212 | 0.53305 | 13.7438 | 13.7438 | 7.9966 | 82.2594 | 0.16708 | 5.653 | 7.313 | 32.7175 | 541.8 | 953.55 | 1122.9479 | -17.765 | 88.9499 | 832.374 | 96.0694 | 101.077 | 55.747 | 18.97 | 1.138 | 2.825 | 3.963 | 3.963 | 0.13581 | 0.28716 | 10.1156 | 10.1156 | 10.0747 | 49.3673 | 0.2049 | 7.313 | 7.313 | 114.985 | 953.55 | 1474.4 | 1291.3507 | 12.4152 | 61.1645 | 1122.4503 | 89.7559
[11 empty] | 1998-07-01 | 21:00 | 924 | 29 | 134.898 | 55.89 | 18.772 | 0 | 14.996 | 2.779 |  | 17.775 | 17.775 | 0.84366 | 0 | 13.6327 | 13.6327 | 9.6444 | 66.9776 | 0.20354 | 9.241 | 5.682 | 36.284 | 306.288 | 297.0779 | 1438.3 | 1704.3701 | -18.4989 | 87.7864 | 1000.724 | 96.3742 | 134.898 | 117.472 | 18.772 | 9.273 | 8.502 | 17.775 | 17.775 | 0.35049 | 0.52169 | 14.0856 | 14.0856 | 4.3041 | 103.1089 | 0.13661 | 5.682 | 7.325 | 18.5574 | 297.0779 | 543.6 | 600.8559 | -10.5327 | 93.7534 | 448.9669 | 95.8666 | 117.472 | 101.185 | 18.772 | 4.524 | 3.978 | 8.502 | 8.502 | 0.33292 | 0.53211 | 13.7438 | 13.7438 | 8.011 | 82.5455 | 0.1665 | 5.682 | 7.325 | 32.9015 | 543.6 | 967.05 | 1124.3944 | -16.2706 | 88.925 | 833.9972 | 96.055 | 101.185 | 55.89 | 18.772 | 1.199 | 2.779 | 3.978 | 3.978 | 0.13519 | 0.30141 | 10.6578 | 10.6578 | 10.3429 | 49.4226 | 0.21565 | 7.325 | 7.325 | 116.29 | 967.05 | 1438.3 | 1334.1105 | 7.2439 | 60.8554 | 1150.5803 | 89.8929
[11 empty] | 1998-07-02 | 0:00 | 927 | 29 | 135.012 | 55.777 | 18.799 | 0 | 14.932 | 3.029 |  | 17.961 | 17.961 | 0.83136 | 0 | 13.5745 | 13.5745 | 9.0506 | 67.5449 | 0.20097 | 9.267 | 5.67 | 36.284 | 306.288 | 297.4954 | 1445.9 | 1585.1842 | -9.633 | 87.8035 | 941.3398 | 96.1455 | 135.012 | 117.622 | 18.799 | 9.273 | 8.688 | 17.961 | 17.961 | 0.35545 | 0.51629 | 14.0856 | 14.0856 | 4.2783 | 103.2397 | 0.13644 | 5.67 | 7.312 | 18.5377 | 297.4954 | 544.05 | 595.2366 | -9.4084 | 93.7687 | 446.366 | 95.847 | 117.622 | 101.064 | 18.799 | 4.522 | 4.166 | 8.688 | 8.688 | 0.3429 | 0.52049 | 13.7377 | 13.7377 | 7.884 | 82.66 | 0.1662 | 5.67 | 7.312 | 33.005 | 544.05 | 967.05 | 1098.7657 | -13.6204 | 88.9057 | 821.4078 | 95.9819 | 101.064 | 55.777 | 18.799 | 1.137 | 3.029 | 4.166 | 4.166 | 0.14395 | 0.27292 | 10.1067 | 10.1067 | 10.1042 | 49.5173 | 0.2041 | 7.312 | 7.312 | 116.3045 | 967.05 | 1445.9 | 1286.3955 | 11.0315 | 60.9055 | 1126.7228 | 89.6776
[11 empty] | 1998-07-02 | 13:00 | 940 | 29 | 132.961 | 57.727 | 18.771 | 0 | 15.056 | 2.905 |  | 17.961 | 17.961 | 0.83826 | 0 | 13.6873 | 13.6873 | 9.1706 | 67.4024 | 0.20307 | 7.894 | 5.685 | 35.015 | 292.512 | 290.3648 | 1400.3 | 1613.7888 | -15.2459 | 87.941 | 952.0768 | 96.3223 | 132.961 | 115.305 | 18.771 | 9.216 | 8.745 | 17.961 | 17.961 | 0.35621 | 0.51311 | 13.999 | 13.999 | 4.1533 | 101.2087 | 0.13832 | 5.685 | 7.332 | 18.3604 | 290.3648 | 515.7 | 577.0192 | -11.8905 | 93.6768 | 433.692 | 95.7665 | 115.305 | 99.394 | 18.771 | 4.522 | 4.223 | 8.745 | 8.745 | 0.34594 | 0.5171 | 13.7377 | 13.7377 | 7.4399 | 81.1386 | 0.16931 | 5.685 | 7.332 | 31.142 | 515.7 | 890.55 | 1034.566 | -16.1716 | 89.2749 | 775.133 | 95.9824 | 99.394 | 57.727 | 18.771 | 1.318 | 2.905 | 4.223 | 4.223 | 0.14261 | 0.3121 | 11.7156 | 11.7156 | 9.6965 | 50.093 | 0.23388 | 7.332 | 7.332 | 100.195 | 890.55 | 1400.3 | 1249.1345 | 10.7952 | 65.4934 | 1069.8422 | 90.6346
[11 empty] | 1998-07-02 | 21:00 | 948 | 29 | 133.055 | 57.585 | 18.934 | 0 | 15.054 | 2.905 |  | 17.959 | 17.959 | 0.83824 | 0 | 13.6855 | 13.6855 | 9.1811 | 67.2049 | 0.20364 | 9.169 | 5.659 | 34.827 | 293.088 | 290.4933 | 1377.5 | 1615.3815 | -17.2691 | 88.0111 | 952.9374 | 96.3453 | 133.055 | 115.402 | 18.934 | 9.214 | 8.745 | 17.959 | 17.959 | 0.35618 | 0.51306 | 13.9959 | 13.9959 | 4.1541 | 101.1404 | 0.13838 | 5.659 | 7.323 | 18.4195 | 290.4933 | 517.95 | 577.1586 | -11.4313 | 93.6592 | 433.8259 | 95.7542 | 115.402 | 99.57 | 18.934 | 4.523 | 4.222 | 8.745 | 8.745 | 0.34591 | 0.51721 | 13.7408 | 13.7408 | 7.4746 | 81.0774 | 0.16948 | 5.659 | 7.323 | 31.211 | 517.95 | 898.2 | 1039.3902 | -15.7192 | 89.2559 | 778.6701 | 95.9918 | 99.57 | 57.585 | 18.934 | 1.317 | 2.905 | 4.222 | 4.222 | 0.14259 | 0.31194 | 11.7067 | 11.7067 | 9.7875 | 49.856 | 0.23481 | 7.323 | 7.323 | 100.311 | 898.2 | 1377.5 | 1259.928 | 8.5352 | 65.4687 | 1079.064 | 90.7039
[11 empty] | 1998-07-03 | 5:00 | 956.0003 | 29 | 133.223 | 57.765 | 18.931 | 0 | 15.116 | 2.957 |  | 18.073 | 18.073 | 0.83639 | 0 | 13.7418 | 13.7418 | 9.1056 | 67.4574 | 0.20371 | 9.132 | 5.635 | 34.686 | 294.096 | 290.7502 | 1373.7 | 1599.7347 | -16.4544 | 88.0702 | 945.2425 | 96.3305 | 133.223 | 115.59 | 18.931 | 9.274 | 8.799 | 18.073 | 18.073 | 0.35842 | 0.51314 | 14.0871 | 14.0871 | 4.1609 | 101.3146 | 0.13904 | 5.635 | 7.292 | 18.2619 | 290.7502 | 516.6 | 577.9484 | -11.8754 | 93.719 | 434.3493 | 95.7956 | 115.59 | 99.646 | 18.931 | 4.524 | 4.275 | 8.799 | 8.799 | 0.34877 | 0.51415 | 13.7438 | 13.7438 | 7.4211 | 81.2659 | 0.16912 | 5.635 | 7.292 | 31.2858 | 516.6 | 900.9 | 1030.1817 | -14.3503 | 89.2396 | 773.3908 | 95.9547 | 99.646 | 57.765 | 18.931 | 1.318 | 2.957 | 4.275 | 4.275 | 0.14469 | 0.3083 | 11.7156 | 11.7156 | 9.7912 | 49.9833 | 0.23439 | 7.292 | 7.292 | 100.224 | 900.9 | 1373.7 | 1257.7789 | 8.4386 | 65.5292 | 1079.3395 | 90.7143
[11 empty] | 1998-07-03 | 13:00 | 964.0003 | 29 | 140.7 | 46.68 | 18.573 | 0 | 14.762 | 5.054 |  | 19.816 | 19.816 | 0.74495 | 0 | 13.42 | 13.42 | 6.2913 | 68.8257 | 0.19499 | 8.863 | 5.737 | 33.511 | 291.024 | 289.2085 | 1354.7 | 1036.0637 | 23.5208 | 88.4129 | 662.6361 | 94.9428 | 140.7 | 120.915 | 18.573 | 8.679 | 11.137 | 19.816 | 19.816 | 0.41286 | 0.43798 | 13.1833 | 13.1833 | 3.7718 | 108.4627 | 0.12155 | 5.737 | 7.362 | 17.7891 | 289.2085 | 513.45 | 500.724 | 2.4785 | 93.849 | 394.9663 | 95.496 | 120.915 | 101.379 | 18.573 | 4.825 | 6.312 | 11.137 | 11.137 | 0.46548 | 0.43324 | 14.6582 | 14.6582 | 6.7028 | 85.8712 | 0.1707 | 5.737 | 7.362 | 28.5143 | 513.45 | 862.2 | 884.1431 | -2.545 | 90.1406 | 698.7966 | 95.9195 | 101.379 | 46.68 | 18.573 | 1.258 | 5.054 | 6.312 | 6.312 | 0.2274 | 0.1993 | 11.1822 | 11.1822 | 8.5904 | 46.8661 | 0.2386 | 7.362 | 7.362 | 98.2375 | 862.2 | 1354.7 | 1052.3592 | 22.3179 | 66.0323 | 957.2796 | 89.7378
[11 empty] | 1998-07-03 | 21:00 | 972 | 29 | 141.169 | 47.055 | 18.58 | 0 | 14.818 | 5.172 |  | 19.99 | 19.99 | 0.74127 | 0 | 13.4709 | 13.4709 | 6.25 | 69.282 | 0.19444 | 8.76 | 5.728 | 33.2055 | 293.52 | 290.14 | 1328.1 | 1026.2681 | 22.7266 | 88.5554 | 658.204 | 94.9551 | 141.169 | 121.56 | 18.58 | 8.735 | 11.255 | 19.99 | 19.99 | 0.41675 | 0.43697 | 13.2684 | 13.2684 | 3.7845 | 109 | 0.12173 | 5.728 | 7.363 | 17.4936 | 290.14 | 514.35 | 501.7407 | 2.4515 | 93.9706 | 395.9403 | 95.5818 | 121.56 | 101.568 | 18.58 | 4.825 | 6.43 | 11.255 | 11.255 | 0.47177 | 0.4287 | 14.6582 | 14.6582 | 6.6791 | 86.3049 | 0.16984 | 5.728 | 7.363 | 28.6695 | 514.35 | 871.2 | 878.7992 | -0.87227 | 90.1187 | 696.5746 | 95.8842 | 101.568 | 47.055 | 18.58 | 1.258 | 5.172 | 6.43 | 6.43 | 0.23212 | 0.19565 | 11.1822 | 11.1822 | 8.6708 | 47.0607 | 0.23761 | 7.363 | 7.363 | 98.136 | 871.2 | 1328.1 | 1059.2345 | 20.2444 | 66.1763 | 965.2173 | 89.8328
[11 empty] | 1998-07-04 | 5:00 | 980.0003 | 29 | 141.316 | 46.777 | 18.532 | 0 | 14.815 | 5.063 |  | 19.878 | 19.878 | 0.7453 | 0 | 13.4682 | 13.4682 | 6.3471 | 69.1674 | 0.19472 | 8.81 | 5.723 | 32.6415 | 293.712 | 290.3327 | 1307.2 | 1044.3708 | 20.1063 | 88.7572 | 667.3517 | 95.1088 | 141.316 | 121.575 | 18.532 | 8.732 | 11.146 | 19.878 | 19.878 | 0.4138 | 0.43928 | 13.2638 | 13.2638 | 3.8001 | 109.1134 | 0.12156 | 5.723 | 7.356 | 17.2769 | 290.3327 | 516.6 | 504.2501 | 2.3906 | 94.0493 | 397.2914 | 95.6513 | 121.575 | 101.676 | 18.532 | 4.825 | 6.321 | 11.146 | 11.146 | 0.46596 | 0.43289 | 14.6582 | 14.6582 | 6.742 | 86.3515 | 0.16975 | 5.723 | 7.356 | 28.6408 | 516.6 | 873.45 | 889.0732 | -1.7887 | 90.1352 | 702.8366 | 95.925 | 101.676 | 46.777 | 18.532 | 1.258 | 5.063 | 6.321 | 6.321 | 0.22776 | 0.19902 | 11.1822 | 11.1822 | 8.7154 | 46.9791 | 0.23803 | 7.356 | 7.356 | 98.223 | 873.45 | 1307.2 | 1066.0701 | 18.4463 | 66.1688 | 969.76 | 89.8714
[11 empty] | 1998-07-04 | 13:00 | 988 | 29 | 136.928 | 45.067 | 18.259 | 0 | 14.455 | 4.878 |  | 19.333 | 19.333 | 0.74769 | 0 | 13.1409 | 13.1409 | 6.2499 | 66.4886 | 0.19764 | 8.892 | 5.721 | 32.5475 | 282.384 | 284.3905 | 1299.6 | 1030.6779 | 20.6927 | 88.5553 | 657.5342 | 95.0501 | 136.928 | 117.285 | 18.259 | 8.495 | 10.838 | 19.333 | 19.333 | 0.40243 | 0.4394 | 12.9038 | 12.9038 | 3.7177 | 105.1298 | 0.12274 | 5.721 | 7.335 | 17.2966 | 284.3905 | 495.45 | 493.743 | 0.34454 | 93.918 | 389.0667 | 95.5543 | 117.285 | 99.381 | 18.259 | 4.763 | 6.075 | 10.838 | 10.838 | 0.45118 | 0.43947 | 14.4699 | 14.4699 | 6.5158 | 83.5582 | 0.17317 | 5.721 | 7.335 | 27.3642 | 495.45 | 829.35 | 862.4446 | -3.9904 | 90.3779 | 678.9473 | 95.9696 | 99.381 | 45.067 | 18.259 | 1.197 | 4.878 | 6.075 | 6.075 | 0.21914 | 0.19704 | 10.64 | 10.64 | 8.2521 | 45.7129 | 0.23276 | 7.335 | 7.335 | 94.3225 | 829.35 | 1299.6 | 1009.7165 | 22.3056 | 66.8335 | 919.5333 | 89.7424
[11 empty] | 1998-07-04 | 21:00 | 996 | 29 | 137.075 | 45.337 | 18.279 | 0 | 14.459 | 5.171 |  | 19.63 | 19.63 | 0.73658 | 0 | 13.1445 | 13.1445 | 6.0815 | 66.8455 | 0.19664 | 8.864 | 5.713 | 32.336 | 284.592 | 285.9322 | 1292 | 995.0307 | 22.9852 | 88.691 | 640.4815 | 94.9513 | 137.075 | 117.832 | 18.279 | 8.555 | 11.075 | 19.63 | 19.63 | 0.40955 | 0.43581 | 12.9949 | 12.9949 | 3.7272 | 105.4473 | 0.12324 | 5.713 | 7.353 | 17.0602 | 285.9322 | 497.7 | 493.6253 | 0.81871 | 94.0335 | 389.7788 | 95.6231 | 117.832 | 99.61 | 18.279 | 4.705 | 6.37 | 11.075 | 11.075 | 0.46537 | 0.42483 | 14.2937 | 14.2937 | 6.4381 | 84.0039 | 0.17015 | 5.713 | 7.353 | 27.531 | 497.7 | 842.85 | 844.9755 | -0.25218 | 90.3715 | 671.3378 | 95.8991 | 99.61 | 45.337 | 18.279 | 1.199 | 5.171 | 6.37 | 6.37 | 0.2309 | 0.18823 | 10.6578 | 10.6578 | 8.3432 | 45.8513 | 0.23244 | 7.353 | 7.353 | 95.207 | 842.85 | 1292 | 1016.206 | 21.3463 | 66.703 | 929.528 | 89.7575
[11 empty] | 1998-07-05 | 0:00 | 999 | 29 | 137.008 | 45.277 | 18.223 | 0 | 14.458 | 4.815 |  | 19.273 | 19.273 | 0.75017 | 0 | 13.1436 | 13.1436 | 6.3417 | 66.5778 | 0.19742 | 8.906 | 5.697 | 32.242 | 285.168 | 285.7716 | 1290.1 | 1047.0451 | 18.84 | 88.7176 | 666.4084 | 95.1618 | 137.008 | 117.742 | 18.223 | 8.616 | 10.657 | 19.273 | 19.273 | 0.39921 | 0.44705 | 13.0876 | 13.0876 | 3.775 | 105.377 | 0.1242 | 5.697 | 7.343 | 16.942 | 285.7716 | 496.8 | 503.1157 | -1.2713 | 94.0715 | 394.4437 | 95.7048 | 117.742 | 99.579 | 18.223 | 4.705 | 5.952 | 10.657 | 10.657 | 0.44307 | 0.44149 | 14.2937 | 14.2937 | 6.5463 | 83.8912 | 0.17038 | 5.697 | 7.343 | 27.6115 | 496.8 | 841.95 | 867.6891 | -3.0571 | 90.3379 | 682.2445 | 95.9528 | 99.579 | 45.277 | 18.223 | 1.137 | 4.815 | 5.952 | 5.952 | 0.21542 | 0.19103 | 10.1067 | 10.1067 | 8.3468 | 45.8582 | 0.22039 | 7.343 | 7.343 | 95.41 | 841.95 | 1290.1 | 1018.2358 | 21.0731 | 66.6132 | 930.0929 | 89.7419
[11 empty] | 1998-07-05 | 13:00 | 1012 | 29 | 136.573 | 45.157 | 18.255 | 0 | 14.46 | 4.81 |  | 19.27 | 19.27 | 0.75039 | 0 | 13.1455 | 13.1455 | 6.3161 | 66.2939 | 0.19829 | 8.601 | 5.719 | 32.477 | 283.056 | 284.808 | 1299.6 | 1043.375 | 19.7157 | 88.5969 | 664.0915 | 95.1096 | 136.573 | 117.037 | 18.255 | 8.558 | 10.712 | 19.27 | 19.27 | 0.39991 | 0.44411 | 12.9995 | 12.9995 | 3.7443 | 104.8057 | 0.12403 | 5.719 | 7.342 | 17.2572 | 284.808 | 499.5 | 498.559 | 0.18839 | 93.9408 | 391.6835 | 95.5941 | 117.037 | 99.381 | 18.255 | 4.704 | 6.008 | 10.712 | 10.712 | 0.44603 | 0.43913 | 14.2906 | 14.2906 | 6.5684 | 83.3856 | 0.17138 | 5.719 | 7.342 | 27.4563 | 499.5 | 836.55 | 869.0895 | -3.8897 | 90.3597 | 684.2948 | 95.9877 | 99.381 | 45.157 | 18.255 | 1.198 | 4.81 | 6.008 | 6.008 | 0.21644 | 0.1994 | 10.6489 | 10.6489 | 8.3383 | 45.6757 | 0.23314 | 7.342 | 7.342 | 95.062 | 836.55 | 1299.6 | 1021.2283 | 21.4198 | 66.6224 | 928.8892 | 89.7661
[11 empty] | 1998-07-05 | 21:00 | 1020 | 29 | 136.693 | 45.24 | 18.217 | 0 | 14.4 | 5.293 |  | 19.693 | 19.693 | 0.73122 | 0 | 13.0909 | 13.0909 | 5.9634 | 66.7861 | 0.19601 | 8.633 | 5.724 | 32.3125 | 284.496 | 284.9686 | 1292 | 972.3385 | 24.7416 | 88.661 | 628.6535 | 94.86 | 136.693 | 117.397 | 18.217 | 8.556 | 11.137 | 19.693 | 19.693 | 0.41122 | 0.43447 | 12.9965 | 12.9965 | 3.7087 | 105.1193 | 0.12364 | 5.724 | 7.359 | 17.0208 | 284.9686 | 497.7 | 490.8196 | 1.3824 | 94.0271 | 387.8941 | 95.612 | 117.397 | 99.538 | 18.217 | 4.707 | 6.43 | 11.137 | 11.137 | 0.46862 | 0.42265 | 14.2997 | 14.2997 | 6.4214 | 83.8291 | 0.17058 | 5.724 | 7.359 | 27.6172 | 497.7 | 838.35 | 841.8181 | -0.41368 | 90.3087 | 669.7591 | 95.8765 | 99.538 | 45.24 | 18.217 | 1.137 | 5.293 | 6.43 | 6.43 | 0.23455 | 0.17683 | 10.1067 | 10.1067 | 8.227 | 45.945 | 0.21997 | 7.359 | 7.359 | 95.439 | 838.35 | 1292 | 997.9362 | 22.7604 | 66.5089 | 918.1431 | 89.6052
[11 empty] | 1998-07-06 | 5:00 | 1028 | 29 | 136.713 | 45.262 | 18.195 | 0 | 14.459 | 5.062 |  | 19.521 | 19.521 | 0.74069 | 0 | 13.1445 | 13.1445 | 6.1552 | 66.6373 | 0.19726 | 8.691 | 5.709 | 32.2185 | 285.168 | 285.7074 | 1290.1 | 1009.7682 | 21.7295 | 88.7233 | 647.7378 | 95.026 | 136.713 | 117.495 | 18.195 | 8.554 | 10.967 | 19.521 | 19.521 | 0.40665 | 0.43819 | 12.9934 | 12.9934 | 3.7369 | 105.1721 | 0.12354 | 5.709 | 7.354 | 16.8632 | 285.7074 | 500.4 | 495.3995 | 0.9993 | 94.0977 | 390.5535 | 95.6822 | 117.495 | 99.511 | 18.195 | 4.707 | 6.26 | 10.967 | 10.967 | 0.45955 | 0.4292 | 14.2997 | 14.2997 | 6.5055 | 83.8025 | 0.17064 | 5.709 | 7.354 | 27.6058 | 500.4 | 845.55 | 855.902 | -1.2243 | 90.3378 | 678.151 | 95.9293 | 99.511 | 45.262 | 18.195 | 1.198 | 5.062 | 6.26 | 6.26 | 0.22652 | 0.19137 | 10.6489 | 10.6489 | 8.3847 | 45.8068 | 0.23247 | 7.354 | 7.354 | 95.8015 | 845.55 | 1290.1 | 1022.9895 | 20.7046 | 66.4687 | 934.2697 | 89.7458
[11 empty] | 1998-07-06 | 13:00 | 1036.0003 | 29 | 136.325 | 44.977 | 18.186 | 0 | 14.519 | 4.754 |  | 19.273 | 19.273 | 0.75333 | 0 | 13.1991 | 13.1991 | 6.3759 | 66.0891 | 0.19972 | 8.681 | 5.707 | 32.5005 | 283.104 | 284.808 | 1299.6 | 1055.3703 | 18.7927 | 88.5886 | 670.0892 | 95.1498 | 136.325 | 117.21 | 18.186 | 8.558 | 10.715 | 19.273 | 19.273 | 0.39999 | 0.44404 | 12.9995 | 12.9995 | 3.744 | 104.8375 | 0.124 | 5.707 | 7.331 | 17.2572 | 284.808 | 499.5 | 498.4991 | 0.20037 | 93.9408 | 391.6536 | 95.5938 | 117.21 | 99.264 | 18.186 | 4.705 | 6.01 | 10.715 | 10.715 | 0.44616 | 0.4391 | 14.2937 | 14.2937 | 6.5673 | 83.4837 | 0.17122 | 5.707 | 7.331 | 27.5195 | 499.5 | 836.55 | 868.9955 | -3.8785 | 90.3375 | 684.2478 | 95.9781 | 99.264 | 44.977 | 18.186 | 1.256 | 4.754 | 6.01 | 6.01 | 0.21536 | 0.20899 | 11.1644 | 11.1644 | 8.3916 | 45.5429 | 0.24514 | 7.331 | 7.331 | 95.3085 | 836.55 | 1299.6 | 1032.3849 | 20.5613 | 66.5359 | 934.4675 | 89.8008
[11 empty] | 1998-07-06 | 21:00 | 1044 | 29 | 123.782 | 54.322 | 17.97 | 0 | 14.335 | 2.84 |  | 17.175 | 17.175 | 0.83464 | 0 | 13.0318 | 13.0318 | 8.8352 | 62.2468 | 0.20936 | 8.881 | 5.541 | 35.6495 | 284.592 | 286.3819 | 1411.7 | 1551.9626 | -9.9357 | 87.5518 | 919.1723 | 96.1216 | 123.782 | 106.65 | 17.97 | 8.795 | 8.38 | 17.175 | 17.175 | 0.34086 | 0.51208 | 13.3595 | 13.3595 | 4.0801 | 93.1659 | 0.14339 | 5.541 | 7.134 | 18.7938 | 286.3819 | 505.8 | 567.2217 | -12.1435 | 93.4375 | 426.8018 | 95.5966 | 106.65 | 99.953 | 17.97 | 4.282 | 4.098 | 8.38 | 8.38 | 0.33287 | 0.51098 | 13.0086 | 13.0086 | 7.2394 | 78.0921 | 0.16658 | 5.541 | 7.134 | 30.291 | 505.8 | 870.75 | 1002.6593 | -15.1489 | 89.4229 | 754.2297 | 95.9838 | 99.953 | 54.322 | 17.97 | 1.258 | 2.84 | 4.098 | 4.098 | 0.13881 | 0.30698 | 11.1822 | 11.1822 | 9.395 | 49.7725 | 0.22467 | 7.134 | 7.134 | 101.6015 | 870.75 | 1411.7 | 1211.4503 | 14.185 | 64.5224 | 1041.1001 | 90.2409
[11 empty] | 1998-07-07 | 5:00 | 1052 | 29 | 123.816 | 54.435 | 17.965 | 0 | 14.276 | 2.9 |  | 17.176 | 17.176 | 0.83116 | 0 | 12.9782 | 12.9782 | 8.6709 | 62.4896 | 0.20769 | 8.49 | 5.536 | 34.2395 | 281.664 | 284.7438 | 1354.7 | 1517.916 | -12.0481 | 87.9753 | 901.3299 | 96.2012 | 123.816 | 106.59 | 17.965 | 8.794 | 8.382 | 17.176 | 17.176 | 0.3409 | 0.51199 | 13.358 | 13.358 | 4.0636 | 93.1744 | 0.14337 | 5.536 | 7.15 | 18.2028 | 284.7438 | 495.9 | 564.3861 | -13.8105 | 93.6073 | 424.5649 | 95.7126 | 106.59 | 100.98 | 17.965 | 4.284 | 4.098 | 8.382 | 8.382 | 0.33292 | 0.5111 | 13.0147 | 13.0147 | 7.0981 | 78.7219 | 0.16532 | 5.536 | 7.15 | 29.7447 | 495.9 | 860.85 | 983.2131 | -14.2142 | 89.5539 | 739.5566 | 95.978 | 100.047 | 54.435 | 17.965 | 1.198 | 2.9 | 4.098 | 4.098 | 0.14001 | 0.29234 | 10.6489 | 10.6489 | 9.2115 | 50.0645 | 0.2127 | 7.15 | 7.15 | 97.3965 | 860.85 | 1354.7 | 1176.2353 | 13.1737 | 65.795 | 1018.5426 | 90.4377
[11 empty] | 1998-07-07 | 13:00 | 1060.0003 | 29 | 124.097 | 54.465 | 18.019 | 0 | 14.344 | 2.892 |  | 17.236 | 17.236 | 0.83221 | 0 | 13.04 | 13.04 | 8.8269 | 62.4351 | 0.20886 | 9.19 | 5.608 | 36.6835 | 291.648 | 290.3327 | 1451.6 | 1548.4045 | -6.6688 | 87.365 | 919.3686 | 96.0099 | 124.097 | 106.837 | 18.019 | 8.86 | 8.376 | 17.236 | 17.236 | 0.34162 | 0.51404 | 13.4582 | 13.4582 | 4.1482 | 93.2998 | 0.14425 | 5.608 | 7.216 | 19.0105 | 290.3327 | 519.75 | 577.333 | -11.079 | 93.4522 | 433.8328 | 95.618 | 106.837 | 100.11 | 18.019 | 4.284 | 4.092 | 8.376 | 8.376 | 0.3326 | 0.51146 | 13.0147 | 13.0147 | 7.4453 | 78.0092 | 0.16684 | 5.608 | 7.216 | 31.0385 | 519.75 | 891.9 | 1031.3922 | -15.6399 | 89.3093 | 775.5711 | 95.998 | 100.11 | 54.465 | 18.019 | 1.2 | 2.892 | 4.092 | 4.092 | 0.13973 | 0.29326 | 10.6667 | 10.6667 | 9.5044 | 49.7641 | 0.21434 | 7.216 | 7.216 | 104.7625 | 891.9 | 1451.6 | 1218.5131 | 16.0572 | 63.9164 | 1055.2065 | 90.0718
[11 empty] | 1998-07-07 | 21:00 | 1068 | 29 | 124.66 | 55.057 | 17.88 | 0 | 14.215 | 3.2 |  | 17.415 | 17.415 | 0.81625 | 0 | 12.9227 | 12.9227 | 8.2364 | 63.7421 | 0.20273 | 9.195 | 5.657 | 35.8845 | 294.48 | 291.5854 | 1421.2 | 1427.4565 | -0.44023 | 87.6933 | 859.5209 | 95.8251 | 124.66 | 107.767 | 17.88 | 8.852 | 8.563 | 17.415 | 17.415 | 0.3465 | 0.5083 | 13.4461 | 13.4461 | 4.1361 | 94.1974 | 0.14274 | 5.657 | 7.251 | 18.912 | 291.5854 | 519.75 | 573.4614 | -10.3341 | 93.5141 | 432.5234 | 95.6275 | 107.767 | 100.623 | 17.88 | 4.226 | 4.337 | 8.563 | 8.563 | 0.34412 | 0.49352 | 12.8385 | 12.8385 | 7.2647 | 79.0503 | 0.16241 | 5.657 | 7.251 | 31.2685 | 519.75 | 908.1 | 995.7294 | -9.6498 | 89.2764 | 757.7397 | 95.8735 | 100.623 | 55.057 | 17.88 | 1.137 | 3.2 | 4.337 | 4.337 | 0.15079 | 0.26216 | 10.1067 | 10.1067 | 9.451 | 50.509 | 0.2001 | 7.251 | 7.251 | 105.5745 | 908.1 | 1421.2 | 1193.2473 | 16.0394 | 63.7929 | 1050.6737 | 89.9517
[11 empty] | 1998-07-08 | 5:00 | 1076 | 29 | 132.379 | 58.642 | 18.879 | 0 | 14.993 | 2.782 |  | 17.775 | 17.775 | 0.84349 | 0 | 13.63 | 13.63 | 9.6712 | 66.9603 | 0.20355 | 9.049 | 5.635 | 37.177 | 308.928 | 298.9408 | 1455.4 | 1709.6616 | -17.4702 | 87.5638 | 1004.3012 | 96.2982 | 132.379 | 114.72 | 18.879 | 9.273 | 8.502 | 17.775 | 17.775 | 0.35049 | 0.52169 | 14.0856 | 14.0856 | 4.3323 | 100.3382 | 0.14038 | 5.635 | 7.289 | 18.5968 | 298.9408 | 548.1 | 604.7078 | -10.328 | 93.7791 | 451.8243 | 95.8841 | 114.72 | 104.327 | 18.879 | 4.522 | 3.98 | 8.502 | 8.502 | 0.33297 | 0.53187 | 13.7377 | 13.7377 | 8.069 | 82.5755 | 0.16637 | 5.635 | 7.289 | 33.5225 | 548.1 | 963.9 | 1132.7531 | -17.5177 | 88.7862 | 840.4266 | 96.0113 | 104.327 | 58.642 | 18.879 | 1.198 | 2.782 | 3.98 | 3.98 | 0.13529 | 0.30101 | 10.6489 | 10.6489 | 10.3594 | 52.2461 | 0.20382 | 7.289 | 7.289 | 111.4905 | 963.9 | 1455.4 | 1330.9692 | 8.5496 | 62.7048 | 1147.4346 | 90.2835
[11 empty] | 1998-07-08 | 13:00 | 1084 | 29 | 131.36 | 57.81 | 18.888 | 0 | 15.112 | 2.72 |  | 17.832 | 17.832 | 0.84747 | 0 | 13.7382 | 13.7382 | 9.5023 | 66.1947 | 0.20754 | 8.815 | 5.669 | 34.122 | 283.92 | 285.6432 | 1347.1 | 1683.0651 | -24.9399 | 88.0543 | 984.3541 | 96.5336 | 131.36 | 113.362 | 18.888 | 9.274 | 8.558 | 17.832 | 17.832 | 0.35199 | 0.52008 | 14.0871 | 14.0871 | 4.128 | 99.345 | 0.1418 | 5.669 | 7.316 | 17.9073 | 285.6432 | 506.7 | 575.779 | -13.6331 | 93.7309 | 430.7111 | 95.8424 | 113.362 | 103.571 | 18.888 | 4.521 | 4.037 | 8.558 | 8.558 | 0.33599 | 0.52828 | 13.7347 | 13.7347 | 7.4235 | 82.155 | 0.16718 | 5.669 | 7.316 | 30.82 | 506.7 | 879.75 | 1039.6337 | -18.1738 | 89.2103 | 773.1669 | 96.0138 | 103.571 | 57.81 | 18.888 | 1.317 | 2.72 | 4.037 | 4.037 | 0.13519 | 0.32623 | 11.7067 | 11.7067 | 9.7116 | 52.0909 | 0.22474 | 7.316 | 7.316 | 97.875 | 879.75 | 1347.1 | 1258.327 | 6.5899 | 65.7352 | 1069.0385 | 90.8446
[11 empty] | 1998-07-08 | 21:00 | 1092 | 29 | 131.173 | 57.907 | 18.856 | 0 | 15.108 | 2.728 |  | 17.836 | 17.836 | 0.84705 | 0 | 13.7345 | 13.7345 | 9.5285 | 66.1555 | 0.20761 | 8.843 | 5.623 | 33.8635 | 286.032 | 286.671 | 1339.5 | 1686.7501 | -25.9239 | 88.1873 | 986.7105 | 96.568 | 131.173 | 113.572 | 18.856 | 9.269 | 8.567 | 17.836 | 17.836 | 0.35217 | 0.51968 | 14.0795 | 14.0795 | 4.141 | 99.3755 | 0.14168 | 5.623 | 7.253 | 17.9467 | 286.671 | 508.5 | 577.4152 | -13.5526 | 93.7396 | 432.0431 | 95.8461 | 113.572 | 103.584 | 18.856 | 4.522 | 4.045 | 8.567 | 8.567 | 0.33644 | 0.52784 | 13.7377 | 13.7377 | 7.4444 | 82.2776 | 0.16697 | 5.623 | 7.253 | 30.9752 | 508.5 | 889.2 | 1042.3361 | -17.2218 | 89.1948 | 775.418 | 96.0053 | 103.584 | 57.907 | 18.856 | 1.317 | 2.728 | 4.045 | 4.045 | 0.13551 | 0.32559 | 11.7067 | 11.7067 | 9.8162 | 52.0733 | 0.22481 | 7.253 | 7.253 | 98.455 | 889.2 | 1339.5 | 1270.949 | 5.1177 | 65.6558 | 1080.0745 | 90.8844
[11 empty] | 1998-07-09 | 5:00 | 1100 | 29 | 134.77 | NR | 18.948 | 0 | 15.051 | 3.981 |  | 19.032 | 19.032 | 0.79083 | 0 | 13.6827 | 13.6827 | 7.4253 | #VALUE! | #VALUE! | 9.036 | 5.745 | 34.686 | 295.344 | 291.5854 | 1337.6 | 1262.8469 | 5.5886 | 88.1043 | 777.2161 | 95.5371 | 134.77 | 115.485 | 18.948 | 9.571 | 9.461 | 19.032 | 19.032 | 0.38004 | 0.50289 | 14.5382 | 14.5382 | 4.1217 | 102.0578 | 0.14245 | 5.745 | 7.252 | 17.8679 | 291.5854 | 511.65 | 568.4852 | -11.1082 | 93.8722 | 430.0353 | 95.845 | 115.485 | 103.188 | 18.948 | 4.522 | 4.939 | 9.461 | 9.461 | 0.38414 | 0.47796 | 13.7377 | 13.7377 | 7.0698 | 83.3187 | 0.16488 | 5.745 | 7.252 | 26.68 | 511.65 | 852.75 | 955.674 | -12.0697 | 90.85 | 733.662 | 96.3634 | 103.188 | 37.432 | 18.948 | 0.958 | 3.981 | 4.939 | 4.939 | 0.17846 | 0.19397 | 8.5156 | 8.5156 | 8.356 | 43.006 | 0.19801 | 7.252 | 7.252 | 106.894 | 852.75 | 1337.6 | 1032.2351 | 22.8293 | 63.3404 | 942.4925 | 88.6584
[11 empty] | 1998-07-09 | 8:41 | 1103.6914 | 29 | 132.157 | NR | 18.64 | 0 | 14.996 | 3.857 |  | 18.853 | 18.853 | 0.79542 | 0 | 13.6327 | 13.6327 | 7.5383 | #VALUE! | #VALUE! | 8.515 | 5.678 | 34.0515 | 294 | 290.1078 | 1328.1 | 1285.6538 | 3.196 | 88.2625 | 787.8808 | 95.6781 | 132.157 | 113.22 | 18.64 | 9.516 | 9.337 | 18.853 | 18.853 | 0.376 | 0.50475 | 14.4547 | 14.4547 | 4.1058 | 99.9427 | 0.14463 | 5.678 | 7.237 | 18.124 | 290.1078 | 510.3 | 567.3059 | -11.1711 | 93.7527 | 428.7069 | 95.7724 | 113.22 | 101.996 | 18.64 | 4.521 | 4.816 | 9.337 | 9.337 | 0.37755 | 0.4842 | 13.7347 | 13.7347 | 7.11 | 81.858 | 0.16779 | 5.678 | 7.237 | 26.4213 | 510.3 | 839.7 | 964.5392 | -14.8671 | 90.8926 | 737.4196 | 96.4171 | 101.996 | 36.802 | 18.64 | 0.959 | 3.857 | 4.816 | 4.816 | 0.17352 | 0.19913 | 8.5244 | 8.5244 | 8.2807 | 42.4783 | 0.20068 | 7.237 | 7.237 | 103.1965 | 839.7 | 1328.1 | 1022.8234 | 22.986 | 64.4282 | 931.2617 | 88.9186
[11 empty] | 1998-07-09 | 16:00 | 1111 | 29 | 124.245 | 53.887 | 17.979 | 0 | 14.279 | 2.956 |  | 17.235 | 17.235 | 0.82849 | 0 | 12.9809 | 12.9809 | 8.6469 | 62.4401 | 0.20789 | 7.458 | 5.605 | 36.989 | 292.224 | 290.1721 | 1464.9 | 1513.1765 | -3.2956 | 87.2527 | 901.6743 | 95.8977 | 124.245 | 107.002 | 17.979 | 8.86 | 8.375 | 17.235 | 17.235 | 0.34159 | 0.51407 | 13.4582 | 13.4582 | 4.1429 | 93.5016 | 0.14394 | 5.605 | 7.197 | 19.2075 | 290.1721 | 518.85 | 576.8283 | -11.1744 | 93.3807 | 433.5002 | 95.5692 | 107.002 | 100.173 | 17.979 | 4.282 | 4.093 | 8.375 | 8.375 | 0.3326 | 0.51128 | 13.0086 | 13.0086 | 7.4318 | 78.1767 | 0.1664 | 5.605 | 7.197 | 30.9062 | 518.85 | 894.6 | 1029.3252 | -15.0598 | 89.349 | 774.0876 | 96.0074 | 100.173 | 53.887 | 17.979 | 1.137 | 2.956 | 4.093 | 4.093 | 0.14103 | 0.27779 | 10.1067 | 10.1067 | 9.3887 | 49.6623 | 0.20351 | 7.197 | 7.197 | 107.1695 | 894.6 | 1464.9 | 1197.4784 | 18.2553 | 63.0669 | 1046.0392 | 89.7547
[11 empty] | 1998-07-10 | 0:00 | 1119 | 29 | 124.426 | 54.187 | 18.105 | 0 | 14.328 | 2.847 |  | 17.175 | 17.175 | 0.83424 | 0 | 13.0255 | 13.0255 | 8.9616 | 62.2399 | 0.20928 | 8.867 | 5.576 | 36.472 | 293.856 | 291.3284 | 1444 | 1573.9355 | -8.9983 | 87.4808 | 932.632 | 96.0893 | 124.426 | 107.34 | 18.105 | 8.908 | 8.267 | 17.175 | 17.175 | 0.33935 | 0.51866 | 13.5311 | 13.5311 | 4.1891 | 93.5889 | 0.14458 | 5.576 | 7.192 | 19.0893 | 291.3284 | 521.55 | 584.6762 | -12.1036 | 93.4475 | 438.0023 | 95.6417 | 107.34 | 100.52 | 18.105 | 4.283 | 3.984 | 8.267 | 8.267 | 0.32681 | 0.51808 | 13.0116 | 13.0116 | 7.5409 | 78.2841 | 0.16621 | 5.576 | 7.192 | 31.096 | 521.55 | 901.8 | 1048.8127 | -16.3021 | 89.3261 | 785.1813 | 96.0396 | 100.52 | 54.187 | 18.105 | 1.137 | 2.847 | 3.984 | 3.984 | 0.13667 | 0.28539 | 10.1067 | 10.1067 | 9.5419 | 49.7066 | 0.20333 | 7.192 | 7.192 | 106.43 | 901.8 | 1444 | 1219.4451 | 15.5509 | 63.4673 | 1060.6226 | 89.9653
[11 empty] | 1998-07-10 | 8:00 | 1127.0003 | 29 | 129.116 | 56.107 | 18.622 | 0 | 14.808 | 2.842 |  | 17.65 | 17.65 | 0.83898 | 0 | 13.4618 | 13.4618 | 9.188 | 64.8015 | 0.20774 | 8.868 | 5.613 | 36.0255 | 293.808 | 290.8787 | 1409.8 | 1618.7698 | -14.8227 | 87.6149 | 954.8243 | 96.227 | 129.116 | 111.217 | 18.622 | 9.15 | 8.5 | 17.65 | 17.65 | 0.34879 | 0.51841 | 13.8987 | 13.8987 | 4.1862 | 97.3583 | 0.14276 | 5.613 | 7.244 | 18.7347 | 290.8787 | 521.1 | 583.8338 | -12.0387 | 93.5593 | 437.3562 | 95.7164 | 111.217 | 102.459 | 18.622 | 4.402 | 4.098 | 8.5 | 8.5 | 0.33607 | 0.51788 | 13.3732 | 13.3732 | 7.5284 | 80.6876 | 0.16574 | 5.613 | 7.244 | 31.3203 | 521.1 | 909.45 | 1047.2129 | -15.1479 | 89.2325 | 784.1564 | 96.0059 | 102.459 | 56.107 | 18.622 | 1.256 | 2.842 | 4.098 | 4.098 | 0.13885 | 0.30649 | 11.1644 | 11.1644 | 9.817 | 50.844 | 0.21958 | 7.244 | 7.244 | 105.415 | 909.45 | 1409.8 | 1264.7871 | 10.2861 | 63.7598 | 1087.1185 | 90.3033
[11 empty] | 1998-07-10 | 16:00 | 1135 | 29 | 128.854 | 55.972 | 18.699 | 0 | 14.811 | 2.784 |  | 17.595 | 17.595 | 0.84177 | 0 | 13.4645 | 13.4645 | 9.2994 | 64.4146 | 0.20903 | 8.982 | 5.671 | 36.284 | 292.512 | 290.3648 | 1430.7 | 1642.0856 | -14.775 | 87.504 | 966.2252 | 96.2448 | 128.854 | 111.135 | 18.699 | 9.152 | 8.443 | 17.595 | 17.595 | 0.3473 | 0.52015 | 13.9018 | 13.9018 | 4.1888 | 97.1067 | 0.14316 | 5.671 | 7.279 | 18.715 | 290.3648 | 522.9 | 584.8264 | -11.8429 | 93.5547 | 437.5956 | 95.7232 | 111.135 | 102.405 | 18.699 | 4.403 | 4.04 | 8.443 | 8.443 | 0.333 | 0.5215 | 13.3762 | 13.3762 | 7.5926 | 80.4784 | 0.16621 | 5.671 | 7.279 | 31.4468 | 522.9 | 904.05 | 1058.5111 | -17.0855 | 89.1699 | 790.7055 | 96.023 | 102.405 | 55.972 | 18.699 | 1.256 | 2.784 | 4.04 | 4.04 | 0.13653 | 0.31089 | 11.1644 | 11.1644 | 9.7927 | 50.6968 | 0.22022 | 7.279 | 7.279 | 105.0235 | 904.05 | 1430.7 | 1264.5303 | 11.6146 | 63.8305 | 1084.2902 | 90.3141
[11 empty] | 1998-07-11 | 0:00 | 1143 | 29 | 129.082 | 56.22 | 18.591 | 0 | 14.87 | 2.725 |  | 17.595 | 17.595 | 0.84513 | 0 | 13.5182 | 13.5182 | 9.5359 | 64.5241 | 0.20951 | 7.458 | 5.615 | 35.6965 | 294.816 | 291.4569 | 1411.7 | 1687.1108 | -19.5092 | 87.7524 | 989.2838 | 96.3917 | 129.082 | 111.495 | 18.591 | 9.211 | 8.384 | 17.595 | 17.595 | 0.34651 | 0.5235 | 13.9914 | 13.9914 | 4.2293 | 97.4682 | 0.14355 | 5.615 | 7.272 | 18.4786 | 291.4569 | 522 | 591.3618 | -13.2877 | 93.6599 | 441.4093 | 95.8137 | 111.495 | 102.486 | 18.591 | 4.403 | 3.981 | 8.384 | 8.384 | 0.32985 | 0.52517 | 13.3762 | 13.3762 | 7.6172 | 80.7823 | 0.16558 | 5.615 | 7.272 | 31.5158 | 522 | 913.95 | 1064.4773 | -16.47 | 89.1868 | 793.2387 | 96.027 | 102.486 | 56.22 | 18.591 | 1.256 | 2.725 | 3.981 | 3.981 | 0.13417 | 0.3155 | 11.1644 | 11.1644 | 9.9639 | 50.7981 | 0.21978 | 7.272 | 7.272 | 104.1825 | 913.95 | 1411.7 | 1287.186 | 8.8201 | 64.2546 | 1100.568 | 90.5338
[11 empty] | 1998-07-11 | 8:00 | 1151 | 29 | 129.149 | 56.167 | 18.64 | 0 | 14.81 | 2.791 |  | 17.601 | 17.601 | 0.84143 | 0 | 13.4636 | 13.4636 | 9.326 | 64.692 | 0.20812 | 9.253 | 5.607 | 35.626 | 293.856 | 290.9108 | 1394.6 | 1645.5395 | -17.9937 | 87.7536 | 968.2252 | 96.3205 | 129.149 | 111.367 | 18.64 | 9.153 | 8.448 | 17.601 | 17.601 | 0.34745 | 0.52003 | 13.9033 | 13.9033 | 4.2011 | 97.4169 | 0.14272 | 5.607 | 7.27 | 18.4195 | 290.9108 | 521.55 | 586.142 | -12.3846 | 93.6683 | 438.5264 | 95.7997 | 111.367 | 102.468 | 18.64 | 4.401 | 4.047 | 8.448 | 8.448 | 0.33332 | 0.52095 | 13.3701 | 13.3701 | 7.565 | 80.7125 | 0.16565 | 5.607 | 7.27 | 31.5042 | 521.55 | 910.8 | 1054.4611 | -15.7731 | 89.1705 | 788.0056 | 96.002 | 102.468 | 56.167 | 18.64 | 1.256 | 2.791 | 4.047 | 4.047 | 0.13681 | 0.31035 | 11.1644 | 11.1644 | 9.8847 | 50.7928 | 0.2198 | 7.27 | 7.27 | 103.8925 | 910.8 | 1394.6 | 1273.9228 | 8.6532 | 64.2872 | 1092.3614 | 90.4892
[11 empty] | 1998-07-11 | 16:00 | 1159.0003 | 29 | 129.075 | 56.032 | 18.66 | 0 | 14.806 | 2.792 |  | 17.598 | 17.598 | 0.84135 | 0 | 13.46 | 13.46 | 9.3373 | 64.5562 | 0.2085 | 8.919 | 5.615 | 35.6495 | 293.904 | 291.3605 | 1409.8 | 1647.3983 | -16.8533 | 87.7645 | 969.3794 | 96.3224 | 129.075 | 111.285 | 18.66 | 9.148 | 8.45 | 17.598 | 17.598 | 0.34743 | 0.51983 | 13.8957 | 13.8957 | 4.2068 | 97.3132 | 0.14279 | 5.615 | 7.239 | 18.4195 | 291.3605 | 523.8 | 586.8474 | -12.0365 | 93.6781 | 439.104 | 95.8052 | 111.285 | 102.491 | 18.66 | 4.402 | 4.048 | 8.45 | 8.45 | 0.3334 | 0.52095 | 13.3732 | 13.3732 | 7.5995 | 80.6285 | 0.16586 | 5.615 | 7.239 | 31.5158 | 523.8 | 909.9 | 1059.1348 | -16.4012 | 89.1832 | 791.4674 | 96.0181 | 102.491 | 56.032 | 18.66 | 1.256 | 2.792 | 4.048 | 4.048 | 0.13685 | 0.31028 | 11.1644 | 11.1644 | 9.8696 | 50.7319 | 0.22007 | 7.239 | 7.239 | 104.168 | 909.9 | 1409.8 | 1272.364 | 9.7486 | 64.2477 | 1091.132 | 90.4532
[11 empty] | 1998-07-12 | 0:00 | 1167 | 29 | 129.39 | 56.205 | 18.625 | 0 | 14.808 | 2.902 |  | 17.71 | 17.71 | 0.83614 | 0 | 13.4618 | 13.4618 | 9.0959 | 65.0766 | 0.20686 | 9.135 | 5.61 | 35.5555 | 294.528 | 291.6817 | 1390.8 | 1598.6139 | -14.942 | 87.8102 | 945.1478 | 96.2381 | 129.39 | 111.907 | 18.625 | 9.149 | 8.561 | 17.71 | 17.71 | 0.35041 | 0.5166 | 13.8972 | 13.8972 | 4.1946 | 97.8289 | 0.14206 | 5.61 | 7.228 | 18.3013 | 291.6817 | 524.7 | 583.8389 | -11.271 | 93.7256 | 437.7603 | 95.8193 | 111.907 | 102.81 | 18.625 | 4.402 | 4.159 | 8.561 | 8.561 | 0.33932 | 0.51419 | 13.3732 | 13.3732 | 7.5407 | 81.1928 | 0.16471 | 5.61 | 7.228 | 31.5905 | 524.7 | 912.6 | 1046.6207 | -14.6856 | 89.1695 | 785.6603 | 95.9791 | 102.81 | 56.205 | 18.625 | 1.257 | 2.902 | 4.159 | 4.159 | 0.14127 | 0.30224 | 11.1733 | 11.1733 | 9.8332 | 51.0493 | 0.21887 | 7.228 | 7.228 | 104.3275 | 912.6 | 1390.8 | 1262.7029 | 9.2103 | 64.2324 | 1087.6514 | 90.408
[11 empty] | 1998-07-12 | 8:00 | 1175 | 29 | 128.948 | 55.995 | 18.576 | 0 | 14.753 | 2.954 |  | 17.707 | 17.707 | 0.83317 | 0 | 13.4118 | 13.4118 | 8.9416 | 64.9539 | 0.20648 | 9.015 | 5.576 | 35.579 | 294.624 | 291.2642 | 1407.9 | 1568.2185 | -11.3871 | 87.7846 | 929.7413 | 96.1732 | 128.948 | 111.322 | 18.576 | 9.213 | 8.494 | 17.707 | 17.707 | 0.34947 | 0.5203 | 13.9944 | 13.9944 | 4.2097 | 97.3493 | 0.14375 | 5.576 | 7.199 | 18.321 | 291.2642 | 524.7 | 587.3114 | -11.9328 | 93.7098 | 439.2878 | 95.8294 | 111.322 | 102.558 | 18.576 | 4.403 | 4.091 | 8.494 | 8.494 | 0.33572 | 0.51837 | 13.3762 | 13.3762 | 7.5846 | 80.7794 | 0.16559 | 5.576 | 7.199 | 31.5963 | 524.7 | 913.05 | 1055.4103 | -15.5917 | 89.152 | 790.0551 | 96.0008 | 102.558 | 55.995 | 18.576 | 1.137 | 2.954 | 4.091 | 4.091 | 0.14095 | 0.27793 | 10.1067 | 10.1067 | 9.6429 | 51.0576 | 0.19795 | 7.199 | 7.199 | 104.3855 | 913.05 | 1407.9 | 1224.3064 | 13.0402 | 64.1612 | 1068.6782 | 90.2323
[11 empty] | 1998-07-12 | 19:00 | 1186 | 29 | 128.834 | 56.152 | 18.531 | 0 | 14.87 | 2.726 |  | 17.596 | 17.596 | 0.84508 | 0 | 13.5182 | 13.5182 | 9.5324 | 64.4296 | 0.20981 | 9.066 | 5.616 | 35.72 | 293.904 | 291.4569 | 1400.3 | 1686.4706 | -20.4364 | 87.7443 | 988.9637 | 96.3881 | 128.834 | 111.375 | 18.531 | 9.21 | 8.386 | 17.596 | 17.596 | 0.34655 | 0.52341 | 13.9899 | 13.9899 | 4.2285 | 97.345 | 0.14371 | 5.616 | 7.236 | 18.4983 | 291.4569 | 525.6 | 591.2361 | -12.4878 | 93.6532 | 441.3465 | 95.8087 | 111.375 | 102.446 | 18.531 | 4.463 | 3.923 | 8.386 | 8.386 | 0.32836 | 0.5322 | 13.5585 | 13.5585 | 7.7499 | 80.6296 | 0.16816 | 5.616 | 7.236 | 31.6077 | 525.6 | 914.4 | 1087.5902 | -18.9403 | 89.1553 | 806.5951 | 96.0813 | 102.446 | 56.152 | 18.531 | 1.197 | 2.726 | 3.923 | 3.923 | 0.13303 | 0.30512 | 10.64 | 10.64 | 9.8809 | 50.8871 | 0.20909 | 7.236 | 7.236 | 104.197 | 914.4 | 1400.3 | 1270.1641 | 9.2934 | 64.2496 | 1092.2821 | 90.4606
[11 empty] | 1998-07-13 | 0:00 | 1191 | 29 | 129.089 | 56.362 | 18.567 | 0 | 14.813 | 2.831 |  | 17.644 | 17.644 | 0.83955 | 0 | 13.4664 | 13.4664 | 9.2615 | 64.897 | 0.2075 | 9.188 | 5.6 | 35.6025 | 295.44 | 291.7138 | 1390.8 | 1631.7977 | -17.328 | 87.7954 | 961.7557 | 96.2982 | 129.089 | 111.495 | 18.567 | 9.213 | 8.431 | 17.644 | 17.644 | 0.34779 | 0.52216 | 13.9944 | 13.9944 | 4.2274 | 97.4976 | 0.14354 | 5.6 | 7.209 | 18.3407 | 291.7138 | 524.7 | 590.4431 | -12.5297 | 93.7128 | 441.0785 | 95.8419 | 111.495 | 102.585 | 18.567 | 4.401 | 4.03 | 8.431 | 8.431 | 0.33241 | 0.522 | 13.3701 | 13.3701 | 7.6235 | 80.8495 | 0.16537 | 5.6 | 7.209 | 31.5963 | 524.7 | 917.1 | 1063.1987 | -15.9305 | 89.1688 | 793.9493 | 96.0204 | 102.585 | 56.362 | 18.567 | 1.199 | 2.831 | 4.03 | 4.03 | 0.13727 | 0.29752 | 10.6578 | 10.6578 | 9.8483 | 51.0582 | 0.20874 | 7.209 | 7.209 | 104.371 | 917.1 | 1390.8 | 1261.3113 | 9.3104 | 64.2214 | 1089.2056 | 90.4177
[11 empty] | 1998-07-13 | 11:00 | 1202 | 29 | 128.948 | 56.137 | 18.538 | 0 | 14.81 | 2.783 |  | 17.593 | 17.593 | 0.84181 | 0 | 13.4636 | 13.4636 | 9.3315 | 64.673 | 0.20818 | 8.979 | 5.634 | 35.814 | 293.28 | 290.7181 | 1398.4 | 1647.2147 | -17.7928 | 87.6809 | 968.9664 | 96.3039 | 128.948 | 111.045 | 18.538 | 9.152 | 8.441 | 17.593 | 17.593 | 0.34725 | 0.52021 | 13.9018 | 13.9018 | 4.2019 | 97.2566 | 0.14294 | 5.634 | 7.267 | 18.2422 | 290.7181 | 522.9 | 586.1452 | -12.0951 | 93.7251 | 438.4316 | 95.8392 | 111.045 | 102.347 | 18.538 | 4.402 | 4.039 | 8.441 | 8.441 | 0.33292 | 0.5215 | 13.3732 | 13.3732 | 7.5926 | 80.5654 | 0.16599 | 5.634 | 7.267 | 31.4468 | 522.9 | 908.1 | 1058.522 | -16.5645 | 89.1831 | 790.711 | 96.023 | 102.347 | 56.137 | 18.538 | 1.256 | 2.783 | 4.039 | 4.039 | 0.13649 | 0.31097 | 11.1644 | 11.1644 | 9.8554 | 50.8486 | 0.21956 | 7.267 | 7.267 | 104.0085 | 908.1 | 1398.4 | 1270.9958 | 9.1107 | 64.2236 | 1089.5479 | 90.454
[11 empty] | 1998-07-13 | 19:00 | 1210 | 29 | 129.263 | 56.31 | 18.565 | 0 | 14.748 | 2.85 |  | 17.598 | 17.598 | 0.83805 | 0 | 13.4073 | 13.4073 | 9.1712 | 65.0503 | 0.20611 | 9.199 | 5.648 | 35.579 | 295.392 | 291.232 | 1390.8 | 1614.1692 | -16.0605 | 87.7833 | 952.7006 | 96.2655 | 129.263 | 111.547 | 18.565 | 9.148 | 8.45 | 17.598 | 17.598 | 0.34743 | 0.51983 | 13.8957 | 13.8957 | 4.2064 | 97.6336 | 0.14232 | 5.648 | 7.28 | 18.321 | 291.232 | 524.7 | 586.6865 | -11.8137 | 93.7091 | 438.9593 | 95.8263 | 111.547 | 102.702 | 18.565 | 4.402 | 4.048 | 8.45 | 8.45 | 0.3334 | 0.52095 | 13.3732 | 13.3732 | 7.6106 | 80.9489 | 0.1652 | 5.648 | 7.28 | 31.6998 | 524.7 | 917.1 | 1060.8134 | -15.6704 | 89.1153 | 792.7567 | 96.0013 | 102.702 | 56.31 | 18.565 | 1.198 | 2.85 | 4.048 | 4.048 | 0.13801 | 0.29595 | 10.6489 | 10.6489 | 9.8325 | 51.1085 | 0.20836 | 7.28 | 7.28 | 104.6175 | 917.1 | 1390.8 | 1258.6277 | 9.5033 | 64.0776 | 1087.8639 | 90.3832
[11 empty] | 1998-07-14 | 3:00 | 1218 | 29 | 129.578 | 56.482 | 18.588 | 0 | 14.75 | 2.896 |  | 17.646 | 17.646 | 0.83588 | 0 | 13.4091 | 13.4091 | 9.1011 | 65.3409 | 0.20522 | 9.327 | 5.608 | 35.485 | 295.296 | 292.0993 | 1388.9 | 1599.0954 | -15.1339 | 87.8517 | 945.5973 | 96.2473 | 129.578 | 112.035 | 18.588 | 9.212 | 8.434 | 17.646 | 17.646 | 0.34786 | 0.52204 | 13.9929 | 13.9929 | 4.2339 | 97.9846 | 0.14281 | 5.608 | 7.239 | 18.2619 | 292.0993 | 524.25 | 591.197 | -12.77 | 93.7481 | 441.6481 | 95.8651 | 112.035 | 102.815 | 18.588 | 4.402 | 4.032 | 8.434 | 8.434 | 0.33255 | 0.52194 | 13.3732 | 13.3732 | 7.6145 | 81.2225 | 0.16465 | 5.608 | 7.239 | 31.6825 | 524.25 | 917.55 | 1062.0184 | -15.745 | 89.1535 | 793.1342 | 96.0054 | 102.815 | 56.482 | 18.588 | 1.136 | 2.896 | 4.032 | 4.032 | 0.13861 | 0.28175 | 10.0978 | 10.0978 | 9.7276 | 51.3329 | 0.19671 | 7.239 | 7.239 | 104.2985 | 917.55 | 1388.9 | 1236.5603 | 10.9684 | 64.2935 | 1077.0551 | 90.3163
[11 empty] | 1998-07-14 | 10:18 | 1225.2981 | 29 | 128.707 | 56.077 | 18.588 | 0 | 14.872 | 2.718 |  | 17.59 | 17.59 | 0.84548 | 0 | 13.52 | 13.52 | 9.5393 | 64.2647 | 0.21038 | 8.801 | 5.595 | 35.7905 | 294.144 | 291.1357 | 1398.4 | 1688.3003 | -20.7309 | 87.7066 | 989.718 | 96.3838 | 128.707 | 111.12 | 18.588 | 9.215 | 8.375 | 17.59 | 17.59 | 0.34633 | 0.52388 | 13.9975 | 13.9975 | 4.2306 | 97.0949 | 0.14416 | 5.595 | 7.252 | 18.2225 | 291.1357 | 526.5 | 591.4216 | -12.3308 | 93.7409 | 441.2787 | 95.8705 | 111.12 | 102.351 | 18.588 | 4.401 | 3.974 | 8.375 | 8.375 | 0.32943 | 0.52549 | 13.3701 | 13.3701 | 7.6904 | 80.4571 | 0.16618 | 5.595 | 7.252 | 31.533 | 526.5 | 911.25 | 1074.6504 | -17.9315 | 89.169 | 800.5752 | 96.0612 | 102.351 | 56.077 | 18.588 | 1.256 | 2.718 | 3.974 | 3.974 | 0.13389 | 0.31605 | 11.1644 | 11.1644 | 9.9411 | 50.6849 | 0.22027 | 7.252 | 7.252 | 103.7185 | 911.25 | 1398.4 | 1284.4139 | 8.1512 | 64.3745 | 1097.832 | 90.5524
[11 empty] | 1998-07-14 | 18:00 | 1233 | 29 | 127.883 | 55.057 | 17.905 | 0 | 14.027 | 3.68 |  | 17.707 | 17.707 | 0.79217 | 0 | 12.7518 | 12.7518 | 7.3092 | 66.2558 | 0.19246 | 8.829 | 5.608 | 35.0385 | 285.024 | 286.5746 | 1404.1 | 1245.3511 | 11.3061 | 87.7733 | 765.9629 | 95.4256 | 127.883 | 109.882 | 17.905 | 8.489 | 9.218 | 17.707 | 17.707 | 0.35913 | 0.47941 | 12.8947 | 12.8947 | 3.9241 | 97.0534 | 0.13286 | 5.608 | 7.224 | 17.8876 | 286.5746 | 508.05 | 534.0127 | -5.1103 | 93.7581 | 410.2937 | 95.6403 | 109.882 | 101.64 | 17.905 | 4.402 | 4.816 | 9.218 | 9.218 | 0.37438 | 0.47754 | 13.3732 | 13.3732 | 6.9513 | 80.9047 | 0.1653 | 5.608 | 7.224 | 30.958 | 508.05 | 895.95 | 944.1295 | -5.3775 | 89.1972 | 726.0898 | 95.7363 | 101.64 | 55.057 | 17.905 | 1.136 | 3.68 | 4.816 | 4.816 | 0.16998 | 0.23588 | 10.0978 | 10.0978 | 9.1327 | 51.3108 | 0.1968 | 7.224 | 7.224 | 104.7915 | 895.95 | 1404.1 | 1140.1772 | 18.7966 | 63.4331 | 1018.0636 | 89.7068
[11 empty] | 1998-07-15 | 2:00 | 1241.0003 | 29 | 127.481 | 54.817 | 17.763 | 0 | 14.206 | 3.497 |  | 17.703 | 17.703 | 0.80246 | 0 | 12.9145 | 12.9145 | 7.6495 | 65.7365 | 0.19646 | 8.74 | 5.58 | 34.6625 | 285.936 | 287.0243 | 1404.1 | 1312.2036 | 6.5449 | 87.9235 | 799.614 | 95.6651 | 127.481 | 109.762 | 17.763 | 8.487 | 9.216 | 17.703 | 17.703 | 0.35905 | 0.47941 | 12.8916 | 12.8916 | 3.9309 | 96.9276 | 0.133 | 5.58 | 7.187 | 17.8679 | 287.0243 | 512.1 | 534.89 | -4.4503 | 93.7748 | 410.9572 | 95.6521 | 109.762 | 101.519 | 17.763 | 4.463 | 4.753 | 9.216 | 9.216 | 0.37264 | 0.48427 | 13.5585 | 13.5585 | 7.0702 | 80.8073 | 0.16779 | 5.58 | 7.187 | 30.9695 | 512.1 | 896.4 | 963.8748 | -7.5273 | 89.2101 | 737.9874 | 95.8035 | 101.519 | 54.817 | 17.763 | 1.256 | 3.497 | 4.753 | 4.753 | 0.16506 | 0.26425 | 11.1644 | 11.1644 | 9.3555 | 51.0495 | 0.2187 | 7.187 | 7.187 | 103.2835 | 896.4 | 1404.1 | 1181.2597 | 15.8707 | 64.0158 | 1038.8298 | 90.0577
[11 empty] | 1998-07-15 | 10:00 | 1249 | 29 | 128.158 | 55.417 | 17.782 | 0 | 14.027 | 3.74 |  | 17.767 | 17.767 | 0.7895 | 0 | 12.7518 | 12.7518 | 7.5045 | 66.501 | 0.19175 | 8.494 | 5.634 | 38.5165 | 310.8 | 299.519 | 1525.7 | 1278.4179 | 16.2078 | 87.1405 | 788.9685 | 95.1181 | 128.158 | 110.385 | 17.782 | 8.429 | 9.338 | 17.767 | 17.767 | 0.36153 | 0.47442 | 12.8035 | 12.8035 | 4.0711 | 97.4184 | 0.13143 | 5.634 | 7.28 | 19.0105 | 299.519 | 556.65 | 552.7216 | 0.70572 | 93.653 | 426.1203 | 95.5387 | 110.385 | 101.996 | 17.782 | 4.4 | 4.938 | 9.338 | 9.338 | 0.38083 | 0.47119 | 13.3671 | 13.3671 | 7.5603 | 80.8482 | 0.16534 | 5.634 | 7.28 | 33.6375 | 556.65 | 976.05 | 1022.6798 | -4.7774 | 88.7695 | 789.6649 | 95.7403 | 101.996 | 55.417 | 17.782 | 1.198 | 3.74 | 4.938 | 4.938 | 0.17362 | 0.24261 | 10.6489 | 10.6489 | 9.9795 | 50.945 | 0.20903 | 7.28 | 7.28 | 115.8695 | 976.05 | 1525.7 | 1251.5838 | 17.9666 | 61.3148 | 1113.8169 | 89.5971
[11 empty] | 1998-07-15 | 18:00 | 1257 | 29 | 128.305 | 55.522 | 17.722 | 0 | 14.03 | 3.5 |  | 17.53 | 17.53 | 0.80034 | 0 | 12.7545 | 12.7545 | 7.8667 | 66.3248 | 0.1923 | 8.963 | 5.623 | 38.023 | 310.656 | 299.8723 | 1508.6 | 1349.514 | 10.5453 | 87.3203 | 824.6932 | 95.3894 | 128.305 | 110.527 | 17.722 | 8.488 | 9.042 | 17.53 | 17.53 | 0.35442 | 0.4842 | 12.8932 | 12.8932 | 4.1278 | 97.5662 | 0.13215 | 5.623 | 7.253 | 18.9514 | 299.8723 | 556.2 | 563.5813 | -1.3271 | 93.6802 | 431.7268 | 95.6103 | 110.527 | 102.059 | 17.722 | 4.344 | 4.698 | 9.042 | 9.042 | 0.36653 | 0.48042 | 13.197 | 13.197 | 7.6417 | 80.9293 | 0.16307 | 5.623 | 7.253 | 33.626 | 556.2 | 975.6 | 1039.3974 | -6.5393 | 88.7866 | 797.7987 | 95.7852 | 102.059 | 55.522 | 17.722 | 1.198 | 3.5 | 4.698 | 4.698 | 0.16402 | 0.255 | 10.6489 | 10.6489 | 10.078 | 50.9905 | 0.20884 | 7.253 | 7.253 | 115.072 | 975.6 | 1508.6 | 1270.1464 | 15.8063 | 61.6263 | 1122.8732 | 89.752
[11 empty] | 1998-07-16 | 2:00 | 1265 | 29 | 128.372 | 55.335 | 17.682 | 0 | 14.145 | 3.558 |  | 17.703 | 17.703 | 0.79902 | 0 | 12.8591 | 12.8591 | 7.8361 | 66.3354 | 0.19385 | 8.812 | 5.608 | 37.9525 | 311.376 | 300.2256 | 1504.8 | 1342.9051 | 10.7586 | 87.3587 | 821.5654 | 95.3805 | 128.372 | 110.707 | 17.682 | 8.489 | 9.214 | 17.703 | 17.703 | 0.35902 | 0.47952 | 12.8947 | 12.8947 | 4.1093 | 97.7482 | 0.13192 | 5.608 | 7.199 | 18.8923 | 300.2256 | 555.75 | 559.4224 | -0.6608 | 93.7073 | 429.824 | 95.6046 | 110.707 | 102.018 | 17.682 | 4.401 | 4.813 | 9.214 | 9.214 | 0.37419 | 0.47764 | 13.3701 | 13.3701 | 7.6056 | 81.0749 | 0.16491 | 5.608 | 7.199 | 33.8158 | 555.75 | 982.8 | 1033.0059 | -5.1085 | 88.7366 | 794.3779 | 95.7431 | 102.018 | 55.335 | 17.682 | 1.255 | 3.558 | 4.813 | 4.813 | 0.16748 | 0.26075 | 11.1556 | 11.1556 | 10.211 | 50.7835 | 0.21967 | 7.199 | 7.199 | 114.782 | 982.8 | 1504.8 | 1288.9727 | 14.3426 | 61.7681 | 1135.8864 | 89.8949
[11 empty] | 1998-07-16 | 10:00 | 1273.0003 | 29 | 127.488 | 54.487 | 17.776 | 0 | 14.088 | 3.675 |  | 17.763 | 17.763 | 0.79311 | 0 | 12.8073 | 12.8073 | 7.2658 | 65.9457 | 0.19421 | 8.387 | 5.566 | 33.5815 | 277.776 | 282.6881 | 1324.3 | 1237.6307 | 6.5445 | 88.1207 | 760.1594 | 95.5823 | 127.488 | 109.74 | 17.776 | 8.431 | 9.332 | 17.763 | 17.763 | 0.3614 | 0.47464 | 12.8066 | 12.8066 | 3.8519 | 96.9861 | 0.13205 | 5.566 | 7.22 | 17.3557 | 282.6881 | 497.7 | 522.4028 | -4.9634 | 93.8605 | 402.5455 | 95.6885 | 109.74 | 101.438 | 17.776 | 4.402 | 4.93 | 9.332 | 9.332 | 0.38046 | 0.47171 | 13.3732 | 13.3732 | 6.7652 | 81.0478 | 0.165 | 5.566 | 7.22 | 29.992 | 497.7 | 863.1 | 915.3168 | -6.0499 | 89.3904 | 706.5084 | 95.7549 | 101.438 | 54.487 | 17.776 | 1.255 | 3.675 | 4.93 | 4.93 | 0.17216 | 0.25456 | 11.1556 | 11.1556 | 8.9991 | 51.1874 | 0.21794 | 7.22 | 7.22 | 94.4385 | 863.1 | 1324.3 | 1125.5953 | 15.0045 | 66.5927 | 994.3476 | 90.5025
[11 empty] | 1998-07-16 | 18:00 | 1281 | 29 | 127.287 | 54.57 | 17.779 | 0 | 14.088 | 3.613 |  | 17.701 | 17.701 | 0.79589 | 0 | 12.8073 | 12.8073 | 7.3473 | 65.8022 | 0.19463 | 9.105 | 5.615 | 33.6285 | 278.592 | 282.7202 | 1345.2 | 1253.9919 | 6.7803 | 88.1054 | 768.3561 | 95.6233 | 127.287 | 109.485 | 17.779 | 8.49 | 9.211 | 17.701 | 17.701 | 0.35896 | 0.47963 | 12.8962 | 12.8962 | 3.8757 | 96.7313 | 0.13332 | 5.615 | 7.234 | 17.4148 | 282.7202 | 497.7 | 527.2586 | -5.939 | 93.8403 | 404.9894 | 95.6999 | 109.485 | 101.303 | 17.779 | 4.4 | 4.811 | 9.211 | 9.211 | 0.37406 | 0.47769 | 13.3671 | 13.3671 | 6.8131 | 80.8019 | 0.16543 | 5.615 | 7.234 | 30.1818 | 497.7 | 866.25 | 925.2785 | -6.8143 | 89.3245 | 711.4893 | 95.7579 | 101.303 | 54.57 | 17.779 | 1.198 | 3.613 | 4.811 | 4.811 | 0.16854 | 0.24901 | 10.6489 | 10.6489 | 8.9918 | 51.1657 | 0.20813 | 7.234 | 7.234 | 94.946 | 866.25 | 1345.2 | 1121.9993 | 16.5924 | 66.417 | 994.1246 | 90.4493
[11 empty] | 1998-07-17 | 2:00 | 1289 | 29 | 127.715 | 54.84 | 17.841 | 0 | 14.15 | 3.551 |  | 17.701 | 17.701 | 0.79939 | 0 | 12.8636 | 12.8636 | 7.5072 | 65.9293 | 0.19511 | 9.019 | 5.611 | 33.0645 | 280.176 | 283.9408 | 1322.4 | 1283.6309 | 2.9317 | 88.3551 | 783.7859 | 95.7814 | 127.715 | 109.815 | 17.841 | 8.551 | 9.15 | 17.701 | 17.701 | 0.35814 | 0.48308 | 12.9889 | 12.9889 | 3.9075 | 97.0165 | 0.13388 | 5.611 | 7.241 | 17.6315 | 283.9408 | 500.85 | 532.8163 | -6.3824 | 93.7904 | 408.3785 | 95.6826 | 109.815 | 101.523 | 17.841 | 4.4 | 4.75 | 9.15 | 9.15 | 0.3708 | 0.48087 | 13.3671 | 13.3671 | 6.8854 | 80.9426 | 0.16514 | 5.611 | 7.241 | 30.268 | 500.85 | 873.45 | 936.7575 | -7.248 | 89.34 | 718.8038 | 95.7891 | 101.523 | 54.84 | 17.841 | 1.199 | 3.551 | 4.75 | 4.75 | 0.16608 | 0.25242 | 10.6578 | 10.6578 | 9.097 | 51.2435 | 0.20798 | 7.241 | 7.241 | 95.149 | 873.45 | 1322.4 | 1136.2444 | 14.0771 | 66.4898 | 1004.8472 | 90.531
[11 empty] | 1998-07-17 | 10:00 | 1297.0003 | 29 | 127.099 | 54.615 | 17.722 | 0 | 14.148 | 3.616 |  | 17.764 | 17.764 | 0.79644 | 0 | 12.8618 | 12.8618 | 7.367 | 65.768 | 0.19556 | 8.742 | 5.617 | 33.652 | 278.688 | 282.8487 | 1347.1 | 1257.8585 | 6.6247 | 88.1025 | 770.3536 | 95.6316 | 127.099 | 109.245 | 17.722 | 8.492 | 9.272 | 17.764 | 17.764 | 0.36061 | 0.47805 | 12.8992 | 12.8992 | 3.869 | 96.581 | 0.13356 | 5.617 | 7.237 | 17.4739 | 282.8487 | 499.05 | 525.8991 | -5.38 | 93.8222 | 404.3739 | 95.6788 | 109.245 | 101.199 | 17.722 | 4.4 | 4.872 | 9.272 | 9.272 | 0.37731 | 0.47455 | 13.3671 | 13.3671 | 6.8071 | 80.6929 | 0.16565 | 5.617 | 7.237 | 30.1013 | 499.05 | 867.15 | 922.5669 | -6.3907 | 89.3578 | 710.8085 | 95.7652 | 101.199 | 54.615 | 17.722 | 1.256 | 3.616 | 4.872 | 4.872 | 0.16982 | 0.2578 | 11.1644 | 11.1644 | 9.0626 | 51.1224 | 0.21839 | 7.237 | 7.237 | 94.9895 | 867.15 | 1347.1 | 1135.3562 | 15.7185 | 66.4169 | 1001.2531 | 90.5129
[11 empty] | 1998-07-17 | 18:00 | 1305 | 29 | 127.28 | 53.805 | 17.835 | 0 | 14.153 | 3.488 |  | 17.641 | 17.641 | 0.80228 | 0 | 12.8664 | 12.8664 | 7.7786 | 64.9289 | 0.19816 | 8.638 | 5.603 | 36.9185 | 298.176 | 293.7374 | 1463 | 1335.8125 | 8.6936 | 87.4315 | 814.7749 | 95.4689 | 127.28 | 109.305 | 17.835 | 8.554 | 9.087 | 17.641 | 17.641 | 0.3565 | 0.48489 | 12.9934 | 12.9934 | 4.0482 | 96.4093 | 0.13477 | 5.603 | 7.234 | 18.4786 | 293.7374 | 534.15 | 552.8508 | -3.501 | 93.7091 | 423.2941 | 95.6346 | 109.305 | 101.294 | 17.835 | 4.4 | 4.687 | 9.087 | 9.087 | 0.36744 | 0.48421 | 13.3671 | 13.3671 | 7.3795 | 80.085 | 0.16691 | 5.603 | 7.234 | 31.9297 | 534.15 | 929.7 | 1005.6177 | -8.1658 | 89.1298 | 769.8838 | 95.8527 | 101.294 | 53.805 | 17.835 | 1.199 | 3.488 | 4.687 | 4.687 | 0.16356 | 0.25581 | 10.6578 | 10.6578 | 9.6173 | 50.0972 | 0.21274 | 7.234 | 7.234 | 109.0255 | 929.7 | 1463 | 1211.8069 | 17.1697 | 62.8833 | 1070.7534 | 89.8179
[11 empty] | 1998-07-18 | 0:00 | 1311 | 29 | 127.494 | 53.887 | 17.844 | 0 | 14.208 | 3.432 |  | 17.64 | 17.64 | 0.80544 | 0 | 12.9164 | 12.9164 | 7.8952 | 64.9513 | 0.19886 | 8.755 | 5.587 | 36.848 | 299.664 | 294.0265 | 1459.2 | 1358.7094 | 6.8867 | 87.4678 | 826.3679 | 95.541 | 127.494 | 109.74 | 17.844 | 8.551 | 9.089 | 17.64 | 17.64 | 0.35652 | 0.48475 | 12.9889 | 12.9889 | 4.0485 | 96.7245 | 0.13429 | 5.587 | 7.179 | 18.6953 | 294.0265 | 536.85 | 553.0601 | -3.0195 | 93.6416 | 423.5433 | 95.586 | 109.74 | 101.429 | 17.844 | 4.401 | 4.688 | 9.089 | 9.089 | 0.36752 | 0.48421 | 13.3701 | 13.3701 | 7.4181 | 80.3224 | 0.16646 | 5.587 | 7.179 | 32.0102 | 536.85 | 932.85 | 1010.7834 | -8.3543 | 89.1131 | 773.8167 | 95.8633 | 101.429 | 53.887 | 17.844 | 1.256 | 3.432 | 4.688 | 4.688 | 0.16246 | 0.26792 | 11.1644 | 11.1644 | 9.7497 | 50.0643 | 0.223 | 7.179 | 7.179 | 108.692 | 932.85 | 1459.2 | 1234.4649 | 15.4013 | 63.0333 | 1083.6575 | 89.9699
[11 empty] | 1998-07-18 | 10:00 | 1321 | 29 | 126.918 | 53.167 | 17.881 | 0 | 14.209 | 3.551 |  | 17.76 | 17.76 | 0.80006 | 0 | 12.9173 | 12.9173 | 7.49 | 64.6715 | 0.19974 | 8.861 | 5.594 | 33.7225 | 279.744 | 283.3305 | 1347.1 | 1282.1141 | 4.8241 | 88.0978 | 782.7223 | 95.6916 | 126.918 | 108.742 | 17.881 | 8.554 | 9.206 | 17.76 | 17.76 | 0.35968 | 0.48164 | 12.9934 | 12.9934 | 3.8879 | 96.0611 | 0.13526 | 5.594 | 7.216 | 17.8679 | 283.3305 | 498.6 | 529.9922 | -6.2961 | 93.6936 | 406.6614 | 95.6062 | 108.742 | 100.929 | 17.881 | 4.399 | 4.807 | 9.206 | 9.206 | 0.37382 | 0.47784 | 13.3641 | 13.3641 | 6.8345 | 80.12 | 0.1668 | 5.594 | 7.216 | 29.6988 | 498.6 | 864 | 927.7027 | -7.373 | 89.518 | 713.1513 | 95.8356 | 100.929 | 53.167 | 17.881 | 1.256 | 3.551 | 4.807 | 4.807 | 0.16722 | 0.26129 | 11.1644 | 11.1644 | 9.0465 | 50.1205 | 0.22275 | 7.216 | 7.216 | 95.294 | 864 | 1347.1 | 1135.8938 | 15.6786 | 66.3665 | 999.9469 | 90.4701
[11 empty] | 1998-07-18 | 18:00 | 1329 | 29 | 127.179 | 53.61 | 17.893 | 0 | 14.27 | 3.494 |  | 17.764 | 17.764 | 0.80331 | 0 | 12.9727 | 12.9727 | 7.5939 | 64.9076 | 0.19986 | 8.788 | 5.652 | 33.605 | 279.504 | 283.2342 | 1345.2 | 1302.7557 | 3.1552 | 88.1353 | 792.9949 | 95.7623 | 127.179 | 109.297 | 17.893 | 8.551 | 9.213 | 17.764 | 17.764 | 0.35982 | 0.48137 | 12.9889 | 12.9889 | 3.8863 | 96.4587 | 0.13466 | 5.652 | 7.262 | 17.7891 | 283.2342 | 498.15 | 529.6057 | -6.3145 | 93.7193 | 406.4199 | 95.623 | 109.297 | 101.123 | 17.893 | 4.462 | 4.751 | 9.213 | 9.213 | 0.37251 | 0.48432 | 13.5554 | 13.5554 | 6.8832 | 80.4338 | 0.16853 | 5.652 | 7.262 | 29.7735 | 498.15 | 862.65 | 938.0355 | -8.7388 | 89.488 | 718.0927 | 95.8538 | 101.123 | 53.61 | 17.893 | 1.257 | 3.494 | 4.751 | 4.751 | 0.16496 | 0.26458 | 11.1733 | 11.1733 | 9.0506 | 50.4229 | 0.22159 | 7.262 | 7.262 | 95.5695 | 862.65 | 1345.2 | 1138.6146 | 15.3572 | 66.2578 | 1000.6323 | 90.4491
[11 empty] | 1998-07-19 | 2:00 | 1337.0003 | 29 | 127.729 | 53.97 | 17.812 | 0 | 14.085 | 3.679 |  | 17.764 | 17.764 | 0.7929 | 0 | 12.8045 | 12.8045 | 7.5064 | 65.5311 | 0.1954 | 8.843 | 5.625 | 36.4485 | 299.76 | 294.0265 | 1444 | 1280.1602 | 11.3462 | 87.6037 | 787.0933 | 95.3692 | 127.729 | 109.65 | 17.812 | 8.548 | 9.216 | 17.764 | 17.764 | 0.35986 | 0.4812 | 12.9843 | 12.9843 | 4.0354 | 96.8421 | 0.13408 | 5.625 | 7.23 | 18.3407 | 294.0265 | 537.3 | 549.7298 | -2.3134 | 93.7622 | 421.8782 | 95.6526 | 109.65 | 101.442 | 17.812 | 4.401 | 4.815 | 9.216 | 9.216 | 0.3743 | 0.47754 | 13.3701 | 13.3701 | 7.3637 | 80.3703 | 0.16636 | 5.625 | 7.23 | 31.901 | 537.3 | 936.45 | 999.2441 | -6.7056 | 89.1503 | 768.2721 | 95.8477 | 101.442 | 53.97 | 17.812 | 1.136 | 3.679 | 4.815 | 4.815 | 0.16994 | 0.23593 | 10.0978 | 10.0978 | 9.5673 | 50.3267 | 0.20064 | 7.23 | 7.23 | 107.677 | 936.45 | 1444 | 1192.3582 | 17.4267 | 63.3785 | 1064.4041 | 89.8838
[11 empty] | 1998-07-19 | 10:00 | 1345.0003 | 29 | 127.568 | 53.842 | 17.845 | 0 | 14.152 | 3.551 |  | 17.703 | 17.703 | 0.79941 | 0 | 12.8655 | 12.8655 | 7.6982 | 65.1618 | 0.19744 | 8.912 | 5.616 | 36.566 | 298.272 | 293.8016 | 1447.8 | 1318.9773 | 8.8978 | 87.5542 | 806.3895 | 95.4655 | 127.568 | 109.575 | 17.845 | 8.554 | 9.149 | 17.703 | 17.703 | 0.35816 | 0.48319 | 12.9934 | 12.9934 | 4.0397 | 96.6868 | 0.13439 | 5.616 | 7.212 | 18.518 | 293.8016 | 534.6 | 551.1824 | -3.1018 | 93.6971 | 422.492 | 95.617 | 109.575 | 101.402 | 17.845 | 4.4 | 4.749 | 9.149 | 9.149 | 0.37075 | 0.48093 | 13.3671 | 13.3671 | 7.3552 | 80.2883 | 0.16649 | 5.616 | 7.212 | 31.9413 | 534.6 | 930.6 | 1000.3188 | -7.4918 | 89.1283 | 767.4594 | 95.8381 | 101.402 | 53.842 | 17.845 | 1.198 | 3.551 | 4.749 | 4.749 | 0.16606 | 0.25226 | 10.6489 | 10.6489 | 9.6281 | 50.1489 | 0.21235 | 7.212 | 7.212 | 106.7635 | 930.6 | 1447.8 | 1208.5375 | 16.5259 | 63.6614 | 1069.5688 | 90.0181
[11 empty] | 1998-07-19 | 18:00 | 1353 | 29 | 127.95 | 54.03 | 17.856 | 0 | 14.206 | 3.494 |  | 17.7 | 17.7 | 0.8026 | 0 | 12.9145 | 12.9145 | 7.7997 | 65.3343 | 0.19767 | 8.882 | 5.615 | 36.472 | 298.944 | 293.641 | 1426.9 | 1339.2459 | 6.143 | 87.5794 | 816.4435 | 95.5328 | 127.95 | 110.235 | 17.856 | 8.55 | 9.15 | 17.7 | 17.7 | 0.35813 | 0.48305 | 12.9873 | 12.9873 | 4.0381 | 97.1984 | 0.13362 | 5.615 | 7.219 | 18.4195 | 293.641 | 537.3 | 550.8153 | -2.5154 | 93.7272 | 422.2282 | 95.6375 | 110.235 | 101.726 | 17.856 | 4.4 | 4.75 | 9.15 | 9.15 | 0.3708 | 0.48087 | 13.3671 | 13.3671 | 7.3933 | 80.7312 | 0.16558 | 5.615 | 7.219 | 32.0045 | 537.3 | 933.3 | 1005.3632 | -7.7213 | 89.1008 | 771.3316 | 95.8507 | 101.726 | 54.03 | 17.856 | 1.256 | 3.494 | 4.75 | 4.75 | 0.16494 | 0.26442 | 11.1644 | 11.1644 | 9.7518 | 50.2702 | 0.22209 | 7.219 | 7.219 | 106.691 | 933.3 | 1426.9 | 1230.4439 | 13.768 | 63.6662 | 1081.872 | 90.1383
[11 empty] | 1998-07-20 | 2:00 | 1361.0003 | 29 | 127.849 | 53.97 | 17.833 | 0 | 14.149 | 3.552 |  | 17.701 | 17.701 | 0.79933 | 0 | 12.8627 | 12.8627 | 7.7067 | 65.3698 | 0.19677 | 8.643 | 5.61 | 36.425 | 299.712 | 294.0265 | 1423.1 | 1320.1535 | 7.234 | 87.6117 | 807.09 | 95.4869 | 127.849 | 110.017 | 17.833 | 8.55 | 9.151 | 17.701 | 17.701 | 0.35816 | 0.48302 | 12.9873 | 12.9873 | 4.0445 | 97.0555 | 0.13381 | 5.61 | 7.205 | 18.3604 | 294.0265 | 536.85 | 551.5879 | -2.7453 | 93.7555 | 422.8072 | 95.6575 | 110.017 | 101.622 | 17.833 | 4.401 | 4.75 | 9.151 | 9.151 | 0.37083 | 0.48093 | 13.3701 | 13.3701 | 7.3872 | 80.5993 | 0.16588 | 5.61 | 7.205 | 32.0045 | 536.85 | 932.4 | 1004.6026 | -7.7437 | 89.1151 | 770.7263 | 95.8475 | 101.622 | 53.97 | 17.833 | 1.198 | 3.552 | 4.75 | 4.75 | 0.1661 | 0.25221 | 10.6489 | 10.6489 | 9.6468 | 50.3162 | 0.21164 | 7.205 | 7.205 | 106.923 | 932.4 | 1423.1 | 1210.8126 | 14.9173 | 63.6349 | 1071.6063 | 90.0222
[11 empty] | 1998-07-20 | 10:00 | 1369.0003 | 29 | 127.963 | 53.835 | 17.815 | 0 | 14.148 | 3.555 |  | 17.703 | 17.703 | 0.79919 | 0 | 12.8618 | 12.8618 | 7.6049 | 65.4791 | 0.19643 | 8.422 | 5.592 | 34.7565 | 290.544 | 289.1121 | 1377.5 | 1301.3831 | 5.5257 | 87.9782 | 795.2476 | 95.6295 | 127.963 | 110.032 | 17.815 | 8.55 | 9.153 | 17.703 | 17.703 | 0.35821 | 0.48297 | 12.9873 | 12.9873 | 3.9767 | 97.2058 | 0.13361 | 5.592 | 7.197 | 18.0452 | 289.1121 | 521.1 | 542.3211 | -4.0724 | 93.7584 | 415.7166 | 95.6593 | 110.032 | 101.451 | 17.815 | 4.4 | 4.753 | 9.153 | 9.153 | 0.37096 | 0.48072 | 13.3671 | 13.3671 | 7.1668 | 80.7597 | 0.16552 | 5.592 | 7.197 | 31.188 | 521.1 | 909 | 974.6268 | -7.2197 | 89.2125 | 747.8634 | 95.8297 | 101.451 | 53.835 | 17.815 | 1.198 | 3.555 | 4.753 | 4.753 | 0.16622 | 0.25205 | 10.6489 | 10.6489 | 9.441 | 50.387 | 0.21134 | 7.197 | 7.197 | 101.036 | 909 | 1377.5 | 1181.2759 | 14.2449 | 65.053 | 1045.138 | 90.3328
[11 empty] | 1998-07-20 | 18:00 | 1377 | 29 | 128.238 | 54.232 | 18.534 | 0 | 14.863 | 2.729 |  | 17.592 | 17.592 | 0.84487 | 0 | 13.5118 | 13.5118 | 9.3396 | 63.3614 | 0.21325 | 8.281 | 5.609 | 32.994 | 280.8 | 283.8444 | 1286.3 | 1650.0555 | -28.2792 | 88.376 | 966.95 | 96.5878 | 128.238 | 110.422 | 18.534 | 9.206 | 8.386 | 17.592 | 17.592 | 0.3465 | 0.52331 | 13.9838 | 13.9838 | 4.1249 | 96.6711 | 0.14465 | 5.609 | 7.225 | 17.533 | 283.8444 | 495.9 | 576.1963 | -16.192 | 93.823 | 430.0204 | 95.9228 | 110.422 | 101.906 | 18.534 | 4.401 | 3.985 | 8.386 | 8.386 | 0.33001 | 0.5248 | 13.3701 | 13.3701 | 7.2373 | 80.3927 | 0.16631 | 5.609 | 7.225 | 29.6355 | 495.9 | 864.45 | 1010.8385 | -16.9343 | 89.5592 | 753.3693 | 96.0663 | 101.906 | 54.232 | 18.534 | 1.256 | 2.729 | 3.985 | 3.985 | 0.13433 | 0.31518 | 11.1644 | 11.1644 | 9.4797 | 50.0553 | 0.22304 | 7.225 | 7.225 | 93.815 | 864.45 | 1286.3 | 1219.1285 | 5.2221 | 66.9484 | 1041.7892 | 90.9948
[11 empty] | 1998-07-21 | 2:00 | 1385 | 29 | 128.486 | 54.375 | 18.552 | 0 | 14.806 | 2.957 |  | 17.763 | 17.763 | 0.83353 | 0 | 13.46 | 13.46 | 8.8041 | 64.0744 | 0.21007 | 8.751 | 5.621 | 32.9705 | 280.752 | 284.262 | 1284.4 | 1542.5041 | -20.0953 | 88.4014 | 913.3831 | 96.3903 | 128.486 | 110.617 | 18.552 | 9.27 | 8.493 | 17.763 | 17.763 | 0.35021 | 0.52187 | 14.081 | 14.081 | 4.1236 | 96.8759 | 0.14535 | 5.621 | 7.223 | 17.4936 | 284.262 | 499.95 | 575.4363 | -15.0988 | 93.846 | 429.8491 | 95.9303 | 110.617 | 102.023 | 18.552 | 4.401 | 4.092 | 8.493 | 8.493 | 0.33572 | 0.51819 | 13.3701 | 13.3701 | 7.2308 | 80.5372 | 0.16601 | 5.621 | 7.223 | 29.7333 | 499.95 | 868.5 | 1005.6743 | -15.7944 | 89.5402 | 752.8122 | 96.0504 | 102.023 | 54.375 | 18.552 | 1.135 | 2.957 | 4.092 | 4.092 | 0.14103 | 0.27737 | 10.0889 | 10.0889 | 9.2307 | 50.4163 | 0.20011 | 7.223 | 7.223 | 94.0615 | 868.5 | 1284.4 | 1165.7566 | 9.2373 | 66.9103 | 1017.1283 | 90.7522
[11 empty] | 1998-07-21 | 10:00 | 1393.0003 | 29 | 127.039 | 53.16 | 17.985 | 0 | 14.147 | 3.614 |  | 17.761 | 17.761 | 0.79652 | 0 | 12.8609 | 12.8609 | 7.5105 | 64.604 | 0.19907 | 8.168 | 5.609 | 36.5895 | 292.128 | 290.5575 | 1445.9 | 1284.7151 | 11.1477 | 87.4071 | 787.6363 | 95.3545 | 127.039 | 109.08 | 17.985 | 8.492 | 9.269 | 17.761 | 17.761 | 0.36053 | 0.47813 | 12.8992 | 12.8992 | 3.9666 | 96.1079 | 0.13422 | 5.609 | 7.186 | 18.518 | 290.5575 | 526.05 | 539.7926 | -2.6124 | 93.6267 | 415.175 | 95.5397 | 109.08 | 101.015 | 17.985 | 4.399 | 4.87 | 9.269 | 9.269 | 0.37718 | 0.47459 | 13.3641 | 13.3641 | 7.1817 | 79.8808 | 0.1673 | 5.609 | 7.186 | 31.3203 | 526.05 | 910.8 | 972.9322 | -6.8217 | 89.2206 | 749.4911 | 95.8211 | 101.015 | 53.16 | 17.985 | 1.256 | 3.614 | 4.87 | 4.87 | 0.16974 | 0.25791 | 11.1644 | 11.1644 | 9.4404 | 49.6621 | 0.22481 | 7.186 | 7.186 | 106.517 | 910.8 | 1445.9 | 1190.3184 | 17.6763 | 63.3405 | 1050.5592 | 89.8609
[11 empty] | 1998-07-21 | 18:00 | 1401 | 29 | 128.158 | 54.075 | 17.902 | 0 | 14.024 | 3.682 |  | 17.706 | 17.706 | 0.79205 | 0 | 12.7491 | 12.7491 | 7.605 | 65.6095 | 0.19432 | 8.686 | 5.62 | 38.0935 | 310.704 | 299.9366 | 1493.4 | 1297.2443 | 13.1348 | 87.2995 | 798.5904 | 95.2299 | 128.158 | 110.31 | 17.902 | 8.488 | 9.218 | 17.706 | 17.706 | 0.35912 | 0.47939 | 12.8932 | 12.8932 | 4.1021 | 97.2299 | 0.1326 | 5.62 | 7.216 | 19.0499 | 299.9366 | 556.65 | 558.579 | -0.34654 | 93.6487 | 429.2578 | 95.5621 | 110.31 | 101.748 | 17.902 | 4.4 | 4.818 | 9.218 | 9.218 | 0.37443 | 0.47733 | 13.3671 | 13.3671 | 7.6227 | 80.5043 | 0.16604 | 5.62 | 7.216 | 33.3327 | 556.65 | 972 | 1034.5653 | -6.4368 | 88.8867 | 795.6076 | 95.8104 | 101.748 | 54.075 | 17.902 | 1.136 | 3.682 | 4.818 | 4.818 | 0.17006 | 0.23578 | 10.0978 | 10.0978 | 9.9028 | 50.1067 | 0.20153 | 7.216 | 7.216 | 114.0715 | 972 | 1493.4 | 1236.6949 | 17.1893 | 61.9681 | 1104.3475 | 89.6707
[11 empty] | 1998-07-22 | 2:00 | 1409.0003 | 29 | 128.586 | 54.27 | 17.793 | 0 | 14.085 | 3.618 |  | 17.703 | 17.703 | 0.79563 | 0 | 12.8045 | 12.8045 | 7.7024 | 65.9326 | 0.19421 | 8.284 | 5.608 | 38.0465 | 309.888 | 299.4548 | 1491.5 | 1317.1262 | 11.6912 | 87.2947 | 808.2905 | 95.293 | 128.586 | 110.497 | 17.793 | 8.488 | 9.215 | 17.703 | 17.703 | 0.35904 | 0.47947 | 12.8932 | 12.8932 | 4.1015 | 97.647 | 0.13204 | 5.608 | 7.191 | 18.6362 | 299.4548 | 552.6 | 558.1187 | -0.99867 | 93.7766 | 428.7867 | 95.6537 | 110.497 | 101.771 | 17.793 | 4.4 | 4.815 | 9.215 | 9.215 | 0.37427 | 0.47748 | 13.3671 | 13.3671 | 7.5669 | 80.7741 | 0.16549 | 5.608 | 7.191 | 33.2178 | 552.6 | 967.95 | 1027.2172 | -6.123 | 88.9073 | 789.9086 | 95.7947 | 101.771 | 54.27 | 17.793 | 1.197 | 3.618 | 4.815 | 4.815 | 0.16872 | 0.2486 | 10.64 | 10.64 | 9.9663 | 50.2612 | 0.21169 | 7.191 | 7.191 | 112.781 | 967.95 | 1491.5 | 1250.879 | 16.1328 | 62.3379 | 1109.4145 | 89.8342
[11 empty] | 1998-07-22 | 10:00 | 1417 | 29 | 128.359 | 54.382 | 17.836 | 0 | 14.144 | 3.496 |  | 17.64 | 17.64 | 0.80181 | 0 | 12.8582 | 12.8582 | 8.0421 | 65.4924 | 0.19633 | 8.058 | 5.586 | 39.292 | 319.92 | 305.3327 | 1537.1 | 1381.6714 | 10.1118 | 87.1314 | 843.502 | 95.3418 | 128.359 | 110.497 | 17.836 | 8.549 | 9.091 | 17.64 | 17.64 | 0.35654 | 0.48464 | 12.9858 | 12.9858 | 4.2106 | 97.3814 | 0.13335 | 5.586 | 7.152 | 18.9317 | 305.3327 | 571.95 | 574.6587 | -0.47359 | 93.7996 | 439.9957 | 95.6973 | 110.497 | 101.748 | 17.836 | 4.398 | 4.693 | 9.091 | 9.091 | 0.36771 | 0.48378 | 13.361 | 13.361 | 7.8951 | 80.3914 | 0.1662 | 5.586 | 7.152 | 34.3447 | 571.95 | 1003.5 | 1075.7616 | -7.201 | 88.7517 | 823.8558 | 95.8312 | 101.748 | 54.382 | 17.836 | 1.197 | 3.496 | 4.693 | 4.693 | 0.16384 | 0.25506 | 10.64 | 10.64 | 10.3629 | 49.8661 | 0.21337 | 7.152 | 7.152 | 118.6825 | 1003.5 | 1537.1 | 1306.4538 | 15.0053 | 61.1301 | 1154.9769 | 89.7243
[11 empty] | 1998-07-22 | 18:00 | 1425 | 29 | 127.025 | 53.25 | 17.856 | 0 | 14.207 | 3.616 |  | 17.823 | 17.823 | 0.79712 | 0 | 12.9155 | 12.9155 | 7.3992 | 64.8823 | 0.19906 | 8.107 | 5.579 | 33.605 | 279.504 | 283.202 | 1326.2 | 1263.8506 | 4.7014 | 88.1339 | 773.5263 | 95.6556 | 127.025 | 109.035 | 17.856 | 8.554 | 9.269 | 17.823 | 17.823 | 0.36136 | 0.47994 | 12.9934 | 12.9934 | 3.8788 | 96.2952 | 0.13493 | 5.579 | 7.209 | 17.7891 | 283.202 | 498.15 | 528.1413 | -6.0205 | 93.7186 | 405.6717 | 95.6149 | 109.035 | 101.015 | 17.856 | 4.397 | 4.872 | 9.269 | 9.269 | 0.37723 | 0.47438 | 13.358 | 13.358 | 6.7957 | 80.3733 | 0.1662 | 5.579 | 7.209 | 29.8885 | 498.15 | 866.7 | 920.7579 | -6.2372 | 89.4462 | 709.454 | 95.7871 | 101.015 | 53.25 | 17.856 | 1.256 | 3.616 | 4.872 | 4.872 | 0.16982 | 0.2578 | 11.1644 | 11.1644 | 9.0693 | 50.2072 | 0.22237 | 7.209 | 7.209 | 93.9745 | 866.7 | 1326.2 | 1135.1024 | 14.4094 | 66.8172 | 1000.9012 | 90.611
[11 empty] | 1998-07-23 | 2:00 | 1433.0003 | 29 | 127.434 | 53.347 | 17.8 | 0 | 14.209 | 3.552 |  | 17.761 | 17.761 | 0.80001 | 0 | 12.9173 | 12.9173 | 7.5142 | 65.0763 | 0.19849 | 8.298 | 5.576 | 33.1585 | 280.272 | 283.6196 | 1326.2 | 1285.5345 | 3.0663 | 88.3088 | 784.5771 | 95.7737 | 127.434 | 109.342 | 17.8 | 8.553 | 9.208 | 17.761 | 17.761 | 0.35972 | 0.48156 | 12.9919 | 12.9919 | 3.8987 | 96.6893 | 0.13437 | 5.576 | 7.169 | 17.3951 | 283.6196 | 501.3 | 530.9065 | -5.906 | 93.8667 | 407.2631 | 95.7288 | 109.342 | 101.154 | 17.8 | 4.4 | 4.808 | 9.208 | 9.208 | 0.3739 | 0.47785 | 13.3671 | 13.3671 | 6.8714 | 80.5766 | 0.16589 | 5.576 | 7.169 | 29.8712 | 501.3 | 869.85 | 932.724 | -7.2281 | 89.4678 | 717.012 | 95.8339 | 101.154 | 53.347 | 17.8 | 1.256 | 3.552 | 4.808 | 4.808 | 0.16726 | 0.26123 | 11.1644 | 11.1644 | 9.1375 | 50.313 | 0.2219 | 7.169 | 7.169 | 93.38 | 869.85 | 1326.2 | 1144.4126 | 13.7074 | 67.0756 | 1007.1313 | 90.7281
[11 empty] | 1998-07-23 | 10:00 | 1441 | 29 | 127.541 | 53.445 | 17.782 | 0 | 14.09 | 3.547 |  | 17.637 | 17.637 | 0.79889 | 0 | 12.8091 | 12.8091 | 7.6204 | 65.0906 | 0.19679 | 8.383 | 5.58 | 35.3675 | 291.936 | 290.5575 | 1396.5 | 1304.267 | 6.6046 | 87.8277 | 797.4122 | 95.5647 | 127.541 | 109.53 | 17.782 | 8.493 | 9.144 | 17.637 | 17.637 | 0.35721 | 0.48154 | 12.9008 | 12.9008 | 3.9889 | 96.7646 | 0.13332 | 5.58 | 7.148 | 18.1634 | 290.5575 | 526.5 | 543.5588 | -3.24 | 93.7488 | 417.0581 | 95.6449 | 109.53 | 101.217 | 17.782 | 4.399 | 4.745 | 9.144 | 9.144 | 0.37051 | 0.48108 | 13.3641 | 13.3641 | 7.2471 | 80.3444 | 0.16633 | 5.58 | 7.148 | 31.326 | 526.5 | 910.8 | 985.5665 | -8.2089 | 89.2187 | 756.0332 | 95.8565 | 101.217 | 53.445 | 17.782 | 1.198 | 3.547 | 4.745 | 4.745 | 0.1659 | 0.25248 | 10.6489 | 10.6489 | 9.4668 | 50.0822 | 0.21263 | 7.148 | 7.148 | 100.891 | 910.8 | 1396.5 | 1184.3469 | 15.1918 | 65.2768 | 1047.5735 | 90.3691
[11 empty] | 1998-07-24 | 1:00 | 1456 | 29 | 127.729 | 53.812 | 18.145 | 0 | 14.33 | 3.431 |  | 17.761 | 17.761 | 0.80682 | 0 | 13.0273 | 13.0273 | 8.0576 | 64.5679 | 0.20176 | 7.774 | 5.601 | 35.6025 | 293.856 | 296.5099 | 1541.106 | 1386.2223 | 10.0502 | 87.9928 | 841.3661 | 95.7685 | 127.729 | 109.942 | 18.145 | 8.731 | 9.03 | 17.761 | 17.761 | 0.35734 | 0.49158 | 13.2623 | 13.2623 | 4.1312 | 96.5593 | 0.13735 | 5.601 | 7.205 | 18.0255 | 296.5099 | 525.15 | 565.7732 | -7.7355 | 93.9208 | 431.1416 | 95.8191 | 109.942 | 101.541 | 18.145 | 4.401 | 4.629 | 9.03 | 9.03 | 0.36437 | 0.48738 | 13.3701 | 13.3701 | 7.2338 | 80.3627 | 0.16637 | 5.601 | 7.205 | 34.845 | 525.15 | 937.6 | 991.3052 | -5.7279 | 88.2483 | 758.2276 | 95.4044 | 101.541 | 53.812 | 18.145 | 1.198 | 3.431 | 4.629 | 4.629 | 0.16126 | 0.2588 | 10.6489 | 10.6489 | 9.8044 | 49.7271 | 0.21415 | 7.205 | 7.205 | 102.888 | 937.6 | 1541.106 | 1229.0558 | 20.2485 | 65.3003 | 1083.3279 | 90.5026
[11 empty] | 1998-07-24 | 9:00 | 1464 | 29 | 127.387 | 53.865 | 18.085 | 0 | 14.385 | 3.318 |  | 17.703 | 17.703 | 0.81257 | 0 | 13.0773 | 13.0773 | 8.2536 | 64.2874 | 0.20342 | 7.769 | 5.628 | 35.6965 | 293.088 | 296.2488 | 1529.388 | 1425.8585 | 6.7693 | 87.9505 | 861.0536 | 95.8543 | 127.387 | 109.41 | 18.085 | 8.73 | 8.973 | 17.703 | 17.703 | 0.35581 | 0.49314 | 13.2608 | 13.2608 | 4.1348 | 96.1787 | 0.13788 | 5.628 | 7.209 | 18.0846 | 296.2488 | 525.6 | 566.88 | -7.8539 | 93.8955 | 431.5644 | 95.8095 | 109.41 | 101.298 | 18.085 | 4.399 | 4.574 | 8.973 | 8.973 | 0.36138 | 0.49025 | 13.3641 | 13.3641 | 7.3183 | 79.9507 | 0.16715 | 5.628 | 7.209 | 31.4123 | 525.6 | 950.4 | 1000.8803 | -5.3115 | 89.3967 | 763.2401 | 95.8844 | 101.298 | 53.865 | 18.085 | 1.256 | 3.318 | 4.574 | 4.574 | 0.1579 | 0.2746 | 11.1644 | 11.1644 | 10.0847 | 49.4118 | 0.22595 | 7.209 | 7.209 | 102.4272 | 950.4 | 1529.388 | 1271.3927 | 16.8692 | 65.4253 | 1110.8964 | 90.7798
[11 empty] | 1998-07-24 | 11:12 | 1466.1986 | 29 | 127.481 | 54.217 | 18.229 | 0 | 14.39 | 3.374 |  | 17.764 | 17.764 | 0.81007 | 0 | 13.0818 | 13.0818 | 8.204 | 64.416 | 0.20308 | 8.118 | 5.572 | 34.5685 | 292.464 | 296.4691 | 1523.178 | 1413.4667 | 7.2028 | 88.3399 | 854.9679 | 95.9567 | 127.481 | 109.402 | 18.229 | 8.855 | 8.909 | 17.764 | 17.764 | 0.35577 | 0.49848 | 13.4506 | 13.4506 | 4.1541 | 96.0584 | 0.14003 | 5.572 | 8.409 | 18.9711 | 296.4691 | 531 | 572.2851 | -7.775 | 93.601 | 434.3771 | 95.6326 | 109.402 | 101.285 | 18.229 | 4.398 | 4.511 | 8.909 | 8.909 | 0.358 | 0.49366 | 13.361 | 13.361 | 7.4478 | 79.6667 | 0.16771 | 5.572 | 8.409 | 30.3025 | 531 | 931.84 | 1019.1551 | -9.3702 | 89.7789 | 775.0775 | 96.0904 | 101.285 | 54.217 | 18.229 | 1.137 | 3.374 | 4.511 | 4.511 | 0.15776 | 0.25205 | 10.1067 | 10.1067 | 9.6492 | 49.8728 | 0.20265 | 8.409 | 8.409 | 106.056 | 931.84 | 1523.178 | 1210.1199 | 20.553 | 64.227 | 1070.98 | 90.0973
[11 empty] | 1998-07-24 | 19:00 | 1474 | 29 | 127.796 | 53.91 | 18.16 | 0 | 14.328 | 3.432 |  | 17.76 | 17.76 | 0.80676 | 0 | 13.0255 | 13.0255 | 8.0441 | 64.6489 | 0.20148 | 7.732 | 5.676 | 35.6965 | 294 | 296.2406 | 1469.6316 | 1383.9669 | 5.829 | 87.9502 | 840.1038 | 95.7509 | 127.796 | 109.927 | 18.16 | 8.793 | 8.967 | 17.76 | 17.76 | 0.35649 | 0.4951 | 13.3565 | 13.3565 | 4.1407 | 96.5608 | 0.13832 | 5.676 | 7.232 | 18.3998 | 296.2406 | 525.6 | 568.6901 | -8.1983 | 93.7889 | 432.4654 | 95.7454 | 109.927 | 101.361 | 18.16 | 4.399 | 4.568 | 8.967 | 8.967 | 0.36106 | 0.49058 | 13.3641 | 13.3641 | 7.3215 | 80.1625 | 0.16671 | 5.676 | 7.232 | 31.4065 | 525.6 | 951.04 | 1001.5101 | -5.3068 | 89.3983 | 763.555 | 95.8868 | 101.361 | 53.91 | 18.16 | 1.136 | 3.432 | 4.568 | 4.568 | 0.16006 | 0.24869 | 10.0978 | 10.0978 | 9.873 | 49.6025 | 0.20357 | 7.232 | 7.232 | 103.9392 | 951.04 | 1469.6316 | 1231.4323 | 16.2081 | 64.9139 | 1091.2362 | 90.4751
[11 empty] | 1998-07-25 | 3:00 | 1482.0003 | 29 | 127.595 | 54.157 | 18.082 | 0 | 14.265 | 3.736 |  | 18.001 | 18.001 | 0.79246 | 0 | 12.9682 | 12.9682 | 7.5897 | 65.2043 | 0.19889 | 7.754 | 5.626 | 35.626 | 294.672 | 296.5181 | 1474.6968 | 1292.6705 | 12.3433 | 87.9852 | 794.5943 | 95.5165 | 127.595 | 109.702 | 18.082 | 8.729 | 9.272 | 18.001 | 18.001 | 0.36377 | 0.48492 | 13.2592 | 13.2592 | 4.0903 | 96.4762 | 0.13744 | 5.626 | 7.218 | 18.3998 | 296.5181 | 525.15 | 558.3488 | -6.3218 | 93.7947 | 427.4334 | 95.6953 | 109.702 | 101.51 | 18.082 | 4.399 | 4.873 | 9.272 | 9.272 | 0.37734 | 0.47444 | 13.3641 | 13.3641 | 7.1662 | 80.3578 | 0.16631 | 5.626 | 7.218 | 31.395 | 525.15 | 949.76 | 970.8771 | -2.2234 | 89.4121 | 748.0136 | 95.8029 | 101.51 | 54.157 | 18.082 | 1.137 | 3.736 | 4.873 | 4.873 | 0.17224 | 0.23333 | 10.1067 | 10.1067 | 9.7484 | 50.0031 | 0.20212 | 7.218 | 7.218 | 103.6656 | 949.76 | 1474.6968 | 1207.2571 | 18.1352 | 65.039 | 1078.5086 | 90.3881
[11 empty] | 1998-07-25 | 11:00 | 1490 | 29 | 127.287 | 53.977 | 18.108 | 0 | 14.394 | 3.303 |  | 17.697 | 17.697 | 0.81336 | 0 | 13.0855 | 13.0855 | 8.2816 | 64.2424 | 0.20369 | 7.842 | 5.636 | 35.814 | 292.512 | 296.3304 | 1465.6518 | 1431.6235 | 2.3217 | 87.9142 | 863.9769 | 95.8548 | 127.287 | 109.297 | 18.108 | 8.797 | 8.9 | 17.697 | 17.697 | 0.35476 | 0.49709 | 13.3625 | 13.3625 | 4.1546 | 96.0294 | 0.13915 | 5.636 | 7.215 | 18.2816 | 296.3304 | 527.4 | 571.1613 | -8.2976 | 93.8307 | 433.7459 | 95.7852 | 109.297 | 101.285 | 18.108 | 4.399 | 4.501 | 8.9 | 8.9 | 0.35749 | 0.49427 | 13.3641 | 13.3641 | 7.3847 | 79.7983 | 0.16747 | 5.636 | 7.215 | 31.3375 | 527.4 | 954.24 | 1012.2209 | -6.0761 | 89.4248 | 769.8105 | 95.9292 | 101.285 | 53.977 | 18.108 | 1.198 | 3.303 | 4.501 | 4.501 | 0.15614 | 0.26616 | 10.6489 | 10.6489 | 10.0529 | 49.4701 | 0.21526 | 7.215 | 7.215 | 103.2768 | 954.24 | 1465.6518 | 1262.8848 | 13.8346 | 65.1481 | 1108.5624 | 90.6837
[11 empty] | 1998-07-25 | 19:00 | 1498 | 29 | 127.715 | 54.022 | 18.087 | 0 | 14.449 | 3.374 |  | 17.823 | 17.823 | 0.81069 | 0 | 13.1355 | 13.1355 | 8.1889 | 64.5926 | 0.20336 | 7.824 | 5.631 | 35.72 | 293.952 | 296.412 | 1469.9934 | 1412.8135 | 3.8898 | 87.9492 | 854.6128 | 95.8203 | 127.715 | 109.725 | 18.087 | 8.792 | 9.031 | 17.823 | 17.823 | 0.35818 | 0.4933 | 13.3549 | 13.3549 | 4.1372 | 96.4958 | 0.1384 | 5.631 | 7.222 | 18.1437 | 296.412 | 525.6 | 567.3161 | -7.9369 | 93.8789 | 431.864 | 95.7987 | 109.725 | 101.411 | 18.087 | 4.4 | 4.631 | 9.031 | 9.031 | 0.36445 | 0.48721 | 13.3671 | 13.3671 | 7.2896 | 80.1914 | 0.16669 | 5.631 | 7.222 | 31.4123 | 525.6 | 951.04 | 995.1371 | -4.6367 | 89.4025 | 760.3685 | 95.8688 | 101.411 | 54.022 | 18.087 | 1.257 | 3.374 | 4.631 | 4.631 | 0.16016 | 0.27143 | 11.1733 | 11.1733 | 10.0578 | 49.5717 | 0.2254 | 7.222 | 7.222 | 103.1904 | 951.04 | 1469.9934 | 1266.9105 | 13.8152 | 65.1868 | 1108.9752 | 90.695
[11 empty] | 1998-07-26 | 3:00 | 1506.0003 | 29 | 127.608 | 54.097 | 18.073 | 0 | 14.383 | 3.612 |  | 17.995 | 17.995 | 0.79928 | 0 | 13.0755 | 13.0755 | 7.8033 | 64.9762 | 0.20123 | 7.752 | 5.625 | 35.626 | 294.72 | 296.5181 | 1475.0586 | 1335.3915 | 9.4686 | 87.9852 | 815.9548 | 95.6338 | 127.608 | 109.8 | 18.073 | 8.726 | 9.269 | 17.995 | 17.995 | 0.36365 | 0.48491 | 13.2547 | 13.2547 | 4.0952 | 96.5358 | 0.1373 | 5.625 | 7.22 | 18.0649 | 296.5181 | 529.2 | 558.6588 | -5.5667 | 93.9077 | 427.5884 | 95.7752 | 109.8 | 101.591 | 18.073 | 4.399 | 4.87 | 9.269 | 9.269 | 0.37718 | 0.47459 | 13.3641 | 13.3641 | 7.2263 | 80.3962 | 0.16623 | 5.625 | 7.22 | 31.4007 | 529.2 | 937.6 | 978.8548 | -4.4 | 89.4102 | 754.0274 | 95.8356 | 101.591 | 54.097 | 18.073 | 1.258 | 3.612 | 4.87 | 4.87 | 0.1697 | 0.25832 | 11.1822 | 11.1822 | 9.7975 | 49.9735 | 0.22376 | 7.22 | 7.22 | 103.1616 | 937.6 | 1475.0586 | 1228.2211 | 16.7341 | 65.209 | 1082.9106 | 90.4737
[11 empty] | 1998-07-26 | 11:00 | 1514 | 29 | 127.407 | 53.82 | 18.093 | 0 | 14.331 | 3.492 |  | 17.823 | 17.823 | 0.80407 | 0 | 13.0282 | 13.0282 | 7.9569 | 64.5636 | 0.20179 | 7.722 | 5.615 | 35.673 | 293.856 | 296.3875 | 1469.9934 | 1366.3474 | 7.0508 | 87.9641 | 831.3674 | 95.7091 | 127.407 | 109.447 | 18.093 | 8.732 | 9.091 | 17.823 | 17.823 | 0.35898 | 0.48993 | 13.2638 | 13.2638 | 4.1193 | 96.2147 | 0.13786 | 5.615 | 7.16 | 18.1043 | 296.3875 | 525.6 | 563.6814 | -7.2453 | 93.8917 | 430.0345 | 95.79 | 109.447 | 101.244 | 18.093 | 4.343 | 4.748 | 9.091 | 9.091 | 0.36917 | 0.47773 | 13.1939 | 13.1939 | 7.2021 | 80.0504 | 0.16482 | 5.615 | 7.16 | 31.4065 | 525.6 | 950.4 | 977.6393 | -2.8661 | 89.4036 | 751.6196 | 95.8215 | 101.244 | 53.82 | 18.093 | 1.256 | 3.492 | 4.748 | 4.748 | 0.16486 | 0.26453 | 11.1644 | 11.1644 | 10.0018 | 49.4372 | 0.22583 | 7.16 | 7.16 | 102.672 | 950.4 | 1469.9934 | 1255.3102 | 14.6044 | 65.3589 | 1102.8551 | 90.6903
[11 empty] | 1998-07-26 | 19:00 | 1522 | 29 | 127.615 | 53.962 | 18.118 | 0 | 14.152 | 3.669 |  | 17.821 | 17.821 | 0.79412 | 0 | 12.8655 | 12.8655 | 7.6403 | 65.0302 | 0.19784 | 7.772 | 5.602 | 35.6495 | 293.904 | 296.5344 | 1469.6316 | 1302.8149 | 11.3509 | 87.978 | 799.6746 | 95.542 | 127.615 | 109.665 | 18.118 | 8.731 | 9.09 | 17.821 | 17.821 | 0.35894 | 0.48993 | 13.2623 | 13.2623 | 4.1218 | 96.4002 | 0.13758 | 5.602 | 7.183 | 18.0846 | 296.5344 | 525.6 | 563.9871 | -7.3035 | 93.9013 | 430.2608 | 95.7968 | 109.665 | 101.478 | 18.118 | 4.341 | 4.749 | 9.09 | 9.09 | 0.36917 | 0.47756 | 13.1878 | 13.1878 | 7.2007 | 80.2528 | 0.16433 | 5.602 | 7.183 | 31.4007 | 525.6 | 951.04 | 977.3412 | -2.7655 | 89.4108 | 751.4706 | 95.8214 | 101.478 | 53.962 | 18.118 | 1.08 | 3.669 | 4.749 | 4.749 | 0.16842 | 0.22742 | 9.6 | 9.6 | 9.7323 | 49.8697 | 0.1925 | 7.183 | 7.183 | 102.672 | 951.04 | 1469.6316 | 1200.764 | 18.2949 | 65.376 | 1075.902 | 90.4571
[11 empty] | 1998-07-27 | 3:00 | 1530 | 29 | 127.702 | 54.09 | 18.114 | 0 | 14.268 | 3.321 |  | 17.589 | 17.589 | 0.81119 | 0 | 12.9709 | 12.9709 | 8.2176 | 64.5644 | 0.2009 | 7.785 | 5.611 | 35.626 | 294.624 | 296.6568 | 1481.571 | 1418.1225 | 4.2825 | 87.9908 | 857.3896 | 95.8448 | 127.702 | 109.807 | 18.114 | 8.79 | 8.799 | 17.589 | 17.589 | 0.35197 | 0.49974 | 13.3519 | 13.3519 | 4.173 | 96.4675 | 0.13841 | 5.611 | 7.157 | 18.3604 | 296.6568 | 525.15 | 574.6685 | -9.4294 | 93.8109 | 435.6627 | 95.7856 | 109.807 | 101.501 | 18.114 | 4.342 | 4.457 | 8.799 | 8.799 | 0.35362 | 0.49347 | 13.1909 | 13.1909 | 7.341 | 80.199 | 0.16448 | 5.611 | 7.157 | 31.5042 | 525.15 | 938.24 | 1006.0586 | -7.2283 | 89.3802 | 765.6043 | 95.885 | 101.501 | 54.09 | 18.114 | 1.136 | 3.321 | 4.457 | 4.457 | 0.15562 | 0.25488 | 10.0978 | 10.0978 | 9.7822 | 49.8993 | 0.20236 | 7.157 | 7.157 | 102.888 | 938.24 | 1481.571 | 1223.9852 | 17.386 | 65.3175 | 1081.1126 | 90.4831
[11 empty] | 1998-07-27 | 11:00 | 1538 | 29 | 127.421 | 53.722 | 18.088 | 0 | 14.266 | 3.434 |  | 17.7 | 17.7 | 0.80599 | 0 | 12.9691 | 12.9691 | 8.02 | 64.4635 | 0.20119 | 7.769 | 5.603 | 35.7905 | 293.28 | 296.4202 | 1465.29 | 1379.1641 | 5.8777 | 87.9258 | 837.7921 | 95.728 | 127.421 | 109.47 | 18.088 | 8.731 | 8.969 | 17.7 | 17.7 | 0.35572 | 0.49328 | 13.2623 | 13.2623 | 4.1355 | 96.222 | 0.13783 | 5.603 | 7.175 | 18.2619 | 296.4202 | 527.4 | 567.1973 | -7.5459 | 93.8392 | 431.8087 | 95.7708 | 109.47 | 101.195 | 18.088 | 4.399 | 4.57 | 8.969 | 8.969 | 0.36117 | 0.49047 | 13.3641 | 13.3641 | 7.3483 | 79.8962 | 0.16727 | 5.603 | 7.175 | 31.326 | 527.4 | 954.88 | 1004.9119 | -5.2396 | 89.4319 | 766.156 | 95.9113 | 101.195 | 53.722 | 18.088 | 1.136 | 3.434 | 4.57 | 4.57 | 0.16014 | 0.24858 | 10.0978 | 10.0978 | 9.9339 | 49.4366 | 0.20426 | 7.175 | 7.175 | 102.4848 | 954.88 | 1465.29 | 1236.8605 | 15.5894 | 65.4258 | 1095.8702 | 90.6481
[11 empty] | 1998-07-27 | 19:00 | 1546 | 29 | 127.876 | 53.842 | 18.214 | 0 | 14.328 | 3.436 |  | 17.764 | 17.764 | 0.80658 | 0 | 13.0255 | 13.0255 | 8.048 | 64.597 | 0.20164 | 7.745 | 5.627 | 35.673 | 293.904 | 296.5507 | 1470.3552 | 1384.4017 | 5.8458 | 87.9707 | 840.4762 | 95.7556 | 127.876 | 109.59 | 18.214 | 8.73 | 9.034 | 17.764 | 17.764 | 0.35744 | 0.49144 | 13.2608 | 13.2608 | 4.1293 | 96.3897 | 0.13757 | 5.627 | 7.171 | 18.1437 | 296.5507 | 526.05 | 565.5892 | -7.5162 | 93.8818 | 431.0699 | 95.791 | 109.59 | 101.649 | 18.214 | 4.399 | 4.635 | 9.034 | 9.034 | 0.36464 | 0.48694 | 13.3641 | 13.3641 | 7.2936 | 80.1119 | 0.16682 | 5.627 | 7.171 | 31.4123 | 526.05 | 951.68 | 995.5023 | -4.6047 | 89.4075 | 760.7762 | 95.871 | 101.649 | 53.842 | 18.214 | 1.199 | 3.436 | 4.635 | 4.635 | 0.16148 | 0.25868 | 10.6578 | 10.6578 | 9.9714 | 49.5601 | 0.21505 | 7.171 | 7.171 | 102.672 | 951.68 | 1470.3552 | 1247.9433 | 15.1264 | 65.3779 | 1099.8116 | 90.6646
[11 empty] | 1998-07-28 | 3:00 | 1554 | 29 | 127.91 | 54.187 | 18.112 | 0 | 14.328 | 3.375 |  | 17.703 | 17.703 | 0.80935 | 0 | 13.0255 | 13.0255 | 8.1514 | 64.7851 | 0.20106 | 7.702 | 5.6 | 35.626 | 294.576 | 296.665 | 1474.6968 | 1404.8624 | 4.7355 | 87.9912 | 850.7637 | 95.8125 | 127.91 | 110.092 | 18.112 | 8.792 | 8.911 | 17.703 | 17.703 | 0.35498 | 0.49664 | 13.3549 | 13.3549 | 4.1557 | 96.7333 | 0.13806 | 5.6 | 7.129 | 18.3801 | 296.665 | 528.75 | 571.2335 | -8.0347 | 93.8044 | 433.9492 | 95.7645 | 110.092 | 101.685 | 18.112 | 4.4 | 4.511 | 8.911 | 8.911 | 0.35805 | 0.49377 | 13.3671 | 13.3671 | 7.3976 | 80.3789 | 0.1663 | 5.6 | 7.129 | 31.4985 | 528.75 | 938.24 | 1013.7659 | -8.0497 | 89.3825 | 771.2579 | 95.916 | 101.685 | 54.187 | 18.112 | 1.136 | 3.375 | 4.511 | 4.511 | 0.15778 | 0.25183 | 10.0978 | 10.0978 | 9.7654 | 50.0586 | 0.20172 | 7.129 | 7.129 | 102.3696 | 938.24 | 1474.6968 | 1219.5878 | 17.2991 | 65.4932 | 1078.9139 | 90.5118
[11 empty] | 1998-07-28 | 11:00 | 1562.0003 | 29 | 127.903 | 54.082 | 18.126 | 0 | 14.27 | 3.491 |  | 17.761 | 17.761 | 0.80345 | 0 | 12.9727 | 12.9727 | 7.9417 | 64.9248 | 0.19981 | 7.714 | 5.583 | 37.882 | 306.96 | 298.7947 | 1541.6298 | 1365.3156 | 11.4369 | 87.3217 | 832.0552 | 95.4472 | 127.903 | 109.86 | 18.126 | 8.733 | 9.028 | 17.761 | 17.761 | 0.35732 | 0.4917 | 13.2653 | 13.2653 | 4.1522 | 96.6033 | 0.13732 | 5.583 | 7.089 | 18.9317 | 298.7947 | 555.3 | 569.5129 | -2.5595 | 93.664 | 434.1538 | 95.6394 | 109.86 | 101.586 | 18.126 | 4.399 | 4.629 | 9.028 | 9.028 | 0.36432 | 0.48726 | 13.3641 | 13.3641 | 7.7053 | 79.8917 | 0.16728 | 5.583 | 7.089 | 32.9648 | 555.3 | 999.68 | 1051.6821 | -5.2019 | 88.9674 | 803.4911 | 95.8973 | 101.586 | 54.082 | 18.126 | 1.138 | 3.491 | 4.629 | 4.629 | 0.16246 | 0.24584 | 10.1156 | 10.1156 | 10.3425 | 49.3655 | 0.20491 | 7.089 | 7.089 | 110.376 | 999.68 | 1541.6298 | 1289.5763 | 16.3498 | 63.0596 | 1144.6281 | 90.357
[11 empty] | 1998-07-28 | 19:00 | 1570 | 29 | 128.325 | 54.36 | 18.103 | 0 | 14.269 | 3.494 |  | 17.763 | 17.763 | 0.8033 | 0 | 12.9718 | 12.9718 | 7.9421 | 65.2974 | 0.19866 | 7.95 | 5.566 | 37.788 | 308.4 | 298.8763 | 1552.4838 | 1365.124 | 12.0684 | 87.3566 | 832.0001 | 95.4582 | 128.325 | 110.332 | 18.103 | 8.791 | 8.972 | 17.763 | 17.763 | 0.3566 | 0.49491 | 13.3534 | 13.3534 | 4.1724 | 97.0531 | 0.13759 | 5.566 | 7.097 | 18.8332 | 298.8763 | 553.95 | 573.2699 | -3.4877 | 93.6987 | 436.0731 | 95.6812 | 110.332 | 101.82 | 18.103 | 4.341 | 4.631 | 8.972 | 8.972 | 0.36288 | 0.48384 | 13.1878 | 13.1878 | 7.6506 | 80.3224 | 0.16419 | 5.566 | 7.097 | 33.0395 | 553.95 | 997.12 | 1042.2403 | -4.5251 | 88.9454 | 798.0952 | 95.8602 | 101.82 | 54.36 | 18.103 | 1.137 | 3.494 | 4.631 | 4.631 | 0.16256 | 0.24552 | 10.1067 | 10.1067 | 10.3081 | 49.6789 | 0.20344 | 7.097 | 7.097 | 110.5632 | 997.12 | 1552.4838 | 1285.6189 | 17.1895 | 63.007 | 1141.3694 | 90.3131
[11 empty] | 1998-07-29 | 5:04 | 1580.0722 | 29 | 123.173 | 55.492 | 18.234 | 0 | 14.323 | 3.015 |  | 17.338 | 17.338 | 0.8261 | 0 | 13.0209 | 13.0209 | 8.7357 | 62.3628 | 0.20879 | 8.185 | 5.454 | 40.5845 | 308.256 | 299.3986 | 1518.4746 | 1528.9156 | -0.6876 | 86.4447 | 914.1571 | 95.5604 | 123.173 | 105.907 | 18.234 | 8.965 | 8.373 | 17.338 | 17.338 | 0.34294 | 0.51707 | 13.6177 | 13.6177 | 4.2835 | 92.0225 | 0.14798 | 5.454 | 7.433 | 20.4092 | 299.3986 | 553.05 | 598.1134 | -8.1482 | 93.1833 | 448.756 | 95.452 | 105.907 | 99.764 | 18.234 | 4.222 | 4.151 | 8.373 | 8.373 | 0.33409 | 0.50424 | 12.8263 | 12.8263 | 7.8311 | 76.7704 | 0.16707 | 5.454 | 7.433 | 33.9365 | 553.05 | 1108.48 | 1081.0426 | 2.4752 | 88.6651 | 817.0463 | 95.8464 | 99.764 | 55.492 | 18.234 | 1.136 | 3.015 | 4.151 | 4.151 | 0.14337 | 0.27367 | 10.0978 | 10.0978 | 11.566 | 47.828 | 0.21113 | 7.433 | 7.433 | 135.2304 | 1108.48 | 1518.4746 | 1475.1837 | 2.8509 | 54.8326 | 1291.8318 | 89.5319
[11 empty] | 1998-07-30 | 18:54 | 1617.9036 | 29 | 124.231 | 56.01 | 18.136 | 0 | 14.389 | 2.84 |  | 17.229 | 17.229 | 0.83516 | 0 | 13.0809 | 13.0809 | 9.1723 | 62.8122 | 0.20825 | 7.823 | 5.529 | 39.4095 | 307.536 | 299.0069 | 1558.6344 | 1614.2698 | -3.5695 | 86.8199 | 956.6383 | 95.8804 | 124.231 | 106.867 | 18.136 | 9.031 | 8.198 | 17.229 | 17.229 | 0.33915 | 0.52417 | 13.718 | 13.718 | 4.3349 | 93.0781 | 0.14738 | 5.529 | 7.033 | 19.4833 | 299.0069 | 553.5 | 606.9329 | -9.6536 | 93.484 | 452.9699 | 95.6988 | 106.867 | 100.29 | 18.136 | 4.222 | 3.976 | 8.198 | 8.198 | 0.32476 | 0.515 | 12.8263 | 12.8263 | 7.9585 | 77.484 | 0.16554 | 5.529 | 7.033 | 33.6547 | 553.5 | 1030.4 | 1105.5087 | -7.2893 | 88.7445 | 829.5044 | 95.9428 | 100.29 | 56.01 | 18.136 | 1.136 | 2.84 | 3.976 | 3.976 | 0.13637 | 0.28571 | 10.0978 | 10.0978 | 10.9772 | 49.0368 | 0.20592 | 7.033 | 7.033 | 115.632 | 1030.4 | 1558.6344 | 1396.3072 | 10.4147 | 61.328 | 1213.3536 | 90.47
[11 empty] | 1998-07-31 | 2:00 | 1625 | 29 | 124.385 | 55.845 | 18.258 | 0 | 14.508 | 2.781 |  | 17.289 | 17.289 | 0.83915 | 0 | 13.1891 | 13.1891 | 9.375 | 62.482 | 0.21109 | 7.429 | 5.535 | 36.848 | 294.672 | 296.6568 | 1481.2092 | 1652.0347 | -11.5328 | 87.5789 | 974.3458 | 96.2182 | 124.385 | 106.95 | 18.258 | 9.03 | 8.259 | 17.289 | 17.289 | 0.34076 | 0.5223 | 13.7165 | 13.7165 | 4.2989 | 93.1106 | 0.14731 | 5.535 | 7.055 | 18.715 | 296.6568 | 529.2 | 600.5452 | -13.4817 | 93.6914 | 448.601 | 95.8281 | 106.95 | 100.205 | 18.258 | 4.28 | 3.979 | 8.259 | 8.259 | 0.32647 | 0.51822 | 13.0025 | 13.0025 | 7.6459 | 77.6736 | 0.1674 | 5.535 | 7.055 | 32.0102 | 529.2 | 972.16 | 1064.0007 | -9.4471 | 89.2097 | 796.6004 | 95.9816 | 100.205 | 55.845 | 18.258 | 1.198 | 2.781 | 3.979 | 3.979 | 0.13525 | 0.30108 | 10.6489 | 10.6489 | 10.5341 | 49.2329 | 0.2163 | 7.055 | 7.055 | 105.4368 | 972.16 | 1481.2092 | 1345.5273 | 9.1602 | 64.4583 | 1158.8436 | 90.9016
[11 empty] | 1998-07-31 | 10:00 | 1633.0003 | 29 | 124.004 | 55.867 | 18.168 | 0 | 14.337 | 2.889 |  | 17.226 | 17.226 | 0.83229 | 0 | 13.0336 | 13.0336 | 9.0264 | 62.7411 | 0.20774 | 7.736 | 5.548 | 39.48 | 306.816 | 298.7621 | 1553.931 | 1585.4797 | -2.0303 | 86.7855 | 942.1209 | 95.8095 | 124.004 | 106.792 | 18.168 | 8.977 | 8.249 | 17.226 | 17.226 | 0.33979 | 0.52113 | 13.6359 | 13.6359 | 4.3112 | 92.9188 | 0.14675 | 5.548 | 7.024 | 19.5621 | 298.7621 | 554.85 | 602.6023 | -8.6063 | 93.4523 | 450.6822 | 95.6594 | 106.792 | 100.218 | 18.168 | 4.223 | 4.026 | 8.249 | 8.249 | 0.32745 | 0.51194 | 12.8294 | 12.8294 | 7.9461 | 77.3909 | 0.16577 | 5.548 | 7.024 | 33.6088 | 554.85 | 1033.6 | 1101.5966 | -6.5786 | 88.7507 | 828.2233 | 95.9421 | 100.218 | 55.867 | 18.168 | 1.137 | 2.889 | 4.026 | 4.026 | 0.13835 | 0.28241 | 10.1067 | 10.1067 | 11.0007 | 48.8738 | 0.20679 | 7.024 | 7.024 | 114.408 | 1033.6 | 1553.931 | 1395.3588 | 10.2046 | 61.706 | 1214.4794 | 90.5797
[11 empty] | 1998-07-31 | 18:00 | 1641 | 29 | 128.881 | 58.972 | 18.219 | 0 | 14.327 | 2.78 |  | 17.107 | 17.107 | 0.83749 | 0 | 13.0245 | 13.0245 | 9.3804 | 66.3271 | 0.19637 | 8.092 | 5.491 | 36.8715 | 308.16 | 299.1293 | 1519.56 | 1650.7002 | -8.6301 | 87.6737 | 974.9148 | 96.218 | 128.881 | 111.93 | 18.219 | 8.907 | 8.2 | 17.107 | 17.107 | 0.33755 | 0.52066 | 13.5296 | 13.5296 | 4.3216 | 97.8649 | 0.13825 | 5.491 | 6.956 | 19.0696 | 299.1293 | 545.4 | 603.3356 | -10.6226 | 93.625 | 451.2324 | 95.7739 | 111.93 | 103.017 | 18.219 | 4.222 | 3.978 | 8.2 | 8.2 | 0.32486 | 0.51488 | 12.8263 | 12.8263 | 7.8439 | 81.4106 | 0.15755 | 5.491 | 6.956 | 32.9532 | 545.4 | 983.68 | 1089.2789 | -10.7351 | 88.9836 | 817.3394 | 95.9682 | 103.017 | 58.972 | 18.219 | 1.198 | 2.78 | 3.978 | 3.978 | 0.13521 | 0.30116 | 10.6489 | 10.6489 | 10.6779 | 52.0976 | 0.2044 | 6.956 | 6.956 | 105.1776 | 983.68 | 1519.56 | 1362.2577 | 10.3518 | 64.8387 | 1172.9688 | 91.0332
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A2: SDS chlorinations were conducted by Pompano Beach.
Note on S8: Reviewer DJ: Changed "Start" to "0.00"
Note on T8: The water source is groundwater
Note on U85: Erroneous data point. No reason for error found
Note on V86: Erroneous data point.
Note on V146: Erroneous data point
Note on V147: Erroneous data point
Note on Z21: Questionable Data Point. Changed to NR
Note on Z22: Questionable Data Point. Changed to NR
Note on AA8: No cleaning events took place during this time
Note on AL44: Erroneous data point. Was 4.17
Note on AM22: Erroneous data point.
Note on DS22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on DS33: C Rice: Lab verified CHCl3 and BDCM data but provided no explanation for the results.
Note on DS37: C Rice: Lab verified THM data for the entire quarter but provided no explanation of the results.
Note on DS39: C. Rice: Lab verified DCAA and TCAA data but provided no explanation for the results.
Note on DU18: Total hardness value questionable. Not reported.
Note on DU33: Reported value was 21.53 ug/L. Due to the low TOC in permeate, this value was questionable. Changed to NR. No reason is available for the fluctuations in the CHCHl3 concentrations.
Note on DU39: Lab Verified Possible sampling error.
Note on DV18: Total hardness value questionable. Not reported.
Note on DV22: During the initial sampling, problems with TOC measurement were encountered. The TOC analyzer was recalibrated and new standards were prepared in later testing. This value falls within the expected range so it was reported.
Note on DV27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on DV33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on DV40: TSC_ADM: Reviewer changed from 170 µg/L to NR due to low feed dose
Note on DV41: TSC_ADM: Reviewer changed from 0 µg/L to NR due to low feed dose
Note on DV42: TSC_ADM: Reviewer changed from 0 µg/L to NR due to low feed dose
Note on DV43: TSC_ADM: Reviewer changed from 43.1 µg/L to NR due to low feed dose
Note on DW18: Total hardness value questionable. Not reported.
Note on ED21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on ED43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on ED65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EM22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EM33: C Rice: Lab verified CHCl3 and BDCM data but provided no explanation for the results.
Note on EM37: C Rice: Lab verified THM data for the entire quarter but provided no explanation of the results.
Note on EM39: C. Rice: Lab verified DCAA and TCAA data but provided no explanation for the results.
Note on EO18: Total hardness value questionable. Not reported.
Note on EO33: Lab Verified. No resom is available for fluctuation in CHCL3 production. Possible sampling eror. However, due to the reasonable TOC concentration, this CHCL3 value was reported.
Note on EO39: Lab Verified Possible sampling or analytical error
Note on EP18: Total hardness value questionable. Not reported.
Note on EP22: During the pilot study, problems with TOC measurement were encountered. This value falls within the expected range of influent TOC.
Note on EP26: The SDS chlorinations were performed by Pompano Beach.
Note on EP27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on EP33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on EQ18: Total hardness value questionable. Not reported.
Note on EX21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EX43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EX65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FG22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FG33: C Rice: Lab verified CHCl3 and BDCM data but provided no explanation for the results.
Note on FG37: C Rice: Lab verified THM data for the entire quarter but provided no explanation of the results.
Note on FI18: Total hardness value questionable. Not reported.
Note on FI22: Lab Verified
Note on FI33: Reported as 33.59. Given the low TOC concentrations, the value was changed to NR
Note on FJ18: Total hardness value questionable. Not reported.
Note on FJ22: During the initial sampling, problems with TOC measurement were encountered. The TOC analyzer was recalibrated and new standards were prepared in later testing. This value was reported because it falls within the range of expected TOC values.
Note on FJ27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on FJ33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on FK18: Total hardness value questionable. Not reported.
Note on FR21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FR43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FR65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GA22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GA33: C Rice: Lab verified CHCl3 and BDCM data but provided no explanation for the results.
Note on GA37: C Rice: Lab verified THM data for the entire quarter but provided no explanation of the results.
Note on GC11: Reviewer DJ: Changed date from 7/7/98 to 7/22/98
Note on GC18: Total hardness value questionable. Not reported.
Note on GC33: Reported as 33.54, however, given the low TOC value, concentration is questionable. Changed to NR
Note on GC34: Lab Verified
Note on GC37: Lab Verified
Note on GC40: Value of concentration found to be 58.9. Because this value is questionable, it is being reported as NR
Note on GD11: Reviewer DJ: Changed date from 7/7/98 to 7/22/98
Note on GD18: Total hardness value questionable. Not reported.
Note on GD22: During the initial sampling, problems with TOC measurement were encountered. The TOC analyzer was recalibrated and new standards were prepared in later testing.
Note on GD27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on GD33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GE11: Reviewer DJ: Changed date from 7/7/98 to 7/22/98
Note on GE18: Total hardness value questionable. Not reported.
Note on GL21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GL43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GL65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GU22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GU33: C Rice: Lab verified CHCl3 and BDCM data but provided no explanation for the results.
Note on GU37: C Rice: Lab verified THM data for the entire quarter but provided no explanation of the results.
Note on GW18: Total hardness value questionable. Not reported.
Note on GW33: Value reported as 32.00. Given the low TOC value, it is unlikely that a high concentration would be reached. Changed to NR
Note on GW37: Lab Verified
Note on GX18: Total hardness value questionable. Not reported.
Note on GX22: During the initial sampling, problems with TOC measurement were encountered. The TOC analyzer was recalibrated and new standards were prepared in later testing.
Note on GX27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on GX33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GY18: Total hardness value questionable. Not reported.
Note on HF21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HF43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HF65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HH60: TSC_ADM: Reviewer switched reported influent and permeate concentrations because they were obviously incorrect
Note on HH62: TSC_ADM: Reviewer switched reported influent and permeate concentrations because they were obviously incorrect
Note on HH63: TSC_ADM: Reviewer switched reported influent and permeate concentrations because they were obviously incorrect
Note on HI60: TSC_ADM: Reviewer switched reported influent and permeate concentrations because they were obviously incorrect
Note on HI62: TSC_ADM: Reviewer switched reported influent and permeate concentrations because they were obviously incorrect
Note on HI63: TSC_ADM: Reviewer switched reported influent and permeate concentrations because they were obviously incorrect
Note on HO3: Reviewer DJ: "Week 10" changed to "Week 8."
Note on HO22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HO33: C Rice: Lab verified CHCl3 and BDCM data but provided no explanation for the results.
Note on HO37: C Rice: Lab verified THM data for the entire quarter but provided no explanation of the results.
Note on HQ11: Reviewer DJ: Changed date from 7/22/98 to 7/7/98
Note on HQ18: Total hardness value questionable. Not reported.
Note on HQ25: Reviewer DJ: Changed 0.0 to BMRL
Note on HQ37: Lab Verified No reason available for fluctuations in THM values. Possible analytical problem. Given this permeate TOC value, the concentrations were reported.
Note on HR11: Reviewer DJ: Changed date from 7/22/98 to 7/7/98
Note on HR18: Total hardness value questionable. Not reported.
Note on HR22: During the initial sampling, problems with TOC measurement were encountered. The TOC analyzer was recalibrated and new standards were prepared in later testing.
Note on HR25: Reviewer DJ: Changed 0.0 to BMRL
Note on HR27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on HR33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR. Pompano Beach conducted the SDS chlorinations.
Note on HS11: Reviewer DJ: Changed date from 7/22/98 to 7/7/98
Note on HS18: Total hardness value questionable. Not reported.
Note on HZ3: Reviewer DJ: "Week 10" changed to "Week 8."
Note on HZ21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HZ43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HZ65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on IB11: Reviewer DJ: Changed date from 7/22/98 to 7/7/98
Note on IC11: Reviewer DJ: Changed date from 7/22/98 to 7/7/98

## Sheet2. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2a: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Week 12 | [9 empty] | Field 2-7: System And Stage Water Quality For Week 12 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 18 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Pompano Beach | Membrane manufacturer | FLUID SYSTEMS CORP. | Average yearly temperature of feed water, TavgoC (oC) | 29 | Alkalinity (mg/L as CaCO3) | 48 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51775 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.48 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.4771 | [6 empty] | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.49016 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.48198 | [6 empty] | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.49016 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4131618 | Membrane trade name | FLUID SYSTEMS | Temperature normalized MTCW (gfd/psi) | 0.12621 | Calcium Hardness (mg/L as CaCO3) | 250 | Cartridge filtration | 1 micron | Pilot - scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 17.86 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.04 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.28 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.73 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.96 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.79 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.72 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.59 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.96 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.79 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.72 |  |  |  |  | Capital Recovery Interest Rate (%) | 3
Water Industry Data Base Number (optional) |  | Membrane element model number | 2540 TFCS / 4921 TFCS |  |  | LSI | 0.3 | sulfuric acid addition | pH = 5.7, Dosage= 42 mg/L | Pilot - scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 17.86 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.46 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.28 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.78 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.79 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.79 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.59 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.59 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.79 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.79 |  |  |  |  | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.1 |  |  |  | 1998-08-01 | 2:00 | 1649 | 29.189 | 128.225 | 58.515 | 18.204 | 0 | 14.384 | 3.109 |  | 17.493 | 17.493 | 0.82227 | 0 | 13.0764 | 13.0035 | 8.6954 | 66.4706 | 0.19563 | 8.093 | 5.501 | 36.7775 | 308.976 | 299.219 | 1531.1376 | 1513.4227 | 1.157 | 87.7088 | 906.3209 | 95.9421 | 128.225 | 111.187 | 18.204 | 8.905 | 8.201 | 17.106 | 17.106 | 0.084387 | 0.52058 | 13.5266 | 13.4512 | 4.3279 | 97.1741 | 0.13842 | 5.501 | 5.501 | 18.72 | 299.219 | 548.1 | 603.797 | -10.1618 | 93.7437 | 451.508 | 95.8539 | 111.187 | 98.752 | 18.204 | 4.222 | 3.979 | 8.201 | 8.201 | 0.08123 | 0.51482 | 12.8263 | 12.7549 | 7.882 | 78.8835 | 0.16169 | 5.501 | 5.501 | 33.12 | 548.1 | 907.3408 | 1094.5301 | -20.6305 | 88.9312 | 821.3151 | 95.9674 | 98.752 | 58.515 | 18.204 | 1.257 | 3.109 | 4.366 | 4.366 | 0.14955 | 0.28791 | 11.1733 | 11.1111 | 9.6287 | 50.8008 | 0.21872 | 5.501 | 6.901 | 106.3872 | 907.3408 | 1531.1376 | 1231.1744 | 19.5909 | 64.445 | 1069.2576 | 90.0504 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Design system recovery, R (decimal) | 0.8 | Total iron (mg/L) | 0.3 |  |  |  | 1998-08-01 | 10:00 | 1657 | 29.478 | 127.367 | 57.727 | 18.213 | 0 | 14.446 | 3.049 |  | 17.495 | 17.495 | 0.82572 | 0 | 13.1327 | 12.9485 | 8.8001 | 65.5339 | 0.19758 | 7.494 | 5.509 | 35.391 | 293.04 | 296.5997 | 1446.1146 | 1534.1925 | -6.0907 | 88.0678 | 915.3961 | 96.1338 | 127.367 | 110.085 | 18.213 | 8.909 | 8.254 | 17.163 | 17.163 | 0.084754 | 0.51908 | 13.5327 | 13.3428 | 4.2836 | 96.2294 | 0.13866 | 5.509 | 5.509 | 18.3885 | 296.5997 | 518.85 | 596.8884 | -15.0407 | 93.8002 | 446.7441 | 95.8839 | 110.085 | 98.027 | 18.213 | 4.281 | 3.973 | 8.254 | 8.254 | 0.081543 | 0.51866 | 13.0056 | 12.8231 | 7.5002 | 78.3428 | 0.16368 | 5.509 | 5.509 | 31.4295 | 518.85 | 942.08 | 1044.0569 | -10.8247 | 89.4034 | 781.4535 | 95.9781 | 98.027 | 57.727 | 18.213 | 1.256 | 3.049 | 4.305 | 4.305 | 0.14713 | 0.29175 | 11.1644 | 11.0078 | 10.1864 | 49.4776 | 0.22248 | 5.509 | 6.914 | 97.416 | 942.08 | 1446.1146 | 1290.0295 | 10.7934 | 67.1557 | 1116.0547 | 91.2714 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-08-01 | 18:00 | 1665 | 29.482 | 127.119 | 57.787 | 18.192 | 0 | 14.506 | 3.049 |  | 17.555 | 17.555 | 0.82632 | 0 | 13.1873 | 13.0007 | 8.832 | 65.429 | 0.1987 | 8.08 | 5.493 | 35.297 | 293.904 | 296.6894 | 1451.1798 | 1540.2968 | -6.141 | 88.103 | 918.4931 | 96.1571 | 127.119 | 110.077 | 18.192 | 8.97 | 8.257 | 17.227 | 17.227 | 0.084978 | 0.52069 | 13.6253 | 13.4326 | 4.2914 | 96.1146 | 0.13976 | 5.493 | 5.493 | 18.603 | 296.6894 | 518.85 | 598.7889 | -15.4069 | 93.7298 | 447.7392 | 95.8451 | 110.077 | 98.054 | 18.192 | 4.279 | 3.978 | 8.257 | 8.257 | 0.081596 | 0.51823 | 12.9995 | 12.8156 | 7.4942 | 78.3793 | 0.16351 | 5.493 | 5.493 | 31.5272 | 518.85 | 940.16 | 1043.0466 | -10.9435 | 89.3737 | 780.9483 | 95.963 | 98.054 | 57.787 | 18.192 | 1.257 | 3.049 | 4.306 | 4.306 | 0.14715 | 0.29192 | 11.1733 | 11.0153 | 10.1573 | 49.5712 | 0.22221 | 5.493 | 6.945 | 98.0208 | 940.16 | 1451.1798 | 1287.3456 | 11.2897 | 66.9618 | 1113.7528 | 91.1991 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 (dup) | CF-sys-18 (dup) | CC-sys-18 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 (dup) | CI-s1-18 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25
|  | Membrane hydrophobicity | HYDRPHILIC | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | 0 |  |  |  | 1998-08-02 | 0:00 | 1671 | 29.41 | 127.702 | 57.96 | 18.276 | 0 | 14.506 | 3.05 |  | 17.556 | 17.556 | 0.82627 | 0 | 13.1873 | 13.0284 | 8.8427 | 65.7123 | 0.19826 | 8 | 5.498 | 35.156 | 295.392 | 296.9261 | 1461.672 | 1541.9217 | -5.4903 | 88.16 | 919.4239 | 96.1763 | 127.702 | 110.7 | 18.276 | 8.969 | 8.257 | 17.226 | 17.226 | 0.084974 | 0.52067 | 13.6238 | 13.4597 | 4.297 | 96.628 | 0.13929 | 5.498 | 5.498 | 18.4665 | 296.9261 | 520.65 | 599.3972 | -15.1248 | 93.7808 | 448.1616 | 95.8795 | 110.7 | 98.356 | 18.276 | 4.281 | 3.976 | 8.257 | 8.257 | 0.081583 | 0.51847 | 13.0056 | 12.8489 | 7.5219 | 78.7301 | 0.1632 | 5.498 | 5.498 | 31.694 | 520.65 | 936.96 | 1047.1139 | -11.7565 | 89.326 | 783.882 | 95.9568 | 98.356 | 57.96 | 18.276 | 1.256 | 3.05 | 4.306 | 4.306 | 0.14717 | 0.29169 | 11.1644 | 11.03 | 10.1102 | 49.7718 | 0.22161 | 5.498 | 6.929 | 98.568 | 936.96 | 1461.672 | 1282.2126 | 12.2777 | 66.8039 | 1109.5863 | 91.1167 | Sampling date | MM/DD/YY | 1998-08-04 | 1998-08-04 | 1998-08-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-04 | 1998-08-04 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-18 | 1998-08-18 | 1998-08-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-18 | 1998-08-18 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-01 | 1998-09-01 | 1998-09-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-01 | 1998-09-01 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-30 | 1998-09-30 | 1998-09-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-30 | 1998-09-30 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 7
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.1 |  |  |  | 1998-08-02 | 10:00 | 1681 | 29.486 | 135.126 | 27.66 | 18.492 | 0 | 14.577 | 3.986 |  | 18.563 | 18.563 | 0.78527 | 0 | 13.2518 | 13.0628 | 7.4514 | 55.4496 | 0.23558 | 8.026 | 5.682 | 32.8765 | 293.232 | 296.3141 | 1281.8574 | 1259.7184 | 1.7271 | 88.9048 | 778.0162 | 95.7743 | 135.126 | 115.537 | 18.492 | 9.335 | 9.445 | 18.78 | 18.78 | 0.094118 | 0.49707 | 14.1797 | 13.9775 | 4.1626 | 102.6769 | 0.13613 | 5.682 | 5.682 | 17.7255 | 296.3141 | 499.05 | 571.6581 | -14.5493 | 94.018 | 433.9861 | 95.9157 | 115.537 | 98.482 | 18.492 | 4.463 | 4.982 | 9.445 | 9.445 | 0.096215 | 0.47253 | 13.5585 | 13.3651 | 6.8726 | 81.6449 | 0.1637 | 5.682 | 5.682 | 24.3915 | 499.05 | 851.2 | 924.2609 | -8.5833 | 91.7684 | 711.6555 | 96.5726 | 98.482 | 27.66 | 18.492 | 0.779 | 3.986 | 4.765 | 4.765 | 0.17508 | 0.16348 | 6.9244 | 6.8257 | 8.2602 | 36.3188 | 0.18794 | 5.682 | 7.038 | 98.712 | 851.2 | 1281.8574 | 998.2618 | 22.1238 | 66.6867 | 924.7309 | 89.3253 | Sampling time | hh:mm | 13:00 | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | 16:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 3391
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-08-02 | 18:00 | 1689 | 29.452 | 134.804 | 27.66 | 18.421 | 0 | 14.637 | 3.986 |  | 18.623 | 18.623 | 0.78596 | 0 | 13.3064 | 13.1298 | 7.4731 | 55.3379 | 0.23727 | 7.985 | 5.688 | 32.7355 | 293.856 | 296.2406 | 1285.8372 | 1263.8585 | 1.7093 | 88.9497 | 780.0496 | 95.8034 | 134.804 | 115.297 | 18.421 | 9.334 | 9.449 | 18.783 | 18.783 | 0.094141 | 0.49694 | 14.1782 | 13.9901 | 4.1684 | 102.4611 | 0.13654 | 5.688 | 5.688 | 17.2185 | 296.2406 | 497.7 | 571.8669 | -14.9019 | 94.1877 | 434.0538 | 96.0331 | 115.297 | 98.374 | 18.421 | 4.462 | 4.987 | 9.449 | 9.449 | 0.096275 | 0.47222 | 13.5554 | 13.3755 | 6.8497 | 81.5648 | 0.16399 | 5.688 | 5.688 | 24.449 | 497.7 | 837.12 | 921.1301 | -10.0356 | 91.7469 | 709.4151 | 96.5536 | 98.374 | 27.66 | 18.421 | 0.841 | 3.986 | 4.827 | 4.827 | 0.17632 | 0.17423 | 7.4756 | 7.3763 | 8.1642 | 36.4318 | 0.20247 | 5.688 | 7.083 | 98.6112 | 837.12 | 1285.8372 | 992.9368 | 22.779 | 66.7125 | 915.0284 | 89.2232 | Operation time | hh.hh | 1721 | 1721 | 1721 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1721 | 1721 | --- | --- | --- | --- | Operation time | hh.hh | 2070 | 2070 | 2070 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2070 | 2070 | --- | --- | --- | --- | Operation time | hh.hh | 2761 | 2761 | 2761 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2761 | 2761 | --- | --- | --- | --- | Operation time | hh.hh | 2815 | 2815 | 2815 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2815 | 2815 | --- | --- | --- | --- | Operation time | hh.hh | 3095 | 3095 | 3095 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3095 | 3095 | --- | --- | --- | --- | Operation time | hh.hh | 2815 | 2815 | 2815 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2815 | 2815 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 267.13
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 8.9 |  |  |  | 1998-08-03 | 2:00 | 1697.0003 | 29.414 | 135.166 | 27.892 | 18.513 | 0 | 13.851 | 3.986 |  | 17.837 | 17.837 | 0.77653 | 0 | 12.5918 | 12.4387 | 7.2329 | 55.7831 | 0.22298 | 7.97 | 5.673 | 32.289 | 294.576 | 296.5099 | 1290.9024 | 1214.6544 | 5.9066 | 89.1103 | 755.5822 | 95.7266 | 135.166 | 115.89 | 18.513 | 9.387 | 9.397 | 18.784 | 18.784 | 0.093971 | 0.49973 | 14.2587 | 14.0853 | 4.1891 | 102.8259 | 0.13698 | 5.673 | 5.673 | 17.1405 | 296.5099 | 501.3 | 575.582 | -14.8179 | 94.2192 | 436.046 | 96.0691 | 115.89 | 98.581 | 18.513 | 4.462 | 4.935 | 9.397 | 9.397 | 0.095581 | 0.47483 | 13.5554 | 13.3906 | 6.9242 | 81.7983 | 0.1637 | 5.673 | 5.673 | 24.4548 | 501.3 | 835.84 | 932.4415 | -11.5574 | 91.7525 | 716.8708 | 96.5887 | 98.581 | 27.892 | 18.513 | 0.002 | 3.986 | 3.988 | 3.988 | 0.15954 | 0.0005015 | 0.017778 | 0.017562 | 7.3728 | 37.3507 | 0.00047018 | 5.673 | 7.055 | 98.7408 | 835.84 | 1290.9024 | 836.2098 | 35.2228 | 66.699 | 836.0249 | 88.1893 | pH | --- | 5.71 | 5.9 | 6.08 | --- | --- | --- | --- | --- | pH | --- | 5.89 | 5.9 | --- | --- | --- | --- | pH | --- | 6.07 | 6.41 | 6.28 | --- | --- | --- | --- | --- | pH | --- | 5.92 | 6.41 | --- | --- | --- | --- | pH | --- | 5.18 | 5.68 | 6.17 | --- | --- | --- | --- | --- | pH | --- | 5.24 | 5.64 | --- | --- | --- | --- | pH | --- | 5.35 | 5.63 | 6.34 | --- | --- | --- | --- | --- | pH | --- | 5.38 | 5.63 | --- | --- | --- | --- | pH | --- | 5.43 | 5.85 | 5.99 | --- | --- | --- | --- | --- | pH | --- | 5.29 | 5.85 | --- | --- | --- | --- | pH | --- | 5.37 | 5.58 | 6.18 | --- | --- | --- | --- | --- | pH | --- | 5.48 | 5.58 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 25
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.82292 | Calcium (mg/L) | 252 |  |  |  | 1998-08-03 | 10:00 | 1705 | 29.478 | 134.697 | 26.212 | 18.399 | 0 | 13.853 | 3.986 |  | 17.839 | 17.839 | 0.77656 | 0 | 12.5936 | 12.417 | 7.2231 | 54.8324 | 0.22645 | 7.898 | 5.698 | 32.4535 | 293.232 | 296.2896 | 1281.4956 | 1213.2293 | 5.3271 | 89.0467 | 754.7594 | 95.7002 | 134.697 | 115.252 | 18.399 | 9.391 | 9.627 | 19.018 | 19.018 | 0.095518 | 0.4938 | 14.2648 | 14.0647 | 4.1501 | 102.4254 | 0.13732 | 5.698 | 5.698 | 17.3355 | 296.2896 | 498.6 | 568.4053 | -14.0003 | 94.1491 | 432.3475 | 95.9904 | 115.252 | 98.203 | 18.399 | 4.461 | 5.166 | 9.627 | 9.627 | 0.098656 | 0.46338 | 13.5524 | 13.3623 | 6.7927 | 81.5358 | 0.16388 | 5.698 | 5.698 | 24.173 | 498.6 | 839.04 | 908.2823 | -8.2526 | 91.8414 | 703.4412 | 96.5636 | 98.203 | 26.212 | 18.399 | 0.001 | 3.986 | 3.987 | 3.987 | 0.15952 | 0.00025082 | 0.0088889 | 0.0087642 | 7.4016 | 36.4069 | 0.00024073 | 5.698 | 7.064 | 98.9712 | 839.04 | 1281.4956 | 839.2257 | 34.512 | 66.5965 | 839.1328 | 88.2055 | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 79 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.9375 | Barium (mg/L) | 0.049 |  |  |  | 1998-08-03 | 18:00 | 1713.0003 | 29.465 | 129.504 | 55.567 | 18.379 | 0 | 14.683 | 3.288 |  | 17.971 | 17.971 | 0.81704 | 0 | 13.3482 | 13.166 | 8.4603 | 65.6962 | 0.20041 | 7.935 | 5.578 | 34.827 | 293.856 | 296.5262 | 1437.7932 | 1465.1789 | -1.9047 | 88.255 | 880.8526 | 96.0462 | 129.504 | 111.877 | 18.379 | 9.028 | 8.496 | 17.524 | 17.524 | 0.086765 | 0.51518 | 13.7134 | 13.5262 | 4.2615 | 98.05 | 0.13795 | 5.578 | 5.578 | 18.2325 | 296.5262 | 517.5 | 592.2461 | -14.4437 | 93.8513 | 444.3862 | 95.8971 | 111.877 | 98.734 | 18.379 | 4.399 | 4.097 | 8.496 | 8.496 | 0.083984 | 0.51777 | 13.3641 | 13.1816 | 7.48 | 79.4465 | 0.16592 | 5.578 | 5.578 | 30.7913 | 517.5 | 928 | 1040.0853 | -12.0782 | 89.616 | 778.7926 | 96.0463 | 98.734 | 55.567 | 18.379 | 1.256 | 3.288 | 4.544 | 4.544 | 0.1567 | 0.27641 | 11.1644 | 11.012 | 9.8662 | 48.9053 | 0.22517 | 5.578 | 7.024 | 99.6048 | 928 | 1437.7932 | 1244.4429 | 13.4477 | 66.4094 | 1086.2215 | 90.8302 | Alkalinity | mg/L as CaCO3 | 18 | 50 | 286 | 195.7778 | 31.5462 | 64 | 122.8889 | 85.3526 | Alkalinity | mg/L as CaCO3 | 16 | 50 | 86.5036 | 68 | 68.2518 | 76.5574 | Alkalinity | mg/L as CaCO3 | 16 | 58 | NR | 226 | #VALUE! | 72.4138 | 142 | 88.7324 | Alkalinity | mg/L as CaCO3 | 14 | 58 | 98.1379 | 75.8621 | 78.069 | 82.0671 | Alkalinity | mg/L as CaCO3 | 16 | 48 | 206 | 184.4211 | 10.4752 | 66.6667 | 116.2105 | 86.2319 | Alkalinity | mg/L as CaCO3 | 16 | 48 | 77.1976 | 66.6667 | 62.5988 | 74.4404 | Alkalinity | mg/L as CaCO3 | 16 | 38 | 176 | 138.2222 | 21.4646 | 57.8947 | 88.1111 | 81.8411 | Alkalinity | mg/L as CaCO3 | 16 | 38 | 59.151 | 57.8947 | 48.5755 | 67.0616 | Alkalinity | mg/L as CaCO3 | 18 | 42 | 160 | 138 | 13.75 | 57.1429 | 90 | 80 | Alkalinity | mg/L as CaCO3 | 16 | 42 | 66.1911 | 61.9048 | 54.0955 | 70.4227 | Alkalinity | mg/L as CaCO3 | 16 | 36 | 162 | 127.1111 | 21.5364 | 55.5556 | 81.5556 | 80.3815 | Alkalinity | mg/L as CaCO3 | 14 | 36 | 57.151 | 61.1111 | 46.5755 | 69.9413 | Electric Rate ($/kW-h) | 0.07
Mailing Address |  | Design flux, FW (gfd) | 17.9 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.875 | Strontium (mg/L) | 0.4 |  |  |  | 1998-08-04 | 2:00 | 1721 | 29.38 | 129.812 | 55.927 | 18.391 | 0 | 14.748 | 3.23 |  | 17.978 | 17.978 | 0.82034 | 0 | 13.4073 | 13.2575 | 8.6036 | 65.8749 | 0.20125 | 7.896 | 5.622 | 34.686 | 295.296 | 296.7547 | 1447.9236 | 1493.3459 | -3.1371 | 88.3116 | 895.0503 | 96.1247 | 129.812 | 112.38 | 18.391 | 9.091 | 8.547 | 17.638 | 17.638 | 0.087315 | 0.51542 | 13.8091 | 13.6549 | 4.2695 | 98.4355 | 0.13872 | 5.622 | 5.622 | 18.0375 | 296.7547 | 520.2 | 593.2118 | -14.0353 | 93.9217 | 444.9832 | 95.9465 | 112.38 | 98.9 | 18.391 | 4.4 | 4.147 | 8.547 | 8.547 | 0.084657 | 0.5148 | 13.3671 | 13.2178 | 7.4894 | 79.7596 | 0.16572 | 5.622 | 5.622 | 30.8603 | 520.2 | 924.16 | 1039.3934 | -12.469 | 89.6008 | 779.7967 | 96.0425 | 98.9 | 55.927 | 18.391 | 1.257 | 3.23 | 4.487 | 4.487 | 0.1544 | 0.28014 | 11.1733 | 11.0485 | 9.8508 | 49.1717 | 0.22469 | 5.622 | 7.05 | 99.5328 | 924.16 | 1447.9236 | 1245.0753 | 14.0096 | 66.4596 | 1084.6176 | 90.8232 | Total dissolved solids | mg/L | 35 | 296.5 | 1495 | 1487.7778 | 0.48309 | 88.1956 | 892.1389 | 96.0768 | Total dissolved solids | mg/L | 18.1 | 297 | 596.4366 | 93.8954 | 446.7183 | 95.9482 | Total dissolved solids | mg/L | 33 | 295 | 1346 | 1343 | 0.22288 | 88.8136 | 819 | 95.9707 | Total dissolved solids | mg/L | 17.1 | 295 | 548.5075 | 94.2034 | 421.7538 | 95.9455 | Total dissolved solids | mg/L | 36.1 | 299 | 1440 | 1419.7842 | 1.4039 | 87.9264 | 859.3921 | 95.7994 | Total dissolved solids | mg/L | 18 | 299 | 555.391 | 93.9799 | 427.1955 | 95.7865 | Total dissolved solids | mg/L | 33.9 | 297 | 1392 | 1495.5667 | -7.4401 | 88.5859 | 896.2833 | 96.2177 | Total dissolved solids | mg/L | 17.1 | 297 | 565.2337 | 93.9394 | 431.1169 | 95.8248 | Total dissolved solids | mg/L | 36 | 292 | 1190 | 1316 | -10.5882 | 87.6712 | 804 | 95.5224 | Total dissolved solids | mg/L | 23 | 292 | 542.2845 | 92.1233 | 417.1423 | 94.4863 | Total dissolved solids | mg/L | 33.9 | 297 | 1392 | 1495.5667 | -7.4401 | 88.5859 | 896.2833 | 96.2177 | Total dissolved solids | mg/L | 17.1 | 297 | 566.099 | 94.2424 | 431.5495 | 96.0375 | Fuel Oil Rate ($/gal) | 0.89
|  | Net driving pressure at the design flux, NDP (psi) | 80 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.9375 | Reactive silica (mg/L as SiO2) | 6.29 |  |  |  | 1998-08-04 | 10:00 | 1729.0003 | 29.525 | 129.283 | 55.59 | 18.343 | 0 | 14.575 | 3.288 |  | 17.863 | 17.863 | 0.81593 | 0 | 13.25 | 13.046 | 8.4089 | 65.6846 | 0.19862 | 7.935 | 5.599 | 35.0385 | 293.376 | 296.4773 | 1435.6224 | 1455.3794 | -1.3762 | 88.1817 | 875.9283 | 95.9998 | 129.283 | 111.66 | 18.343 | 9.036 | 8.427 | 17.463 | 17.463 | 0.086331 | 0.51744 | 13.7256 | 13.5142 | 4.2763 | 97.8522 | 0.13811 | 5.599 | 5.599 | 18.096 | 296.4773 | 519.75 | 594.9765 | -14.4736 | 93.8963 | 445.7269 | 95.9401 | 111.66 | 98.504 | 18.343 | 4.341 | 4.086 | 8.427 | 8.427 | 0.08345 | 0.51513 | 13.1878 | 12.9848 | 7.4863 | 79.2527 | 0.16384 | 5.599 | 5.599 | 30.8373 | 519.75 | 931.84 | 1039.1749 | -11.5186 | 89.5988 | 779.4625 | 96.0438 | 98.504 | 55.59 | 18.343 | 1.198 | 3.288 | 4.486 | 4.486 | 0.15554 | 0.26705 | 10.6489 | 10.4849 | 9.8603 | 48.8437 | 0.21466 | 5.599 | 6.992 | 97.7616 | 931.84 | 1435.6224 | 1235.7408 | 13.923 | 67.0256 | 1083.7904 | 90.9797 | Total hardness | mg/L as CaCO3 | 18 | 340 | 1660 | 1806.8889 | -8.8487 | 94.7059 | 1073.4444 | 98.3232 | Total hardness | mg/L as CaCO3 | 12 | 340 | 692.152 | 96.4706 | 516.076 | 97.6748 | Total hardness | mg/L as CaCO3 | 22 | 268 | NR | 1252 | #VALUE! | 91.791 | 760 | 97.1053 | Total hardness | mg/L as CaCO3 | 12 | 268 | 501.5298 | 95.5224 | 384.7649 | 96.8812 | Total hardness | mg/L as CaCO3 | 20 | 272 | 1660 | 1346.3158 | 18.8966 | 92.6471 | 809.1579 | 97.5283 | Total hardness | mg/L as CaCO3 | 14 | 272 | 507.4053 | 94.8529 | 389.7026 | 96.4075 | Total hardness | mg/L as CaCO3 | 18 | 294 | 1680 | 1551.3333 | 7.6587 | 93.8776 | 922.6667 | 98.0491 | Total hardness | mg/L as CaCO3 | 18 | 294 | 563.1951 | 95.2381 | 428.5976 | 96.7335 | Total hardness | mg/L as CaCO3 | 20 | 288 | 1660 | 1360 | 18.0723 | 93.0556 | 824 | 97.5728 | Total hardness | mg/L as CaCO3 | 28 | 288 | 529.9107 | 90.2778 | 408.9553 | 93.1533 | Total hardness | mg/L as CaCO3 | 20 | 286 | 1671 | 1497.7778 | 10.3664 | 93.007 | 891.8889 | 97.7576 | Total hardness | mg/L as CaCO3 | 18 | 286 | 543.6582 | 93.7063 | 414.8291 | 95.6609 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 4.9375 | Turbidity (ntu) | 0.24 |  |  |  | 1998-08-04 | 18:00 | 1737 | 29.435 | 129.665 | 55.642 | 18.39 | 0 | 14.689 | 3.288 |  | 17.977 | 17.977 | 0.8171 | 0 | 13.3536 | 13.183 | 8.4734 | 65.7901 | 0.20038 | 8.158 | 5.565 | 34.78 | 294.624 | 296.8118 | 1443.9438 | 1467.4279 | -1.6264 | 88.2821 | 882.1199 | 96.0572 | 129.665 | 111.945 | 18.39 | 9.093 | 8.371 | 17.464 | 17.464 | 0.086148 | 0.52067 | 13.8122 | 13.6357 | 4.2991 | 98.1159 | 0.13898 | 5.565 | 5.565 | 18.213 | 296.8118 | 521.55 | 599.4399 | -14.9343 | 93.8638 | 448.1259 | 95.9357 | 111.945 | 98.752 | 18.39 | 4.339 | 4.032 | 8.371 | 8.371 | 0.082717 | 0.51834 | 13.1818 | 13.0134 | 7.5466 | 79.4119 | 0.16387 | 5.565 | 5.565 | 30.8947 | 521.55 | 927.36 | 1049.5642 | -13.1776 | 89.5911 | 785.5571 | 96.0672 | 98.752 | 55.642 | 18.39 | 1.257 | 3.288 | 4.545 | 4.545 | 0.15672 | 0.27657 | 11.1733 | 11.0306 | 9.8749 | 48.9321 | 0.22543 | 5.565 | 7.018 | 98.3376 | 927.36 | 1443.9438 | 1244.2947 | 13.8267 | 66.8687 | 1085.8273 | 90.9435 | Calcium hardness | mg/L as CaCO3 | 18 | 320 | 1540 | 1695.7778 | -10.1154 | 94.375 | 1007.8889 | 98.2141 | Calcium hardness | mg/L as CaCO3 | 12 | 320 | 650.6793 | 96.25 | 485.3397 | 97.5275 | Calcium hardness | mg/L as CaCO3 | 16 | 250 | NR | 1186 | #VALUE! | 93.6 | 718 | 97.7716 | Calcium hardness | mg/L as CaCO3 | 8 | 250 | 470.7586 | 96.8 | 360.3793 | 97.7801 | Calcium hardness | mg/L as CaCO3 | 18 | 268 | 1400 | 1333.7895 | 4.7293 | 93.2836 | 800.8947 | 97.7525 | Calcium hardness | mg/L as CaCO3 | 12 | 268 | 501.5804 | 95.5224 | 384.7902 | 96.8814 | Calcium hardness | mg/L as CaCO3 | 16 | 258 | 1562 | 1360.4444 | 12.9037 | 93.7984 | 809.2222 | 98.0228 | Calcium hardness | mg/L as CaCO3 | 14 | 258 | 505.8326 | 99.9147 | 381.9163 | 99.9424 | Calcium hardness | mg/L as CaCO3 | 18 | 280 | 1520 | 1328 | 12.6316 | 93.5714 | 804 | 97.7612 | Calcium hardness | mg/L as CaCO3 | 24 | 280 | 518.189 | 91.4286 | 399.0945 | 93.9864 | Calcium hardness | mg/L as CaCO3 | 18 | 252 | 1580 | 1318 | 16.5823 | 92.8571 | 785 | 97.707 | Calcium hardness | mg/L as CaCO3 | 14 | 252 | 480.8159 | 94.4444 | 366.4079 | 96.1791 | Current Process Water Rate ($/1000 gal) | 0.95
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Permeate flow rate from system, Qp-sys (gpm) | 19.75 | SDI | 2.5 |  |  |  | 1998-08-05 | 4:00 | 1747 | 29.418 | 132.332 | 46.575 | 17.931 | 0 | 14.25 | 3.947 |  | 18.197 | 18.197 | 0.7831 | 0 | 12.9545 | 12.7955 | 7.3754 | 64.1471 | 0.19947 | 8.095 | 5.622 | 33.8165 | 295.2 | 296.7384 | 1402.6986 | 1245.9751 | 11.173 | 88.6039 | 771.3567 | 95.616 | 132.332 | 114.052 | 17.931 | 8.61 | 9.453 | 18.063 | 18.063 | 0.091753 | 0.47667 | 13.0785 | 12.9179 | 4.0614 | 101.1996 | 0.12765 | 5.622 | 5.622 | 17.6865 | 296.7384 | 515.7 | 550.905 | -6.8266 | 94.0397 | 423.8217 | 95.8269 | 114.052 | 98.95 | 17.931 | 4.5 | 4.953 | 9.453 | 9.453 | 0.096075 | 0.47604 | 13.6709 | 13.503 | 7.085 | 81.485 | 0.16571 | 5.622 | 5.622 | 28.5143 | 515.7 | 899.84 | 958.3279 | -6.4998 | 90.3908 | 737.0139 | 96.1311 | 98.95 | 46.575 | 17.931 | 1.14 | 3.947 | 5.087 | 5.087 | 0.18075 | 0.2241 | 10.1333 | 10.0089 | 9.1648 | 45.6667 | 0.21917 | 5.622 | 7.074 | 99.0144 | 899.84 | 1402.6986 | 1131.14 | 19.3597 | 66.6324 | 1015.49 | 90.2496 | Turbidity | ntu | 0.526 | 64 | 27.1 | 353.1593 | -1203.171 | 99.1781 | 208.5797 | 99.7478 | Turbidity | ntu | 0.205 | 0.64 | 1.107 | 99.6797 | 0.87352 | 76.5316 | Turbidity | ntu | 0.203 | 2.23 | 0.203 | 10.338 | -4992.6108 | 90.8969 | 6.284 | 96.7696 | Turbidity | ntu | 0.277 | 2.23 | 4.0116 | 87.5785 | 3.1208 | 91.124 | Turbidity | ntu | 0.374 | 1.34 | 6.95 | 5.4582 | 21.4646 | 72.0896 | 3.3991 | 88.9971 | Turbidity | ntu | 0.328 | 1.34 | 2.2634 | 75.5224 | 1.8017 | 81.7948 | Turbidity | ntu | 0.08 | 0.79 | 112 | 4.0244 | 96.4067 | 89.8734 | 2.4072 | 96.6767 | Turbidity | ntu | 0.22 | 0.79 | -3.0845 | -510.1266 | -1.1472 | 520.1374 | Turbidity | ntu | 0.951 | 3.17 | 146 | 12.046 | 91.7493 | 70 | 7.608 | 87.5 | Turbidity | ntu | 0.327 | 3.17 | 5.8152 | 89.6845 | 4.4926 | 92.7214 | Turbidity | ntu | 2.38 | 3.92 | 112 | 10.9356 | 90.2361 | 39.2857 | 7.4278 | 67.9581 | Turbidity | ntu | 0.23 | 3.92 | 7.4676 | 94.1327 | 5.6938 | 95.9605 | Modifications to Existing Plant (% of construction costs) | 75
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | Feed flow rate to system, QF-sys (gpm) | 24.6875 | MFI |  |  |  |  | 1998-08-05 | 12:00 | 1755 | 29.435 | 131.869 | 46.26 | 17.919 | 0 | 14.14 | 3.946 |  | 18.086 | 18.086 | 0.78182 | 0 | 12.8545 | 12.6903 | 7.3207 | 63.8248 | 0.19883 | 7.687 | 5.645 | 34.2865 | 293.424 | 296.5181 | 1384.9704 | 1236.1923 | 10.7423 | 88.437 | 766.3552 | 95.526 | 131.869 | 113.325 | 17.919 | 8.62 | 9.503 | 18.123 | 18.123 | 0.09212 | 0.47564 | 13.0937 | 12.9264 | 4.0504 | 100.6276 | 0.12846 | 5.645 | 5.645 | 17.862 | 296.5181 | 516.15 | 549.282 | -6.4191 | 93.9761 | 422.9 | 95.7763 | 113.325 | 98.626 | 17.919 | 4.44 | 5.063 | 9.503 | 9.503 | 0.097142 | 0.46722 | 13.4886 | 13.3163 | 7.0162 | 81.0403 | 0.16432 | 5.645 | 5.645 | 28.3992 | 516.15 | 912 | 943.8832 | -3.496 | 90.4224 | 730.0166 | 96.1098 | 98.626 | 46.26 | 17.919 | 1.08 | 3.946 | 5.026 | 5.026 | 0.17951 | 0.21488 | 9.6 | 9.4774 | 9.2652 | 45.2588 | 0.2094 | 5.645 | 7.053 | 97.0128 | 912 | 1384.9704 | 1135.0578 | 18.0446 | 67.2827 | 1023.5289 | 90.5217 | Ammonia | mg NH3-N / L | 0.15 | NA | 2.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.09 | 17.1 | 34.2889 | 93.6257 | 25.6944 | 95.7578 | Ammonia | mg NH3-N / L | 0.15 | 0.75 | 2.92 | 3.15 | -7.8767 | 80 | 1.95 | 92.3077 | Total organic carbon | mg/L | 8.11 | 24.5 | 39.4514 | 66.898 | 31.9757 | 74.637 | Ammonia | mg NH3-N / L | BMRL | 0.8 | 3.08 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 32.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | 1.45 | 2.88 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 4.82 | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 7.9 | 19.8 | 30.8721 | 60.101 | 25.336 | 68.8191 | Ammonia | mg NH3-N / L | BMRL | 1.15 | 2.55 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 12 | 38.2 | 63.389 | 68.5864 | 50.7945 | 76.3754
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Concentrate-waste flow rate from system, QW-sys (gpm) | 4.9375 | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-08-05 | 20:00 | 1763.0003 | 29.406 | 131.883 | 46.26 | 17.97 | 0 | 14.309 | 3.888 |  | 18.197 | 18.197 | 0.78634 | 0 | 13.0082 | 12.853 | 7.4637 | 63.6378 | 0.20197 | 8.035 | 5.564 | 32.2655 | 285.264 | 295.0574 | 1347.705 | 1262.2102 | 6.3437 | 89.0647 | 778.6338 | 95.8561 | 131.883 | 113.34 | 17.97 | 8.669 | 9.689 | 18.358 | 18.358 | 0.093524 | 0.47222 | 13.1681 | 13.011 | 4.0275 | 100.614 | 0.12932 | 5.564 | 5.564 | 16.7895 | 295.0574 | 496.8 | 544.031 | -9.507 | 94.3098 | 419.5442 | 95.9982 | 113.34 | 98.567 | 17.97 | 4.5 | 5.189 | 9.689 | 9.689 | 0.099223 | 0.46444 | 13.6709 | 13.5078 | 6.7277 | 81.2558 | 0.16624 | 5.564 | 5.564 | 27.5138 | 496.8 | 858.24 | 903.774 | -5.3055 | 90.6751 | 700.287 | 96.0711 | 98.567 | 46.26 | 17.97 | 1.14 | 3.888 | 5.028 | 5.028 | 0.17838 | 0.22673 | 10.1333 | 10.0125 | 8.7776 | 45.6659 | 0.21925 | 5.564 | 6.979 | 92.7072 | 858.24 | 1347.705 | 1082.7018 | 19.6633 | 68.5799 | 970.4709 | 90.4472 | Total organic carbon | mg/L | 1.35 | 17.1 | 93.4 | 88.85 | 4.8715 | 92.1053 | 52.975 | 97.4516 | UV254 | cm-1 | 0.07 | 0.51 | 0.9824 | 86.2745 | 0.7462 | 90.6191 | Total organic carbon | mg/L | 8.46 | 24.5 | 150 | 88.66 | 40.8933 | 65.4694 | 56.58 | 85.0477 | UV254 | cm-1 | 0.232 | 0.465 | 0.67755 | 50.1075 | 0.57127 | 59.389 | Total organic carbon | mg/L | BMRL | 32.1 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.568 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 4.9 | 19.8 | 92.6 | 77.6778 | 16.1147 | 72.7778 | 47.8389 | 89.7573 | UV254 | cm-1 | BMRL | 0.552 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 4.9 | 18 | 92.6 | 79.4 | 14.2549 | 75.2525 | 49.6 | 90.121 | UV254 | cm-1 | 0.02 | 0.45 | 0.85008 | 95.5556 | 0.65004 | 96.9233 | Total organic carbon | mg/L | 10.1 | 38.2 | 70.4 | 166.2111 | -136.0953 | 73.5602 | 102.2056 | 90.118 | UV254 | cm-1 | 0.008 | 0.55 | 1.0711 | 98.5455 | 0.81054 | 99.013
Plant Name | Pompano Beach WTP | Total width of all membrane envelopes in the element, w (ft) | 57.6 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-08-06 | 4:00 | 1771.0003 | 29.393 | 132.124 | 46.35 | 17.986 | 0 | 14.366 | 3.947 |  | 18.313 | 18.313 | 0.78447 | 0 | 13.06 | 12.9092 | 7.4223 | 63.8287 | 0.20225 | 7.873 | 5.598 | 33.3935 | 294.432 | 296.6078 | 1396.548 | 1254.636 | 10.1616 | 88.7415 | 775.6219 | 95.6946 | 132.124 | 113.58 | 17.986 | 8.666 | 9.397 | 18.063 | 18.063 | 0.091567 | 0.47977 | 13.1635 | 13.0115 | 4.081 | 100.785 | 0.1291 | 5.598 | 5.598 | 17.2965 | 296.6078 | 516.15 | 554.1913 | -7.3702 | 94.1686 | 425.3996 | 95.9341 | 113.58 | 98.675 | 17.986 | 4.5 | 4.897 | 9.397 | 9.397 | 0.095328 | 0.47888 | 13.6709 | 13.513 | 7.1169 | 81.0246 | 0.16678 | 5.598 | 5.598 | 28.5143 | 516.15 | 889.6 | 964.2531 | -8.3918 | 90.3865 | 740.2015 | 96.1478 | 98.675 | 46.35 | 17.986 | 1.2 | 3.947 | 5.147 | 5.147 | 0.18195 | 0.23315 | 10.6667 | 10.5435 | 9.1314 | 45.3951 | 0.23226 | 5.598 | 7.011 | 96.9552 | 889.6 | 1396.548 | 1130.5865 | 19.0442 | 67.312 | 1010.0933 | 90.4014 | UV254 | cm-1 | 0.052 | 0.51 | 3.15 | 2.5964 | 17.5732 | 89.8039 | 1.5532 | 96.6521 | SUVA | L/(mg*m) | 6.422 | 2.9825 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.465 | 2.55 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 2.8607 | 1.898 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.568 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 1.7695 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.45 | 1.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.0667 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.552 | 1.85 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.25316 | 2.2727 | --- | --- | --- | --- | UV254 | cm-1 | 0.019 | 0.55 | 2.79 | 2.969 | -6.4158 | 96.5455 | 1.7595 | 98.9201 | SUVA | L/(mg*m) | 0.066667 | 1.4398 | --- | --- | --- | ---
Treatment Plant Category | CONV | Feed spacer thickness, T (ft) | 0.0029 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-08-06 | 12:00 | 1779.0003 | 29.372 | 127.655 | 52.507 | 17.55 | 0 | 14.009 | 3.349 |  | 17.358 | 17.358 | 0.80706 | 0 | 12.7355 | 12.5962 | 8.1022 | 64.4288 | 0.19551 | 8.115 | 5.587 | 34.7095 | 295.296 | 296.7874 | 1441.0494 | 1393.0695 | 3.3295 | 88.3049 | 844.9284 | 95.892 | 127.655 | 109.98 | 17.55 | 8.369 | 9.158 | 17.527 | 17.527 | 0.088982 | 0.47749 | 12.7124 | 12.5734 | 4.06 | 97.2075 | 0.12935 | 5.587 | 5.587 | 18.1155 | 296.7874 | 520.65 | 551.4505 | -5.9158 | 93.8961 | 424.1189 | 95.7287 | 109.98 | 97.429 | 17.55 | 4.5 | 4.658 | 9.158 | 9.158 | 0.09214 | 0.49137 | 13.6709 | 13.5214 | 7.2712 | 78.8833 | 0.17141 | 5.587 | 5.587 | 30.36 | 520.65 | 936.96 | 994.3093 | -6.1208 | 89.7705 | 757.4796 | 95.992 | 97.429 | 52.507 | 17.55 | 1.14 | 3.349 | 4.489 | 4.489 | 0.15682 | 0.25395 | 10.1333 | 10.0225 | 9.7905 | 47.6275 | 0.21044 | 5.587 | 7.015 | 100.3104 | 936.96 | 1441.0494 | 1221.7556 | 15.2176 | 66.2013 | 1079.3578 | 90.7065 | SUVA | L/(mg*m) | 3.8519 | 2.9825 | 3.3726 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 1.898 | 1.7 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 1.7695 | #VALUE! | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 2.2727 | 1.9978 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 3.0667 | 1.9978 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 0.18812 | 1.4398 | 3.9631 | --- | --- | --- | --- | ---
Process Train Name | Conventional train | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 16.4583 | [5 empty] | 1998-08-06 | 20:00 | 1787 | 29.35 | 127.642 | 52.417 | 17.52 | 0 | 13.949 | 3.409 |  | 17.358 | 17.358 | 0.80361 | 0 | 12.6809 | 12.5504 | 7.9824 | 64.5271 | 0.1945 | 8.141 | 5.526 | 34.7095 | 294.528 | 296.7792 | 1442.1348 | 1369.1201 | 5.063 | 88.3046 | 832.9497 | 95.8329 | 127.642 | 110.032 | 17.52 | 8.369 | 9.155 | 17.524 | 17.524 | 0.088962 | 0.47757 | 12.7124 | 12.5816 | 4.0603 | 97.2567 | 0.12936 | 5.526 | 5.526 | 18.1155 | 296.7792 | 520.65 | 551.5183 | -5.9288 | 93.896 | 424.1488 | 95.729 | 110.032 | 97.397 | 17.52 | 4.38 | 4.775 | 9.155 | 9.155 | 0.0929 | 0.47843 | 13.3063 | 13.1694 | 7.1515 | 79.043 | 0.16661 | 5.526 | 5.526 | 30.3657 | 520.65 | 936.32 | 970.3767 | -3.6373 | 89.7682 | 745.5134 | 95.9269 | 97.397 | 52.417 | 17.52 | 1.2 | 3.409 | 4.609 | 4.609 | 0.16042 | 0.26036 | 10.6667 | 10.5569 | 9.8371 | 47.5499 | 0.22202 | 5.526 | 6.978 | 99.8352 | 936.32 | 1442.1348 | 1230.7705 | 14.6563 | 66.3604 | 1083.5453 | 90.7862 | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | 0.002 | 0.71111 | --- | -20 | 4.3556 | -120.4082 | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 1080 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 10.6979 | [5 empty] | 1998-08-07 | 0:00 | 1791 | 29.384 | 127.601 | 52.335 | 17.436 | 0 | 13.888 | 3.409 |  | 17.297 | 17.297 | 0.80291 | 0 | 12.6255 | 12.483 | 7.9639 | 64.5681 | 0.19333 | 8.024 | 5.513 | 34.686 | 295.296 | 296.9179 | 1441.4112 | 1365.2303 | 5.2852 | 88.318 | 831.0741 | 95.8264 | 127.601 | 109.807 | 17.436 | 8.368 | 9.033 | 17.401 | 17.401 | 0.088145 | 0.48089 | 12.7109 | 12.5674 | 4.0797 | 97.1883 | 0.12931 | 5.513 | 5.513 | 18.096 | 296.9179 | 520.65 | 555.2133 | -6.6385 | 93.9054 | 426.0656 | 95.7528 | 109.807 | 97.442 | 17.436 | 4.38 | 4.653 | 9.033 | 9.033 | 0.091273 | 0.48489 | 13.3063 | 13.1561 | 7.2105 | 78.978 | 0.16658 | 5.513 | 5.513 | 30.36 | 520.65 | 935.68 | 982.1738 | -4.969 | 89.775 | 751.4119 | 95.9596 | 97.442 | 52.335 | 17.436 | 1.14 | 3.409 | 4.549 | 4.549 | 0.15922 | 0.2506 | 10.1333 | 10.019 | 9.7595 | 47.693 | 0.21007 | 5.513 | 6.95 | 99.5328 | 935.68 | 1441.4112 | 1215.2951 | 15.6871 | 66.478 | 1075.4875 | 90.7453 | SDS-Cl2 dose | mg/L | 9 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 8.7 | 7.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 9.6 | 8 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 9.6 | 9 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4131618 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 5.7604 | [5 empty] | 1998-08-07 | 12:00 | 1803 | 29.508 | 127.119 | 51.982 | 17.524 | 0 | 13.951 | 3.408 |  | 17.359 | 17.359 | 0.80368 | 0 | 12.6827 | 12.4937 | 7.9688 | 64.0577 | 0.19504 | 7.771 | 5.57 | 34.8975 | 292.272 | 296.4446 | 1421.874 | 1367.1149 | 3.8512 | 88.228 | 831.7798 | 95.8045 | 127.119 | 109.29 | 17.524 | 8.371 | 9.093 | 17.464 | 17.464 | 0.088555 | 0.47933 | 12.7154 | 12.5259 | 4.0659 | 96.6146 | 0.12965 | 5.57 | 5.57 | 18.018 | 296.4446 | 518.4 | 552.7637 | -6.6288 | 93.922 | 424.6042 | 95.7565 | 109.29 | 97.051 | 17.524 | 4.38 | 4.713 | 9.093 | 9.093 | 0.092073 | 0.48169 | 13.3063 | 13.108 | 7.1491 | 78.4974 | 0.16699 | 5.57 | 5.57 | 30.2967 | 518.4 | 942.08 | 972.016 | -3.1777 | 89.78 | 745.208 | 95.9345 | 97.051 | 51.982 | 17.524 | 1.2 | 3.408 | 4.608 | 4.608 | 0.16038 | 0.26042 | 10.6667 | 10.5077 | 9.9192 | 47.0733 | 0.22322 | 5.57 | 6.998 | 98.6544 | 942.08 | 1421.874 | 1239.0608 | 12.8572 | 66.7208 | 1090.5704 | 90.9539 | SDS-Free Cl2 residual | mg/L | 1.3 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.52 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.2 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 3.3 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 8.6 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 8.1 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 9.05 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-08-07 | 20:00 | 1811.0003 | 29.401 | 127.327 | 52.56 | 17.475 | 0 | 13.889 | 3.468 |  | 17.357 | 17.357 | 0.8002 | 0 | 12.6264 | 12.4776 | 7.8586 | 64.6099 | 0.19312 | 8.084 | 5.601 | 34.78 | 294.672 | 296.5181 | 1431.2808 | 1344.7534 | 6.0455 | 88.2705 | 820.6358 | 95.7618 | 127.327 | 109.785 | 17.475 | 8.369 | 9.391 | 17.76 | 17.76 | 0.090536 | 0.47123 | 12.7124 | 12.5626 | 4.0282 | 97.0528 | 0.12944 | 5.601 | 5.601 | 17.862 | 296.5181 | 520.2 | 544.8487 | -4.7383 | 93.9761 | 420.6834 | 95.7541 | 109.785 | 97.294 | 17.475 | 4.38 | 5.011 | 9.391 | 9.391 | 0.096048 | 0.4664 | 13.3063 | 13.1495 | 7.0389 | 79.0256 | 0.1664 | 5.601 | 5.601 | 30.3773 | 520.2 | 926.72 | 948.3428 | -2.3333 | 89.7553 | 734.2714 | 95.8629 | 97.294 | 52.56 | 17.475 | 1.14 | 3.468 | 4.608 | 4.608 | 0.16158 | 0.2474 | 10.1333 | 10.0139 | 9.6366 | 47.8154 | 0.20943 | 5.601 | 7.055 | 99.0864 | 926.72 | 1431.2808 | 1198.7795 | 16.2443 | 66.5834 | 1062.7497 | 90.6764 | SDS-Cl2 demand | mg/L | 7.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.34 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.7 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.7 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.1 | NR | --- | 34.8333 | --- | 80 | 21.1667 | 92.9134 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.68 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.5 | NR | --- | 34.1 | --- | 98.5507 | 20.5 | 99.5122 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.68 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.55 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.68
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-08-08 | 5:55 | 1820.9133 | 29.359 | 124.573 | 52.215 | 17.25 | 0 | 14.606 | 3.409 |  | 18.015 | 18.015 | 0.81077 | 0 | 13.2782 | 13.138 | 8.247 | 62.897 | 0.20888 | 8.104 | 5.571 | 34.31 | 294.48 | 296.7629 | 1467.099 | 1421.253 | 3.1249 | 88.4386 | 859.0079 | 96.0059 | 124.573 | 107.22 | 17.25 | 8.726 | 9.034 | 17.76 | 17.76 | 0.089346 | 0.49133 | 13.2547 | 13.1148 | 4.1432 | 94.5033 | 0.13878 | 5.571 | 5.571 | 17.3745 | 296.7629 | 524.25 | 566.626 | -8.0832 | 94.1453 | 431.6944 | 95.9753 | 107.22 | 95.971 | 17.25 | 4.56 | 4.474 | 9.034 | 9.034 | 0.090086 | 0.50476 | 13.8532 | 13.7069 | 7.4419 | 76.9036 | 0.17824 | 5.571 | 5.571 | 31.28 | 524.25 | 960 | 1026.696 | -6.9475 | 89.4596 | 775.473 | 95.9663 | 95.971 | 52.215 | 17.25 | 1.32 | 3.409 | 4.729 | 4.729 | 0.16282 | 0.27913 | 11.7333 | 11.6095 | 10.2646 | 46.5784 | 0.24925 | 5.571 | 7.064 | 100.0368 | 960 | 1467.099 | 1292.9866 | 11.8678 | 66.2907 | 1126.4933 | 91.1196 | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.43 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.56 |  |  |  |  | SDS-Chlorination temp. | oC | 24.6 | 24.6 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.82 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.69 |  |  |  |  | SDS-Chlorination temp. | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.39 |  |  |  |  | SDS-Chlorination temp. | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.69
State Approved Plant Capacity (MGD) | 18 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -8.4583 | [5 empty] | 1998-08-08 | 13:00 | 1828 | 29.478 | 133.732 | 54.99 | 18.304 | 0 | 14.672 | 3.466 |  | 18.138 | 18.138 | 0.80891 | 0 | 13.3382 | 13.1511 | 8.1577 | 67.8993 | 0.19368 | 8.245 | 5.7 | 34.5685 | 292.464 | 296.3222 | 1446.4764 | 1404.3577 | 2.9118 | 88.3342 | 850.34 | 95.9347 | 133.732 | 115.395 | 18.304 | 8.732 | 9.688 | 18.42 | 18.42 | 0.093727 | 0.47405 | 13.2638 | 13.0777 | 4.0412 | 102.2183 | 0.12794 | 5.7 | 5.7 | 17.745 | 296.3222 | 523.35 | 547.4098 | -4.5973 | 94.0116 | 421.866 | 95.7937 | 115.395 | 100.165 | 18.304 | 4.62 | 5.068 | 9.688 | 9.688 | 0.098409 | 0.47688 | 14.0354 | 13.8385 | 7.1672 | 82.3088 | 0.16813 | 5.7 | 5.7 | 31.027 | 523.35 | 932.48 | 972.1527 | -4.2545 | 89.5293 | 747.7514 | 95.8506 | 100.165 | 54.99 | 18.304 | 1.32 | 3.466 | 4.786 | 4.786 | 0.1651 | 0.2758 | 11.7333 | 11.5687 | 9.9255 | 49.348 | 0.23443 | 5.7 | 7.127 | 98.6976 | 932.48 | 1446.4764 | 1250.0197 | 13.5817 | 66.6925 | 1091.2499 | 90.9555 | SDS-Chlorination pH | --- | 8 | 8.45 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.76 | 8.55 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.87 | 8.72 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.9 | 8.76 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.92 | 8.4 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.57 | 8.61 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NA | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -6.6979 | [5 empty] | 1998-08-08 | 21:00 | 1836 | 29.427 | 134.033 | 55.312 | 18.285 | 0 | 14.543 | 3.468 |  | 18.011 | 18.011 | 0.80745 | 0 | 13.2209 | 13.0551 | 8.1303 | 68.2572 | 0.19126 | 8.213 | 5.7 | 33.981 | 294.72 | 296.5262 | 1456.245 | 1397.5053 | 4.0336 | 88.5403 | 847.0158 | 95.9882 | 134.033 | 115.575 | 18.285 | 8.663 | 9.395 | 18.058 | 18.058 | 0.091543 | 0.47973 | 13.159 | 12.9939 | 4.0762 | 102.4428 | 0.12684 | 5.7 | 5.7 | 17.5305 | 296.5262 | 521.1 | 553.7844 | -6.2722 | 94.088 | 425.1553 | 95.8767 | 115.575 | 100.381 | 18.285 | 4.68 | 4.715 | 9.395 | 9.395 | 0.094101 | 0.49814 | 14.2177 | 14.0394 | 7.3319 | 82.3611 | 0.17046 | 5.7 | 5.7 | 31.096 | 521.1 | 915.2 | 1007.4666 | -10.0816 | 89.5132 | 764.2833 | 95.9314 | 100.381 | 55.312 | 18.285 | 1.2 | 3.468 | 4.668 | 4.668 | 0.16278 | 0.25707 | 10.6667 | 10.5329 | 9.5788 | 49.9827 | 0.21073 | 5.7 | 7.106 | 98.5968 | 915.2 | 1456.245 | 1197.7617 | 17.75 | 66.7494 | 1056.4808 | 90.6674 | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -1.7604 | [5 empty] | 1998-08-09 | 5:00 | 1844.0003 | 29.389 | 134.194 | 55.245 | 18.376 | 0 | 14.487 | 3.409 |  | 17.896 | 17.896 | 0.80951 | 0 | 13.17 | 13.0194 | 8.2052 | 68.1383 | 0.19107 | 8.049 | 5.68 | 33.9105 | 294.528 | 296.4936 | 1455.1596 | 1412.3755 | 2.9402 | 88.5628 | 854.4345 | 96.0312 | 134.194 | 115.717 | 18.376 | 8.667 | 9.517 | 18.184 | 18.184 | 0.09237 | 0.47663 | 13.1651 | 13.0146 | 4.061 | 102.5185 | 0.12695 | 5.68 | 5.68 | 17.4525 | 296.4936 | 520.65 | 550.6125 | -5.7548 | 94.1137 | 423.553 | 95.8795 | 115.717 | 100.399 | 18.376 | 4.62 | 4.897 | 9.517 | 9.517 | 0.096128 | 0.48545 | 14.0354 | 13.875 | 7.205 | 82.477 | 0.16823 | 5.68 | 5.68 | 31.0845 | 520.65 | 913.92 | 982.5231 | -7.5065 | 89.516 | 751.5866 | 95.8641 | 100.399 | 55.245 | 18.376 | 1.2 | 3.409 | 4.609 | 4.609 | 0.16042 | 0.26036 | 10.6667 | 10.5447 | 9.5947 | 49.8513 | 0.21152 | 5.68 | 7.091 | 98.0496 | 913.92 | 1455.1596 | 1201.114 | 17.4583 | 66.9303 | 1057.517 | 90.7283 | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-18 (dup) | CI-s2-18 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-08-09 | 13:00 | 1852.0003 | 29.512 | 133.638 | 55.027 | 18.358 | 0 | 14.549 | 3.467 |  | 18.016 | 18.016 | 0.80756 | 0 | 13.2264 | 13.0277 | 8.1216 | 67.8529 | 0.192 | 8.039 | 5.7 | 34.1925 | 292.464 | 296.3304 | 1446.4764 | 1396.372 | 3.4639 | 88.4614 | 846.3512 | 95.96 | 133.638 | 115.207 | 18.358 | 8.669 | 9.511 | 18.18 | 18.18 | 0.092337 | 0.47684 | 13.1681 | 12.9703 | 4.0603 | 102.0042 | 0.12715 | 5.7 | 5.7 | 17.4135 | 296.3304 | 521.55 | 550.555 | -5.5613 | 94.1236 | 423.4427 | 95.8876 | 115.207 | 100.084 | 18.358 | 4.62 | 4.891 | 9.511 | 9.511 | 0.096048 | 0.48575 | 14.0354 | 13.8246 | 7.2219 | 82.0656 | 0.16846 | 5.7 | 5.7 | 31.0328 | 521.55 | 920.96 | 984.8887 | -6.9415 | 89.5277 | 753.2194 | 95.88 | 100.084 | 55.027 | 18.358 | 1.26 | 3.467 | 4.727 | 4.727 | 0.16394 | 0.26655 | 11.2 | 11.0318 | 9.7318 | 49.4657 | 0.22302 | 5.7 | 7.09 | 97.4304 | 920.96 | 1446.4764 | 1220.2526 | 15.6396 | 67.121 | 1070.6063 | 90.8995 | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-08-04 | 1998-08-04 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-08-18 | 1998-08-18 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-01 | 1998-09-01 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 16.46 | NR | --- | 317.1768 | --- | 42.7781 | 212.3694 | 71.018 | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | 458.16 | --- | 84.2939 | 281.48 | 94.1523 | Sampling date | MM/DD/YY | 1998-09-30 | 1998-09-30 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-08-10 | 5:00 | 1868 | 29.219 | 134.442 | 55.365 | 18.163 | 0 | 14.424 | 3.468 |  | 17.892 | 17.892 | 0.80617 | 0 | 13.1127 | 13.0281 | 8.1072 | 68.6333 | 0.18982 | 8.256 | 5.68 | 35.9785 | 310.656 | 299.2354 | 1543.4388 | 1394.1653 | 9.6715 | 87.9765 | 846.7003 | 95.7507 | 134.442 | 116.062 | 18.163 | 8.664 | 9.693 | 18.357 | 18.357 | 0.093534 | 0.47197 | 13.1605 | 13.0756 | 4.0735 | 103.0155 | 0.12693 | 5.68 | 5.68 | 17.706 | 299.2354 | 552.6 | 550.8778 | 0.31165 | 94.0829 | 425.0566 | 95.8344 | 116.062 | 100.561 | 18.163 | 4.56 | 5.133 | 9.693 | 9.693 | 0.098876 | 0.47044 | 13.8532 | 13.7638 | 7.5067 | 82.6418 | 0.16655 | 5.68 | 5.68 | 32.8152 | 552.6 | 970.88 | 1014.3609 | -4.4785 | 89.0336 | 783.4804 | 95.8116 | 100.561 | 55.365 | 18.163 | 1.2 | 3.468 | 4.668 | 4.668 | 0.16278 | 0.25707 | 10.6667 | 10.5978 | 10.1316 | 49.6684 | 0.21337 | 5.68 | 7.102 | 107.1504 | 970.88 | 1543.4388 | 1269.7484 | 17.7325 | 64.1919 | 1120.3142 | 90.4357 | SDS-BDCM | mg/L | 3.08 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 9.93 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 14 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.55 | NR | --- | 59.3883 | --- | 49.3681 | 38.8337 | 76.1676 | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 9.255 | NR | --- | 79 | --- | 85.7063 | 48.42 | 94.7336 | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 8.871 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-08-10 | 13:00 | 1876.0003 | 29.482 | 126.188 | 55.47 | 17.563 | 0 | 14.065 | 3.048 |  | 17.113 | 17.113 | 0.82189 | 0 | 12.7864 | 12.6055 | 8.6261 | 64.6399 | 0.19501 | 8.191 | 5.68 | 35.767 | 293.136 | 296.5915 | 1464.5664 | 1500.1666 | -2.4308 | 87.9407 | 898.3791 | 96.0187 | 126.188 | 108.577 | 17.563 | 8.185 | 9.15 | 17.335 | 17.335 | 0.088315 | 0.47217 | 12.4329 | 12.257 | 4.0272 | 95.7923 | 0.12795 | 5.68 | 5.68 | 18.33 | 296.5915 | 522.9 | 545.5063 | -4.3233 | 93.8198 | 421.0489 | 95.6466 | 108.577 | 97.024 | 17.563 | 4.56 | 4.59 | 9.15 | 9.15 | 0.091633 | 0.49836 | 13.8532 | 13.6572 | 7.3501 | 77.8874 | 0.17535 | 5.68 | 5.68 | 31.8263 | 522.9 | 964.48 | 1010.7641 | -4.7989 | 89.2693 | 766.8321 | 95.8496 | 97.024 | 55.47 | 17.563 | 1.32 | 3.048 | 4.368 | 4.368 | 0.14837 | 0.3022 | 11.7333 | 11.5673 | 10.5112 | 48.1728 | 0.24012 | 5.68 | 6.91 | 100.4544 | 964.48 | 1464.5664 | 1338.6643 | 8.5965 | 66.1304 | 1151.5722 | 91.2768 | SDS-DBCM | mg/L | 2.36 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1721 | 1721 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2070 | 2070 | --- | --- | --- | --- | SDS-DBCM | mg/L | 3.77 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2401 | 2401 | --- | --- | --- | --- | SDS-DBCM | mg/L | 0.08 | NR | --- | 1.77 | --- | -1.4263 | 1.8315 | -4.8321 | Operation time | hh.hh | 2815 | 2815 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.92 | NR | --- | 8.58 | --- | 95.5056 | 5.18 | 98.4556 | Operation time | hh.hh | 3087 | 3087 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.894 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2815 | 2815 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-08-10 | 21:00 | 1884 | 29.427 | 126.596 | 55.747 | 17.448 | 0 | 13.825 | 3.108 |  | 16.933 | 16.933 | 0.81645 | 0 | 12.5682 | 12.4105 | 8.4295 | 65.294 | 0.19007 | 8.27 | 5.62 | 35.203 | 294.624 | 296.6568 | 1475.0586 | 1459.6551 | 1.0443 | 88.1334 | 878.156 | 95.9913 | 126.596 | 109.185 | 17.448 | 8.245 | 9.149 | 17.394 | 17.394 | 0.088509 | 0.47401 | 12.5241 | 12.367 | 4.0399 | 96.4026 | 0.12828 | 5.62 | 5.62 | 18.1545 | 296.6568 | 525.15 | 547.6407 | -4.2827 | 93.8803 | 422.1487 | 95.6995 | 109.185 | 97.181 | 17.448 | 4.32 | 4.829 | 9.149 | 9.149 | 0.093221 | 0.47218 | 13.1241 | 12.9594 | 7.1387 | 78.5963 | 0.16489 | 5.62 | 5.62 | 31.9067 | 525.15 | 949.76 | 966.403 | -1.7523 | 89.2446 | 745.7765 | 95.7217 | 97.181 | 55.747 | 17.448 | 1.26 | 3.108 | 4.368 | 4.368 | 0.14957 | 0.28846 | 11.2 | 11.0595 | 10.2129 | 48.8031 | 0.22662 | 5.62 | 7.003 | 100.5984 | 949.76 | 1475.0586 | 1294.0147 | 12.2737 | 66.0893 | 1121.8874 | 91.0331 | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.81 | 5.9 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.38 | 29 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.24 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.2 | 5.83 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.06 | NR | --- | -0.12078 | --- | -62.1212 | -0.027389 | 490.6694 | pH | --- | 5.5 | 6.02 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.107 | NR | --- | 0.06 | --- | 0 | 0.06 | 0 | pH | --- | 5.3 | 5.91 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.112 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.47 | 5.99 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 7.3125 | [5 empty] | 1998-08-11 | 1:45 | 1888.7544 | 29.384 | 126.63 | 55.89 | 17.46 | 0 | 13.884 | 3.108 |  | 16.992 | 16.992 | 0.81709 | 0 | 12.6218 | 12.4794 | 8.4591 | 65.3409 | 0.19099 | 8.268 | 5.6 | 35.203 | 294.576 | 296.8037 | 1474.6968 | 1465.4214 | 0.62897 | 88.1393 | 881.1125 | 96.0047 | 126.63 | 109.245 | 17.46 | 8.244 | 9.156 | 17.4 | 17.4 | 0.088552 | 0.47379 | 12.5225 | 12.3812 | 4.0412 | 96.4363 | 0.12839 | 5.6 | 5.6 | 18.135 | 296.8037 | 525.15 | 547.7151 | -4.2969 | 93.8899 | 422.2594 | 95.7052 | 109.245 | 97.307 | 17.46 | 4.38 | 4.776 | 9.156 | 9.156 | 0.092914 | 0.47837 | 13.3063 | 13.1561 | 7.1933 | 78.6227 | 0.16733 | 5.6 | 5.6 | 31.9642 | 525.15 | 949.76 | 977.4435 | -2.9148 | 89.2305 | 751.2967 | 95.7455 | 97.307 | 55.89 | 17.46 | 1.26 | 3.108 | 4.368 | 4.368 | 0.14957 | 0.28846 | 11.2 | 11.0736 | 10.2191 | 48.9194 | 0.22636 | 5.6 | 6.99 | 100.08 | 949.76 | 1474.6968 | 1294.2249 | 12.2379 | 66.2807 | 1121.9924 | 91.0802 | SDS-THM4 | mg/L | 5.44 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 9.93 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 18.01 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 19.15 | NR | --- | 378.2143 | --- | 43.0117 | 253.0072 | 71.2139 | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 11.282 | NR | --- | 545.8 | --- | 84.616 | 335.14 | 94.286 | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 10.877 | 0 | --- | -49.5508 | --- | #DIV/0! | -24.7754 | 143.9024 | Temperature | oC | 29 | 29 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 80 - 350 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 1.1875 | [5 empty] | 1998-08-11 | 9:00 | 1896 | 29.253 | 127.146 | 56.272 | 17.457 | 0 | 13.949 | 3.108 |  | 17.057 | 17.057 | 0.81779 | 0 | 12.6809 | 12.5864 | 8.4739 | 65.7781 | 0.19135 | 8.197 | 5.69 | 37.835 | 309.408 | 299.0477 | 1554.2928 | 1471.3951 | 5.3335 | 87.3482 | 885.2214 | 95.7259 | 127.146 | 109.425 | 17.457 | 8.249 | 9.149 | 17.398 | 17.398 | 0.088522 | 0.47413 | 12.5301 | 12.4368 | 4.0679 | 96.7606 | 0.12853 | 5.69 | 5.69 | 18.6615 | 299.0477 | 554.85 | 551.8519 | 0.54035 | 93.7597 | 425.4498 | 95.6137 | 109.425 | 97.442 | 17.457 | 4.44 | 4.709 | 9.149 | 9.149 | 0.09242 | 0.4853 | 13.4886 | 13.3881 | 7.6688 | 78.3077 | 0.17097 | 5.69 | 5.69 | 33.672 | 554.85 | 1009.92 | 1046.2559 | -3.5979 | 88.7403 | 800.5529 | 95.7939 | 97.442 | 56.272 | 17.457 | 1.26 | 3.108 | 4.368 | 4.368 | 0.14957 | 0.28846 | 11.2 | 11.1166 | 10.8341 | 48.5659 | 0.2289 | 5.69 | 6.995 | 109.1088 | 1009.92 | 1554.2928 | 1375.1137 | 11.528 | 63.5146 | 1192.5169 | 90.8505 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 76 | 135.423 | 60 | 105.7115 | 81.0806 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 90 | 161.5638 | 72.4138 | 125.7819 | 87.2796 | SDS-MCAA* | mg/L | 5.67 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 84 | 144.5859 | 62.5 | 114.293 | 84.251 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 116 | 205.6766 | 47.3684 | 160.8383 | 87.5652 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 76 | 135.6178 | 61.9048 | 105.8089 | 84.8784 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 58 | 95.3653 | 50 | 76.6826 | 76.5266
|  | Acceptable range of operating pH values | 4 - 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 6.125 | [5 empty] | 1998-08-12 | 1:00 | 1912.0003 | 29.129 | 135.782 | 51.12 | 18.648 | 0 | 14.85 | 3.827 |  | 18.677 | 18.677 | 0.7951 | 0 | 13.5 | 13.4486 | 7.7606 | 67.0424 | 0.2006 | 8.222 | 5.69 | 35.1795 | 309.984 | 299.1293 | 1501.8318 | 1323.3399 | 11.8849 | 88.2394 | 811.2346 | 95.6635 | 135.782 | 117.232 | 18.648 | 9.09 | 9.265 | 18.355 | 18.355 | 0.0921 | 0.49523 | 13.8076 | 13.755 | 4.1927 | 103.6663 | 0.13269 | 5.69 | 5.69 | 17.8425 | 299.1293 | 549.45 | 575.103 | -4.6689 | 94.0352 | 437.1162 | 95.9181 | 117.232 | 100.957 | 18.648 | 4.56 | 8.065 | 12.625 | 12.625 | 0.13798 | 0.36119 | 13.8532 | 13.8004 | 6.6298 | 83.8167 | 0.16465 | 5.69 | 5.69 | 32.591 | 549.45 | 927.36 | 841.6852 | 9.2386 | 89.1047 | 695.5676 | 95.3145 | 100.957 | 51.12 | 18.648 | 1.2 | 3.827 | 5.027 | 5.027 | 0.17714 | 0.23871 | 10.6667 | 10.6261 | 9.5181 | 47.8724 | 0.22197 | 5.69 | 7.021 | 104.5473 | 927.36 | 1501.8318 | 1185.3624 | 21.0722 | 65.0495 | 1056.3612 | 90.1031 | SDS-DCAA* | mg/L | 25.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 30.8 | 519 | 1037.0411 | 89.6121 | 778.0205 | 96.0412 | SDS-DCAA* | mg/L | 8.82 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32.3 | 504 | 960.1708 | 89.0508 | 732.0854 | 95.5879 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32.9 | 557 | 1038.1074 | 88.9967 | 797.5537 | 95.8749 | SDS-DCAA* | mg/L | 9.22 | NR | --- | 241.5822 | --- | 96.9507 | 143.0911 | 99.0496 | Total dissolved solids | mg/L | 32.8 | 532 | #VALUE! | 93.266 | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 1.36 | NR | --- | 186.12 | --- | 79.3274 | 115.36 | 92.0076 | Total dissolved solids | mg/L | 33.5 | 567 | 1097.1019 | 88.5274 | 832.051 | 95.9738 | SDS-DCAA* | mg/L | 6.78 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32.8 | 532 | 998.3186 | 88.9562 | 765.1593 | 95.7133
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-08-12 | 9:00 | 1920 | 29.185 | 135.869 | 51.18 | 18.646 | 0 | 14.855 | 3.827 |  | 18.682 | 18.682 | 0.79515 | 0 | 13.5045 | 13.4309 | 7.7502 | 67.1283 | 0.20008 | 8.212 | 5.78 | 35.344 | 309.36 | 298.8845 | 1496.7666 | 1321.8513 | 11.6862 | 88.1747 | 810.3679 | 95.6385 | 135.869 | 117.03 | 18.646 | 9.095 | 9.386 | 18.481 | 18.481 | 0.092924 | 0.49213 | 13.8152 | 13.7398 | 4.1706 | 103.6329 | 0.13258 | 5.78 | 5.78 | 17.94 | 298.8845 | 546.3 | 571.1187 | -4.543 | 93.9977 | 435.0016 | 95.8759 | 117.03 | 100.795 | 18.646 | 4.56 | 8.186 | 12.746 | 12.746 | 0.1396 | 0.35776 | 13.8532 | 13.7776 | 6.5678 | 83.6987 | 0.16461 | 5.78 | 5.78 | 32.5956 | 546.3 | 937.6 | 832.4583 | 11.2139 | 89.0942 | 689.3792 | 95.2717 | 100.795 | 51.18 | 18.646 | 1.2 | 3.827 | 5.027 | 5.027 | 0.17714 | 0.23871 | 10.6667 | 10.6085 | 9.6369 | 47.7046 | 0.22238 | 5.78 | 7.013 | 104.5192 | 937.6 | 1496.7666 | 1198.8221 | 19.9059 | 65.0302 | 1068.211 | 90.2155 | SDS-TCAA* | mg/L | 9.16 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 18 | 570 | 1155.7408 | 94.7059 | 862.8704 | 97.9139 | SDS-TCAA* | mg/L | 3.75 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 22 | 520 | 1001.6049 | 91.791 | 760.8025 | 97.1083 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 16 | 590 | 1116.9141 | 94.1176 | 853.457 | 98.1253 | SDS-TCAA* | mg/L | 4.99 | NR | --- | 152.3378 | --- | 94.5645 | 90.5189 | 98.2766 | Total hardness | mg/L as CaCO3 | 20 | NA | 946.2515 | 95.2381 | 721.1257 | 98.0586 | SDS-TCAA* | mg/L | 1.56 | NR | --- | 123.54 | --- | 82.6132 | 76.12 | 93.4446 | Total hardness | mg/L as CaCO3 | 20 | 560 | 1096.5605 | 93.0556 | 828.2803 | 97.5854 | SDS-TCAA* | mg/L | 4.74 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | NA | 18 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-08-12 | 17:00 | 1928 | 29.193 | 135.219 | 51.075 | 18.642 | 0 | 14.789 | 3.827 |  | 18.616 | 18.616 | 0.79442 | 0 | 13.4445 | 13.3681 | 7.7293 | 66.7757 | 0.20019 | 8.192 | 5.71 | 35.2735 | 308.4 | 298.8763 | 1494.9576 | 1317.539 | 11.8678 | 88.198 | 808.2077 | 95.6356 | 135.219 | 116.617 | 18.642 | 9.029 | 9.326 | 18.355 | 18.355 | 0.092304 | 0.49191 | 13.7149 | 13.6369 | 4.1745 | 103.1015 | 0.13227 | 5.71 | 5.71 | 17.589 | 298.8763 | 546.3 | 571.2056 | -4.559 | 94.115 | 435.041 | 95.9569 | 116.617 | 100.601 | 18.642 | 4.56 | 8.126 | 12.686 | 12.686 | 0.1388 | 0.35945 | 13.8532 | 13.7744 | 6.5784 | 83.3886 | 0.16518 | 5.71 | 5.71 | 32.5928 | 546.3 | 929.92 | 834.5728 | 10.2533 | 89.0949 | 690.4364 | 95.2794 | 100.601 | 51.075 | 18.642 | 1.2 | 3.827 | 5.027 | 5.027 | 0.17714 | 0.23871 | 10.6667 | 10.606 | 9.5482 | 47.6478 | 0.22259 | 5.71 | 7.021 | 104.5083 | 929.92 | 1494.9576 | 1188.7374 | 20.4835 | 65.0329 | 1059.3287 | 90.1345 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 520 | 1054.8068 | 95 | 787.4034 | 97.968 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 430 | 830.3704 | 93.6 | 630.1852 | 97.4611 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 516 | 974.9844 | 94.0299 | 745.4922 | 97.8538 | SDS-MBAA* | mg/L | 1.56 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 14 | 496 | 10.1041 | 99.907 | 7.722 | 96.892 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 550 | 1080.5987 | 94.2857 | 815.2994 | 98.0375 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 1124 | 14 | -1022.8862 | -346.0317 | -504.4431 | 322.82
|  | Maximum permissible turbidity (ntu) | less than 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-08-13 | 1:00 | 1936.0003 | 29.134 | 135.588 | 51.225 | 18.6 | 0 | 14.85 | 3.887 |  | 18.737 | 18.737 | 0.79255 | 0 | 13.5 | 13.4466 | 7.6846 | 67.1219 | 0.20033 | 8.166 | 5.68 | 35.2265 | 309.984 | 299.2843 | 1507.2588 | 1308.098 | 13.2134 | 88.2298 | 803.6911 | 95.6169 | 135.588 | 116.992 | 18.6 | 9.09 | 9.208 | 18.298 | 18.298 | 0.09172 | 0.49678 | 13.8076 | 13.753 | 4.2033 | 103.4867 | 0.1329 | 5.68 | 5.68 | 17.862 | 299.2843 | 545.4 | 577.1002 | -5.8123 | 94.0318 | 438.1923 | 95.9237 | 116.992 | 100.759 | 18.6 | 4.56 | 8.008 | 12.568 | 12.568 | 0.13722 | 0.36283 | 13.8532 | 13.7984 | 6.5879 | 83.6876 | 0.16488 | 5.68 | 5.68 | 32.6076 | 545.4 | 927.36 | 837.3997 | 9.7007 | 89.1048 | 691.3998 | 95.2838 | 100.759 | 51.225 | 18.6 | 1.2 | 3.887 | 5.087 | 5.087 | 0.17955 | 0.2359 | 10.6667 | 10.6245 | 9.4981 | 47.8939 | 0.22183 | 5.68 | 7.006 | 104.5559 | 927.36 | 1507.2588 | 1181.3772 | 21.6208 | 65.0647 | 1054.3686 | 90.0836 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.44 | 3.28 | 6.2936 | 99.3125 | 4.7868 | 90.808 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.328 | 10.8 | 20.9272 | 85.2915 | 15.8636 | 97.9324 | SDS-DBAA* | mg/L | 7.44 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.98 | 6.5 | 11.5672 | 26.8657 | 9.0336 | 89.1516 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.24 | 5.34 | #REF! | #REF! | #REF! | #REF! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.513 | 8.29 | 16.0175 | 83.817 | 12.1537 | 95.7791 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.48 | 5.64 | 10.4601 | 87.7551 | 8.0501 | 94.0373
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 1.1875 | [5 empty] | 1998-08-13 | 9:00 | 1944 | 29.21 | 135.327 | 51.15 | 18.645 | 0 | 14.79 | 3.827 |  | 18.617 | 18.617 | 0.79444 | 0 | 13.4455 | 13.3623 | 7.724 | 66.8695 | 0.19983 | 8.048 | 5.71 | 35.344 | 308.496 | 298.7539 | 1497.1284 | 1316.74 | 12.049 | 88.1695 | 807.747 | 95.6244 | 135.327 | 116.685 | 18.645 | 9.03 | 9.265 | 18.295 | 18.295 | 0.0919 | 0.49358 | 13.7165 | 13.6316 | 4.1812 | 103.1798 | 0.13211 | 5.71 | 5.71 | 17.628 | 298.7539 | 546.3 | 572.7493 | -4.8415 | 94.0995 | 435.7516 | 95.9546 | 116.685 | 100.48 | 18.645 | 4.56 | 8.065 | 12.625 | 12.625 | 0.13798 | 0.36119 | 13.8532 | 13.7674 | 6.5895 | 83.348 | 0.16518 | 5.71 | 5.71 | 32.5781 | 546.3 | 929.28 | 836.7615 | 9.9559 | 89.0953 | 691.5307 | 95.289 | 100.48 | 51.15 | 18.645 | 1.2 | 3.827 | 5.027 | 5.027 | 0.17714 | 0.23871 | 10.6667 | 10.6007 | 9.5412 | 47.6288 | 0.22257 | 5.71 | 7.013 | 104.4716 | 929.28 | 1497.1284 | 1187.9082 | 20.6542 | 65.0309 | 1058.5941 | 90.1311 | SDS-BCAA* | mg/L | 0.77 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.05 | 35.1 | 71.2313 | 93.8596 | 53.1656 | 98.025 | SDS-BCAA* | mg/L | 0.64 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 8.95 | 45.5 | 80.8467 | 63.4694 | 63.1734 | 85.8326 | SDS-BCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.5 | 55.8 | 105.6457 | 95.3271 | 80.7229 | 98.1418 | SDS-BCAA* | mg/L | 1.06 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0 | 36.5 | 70.5958 | 100 | 53.5479 | 100 | SDS-BCAA* | mg/L | BMRL | NR | --- | 27.56 | --- | 83.3333 | 16.96 | 93.75 | Total organic carbon | mg/L | 1.5 | 36.5 | 71.2771 | 92.4242 | 53.8885 | 97.2165 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.57 | 27.7 | 53.043 | 98.5079 | 40.3715 | 98.5881
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-08-13 | 17:00 | 1952 | 29.176 | 135.367 | 51.135 | 18.624 | 0 | 14.908 | 3.826 |  | 18.734 | 18.734 | 0.79577 | 0 | 13.5527 | 13.4824 | 7.7714 | 66.8556 | 0.20166 | 8.033 | 5.71 | 35.2735 | 308.544 | 298.8682 | 1494.9576 | 1325.9641 | 11.3042 | 88.1976 | 812.4161 | 95.6582 | 135.367 | 116.715 | 18.624 | 9.088 | 9.33 | 18.418 | 18.418 | 0.092527 | 0.49343 | 13.8046 | 13.7329 | 4.1827 | 103.2343 | 0.13303 | 5.71 | 5.71 | 17.589 | 298.8682 | 545.85 | 572.8515 | -4.9467 | 94.1148 | 435.8599 | 95.9645 | 116.715 | 100.606 | 18.624 | 4.62 | 8.13 | 12.75 | 12.75 | 0.13925 | 0.36235 | 14.0354 | 13.9626 | 6.5909 | 83.4456 | 0.16733 | 5.71 | 5.71 | 32.5919 | 545.85 | 928.64 | 837.517 | 9.8125 | 89.0949 | 691.6835 | 95.288 | 100.606 | 51.135 | 18.624 | 1.2 | 3.826 | 5.026 | 5.026 | 0.1771 | 0.23876 | 10.6667 | 10.6113 | 9.5349 | 47.7116 | 0.22241 | 5.71 | 7.02 | 104.4069 | 928.64 | 1494.9576 | 1187.1553 | 20.5894 | 65.0659 | 1057.8977 | 90.1307 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.016 | 1.15 | 2.3533 | 96.8627 | 1.7517 | 99.0866 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.816 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.016 | 1.68 | 3.2075 | 97.1831 | 2.4438 | 99.3453 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0 | 1.12 | 2.1662 | 100 | 1.6431 | 100 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.024 | 1.12 | 2.209 | 94.6667 | 1.6645 | 98.5581 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.008 | 1.14 | 2.1974 | 98.5455 | 1.6687 | 99.5206
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 24.6875 | [5 empty] | 1998-08-14 | 1:00 | 1960 | 29.121 | 135.621 | 50.955 | 18.594 | 0 | 14.787 | 3.827 |  | 18.614 | 18.614 | 0.7944 | 0 | 13.4427 | 13.3947 | 7.7431 | 66.9509 | 0.20007 | 8.289 | 5.67 | 35.1325 | 309.792 | 299.2272 | 1508.706 | 1319.6527 | 12.5308 | 88.2589 | 809.4399 | 95.6597 | 135.621 | 116.872 | 18.594 | 9.027 | 9.219 | 18.246 | 18.246 | 0.091583 | 0.49474 | 13.7119 | 13.6629 | 4.1935 | 103.459 | 0.13206 | 5.67 | 5.67 | 17.706 | 299.2272 | 548.1 | 574.8853 | -4.8869 | 94.0828 | 437.0562 | 95.9488 | 116.872 | 100.637 | 18.594 | 4.62 | 8.079 | 12.699 | 12.699 | 0.13857 | 0.36381 | 14.0354 | 13.9853 | 6.6289 | 83.5316 | 0.16743 | 5.67 | 5.67 | 32.6048 | 548.1 | 924.8 | 842.8875 | 8.8573 | 89.1037 | 695.4937 | 95.312 | 100.637 | 50.955 | 18.594 | 1.14 | 3.827 | 4.967 | 4.967 | 0.17594 | 0.22951 | 10.1333 | 10.0972 | 9.4243 | 47.7777 | 0.21134 | 5.67 | 6.976 | 104.5418 | 924.8 | 1508.706 | 1169.1413 | 22.507 | 65.0627 | 1046.9707 | 90.0148 | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.5238 | 3.2764 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 1.7934 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 11 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.0667 | 3.0108 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #DIV/0! | 3.0685 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.6 | 3.0685 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 1.4035 | 4.1155 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-08-14 | 16:25 | 1975.4108 | 29.168 | 134.348 | 50.7 | 17.952 | 0 | 14.185 | 3.767 |  | 17.952 | 17.952 | 0.79016 | 0 | 12.8955 | 12.8316 | 7.5879 | 66.9841 | 0.19156 | 8.33 | 5.75 | 35.673 | 308.784 | 298.8845 | 1507.9824 | 1290.0326 | 14.4531 | 88.0646 | 794.4585 | 95.5098 | 134.348 | 115.905 | 17.952 | 8.425 | 9.995 | 18.42 | 18.42 | 0.094751 | 0.45738 | 12.7975 | 12.7341 | 3.9982 | 103.1763 | 0.12342 | 5.75 | 5.75 | 17.6085 | 298.8845 | 545.85 | 535.978 | 1.8085 | 94.1086 | 417.4313 | 95.7817 | 115.905 | 100.174 | 17.952 | 4.56 | 8.795 | 13.355 | 13.355 | 0.14772 | 0.34145 | 13.8532 | 13.7845 | 6.4627 | 83.6248 | 0.16484 | 5.75 | 5.75 | 32.626 | 545.85 | 951.68 | 811.9446 | 14.683 | 89.0841 | 678.8973 | 95.1943 | 100.174 | 50.7 | 17.952 | 1.2 | 3.767 | 4.967 | 4.967 | 0.17474 | 0.24159 | 10.6667 | 10.6138 | 9.8182 | 47.6668 | 0.22267 | 5.75 | 7.021 | 104.7579 | 951.68 | 1507.9824 | 1221.472 | 18.9996 | 64.9504 | 1086.576 | 90.3589 | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 3.02 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | 6.36 | --- | 0 | 6.36 | -1.3965e-14 | [8 empty] | SDS-DCBAA | mg/L | 6.36 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.28 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-08-14 | 17:00 | 1976 | 29.168 | 134.348 | 50.7 | 18.079 | 0 | 14.185 | 3.767 |  | 17.952 | 17.952 | 0.79016 | 0 | 12.8955 | 12.8316 | 7.6028 | 66.8422 | 0.19197 | 8.33 | 5.75 | 35.156 | 308.784 | 298.8845 | 1515.942 | 1291.9794 | 14.7738 | 88.2376 | 795.4319 | 95.5803 | 134.348 | 115.905 | 18.079 | 8.425 | 9.995 | 18.42 | 18.42 | 0.094751 | 0.45738 | 12.7975 | 12.7341 | 3.9982 | 103.0493 | 0.12357 | 5.75 | 5.75 | 17.6085 | 298.8845 | 545.85 | 535.978 | 1.8085 | 94.1086 | 417.4313 | 95.7817 | 115.905 | 100.385 | 18.079 | 4.56 | 8.795 | 13.355 | 13.355 | 0.14772 | 0.34145 | 13.8532 | 13.7845 | 6.4625 | 83.6035 | 0.16488 | 5.75 | 5.75 | 32.6398 | 545.85 | 951.68 | 811.9374 | 14.6838 | 89.0795 | 678.8937 | 95.1922 | 100.385 | 50.7 | 18.079 | 1.2 | 3.767 | 4.967 | 4.967 | 0.17474 | 0.24159 | 10.6667 | 10.6138 | 9.8171 | 47.6464 | 0.22276 | 5.75 | 7.021 | 104.8534 | 951.68 | 1515.942 | 1221.4416 | 19.4269 | 64.9184 | 1086.5608 | 90.35 | SDS-HAA5 | mg/L | 34.36 | 0 | --- | -156.5289 | --- | #DIV/0! | -78.2644 | 143.9024 | [8 empty] | SDS-HAA5 | mg/L | 12.57 | 0 | --- | -50.28 | --- | #DIV/0! | -25.14 | 150 | [8 empty] | SDS-HAA5 | mg/L | 13.11 | 0 | --- | -55.89 | --- | #DIV/0! | -27.945 | 146.9136 | [8 empty] | SDS-HAA5 | mg/L | 2.92 | NR | --- | 438.3644 | --- | 96.4084 | 259.8322 | 98.8762 | [8 empty] | SDS-HAA5 | mg/L | 15.77 | NR | --- | 329.62 | --- | 79.9211 | 204.08 | 92.2726 | [8 empty] | SDS-HAA5 | mg/L | 11.52 | 0 | --- | -52.48 | --- | #DIV/0! | -26.24 | 143.9024
|  | Field 2-2b: Manufacturer Reported Membrane Characteristics1 |  | maximum system recycle flow rates. | [6 empty] | 1998-08-15 | 1:04 | 1984.0722 | 29.163 | 132.191 | 51.712 | 17.727 | 0 | 14.13 | 3.647 |  | 17.777 | 17.777 | 0.79485 | 0 | 12.8455 | 12.7837 | 7.7263 | 66.4982 | 0.19224 | 8.183 | 5.61 | 36.3075 | 310.512 | 299.3578 | 1529.6904 | 1318.5242 | 13.8045 | 87.8715 | 808.941 | 95.5117 | 132.191 | 113.805 | 17.727 | 8.37 | 9.874 | 18.244 | 18.244 | 0.093761 | 0.45878 | 12.7139 | 12.6528 | 4.0061 | 101.2649 | 0.12495 | 5.61 | 5.61 | 17.9985 | 299.3578 | 551.7 | 537.8606 | 2.5085 | 93.9876 | 418.6092 | 95.7004 | 113.805 | 99.238 | 17.727 | 4.56 | 8.674 | 13.234 | 13.234 | 0.14611 | 0.34457 | 13.8532 | 13.7866 | 6.554 | 82.2405 | 0.16764 | 5.61 | 5.61 | 32.717 | 551.7 | 979.84 | 824.534 | 15.8501 | 89.0709 | 688.117 | 95.2454 | 99.238 | 51.712 | 17.727 | 1.2 | 3.647 | 4.847 | 4.847 | 0.16994 | 0.24758 | 10.6667 | 10.6154 | 10.1833 | 47.5647 | 0.22318 | 5.61 | 6.873 | 105.3788 | 979.84 | 1529.6904 | 1267.5706 | 17.1355 | 64.7984 | 1123.7053 | 90.6222 | SDS-HAA6 | mg/L | 35.13 | 0 | --- | -160.0367 | --- | #DIV/0! | -80.0183 | 143.9024 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 13.21 | 0 | --- | -52.84 | --- | #DIV/0! | -26.42 | 150 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 13.11 | 0 | --- | -55.89 | --- | #DIV/0! | -27.945 | 146.9136 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 2.92 | NR | --- | 439.8089 | --- | 96.4198 | 260.6844 | 98.8799 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 16.83 | NR | --- | 357.18 | --- | 80.1767 | 221.04 | 92.386 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 11.52 | 0 | --- | -52.48 | --- | #DIV/0! | -26.24 | 143.9024 | Stage 3 Operating Parameters During Sample Collection
|  | General Information | [8 empty] | 1998-08-15 | 1:09 | 1984.1508 | 29.163 | 132.191 | 51.712 | 18.177 | 0 | 14.13 | 3.647 |  | 17.777 | 17.777 | 0.79485 | 0 | 12.8455 | 12.7837 | 7.727 | 66.0475 | 0.19355 | 8.183 | 5.68 | 36.284 | 310.512 | 299.3578 | 1529.6904 | 1318.6153 | 13.7986 | 87.8794 | 808.9865 | 95.5149 | 132.191 | 113.805 | 18.177 | 8.37 | 9.874 | 18.244 | 18.244 | 0.093761 | 0.45878 | 12.7139 | 12.6528 | 4.0061 | 100.8149 | 0.12551 | 5.68 | 5.68 | 17.9985 | 299.3578 | 551.7 | 537.8606 | 2.5085 | 93.9876 | 418.6092 | 95.7004 | 113.805 | 100.934 | 18.177 | 4.5 | 8.614 | 13.114 | 13.114 | 0.14491 | 0.34314 | 13.6709 | 13.6052 | 6.5454 | 82.6471 | 0.16462 | 5.68 | 5.68 | 32.7161 | 551.7 | 979.84 | 822.82 | 16.0251 | 89.0712 | 687.26 | 95.2396 | 100.934 | 51.712 | 18.177 | 1.26 | 3.647 | 4.907 | 4.907 | 0.17114 | 0.25678 | 11.2 | 11.1462 | 10.2552 | 47.8908 | 0.23274 | 5.68 | 6.873 | 105.3757 | 979.84 | 1529.6904 | 1281.9582 | 16.1949 | 64.7994 | 1130.8991 | 90.6821 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.27 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.25 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.26 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.28 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.24 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.28
|  | Membrane manufacturer | FLUID SYSTEMS CORP. | Summary of the Stage and System Flow Rates | [6 empty] | 1998-08-15 | 9:00 | 1992 | 29.41 | 132.285 | 51.292 | 17.841 | 0 | 14.07 | 3.647 |  | 17.717 | 17.717 | 0.79415 | 0 | 12.7909 | 12.6368 | 7.6574 | 66.2901 | 0.19063 | 8.111 | 5.67 | 34.8035 | 293.04 | 296.2406 | 1450.818 | 1304.8561 | 10.0607 | 88.2516 | 800.5484 | 95.6525 | 132.285 | 113.632 | 17.841 | 8.37 | 9.873 | 18.243 | 18.243 | 0.093754 | 0.45881 | 12.7139 | 12.5608 | 3.9691 | 101.1484 | 0.12418 | 5.67 | 5.67 | 17.4915 | 296.2406 | 521.55 | 532.5549 | -2.11 | 94.0955 | 414.3978 | 95.7791 | 113.632 | 98.932 | 17.841 | 4.56 | 8.733 | 13.293 | 13.293 | 0.14689 | 0.34304 | 13.8532 | 13.6863 | 6.1676 | 82.2734 | 0.16635 | 5.67 | 5.67 | 32.4778 | 521.55 | 938.24 | 776.9226 | 17.1936 | 89.0367 | 649.2363 | 94.9975 | 98.932 | 51.292 | 17.841 | 1.14 | 3.647 | 4.787 | 4.787 | 0.16874 | 0.23814 | 10.1333 | 10.0113 | 9.6472 | 47.6238 | 0.21022 | 5.67 | 6.958 | 103.9186 | 938.24 | 1450.818 | 1199.0369 | 17.3544 | 64.9209 | 1068.6385 | 90.2756 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.2 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.21 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.21 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.21 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.21
|  | Membrane trade name | FLUID SYSTEMS | Influent flow rate to stage 1, QI-s(1) (gpm) | 24.6875 | [5 empty] | 1998-08-15 | 17:00 | 2000 | 29.389 | 133.169 | 51.51 | 17.992 | 0 | 14.252 | 3.646 |  | 17.898 | 17.898 | 0.79629 | 0 | 12.9564 | 12.8082 | 7.741 | 66.6065 | 0.1923 | 8.973 | 5.62 | 35.25 | 298.944 | 297.2606 | 1469.2698 | 1321.4449 | 10.0611 | 88.1417 | 809.3527 | 95.6447 | 133.169 | 114.36 | 17.992 | 8.552 | 9.508 | 18.06 | 18.06 | 0.091927 | 0.47353 | 12.9904 | 12.8419 | 4.0553 | 101.7172 | 0.12625 | 5.62 | 5.62 | 17.5305 | 297.2606 | 533.7 | 548.8648 | -2.8414 | 94.1027 | 423.0627 | 95.8563 | 114.36 | 99.233 | 17.992 | 4.56 | 8.368 | 12.928 | 12.928 | 0.14202 | 0.35272 | 13.8532 | 13.6948 | 6.3768 | 82.4277 | 0.16614 | 5.62 | 5.62 | 32.5597 | 533.7 | 940.16 | 806.7879 | 14.1861 | 89.0467 | 670.244 | 95.1421 | 99.233 | 51.51 | 17.992 | 1.14 | 3.646 | 4.786 | 4.786 | 0.1687 | 0.23819 | 10.1333 | 10.0175 | 9.6653 | 47.7142 | 0.20995 | 5.62 | 7.007 | 104.3059 | 940.16 | 1469.2698 | 1201.5077 | 18.2242 | 64.911 | 1070.8338 | 90.2594 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.49 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.85 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.74 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.38 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.97 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.38
|  | Membrane element model number | 2540 TFCS / 4921 TFCS | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.875 | [5 empty] | 1998-08-16 | 1:00 | 2008 | 29.316 | 133.839 | 52.11 | 18.07 | 0 | 14.365 | 3.707 |  | 18.072 | 18.072 | 0.79488 | 0 | 13.0591 | 12.9377 | 7.7189 | 67.1856 | 0.19257 | 8.445 | 5.62 | 34.7565 | 299.712 | 297.5218 | 1474.6968 | 1315.7637 | 10.7773 | 88.318 | 806.6427 | 95.6912 | 133.839 | 115.027 | 18.07 | 8.665 | 9.398 | 18.063 | 18.063 | 0.09157 | 0.47971 | 13.162 | 13.0397 | 4.0918 | 102.2712 | 0.1275 | 5.62 | 5.62 | 17.4525 | 297.5218 | 532.8 | 555.7469 | -4.3069 | 94.134 | 426.6343 | 95.9093 | 115.027 | 99.751 | 18.07 | 4.56 | 8.258 | 12.818 | 12.818 | 0.14056 | 0.35575 | 13.8532 | 13.7244 | 6.3834 | 82.9356 | 0.16548 | 5.62 | 5.62 | 32.5735 | 532.8 | 935.68 | 809.021 | 13.5366 | 89.0517 | 670.9105 | 95.1449 | 99.751 | 52.11 | 18.07 | 1.14 | 3.707 | 4.847 | 4.847 | 0.17114 | 0.2352 | 10.1333 | 10.0391 | 9.5945 | 48.266 | 0.208 | 5.62 | 6.941 | 104.1011 | 935.68 | 1474.6968 | 1191.4124 | 19.2097 | 65.0106 | 1063.5462 | 90.2119 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Molecular weight cutoff (Daltons) | 200 | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 14.8125 | [5 empty] | 1998-08-16 | 9:00 | 2016 | 29.312 | 133.832 | 52.192 | 18.148 | 0 | 14.429 | 3.588 |  | 18.017 | 18.017 | 0.80085 | 0 | 13.1173 | 12.9969 | 7.9053 | 66.9587 | 0.1941 | 8.505 | 5.68 | 34.827 | 299.04 | 297.3994 | 1472.1642 | 1353.3237 | 8.0725 | 88.2895 | 825.3615 | 95.7804 | 133.832 | 114.93 | 18.148 | 8.609 | 9.634 | 18.243 | 18.243 | 0.092957 | 0.47191 | 13.077 | 12.9569 | 4.0489 | 102.1841 | 0.1268 | 5.68 | 5.68 | 17.55 | 297.3994 | 533.7 | 547.4744 | -2.5809 | 94.0988 | 422.4369 | 95.8455 | 114.93 | 99.638 | 18.148 | 4.56 | 8.374 | 12.934 | 12.934 | 0.1421 | 0.35256 | 13.8532 | 13.726 | 6.3759 | 82.7601 | 0.16585 | 5.68 | 5.68 | 32.5588 | 533.7 | 928.64 | 806.5927 | 13.1426 | 89.0522 | 670.1464 | 95.1415 | 99.638 | 52.192 | 18.148 | 1.26 | 3.588 | 4.848 | 4.848 | 0.16878 | 0.2599 | 11.2 | 11.0972 | 9.6959 | 48.0711 | 0.23085 | 5.68 | 6.957 | 103.8679 | 928.64 | 1472.1642 | 1218.2757 | 17.2459 | 65.0746 | 1073.4578 | 90.324 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Influent flow rate to stage 2, QI-s(2) (gpm) | 14.8125 | [5 empty] | 1998-08-16 | 17:00 | 2024 | 29.423 | 133.363 | 51.952 | 18.183 | 0 | 14.427 | 3.647 |  | 18.074 | 18.074 | 0.79822 | 0 | 13.1155 | 12.9525 | 7.8133 | 66.6612 | 0.1943 | 8.147 | 5.65 | 33.605 | 290.592 | 295.9795 | 1425.492 | 1333.8948 | 6.4257 | 88.6462 | 814.9372 | 95.8764 | 133.363 | 114.787 | 18.183 | 8.667 | 9.58 | 18.247 | 18.247 | 0.09279 | 0.47498 | 13.1651 | 13.0015 | 4.048 | 101.844 | 0.12766 | 5.65 | 5.65 | 17.2575 | 295.9795 | 517.95 | 548.1386 | -5.8285 | 94.1694 | 422.059 | 95.9111 | 114.787 | 99.661 | 18.183 | 4.56 | 4.85 | 9.41 | 9.41 | 0.095101 | 0.48459 | 13.8532 | 13.681 | 7.1376 | 81.9034 | 0.16704 | 5.65 | 5.65 | 32.43 | 517.95 | 895.36 | 974.4389 | -8.8321 | 89.0432 | 746.1945 | 95.6539 | 99.661 | 51.952 | 18.183 | 1.2 | 3.647 | 4.847 | 4.847 | 0.16994 | 0.24758 | 10.6667 | 10.5341 | 9.2287 | 48.3948 | 0.21767 | 5.65 | 7.021 | 102.8738 | 895.36 | 1425.492 | 1156.1177 | 18.8969 | 65.2429 | 1025.7389 | 89.9708 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-12 | CI-s3-12 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-14 | CI-s3-14 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-16 | CI-s3-16 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-18 | CI-s3-18 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-20 | CI-s3-20 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-18 (dup) | CI-s3-18 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.9375 | [5 empty] | 1998-08-17 | 1:00 | 2032 | 29.393 | 133.672 | 52.267 | 18.097 | 0 | 14.547 | 3.647 |  | 18.194 | 18.194 | 0.79955 | 0 | 13.2245 | 13.0718 | 7.8745 | 66.998 | 0.19511 | 8.458 | 5.66 | 33.5345 | 293.76 | 296.5099 | 1443.2202 | 1345.4552 | 6.7741 | 88.6903 | 820.9826 | 95.9153 | 133.672 | 114.87 | 18.097 | 8.667 | 9.754 | 18.421 | 18.421 | 0.093951 | 0.4705 | 13.1651 | 13.013 | 4.0349 | 102.1391 | 0.1274 | 5.66 | 5.66 | 17.1405 | 296.5099 | 521.55 | 544.746 | -4.4475 | 94.2192 | 420.628 | 95.925 | 114.87 | 99.661 | 18.097 | 4.62 | 4.91 | 9.53 | 9.53 | 0.096302 | 0.48478 | 14.0354 | 13.8733 | 7.1919 | 81.9766 | 0.16924 | 5.66 | 5.66 | 32.4604 | 521.55 | 892.16 | 981.7525 | -10.0422 | 89.0525 | 751.6512 | 95.6815 | 99.661 | 52.267 | 18.097 | 1.26 | 3.647 | 4.907 | 4.907 | 0.17114 | 0.25678 | 11.2 | 11.0706 | 9.2553 | 48.6117 | 0.22774 | 5.66 | 6.98 | 102.9639 | 892.16 | 1443.2202 | 1164.8189 | 19.2903 | 65.2747 | 1028.4895 | 89.9888 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 157.1595 | 78.5797 |  |  |  | Sampling date | MM/DD/YY | 1998-08-04 | 1998-08-04 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 429.5943 | 214.7971 |  |  |  | Sampling date | MM/DD/YY | 1998-08-18 | 1998-08-18 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 411.8993 | 205.9497 |  |  |  | Sampling date | MM/DD/YY | 1998-09-01 | 1998-09-01 | --- | --- | --- | --- | Qp/QT (THM4), % | 101.5118 | 167.0032 |  | Qp/QT (HAA5), % | 34.8303 | 69.2779 |  |  |  | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | Qp/QT (THM4), % | 49.8244 | 84.0027 |  | Qp/QT (HAA5), % | 39.0951 | 82.1093 |  |  |  | Sampling date | MM/DD/YY | 1998-09-30 | 1998-09-30 | --- | --- | --- | --- | Qp/QT (THM4), % | 661.9472 | 330.9736 |  | Qp/QT (HAA5), % | 468.75 | 234.375 |  |  |  | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | ---
|  | Membrane hydrophobicity | HYDRPHILIC | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 9.875 | [5 empty] | 1998-08-17 | 9:00 | 2040 | 29.491 | 133.055 | 51.765 | 18.219 | 0 | 14.429 | 3.707 |  | 18.136 | 18.136 | 0.7956 | 0 | 13.1173 | 12.9283 | 7.7248 | 66.4662 | 0.19451 | 8.169 | 5.66 | 32.3125 | 282.912 | 294.5107 | 1387.1412 | 1315.0821 | 5.1948 | 89.0284 | 804.7964 | 95.985 | 133.055 | 114.577 | 18.219 | 8.669 | 9.689 | 18.358 | 18.358 | 0.093524 | 0.47222 | 13.1681 | 12.9784 | 4.0239 | 101.5731 | 0.12777 | 5.66 | 5.66 | 16.497 | 294.5107 | 502.2 | 543.2568 | -8.1754 | 94.3985 | 418.8838 | 96.0617 | 114.577 | 99.413 | 18.219 | 4.56 | 4.91 | 9.47 | 9.47 | 0.095902 | 0.48152 | 13.8532 | 13.6536 | 6.881 | 81.895 | 0.16672 | 5.66 | 5.66 | 32.2994 | 502.2 | 861.44 | 938.6047 | -8.9576 | 89.0329 | 720.4023 | 95.5165 | 99.413 | 51.765 | 18.219 | 1.2 | 3.707 | 4.907 | 4.907 | 0.17234 | 0.24455 | 10.6667 | 10.513 | 8.8238 | 48.5462 | 0.21656 | 5.66 | 6.957 | 101.9811 | 861.44 | 1387.1412 | 1107.2859 | 20.175 | 65.3727 | 984.3629 | 89.6399 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | #VALUE! |  |  |  | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | 108.6541 | 89.7186 |  |  |  | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 83.3011 | 37.9943 |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | NA | NA |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Influent flow rate to stage 3, QI-s(3) (gpm) | 9.875 | [5 empty] | 1998-08-17 | 17:00 | 2048 | 29.512 | 133.209 | 51.885 | 18.205 | 0 | 14.43 | 3.646 |  | 18.076 | 18.076 | 0.7983 | 0 | 13.1182 | 12.9211 | 7.8181 | 66.5239 | 0.19423 | 8.214 | 5.66 | 32.336 | 283.584 | 294.7882 | 1387.1412 | 1333.5113 | 3.8662 | 89.0308 | 814.1497 | 96.0282 | 133.209 | 114.585 | 18.205 | 8.61 | 9.573 | 18.183 | 18.183 | 0.092554 | 0.47352 | 13.0785 | 12.882 | 4.029 | 101.663 | 0.12671 | 5.66 | 5.66 | 16.8675 | 294.7882 | 501.75 | 544.7513 | -8.5703 | 94.2781 | 419.7697 | 95.9817 | 114.585 | 99.422 | 18.205 | 4.62 | 4.85 | 9.47 | 9.47 | 0.095501 | 0.48786 | 14.0354 | 13.8246 | 6.9305 | 81.868 | 0.16886 | 5.66 | 5.66 | 32.2984 | 501.75 | 866.56 | 948.9389 | -9.5064 | 89.0435 | 725.3445 | 95.5472 | 99.422 | 51.885 | 18.205 | 1.2 | 3.646 | 4.846 | 4.846 | 0.1699 | 0.24763 | 10.6667 | 10.5065 | 8.9046 | 48.5439 | 0.21643 | 5.66 | 6.957 | 101.9304 | 866.56 | 1387.1412 | 1118.2209 | 19.3867 | 65.4225 | 992.3904 | 89.7288 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 1721 | 1721 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 2070 | 2070 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 2401 | 2401 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 2815 | 2815 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 47.2652 | 25.8115 |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 3087 | 3087 | --- | --- | --- | --- | SDS-HAA5b, mg/L | NA | NA |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 2815 | 2815 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 4.9375 | [5 empty] | 1998-08-18 | 1:00 | 2056 | 29.448 | 133.343 | 52.252 | 18.34 | 0 | 14.545 | 3.647 |  | 18.192 | 18.192 | 0.79953 | 0 | 13.2227 | 13.0488 | 7.8629 | 66.5946 | 0.19594 | 8.325 | 5.64 | 32.289 | 284.4 | 294.9024 | 1391.8446 | 1342.2597 | 3.5625 | 89.051 | 818.581 | 96.0555 | 133.343 | 114.562 | 18.34 | 8.665 | 9.516 | 18.181 | 18.181 | 0.092357 | 0.4766 | 13.162 | 12.9889 | 4.0476 | 101.5649 | 0.12789 | 5.64 | 5.64 | 16.77 | 294.9024 | 504.9 | 548.1619 | -8.5684 | 94.3134 | 421.5321 | 96.0217 | 114.562 | 99.593 | 18.34 | 4.56 | 4.72 | 9.28 | 9.28 | 0.093367 | 0.49138 | 13.8532 | 13.6709 | 7.0087 | 81.7288 | 0.16727 | 5.64 | 5.64 | 32.3122 | 504.9 | 824.7968 | 961.4678 | -16.5703 | 89.0431 | 733.1839 | 95.5929 | 99.593 | 52.252 | 18.34 | 1.32 | 3.647 | 4.967 | 4.967 | 0.17234 | 0.26575 | 11.7333 | 11.579 | 8.5363 | 49.0462 | 0.23608 | 5.64 | 6.941 | 101.9725 | 824.7968 | 1391.8446 | 1086.4168 | 21.9441 | 65.4216 | 955.6068 | 89.329 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.72 | 6.05 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.57 | 6.27 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.41 | 6.07 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.55 | 6.25 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.54 | 6.01 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | NA | NA |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.7 | 6.45 | --- | --- | --- | ---
|  | Design Parameters |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 4.9375 | [5 empty] | 1998-08-18 | 9:00 | 2064 | 29.529 | 132.982 | 52.252 | 18.222 | 0 | 14.435 | 3.587 |  | 18.022 | 18.022 | 0.80097 | 0 | 13.1227 | 12.9191 | 7.8996 | 66.4954 | 0.19429 | 8.273 | 5.69 | 32.4065 | 283.872 | 294.6658 | 1388.5884 | 1350.0637 | 2.7744 | 89.0023 | 822.3647 | 96.0594 | 132.982 | 114.285 | 18.222 | 8.615 | 9.74 | 18.355 | 18.355 | 0.093684 | 0.46935 | 13.0861 | 12.883 | 4.006 | 101.4055 | 0.12704 | 5.69 | 5.69 | 16.9065 | 294.6658 | 502.2 | 540.343 | -7.5952 | 94.2625 | 417.5044 | 95.9506 | 114.285 | 99.328 | 18.222 | 4.62 | 4.76 | 9.38 | 9.38 | 0.094301 | 0.49254 | 14.0354 | 13.8177 | 6.9794 | 81.6051 | 0.16932 | 5.69 | 5.69 | 32.3012 | 502.2 | 822.8672 | 958.2782 | -16.456 | 89.038 | 730.2391 | 95.5766 | 99.328 | 52.252 | 18.222 | 1.2 | 3.587 | 4.787 | 4.787 | 0.16754 | 0.25068 | 10.6667 | 10.5012 | 8.414 | 49.154 | 0.21364 | 5.69 | 6.96 | 102.04 | 822.8672 | 1388.5884 | 1064.0137 | 23.3744 | 65.3709 | 943.4405 | 89.1843 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | #VALUE! |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | 5.4102 | 3.3433 |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | 3.5119 | 1.1878 |  | SDS-CDb, mg/L | 4.2415 | 1.3166 |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | NA | NA |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-08-18 | 12:47 | 2067.7844 | 29.576 | 132.874 | 51.93 | 18.309 | 0 | 15.056 | 3.589 |  | 18.645 | 18.645 | 0.80751 | 0 | 13.6873 | 13.4562 | 8.1005 | 65.9925 | 0.20391 | 8.308 | 5.789 | 33.37 | 283.44 | 294.8861 | 1379.592 | 1391.9566 | -0.89625 | 88.6838 | 843.4213 | 96.0435 | 132.874 | 114.427 | 18.309 | 8.615 | 9.329 | 17.944 | 17.944 | 0.090943 | 0.4801 | 13.0861 | 12.8652 | 4.0613 | 101.2802 | 0.12703 | 5.789 | 5.789 | 17.043 | 294.8861 | 503.55 | 551.4643 | -9.5153 | 94.2205 | 423.1752 | 95.9726 | 114.427 | 98.925 | 18.309 | 4.684 | 4.645 | 9.329 | 9.329 | 0.093194 | 0.50209 | 14.2299 | 13.9896 | 7.0887 | 81.2783 | 0.17212 | 5.789 | 5.789 | 32.2892 | 503.55 | 870.1875 | 978.7675 | -12.4778 | 89.0503 | 741.1588 | 95.6434 | 98.925 | 51.93 | 18.309 | 1.207 | 3.589 | 4.796 | 4.796 | 0.16776 | 0.25167 | 10.7289 | 10.5478 | 8.9365 | 48.182 | 0.21891 | 5.789 | 6.973 | 105.1805 | 870.1875 | 1379.592 | 1127.4635 | 18.2756 | 64.3318 | 998.8255 | 89.4696 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | 4.7237 |  |  |  | Alkalinity | mg/L as CaCO3 | 26 | 136 | 176.1216 | 48 | 156.0608 | 83.3398 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 146 | 184.7945 | 51.7241 | 165.3973 | 83.0711 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 156 | 199.8754 | 41.6667 | 177.9377 | 84.2642 | TOCb, mg/L | NA | NA |  | TOCb, mg/L | 13.4372 | 8.9246 |  |  |  | Alkalinity | mg/L as CaCO3 | 24 | 116 | 151.1167 | 36.8421 | 133.5584 | 82.0303 | TOCb, mg/L | 12.3762 | 7.2836 |  | TOCb, mg/L | 13.9748 | 7.5657 |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 124 | 154.8936 | 33.3333 | 139.4468 | 79.9207 | TOCb, mg/L | NA | NA |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 26 | 110 | 142.0631 | 27.7778 | 126.0315 | 79.3702
|  | Active membrane area of membrane element used, A (ft2) | 27 | System concentrate waste flow rate, QW-sys (gpm) | 4.9375 | [5 empty] | 1998-08-18 | 13:09 | 2068.1531 | 29.563 | 133.055 | 52.035 | 18.222 | 0 | 14.633 | 3.648 |  | 18.281 | 18.281 | 0.80045 | 0 | 13.3027 | 13.0832 | 7.8722 | 66.4508 | 0.19689 | 8.25 | 5.788 | 32.9705 | 283.2 | 294.8861 | 1378.3765 | 1345.4921 | 2.3857 | 88.8192 | 820.1891 | 95.9801 | 133.055 | 114.337 | 18.222 | 8.732 | 9.563 | 18.295 | 18.295 | 0.092894 | 0.47729 | 13.2638 | 13.0449 | 4.0466 | 101.4274 | 0.12861 | 5.788 | 5.788 | 17.0625 | 294.8861 | 503.55 | 548.5675 | -8.94 | 94.2139 | 421.7268 | 95.9541 | 114.337 | 98.947 | 18.222 | 4.7 | 4.863 | 9.563 | 9.563 | 0.096208 | 0.49148 | 14.2785 | 14.0428 | 6.99 | 81.43 | 0.17245 | 5.788 | 5.788 | 32.2874 | 503.55 | 870.415 | 959.0166 | -10.1792 | 89.0509 | 731.2833 | 95.5848 | 98.947 | 52.035 | 18.222 | 1.201 | 3.648 | 4.849 | 4.849 | 0.17 | 0.24768 | 10.6756 | 10.4994 | 8.9144 | 48.3546 | 0.21713 | 5.788 | 6.954 | 104.9789 | 870.415 | 1378.3765 | 1122.413 | 18.5699 | 64.4002 | 996.414 | 89.4643 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | 0.1501 |  |  |  | Total dissolved solids | mg/L | 97.8 | 932 | 1236.2675 | 67.0152 | 1084.1337 | 90.979 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 105 | 870 | 1121.5068 | 64.4068 | 995.7534 | 89.4552 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 107.5 | 984 | 1284.4433 | 64.0468 | 1134.2217 | 90.5221 | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 105.5 | 943 | 1262.6767 | 64.4781 | 1102.8383 | 90.4338 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 99 | 925 | 1190.8138 | 66.0959 | 1057.9069 | 90.6419 | UV254 b, cm-1 | NA | NA |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 105.5 | 943 | 1262.6767 | 64.4781 | 1102.8383 | 90.4338
|  | Design flux, FW (gfd) | 17.9 | System permeate flow rate, Qp-sys (gpm) | 19.75 | [5 empty] | 1998-08-18 | 21:00 | 2076 | 29.491 | 133.283 | 52.162 | 18.273 | 0 | 14.569 | 3.647 |  | 18.216 | 18.216 | 0.79979 | 0 | 13.2445 | 13.0537 | 7.8767 | 66.5728 | 0.19608 | 7.962 | 5.776 | 32.2655 | 285.216 | 295.0493 | 1361.3611 | 1344.8154 | 1.2154 | 89.0644 | 819.9323 | 96.0649 | 133.283 | 114.832 | 18.273 | 8.663 | 9.635 | 18.298 | 18.298 | 0.093144 | 0.47344 | 13.159 | 12.9694 | 4.0338 | 101.7507 | 0.12746 | 5.776 | 5.776 | 16.77 | 295.0493 | 504.9 | 545.2551 | -7.9927 | 94.3162 | 420.1522 | 96.0086 | 114.832 | 99.142 | 18.273 | 4.699 | 4.936 | 9.635 | 9.635 | 0.097175 | 0.4877 | 14.2754 | 14.0698 | 6.9754 | 81.7386 | 0.17213 | 5.776 | 5.776 | 32.3122 | 504.9 | 879.515 | 954.7967 | -8.5595 | 89.0485 | 729.8483 | 95.5727 | 99.142 | 52.162 | 18.273 | 1.207 | 3.647 | 4.854 | 4.854 | 0.17008 | 0.24866 | 10.7289 | 10.5743 | 9.0292 | 48.3498 | 0.2187 | 5.776 | 6.943 | 104.7917 | 879.515 | 1361.3611 | 1135.9151 | 16.5603 | 64.4833 | 1007.715 | 89.6011 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 64 | 1020 | 1368.693 | 81.1765 | 1194.3465 | 94.6414 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 54 | 1267 | 1665.7945 | 79.8507 | 1466.3973 | 96.3175 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 56 | 1080 | 1431.0028 | 79.4118 | 1255.5014 | 95.5396 | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | 8.5573 | 9.1084 |  |  |  | Total hardness | mg/L as CaCO3 | 56 | 1140 | 1553.7666 | 80.9524 | 1346.8833 | 95.8423 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 60 | 1090 | 1421.4628 | 79.1667 | 1255.7314 | 95.2219 | Bromideb, mg/L | NA | NA |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 58 | 1124 | 1530.8959 | 79.7203 | 1327.4479 | 95.6307
|  | Net driving pressure at the design flux, NDP (psi) | 109 | System feed flow rate, QF-sys (gpm) | 24.6875 | [5 empty] | 1998-08-19 | 5:00 | 2084 | 29.448 | 133.256 | 52.335 | 18.211 | 0 | 14.637 | 3.588 |  | 18.225 | 18.225 | 0.80313 | 0 | 13.3064 | 13.1313 | 7.9928 | 66.5917 | 0.19719 | 8.185 | 5.778 | 32.2185 | 285.936 | 295.1635 | 1360.1455 | 1367.8297 | -0.56495 | 89.0845 | 831.4966 | 96.1252 | 133.256 | 114.45 | 18.211 | 8.724 | 9.699 | 18.423 | 18.423 | 0.093774 | 0.47354 | 13.2516 | 13.0773 | 4.0374 | 101.6046 | 0.12871 | 5.778 | 5.778 | 16.6725 | 295.1635 | 504 | 545.659 | -8.2657 | 94.3514 | 420.4113 | 96.0342 | 114.45 | 99.262 | 18.211 | 4.699 | 5 | 9.699 | 9.699 | 0.098029 | 0.48448 | 14.2754 | 14.0876 | 6.9334 | 81.7116 | 0.17241 | 5.778 | 5.778 | 32.3095 | 504 | 882.4725 | 947.2948 | -7.3455 | 89.0537 | 725.6474 | 95.5475 | 99.262 | 52.335 | 18.211 | 1.214 | 3.588 | 4.802 | 4.802 | 0.16786 | 0.25281 | 10.7911 | 10.6492 | 9.0926 | 48.4949 | 0.21959 | 5.778 | 6.914 | 104.7802 | 882.4725 | 1360.1455 | 1145.6047 | 15.7734 | 64.501 | 1014.0386 | 89.667 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | 24.8545 |  |  |  | Calcium hardness | mg/L as CaCO3 | 58 | 970 | 1302.6444 | 81.875 | 1136.3222 | 94.8958 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 48 | 1094 | 1437.8904 | 80.8 | 1265.9452 | 96.2084 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 54 | 1070 | 1418.2606 | 79.8507 | 1244.1303 | 95.6596 | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | 30.3373 | 22.7589 |  |  |  | Calcium hardness | mg/L as CaCO3 | 52 | 1018 | 1386.7256 | 79.845 | 1202.3628 | 95.6752 | Alkb, mg/L CaCO3 | 30.0422 | 21.8394 |  | Alkb, mg/L CaCO3 | 32.6172 | 22.2938 |  |  |  | Calcium hardness | mg/L as CaCO3 | 56 | 1020 | 1330.2234 | 80 | 1175.1117 | 95.2345 | Alkb, mg/L CaCO3 | NA | NA |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 56 | 1008 | 1371.3817 | 77.7778 | 1189.6909 | 95.2929
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | [7 empty] | 1998-08-19 | 13:00 | 2092 | 29.533 | 133.089 | 52.08 | 18.294 | 0 | 14.642 | 3.647 |  | 18.289 | 18.289 | 0.80059 | 0 | 13.3109 | 13.1028 | 7.8778 | 66.4127 | 0.19729 | 8.186 | 5.782 | 32.9 | 283.872 | 294.8453 | 1365.6152 | 1346.5049 | 1.3994 | 88.8416 | 820.6751 | 95.9911 | 133.089 | 114.24 | 18.294 | 8.729 | 9.514 | 18.243 | 18.243 | 0.092557 | 0.47848 | 13.2592 | 13.052 | 4.0533 | 101.3172 | 0.12882 | 5.782 | 5.782 | 16.9845 | 294.8453 | 506.7 | 549.7798 | -8.502 | 94.2395 | 422.3125 | 95.9782 | 114.24 | 98.82 | 18.294 | 4.699 | 4.815 | 9.514 | 9.514 | 0.095561 | 0.4939 | 14.2754 | 14.0523 | 7.0588 | 81.1772 | 0.17311 | 5.782 | 5.782 | 32.3021 | 506.7 | 873.8275 | 969.669 | -10.968 | 89.0444 | 738.1845 | 95.6241 | 98.82 | 52.08 | 18.294 | 1.214 | 3.647 | 4.861 | 4.861 | 0.17022 | 0.24974 | 10.7911 | 10.6224 | 8.9712 | 48.1848 | 0.22045 | 5.782 | 6.924 | 104.7139 | 873.8275 | 1365.6152 | 1129.8472 | 17.2646 | 64.4851 | 1001.8374 | 89.5478 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | 86.9732 |  |  |  | Turbidity | ntu | 0.304 | 24.6 | 33.4618 | 99.525 | 29.0309 | 98.9528 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.138 | 58.8 | 78.0861 | 93.8117 | 68.4431 | 99.7984 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.893 | 38.5 | 51.3908 | 33.3582 | 44.9454 | 98.0131 | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | 197.8683 | 102.7931 |  |  |  | Turbidity | ntu | 0.42 | 47.2 | 65.0561 | 46.8354 | 56.128 | 99.2517 | T-Hdb, mg/L CaCO3 | 154.4707 | 62.8729 |  | T-Hdb, mg/L CaCO3 | 183.2251 | 67.9471 |  |  |  | Turbidity | ntu | 0.462 | 63 | 83.1253 | 85.4259 | 73.0626 | 99.3677 | T-Hdb, mg/L CaCO3 | NA | NA |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.23 | 44.3 | 61.1217 | 94.1327 | 52.7108 | 99.5637
|  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Calculate the Required System Influent Pressure | [6 empty] | 1998-08-19 | 21:00 | 2100 | 29.482 | 133.384 | 52.357 | 18.208 | 0 | 14.57 | 3.589 |  | 18.159 | 18.159 | 0.80236 | 0 | 13.2455 | 13.0581 | 7.9661 | 66.6964 | 0.19578 | 8.187 | 5.778 | 32.2655 | 286.08 | 295.188 | 1360.7536 | 1362.5552 | -0.1324 | 89.0695 | 828.8716 | 96.1073 | 133.384 | 115.005 | 18.208 | 8.664 | 9.451 | 18.115 | 18.115 | 0.09192 | 0.47828 | 13.1605 | 12.9743 | 4.0603 | 101.9262 | 0.12729 | 5.778 | 5.778 | 16.77 | 295.188 | 504.9 | 550.4217 | -9.016 | 94.3189 | 422.8048 | 96.0336 | 115.005 | 99.42 | 18.208 | 4.699 | 4.752 | 9.451 | 9.451 | 0.094721 | 0.4972 | 14.2754 | 14.0735 | 7.0622 | 81.9423 | 0.17175 | 5.778 | 5.778 | 32.3279 | 504.9 | 879.2875 | 972.2014 | -10.567 | 89.0484 | 738.5507 | 95.6228 | 99.42 | 52.357 | 18.208 | 1.207 | 3.589 | 4.796 | 4.796 | 0.16776 | 0.25167 | 10.7289 | 10.5771 | 9.0473 | 48.6332 | 0.21749 | 5.778 | 6.929 | 104.7888 | 879.2875 | 1360.7536 | 1139.7556 | 16.2409 | 64.501 | 1009.5215 | 89.62 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | 82.6892 |  |  |  | Total organic carbon | mg/L | 3.28 | 55.8 | 74.9562 | 80.8187 | 65.3781 | 94.983 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | BMRL | 101 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 8.34 | 52.5 | 67.637 | 74.0187 | 60.0685 | 86.1159 | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | 173.7106 | 90.3475 |  |  |  | Total organic carbon | mg/L | 7.91 | 55.1 | 73.1126 | 56.0556 | 64.1063 | 87.6611 | Ca-Hdb, mg/L CaCO3 | 149.4602 | 59.913 |  | Ca-Hdb, mg/L CaCO3 | 177.5708 | 64.8737 |  |  |  | Total organic carbon | mg/L | 5.2 | 55.1 | 71.1582 | 73.7374 | 63.1291 | 91.7629 | Ca-Hdb, mg/L CaCO3 | NA | NA |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 1.05 | 57 | 78.3563 | 97.2513 | 67.6782 | 98.4485
|  | Maximum flow rate to the element, QI, max (gpm) | 8 | Osmotic pressure for stage 13, Dp1 (psi) | 2.8 | [5 empty] | 1998-08-20 | 0:00 | 2103 | 29.495 | 133.337 | 52.47 | 18.243 | 0 | 14.641 | 3.647 |  | 18.288 | 18.288 | 0.80058 | 0 | 13.31 | 13.1167 | 7.9028 | 66.7577 | 0.19648 | 8.164 | 5.776 | 32.242 | 286.08 | 295.033 | 1360.7536 | 1350.0158 | 0.7891 | 89.0717 | 822.5244 | 96.0801 | 133.337 | 114.54 | 18.243 | 8.728 | 9.63 | 18.358 | 18.358 | 0.093327 | 0.47543 | 13.2577 | 13.0652 | 4.0439 | 101.6516 | 0.12853 | 5.776 | 5.776 | 16.7505 | 295.033 | 504.9 | 547.2499 | -8.3878 | 94.3225 | 421.1414 | 96.0226 | 114.54 | 99.12 | 18.243 | 4.699 | 4.931 | 9.63 | 9.63 | 0.097109 | 0.48795 | 14.2754 | 14.0681 | 6.9777 | 81.6093 | 0.17238 | 5.776 | 5.776 | 32.3113 | 504.9 | 878.8325 | 955.2537 | -8.6958 | 89.0482 | 730.0769 | 95.5743 | 99.12 | 52.47 | 18.243 | 1.214 | 3.647 | 4.861 | 4.861 | 0.17022 | 0.24974 | 10.7911 | 10.6344 | 9.0293 | 48.5227 | 0.21916 | 5.776 | 6.926 | 104.737 | 878.8325 | 1360.7536 | 1136.5106 | 16.4793 | 64.4999 | 1007.6715 | 89.606 | Notes: | [9 empty] | UV254 | cm-1 | 0.043 | 1.68 | 2.2771 | 91.5686 | 1.9785 | 97.8267 | Notes: | [9 empty] | UV254 | cm-1 | 0.038 | 1.51 | 1.9939 | 91.828 | 1.752 | 97.831 | Notes: | [9 empty] | UV254 | cm-1 | 0.033 | 1.95 | 2.6071 | 94.1901 | 2.2786 | 98.5517 | Notes: | [9 empty] | UV254 | cm-1 | 0.014 | 2.03 | 2.7995 | 97.4638 | 2.4148 | 99.4202 | Notes: | [9 empty] | UV254 | cm-1 | 0.038 | 2.03 | 2.671 | 91.5556 | 2.3505 | 98.3833 | Notes: | [9 empty] | UV254 | cm-1 | 0.038 | 1.83 | 2.514 | 93.0909 | 2.172 | 98.2505
|  | Minimum flow rate to the element, QI, min (gpm) | 2 | Osmotic pressure for stage 23, Dp2 (psi) | 5 | [5 empty] | 1998-08-20 | 13:00 | 2116 | 29.584 | 132.801 | 51.975 | 18.216 | 0 | 14.574 | 3.588 |  | 18.162 | 18.162 | 0.80244 | 0 | 13.2491 | 13.0223 | 7.9408 | 66.2312 | 0.19662 | 7.509 | 5.779 | 32.853 | 283.872 | 294.8453 | 1365.6152 | 1359.0246 | 0.48261 | 88.8575 | 826.935 | 96.0271 | 132.801 | 114.247 | 18.216 | 8.668 | 9.687 | 18.355 | 18.355 | 0.093507 | 0.47224 | 13.1666 | 12.9412 | 4.0218 | 101.2862 | 0.12777 | 5.779 | 5.779 | 16.9845 | 294.8453 | 502.65 | 543.4772 | -8.1224 | 94.2395 | 419.1612 | 95.948 | 114.247 | 98.812 | 18.216 | 4.699 | 4.988 | 9.687 | 9.687 | 0.097869 | 0.48508 | 14.2754 | 14.0311 | 6.919 | 81.3945 | 0.17238 | 5.779 | 5.779 | 32.3012 | 502.65 | 873.145 | 945.7472 | -8.315 | 89.0447 | 724.1986 | 95.5397 | 98.812 | 51.975 | 18.216 | 1.207 | 3.588 | 4.795 | 4.795 | 0.16772 | 0.25172 | 10.7289 | 10.5453 | 8.9774 | 48.2001 | 0.21878 | 5.779 | 6.949 | 104.6592 | 873.145 | 1365.6152 | 1131.6629 | 17.1316 | 64.5037 | 1002.404 | 89.5592 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.311 | 3.0108 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #VALUE! | 1.495 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.39568 | 3.7143 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.17699 | 3.6842 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.73077 | 3.6842 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 3.619 | 3.2105 | --- | --- | --- | ---
|  | Total width of all membrane envelopes in the element, w (ft) | 19.2 | Osmotic pressure for stage 33, Dp3 (psi) | 9 | [5 empty] | 1998-08-20 | 21:00 | 2124 | 29.588 | 133.142 | 52.267 | 18.261 | 0 | 14.624 | 3.648 |  | 18.272 | 18.272 | 0.80035 | 0 | 13.2945 | 13.0655 | 7.8825 | 66.561 | 0.19629 | 7.416 | 5.783 | 32.665 | 285.264 | 295.033 | 1361.3611 | 1346.8063 | 1.0691 | 88.9284 | 820.9196 | 96.0209 | 133.142 | 114.45 | 18.261 | 8.724 | 9.694 | 18.418 | 18.418 | 0.093741 | 0.47367 | 13.2516 | 13.0233 | 4.035 | 101.5 | 0.12831 | 5.783 | 5.783 | 16.7505 | 295.033 | 504.45 | 545.4699 | -8.1316 | 94.3225 | 420.2515 | 96.0142 | 114.45 | 99.105 | 18.261 | 4.699 | 4.995 | 9.694 | 9.694 | 0.097962 | 0.48473 | 14.2754 | 14.0295 | 6.942 | 81.5745 | 0.17198 | 5.783 | 5.783 | 32.327 | 504.45 | 879.2875 | 948.5954 | -7.8823 | 89.0429 | 726.5227 | 95.5505 | 99.105 | 52.267 | 18.261 | 1.201 | 3.648 | 4.849 | 4.849 | 0.17 | 0.24768 | 10.6756 | 10.4916 | 9.0199 | 48.4051 | 0.21675 | 5.783 | 6.928 | 104.7859 | 879.2875 | 1361.3611 | 1134.2701 | 16.6812 | 64.4833 | 1006.7788 | 89.592 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Feed spacer thickness, T (ft) | 0.0029 | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1998-08-21 | 5:00 | 2132 | 29.393 | 133.551 | 52.492 | 18.202 | 0 | 14.572 | 3.647 |  | 18.219 | 18.219 | 0.79982 | 0 | 13.2473 | 13.0943 | 7.8937 | 66.9258 | 0.19565 | 6.531 | 5.776 | 33.464 | 295.344 | 296.7792 | 1391.1377 | 1348.8848 | 3.0373 | 88.7243 | 822.832 | 95.9331 | 133.551 | 114.93 | 18.202 | 8.665 | 9.578 | 18.243 | 18.243 | 0.09277 | 0.47498 | 13.162 | 13.01 | 4.0622 | 101.9763 | 0.12758 | 5.776 | 5.776 | 17.082 | 296.7792 | 524.25 | 549.8149 | -4.8765 | 94.2442 | 423.2971 | 95.9645 | 114.93 | 99.72 | 18.202 | 4.7 | 4.878 | 9.578 | 9.578 | 0.096408 | 0.49071 | 14.2785 | 14.1136 | 7.2867 | 81.8363 | 0.17246 | 5.776 | 5.776 | 32.4907 | 524.25 | 910.6825 | 998.0648 | -9.5953 | 89.0522 | 761.1574 | 95.7314 | 99.72 | 52.492 | 18.202 | 1.207 | 3.647 | 4.854 | 4.854 | 0.17008 | 0.24866 | 10.7289 | 10.605 | 9.3824 | 48.5216 | 0.21856 | 5.776 | 6.915 | 105.6528 | 910.6825 | 1391.1377 | 1177.1127 | 15.3849 | 64.4002 | 1043.8976 | 89.879 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses in a single element, DPe (psi) | 6.7 | [5 empty] | 1998-08-21 | 13:00 | 2140 | 29.401 | 133.544 | 52.56 | 18.166 | 0 | 14.621 | 3.707 |  | 18.328 | 18.328 | 0.79774 | 0 | 13.2918 | 13.1352 | 7.8211 | 67.0649 | 0.19586 | 7.431 | 5.786 | 33.511 | 294.624 | 296.665 | 1383.2381 | 1334.5862 | 3.5172 | 88.7041 | 815.6256 | 95.8914 | 133.544 | 115.05 | 18.166 | 8.723 | 9.569 | 18.292 | 18.292 | 0.092904 | 0.47688 | 13.2501 | 13.094 | 4.0687 | 102.0623 | 0.12829 | 5.786 | 5.786 | 17.1795 | 296.665 | 521.1 | 551.441 | -5.8225 | 94.2091 | 424.053 | 95.9487 | 115.05 | 99.682 | 18.166 | 4.684 | 4.885 | 9.569 | 9.569 | 0.096395 | 0.4895 | 14.2299 | 14.0622 | 7.2288 | 81.9712 | 0.17155 | 5.786 | 5.786 | 32.4751 | 521.1 | 911.1375 | 989.6198 | -8.6137 | 89.0533 | 755.3599 | 95.7007 | 99.682 | 52.56 | 18.166 | 1.214 | 3.707 | 4.921 | 4.921 | 0.17262 | 0.2467 | 10.7911 | 10.664 | 9.3749 | 48.5801 | 0.21951 | 5.786 | 6.943 | 105.5549 | 911.1375 | 1383.2381 | 1174.9566 | 15.0575 | 64.4195 | 1043.047 | 89.8801 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Design permeate pressure, Pp (psi) | 15 | [5 empty] | 1998-08-21 | 21:00 | 2148 | 29.397 | 133.745 | 52.732 | 18.207 | 0 | 14.563 | 3.648 |  | 18.211 | 18.211 | 0.79968 | 0 | 13.2391 | 13.0846 | 7.8894 | 67.1421 | 0.19488 | 7.45 | 5.78 | 33.4405 | 295.2 | 296.771 | 1382.0225 | 1347.9998 | 2.4618 | 88.7319 | 822.3854 | 95.9337 | 133.745 | 115.282 | 18.207 | 8.663 | 9.754 | 18.417 | 18.417 | 0.093937 | 0.47038 | 13.159 | 13.0055 | 4.0392 | 102.2673 | 0.12717 | 5.78 | 5.78 | 17.0625 | 296.771 | 524.25 | 545.1937 | -3.995 | 94.2506 | 420.9824 | 95.947 | 115.282 | 99.825 | 18.207 | 4.699 | 5.055 | 9.754 | 9.754 | 0.098763 | 0.48175 | 14.2754 | 14.1089 | 7.2035 | 82.143 | 0.17176 | 5.78 | 5.78 | 32.4732 | 524.25 | 910.6825 | 981.3932 | -7.7646 | 89.0578 | 752.8216 | 95.6865 | 99.825 | 52.732 | 18.207 | 1.201 | 3.648 | 4.849 | 4.849 | 0.17 | 0.24768 | 10.6756 | 10.551 | 9.3773 | 48.6942 | 0.21668 | 5.78 | 6.914 | 105.4973 | 910.6825 | 1382.0225 | 1175.7668 | 14.9242 | 64.4516 | 1043.2246 | 89.8874 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 45.2 | [5 empty] | 1998-08-22 | 5:00 | 2156 | 29.372 | 133.792 | 52.695 | 18.192 | 0 | 14.63 | 3.648 |  | 18.278 | 18.278 | 0.80042 | 0 | 13.3 | 13.1546 | 7.9129 | 67.1386 | 0.19593 | 7.387 | 5.78 | 33.4405 | 295.296 | 296.7466 | 1380.807 | 1352.7136 | 2.0346 | 88.731 | 824.7301 | 95.9453 | 133.792 | 115.297 | 18.192 | 8.724 | 9.57 | 18.294 | 18.294 | 0.092914 | 0.47688 | 13.2516 | 13.1067 | 4.0725 | 102.28 | 0.12815 | 5.78 | 5.78 | 17.004 | 296.7466 | 523.8 | 551.7595 | -5.3378 | 94.2699 | 424.253 | 95.992 | 115.297 | 99.727 | 18.192 | 4.699 | 4.871 | 9.57 | 9.57 | 0.096308 | 0.49101 | 14.2754 | 14.1193 | 7.2832 | 82.0368 | 0.17211 | 5.78 | 5.78 | 32.4732 | 523.8 | 910.2275 | 997.7775 | -9.6185 | 89.0569 | 760.7888 | 95.7316 | 99.727 | 52.695 | 18.192 | 1.207 | 3.648 | 4.855 | 4.855 | 0.17012 | 0.24861 | 10.7289 | 10.6116 | 9.3787 | 48.6403 | 0.21816 | 5.78 | 6.9 | 105.4915 | 910.2275 | 1380.807 | 1176.4875 | 14.7971 | 64.4506 | 1043.3575 | 89.8892 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Additional Information |  | Net driving pressure required for permeation, NDP (psi) | 118.8462 | [5 empty] | 1998-08-22 | 13:00 | 2164 | 29.508 | 133.477 | 52.44 | 18.166 | 0 | 14.562 | 3.646 |  | 18.208 | 18.208 | 0.79976 | 0 | 13.2382 | 13.0409 | 7.8694 | 66.9231 | 0.19486 | 7.394 | 5.791 | 33.746 | 293.28 | 296.3222 | 1386.8842 | 1345.0428 | 3.0169 | 88.6117 | 820.6825 | 95.8881 | 133.477 | 114.69 | 18.166 | 8.669 | 9.926 | 18.595 | 18.595 | 0.095105 | 0.4662 | 13.1681 | 12.9718 | 4.0076 | 101.9099 | 0.12729 | 5.791 | 5.791 | 17.3745 | 296.3222 | 522.9 | 539.9448 | -3.2597 | 94.1366 | 418.1335 | 95.8447 | 114.69 | 99.247 | 18.166 | 4.699 | 5.227 | 9.926 | 9.926 | 0.10106 | 0.4734 | 14.2754 | 14.0627 | 7.109 | 81.6935 | 0.17214 | 5.791 | 5.791 | 32.453 | 522.9 | 901.5825 | 963.805 | -6.9015 | 89.0481 | 743.3525 | 95.6342 | 99.247 | 52.44 | 18.166 | 1.194 | 3.646 | 4.84 | 4.84 | 0.16978 | 0.24669 | 10.6133 | 10.4552 | 9.2651 | 48.4124 | 0.21596 | 5.791 | 6.951 | 105.431 | 901.5825 | 1386.8842 | 1162.3079 | 16.1929 | 64.4201 | 1031.9452 | 89.7833 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 1 | Flow weighted system pressure losses, Lsys (psi) | 61.4 | [5 empty] | 1998-08-22 | 21:00 | 2172 | 29.406 | 133.745 | 52.5 | 18.174 | 0 | 14.555 | 3.646 |  | 18.201 | 18.201 | 0.79968 | 0 | 13.2318 | 13.074 | 7.8834 | 67.0651 | 0.19494 | 7.408 | 5.783 | 33.5345 | 294.624 | 296.665 | 1383.2381 | 1347.0939 | 2.613 | 88.6962 | 821.8794 | 95.9198 | 133.745 | 114.937 | 18.174 | 8.664 | 9.519 | 18.183 | 18.183 | 0.092374 | 0.47649 | 13.1605 | 13.0035 | 4.0668 | 102.1002 | 0.12736 | 5.783 | 5.783 | 17.1795 | 296.665 | 521.1 | 551.0469 | -5.7469 | 94.2091 | 423.8559 | 95.9469 | 114.937 | 99.54 | 18.174 | 4.684 | 4.835 | 9.519 | 9.519 | 0.095728 | 0.49207 | 14.2299 | 14.0601 | 7.253 | 81.8115 | 0.17186 | 5.783 | 5.783 | 32.4769 | 521.1 | 907.725 | 994.4631 | -9.5555 | 89.0527 | 757.7815 | 95.7142 | 99.54 | 52.5 | 18.174 | 1.207 | 3.646 | 4.853 | 4.853 | 0.17004 | 0.24871 | 10.7289 | 10.6009 | 9.35 | 48.496 | 0.21859 | 5.783 | 6.943 | 105.5117 | 907.725 | 1383.2381 | 1173.2959 | 15.1776 | 64.4341 | 1040.5104 | 89.8596 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[11 empty] | 1998-09-01 | 7:00 | 2184 | 29.095 | 135.474 | 55.335 | 18.628 | 0 | 14.864 | 3.528 |  | 18.392 | 18.392 | 0.80818 | 0 | 13.5127 | 13.4748 | 8.1886 | 68.5879 | 0.19646 | 8.265 | 5.778 | 35.9315 | 310.608 | 299.521 | 1435.4998 | 1410.0634 | 1.772 | 88.0037 | 854.7922 | 95.7965 | 135.474 | 116.85 | 18.628 | 8.964 | 9.817 | 18.781 | 18.781 | 0.095361 | 0.47729 | 13.6162 | 13.578 | 4.1045 | 103.4295 | 0.13128 | 5.778 | 5.778 | 17.7255 | 299.521 | 558.45 | 556.8312 | 0.28988 | 94.0821 | 428.1761 | 95.8602 | 116.85 | 101.572 | 18.628 | 4.699 | 5.118 | 9.817 | 9.817 | 0.099603 | 0.47866 | 14.2754 | 14.2354 | 7.6679 | 82.9151 | 0.17169 | 5.778 | 5.778 | 32.9148 | 558.45 | 986.44 | 1040.9607 | -5.527 | 89.0108 | 799.7053 | 95.8841 | 101.572 | 55.335 | 18.628 | 1.201 | 3.528 | 4.729 | 4.729 | 0.1652 | 0.25396 | 10.6756 | 10.6456 | 10.2852 | 49.5403 | 0.21489 | 5.778 | 6.826 | 107.5248 | 986.44 | 1435.4998 | 1285.6399 | 10.4396 | 64.1011 | 1136.0399 | 90.5351
[11 empty] | 1998-09-01 | 15:00 | 2192 | 29.112 | 135.628 | 55.252 | 18.7 | 0 | 14.875 | 3.527 |  | 18.402 | 18.402 | 0.80834 | 0 | 13.5227 | 13.478 | 8.1826 | 68.5574 | 0.19659 | 8.276 | 5.787 | 36.096 | 310.56 | 299.3088 | 1439.7534 | 1409.3996 | 2.1083 | 87.9402 | 854.3542 | 95.7751 | 135.628 | 117.082 | 18.7 | 8.962 | 9.816 | 18.778 | 18.778 | 0.095348 | 0.47726 | 13.6132 | 13.5682 | 4.0979 | 103.5571 | 0.13102 | 5.787 | 5.787 | 17.9595 | 299.3088 | 557.55 | 556.1805 | 0.24563 | 93.9997 | 427.7446 | 95.8014 | 117.082 | 101.79 | 18.7 | 4.699 | 5.117 | 9.816 | 9.816 | 0.09959 | 0.47871 | 14.2754 | 14.2283 | 7.6552 | 83.0808 | 0.17126 | 5.787 | 5.787 | 32.9194 | 557.55 | 984.165 | 1039.3243 | -5.6047 | 89.0015 | 798.4371 | 95.877 | 101.79 | 55.252 | 18.7 | 1.214 | 3.527 | 4.741 | 4.741 | 0.16542 | 0.25606 | 10.7911 | 10.7554 | 10.2755 | 49.5455 | 0.21708 | 5.787 | 6.883 | 107.4931 | 984.165 | 1439.7534 | 1285.9171 | 10.6849 | 64.0862 | 1135.0411 | 90.5296
[11 empty] | 1998-09-01 | 23:00 | 2200 | 29.146 | 135.4 | 55.327 | 18.67 | 0 | 14.884 | 3.467 |  | 18.351 | 18.351 | 0.81107 | 0 | 13.5309 | 13.4726 | 8.286 | 68.4075 | 0.19695 | 8.185 | 5.772 | 36.331 | 311.472 | 299.6678 | 1445.8306 | 1430.1857 | 1.0821 | 87.8762 | 864.9268 | 95.7995 | 135.4 | 116.782 | 18.67 | 8.964 | 9.943 | 18.907 | 18.907 | 0.096202 | 0.47411 | 13.6162 | 13.5576 | 4.0852 | 103.3358 | 0.1312 | 5.772 | 5.772 | 18.0765 | 299.6678 | 559.8 | 553.5334 | 1.1194 | 93.9678 | 426.6006 | 95.7627 | 116.782 | 101.52 | 18.67 | 4.713 | 5.23 | 9.943 | 9.943 | 0.10119 | 0.474 | 14.318 | 14.2563 | 7.6426 | 82.8384 | 0.1721 | 5.772 | 5.772 | 32.9296 | 559.8 | 990.3075 | 1034.5878 | -4.4714 | 89.0113 | 797.1939 | 95.8693 | 101.52 | 55.327 | 18.67 | 1.207 | 3.467 | 4.674 | 4.674 | 0.16288 | 0.25824 | 10.7289 | 10.6827 | 10.3645 | 49.389 | 0.2163 | 5.772 | 6.724 | 107.5248 | 990.3075 | 1445.8306 | 1297.6391 | 10.2496 | 64.1187 | 1143.9733 | 90.6008
|  | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Required influent pressure to the system, PI (psi) | 195.2462 | [5 empty] | 1998-09-02 | 7:00 | 2208.0003 | 29.537 | 134.851 | 54.682 | 18.793 | 0 | 14.958 | 3.467 |  | 18.425 | 18.425 | 0.81183 | 0 | 13.5982 | 13.384 | 8.2926 | 67.6809 | 0.19775 | 8.151 | 5.77 | 31.772 | 280.848 | 294.4291 | 1338.2685 | 1427.6351 | -6.6778 | 89.2089 | 861.0321 | 96.31 | 134.851 | 116.107 | 18.793 | 9.025 | 9.633 | 18.658 | 18.658 | 0.094338 | 0.48371 | 13.7089 | 13.493 | 4.0784 | 102.6076 | 0.1315 | 5.77 | 5.77 | 16.692 | 294.4291 | 499.95 | 554.6365 | -10.9384 | 94.3307 | 424.5328 | 96.0681 | 116.107 | 100.755 | 18.793 | 4.713 | 4.92 | 9.633 | 9.633 | 0.097055 | 0.48926 | 14.318 | 14.0925 | 6.9153 | 82.7227 | 0.17036 | 5.77 | 5.77 | 32.3757 | 499.95 | 881.79 | 947.8519 | -7.4918 | 89.0039 | 723.901 | 95.5276 | 100.755 | 54.682 | 18.793 | 1.22 | 3.467 | 4.687 | 4.687 | 0.16314 | 0.26029 | 10.8444 | 10.6737 | 9.1474 | 49.7781 | 0.21442 | 5.77 | 6.788 | 103.9133 | 881.79 | 1338.2685 | 1155.5164 | 13.6559 | 64.7069 | 1018.6532 | 89.799 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Maximum element recovery (%) | NA | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-09-02 | 8:02 | 2209.0406 | 29.601 | 134.114 | 45.435 | 18.559 | 0 | 14.932 | 3.408 |  | 18.34 | 18.34 | 0.81418 | 0 | 13.5745 | 13.3355 | 8.3713 | 62.8442 | 0.2122 | 8.181 | 5.778 | 31.7955 | 279.216 | 294.1598 | 1346.1687 | 1443.6975 | -7.2449 | 89.1911 | 868.9287 | 96.3408 | 134.114 | 114.937 | 18.559 | 9.025 | 9.876 | 18.901 | 18.901 | 0.095958 | 0.47749 | 13.7089 | 13.4675 | 4.0419 | 101.9246 | 0.13213 | 5.778 | 5.778 | 16.731 | 294.1598 | 500.85 | 547.6831 | -9.3507 | 94.3123 | 420.9214 | 96.0251 | 114.937 | 98.94 | 18.559 | 4.713 | 5.163 | 9.876 | 9.876 | 0.1003 | 0.47722 | 14.318 | 14.0659 | 6.8227 | 81.5568 | 0.17247 | 5.778 | 5.778 | 32.3914 | 500.85 | 879.06 | 928.4784 | -5.6217 | 88.9885 | 714.6642 | 95.4676 | 98.94 | 45.435 | 18.559 | 1.194 | 3.408 | 4.602 | 4.602 | 0.16026 | 0.25945 | 10.6133 | 10.4265 | 9.1074 | 44.5211 | 0.23419 | 5.778 | 6.843 | 104.0746 | 879.06 | 1346.1687 | 1150.5778 | 14.5295 | 64.6197 | 1014.8189 | 89.7445 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Variability of design flux (%) | 15 | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-09-02 | 16:00 | 2217.0003 | 29.367 | 126.958 | 54.06 | 17.736 | 0 | 14.333 | 3.167 |  | 17.5 | 17.5 | 0.81903 | 0 | 13.03 | 12.8894 | 8.5288 | 64.2442 | 0.20063 | 9.102 | 5.774 | 37.788 | 308.496 | 299.1782 | 1482.8999 | 1482.161 | 0.049833 | 87.3694 | 890.6696 | 95.7573 | 126.958 | 108.93 | 17.736 | 8.484 | 9.148 | 17.632 | 17.632 | 0.089299 | 0.48117 | 12.8871 | 12.748 | 4.1059 | 96.1021 | 0.13265 | 5.774 | 5.774 | 18.6615 | 299.1782 | 558 | 559.3339 | -0.23905 | 93.7624 | 429.2561 | 95.6526 | 108.93 | 95.077 | 17.736 | 4.642 | 4.506 | 9.148 | 9.148 | 0.09106 | 0.50743 | 14.1023 | 13.9501 | 7.9547 | 76.3128 | 0.1828 | 5.774 | 5.774 | 32.9691 | 558 | 980.07 | 1098.8774 | -12.1223 | 88.9801 | 828.4387 | 96.0203 | 95.077 | 54.06 | 17.736 | 1.207 | 3.167 | 4.374 | 4.374 | 0.15087 | 0.27595 | 10.7289 | 10.6131 | 10.3825 | 46.45 | 0.22848 | 5.774 | 6.773 | 108.0029 | 980.07 | 1482.8999 | 1312.4303 | 11.4957 | 63.9002 | 1146.2501 | 90.5777
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | [7 empty] | 1998-09-03 | 0:00 | 2225 | 29.41 | 126.556 | 53.775 | 17.743 | 0 | 14.308 | 3.167 |  | 17.475 | 17.475 | 0.81877 | 0 | 13.0073 | 12.8506 | 8.5196 | 63.9029 | 0.2011 | 8.338 | 5.759 | 33.9105 | 285.264 | 295.3349 | 1394.1763 | 1476.4085 | -5.8983 | 88.5179 | 885.8717 | 96.1721 | 126.556 | 108.472 | 17.743 | 8.485 | 9.146 | 17.631 | 17.631 | 0.089289 | 0.48125 | 12.8886 | 12.7334 | 4.0678 | 95.7032 | 0.13305 | 5.759 | 5.759 | 17.4525 | 295.3349 | 513 | 553.1341 | -7.8234 | 94.0906 | 424.2345 | 95.8861 | 108.472 | 94.462 | 17.743 | 4.642 | 4.504 | 9.146 | 9.146 | 0.091033 | 0.50754 | 14.1023 | 13.9324 | 7.2807 | 76.4433 | 0.18226 | 5.759 | 5.759 | 32.5248 | 513 | 899.08 | 1008.1967 | -12.1365 | 88.9872 | 760.5984 | 95.7238 | 94.462 | 53.775 | 17.743 | 1.181 | 3.167 | 4.348 | 4.348 | 0.15035 | 0.27162 | 10.4978 | 10.3713 | 9.4186 | 46.9569 | 0.22087 | 5.759 | 6.664 | 105.2352 | 899.08 | 1394.1763 | 1195.1112 | 14.2783 | 64.3675 | 1047.0956 | 89.9498
|  | (e.g., solute type and concentration) | [8 empty] | 1998-09-03 | 8:00 | 2233.0003 | 29.41 | 126.717 | 54.337 | 17.697 | 0 | 14.313 | 3.228 |  | 17.541 | 17.541 | 0.81597 | 0 | 13.0118 | 12.8551 | 8.417 | 64.413 | 0.19957 | 8.418 | 5.765 | 35.156 | 293.76 | 296.7955 | 1426.3841 | 1456.909 | -2.14 | 88.1548 | 876.8523 | 95.9907 | 126.717 | 108.727 | 17.697 | 8.484 | 9.147 | 17.631 | 17.631 | 0.089292 | 0.4812 | 12.8871 | 12.7319 | 4.0832 | 95.9418 | 0.1327 | 5.765 | 5.765 | 17.8425 | 296.7955 | 529.2 | 555.5292 | -4.9753 | 93.9883 | 426.1624 | 95.8132 | 108.727 | 94.837 | 17.697 | 4.641 | 4.506 | 9.147 | 9.147 | 0.091053 | 0.50738 | 14.0992 | 13.9294 | 7.522 | 76.563 | 0.18193 | 5.765 | 5.765 | 32.6885 | 529.2 | 927.29 | 1040.587 | -12.2181 | 88.9862 | 784.8935 | 95.8353 | 94.837 | 54.337 | 17.697 | 1.188 | 3.228 | 4.416 | 4.416 | 0.15294 | 0.26902 | 10.56 | 10.4328 | 9.7235 | 47.1665 | 0.22119 | 5.765 | 6.716 | 106.0618 | 927.29 | 1426.3841 | 1229.5264 | 13.8012 | 64.2644 | 1078.4082 | 90.165
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-09-04 | 0:00 | 2249 | 29.533 | 134.583 | 51.172 | 18.576 | 0 | 14.774 | 3.646 |  | 18.42 | 18.42 | 0.80206 | 0 | 13.4309 | 13.221 | 7.9315 | 66.37 | 0.1992 | 6.926 | 5.795 | 34.4275 | 293.952 | 296.5344 | 1406.9381 | 1358.6209 | 3.4342 | 88.39 | 827.5776 | 95.84 | 134.583 | 115.402 | 18.576 | 8.847 | 9.802 | 18.649 | 18.649 | 0.094871 | 0.4744 | 13.4385 | 13.2284 | 4.0489 | 102.3676 | 0.12922 | 5.795 | 5.795 | 17.55 | 296.5344 | 525.6 | 548.3376 | -4.326 | 94.0816 | 422.436 | 95.8455 | 115.402 | 99.742 | 18.576 | 4.713 | 5.089 | 9.802 | 9.802 | 0.099309 | 0.48082 | 14.318 | 14.0942 | 7.2142 | 81.7818 | 0.17234 | 5.795 | 5.795 | 32.51 | 525.6 | 923.8775 | 982.2581 | -6.3191 | 89.0367 | 753.929 | 95.6879 | 99.742 | 51.172 | 18.576 | 1.214 | 3.646 | 4.86 | 4.86 | 0.17018 | 0.24979 | 10.7911 | 10.6224 | 9.5372 | 47.3438 | 0.22437 | 5.795 | 6.881 | 106.272 | 923.8775 | 1406.9381 | 1196.1137 | 14.9846 | 64.162 | 1059.9956 | 89.9743
|  | Standard testing recovery (%) | 10 | [7 empty] | 1998-09-04 | 8:00 | 2257 | 29.185 | 135.501 | 51.982 | 18.447 | 0 | 14.761 | 3.706 |  | 18.467 | 18.467 | 0.79932 | 0 | 13.4191 | 13.3459 | 7.8712 | 67.4233 | 0.19794 | 8.508 | 5.791 | 36.425 | 310.704 | 299.5454 | 1447.0461 | 1347.5543 | 6.8755 | 87.8399 | 823.5499 | 95.5771 | 135.501 | 116.557 | 18.447 | 8.847 | 9.991 | 18.838 | 18.838 | 0.096132 | 0.46964 | 13.4385 | 13.3652 | 4.0598 | 103.5222 | 0.1291 | 5.791 | 5.791 | 18.1545 | 299.5454 | 560.7 | 548.7163 | 2.1373 | 93.9393 | 424.1308 | 95.7196 | 116.557 | 100.972 | 18.447 | 4.713 | 5.278 | 9.991 | 9.991 | 0.10183 | 0.47172 | 14.318 | 14.2399 | 7.6359 | 82.6816 | 0.17223 | 5.791 | 5.791 | 32.8044 | 560.7 | 983.0275 | 1032.0853 | -4.9905 | 89.0486 | 796.3927 | 95.8809 | 100.972 | 51.982 | 18.447 | 1.201 | 3.706 | 4.907 | 4.907 | 0.17232 | 0.24475 | 10.6756 | 10.6173 | 10.1688 | 47.8612 | 0.22184 | 5.791 | 6.866 | 107.9424 | 983.0275 | 1447.0461 | 1266.6155 | 12.4689 | 63.9646 | 1124.8215 | 90.4036
|  | Standard testing pH | 7.5 | [7 empty] | 1998-09-04 | 18:00 | 2267 | 29.223 | 140.599 | 42.442 | 18.84 | 0 | 14.998 | 3.985 |  | 18.983 | 18.983 | 0.79008 | 0 | 13.6345 | 13.545 | 7.605 | 65.0755 | 0.20814 | 8.904 | 5.798 | 35.2735 | 310.08 | 299.1701 | 1406.9381 | 1292.3748 | 8.1427 | 88.2095 | 795.7725 | 95.5674 | 140.599 | 120.307 | 18.84 | 9.089 | 10.948 | 20.037 | 20.037 | 0.10332 | 0.45361 | 13.8061 | 13.7154 | 3.9891 | 107.6239 | 0.12744 | 5.798 | 5.798 | 17.277 | 299.1701 | 553.95 | 533.197 | 3.7464 | 94.225 | 416.1835 | 95.8487 | 120.307 | 102.675 | 18.84 | 4.728 | 6.22 | 10.948 | 10.948 | 0.11449 | 0.43186 | 14.3635 | 14.2692 | 7.1978 | 85.4532 | 0.16698 | 5.798 | 5.798 | 32.395 | 553.95 | 940.485 | 950.3989 | -1.0541 | 89.1717 | 752.1744 | 95.6931 | 102.675 | 42.442 | 18.84 | 1.181 | 3.985 | 5.166 | 5.166 | 0.18309 | 0.22861 | 10.4978 | 10.4288 | 9.5648 | 44.1537 | 0.23619 | 5.798 | 6.862 | 107.4442 | 940.485 | 1406.9381 | 1187.3661 | 15.6064 | 64.0859 | 1063.9256 | 89.9012
|  | Acceptable range of operating pressures | 80 - 350 | [7 empty] | 1998-09-04 | 19:45 | 2268.7481 | 29.223 | 121.23 | 59.715 | 18.109 | 0 | 13.815 | 3.168 |  | 16.983 | 16.983 | 0.81346 | 0 | 12.5591 | 12.4766 | 8.3967 | 63.9668 | 0.19505 | 8.934 | 5.703 | 37.318 | 310.896 | 301.3325 | 1535.7692 | 1452.6456 | 5.4125 | 87.6157 | 876.9891 | 95.7448 | 121.23 | 104.61 | 18.109 | 8.003 | 8.792 | 16.795 | 16.795 | 0.085321 | 0.47651 | 12.1565 | 12.0766 | 4.1144 | 90.6966 | 0.13315 | 5.703 | 5.703 | 18.5835 | 301.3325 | 569.7 | 558.7074 | 1.9295 | 93.8329 | 430.0199 | 95.6785 | 104.61 | 92.94 | 18.109 | 4.598 | 4.194 | 8.792 | 8.792 | 0.086605 | 0.52298 | 13.9686 | 13.8768 | 8.312 | 72.354 | 0.19179 | 5.703 | 5.703 | 32.8035 | 569.7 | 987.805 | 1158.3147 | -17.2615 | 89.1138 | 864.0073 | 96.2033 | 92.94 | 59.715 | 18.109 | 1.214 | 3.168 | 4.382 | 4.382 | 0.15105 | 0.27704 | 10.7911 | 10.7202 | 10.4869 | 47.7316 | 0.22459 | 5.703 | 6.982 | 107.7408 | 987.805 | 1535.7692 | 1325.0518 | 13.7206 | 64.2452 | 1156.4284 | 90.6833
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 1998-09-05 | 3:00 | 2276.0003 | 29.236 | 135.702 | 51.12 | 18.361 | 0 | 14.631 | 3.766 |  | 18.397 | 18.397 | 0.79529 | 0 | 13.3009 | 13.2084 | 7.7419 | 67.3081 | 0.19624 | 8.358 | 5.791 | 36.4485 | 311.664 | 299.5536 | 1447.6536 | 1321.7232 | 8.6989 | 87.8324 | 810.6384 | 95.5037 | 135.702 | 116.692 | 18.361 | 8.725 | 10.352 | 19.077 | 19.077 | 0.098132 | 0.45736 | 13.2532 | 13.161 | 4.0043 | 103.8317 | 0.12675 | 5.791 | 5.791 | 17.8425 | 299.5536 | 561.15 | 536.9888 | 4.3057 | 94.0436 | 418.2712 | 95.7342 | 116.692 | 100.687 | 18.361 | 4.699 | 5.653 | 10.352 | 10.352 | 0.10674 | 0.45392 | 14.2754 | 14.1762 | 7.4797 | 82.8488 | 0.17111 | 5.791 | 5.791 | 32.7778 | 561.15 | 975.2925 | 1000.3542 | -2.5697 | 89.0578 | 780.7521 | 95.8018 | 100.687 | 51.12 | 18.361 | 1.207 | 3.766 | 4.973 | 4.973 | 0.17484 | 0.24271 | 10.7289 | 10.6543 | 10.0635 | 47.479 | 0.2244 | 5.791 | 6.854 | 107.9395 | 975.2925 | 1447.6536 | 1253.2784 | 13.4269 | 63.9665 | 1114.2855 | 90.3131
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-09-05 | 11:00 | 2284.0003 | 29.223 | 135.909 | 51.442 | 18.319 | 0 | 14.635 | 3.826 |  | 18.461 | 18.461 | 0.79275 | 0 | 13.3045 | 13.2171 | 7.6806 | 67.6759 | 0.1953 | 8.474 | 5.796 | 35.9785 | 312.384 | 299.6842 | 1436.7148 | 1308.3962 | 8.9314 | 87.9945 | 804.0402 | 95.5253 | 135.909 | 116.775 | 18.319 | 8.721 | 10.293 | 19.014 | 19.014 | 0.097725 | 0.45866 | 13.2471 | 13.1601 | 4.0127 | 104.0103 | 0.12653 | 5.796 | 5.796 | 17.823 | 299.6842 | 560.25 | 538.498 | 3.8825 | 94.0527 | 419.0911 | 95.7472 | 116.775 | 100.867 | 18.319 | 4.713 | 5.58 | 10.293 | 10.293 | 0.10586 | 0.45788 | 14.318 | 14.2239 | 7.5022 | 82.9998 | 0.17137 | 5.796 | 5.796 | 32.7842 | 560.25 | 978.4775 | 1005.7601 | -2.7883 | 89.0604 | 783.005 | 95.813 | 100.867 | 51.442 | 18.319 | 1.201 | 3.826 | 5.027 | 5.027 | 0.17712 | 0.23891 | 10.6756 | 10.6054 | 10.0741 | 47.7614 | 0.22205 | 5.796 | 6.851 | 107.735 | 978.4775 | 1436.7148 | 1251.8078 | 12.8701 | 64.0505 | 1115.1426 | 90.3389
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-09-05 | 19:00 | 2292 | 29.223 | 135.635 | 51.427 | 18.354 | 0 | 14.642 | 3.765 |  | 18.407 | 18.407 | 0.79546 | 0 | 13.3109 | 13.2235 | 7.7698 | 67.4072 | 0.19617 | 8.36 | 5.776 | 35.955 | 312.432 | 299.831 | 1446.4381 | 1326.039 | 8.3238 | 88.0082 | 812.935 | 95.5771 | 135.635 | 116.617 | 18.354 | 8.723 | 9.992 | 18.715 | 18.715 | 0.095725 | 0.4661 | 13.2501 | 13.1631 | 4.0513 | 103.7207 | 0.12691 | 5.776 | 5.776 | 17.8035 | 299.831 | 560.7 | 546.0406 | 2.6145 | 94.0622 | 422.9358 | 95.7905 | 116.617 | 100.95 | 18.354 | 4.712 | 5.28 | 9.992 | 9.992 | 0.10185 | 0.47158 | 14.3149 | 14.2209 | 7.635 | 82.7945 | 0.17176 | 5.776 | 5.776 | 32.7676 | 560.7 | 978.705 | 1031.8396 | -5.4291 | 89.0713 | 796.2698 | 95.8849 | 100.95 | 51.427 | 18.354 | 1.207 | 3.765 | 4.972 | 4.972 | 0.1748 | 0.24276 | 10.7289 | 10.6584 | 10.1076 | 47.7269 | 0.22332 | 5.776 | 6.776 | 107.5824 | 978.705 | 1446.4381 | 1257.9733 | 13.0296 | 64.119 | 1118.3391 | 90.3802
|  | Maximum permissible turbidity (ntu) | less than 1 | [7 empty] | 1998-09-06 | 3:00 | 2300.0003 | 29.278 | 135.715 | 51.202 | 18.322 | 0 | 14.637 | 3.765 |  | 18.402 | 18.402 | 0.7954 | 0 | 13.3064 | 13.1975 | 7.7628 | 67.3737 | 0.19588 | 8.702 | 5.78 | 36.002 | 312.432 | 299.7005 | 1436.7148 | 1324.8677 | 7.7849 | 87.9873 | 812.2841 | 95.5678 | 135.715 | 116.602 | 18.322 | 8.723 | 10.229 | 18.952 | 18.952 | 0.097305 | 0.46027 | 13.2501 | 13.1417 | 4.0207 | 103.8158 | 0.12659 | 5.78 | 5.78 | 17.823 | 299.7005 | 560.7 | 540.0776 | 3.678 | 94.0531 | 419.889 | 95.7553 | 116.602 | 100.725 | 18.322 | 4.713 | 5.516 | 10.229 | 10.229 | 0.105 | 0.46075 | 14.318 | 14.2008 | 7.5347 | 82.8068 | 0.17149 | 5.78 | 5.78 | 32.7686 | 560.7 | 974.8375 | 1011.777 | -3.7893 | 89.0662 | 786.2385 | 95.8322 | 100.725 | 51.202 | 18.322 | 1.201 | 3.765 | 4.966 | 4.966 | 0.17468 | 0.24184 | 10.6756 | 10.5882 | 10.0564 | 47.5851 | 0.22251 | 5.78 | 6.777 | 107.5306 | 974.8375 | 1436.7148 | 1251.5004 | 12.8915 | 64.1207 | 1113.1689 | 90.3401
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-09-06 | 11:00 | 2308.0003 | 29.316 | 135.367 | 50.977 | 18.25 | 0 | 14.648 | 3.765 |  | 18.413 | 18.413 | 0.79552 | 0 | 13.3164 | 13.1926 | 7.7513 | 67.1707 | 0.1964 | 8.379 | 5.788 | 36.1665 | 310.224 | 299.3414 | 1440.3614 | 1323.2422 | 8.1312 | 87.918 | 811.2918 | 95.5421 | 135.367 | 116.22 | 18.25 | 8.728 | 10.043 | 18.771 | 18.771 | 0.096082 | 0.46497 | 13.2577 | 13.1345 | 4.036 | 103.5075 | 0.12689 | 5.788 | 5.788 | 17.9985 | 299.3414 | 558.45 | 543.8462 | 2.6151 | 93.9873 | 421.5938 | 95.7308 | 116.22 | 100.432 | 18.25 | 4.713 | 5.33 | 10.043 | 10.043 | 0.10252 | 0.46928 | 14.318 | 14.1849 | 7.5811 | 82.4949 | 0.17195 | 5.788 | 5.788 | 32.7584 | 558.45 | 968.4675 | 1023.2876 | -5.6605 | 89.0565 | 790.8688 | 95.8579 | 100.432 | 50.977 | 18.25 | 1.207 | 3.765 | 4.972 | 4.972 | 0.1748 | 0.24276 | 10.7289 | 10.6291 | 9.9909 | 47.4636 | 0.22394 | 5.788 | 6.81 | 107.401 | 968.4675 | 1440.3614 | 1244.5119 | 13.5972 | 64.1209 | 1106.4897 | 90.2935
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-09-06 | 19:00 | 2316 | 29.367 | 135.708 | 51.307 | 18.352 | 0 | 14.638 | 3.765 |  | 18.403 | 18.403 | 0.79541 | 0 | 13.3073 | 13.1637 | 7.7536 | 67.4019 | 0.1953 | 8.556 | 5.792 | 36.0725 | 310.896 | 299.4475 | 1439.1459 | 1323.4272 | 8.0408 | 87.9536 | 811.4374 | 95.5545 | 135.708 | 116.61 | 18.352 | 8.724 | 10.224 | 18.948 | 18.948 | 0.097275 | 0.46042 | 13.2516 | 13.1087 | 4.0164 | 103.7906 | 0.1263 | 5.792 | 5.792 | 17.9205 | 299.4475 | 557.55 | 539.6707 | 3.2068 | 94.0155 | 419.5591 | 95.7287 | 116.61 | 100.83 | 18.352 | 4.713 | 5.511 | 10.224 | 10.224 | 0.10494 | 0.46097 | 14.318 | 14.1635 | 7.4917 | 82.8763 | 0.1709 | 5.792 | 5.792 | 32.7713 | 557.55 | 971.88 | 1006.34 | -3.5457 | 89.0561 | 781.945 | 95.809 | 100.83 | 51.307 | 18.352 | 1.201 | 3.765 | 4.966 | 4.966 | 0.17468 | 0.24184 | 10.6756 | 10.5604 | 10.0243 | 47.6922 | 0.22143 | 5.792 | 6.842 | 107.3405 | 971.88 | 1439.1459 | 1247.6601 | 13.3055 | 64.1538 | 1109.77 | 90.3277
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-09-07 | 0:00 | 2321 | 29.304 | 135.95 | 51.502 | 18.355 | 0 | 14.642 | 3.825 |  | 18.467 | 18.467 | 0.79287 | 0 | 13.3109 | 13.1918 | 7.69 | 67.681 | 0.19491 | 8.466 | 5.786 | 37.694 | 323.616 | 301.5936 | 1480.4689 | 1311.7944 | 11.3933 | 87.5017 | 806.694 | 95.3273 | 135.95 | 116.842 | 18.355 | 8.722 | 10.113 | 18.835 | 18.835 | 0.096528 | 0.46307 | 13.2486 | 13.1301 | 4.0564 | 103.9846 | 0.12627 | 5.786 | 5.786 | 18.174 | 301.5936 | 580.95 | 546.03 | 6.0108 | 93.974 | 423.8118 | 95.7118 | 116.842 | 101.085 | 18.355 | 4.713 | 5.4 | 10.113 | 10.113 | 0.10346 | 0.46603 | 14.318 | 14.1899 | 7.871 | 82.7375 | 0.1715 | 5.786 | 5.786 | 32.982 | 580.95 | 1015.3325 | 1059.2043 | -4.3209 | 89.0641 | 820.0771 | 95.9782 | 101.085 | 51.502 | 18.355 | 1.207 | 3.825 | 5.032 | 5.032 | 0.1772 | 0.23986 | 10.7289 | 10.6329 | 10.4962 | 47.4423 | 0.22412 | 5.786 | 6.804 | 108.7546 | 1015.3325 | 1480.4689 | 1301.4082 | 12.0949 | 63.94 | 1158.3704 | 90.6114
[11 empty] | 1998-09-07 | 11:00 | 2332 | 29.274 | 135.615 | 51.33 | 18.292 | 0 | 14.627 | 3.825 |  | 18.452 | 18.452 | 0.79271 | 0 | 13.2973 | 13.19 | 7.6713 | 67.5092 | 0.19538 | 8.352 | 5.798 | 35.767 | 309.408 | 299.2027 | 1430.0307 | 1306.5947 | 8.6317 | 88.0459 | 802.8987 | 95.5453 | 135.615 | 116.662 | 18.292 | 8.726 | 10.225 | 18.951 | 18.951 | 0.097289 | 0.46045 | 13.2547 | 13.1478 | 4.0161 | 103.8304 | 0.12663 | 5.798 | 5.798 | 17.706 | 299.2027 | 554.85 | 539.4316 | 2.7788 | 94.0823 | 419.3172 | 95.7774 | 116.662 | 100.785 | 18.292 | 4.713 | 5.512 | 10.225 | 10.225 | 0.10495 | 0.46093 | 14.318 | 14.2025 | 7.4532 | 82.9783 | 0.17116 | 5.798 | 5.798 | 32.7419 | 554.85 | 965.055 | 1001.2752 | -3.7532 | 89.057 | 778.0626 | 95.7919 | 100.785 | 51.33 | 18.292 | 1.188 | 3.825 | 5.013 | 5.013 | 0.17682 | 0.23698 | 10.56 | 10.4748 | 9.9119 | 47.8536 | 0.21889 | 5.798 | 6.849 | 107.0986 | 965.055 | 1430.0307 | 1231.5262 | 13.8811 | 64.2054 | 1098.2906 | 90.2486
[11 empty] | 1998-09-07 | 19:00 | 2340 | 29.236 | 135.896 | 51.517 | 18.289 | 0 | 14.622 | 3.706 |  | 18.328 | 18.328 | 0.7978 | 0 | 13.2927 | 13.2003 | 7.8411 | 67.5764 | 0.19534 | 8.385 | 5.789 | 35.673 | 311.76 | 299.4394 | 1428.2071 | 1340.1279 | 6.1671 | 88.0867 | 819.7836 | 95.6485 | 135.896 | 116.887 | 18.289 | 8.723 | 10.289 | 19.012 | 19.012 | 0.097705 | 0.45882 | 13.2501 | 13.158 | 4.0133 | 104.0892 | 0.12641 | 5.789 | 5.789 | 17.589 | 299.4394 | 557.55 | 538.3917 | 3.4362 | 94.126 | 418.9155 | 95.8013 | 116.887 | 101.137 | 18.289 | 4.699 | 5.59 | 10.289 | 10.289 | 0.1059 | 0.4567 | 14.2754 | 14.1762 | 7.4537 | 83.2693 | 0.17025 | 5.789 | 5.789 | 32.7548 | 557.55 | 971.88 | 998.6972 | -2.7593 | 89.0613 | 778.1236 | 95.7905 | 101.137 | 51.517 | 18.289 | 1.2 | 3.706 | 4.906 | 4.906 | 0.1723 | 0.2446 | 10.6667 | 10.5925 | 10.0469 | 47.9911 | 0.22072 | 5.789 | 6.831 | 107.1878 | 971.88 | 1428.2071 | 1251.8667 | 12.347 | 64.2038 | 1111.8733 | 90.3597
[11 empty] | 1998-09-08 | 0:00 | 2345 | 29.219 | 135.923 | 51.787 | 18.319 | 0 | 14.64 | 3.825 |  | 18.465 | 18.465 | 0.79285 | 0 | 13.3091 | 13.2232 | 7.6913 | 67.8447 | 0.1949 | 8.394 | 5.789 | 35.579 | 311.616 | 299.5454 | 1426.3841 | 1309.864 | 8.1689 | 88.1223 | 804.7047 | 95.5786 | 135.923 | 116.887 | 18.319 | 8.72 | 10.177 | 18.897 | 18.897 | 0.096949 | 0.46145 | 13.2456 | 13.1601 | 4.0242 | 104.0618 | 0.12646 | 5.789 | 5.789 | 17.823 | 299.5454 | 556.65 | 540.9348 | 2.8232 | 94.05 | 420.2401 | 95.7589 | 116.887 | 101.212 | 18.319 | 4.713 | 5.464 | 10.177 | 10.177 | 0.10431 | 0.4631 | 14.318 | 14.2256 | 7.4982 | 83.2323 | 0.17091 | 5.789 | 5.789 | 32.7686 | 556.65 | 975.065 | 1008.5265 | -3.4317 | 89.0606 | 782.5883 | 95.8128 | 101.212 | 51.787 | 18.319 | 1.207 | 3.825 | 5.032 | 5.032 | 0.1772 | 0.23986 | 10.7289 | 10.6597 | 10.0482 | 48.1323 | 0.22147 | 5.789 | 6.828 | 107.1792 | 975.065 | 1426.3841 | 1248.9312 | 12.4408 | 64.2194 | 1111.9981 | 90.3616
[11 empty] | 1998-09-08 | 11:00 | 2356 | 29.299 | 135.327 | 51.375 | 18.216 | 0 | 14.578 | 3.825 |  | 18.403 | 18.403 | 0.79215 | 0 | 13.2527 | 13.1361 | 7.6545 | 67.4805 | 0.19467 | 8.337 | 5.804 | 35.7905 | 309.36 | 299.2272 | 1431.2457 | 1303.2482 | 8.9431 | 88.039 | 801.2377 | 95.5331 | 135.327 | 116.362 | 18.216 | 8.665 | 10.703 | 19.368 | 19.368 | 0.10027 | 0.44739 | 13.162 | 13.0462 | 3.9542 | 103.6743 | 0.12584 | 5.804 | 5.804 | 17.745 | 299.2272 | 555.3 | 527.1113 | 5.0763 | 94.0697 | 413.1692 | 95.7051 | 116.362 | 100.695 | 18.216 | 4.713 | 5.99 | 10.703 | 10.703 | 0.11133 | 0.44034 | 14.318 | 14.192 | 7.2816 | 83.0309 | 0.17092 | 5.804 | 5.804 | 32.7262 | 555.3 | 961.1875 | 966.467 | -0.54927 | 89.0631 | 760.8835 | 95.6989 | 100.695 | 51.375 | 18.216 | 1.2 | 3.825 | 5.025 | 5.025 | 0.17706 | 0.23881 | 10.6667 | 10.5728 | 9.8806 | 47.9384 | 0.22055 | 5.804 | 6.861 | 107.1014 | 961.1875 | 1431.2457 | 1229.1361 | 14.1212 | 64.2073 | 1095.1618 | 90.2205
[11 empty] | 1998-09-08 | 19:00 | 2364.0003 | 29.24 | 135.635 | 51.525 | 18.295 | 0 | 14.639 | 3.766 |  | 18.405 | 18.405 | 0.79538 | 0 | 13.3082 | 13.2141 | 7.7603 | 67.5247 | 0.19569 | 8.276 | 5.8 | 35.673 | 310.896 | 299.3088 | 1428.2071 | 1324.1002 | 7.2893 | 88.0815 | 811.7045 | 95.6052 | 135.635 | 116.73 | 18.295 | 8.725 | 10.172 | 18.897 | 18.897 | 0.096932 | 0.46171 | 13.2532 | 13.1595 | 4.0251 | 103.8624 | 0.1267 | 5.8 | 5.8 | 17.6085 | 299.3088 | 557.55 | 540.9363 | 2.9798 | 94.1169 | 420.1226 | 95.8087 | 116.73 | 100.897 | 18.295 | 4.713 | 5.459 | 10.172 | 10.172 | 0.10424 | 0.46333 | 14.318 | 14.2168 | 7.5134 | 83.0051 | 0.17128 | 5.8 | 5.8 | 32.7538 | 557.55 | 968.0125 | 1010.6301 | -4.4026 | 89.0568 | 784.0901 | 95.8227 | 100.897 | 51.525 | 18.295 | 1.201 | 3.766 | 4.967 | 4.967 | 0.17472 | 0.2418 | 10.6756 | 10.6001 | 9.9809 | 47.9351 | 0.22113 | 5.8 | 6.882 | 107.1878 | 968.0125 | 1428.2071 | 1242.5346 | 13.0004 | 64.1882 | 1105.2736 | 90.3021
[11 empty] | 1998-09-09 | 0:48 | 2369.7964 | 29.227 | 128.794 | 56.625 | 18.331 | 0 | 14.958 | 3.347 |  | 18.305 | 18.305 | 0.81715 | 0 | 13.5982 | 13.5072 | 8.4655 | 65.913 | 0.20493 | 8.199 | 5.77 | 38.0935 | 311.616 | 299.8147 | 1480.4689 | 1469.4669 | 0.74314 | 87.2943 | 884.6408 | 95.6939 | 128.794 | 111.127 | 18.331 | 9.087 | 8.428 | 17.515 | 17.515 | 0.086508 | 0.51881 | 13.803 | 13.7107 | 4.3296 | 97.2999 | 0.14091 | 5.77 | 5.77 | 18.5055 | 299.8147 | 568.8 | 603.12 | -6.0338 | 93.8277 | 451.4674 | 95.901 | 111.127 | 97.267 | 18.331 | 4.67 | 3.758 | 8.428 | 8.428 | 0.08127 | 0.55411 | 14.1873 | 14.0925 | 8.6758 | 77.1902 | 0.18257 | 5.77 | 5.77 | 33.6987 | 568.8 | 1047.41 | 1233.7609 | -17.7916 | 88.7602 | 901.2805 | 96.261 | 97.267 | 56.625 | 18.331 | 1.201 | 3.347 | 4.548 | 4.548 | 0.15796 | 0.26407 | 10.6756 | 10.6042 | 11.0613 | 47.5537 | 0.22299 | 5.77 | 6.942 | 109.5494 | 1047.41 | 1480.4689 | 1383.9414 | 6.5201 | 63.461 | 1215.6757 | 90.9886
[11 empty] | 1998-09-09 | 8:00 | 2377 | 29.21 | 133.739 | 47.617 | 18.271 | 0 | 14.725 | 3.945 |  | 18.67 | 18.67 | 0.7887 | 0 | 13.3864 | 13.3035 | 7.5613 | 64.8457 | 0.20516 | 5.92 | 5.788 | 34.7095 | 305.568 | 298.5091 | 1392.9613 | 1283.1604 | 7.8826 | 88.3724 | 790.8348 | 95.611 | 133.739 | 115.057 | 18.271 | 8.847 | 9.865 | 18.712 | 18.712 | 0.095291 | 0.4728 | 13.4385 | 13.3553 | 4.0663 | 102.0607 | 0.13086 | 5.788 | 5.788 | 17.7645 | 298.5091 | 540.45 | 550.2828 | -1.8194 | 94.0489 | 424.396 | 95.8142 | 115.057 | 98.977 | 18.271 | 4.684 | 5.181 | 9.865 | 9.865 | 0.10034 | 0.47481 | 14.2299 | 14.1418 | 7.3765 | 81.3695 | 0.1738 | 5.788 | 5.788 | 32.441 | 540.45 | 926.835 | 999.727 | -7.8646 | 89.1323 | 770.0885 | 95.7874 | 98.977 | 47.617 | 18.271 | 1.194 | 3.945 | 5.139 | 5.139 | 0.18175 | 0.23234 | 10.6133 | 10.5477 | 9.4475 | 45.5785 | 0.23142 | 5.788 | 6.751 | 106.2605 | 926.835 | 1392.9613 | 1175.1914 | 15.6336 | 64.4029 | 1051.0132 | 89.8897
[11 empty] | 1998-09-09 | 16:00 | 2385 | 29.18 | 134.1 | 48.06 | 18.303 | 0 | 14.723 | 3.984 |  | 18.707 | 18.707 | 0.78703 | 0 | 13.3845 | 13.3135 | 7.5226 | 65.2544 | 0.20402 | 8.364 | 5.791 | 35.485 | 312.192 | 299.6434 | 1412.4073 | 1275.8491 | 9.6685 | 88.1576 | 787.7462 | 95.4954 | 134.1 | 115.207 | 18.303 | 8.845 | 9.87 | 18.715 | 18.715 | 0.095318 | 0.47262 | 13.4354 | 13.3641 | 4.0824 | 102.2681 | 0.13068 | 5.791 | 5.791 | 17.7255 | 299.6434 | 552.15 | 552.284 | -0.024275 | 94.0845 | 425.9637 | 95.8387 | 115.207 | 99.322 | 18.303 | 4.684 | 5.186 | 9.87 | 9.87 | 0.10041 | 0.47457 | 14.2299 | 14.1544 | 7.542 | 81.4195 | 0.17384 | 5.791 | 5.791 | 32.5855 | 552.15 | 957.775 | 1021.4212 | -6.6452 | 89.1252 | 786.7856 | 95.8584 | 99.322 | 48.06 | 18.303 | 1.194 | 3.984 | 5.178 | 5.178 | 0.18331 | 0.23059 | 10.6133 | 10.557 | 9.7813 | 45.6067 | 0.23148 | 5.791 | 6.773 | 107.113 | 957.775 | 1412.4073 | 1212.7174 | 14.1383 | 64.2532 | 1085.2462 | 90.1301
[11 empty] | 1998-09-10 | 0:00 | 2393 | 29.189 | 134.06 | 47.872 | 18.262 | 0 | 14.718 | 3.945 |  | 18.663 | 18.663 | 0.78862 | 0 | 13.38 | 13.3055 | 7.5679 | 65.1361 | 0.20427 | 8.628 | 5.78 | 35.5555 | 311.472 | 299.6678 | 1414.2303 | 1285.0178 | 9.1366 | 88.135 | 792.3428 | 95.5126 | 134.06 | 115.635 | 18.262 | 8.846 | 9.742 | 18.588 | 18.588 | 0.094468 | 0.4759 | 13.437 | 13.3621 | 4.0986 | 102.4869 | 0.13038 | 5.78 | 5.78 | 17.784 | 299.6678 | 556.2 | 555.626 | 0.1032 | 94.0654 | 427.6469 | 95.8414 | 115.635 | 99.6 | 18.262 | 4.684 | 5.058 | 9.742 | 9.742 | 0.098703 | 0.4808 | 14.2299 | 14.1506 | 7.6606 | 81.6949 | 0.17321 | 5.78 | 5.78 | 32.5864 | 556.2 | 958.685 | 1041.0964 | -8.5963 | 89.1258 | 798.6482 | 95.9198 | 99.6 | 47.872 | 18.262 | 1.188 | 3.945 | 5.133 | 5.133 | 0.18163 | 0.23144 | 10.56 | 10.5012 | 9.799 | 45.675 | 0.22991 | 5.78 | 6.663 | 107.0208 | 958.685 | 1414.2303 | 1215.1557 | 14.0765 | 64.2869 | 1086.9204 | 90.1538
[11 empty] | 1998-09-10 | 8:00 | 2401 | 29.168 | 134.603 | 55.972 | 18.409 | 0 | 14.738 | 3.407 |  | 18.145 | 18.145 | 0.81223 | 0 | 13.3982 | 13.3318 | 8.3415 | 68.537 | 0.19452 | 8.465 | 5.778 | 35.9315 | 311.472 | 299.6597 | 1437.3229 | 1440.495 | -0.2207 | 88.0092 | 870.0773 | 95.8703 | 134.603 | 116.047 | 18.409 | 8.845 | 9.63 | 18.475 | 18.475 | 0.093717 | 0.47876 | 13.4354 | 13.3689 | 4.1141 | 102.8019 | 0.13005 | 5.778 | 5.778 | 17.7255 | 299.6597 | 559.8 | 558.6117 | 0.21227 | 94.0848 | 429.1357 | 95.8695 | 116.047 | 100.942 | 18.409 | 4.699 | 4.931 | 9.63 | 9.63 | 0.097109 | 0.48795 | 14.2754 | 14.2047 | 7.7784 | 82.3071 | 0.17258 | 5.778 | 5.778 | 32.9792 | 559.8 | 994.175 | 1061.8342 | -6.8056 | 88.9944 | 810.8171 | 95.9326 | 100.942 | 55.972 | 18.409 | 1.194 | 3.407 | 4.601 | 4.601 | 0.16022 | 0.25951 | 10.6133 | 10.5608 | 10.422 | 49.626 | 0.21281 | 5.778 | 6.735 | 107.3722 | 994.175 | 1437.3229 | 1304.9594 | 9.209 | 64.1686 | 1149.5672 | 90.6598
[11 empty] | 1998-09-11 | 0:00 | 2417 | 29.253 | 134.958 | 55.92 | 18.735 | 0 | 14.921 | 3.466 |  | 18.387 | 18.387 | 0.8115 | 0 | 13.5645 | 13.4635 | 8.2919 | 68.4121 | 0.1968 | 7.151 | 5.775 | 36.3545 | 309.84 | 299.3822 | 1446.4381 | 1431.7068 | 1.0185 | 87.8568 | 865.5445 | 95.7998 | 134.958 | 116.197 | 18.735 | 9.021 | 9.513 | 18.534 | 18.534 | 0.093524 | 0.48673 | 13.7028 | 13.6007 | 4.1463 | 102.6962 | 0.13244 | 5.775 | 5.775 | 18.1155 | 299.3822 | 556.2 | 566.1022 | -1.7803 | 93.949 | 432.7422 | 95.8138 | 116.197 | 101.19 | 18.735 | 4.699 | 4.814 | 9.513 | 9.513 | 0.095548 | 0.49396 | 14.2754 | 14.1691 | 7.786 | 82.1725 | 0.17243 | 5.775 | 5.775 | 32.9636 | 556.2 | 986.44 | 1066.937 | -8.1604 | 88.9895 | 811.5685 | 95.9383 | 101.19 | 55.92 | 18.735 | 1.201 | 3.466 | 4.667 | 4.667 | 0.16272 | 0.25734 | 10.6756 | 10.596 | 10.3105 | 49.5095 | 0.21402 | 5.775 | 6.712 | 107.6486 | 986.44 | 1446.4381 | 1290.9491 | 10.7498 | 64.0431 | 1138.6945 | 90.5463
[11 empty] | 1998-09-11 | 8:00 | 2425 | 29.155 | 135.387 | 56.332 | 18.75 | 0 | 14.998 | 3.466 |  | 18.464 | 18.464 | 0.81228 | 0 | 13.6345 | 13.5722 | 8.3389 | 68.7706 | 0.19735 | 8.162 | 5.783 | 35.9315 | 310.656 | 299.521 | 1434.8923 | 1440.1196 | -0.36429 | 88.0037 | 869.8203 | 95.8691 | 135.387 | 116.79 | 18.75 | 9.085 | 9.863 | 18.948 | 18.948 | 0.096072 | 0.47947 | 13.8 | 13.7369 | 4.1152 | 103.2233 | 0.13308 | 5.783 | 5.783 | 17.7645 | 299.521 | 560.25 | 559.0523 | 0.21378 | 94.069 | 429.2866 | 95.8619 | 116.79 | 101.692 | 18.75 | 4.699 | 5.164 | 9.863 | 9.863 | 0.10022 | 0.47643 | 14.2754 | 14.2102 | 7.6717 | 82.8193 | 0.17158 | 5.783 | 5.783 | 32.9792 | 560.25 | 990.535 | 1040.0419 | -4.998 | 88.9893 | 800.1459 | 95.8783 | 101.692 | 56.332 | 18.75 | 1.214 | 3.466 | 4.68 | 4.68 | 0.16298 | 0.2594 | 10.7911 | 10.7418 | 10.3771 | 49.8849 | 0.21533 | 5.783 | 6.751 | 107.4787 | 990.535 | 1434.8923 | 1299.834 | 9.4124 | 64.1165 | 1145.1845 | 90.6147
[11 empty] | 1998-09-11 | 16:00 | 2433 | 29.274 | 143.588 | 49.147 | 19.311 | 0 | 15.223 | 3.983 |  | 19.206 | 19.206 | 0.79262 | 0 | 13.8391 | 13.7275 | 7.7111 | 69.3454 | 0.19796 | 8.476 | 5.792 | 34.3805 | 309.936 | 299.2762 | 1394.1763 | 1311.7056 | 5.9154 | 88.5121 | 805.4909 | 95.7317 | 143.588 | 123.712 | 19.311 | 9.264 | 11.187 | 20.451 | 20.451 | 0.1055 | 0.45299 | 14.0719 | 13.9584 | 3.989 | 110.35 | 0.12649 | 5.792 | 5.792 | 17.1795 | 299.2762 | 553.5 | 532.8815 | 3.7251 | 94.2596 | 416.0789 | 95.8711 | 123.712 | 106.14 | 19.311 | 4.771 | 6.416 | 11.187 | 11.187 | 0.1174 | 0.42648 | 14.4942 | 14.3773 | 7.1456 | 88.4694 | 0.16251 | 5.792 | 5.792 | 32.6066 | 553.5 | 959.595 | 940.8414 | 1.9543 | 89.1048 | 747.1707 | 95.636 | 106.14 | 49.147 | 19.311 | 1.188 | 3.983 | 5.171 | 5.171 | 0.18315 | 0.22974 | 10.56 | 10.4748 | 9.7982 | 48.5343 | 0.21582 | 5.792 | 6.818 | 106.9315 | 959.595 | 1394.1763 | 1213.9169 | 12.9295 | 64.27 | 1086.756 | 90.1605
[11 empty] | 1998-09-12 | 0:00 | 2441.0003 | 29.474 | 135.233 | 52.155 | 18.547 | 0 | 14.766 | 3.765 |  | 18.531 | 18.531 | 0.79683 | 0 | 13.4236 | 13.2369 | 7.7858 | 67.3612 | 0.19651 | 8.702 | 5.764 | 31.3255 | 279.984 | 294.2741 | 1326.7222 | 1325.5354 | 0.089458 | 89.355 | 809.9047 | 96.1322 | 135.233 | 115.965 | 18.547 | 8.846 | 10.228 | 19.074 | 19.074 | 0.097709 | 0.46377 | 13.437 | 13.25 | 3.9815 | 103.0705 | 0.12855 | 5.764 | 5.764 | 16.3215 | 294.2741 | 499.95 | 534.6699 | -6.9447 | 94.4536 | 414.472 | 96.0621 | 115.965 | 100.125 | 18.547 | 4.713 | 5.515 | 10.228 | 10.228 | 0.10499 | 0.46079 | 14.318 | 14.1188 | 6.6748 | 82.8232 | 0.17047 | 5.764 | 5.764 | 32.292 | 499.95 | 874.2825 | 899.6004 | -2.8959 | 89.0266 | 699.7752 | 95.3854 | 100.125 | 52.155 | 18.547 | 1.207 | 3.765 | 4.972 | 4.972 | 0.1748 | 0.24276 | 10.7289 | 10.5796 | 8.9379 | 48.6551 | 0.21744 | 5.764 | 6.674 | 103.9651 | 874.2825 | 1326.7222 | 1121.2342 | 15.4884 | 64.6706 | 997.7583 | 89.5801
[11 empty] | 1998-09-12 | 8:00 | 2449 | 29.516 | 132.915 | 54.315 | 18.303 | 0 | 14.566 | 3.467 |  | 18.033 | 18.033 | 0.80774 | 0 | 13.2418 | 13.0414 | 8.14 | 67.172 | 0.19415 | 8.531 | 5.764 | 31.7485 | 279.936 | 294.2741 | 1337.661 | 1397.2298 | -4.4532 | 89.2112 | 845.752 | 96.2461 | 132.915 | 114.322 | 18.303 | 8.66 | 9.878 | 18.538 | 18.538 | 0.094754 | 0.46715 | 13.1544 | 12.9553 | 3.9926 | 101.3229 | 0.12786 | 5.764 | 5.764 | 16.692 | 294.2741 | 499.95 | 537.6291 | -7.5366 | 94.3277 | 415.9516 | 95.987 | 114.322 | 99.255 | 18.303 | 4.699 | 5.179 | 9.878 | 9.878 | 0.10042 | 0.4757 | 14.2754 | 14.0594 | 6.7966 | 81.6889 | 0.17211 | 5.764 | 5.764 | 32.4006 | 499.95 | 882.245 | 924.166 | -4.7516 | 88.9897 | 712.058 | 95.4497 | 99.255 | 54.315 | 18.303 | 1.207 | 3.467 | 4.674 | 4.674 | 0.16288 | 0.25824 | 10.7289 | 10.5665 | 9.1364 | 49.3456 | 0.21413 | 5.764 | 6.672 | 104.0659 | 882.245 | 1337.661 | 1153.16 | 13.7928 | 64.6364 | 1017.7025 | 89.7744
[11 empty] | 1998-09-12 | 16:00 | 2457 | 29.601 | 132.747 | 54.337 | 18.391 | 0 | 14.575 | 3.466 |  | 18.041 | 18.041 | 0.80788 | 0 | 13.25 | 13.0167 | 8.1338 | 67.0172 | 0.19423 | 8.57 | 5.773 | 31.8895 | 278.448 | 294.0538 | 1340.6996 | 1396.49 | -4.1613 | 89.1552 | 845.2719 | 96.2273 | 132.747 | 113.895 | 18.391 | 8.662 | 9.749 | 18.411 | 18.411 | 0.093901 | 0.47048 | 13.1575 | 12.9258 | 4.0083 | 100.9217 | 0.12808 | 5.773 | 5.773 | 16.5165 | 294.0538 | 501.3 | 540.646 | -7.8488 | 94.3832 | 417.3499 | 96.0425 | 113.895 | 99.007 | 18.391 | 4.713 | 5.036 | 9.749 | 9.749 | 0.098602 | 0.48343 | 14.318 | 14.0659 | 6.8832 | 81.1768 | 0.17327 | 5.773 | 5.773 | 32.3941 | 501.3 | 879.7425 | 940.1311 | -6.8643 | 88.9836 | 720.7155 | 95.5053 | 99.007 | 54.337 | 18.391 | 1.2 | 3.466 | 4.666 | 4.666 | 0.1627 | 0.25718 | 10.6667 | 10.4788 | 9.1005 | 49.1805 | 0.21307 | 5.773 | 6.73 | 103.9824 | 879.7425 | 1340.6996 | 1148.3265 | 14.3487 | 64.6383 | 1014.0345 | 89.7457
[11 empty] | 1998-09-13 | 0:00 | 2465 | 29.529 | 133.799 | 64.08 | 18.603 | 0 | 14.536 | 3.407 |  | 17.943 | 17.943 | 0.81012 | 0 | 13.2145 | 13.0095 | 8.2353 | 72.1012 | 0.18043 | 6.816 | 5.783 | 31.725 | 282.432 | 294.5597 | 1369.2607 | 1415.9465 | -3.4096 | 89.2297 | 855.2531 | 96.2906 | 133.799 | 115.177 | 18.603 | 8.604 | 11.914 | 20.518 | 20.518 | 0.10815 | 0.41934 | 13.0694 | 12.8666 | 3.7871 | 102.0979 | 0.12602 | 5.783 | 5.783 | 16.3215 | 294.5597 | 504 | 495.4965 | 1.6872 | 94.459 | 395.0281 | 95.8683 | 115.177 | 101.205 | 18.603 | 4.699 | 7.215 | 11.914 | 11.914 | 0.12757 | 0.39441 | 14.2754 | 14.054 | 6.2514 | 83.3366 | 0.16864 | 5.783 | 5.783 | 32.4226 | 504 | 893.8475 | 811.1299 | 9.2541 | 88.9928 | 657.5649 | 95.0693 | 101.205 | 64.08 | 18.603 | 1.233 | 3.407 | 4.64 | 4.64 | 0.161 | 0.26573 | 10.96 | 10.79 | 9.3222 | 54.7173 | 0.19719 | 5.783 | 6.787 | 104.4662 | 893.8475 | 1369.2607 | 1179.5261 | 13.8567 | 64.5348 | 1036.6868 | 89.9231
[11 empty] | 1998-09-13 | 8:00 | 2473 | 29.389 | 125.906 | 78.315 | 17.854 | 0 | 14.142 | NR |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 12.8564 | 12.7094 | #VALUE! | #VALUE! | #VALUE! | 8.586 | 5.722 | 35.861 | 284.16 | 295.2859 | 1531.5156 | #VALUE! | #VALUE! | 87.8555 | #VALUE! | #VALUE! | 125.906 | 109.777 | 17.854 | 8.239 | 8.621 | 16.86 | 16.86 | 0.084968 | 0.48867 | 12.5149 | 12.3719 | 4.1077 | 95.8798 | 0.12904 | 5.722 | 5.722 | 17.3355 | 295.2859 | 539.55 | 560.9202 | -3.9608 | 94.1292 | 428.1031 | 95.9506 | 109.777 | 99.397 | 17.854 | 4.67 | 3.951 | 8.621 | 8.621 | 0.083844 | 0.5417 | 14.1873 | 14.0251 | 8.125 | 78.608 | 0.17842 | 5.722 | 5.722 | 28.8586 | 539.55 | 1101.555 | 1143.1767 | -3.7784 | 90.2269 | 841.3633 | 96.57 | 99.397 | 78.315 | 17.854 | 1.233 | 1.61 | 2.843 | 2.843 | 0.089092 | 0.4337 | 10.96 | 10.8347 | 13.7137 | 57.2883 | 0.18913 | 5.722 | 6.81 | 109.9066 | 1101.555 | 1531.5156 | 1860.9976 | -21.5135 | 62.7796 | 1481.2763 | 92.5803
[11 empty] | 1998-09-14 | 0:00 | 2489 | 29.321 | 133.605 | 59.025 | 18.495 | 0 | 14.695 | 3.168 |  | 17.863 | 17.863 | 0.82265 | 0 | 13.3591 | 13.2329 | 8.7336 | 69.0864 | 0.19154 | 8.471 | 5.775 | 33.3935 | 293.52 | 296.5099 | 1391.7458 | 1516.9947 | -8.9994 | 88.7378 | 906.7523 | 96.3172 | 133.605 | 115.365 | 18.495 | 8.782 | 9.458 | 18.24 | 18.24 | 0.09236 | 0.48147 | 13.3397 | 13.2138 | 4.0927 | 101.8973 | 0.12968 | 5.775 | 5.775 | 17.004 | 296.5099 | 527.4 | 556.0385 | -5.4301 | 94.2653 | 426.2742 | 96.011 | 115.365 | 100.777 | 18.495 | 4.699 | 4.759 | 9.458 | 9.458 | 0.094814 | 0.49683 | 14.2754 | 14.1406 | 7.3874 | 82.1886 | 0.17205 | 5.775 | 5.775 | 32.8311 | 527.4 | 945.945 | 1015.7335 | -7.3776 | 88.9275 | 771.5668 | 95.7449 | 100.777 | 59.025 | 18.495 | 1.214 | 3.168 | 4.382 | 4.382 | 0.15105 | 0.27704 | 10.7911 | 10.6892 | 10.0155 | 51.3905 | 0.208 | 5.775 | 6.744 | 105.4368 | 945.945 | 1391.7458 | 1268.0337 | 8.889 | 64.4407 | 1106.9893 | 90.4754
[11 empty] | 1998-09-14 | 8:00 | 2497 | 29.316 | 133.216 | 58.83 | 18.418 | 0 | 14.689 | 3.168 |  | 17.857 | 17.857 | 0.82259 | 0 | 13.3536 | 13.2295 | 8.729 | 68.876 | 0.19208 | 8.354 | 5.77 | 33.417 | 292.752 | 296.4691 | 1392.3533 | 1516.1574 | -8.8917 | 88.7283 | 906.3133 | 96.3129 | 133.216 | 114.99 | 18.418 | 8.783 | 9.455 | 18.238 | 18.238 | 0.092344 | 0.48158 | 13.3413 | 13.2172 | 4.0924 | 101.5926 | 0.1301 | 5.77 | 5.77 | 17.0235 | 296.4691 | 527.85 | 556.0536 | -5.3431 | 94.2579 | 426.2613 | 96.0063 | 114.99 | 100.447 | 18.418 | 4.699 | 4.756 | 9.455 | 9.455 | 0.094774 | 0.49699 | 14.2754 | 14.1427 | 7.3956 | 81.9049 | 0.17267 | 5.77 | 5.77 | 32.8311 | 527.85 | 946.1725 | 1016.9361 | -7.4789 | 88.926 | 772.3931 | 95.7494 | 100.447 | 58.83 | 18.418 | 1.207 | 3.168 | 4.375 | 4.375 | 0.15091 | 0.27589 | 10.7289 | 10.6291 | 10.0089 | 51.2116 | 0.20755 | 5.77 | 6.749 | 105.4397 | 946.1725 | 1392.3533 | 1266.4896 | 9.0396 | 64.4349 | 1106.331 | 90.4694
[11 empty] | 1998-09-14 | 16:00 | 2505 | 29.359 | 133.022 | 58.62 | 18.352 | 0 | 14.629 | 3.167 |  | 17.796 | 17.796 | 0.82204 | 0 | 13.2991 | 13.1587 | 8.6854 | 68.7836 | 0.19131 | 8.203 | 5.778 | 33.9575 | 292.08 | 296.3875 | 1395.3919 | 1508.6037 | -8.1133 | 88.5429 | 902.4956 | 96.2374 | 133.022 | 114.66 | 18.352 | 8.723 | 9.691 | 18.414 | 18.414 | 0.093717 | 0.47372 | 13.2501 | 13.1103 | 4.0481 | 101.4409 | 0.12924 | 5.778 | 5.778 | 17.2185 | 296.3875 | 529.2 | 547.6713 | -3.4904 | 94.1905 | 422.0294 | 95.9201 | 114.66 | 100.26 | 18.352 | 4.699 | 4.992 | 9.691 | 9.691 | 0.097922 | 0.48488 | 14.2754 | 14.1248 | 7.3013 | 81.8067 | 0.17266 | 5.778 | 5.778 | 32.7364 | 529.2 | 943.4425 | 996.5242 | -5.6264 | 88.9549 | 762.8621 | 95.7087 | 100.26 | 58.62 | 18.352 | 1.207 | 3.167 | 4.374 | 4.374 | 0.15087 | 0.27595 | 10.7289 | 10.6156 | 9.9767 | 51.1113 | 0.2077 | 5.778 | 6.767 | 105.4541 | 943.4425 | 1395.3919 | 1262.8148 | 9.5011 | 64.4202 | 1103.1286 | 90.4405
[11 empty] | 1998-09-15 | 0:00 | 2513 | 29.299 | 133.236 | 58.995 | 18.423 | 0 | 14.688 | 3.167 |  | 17.855 | 17.855 | 0.82263 | 0 | 13.3527 | 13.2352 | 8.7208 | 68.9717 | 0.19189 | 8.221 | 5.767 | 33.8635 | 293.664 | 296.6242 | 1392.3533 | 1515.2628 | -8.8275 | 88.5837 | 905.9435 | 96.2621 | 133.236 | 115.05 | 18.423 | 8.784 | 9.456 | 18.24 | 18.24 | 0.092354 | 0.48158 | 13.3428 | 13.2254 | 4.0938 | 101.6262 | 0.13014 | 5.767 | 5.767 | 17.082 | 296.6242 | 528.3 | 556.3004 | -5.3001 | 94.2412 | 426.4623 | 95.9945 | 115.05 | 100.597 | 18.423 | 4.684 | 4.772 | 9.456 | 9.456 | 0.094888 | 0.49535 | 14.2299 | 14.1047 | 7.3866 | 82.0139 | 0.17198 | 5.767 | 5.767 | 32.8164 | 528.3 | 943.4425 | 1014.6464 | -7.5472 | 88.9367 | 771.4732 | 95.7463 | 100.597 | 58.995 | 18.423 | 1.22 | 3.167 | 4.387 | 4.387 | 0.15113 | 0.27809 | 10.8444 | 10.749 | 9.9939 | 51.3791 | 0.20921 | 5.767 | 6.726 | 105.4541 | 943.4425 | 1392.3533 | 1266.2546 | 9.0565 | 64.4486 | 1104.8485 | 90.4553
[11 empty] | 1998-09-15 | 8:00 | 2521 | 29.321 | 133.109 | 58.815 | 18.375 | 0 | 14.636 | 3.167 |  | 17.803 | 17.803 | 0.82211 | 0 | 13.3055 | 13.1798 | 8.6995 | 68.8875 | 0.19132 | 8.104 | 5.766 | 33.84 | 293.568 | 296.6078 | 1391.7458 | 1510.9653 | -8.5662 | 88.591 | 903.7866 | 96.2558 | 133.109 | 114.967 | 18.375 | 8.723 | 9.628 | 18.351 | 18.351 | 0.093297 | 0.47534 | 13.2501 | 13.125 | 4.0575 | 101.6055 | 0.12918 | 5.766 | 5.766 | 17.355 | 296.6078 | 531.9 | 549.6118 | -3.3299 | 94.1488 | 423.1098 | 95.8982 | 114.967 | 100.237 | 18.375 | 4.699 | 4.929 | 9.628 | 9.628 | 0.097082 | 0.48806 | 14.2754 | 14.1406 | 7.3693 | 81.8577 | 0.17275 | 5.766 | 5.766 | 32.8477 | 531.9 | 943.4425 | 1007.6652 | -6.8073 | 88.9256 | 769.7826 | 95.7329 | 100.237 | 58.815 | 18.375 | 1.214 | 3.167 | 4.381 | 4.381 | 0.15101 | 0.27711 | 10.7911 | 10.6892 | 9.986 | 51.165 | 0.20892 | 5.766 | 6.699 | 105.4541 | 943.4425 | 1391.7458 | 1264.667 | 9.1309 | 64.4466 | 1104.0547 | 90.4485
[11 empty] | 1998-09-15 | 16:00 | 2529 | 29.248 | 133.451 | 58.912 | 18.438 | 0 | 14.695 | 3.168 |  | 17.863 | 17.863 | 0.82265 | 0 | 13.3591 | 13.2615 | 8.7384 | 69.0051 | 0.19218 | 7.71 | 5.761 | 33.746 | 294.288 | 297.0077 | 1389.9227 | 1518.1663 | -9.2267 | 88.638 | 907.587 | 96.2818 | 133.451 | 114.907 | 18.438 | 8.782 | 9.396 | 18.178 | 18.178 | 0.091947 | 0.48311 | 13.3397 | 13.2423 | 4.1046 | 101.6364 | 0.13029 | 5.761 | 5.761 | 17.277 | 297.0077 | 531 | 558.4588 | -5.1712 | 94.183 | 427.7332 | 95.9608 | 114.907 | 100.357 | 18.438 | 4.699 | 4.697 | 9.396 | 9.396 | 0.093987 | 0.50011 | 14.2754 | 14.1712 | 7.473 | 81.721 | 0.17341 | 5.761 | 5.761 | 32.8679 | 531 | 943.4425 | 1029.3442 | -9.1051 | 88.9336 | 780.1721 | 95.7871 | 100.357 | 58.912 | 18.438 | 1.214 | 3.168 | 4.382 | 4.382 | 0.15105 | 0.27704 | 10.7911 | 10.7123 | 9.9855 | 51.211 | 0.20918 | 5.761 | 6.67 | 105.4541 | 943.4425 | 1389.9227 | 1264.5656 | 9.019 | 64.4945 | 1104.004 | 90.448
[11 empty] | 1998-09-16 | 0:00 | 2537 | 29.342 | 133.33 | 58.882 | 18.364 | 0 | 14.684 | 3.167 |  | 17.851 | 17.851 | 0.82259 | 0 | 13.3491 | 13.2148 | 8.7243 | 69.0177 | 0.19147 | 7.426 | 5.77 | 33.84 | 293.616 | 296.7547 | 1391.7458 | 1515.7758 | -8.9118 | 88.5966 | 906.2653 | 96.266 | 133.33 | 115.095 | 18.364 | 8.787 | 9.502 | 18.289 | 18.289 | 0.09267 | 0.48045 | 13.3473 | 13.2131 | 4.0856 | 101.7629 | 0.12984 | 5.77 | 5.77 | 17.3745 | 296.7547 | 531.9 | 555.1123 | -4.364 | 94.1452 | 425.9335 | 95.9208 | 115.095 | 100.545 | 18.364 | 4.684 | 4.818 | 9.502 | 9.502 | 0.095501 | 0.49295 | 14.2299 | 14.0867 | 7.4164 | 82.0396 | 0.17171 | 5.77 | 5.77 | 32.8477 | 531.9 | 943.4425 | 1017.0725 | -7.8044 | 88.931 | 774.4862 | 95.7588 | 100.545 | 58.882 | 18.364 | 1.213 | 3.167 | 4.38 | 4.38 | 0.15099 | 0.27694 | 10.7822 | 10.6738 | 9.9847 | 51.3648 | 0.2078 | 5.77 | 6.674 | 105.4541 | 943.4425 | 1391.7458 | 1264.4024 | 9.1499 | 64.4642 | 1103.9224 | 90.4473
[11 empty] | 1998-09-16 | 8:00 | 2545 | 29.24 | 133.256 | 58.755 | 18.294 | 0 | 14.694 | 3.167 |  | 17.861 | 17.861 | 0.82269 | 0 | 13.3582 | 13.2638 | 8.7335 | 68.978 | 0.19229 | 6.778 | 5.757 | 33.793 | 294.336 | 296.8608 | 1389.9227 | 1517.4223 | -9.1731 | 88.6166 | 907.1415 | 96.2748 | 133.256 | 115.26 | 18.294 | 8.781 | 9.397 | 18.178 | 18.178 | 0.09195 | 0.48306 | 13.3382 | 13.2439 | 4.1021 | 101.8619 | 0.13002 | 5.757 | 5.757 | 17.277 | 296.8608 | 531 | 558.1171 | -5.1068 | 94.1801 | 427.4889 | 95.9585 | 115.26 | 100.68 | 18.294 | 4.699 | 4.698 | 9.397 | 9.397 | 0.094001 | 0.50005 | 14.2754 | 14.1745 | 7.4726 | 82.2034 | 0.17243 | 5.757 | 5.757 | 32.8652 | 531 | 943.4425 | 1029.2409 | -9.0942 | 88.9291 | 780.1204 | 95.7872 | 100.68 | 58.755 | 18.294 | 1.214 | 3.167 | 4.381 | 4.381 | 0.15101 | 0.27711 | 10.7911 | 10.7148 | 9.986 | 51.4375 | 0.20831 | 5.757 | 6.596 | 105.4541 | 943.4425 | 1389.9227 | 1264.667 | 9.0117 | 64.4769 | 1104.0547 | 90.4485
[11 empty] | 1998-09-16 | 16:00 | 2553 | 29.291 | 133.136 | 58.86 | 18.279 | 0 | 14.618 | 3.167 |  | 17.785 | 17.785 | 0.82193 | 0 | 13.2891 | 13.1753 | 8.6966 | 69.0224 | 0.19088 | 7.295 | 5.759 | 33.8635 | 293.616 | 296.771 | 1392.3533 | 1510.2799 | -8.4696 | 88.5894 | 903.5254 | 96.2521 | 133.136 | 115.185 | 18.279 | 8.721 | 9.691 | 18.412 | 18.412 | 0.093711 | 0.47366 | 13.2471 | 13.1336 | 4.0554 | 101.8261 | 0.12898 | 5.759 | 5.759 | 17.082 | 296.771 | 531.9 | 548.4652 | -3.1143 | 94.244 | 422.6181 | 95.9581 | 115.185 | 100.672 | 18.279 | 4.684 | 5.007 | 9.691 | 9.691 | 0.098022 | 0.48334 | 14.2299 | 14.108 | 7.325 | 82.3245 | 0.17137 | 5.759 | 5.759 | 32.832 | 531.9 | 943.4425 | 998.7732 | -5.8648 | 88.9369 | 765.3366 | 95.7101 | 100.672 | 58.86 | 18.279 | 1.213 | 3.167 | 4.38 | 4.38 | 0.15099 | 0.27694 | 10.7822 | 10.6899 | 9.9847 | 51.5023 | 0.20756 | 5.759 | 6.671 | 105.4541 | 943.4425 | 1392.3533 | 1264.4024 | 9.1895 | 64.4662 | 1103.9224 | 90.4473
[11 empty] | 1998-09-17 | 0:00 | 2561 | 29.274 | 132.754 | 58.68 | 18.052 | 0 | 14.324 | 3.106 |  | 17.43 | 17.43 | 0.8218 | 0 | 13.0218 | 12.9168 | 8.6822 | 68.9828 | 0.18725 | 7.259 | 5.762 | 34.263 | 294.432 | 296.8934 | 1413.6228 | 1508.0713 | -6.6813 | 88.4595 | 902.4824 | 96.2035 | 132.754 | 114.412 | 18.052 | 8.419 | 9.818 | 18.237 | 18.237 | 0.093551 | 0.46164 | 12.7884 | 12.6852 | 3.9936 | 101.5374 | 0.12493 | 5.762 | 5.762 | 17.3745 | 296.8934 | 531.9 | 536.5828 | -0.88039 | 94.1479 | 416.7381 | 95.8308 | 114.412 | 99.945 | 18.052 | 4.698 | 5.12 | 9.818 | 9.818 | 0.099623 | 0.47851 | 14.2724 | 14.1573 | 7.2796 | 81.8469 | 0.17297 | 5.762 | 5.762 | 32.8808 | 531.9 | 943.4425 | 989.7891 | -4.9125 | 88.9251 | 760.8446 | 95.6784 | 99.945 | 58.68 | 18.052 | 1.207 | 3.106 | 4.313 | 4.313 | 0.14843 | 0.27985 | 10.7289 | 10.6423 | 10.0081 | 51.2524 | 0.20765 | 5.762 | 6.61 | 105.4541 | 943.4425 | 1413.6228 | 1269.0871 | 10.2245 | 64.4808 | 1106.2648 | 90.4676
[11 empty] | 1998-09-17 | 8:00 | 2569 | 29.431 | 132.291 | 58.117 | 18.045 | 0 | 14.332 | 3.107 |  | 17.439 | 17.439 | 0.82184 | 0 | 13.0291 | 12.8642 | 8.686 | 68.473 | 0.18787 | 7.64 | 5.753 | 31.678 | 279.792 | 294.3802 | 1346.7762 | 1506.1753 | -11.8356 | 89.2391 | 900.2777 | 96.4813 | 132.291 | 113.677 | 18.045 | 8.421 | 9.93 | 18.351 | 18.351 | 0.094304 | 0.45889 | 12.7914 | 12.6295 | 3.9563 | 100.9827 | 0.12507 | 5.753 | 5.753 | 16.5555 | 294.3802 | 503.1 | 529.9855 | -5.344 | 94.3761 | 412.1829 | 95.9835 | 113.677 | 99.33 | 18.045 | 4.698 | 5.232 | 9.93 | 9.93 | 0.10112 | 0.47311 | 14.2724 | 14.0917 | 6.8174 | 81.6411 | 0.17261 | 5.753 | 5.753 | 32.5993 | 503.1 | 943.4425 | 925.5794 | 1.8934 | 88.9261 | 714.3397 | 95.4364 | 99.33 | 58.117 | 18.045 | 1.213 | 3.107 | 4.32 | 4.32 | 0.14859 | 0.28079 | 10.7822 | 10.6457 | 10.0157 | 50.6628 | 0.21013 | 5.753 | 6.619 | 105.4541 | 943.4425 | 1346.7762 | 1270.6005 | 5.6562 | 64.1776 | 1107.0215 | 90.4741
[11 empty] | 1998-09-17 | 16:00 | 2577 | 29.537 | 133.156 | 58.605 | 18.876 | 0 | 15.039 | 3.167 |  | 18.206 | 18.206 | 0.82605 | 0 | 13.6718 | 13.4565 | 8.8518 | 68.1527 | 0.19745 | 7.816 | 5.769 | 31.866 | 279.264 | 294.1925 | 1340.0915 | 1539.8912 | -14.9094 | 89.1683 | 917.0419 | 96.5251 | 133.156 | 114.727 | 18.876 | 9.139 | 9.146 | 18.285 | 18.285 | 0.09147 | 0.49981 | 13.882 | 13.6634 | 4.16 | 100.9055 | 0.13541 | 5.769 | 5.769 | 16.7895 | 294.1925 | 500.85 | 571.3831 | -14.0827 | 94.293 | 432.7878 | 96.1206 | 114.727 | 100.275 | 18.876 | 4.699 | 4.447 | 9.146 | 9.146 | 0.090653 | 0.51378 | 14.2754 | 14.0506 | 7.1573 | 81.4677 | 0.17247 | 5.769 | 5.769 | 32.5395 | 500.85 | 943.4425 | 995.6985 | -5.5389 | 88.9394 | 748.2742 | 95.6514 | 100.275 | 58.605 | 18.876 | 1.201 | 3.167 | 4.368 | 4.368 | 0.15075 | 0.27495 | 10.6756 | 10.5074 | 9.9688 | 50.5952 | 0.20768 | 5.769 | 6.677 | 105.4541 | 943.4425 | 1340.0915 | 1261.2272 | 5.885 | 64.1547 | 1102.3348 | 90.4336
[11 empty] | 1998-09-18 | 0:00 | 2585 | 29.452 | 133.296 | 58.942 | 18.843 | 0 | 15.059 | 3.107 |  | 18.166 | 18.166 | 0.82897 | 0 | 13.69 | 13.5083 | 8.9941 | 68.2819 | 0.19783 | 7.238 | 5.758 | 31.6545 | 280.56 | 294.3802 | 1335.2299 | 1567.7582 | -17.4149 | 89.2471 | 931.0692 | 96.6002 | 133.296 | 115.192 | 18.843 | 9.14 | 9.098 | 18.238 | 18.238 | 0.091153 | 0.50115 | 13.8835 | 13.6993 | 4.1741 | 101.2269 | 0.13533 | 5.758 | 5.758 | 16.536 | 294.3802 | 502.65 | 573.507 | -14.0967 | 94.3828 | 433.9436 | 96.1894 | 115.192 | 100.567 | 18.843 | 4.699 | 4.399 | 9.098 | 9.098 | 0.090013 | 0.51649 | 14.2754 | 14.086 | 7.2118 | 81.8247 | 0.17215 | 5.758 | 5.758 | 32.5496 | 502.65 | 943.4425 | 1004.81 | -6.5046 | 88.943 | 753.73 | 95.6815 | 100.567 | 58.942 | 18.843 | 1.22 | 3.107 | 4.327 | 4.327 | 0.14873 | 0.28195 | 10.8444 | 10.7005 | 10.0251 | 50.8864 | 0.21028 | 5.758 | 6.643 | 105.4541 | 943.4425 | 1335.2299 | 1272.4885 | 4.6989 | 64.1776 | 1107.9655 | 90.4822
[11 empty] | 1998-09-18 | 8:00 | 2593 | 29.482 | 129.605 | 45.022 | 18.64 | 0 | 15.263 | 3.885 |  | 19.148 | 19.148 | 0.79711 | 0 | 13.8755 | 13.6792 | 7.7793 | 60.8942 | 0.22464 | 7.171 | 5.759 | 32.1245 | 279.84 | 294.5515 | 1336.4455 | 1325.5486 | 0.81536 | 89.0938 | 810.0501 | 96.0343 | 129.605 | 110.955 | 18.64 | 9.44 | 8.605 | 18.045 | 18.045 | 0.088866 | 0.52314 | 14.3392 | 14.1364 | 4.2933 | 97.3467 | 0.14522 | 5.759 | 5.759 | 17.2965 | 294.5515 | 495.45 | 598.7104 | -20.8417 | 94.1279 | 446.631 | 96.1273 | 110.955 | 95.722 | 18.64 | 4.655 | 3.95 | 8.605 | 8.605 | 0.08373 | 0.54096 | 14.1418 | 13.9417 | 7.3664 | 77.3321 | 0.18028 | 5.759 | 5.759 | 31.9314 | 495.45 | 943.4425 | 1041.6979 | -10.4146 | 89.1593 | 768.574 | 95.8454 | 95.722 | 45.022 | 18.64 | 1.168 | 3.885 | 5.053 | 5.053 | 0.17882 | 0.23115 | 10.3822 | 10.2354 | 9.6396 | 42.0924 | 0.24316 | 5.759 | 6.469 | 105.4541 | 943.4425 | 1336.4455 | 1195.3783 | 10.5554 | 64.1984 | 1069.4104 | 90.139
[11 empty] | 1998-09-18 | 16:00 | 2601 | 29.546 | 129.484 | 45.007 | 18.708 | 0 | 15.235 | 3.885 |  | 19.12 | 19.12 | 0.79681 | 0 | 13.85 | 13.6283 | 7.7643 | 60.7732 | 0.22425 | 7.794 | 5.759 | 32.195 | 279.12 | 294.4373 | 1327.3303 | 1322.8185 | 0.33991 | 89.0656 | 808.6279 | 96.0186 | 129.484 | 110.887 | 18.708 | 9.378 | 8.67 | 18.048 | 18.048 | 0.089092 | 0.51961 | 14.2451 | 14.017 | 4.2745 | 97.203 | 0.1442 | 5.759 | 5.759 | 17.0235 | 294.4373 | 492.3 | 594.5049 | -20.7607 | 94.2183 | 444.4711 | 96.1699 | 110.887 | 95.467 | 18.708 | 4.669 | 4.001 | 8.67 | 8.67 | 0.084504 | 0.53852 | 14.1843 | 13.9572 | 7.2898 | 77.1792 | 0.18084 | 5.759 | 5.759 | 31.9323 | 492.3 | 943.4425 | 1029.5299 | -9.1248 | 89.1548 | 760.915 | 95.8034 | 95.467 | 45.007 | 18.708 | 1.188 | 3.885 | 5.073 | 5.073 | 0.17923 | 0.23418 | 10.56 | 10.3909 | 9.6611 | 41.8679 | 0.24818 | 5.759 | 6.472 | 105.4541 | 943.4425 | 1327.3303 | 1199.6922 | 9.6161 | 64.1845 | 1071.5674 | 90.1589
[11 empty] | 1998-09-19 | 0:00 | 2609.0006 | 29.499 | 127.253 | 55.77 | 17.871 | 0 | 14.41 | 3.048 |  | 17.458 | 17.458 | 0.82541 | 0 | 13.1 | 12.9082 | 8.8196 | 64.8209 | 0.19914 | 7.11 | 5.741 | 32.477 | 280.56 | 294.6658 | 1367.4377 | 1534.213 | -12.1962 | 88.9784 | 914.4394 | 96.4484 | 127.253 | 109.447 | 17.871 | 8.541 | 9.207 | 17.748 | 17.748 | 0.089883 | 0.48124 | 12.9737 | 12.7837 | 4.0616 | 96.4174 | 0.13259 | 5.741 | 5.741 | 17.199 | 294.6658 | 502.65 | 552.0616 | -9.8302 | 94.1632 | 423.3637 | 95.9375 | 109.447 | 95.565 | 17.871 | 4.655 | 4.552 | 9.207 | 9.207 | 0.09176 | 0.50559 | 14.1418 | 13.9347 | 7.1052 | 77.5298 | 0.17973 | 5.741 | 5.741 | 32.5165 | 502.65 | 943.4425 | 983.4214 | -4.2376 | 88.965 | 743.0357 | 95.6238 | 95.565 | 55.77 | 17.871 | 1.214 | 3.048 | 4.262 | 4.262 | 0.14625 | 0.28484 | 10.7911 | 10.6331 | 10.0487 | 47.7478 | 0.22269 | 5.741 | 6.465 | 105.4541 | 943.4425 | 1367.4377 | 1277.2082 | 6.5984 | 64.2123 | 1110.3254 | 90.5024
[11 empty] | 1998-09-19 | 8:00 | 2617.0003 | 29.491 | 128.573 | 64.05 | 18.177 | 0 | 14.482 | 2.749 |  | 17.231 | 17.231 | 0.84046 | 0 | 13.1655 | 12.9758 | 9.5104 | 68.6241 | 0.18908 | 6.928 | 5.732 | 32.9705 | 280.704 | 294.6739 | 1392.9613 | 1673.3531 | -20.1292 | 88.8112 | 984.0135 | 96.6494 | 128.573 | 110.962 | 18.177 | 8.606 | 9.019 | 17.625 | 17.625 | 0.088846 | 0.48828 | 13.0724 | 12.8841 | 4.098 | 97.4925 | 0.13215 | 5.732 | 5.732 | 17.238 | 294.6739 | 511.2 | 559.4054 | -9.4299 | 94.1501 | 427.0397 | 95.9634 | 110.962 | 97.95 | 18.177 | 4.669 | 4.35 | 9.019 | 9.019 | 0.089159 | 0.51768 | 14.1843 | 13.9799 | 7.356 | 78.923 | 0.17713 | 5.732 | 5.732 | 32.5036 | 511.2 | 943.4425 | 1025.0008 | -8.6448 | 88.9696 | 768.1004 | 95.7683 | 97.95 | 64.05 | 18.177 | 1.207 | 2.749 | 3.956 | 3.956 | 0.13415 | 0.30511 | 10.7289 | 10.5743 | 10.2196 | 52.6034 | 0.20102 | 5.732 | 6.469 | 105.4541 | 943.4425 | 1392.9613 | 1311.377 | 5.8569 | 64.2133 | 1127.4098 | 90.6463
[11 empty] | 1998-09-19 | 16:00 | 2625 | 29.478 | 127.715 | 58.86 | 17.991 | 0 | 14.478 | 2.986 |  | 17.464 | 17.464 | 0.82902 | 0 | 13.1618 | 12.9772 | 8.9779 | 66.3186 | 0.19568 | 7.192 | 5.748 | 32.5005 | 280.56 | 294.6821 | 1379.592 | 1565.9027 | -13.5048 | 88.971 | 930.2924 | 96.5064 | 127.715 | 110.122 | 17.991 | 8.602 | 9.146 | 17.748 | 17.748 | 0.089679 | 0.48467 | 13.0663 | 12.883 | 4.0789 | 96.8486 | 0.13302 | 5.748 | 5.748 | 17.2575 | 294.6821 | 507.15 | 555.6056 | -9.5545 | 94.1437 | 425.1438 | 95.9408 | 110.122 | 96.495 | 17.991 | 4.669 | 4.477 | 9.146 | 9.146 | 0.090853 | 0.5105 | 14.1843 | 13.9853 | 7.2288 | 78.0887 | 0.1791 | 5.748 | 5.748 | 32.0197 | 507.15 | 943.4425 | 1002.6567 | -6.2764 | 89.1342 | 754.9033 | 95.7584 | 96.495 | 58.86 | 17.991 | 1.207 | 2.986 | 4.193 | 4.193 | 0.14363 | 0.28786 | 10.7289 | 10.5784 | 10.0735 | 49.613 | 0.21322 | 5.748 | 6.539 | 105.4541 | 943.4425 | 1379.592 | 1282.1739 | 7.0614 | 64.2143 | 1112.8082 | 90.5236
[11 empty] | 1998-09-20 | 0:00 | 2633 | 29.516 | 127.668 | 58.83 | 17.946 | 0 | 14.409 | 2.987 |  | 17.396 | 17.396 | 0.82829 | 0 | 13.0991 | 12.9008 | 8.9437 | 66.3593 | 0.19441 | 7.066 | 5.729 | 32.571 | 280.752 | 294.6984 | 1377.1609 | 1559.1757 | -13.2167 | 88.9477 | 926.9371 | 96.4862 | 127.668 | 109.807 | 17.946 | 8.542 | 9.083 | 17.625 | 17.625 | 0.089059 | 0.48465 | 12.9752 | 12.7788 | 4.0784 | 96.7131 | 0.13213 | 5.729 | 5.729 | 17.2965 | 294.6984 | 507.6 | 555.5777 | -9.4519 | 94.1308 | 425.1381 | 95.9316 | 109.807 | 96.322 | 17.946 | 4.654 | 4.429 | 9.083 | 9.083 | 0.090113 | 0.51239 | 14.1387 | 13.9247 | 7.2524 | 77.8661 | 0.17883 | 5.729 | 5.729 | 32.1604 | 507.6 | 943.4425 | 1007.1926 | -6.7572 | 89.087 | 757.3963 | 95.7538 | 96.322 | 58.83 | 17.946 | 1.213 | 2.987 | 4.2 | 4.2 | 0.14379 | 0.28881 | 10.7822 | 10.619 | 10.0814 | 49.5486 | 0.21432 | 5.729 | 6.396 | 105.4541 | 943.4425 | 1377.1609 | 1283.7438 | 6.7833 | 64.2163 | 1113.5931 | 90.5303
[11 empty] | 1998-09-20 | 8:00 | 2641 | 29.389 | 135.032 | 65.505 | 18.741 | 0 | 14.885 | 2.867 |  | 17.752 | 17.752 | 0.8385 | 0 | 13.5318 | 13.3771 | 9.4285 | 72.099 | 0.18554 | 7.299 | 5.751 | 34.686 | 294.384 | 296.8853 | 1423.9535 | 1658.1815 | -16.4491 | 88.3167 | 977.5334 | 96.4517 | 135.032 | 116.542 | 18.741 | 8.96 | 9.322 | 18.282 | 18.282 | 0.092047 | 0.4901 | 13.6101 | 13.4545 | 4.139 | 102.907 | 0.13074 | 5.751 | 5.751 | 17.3355 | 296.8853 | 540 | 565.5793 | -4.7369 | 94.1609 | 431.2323 | 95.98 | 116.542 | 102.6 | 18.741 | 4.712 | 4.61 | 9.322 | 9.322 | 0.092914 | 0.50547 | 14.3149 | 14.1513 | 7.6644 | 83.1656 | 0.17016 | 5.751 | 5.751 | 32.7824 | 540 | 943.4425 | 1058.4402 | -12.1892 | 88.9579 | 799.2201 | 95.8982 | 102.6 | 65.505 | 18.741 | 1.213 | 2.867 | 4.08 | 4.08 | 0.13899 | 0.2973 | 10.7822 | 10.659 | 10.1526 | 55.1589 | 0.19324 | 5.751 | 6.597 | 105.4541 | 943.4425 | 1423.9535 | 1297.9873 | 8.8462 | 64.4799 | 1120.7149 | 90.5905
[11 empty] | 1998-09-20 | 16:00 | 2649 | 29.567 | 134.402 | 65.145 | 18.868 | 0 | 14.901 | 2.927 |  | 17.828 | 17.828 | 0.83582 | 0 | 13.5464 | 13.3212 | 9.2886 | 71.6169 | 0.18601 | 7.76 | 5.757 | 32.3595 | 279.36 | 294.3475 | 1362.5766 | 1628.0966 | -19.4866 | 89.0064 | 961.222 | 96.6335 | 134.402 | 116.197 | 18.868 | 8.962 | 9.321 | 18.283 | 18.283 | 0.092047 | 0.49018 | 13.6132 | 13.3869 | 4.1093 | 102.3222 | 0.13083 | 5.757 | 5.757 | 16.8285 | 294.3475 | 509.4 | 561.1778 | -10.1645 | 94.2828 | 427.7627 | 96.0659 | 116.197 | 102.195 | 18.868 | 4.713 | 4.608 | 9.321 | 9.321 | 0.092894 | 0.50563 | 14.318 | 14.08 | 7.2129 | 83.1151 | 0.1694 | 5.757 | 5.757 | 32.1632 | 509.4 | 943.4425 | 997.5113 | -5.731 | 89.0731 | 753.4557 | 95.7312 | 102.195 | 65.145 | 18.868 | 1.226 | 2.927 | 4.153 | 4.153 | 0.14165 | 0.29521 | 10.8978 | 10.7167 | 10.1349 | 54.6671 | 0.19603 | 5.757 | 6.667 | 105.4541 | 943.4425 | 1362.5766 | 1294.4414 | 5.0005 | 64.1736 | 1118.942 | 90.5756
[11 empty] | 1998-09-21 | 0:00 | 2657 | 29.529 | 134.462 | 65.37 | 18.894 | 0 | 14.912 | 2.928 |  | 17.84 | 17.84 | 0.83587 | 0 | 13.5564 | 13.346 | 9.3183 | 71.7037 | 0.18613 | 7.474 | 5.743 | 31.8425 | 280.896 | 294.5923 | 1360.1455 | 1632.7499 | -20.0423 | 89.191 | 963.6711 | 96.6957 | 134.462 | 116.167 | 18.894 | 8.959 | 9.21 | 18.169 | 18.169 | 0.091296 | 0.49309 | 13.6086 | 13.3975 | 4.1301 | 102.2904 | 0.13097 | 5.743 | 5.743 | 16.731 | 294.5923 | 512.1 | 564.8811 | -10.3068 | 94.3206 | 429.7367 | 96.1067 | 116.167 | 102.15 | 18.894 | 4.727 | 4.483 | 9.21 | 9.21 | 0.09132 | 0.51325 | 14.3605 | 14.1377 | 7.3286 | 82.9359 | 0.17047 | 5.743 | 5.743 | 32.2294 | 512.1 | 934.7975 | 1018.0889 | -8.9101 | 89.0596 | 765.0944 | 95.7875 | 102.15 | 65.37 | 18.894 | 1.226 | 2.928 | 4.154 | 4.154 | 0.14169 | 0.29514 | 10.8978 | 10.7287 | 10.044 | 54.822 | 0.1957 | 5.743 | 6.61 | 104.2762 | 934.7975 | 1360.1455 | 1282.5499 | 5.7049 | 64.6032 | 1108.6737 | 90.5945
[11 empty] | 1998-09-21 | 8:00 | 2665 | 29.308 | 134.918 | 65.805 | 18.648 | 0 | 14.886 | 2.867 |  | 17.753 | 17.753 | 0.83851 | 0 | 13.5327 | 13.4101 | 9.4494 | 72.2641 | 0.18557 | 7.471 | 5.748 | 34.263 | 295.248 | 297.0322 | 1413.6228 | 1661.3788 | -17.5263 | 88.4649 | 979.2055 | 96.5009 | 134.918 | 117 | 18.648 | 8.961 | 9.27 | 18.231 | 18.231 | 0.091703 | 0.49153 | 13.6116 | 13.4883 | 4.1488 | 103.1622 | 0.13075 | 5.748 | 5.748 | 17.3355 | 297.0322 | 539.55 | 567.4056 | -5.1627 | 94.1638 | 432.2189 | 95.9892 | 117 | 102.952 | 18.648 | 4.712 | 4.558 | 9.27 | 9.27 | 0.09222 | 0.50831 | 14.3149 | 14.1852 | 7.6812 | 83.6468 | 0.16958 | 5.748 | 5.748 | 33.1734 | 539.55 | 993.9475 | 1063.0355 | -6.9509 | 88.8317 | 801.2927 | 95.86 | 102.952 | 65.805 | 18.648 | 1.213 | 2.867 | 4.08 | 4.08 | 0.13899 | 0.2973 | 10.7822 | 10.6845 | 10.7554 | 54.9751 | 0.19435 | 5.748 | 6.511 | 106.2029 | 993.9475 | 1413.6228 | 1369.5437 | 3.1182 | 64.2453 | 1181.7456 | 91.0131
[11 empty] | 1998-09-21 | 16:00 | 2673 | 29.588 | 132.03 | 54.51 | 17.998 | 0 | 14.387 | 3.345 |  | 17.732 | 17.732 | 0.81136 | 0 | 13.0791 | 12.8537 | 8.2584 | 67.0136 | 0.19181 | 8.354 | 5.779 | 31.96 | 278.736 | 294.0864 | 1353.4609 | 1421.5042 | -5.0274 | 89.1324 | 857.7953 | 96.2742 | 132.03 | 113.377 | 17.998 | 8.482 | 9.801 | 18.283 | 18.283 | 0.093647 | 0.46393 | 12.8841 | 12.6621 | 3.9712 | 100.7343 | 0.1257 | 5.779 | 5.779 | 16.9065 | 294.0864 | 501.75 | 533.964 | -6.4203 | 94.2512 | 414.0252 | 95.9166 | 113.377 | 98.625 | 17.998 | 4.698 | 5.103 | 9.801 | 9.801 | 0.099396 | 0.47934 | 14.2724 | 14.0265 | 6.8539 | 81.1491 | 0.17285 | 5.779 | 5.779 | 32.4088 | 501.75 | 880.1975 | 933.8419 | -6.0946 | 88.9798 | 717.7959 | 95.485 | 98.625 | 54.51 | 17.998 | 1.207 | 3.345 | 4.552 | 4.552 | 0.158 | 0.26516 | 10.7289 | 10.544 | 9.1631 | 49.4064 | 0.21341 | 5.779 | 6.681 | 103.9363 | 880.1975 | 1353.4609 | 1160.3013 | 14.2715 | 64.6579 | 1020.2494 | 89.8127
[11 empty] | 1998-09-22 | 0:00 | 2681 | 29.508 | 132.539 | 55.005 | 18.061 | 0 | 14.375 | 3.408 |  | 17.783 | 17.783 | 0.80836 | 0 | 13.0682 | 12.8734 | 8.1703 | 67.5407 | 0.1906 | 7.758 | 5.762 | 31.772 | 280.8 | 294.5678 | 1348.5992 | 1403.045 | -4.0372 | 89.214 | 848.8064 | 96.2569 | 132.539 | 113.782 | 18.061 | 8.479 | 9.801 | 18.28 | 18.28 | 0.093637 | 0.46384 | 12.8795 | 12.6875 | 3.981 | 101.1185 | 0.12547 | 5.762 | 5.762 | 16.6725 | 294.5678 | 504 | 534.9795 | -6.1467 | 94.34 | 414.7737 | 95.9803 | 113.782 | 98.977 | 18.061 | 4.683 | 5.118 | 9.801 | 9.801 | 0.099496 | 0.47781 | 14.2268 | 14.0148 | 6.873 | 81.4455 | 0.17208 | 5.762 | 5.762 | 32.4392 | 504 | 890.2075 | 935.4809 | -5.0857 | 88.9875 | 719.7404 | 95.4929 | 98.977 | 55.005 | 18.061 | 1.213 | 3.408 | 4.621 | 4.621 | 0.16064 | 0.2625 | 10.7822 | 10.6215 | 9.2616 | 49.6684 | 0.21385 | 5.762 | 6.649 | 103.968 | 890.2075 | 1348.5992 | 1170.0515 | 13.2395 | 64.7049 | 1030.1295 | 89.9073
[11 empty] | 1998-09-22 | 8:00 | 2689 | 29.533 | 132.338 | 54.787 | 17.989 | 0 | 14.384 | 3.407 |  | 17.791 | 17.791 | 0.8085 | 0 | 13.0764 | 12.872 | 8.1711 | 67.4024 | 0.19097 | 7.206 | 5.764 | 31.7485 | 280.752 | 294.4046 | 1348.5992 | 1403.3116 | -4.057 | 89.216 | 848.8581 | 96.2599 | 132.338 | 113.745 | 17.989 | 8.479 | 9.99 | 18.469 | 18.469 | 0.094898 | 0.45909 | 12.8795 | 12.6782 | 3.9573 | 101.0952 | 0.12541 | 5.764 | 5.764 | 16.575 | 294.4046 | 503.55 | 530.2122 | -5.2948 | 94.37 | 412.3084 | 95.98 | 113.745 | 98.857 | 17.989 | 4.698 | 5.292 | 9.99 | 9.99 | 0.10192 | 0.47027 | 14.2724 | 14.0493 | 6.8025 | 81.5095 | 0.17236 | 5.764 | 5.764 | 32.4236 | 503.55 | 886.1125 | 921.7949 | -4.0268 | 88.9867 | 712.6725 | 95.4504 | 98.857 | 54.787 | 17.989 | 1.207 | 3.407 | 4.614 | 4.614 | 0.16048 | 0.2616 | 10.7289 | 10.5612 | 9.2081 | 49.6249 | 0.21282 | 5.764 | 6.618 | 103.8643 | 886.1125 | 1348.5992 | 1163.24 | 13.7446 | 64.7206 | 1024.6763 | 89.8637
[11 empty] | 1998-09-22 | 16:00 | 2697 | 29.605 | 132.157 | 54.637 | 18.025 | 0 | 14.389 | 3.345 |  | 17.734 | 17.734 | 0.81138 | 0 | 13.0809 | 12.8491 | 8.264 | 67.108 | 0.19147 | 7.945 | 5.776 | 31.9365 | 279.36 | 294.217 | 1352.2453 | 1422.4542 | -5.192 | 89.1453 | 858.3356 | 96.2793 | 132.157 | 113.512 | 18.025 | 8.484 | 9.924 | 18.408 | 18.408 | 0.094474 | 0.46089 | 12.8871 | 12.6587 | 3.959 | 100.8505 | 0.12552 | 5.776 | 5.776 | 16.8675 | 294.217 | 501.75 | 531.3222 | -5.8938 | 94.267 | 412.7696 | 95.9136 | 113.512 | 98.595 | 18.025 | 4.698 | 5.226 | 9.924 | 9.924 | 0.10104 | 0.4734 | 14.2724 | 14.0194 | 6.803 | 81.2255 | 0.1726 | 5.776 | 5.776 | 32.4116 | 501.75 | 879.7425 | 923.6696 | -4.9932 | 88.9838 | 712.7098 | 95.4523 | 98.595 | 54.637 | 18.025 | 1.207 | 3.345 | 4.552 | 4.552 | 0.158 | 0.26516 | 10.7289 | 10.5387 | 9.159 | 49.432 | 0.2132 | 5.776 | 6.705 | 103.8326 | 879.7425 | 1352.2453 | 1159.7195 | 14.2375 | 64.7088 | 1019.731 | 89.8176
[11 empty] | 1998-09-23 | 0:00 | 2705 | 29.401 | 132.64 | 54.93 | 18.001 | 0 | 14.393 | 3.407 |  | 17.8 | 17.8 | 0.8086 | 0 | 13.0845 | 12.9304 | 8.1793 | 67.6047 | 0.19126 | 8.155 | 5.757 | 32.665 | 286.032 | 295.4736 | 1361.3611 | 1405.7184 | -3.2583 | 88.9449 | 850.596 | 96.1598 | 132.64 | 114.075 | 18.001 | 8.481 | 10.101 | 18.582 | 18.582 | 0.095645 | 0.45641 | 12.8825 | 12.7307 | 3.9576 | 101.3989 | 0.12555 | 5.757 | 5.757 | 16.731 | 295.4736 | 513 | 529.5114 | -3.2186 | 94.3376 | 412.4925 | 95.9439 | 114.075 | 99.082 | 18.001 | 4.698 | 5.403 | 10.101 | 10.101 | 0.1034 | 0.4651 | 14.2724 | 14.1042 | 6.8934 | 81.6841 | 0.17267 | 5.757 | 5.757 | 32.5395 | 513 | 907.0425 | 930.7686 | -2.6158 | 88.9873 | 721.8843 | 95.4924 | 99.082 | 54.93 | 18.001 | 1.214 | 3.407 | 4.621 | 4.621 | 0.16062 | 0.26271 | 10.7911 | 10.664 | 9.4549 | 49.5501 | 0.21522 | 5.757 | 6.575 | 104.5325 | 907.0425 | 1361.3611 | 1192.9971 | 12.3673 | 64.6221 | 1050.0198 | 90.0447
[11 empty] | 1998-09-23 | 8:00 | 2713 | 29.359 | 132.76 | 55.102 | 18.013 | 0 | 14.453 | 3.407 |  | 17.86 | 17.86 | 0.80924 | 0 | 13.1391 | 13.0004 | 8.2034 | 67.7146 | 0.19199 | 8.067 | 5.753 | 32.5945 | 285.936 | 295.4328 | 1359.538 | 1410.4319 | -3.7435 | 88.9672 | 852.9324 | 96.1785 | 132.76 | 114.135 | 18.013 | 8.541 | 9.742 | 18.283 | 18.283 | 0.093451 | 0.46716 | 12.9737 | 12.8367 | 4.0101 | 101.4244 | 0.12656 | 5.753 | 5.753 | 16.6335 | 295.4328 | 515.7 | 539.8615 | -4.6852 | 94.3698 | 417.6472 | 96.0173 | 114.135 | 99.352 | 18.013 | 4.698 | 5.044 | 9.742 | 9.742 | 0.098609 | 0.48224 | 14.2724 | 14.1218 | 7.0817 | 81.6488 | 0.17296 | 5.753 | 5.753 | 32.5358 | 515.7 | 906.36 | 965.7209 | -6.5494 | 88.9871 | 740.7104 | 95.6075 | 99.352 | 55.102 | 18.013 | 1.214 | 3.407 | 4.621 | 4.621 | 0.16062 | 0.26271 | 10.7911 | 10.6772 | 9.4469 | 49.7671 | 0.21454 | 5.753 | 6.547 | 104.5238 | 906.36 | 1359.538 | 1192.0744 | 12.3177 | 64.6201 | 1049.2172 | 90.0379
[11 empty] | 1998-09-23 | 16:00 | 2721 | 29.427 | 132.633 | 54.802 | 18.04 | 0 | 14.329 | 3.406 |  | 17.735 | 17.735 | 0.80795 | 0 | 13.0264 | 12.863 | 8.1412 | 67.5363 | 0.19046 | 8.066 | 5.776 | 32.759 | 284.4 | 295.0819 | 1374.1223 | 1398.6712 | -1.7865 | 88.8983 | 846.8766 | 96.1318 | 132.633 | 113.985 | 18.04 | 8.417 | 9.811 | 18.228 | 18.228 | 0.093497 | 0.46176 | 12.7853 | 12.625 | 3.9758 | 101.2932 | 0.12464 | 5.776 | 5.776 | 16.848 | 295.0819 | 513.45 | 533.7829 | -3.96 | 94.2904 | 414.4324 | 95.9347 | 113.985 | 99.112 | 18.04 | 4.698 | 5.113 | 9.811 | 9.811 | 0.099529 | 0.47885 | 14.2724 | 14.0934 | 7.0187 | 81.4898 | 0.17295 | 5.776 | 5.776 | 32.5248 | 513.45 | 899.7625 | 955.3406 | -6.177 | 88.9777 | 734.3953 | 95.5712 | 99.112 | 54.802 | 18.04 | 1.214 | 3.406 | 4.62 | 4.62 | 0.16058 | 0.26277 | 10.7911 | 10.6558 | 9.37 | 49.547 | 0.21506 | 5.776 | 6.656 | 104.495 | 899.7625 | 1374.1223 | 1183.2195 | 13.8927 | 64.5878 | 1041.491 | 89.9668
[11 empty] | 1998-09-24 | 0:00 | 2729 | 29.35 | 133.015 | 55.147 | 18.012 | 0 | 14.386 | 3.407 |  | 17.793 | 17.793 | 0.80852 | 0 | 13.0782 | 12.9436 | 8.1792 | 67.8898 | 0.19066 | 7.439 | 5.767 | 33.887 | 295.008 | 296.7792 | 1392.9613 | 1406.8371 | -0.99613 | 88.5817 | 851.8081 | 96.0218 | 133.015 | 114.42 | 18.012 | 8.481 | 9.988 | 18.469 | 18.469 | 0.094891 | 0.4592 | 12.8825 | 12.7499 | 3.9845 | 101.721 | 0.12534 | 5.767 | 5.767 | 17.082 | 296.7792 | 528.3 | 534.2754 | -1.1311 | 94.2442 | 415.5273 | 95.8891 | 114.42 | 99.607 | 18.012 | 4.698 | 5.29 | 9.988 | 9.988 | 0.10189 | 0.47036 | 14.2724 | 14.1255 | 7.1567 | 81.8448 | 0.17259 | 5.767 | 5.767 | 32.7014 | 528.3 | 934.7975 | 968.4365 | -3.5985 | 88.9812 | 748.3683 | 95.6303 | 99.607 | 55.147 | 18.012 | 1.207 | 3.407 | 4.614 | 4.614 | 0.16048 | 0.2616 | 10.7289 | 10.6185 | 9.7626 | 49.6024 | 0.21407 | 5.767 | 6.625 | 105.4454 | 934.7975 | 1392.9613 | 1228.6126 | 11.7985 | 64.4701 | 1081.705 | 90.2519
[11 empty] | 1998-09-24 | 8:00 | 2737 | 29.346 | 132.539 | 54.72 | 17.904 | 0 | 14.376 | 3.407 |  | 17.783 | 17.783 | 0.80841 | 0 | 13.0691 | 12.9361 | 8.1691 | 67.5564 | 0.19149 | 6.565 | 5.764 | 32.618 | 285.936 | 295.3104 | 1360.1455 | 1403.7536 | -3.2061 | 88.9547 | 849.532 | 96.1605 | 132.539 | 113.962 | 17.904 | 8.48 | 9.806 | 18.286 | 18.286 | 0.093674 | 0.46374 | 12.881 | 12.7499 | 3.9912 | 101.3553 | 0.12579 | 5.764 | 5.764 | 16.6725 | 295.3104 | 512.1 | 536.27 | -4.7198 | 94.3542 | 415.7902 | 95.9902 | 113.962 | 99.172 | 17.904 | 4.683 | 5.123 | 9.806 | 9.806 | 0.099563 | 0.47756 | 14.2268 | 14.0821 | 6.9875 | 81.6755 | 0.17241 | 5.764 | 5.764 | 32.5386 | 512.1 | 902.9475 | 950.4733 | -5.2634 | 88.9816 | 731.2866 | 95.5505 | 99.172 | 54.72 | 17.904 | 1.213 | 3.407 | 4.62 | 4.62 | 0.1606 | 0.26255 | 10.7822 | 10.6725 | 9.4062 | 49.6358 | 0.21502 | 5.764 | 6.6 | 104.4662 | 902.9475 | 1360.1455 | 1187.2321 | 12.7129 | 64.6249 | 1045.0898 | 90.0041
[11 empty] | 1998-09-24 | 16:00 | 2745 | 29.486 | 132.379 | 54.54 | 17.944 | 0 | 14.394 | 3.346 |  | 17.74 | 17.74 | 0.81139 | 0 | 13.0855 | 12.8988 | 8.271 | 67.2445 | 0.19182 | 8.078 | 5.761 | 32.7355 | 285.312 | 295.2288 | 1373.5148 | 1424.4364 | -3.7074 | 88.9118 | 859.8326 | 96.1928 | 132.379 | 113.595 | 17.944 | 8.482 | 9.989 | 18.471 | 18.471 | 0.094901 | 0.45921 | 12.8841 | 12.7003 | 3.9654 | 101.0776 | 0.12565 | 5.761 | 5.761 | 16.8675 | 295.2288 | 513.45 | 531.5949 | -3.5339 | 94.2866 | 413.4118 | 95.9199 | 113.595 | 98.7 | 17.944 | 4.698 | 5.291 | 9.989 | 9.989 | 0.1019 | 0.47032 | 14.2724 | 14.0688 | 6.9441 | 81.2594 | 0.17314 | 5.761 | 5.761 | 32.5404 | 513.45 | 904.085 | 940.4606 | -4.0235 | 88.9779 | 726.9553 | 95.5237 | 98.7 | 54.54 | 17.944 | 1.214 | 3.346 | 4.56 | 4.56 | 0.15818 | 0.26623 | 10.7911 | 10.6372 | 9.447 | 49.229 | 0.21608 | 5.761 | 6.58 | 104.4461 | 904.085 | 1373.5148 | 1194.211 | 13.0544 | 64.622 | 1049.148 | 90.0447
[11 empty] | 1998-09-25 | 0:00 | 2753 | 29.431 | 132.479 | 54.795 | 18.031 | 0 | 14.395 | 3.407 |  | 17.802 | 17.802 | 0.80862 | 0 | 13.0864 | 12.9207 | 8.1815 | 67.4245 | 0.19163 | 8.323 | 5.752 | 32.5945 | 285.936 | 295.4491 | 1369.8688 | 1406.0427 | -2.6407 | 88.9678 | 850.7459 | 96.1687 | 132.479 | 113.857 | 18.031 | 8.482 | 9.932 | 18.414 | 18.414 | 0.094521 | 0.46063 | 12.8841 | 12.721 | 3.9779 | 101.1591 | 0.12575 | 5.752 | 5.752 | 16.692 | 295.4491 | 515.7 | 533.5097 | -3.4535 | 94.3503 | 414.4794 | 95.9728 | 113.857 | 98.835 | 18.031 | 4.699 | 5.233 | 9.932 | 9.932 | 0.10114 | 0.47312 | 14.2754 | 14.0947 | 7.0009 | 81.3141 | 0.17334 | 5.752 | 5.752 | 32.5376 | 515.7 | 906.36 | 949.5582 | -4.7661 | 88.9871 | 732.6291 | 95.5588 | 98.835 | 54.795 | 18.031 | 1.214 | 3.407 | 4.621 | 4.621 | 0.16062 | 0.26271 | 10.7911 | 10.6545 | 9.4476 | 49.3364 | 0.21596 | 5.752 | 6.498 | 104.4662 | 906.36 | 1369.8688 | 1192.095 | 12.9774 | 64.6415 | 1049.2275 | 90.0435
[11 empty] | 1998-09-26 | 0:21 | 2777.3492 | 29.372 | 134.858 | 71.062 | 18.946 | 0 | 14.691 | 2.748 |  | 17.439 | 17.439 | 0.84242 | 0 | 13.3555 | 13.2094 | 9.6065 | 74.4075 | 0.17753 | 8.243 | 5.786 | 35.5085 | 296.208 | 297.0485 | 1451.9077 | 1695.2595 | -16.7608 | 88.0462 | 996.154 | 96.4354 | 134.858 | 117.285 | 18.946 | 8.778 | 11.29 | 20.068 | 20.068 | 0.10456 | 0.43741 | 13.3337 | 13.1879 | 3.8788 | 103.2467 | 0.12773 | 5.786 | 5.786 | 17.745 | 297.0485 | 540 | 514.2076 | 4.7764 | 94.0262 | 405.628 | 95.6253 | 117.285 | 104.452 | 18.946 | 4.712 | 6.578 | 11.29 | 11.29 | 0.11916 | 0.41736 | 14.3149 | 14.1584 | 6.8877 | 85.0348 | 0.1665 | 5.786 | 5.786 | 32.8688 | 540 | 978.705 | 903.2718 | 7.7074 | 88.9349 | 721.6359 | 95.4452 | 104.452 | 71.062 | 18.946 | 1.233 | 2.748 | 3.981 | 3.981 | 0.13463 | 0.30972 | 10.96 | 10.8401 | 10.6548 | 58.1562 | 0.1864 | 5.786 | 6.536 | 108.4608 | 978.705 | 1451.9077 | 1369.1748 | 5.6982 | 63.4872 | 1173.9399 | 90.761
[11 empty] | 1998-09-26 | 0:26 | 2777.4364 | 29.372 | 134.858 | 71.062 | 18.516 | 0 | 14.605 | 2.748 |  | 17.353 | 17.353 | 0.84164 | 0 | 13.2773 | 13.1321 | 9.3979 | 75.0461 | 0.17499 | 8.243 | 5.786 | 40.091 | 296.208 | 297.0485 | 1451.9077 | 1662.7195 | -14.5196 | 86.5035 | 979.884 | 95.9086 | 134.858 | 117.285 | 18.516 | 8.778 | 11.29 | 20.068 | 20.068 | 0.10456 | 0.43741 | 13.3337 | 13.1879 | 3.8788 | 103.6767 | 0.1272 | 5.786 | 5.786 | 17.745 | 297.0485 | 540 | 514.2076 | 4.7764 | 94.0262 | 405.628 | 95.6253 | 117.285 | 99.945 | 18.516 | 4.626 | 6.664 | 11.29 | 11.29 | 0.11974 | 0.40974 | 14.0537 | 13.9 | 6.7995 | 83.2995 | 0.16687 | 5.786 | 5.786 | 35.247 | 540 | 1134.0875 | 890.3882 | 21.4886 | 88.1342 | 715.1941 | 95.0717 | 99.945 | 71.062 | 18.516 | 1.239 | 2.748 | 3.987 | 3.987 | 0.13475 | 0.31076 | 11.0133 | 10.8929 | 12.466 | 54.5215 | 0.19979 | 5.786 | 6.536 | 116.8157 | 1134.0875 | 1451.9077 | 1592.7483 | -9.7004 | 60.6745 | 1363.4179 | 91.4321
[11 empty] | 1998-09-26 | 0:29 | 2777.4803 | 29.372 | 134.858 | 71.062 | 17.25 | 0 | 14.649 | 2.748 |  | 17.397 | 17.397 | 0.84204 | 0 | 13.3173 | 13.1716 | 9.4797 | 76.2303 | 0.17279 | 8.243 | 5.786 | 38.4225 | 296.208 | 297.0485 | 1451.9077 | 1675.7282 | -15.4156 | 87.0652 | 986.3884 | 96.1047 | 134.858 | 117.285 | 17.25 | 8.778 | 11.29 | 20.068 | 20.068 | 0.10456 | 0.43741 | 13.3337 | 13.1879 | 3.8788 | 104.9427 | 0.12567 | 5.786 | 5.786 | 17.745 | 297.0485 | 540 | 514.2076 | 4.7764 | 94.0262 | 405.628 | 95.6253 | 117.285 | 95.385 | 17.25 | 4.683 | 6.607 | 11.29 | 11.29 | 0.11936 | 0.41479 | 14.2268 | 14.0713 | 6.8406 | 82.2444 | 0.17109 | 5.786 | 5.786 | 34.9315 | 540 | 1110.2 | 897.9894 | 19.1146 | 88.2405 | 718.9947 | 95.1416 | 95.385 | 71.062 | 17.25 | 1.2 | 2.748 | 3.948 | 3.948 | 0.13397 | 0.30395 | 10.6667 | 10.55 | 12.1422 | 53.8313 | 0.19598 | 5.786 | 6.536 | 113.5814 | 1110.2 | 1451.9077 | 1545.4046 | -6.4396 | 61.7633 | 1327.8023 | 91.4459
[11 empty] | 1998-09-26 | 8:00 | 2785 | 29.338 | 132.472 | 49.387 | 18.585 | 0 | 14.83 | 3.764 |  | 18.594 | 18.594 | 0.79757 | 0 | 13.4818 | 13.3478 | 7.8053 | 64.5392 | 0.20682 | 8.114 | 5.751 | 32.6415 | 285.936 | 295.4491 | 1349.2073 | 1330.9 | 1.3569 | 88.9519 | 813.1745 | 95.9859 | 132.472 | 113.617 | 18.585 | 8.958 | 9.621 | 18.579 | 18.579 | 0.094034 | 0.48216 | 13.6071 | 13.4718 | 4.0799 | 100.3796 | 0.13421 | 5.751 | 5.751 | 17.0625 | 295.4491 | 512.1 | 554.6516 | -8.3092 | 94.2249 | 425.0504 | 95.9858 | 113.617 | 98.325 | 18.585 | 4.684 | 4.937 | 9.621 | 9.621 | 0.097089 | 0.48685 | 14.2299 | 14.0884 | 7.0746 | 80.3114 | 0.17542 | 5.751 | 5.751 | 32.2607 | 512.1 | 886.795 | 967.3496 | -9.0838 | 89.0808 | 739.7248 | 95.6388 | 98.325 | 49.387 | 18.585 | 1.194 | 3.764 | 4.958 | 4.958 | 0.1745 | 0.24082 | 10.6133 | 10.5078 | 9.0616 | 46.2094 | 0.2274 | 5.751 | 6.449 | 104.6851 | 886.795 | 1349.2073 | 1134.8926 | 15.8845 | 64.5675 | 1010.8438 | 89.6438
[11 empty] | 1998-09-26 | 16:00 | 2793 | 29.397 | 132.385 | 49.402 | 18.466 | 0 | 14.84 | 3.764 |  | 18.604 | 18.604 | 0.79768 | 0 | 13.4909 | 13.3335 | 7.8029 | 64.6246 | 0.20632 | 8.273 | 5.763 | 32.759 | 285.36 | 295.3675 | 1352.2453 | 1330.7316 | 1.591 | 88.9091 | 813.0496 | 95.9708 | 132.385 | 113.46 | 18.466 | 8.963 | 9.617 | 18.58 | 18.58 | 0.094024 | 0.4824 | 13.6147 | 13.4559 | 4.0774 | 100.3791 | 0.13405 | 5.763 | 5.763 | 17.238 | 295.3675 | 509.4 | 554.583 | -8.8698 | 94.1639 | 424.9752 | 95.9438 | 113.46 | 98.04 | 18.466 | 4.683 | 4.934 | 9.617 | 9.617 | 0.097042 | 0.48695 | 14.2268 | 14.0609 | 7.0359 | 80.2481 | 0.17522 | 5.763 | 5.763 | 32.2497 | 509.4 | 884.065 | 962.277 | -8.8469 | 89.0815 | 735.8385 | 95.6173 | 98.04 | 49.402 | 18.466 | 1.207 | 3.764 | 4.971 | 4.971 | 0.17476 | 0.24281 | 10.7289 | 10.6037 | 9.0444 | 46.2106 | 0.22947 | 5.763 | 6.517 | 104.5987 | 884.065 | 1352.2453 | 1134.0161 | 16.1383 | 64.5869 | 1009.0405 | 89.6338
[11 empty] | 1998-09-27 | 0:00 | 2801.0003 | 29.393 | 132.513 | 49.59 | 18.477 | 0 | 14.864 | 3.825 |  | 18.689 | 18.689 | 0.79533 | 0 | 13.5127 | 13.3567 | 7.7397 | 64.8348 | 0.20601 | 8.187 | 5.751 | 32.618 | 286.896 | 295.6042 | 1349.8148 | 1317.5718 | 2.3887 | 88.9656 | 806.588 | 95.9561 | 132.513 | 113.632 | 18.477 | 8.959 | 9.678 | 18.637 | 18.637 | 0.094418 | 0.48071 | 13.6086 | 13.4514 | 4.0741 | 100.5214 | 0.13382 | 5.751 | 5.751 | 17.1015 | 295.6042 | 512.55 | 553.4162 | -7.9731 | 94.2147 | 424.5102 | 95.9715 | 113.632 | 98.385 | 18.477 | 4.698 | 4.98 | 9.678 | 9.678 | 0.097756 | 0.48543 | 14.2724 | 14.1076 | 7.0683 | 80.4632 | 0.17533 | 5.751 | 5.751 | 32.2616 | 512.55 | 887.25 | 965.6413 | -8.8353 | 89.0862 | 739.0957 | 95.635 | 98.385 | 49.59 | 18.477 | 1.181 | 3.825 | 5.006 | 5.006 | 0.17668 | 0.23592 | 10.4978 | 10.3765 | 9.035 | 46.4755 | 0.22327 | 5.751 | 6.462 | 104.5814 | 887.25 | 1349.8148 | 1128.9053 | 16.3659 | 64.6211 | 1008.0777 | 89.6257
[11 empty] | 1998-09-27 | 8:00 | 2809 | 29.512 | 132.131 | 49.117 | 18.499 | 0 | 14.85 | 3.764 |  | 18.614 | 18.614 | 0.79779 | 0 | 13.5 | 13.2972 | 7.812 | 64.313 | 0.20676 | 8.382 | 5.751 | 31.772 | 280.848 | 294.5678 | 1327.9378 | 1331.3686 | -0.25836 | 89.214 | 812.9682 | 96.0919 | 132.131 | 113.37 | 18.499 | 8.96 | 9.617 | 18.577 | 18.577 | 0.094014 | 0.48232 | 13.6101 | 13.4057 | 4.0729 | 100.1786 | 0.13382 | 5.751 | 5.751 | 16.7115 | 294.5678 | 500.4 | 553.442 | -10.5999 | 94.3268 | 424.0049 | 96.0587 | 113.37 | 98.122 | 18.499 | 4.683 | 4.934 | 9.617 | 9.617 | 0.097042 | 0.48695 | 14.2268 | 14.0131 | 6.9047 | 80.3423 | 0.17442 | 5.751 | 5.751 | 32.1457 | 500.4 | 866.775 | 944.8335 | -9.0056 | 89.0872 | 722.6167 | 95.5515 | 98.122 | 49.117 | 18.499 | 1.201 | 3.764 | 4.965 | 4.965 | 0.17464 | 0.24189 | 10.6756 | 10.5152 | 8.8479 | 46.2726 | 0.22724 | 5.751 | 6.461 | 103.7174 | 866.775 | 1327.9378 | 1110.2479 | 16.3931 | 64.79 | 988.5115 | 89.5077
[11 empty] | 1998-09-27 | 16:00 | 2817 | 29.656 | 132.318 | 49.312 | 18.492 | 0 | 14.859 | 3.705 |  | 18.564 | 18.564 | 0.80042 | 0 | 13.5082 | 13.2488 | 7.8947 | 64.4283 | 0.20564 | 8.445 | 5.759 | 31.5135 | 277.632 | 294.2088 | 1330.9763 | 1347.7552 | -1.2606 | 89.2887 | 820.982 | 96.1615 | 132.318 | 113.377 | 18.492 | 8.962 | 9.441 | 18.403 | 18.403 | 0.092847 | 0.48699 | 13.6132 | 13.3517 | 4.0895 | 100.266 | 0.13316 | 5.759 | 5.759 | 16.887 | 294.2088 | 497.7 | 557.4604 | -12.0073 | 94.2602 | 425.8346 | 96.0344 | 113.377 | 97.695 | 18.492 | 4.683 | 4.758 | 9.441 | 9.441 | 0.094694 | 0.49603 | 14.2268 | 13.9536 | 6.9468 | 80.0972 | 0.17421 | 5.759 | 5.759 | 32.1338 | 497.7 | 860.1775 | 955.9276 | -11.1314 | 89.0779 | 726.8138 | 95.5788 | 97.695 | 49.312 | 18.492 | 1.207 | 3.705 | 4.912 | 4.912 | 0.1724 | 0.24572 | 10.7289 | 10.5229 | 8.7978 | 46.2137 | 0.2277 | 5.759 | 6.53 | 103.631 | 860.1775 | 1330.9763 | 1106.6422 | 16.8549 | 64.7764 | 983.4098 | 89.4621
[11 empty] | 1998-09-28 | 0:00 | 2825 | 29.431 | 132.446 | 49.327 | 18.454 | 0 | 14.829 | 3.706 |  | 18.535 | 18.535 | 0.80005 | 0 | 13.4809 | 13.3103 | 7.8993 | 64.5332 | 0.20625 | 7.834 | 5.759 | 31.3255 | 281.712 | 294.576 | 1326.7222 | 1347.9332 | -1.5987 | 89.3659 | 821.2546 | 96.1857 | 132.446 | 113.662 | 18.454 | 8.958 | 9.451 | 18.409 | 18.409 | 0.0929 | 0.48661 | 13.6071 | 13.4348 | 4.0958 | 100.5042 | 0.13367 | 5.759 | 5.759 | 16.692 | 294.576 | 499.95 | 557.9645 | -11.6041 | 94.3336 | 426.2703 | 96.0842 | 113.662 | 97.972 | 18.454 | 4.683 | 4.768 | 9.451 | 9.451 | 0.094828 | 0.4955 | 14.2268 | 14.0467 | 6.9753 | 80.3877 | 0.17474 | 5.759 | 5.759 | 32.1476 | 499.95 | 866.5475 | 959.4128 | -10.7167 | 89.0868 | 729.6814 | 95.5943 | 97.972 | 49.327 | 18.454 | 1.207 | 3.706 | 4.913 | 4.913 | 0.17244 | 0.24567 | 10.7289 | 10.5931 | 8.8712 | 46.3243 | 0.22867 | 5.759 | 6.435 | 103.6627 | 866.5475 | 1326.7222 | 1115.01 | 15.9575 | 64.8095 | 990.7787 | 89.5372
[11 empty] | 1998-09-28 | 8:00 | 2833 | 29.546 | 132.626 | 49.5 | 18.445 | 0 | 14.85 | 3.706 |  | 18.556 | 18.556 | 0.80028 | 0 | 13.5 | 13.2839 | 7.906 | 64.712 | 0.20528 | 8.423 | 5.754 | 31.349 | 280.848 | 294.576 | 1327.3303 | 1349.3307 | -1.6575 | 89.3579 | 821.9534 | 96.186 | 132.626 | 113.572 | 18.445 | 8.958 | 9.508 | 18.466 | 18.466 | 0.093281 | 0.48511 | 13.6071 | 13.3892 | 4.0882 | 100.5658 | 0.13314 | 5.754 | 5.754 | 16.6725 | 294.576 | 500.4 | 556.4039 | -11.1918 | 94.3402 | 425.4899 | 96.0816 | 113.572 | 98.04 | 18.445 | 4.698 | 4.81 | 9.508 | 9.508 | 0.095488 | 0.49411 | 14.2724 | 14.0439 | 6.9693 | 80.3917 | 0.17469 | 5.754 | 5.754 | 32.1448 | 500.4 | 866.5475 | 957.752 | -10.525 | 89.0878 | 729.076 | 95.591 | 98.04 | 49.5 | 18.445 | 1.201 | 3.706 | 4.907 | 4.907 | 0.17232 | 0.24475 | 10.6756 | 10.5046 | 8.865 | 46.46 | 0.2261 | 5.754 | 6.486 | 103.6627 | 866.5475 | 1327.3303 | 1113.7749 | 16.0891 | 64.8095 | 990.1612 | 89.5307
[11 empty] | 1998-09-28 | 16:00 | 2841.0003 | 29.661 | 132.137 | 49.147 | 18.456 | 0 | 14.832 | 3.824 |  | 18.656 | 18.656 | 0.79503 | 0 | 13.4836 | 13.2227 | 7.7147 | 64.4713 | 0.2051 | 8.637 | 5.776 | 31.866 | 280.128 | 294.3312 | 1329.7608 | 1312.3448 | 1.3097 | 89.1734 | 803.338 | 96.0333 | 132.137 | 113.085 | 18.456 | 8.961 | 9.622 | 18.583 | 18.583 | 0.094051 | 0.48221 | 13.6116 | 13.3483 | 4.0675 | 100.0875 | 0.13337 | 5.776 | 5.776 | 16.809 | 294.3312 | 496.8 | 552.7885 | -11.2698 | 94.2891 | 423.5599 | 96.0315 | 113.085 | 97.62 | 18.456 | 4.683 | 4.939 | 9.622 | 9.622 | 0.097109 | 0.4867 | 14.2268 | 13.9516 | 6.8494 | 80.0471 | 0.17429 | 5.776 | 5.776 | 32.1485 | 496.8 | 859.7225 | 937.3675 | -9.0314 | 89.0774 | 717.0838 | 95.5168 | 97.62 | 49.147 | 18.456 | 1.201 | 3.824 | 5.025 | 5.025 | 0.17704 | 0.239 | 10.6756 | 10.469 | 8.7472 | 46.1803 | 0.2267 | 5.776 | 6.614 | 103.7232 | 859.7225 | 1329.7608 | 1097.1585 | 17.492 | 64.7597 | 978.4405 | 89.3991
[11 empty] | 1998-09-29 | 0:00 | 2849 | 29.584 | 132.787 | 49.26 | 18.511 | 0 | 14.901 | 3.764 |  | 18.665 | 18.665 | 0.79834 | 0 | 13.5464 | 13.3145 | 7.8412 | 64.6713 | 0.20588 | 8.9 | 5.767 | 31.4195 | 281.712 | 294.6005 | 1327.9378 | 1336.4867 | -0.64378 | 89.3349 | 815.5436 | 96.1474 | 132.787 | 113.94 | 18.511 | 9.023 | 9.509 | 18.532 | 18.532 | 0.093504 | 0.48689 | 13.7058 | 13.4713 | 4.0965 | 100.756 | 0.1337 | 5.767 | 5.767 | 16.77 | 294.6005 | 500.85 | 558.2312 | -11.4568 | 94.3075 | 426.4158 | 96.0672 | 113.94 | 98.04 | 18.511 | 4.684 | 4.825 | 9.509 | 9.509 | 0.095595 | 0.49259 | 14.2299 | 13.9863 | 6.9618 | 80.5172 | 0.17371 | 5.767 | 5.767 | 32.1623 | 500.85 | 863.135 | 955.8414 | -10.7407 | 89.0827 | 728.3457 | 95.5842 | 98.04 | 49.26 | 18.511 | 1.188 | 3.764 | 4.952 | 4.952 | 0.17438 | 0.2399 | 10.56 | 10.3793 | 8.7926 | 46.3464 | 0.22395 | 5.767 | 6.574 | 103.7174 | 863.135 | 1327.9378 | 1102.8236 | 16.9522 | 64.7939 | 982.9793 | 89.4487
[11 empty] | 1998-09-29 | 8:00 | 2857 | 29.58 | 132.312 | 49.297 | 18.388 | 0 | 14.851 | 3.765 |  | 18.616 | 18.616 | 0.79775 | 0 | 13.5009 | 13.2714 | 7.824 | 64.5925 | 0.20546 | 8.573 | 5.762 | 31.3255 | 281.712 | 294.5597 | 1316.3915 | 1332.8839 | -1.2529 | 89.3653 | 813.7218 | 96.1503 | 132.312 | 113.445 | 18.388 | 8.959 | 9.324 | 18.283 | 18.283 | 0.092057 | 0.49002 | 13.6086 | 13.3773 | 4.1139 | 100.3766 | 0.13327 | 5.762 | 5.762 | 16.6725 | 294.5597 | 499.95 | 561.5686 | -12.325 | 94.3399 | 428.0641 | 96.1051 | 113.445 | 97.897 | 18.388 | 4.698 | 4.626 | 9.324 | 9.324 | 0.093034 | 0.50386 | 14.2724 | 14.0298 | 7.0532 | 80.2298 | 0.17487 | 5.762 | 5.762 | 32.1604 | 499.95 | 862.4525 | 975.0203 | -13.0521 | 89.0819 | 737.4852 | 95.6392 | 97.897 | 49.297 | 18.388 | 1.188 | 3.765 | 4.953 | 4.953 | 0.17442 | 0.23985 | 10.56 | 10.3805 | 8.7862 | 46.4228 | 0.22361 | 5.762 | 6.56 | 103.559 | 862.4525 | 1316.3915 | 1101.9121 | 16.293 | 64.8428 | 982.1823 | 89.4562
[11 empty] | 1998-09-29 | 16:00 | 2865 | 29.661 | 132.352 | 49.305 | 18.495 | 0 | 14.901 | 3.764 |  | 18.665 | 18.665 | 0.79834 | 0 | 13.5464 | 13.2843 | 7.8376 | 64.4959 | 0.20597 | 8.399 | 5.762 | 31.4195 | 280.176 | 294.4781 | 1329.7608 | 1335.8798 | -0.46015 | 89.3304 | 815.1789 | 96.1457 | 132.352 | 113.362 | 18.495 | 9.024 | 9.322 | 18.346 | 18.346 | 0.09226 | 0.49188 | 13.7073 | 13.4421 | 4.1204 | 100.2416 | 0.1341 | 5.762 | 5.762 | 16.8285 | 294.4781 | 496.8 | 563.2519 | -13.376 | 94.2853 | 428.865 | 96.076 | 113.362 | 97.837 | 18.495 | 4.683 | 4.639 | 9.322 | 9.322 | 0.093107 | 0.50236 | 14.2268 | 13.9516 | 6.9918 | 80.1127 | 0.17415 | 5.762 | 5.762 | 32.1485 | 496.8 | 859.495 | 965.8586 | -12.3751 | 89.0829 | 731.3293 | 95.6041 | 97.837 | 49.305 | 18.495 | 1.194 | 3.764 | 4.958 | 4.958 | 0.1745 | 0.24082 | 10.6133 | 10.408 | 8.7588 | 46.3172 | 0.22471 | 5.762 | 6.551 | 103.5187 | 859.495 | 1329.7608 | 1099.3026 | 17.3308 | 64.8467 | 979.3988 | 89.4304
[11 empty] | 1998-09-30 | 0:00 | 2873 | 29.631 | 132.58 | 49.47 | 18.454 | 0 | 14.891 | 3.706 |  | 18.597 | 18.597 | 0.80072 | 0 | 13.5373 | 13.2871 | 7.9245 | 64.6465 | 0.20554 | 8.265 | 5.753 | 31.349 | 281.712 | 294.7066 | 1327.3303 | 1352.898 | -1.9263 | 89.3626 | 823.8023 | 96.1946 | 132.58 | 113.685 | 18.454 | 9.019 | 9.512 | 18.531 | 18.531 | 0.093511 | 0.4867 | 13.6997 | 13.4466 | 4.0982 | 100.5803 | 0.13369 | 5.753 | 5.753 | 16.692 | 294.7066 | 499.95 | 558.3118 | -11.6735 | 94.3361 | 426.5092 | 96.0864 | 113.685 | 98.137 | 18.454 | 4.684 | 4.828 | 9.512 | 9.512 | 0.095635 | 0.49243 | 14.2299 | 13.9669 | 6.9471 | 80.5099 | 0.17348 | 5.753 | 5.753 | 32.1604 | 499.95 | 866.32 | 953.7873 | -10.0964 | 89.0873 | 726.8686 | 95.5755 | 98.137 | 49.47 | 18.454 | 1.207 | 3.706 | 4.913 | 4.913 | 0.17244 | 0.24567 | 10.7289 | 10.5306 | 8.8697 | 46.4798 | 0.22656 | 5.753 | 6.471 | 103.559 | 866.32 | 1327.3303 | 1114.7421 | 16.0162 | 64.8603 | 990.5311 | 89.5451
[11 empty] | 1998-09-30 | 8:00 | 2881 | 29.614 | 132.251 | 49.387 | 18.43 | 0 | 14.824 | 3.765 |  | 18.589 | 18.589 | 0.79746 | 0 | 13.4764 | 13.234 | 7.8175 | 64.5715 | 0.20495 | 8.417 | 5.748 | 31.3725 | 281.664 | 294.7066 | 1327.3303 | 1331.5363 | -0.31688 | 89.3547 | 813.1214 | 96.1417 | 132.251 | 113.445 | 18.43 | 8.959 | 9.386 | 18.345 | 18.345 | 0.09247 | 0.48836 | 13.6086 | 13.3639 | 4.1076 | 100.3104 | 0.13322 | 5.748 | 5.748 | 16.653 | 294.7066 | 499.95 | 560.1105 | -12.0333 | 94.3493 | 427.4086 | 96.1037 | 113.445 | 98.055 | 18.43 | 4.684 | 4.702 | 9.386 | 9.386 | 0.093954 | 0.49904 | 14.2299 | 13.9739 | 7.0079 | 80.3121 | 0.174 | 5.748 | 5.748 | 32.1623 | 499.95 | 862.68 | 965.947 | -11.9705 | 89.0867 | 732.9485 | 95.6119 | 98.055 | 49.387 | 18.43 | 1.207 | 3.765 | 4.972 | 4.972 | 0.1748 | 0.24276 | 10.7289 | 10.5359 | 8.8081 | 46.4829 | 0.22666 | 5.748 | 6.468 | 103.5504 | 862.68 | 1327.3303 | 1106.0451 | 16.6715 | 64.8632 | 984.3625 | 89.4805
[11 empty] | 1998-09-30 | 16:00 | 2889 | 29.648 | 132.419 | 49.312 | 18.465 | 0 | 14.927 | 3.705 |  | 18.632 | 18.632 | 0.80115 | 0 | 13.57 | 13.3126 | 7.929 | 64.4715 | 0.20649 | 8.393 | 5.76 | 31.4195 | 280.896 | 294.4536 | 1329.1533 | 1354.1864 | -1.8834 | 89.3296 | 824.32 | 96.1884 | 132.419 | 113.317 | 18.465 | 9.022 | 9.507 | 18.529 | 18.529 | 0.093487 | 0.48691 | 13.7043 | 13.4443 | 4.0944 | 100.3086 | 0.13403 | 5.76 | 5.76 | 16.77 | 294.4536 | 500.4 | 557.9712 | -11.505 | 94.3047 | 426.2124 | 96.0653 | 113.317 | 97.957 | 18.465 | 4.698 | 4.809 | 9.507 | 9.507 | 0.095475 | 0.49416 | 14.2724 | 14.0016 | 6.9698 | 80.2022 | 0.17458 | 5.76 | 5.76 | 32.1466 | 500.4 | 859.04 | 957.8453 | -11.5018 | 89.0826 | 729.1226 | 95.5911 | 97.957 | 49.312 | 18.465 | 1.214 | 3.705 | 4.919 | 4.919 | 0.17254 | 0.2468 | 10.7911 | 10.5864 | 8.7925 | 46.377 | 0.22827 | 5.76 | 6.55 | 103.5648 | 859.04 | 1329.1533 | 1106.583 | 16.7453 | 64.8281 | 982.8115 | 89.4624
[11 empty] | 1998-10-01 | 0:00 | 2897 | 29.287 | 133.37 | 50.137 | 18.249 | 0 | 14.833 | 3.764 |  | 18.597 | 18.597 | 0.7976 | 0 | 13.4845 | 13.3706 | 7.862 | 65.6425 | 0.20369 | 8.35 | 5.748 | 34.686 | 308.016 | 299.3659 | 1403.2921 | 1342.4045 | 4.3389 | 88.4135 | 820.8852 | 95.7746 | 133.37 | 114.6 | 18.249 | 8.956 | 9.516 | 18.472 | 18.472 | 0.093327 | 0.48484 | 13.6041 | 13.4891 | 4.1414 | 101.5946 | 0.13277 | 5.748 | 5.748 | 17.745 | 299.3659 | 552.15 | 564.4139 | -2.2211 | 94.0725 | 431.8899 | 95.8913 | 114.6 | 99.022 | 18.249 | 4.683 | 4.833 | 9.516 | 9.516 | 0.095695 | 0.49212 | 14.2268 | 14.1067 | 7.7123 | 80.8497 | 0.17448 | 5.748 | 5.748 | 32.6195 | 552.15 | 954.3625 | 1055.556 | -10.6033 | 89.1038 | 803.853 | 95.9421 | 99.022 | 50.137 | 18.249 | 1.188 | 3.764 | 4.952 | 4.952 | 0.17438 | 0.2399 | 10.56 | 10.4708 | 9.8207 | 46.5098 | 0.22513 | 5.748 | 6.435 | 106.1539 | 954.3625 | 1403.2921 | 1222.0755 | 12.9137 | 64.5404 | 1088.219 | 90.2452
[11 empty] | 1998-10-01 | 8:00 | 2905 | 29.244 | 133.116 | 50.197 | 18.346 | 0 | 14.773 | 3.764 |  | 18.537 | 18.537 | 0.79695 | 0 | 13.43 | 13.3335 | 7.8377 | 65.4728 | 0.20365 | 8.364 | 5.751 | 34.6155 | 307.968 | 299.1864 | 1391.1377 | 1337.578 | 3.8501 | 88.4301 | 818.3822 | 95.7703 | 133.116 | 114.337 | 18.346 | 8.901 | 9.505 | 18.406 | 18.406 | 0.09307 | 0.48359 | 13.5205 | 13.4233 | 4.1342 | 101.2463 | 0.13258 | 5.751 | 5.751 | 17.6085 | 299.1864 | 551.7 | 562.8713 | -2.0249 | 94.1145 | 431.0288 | 95.9148 | 114.337 | 99.082 | 18.346 | 4.684 | 4.821 | 9.505 | 9.505 | 0.095541 | 0.49279 | 14.2299 | 14.1276 | 7.7125 | 80.651 | 0.17517 | 5.751 | 5.751 | 32.6177 | 551.7 | 950.95 | 1056.0314 | -11.0501 | 89.0979 | 803.8657 | 95.9424 | 99.082 | 50.197 | 18.346 | 1.194 | 3.764 | 4.958 | 4.958 | 0.1745 | 0.24082 | 10.6133 | 10.5371 | 9.7886 | 46.5049 | 0.22658 | 5.751 | 6.42 | 106.0934 | 950.95 | 1391.1377 | 1218.9518 | 12.3773 | 64.5394 | 1084.9509 | 90.2214
[11 empty] | 1998-10-01 | 16:00 | 2913.0003 | 29.346 | 132.948 | 50.13 | 18.34 | 0 | 14.855 | 3.705 |  | 18.56 | 18.56 | 0.80038 | 0 | 13.5045 | 13.3671 | 7.9265 | 65.2725 | 0.20479 | 8.358 | 5.771 | 34.968 | 305.136 | 298.7702 | 1409.3687 | 1356.4713 | 3.7533 | 88.296 | 827.6207 | 95.7749 | 132.948 | 113.925 | 18.34 | 8.964 | 9.508 | 18.472 | 18.472 | 0.093301 | 0.48528 | 13.6162 | 13.4777 | 4.1358 | 100.9607 | 0.13349 | 5.771 | 5.771 | 17.6865 | 298.7702 | 546.75 | 563.7718 | -3.1133 | 94.0802 | 431.271 | 95.899 | 113.925 | 98.535 | 18.34 | 4.684 | 4.824 | 9.508 | 9.508 | 0.095581 | 0.49264 | 14.2299 | 14.0851 | 7.6377 | 80.2523 | 0.17551 | 5.771 | 5.771 | 32.5947 | 546.75 | 942.9875 | 1045.9837 | -10.9223 | 89.0904 | 796.3669 | 95.9071 | 98.535 | 50.13 | 18.34 | 1.188 | 3.705 | 4.893 | 4.893 | 0.17202 | 0.2428 | 10.56 | 10.4525 | 9.712 | 46.2805 | 0.22585 | 5.771 | 6.536 | 105.984 | 942.9875 | 1409.3687 | 1211.3708 | 14.0487 | 64.5266 | 1077.1792 | 90.161
[11 empty] | 1998-10-02 | 0:00 | 2921 | 29.261 | 133.323 | 50.205 | 18.33 | 0 | 14.78 | 3.765 |  | 18.545 | 18.545 | 0.79698 | 0 | 13.4364 | 13.3331 | 7.8335 | 65.6005 | 0.20325 | 8.297 | 5.756 | 34.686 | 307.152 | 299.0803 | 1392.3533 | 1336.9948 | 3.9759 | 88.4024 | 818.0376 | 95.7599 | 133.323 | 114.667 | 18.33 | 8.896 | 9.453 | 18.349 | 18.349 | 0.092707 | 0.48482 | 13.5129 | 13.4091 | 4.1377 | 101.5273 | 0.13207 | 5.756 | 5.756 | 17.706 | 299.0803 | 548.55 | 563.8752 | -2.7938 | 94.0799 | 431.4778 | 95.8964 | 114.667 | 99.105 | 18.33 | 4.67 | 4.783 | 9.453 | 9.453 | 0.094941 | 0.49402 | 14.1873 | 14.0783 | 7.6783 | 80.8777 | 0.17407 | 5.756 | 5.756 | 32.602 | 548.55 | 950.495 | 1052.3085 | -10.7116 | 89.0992 | 800.4293 | 95.9269 | 99.105 | 50.205 | 18.33 | 1.194 | 3.765 | 4.959 | 4.959 | 0.17454 | 0.24077 | 10.6133 | 10.5318 | 9.784 | 46.541 | 0.22629 | 5.756 | 6.46 | 105.9984 | 950.495 | 1392.3533 | 1218.3115 | 12.4998 | 64.5586 | 1084.4032 | 90.2252
[11 empty] | 1998-10-02 | 8:00 | 2929.0003 | 29.227 | 133.028 | 50.235 | 18.366 | 0 | 14.789 | 3.825 |  | 18.614 | 18.614 | 0.79451 | 0 | 13.4445 | 13.3546 | 7.7604 | 65.5051 | 0.20387 | 8.017 | 5.74 | 34.6155 | 307.152 | 299.1864 | 1390.5302 | 1322.1247 | 4.9194 | 88.4301 | 810.6556 | 95.7299 | 133.028 | 114.36 | 18.366 | 8.898 | 9.685 | 18.583 | 18.583 | 0.094261 | 0.47882 | 13.5159 | 13.4256 | 4.109 | 101.219 | 0.13264 | 5.74 | 5.74 | 17.628 | 299.1864 | 547.2 | 557.8655 | -1.9491 | 94.108 | 428.5259 | 95.8864 | 114.36 | 98.947 | 18.366 | 4.684 | 5.001 | 9.685 | 9.685 | 0.097942 | 0.48363 | 14.2299 | 14.1347 | 7.5559 | 80.7316 | 0.17508 | 5.74 | 5.74 | 32.6002 | 547.2 | 950.04 | 1029.1807 | -8.3302 | 89.1037 | 788.1903 | 95.8639 | 98.947 | 50.235 | 18.366 | 1.194 | 3.825 | 5.019 | 5.019 | 0.17694 | 0.2379 | 10.6133 | 10.5424 | 9.7578 | 46.4672 | 0.22688 | 5.74 | 6.418 | 105.9926 | 950.04 | 1390.5302 | 1213.5152 | 12.73 | 64.573 | 1081.7776 | 90.202
[11 empty] | 1998-10-02 | 16:00 | 2937 | 29.414 | 147.011 | 55.147 | 19.501 | 0 | 15.239 | 3.983 |  | 19.222 | 19.222 | 0.79279 | 0 | 13.8536 | 13.6851 | 7.731 | 73.847 | 0.18532 | 6.917 | 5.8 | 35.438 | 318.816 | 300.8347 | 1431.8537 | 1316.2454 | 8.074 | 88.2201 | 808.54 | 95.617 | 147.011 | 126.517 | 19.501 | 9.266 | 11.483 | 20.749 | 20.749 | 0.10748 | 0.44658 | 14.0749 | 13.9037 | 3.9774 | 113.2856 | 0.12273 | 5.8 | 5.8 | 17.433 | 300.8347 | 579.6 | 529.5206 | 8.6403 | 94.2051 | 415.1777 | 95.8011 | 126.517 | 109.185 | 19.501 | 4.785 | 6.698 | 11.483 | 11.483 | 0.12125 | 0.4167 | 14.5367 | 14.3599 | 7.4177 | 90.9323 | 0.15792 | 5.8 | 5.8 | 33.0547 | 579.6 | 1017.6075 | 970.0478 | 4.6737 | 89.0123 | 774.8239 | 95.7339 | 109.185 | 55.147 | 19.501 | 1.194 | 3.983 | 5.177 | 5.177 | 0.18327 | 0.23064 | 10.6133 | 10.4842 | 10.4679 | 52.1971 | 0.20086 | 5.8 | 6.777 | 107.2627 | 1017.6075 | 1431.8537 | 1290.5052 | 9.8717 | 64.345 | 1154.0564 | 90.7056
[11 empty] | 1998-10-02 | 20:06 | 2941.1008 | 29.083 | 124.004 | 52.635 | 17.808 | 0 | 15.043 | 3.346 |  | 18.389 | 18.389 | 0.81804 | 0 | 13.6755 | 13.6419 | 8.5368 | 61.9747 | 0.22012 | 8.666 | 5.767 | 38.8925 | 323.472 | 301.7323 | 1490.7996 | 1483.4118 | 0.49556 | 87.1103 | 892.572 | 95.6426 | 124.004 | 106.507 | 17.808 | 9.201 | 8.484 | 17.685 | 17.685 | 0.087262 | 0.52027 | 13.9762 | 13.942 | 4.3573 | 93.0902 | 0.14977 | 5.767 | 5.767 | 19.2075 | 301.7323 | 580.95 | 608.1339 | -4.6792 | 93.6343 | 454.9331 | 95.778 | 106.507 | 92.985 | 17.808 | 4.641 | 3.843 | 8.484 | 8.484 | 0.08221 | 0.54703 | 14.0992 | 14.0647 | 8.7864 | 73.1516 | 0.19227 | 5.767 | 5.767 | 33.1108 | 580.95 | 1022.84 | 1242.5482 | -21.4802 | 89.0264 | 911.7491 | 96.3684 | 92.985 | 52.635 | 17.808 | 1.188 | 3.346 | 4.534 | 4.534 | 0.15766 | 0.26202 | 10.56 | 10.5341 | 10.7612 | 44.2408 | 0.23811 | 5.767 | 6.522 | 108.9533 | 1022.84 | 1490.7996 | 1347.3162 | 9.6246 | 63.8907 | 1185.0781 | 90.8062
[11 empty] | 1998-10-03 | 9:17 | 2954.2767 | 29.027 | 137.812 | 39.21 | 18.007 | 0 | 14.576 | 3.984 |  | 18.56 | 18.56 | 0.78534 | 0 | 13.2509 | 13.2403 | 7.5026 | 63.0014 | 0.21016 | 8.399 | 5.793 | 35.7435 | 321.216 | 300.9163 | 1417.8764 | 1271.0868 | 10.3528 | 88.1218 | 786.0015 | 95.4525 | 137.812 | 118.185 | 18.007 | 8.663 | 10.886 | 19.549 | 19.549 | 0.10149 | 0.44314 | 13.159 | 13.1485 | 3.9603 | 106.0312 | 0.12401 | 5.793 | 5.793 | 17.6085 | 300.9163 | 569.7 | 526.3706 | 7.6056 | 94.1484 | 413.6435 | 95.7431 | 118.185 | 100.702 | 18.007 | 4.712 | 6.174 | 10.886 | 10.886 | 0.11377 | 0.43285 | 14.3149 | 14.3035 | 7.4229 | 84.0136 | 0.17025 | 5.793 | 5.793 | 32.43 | 569.7 | 961.1875 | 979.7447 | -1.9307 | 89.2229 | 774.7224 | 95.814 | 100.702 | 39.21 | 18.007 | 1.181 | 3.984 | 5.165 | 5.165 | 0.18305 | 0.22865 | 10.4978 | 10.4894 | 9.7992 | 42.1498 | 0.24886 | 5.793 | 6.644 | 107.7638 | 961.1875 | 1417.8764 | 1214.1728 | 14.3668 | 64.1881 | 1087.6801 | 90.0923
[11 empty] | 1998-10-03 | 12:00 | 2957.0003 | 29.032 | 130.71 | 57.697 | 17.649 | 0 | 14.128 | 3.106 |  | 17.234 | 17.234 | 0.81977 | 0 | 12.8436 | 12.8315 | 8.612 | 67.9425 | 0.18886 | 8.536 | 5.772 | 38.4225 | 320.64 | 301.4386 | 1519.3613 | 1497.7975 | 1.4193 | 87.2536 | 899.618 | 95.729 | 130.71 | 112.53 | 17.649 | 8.246 | 9.629 | 17.875 | 17.875 | 0.091713 | 0.46131 | 12.5256 | 12.5137 | 4.0355 | 99.9355 | 0.12522 | 5.772 | 5.772 | 18.876 | 301.4386 | 587.7 | 543.417 | 7.535 | 93.738 | 422.4278 | 95.5315 | 112.53 | 98.415 | 17.649 | 4.669 | 4.96 | 9.629 | 9.629 | 0.097295 | 0.48489 | 14.1843 | 14.1709 | 8.1526 | 79.6709 | 0.17787 | 5.772 | 5.772 | 33.35 | 587.7 | 1046.045 | 1109.5266 | -6.0687 | 88.9364 | 848.6133 | 96.0701 | 98.415 | 57.697 | 17.649 | 1.207 | 3.106 | 4.313 | 4.313 | 0.14843 | 0.27985 | 10.7289 | 10.7187 | 11.1924 | 49.2146 | 0.2178 | 5.772 | 6.539 | 108.8928 | 1046.045 | 1519.3613 | 1410.2249 | 7.183 | 63.8756 | 1228.1349 | 91.1335
[11 empty] | 1998-10-03 | 20:00 | 2965 | 29.015 | 130.905 | 57.802 | 17.7 | 0 | 14.146 | 3.167 |  | 17.313 | 17.313 | 0.81707 | 0 | 12.86 | 12.8543 | 8.5209 | 68.1326 | 0.18867 | 8.418 | 5.754 | 38.07 | 321.792 | 301.6018 | 1508.423 | 1478.7158 | 1.9694 | 87.3774 | 890.1588 | 95.7232 | 130.905 | 112.65 | 17.7 | 8.303 | 9.634 | 17.937 | 17.937 | 0.091937 | 0.4629 | 12.6122 | 12.6066 | 4.05 | 100.0275 | 0.12603 | 5.754 | 5.754 | 18.564 | 301.6018 | 585 | 545.536 | 6.746 | 93.8449 | 423.5689 | 95.6172 | 112.65 | 98.677 | 17.7 | 4.655 | 4.979 | 9.634 | 9.634 | 0.097455 | 0.48318 | 14.1418 | 14.1355 | 8.0952 | 79.8683 | 0.17699 | 5.754 | 5.754 | 33.3574 | 585 | 1051.2775 | 1100.7454 | -4.7055 | 88.9399 | 842.8727 | 96.0424 | 98.677 | 57.802 | 17.7 | 1.194 | 3.167 | 4.361 | 4.361 | 0.15061 | 0.27379 | 10.6133 | 10.6086 | 11.2007 | 49.3388 | 0.21502 | 5.754 | 6.464 | 108.8554 | 1051.2775 | 1508.423 | 1406.5828 | 6.7514 | 63.9076 | 1228.9302 | 91.1423
[11 empty] | 1998-10-04 | 4:00 | 2973.0003 | 29.066 | 130.864 | 57.705 | 17.647 | 0 | 14.165 | 3.107 |  | 17.272 | 17.272 | 0.82011 | 0 | 12.8773 | 12.8522 | 8.658 | 67.9795 | 0.18906 | 8.319 | 5.743 | 37.9525 | 322.368 | 301.9526 | 1498.6998 | 1505.5452 | -0.45675 | 87.431 | 903.7489 | 95.8005 | 130.864 | 112.665 | 17.647 | 8.301 | 9.691 | 17.992 | 17.992 | 0.09231 | 0.46137 | 12.6091 | 12.5845 | 4.0459 | 100.0716 | 0.12576 | 5.743 | 5.743 | 18.681 | 301.9526 | 587.25 | 544.594 | 7.2637 | 93.8133 | 423.2733 | 95.5865 | 112.665 | 98.745 | 17.647 | 4.67 | 5.021 | 9.691 | 9.691 | 0.098116 | 0.48189 | 14.1873 | 14.1597 | 8.1144 | 79.9436 | 0.17712 | 5.743 | 5.743 | 33.3822 | 587.25 | 1057.6475 | 1102.3989 | -4.2312 | 88.9446 | 844.8244 | 96.0486 | 98.745 | 57.705 | 17.647 | 1.188 | 3.107 | 4.295 | 4.295 | 0.14809 | 0.2766 | 10.56 | 10.5394 | 11.302 | 49.276 | 0.21389 | 5.743 | 6.306 | 108.8381 | 1057.6475 | 1498.6998 | 1420.4366 | 5.2221 | 63.9552 | 1239.042 | 91.2159
[11 empty] | 1998-10-04 | 12:00 | 2981.0003 | 29.146 | 130.704 | 57.727 | 17.695 | 0 | 14.045 | 3.166 |  | 17.211 | 17.211 | 0.81605 | 0 | 12.7682 | 12.7132 | 8.4649 | 68.0556 | 0.18681 | 8.33 | 5.763 | 39.01 | 324.48 | 302.0506 | 1524.8309 | 1468.9503 | 3.6647 | 87.0849 | 885.5004 | 95.5946 | 130.704 | 112.657 | 17.695 | 8.304 | 9.504 | 17.808 | 17.808 | 0.091073 | 0.46631 | 12.6137 | 12.5594 | 4.0677 | 99.9178 | 0.1257 | 5.763 | 5.763 | 18.954 | 302.0506 | 593.55 | 549.4026 | 7.4379 | 93.7249 | 425.7266 | 95.5478 | 112.657 | 98.58 | 17.695 | 4.67 | 4.834 | 9.504 | 9.504 | 0.095621 | 0.49137 | 14.1873 | 14.1262 | 8.3069 | 79.6166 | 0.17743 | 5.763 | 5.763 | 33.4245 | 593.55 | 1059.9225 | 1134.6725 | -7.0524 | 88.9341 | 864.1112 | 96.1319 | 98.58 | 57.727 | 17.695 | 1.207 | 3.166 | 4.373 | 4.373 | 0.15083 | 0.27601 | 10.7289 | 10.6827 | 11.3192 | 49.1393 | 0.2174 | 5.763 | 6.455 | 109.224 | 1059.9225 | 1524.8309 | 1422.365 | 6.7198 | 63.8392 | 1241.1438 | 91.1997
[11 empty] | 1998-10-04 | 20:00 | 2989.0003 | 29.274 | 130.121 | 56.842 | 17.775 | 0 | 14.163 | 3.106 |  | 17.269 | 17.269 | 0.82014 | 0 | 12.8755 | 12.7716 | 8.6356 | 67.0709 | 0.19042 | 8.314 | 5.744 | 33.934 | 295.392 | 297.2198 | 1404.5071 | 1497.7728 | -6.6405 | 88.5829 | 897.4963 | 96.219 | 130.121 | 111.832 | 17.775 | 8.363 | 9.508 | 17.871 | 17.871 | 0.091296 | 0.46796 | 12.7033 | 12.6008 | 4.0325 | 99.169 | 0.12706 | 5.744 | 5.744 | 17.1405 | 297.2198 | 536.85 | 543.5707 | -1.2519 | 94.2331 | 420.3952 | 95.9228 | 111.832 | 97.687 | 17.775 | 4.684 | 4.824 | 9.508 | 9.508 | 0.095581 | 0.49264 | 14.2299 | 14.1151 | 7.4866 | 79.4979 | 0.17755 | 5.744 | 5.744 | 32.8661 | 536.85 | 959.14 | 1026.2075 | -6.9925 | 88.9422 | 781.5288 | 95.7946 | 97.687 | 56.842 | 17.775 | 1.214 | 3.106 | 4.32 | 4.32 | 0.14857 | 0.28102 | 10.7911 | 10.7041 | 10.2035 | 49.286 | 0.21718 | 5.744 | 6.299 | 105.5981 | 959.14 | 1404.5071 | 1292.7523 | 7.9569 | 64.4714 | 1125.9462 | 90.6214
[11 empty] | 1998-10-05 | 4:00 | 2997.0003 | 29.1 | 131.28 | 58.185 | 17.7 | 0 | 14.024 | 3.106 |  | 17.13 | 17.13 | 0.81868 | 0 | 12.7491 | 12.7115 | 8.5844 | 68.4481 | 0.18571 | 8.207 | 5.754 | 38.023 | 321.696 | 301.5446 | 1499.9153 | 1491.3796 | 0.56908 | 87.3906 | 896.4621 | 95.7585 | 131.28 | 113.032 | 17.7 | 8.298 | 9.639 | 17.937 | 17.937 | 0.091953 | 0.46262 | 12.6046 | 12.5674 | 4.0498 | 100.4062 | 0.12517 | 5.754 | 5.754 | 18.4275 | 301.5446 | 583.65 | 545.2739 | 6.5752 | 93.889 | 423.4093 | 95.6478 | 113.032 | 98.872 | 17.7 | 4.655 | 4.984 | 9.639 | 9.639 | 0.097522 | 0.48293 | 14.1418 | 14.1 | 8.0737 | 80.1783 | 0.17586 | 5.754 | 5.754 | 33.293 | 583.65 | 1054.235 | 1097.6773 | -4.1207 | 88.9592 | 840.6636 | 96.0397 | 98.872 | 58.185 | 17.7 | 1.207 | 3.106 | 4.313 | 4.313 | 0.14843 | 0.27985 | 10.7289 | 10.6972 | 11.2932 | 49.5353 | 0.21595 | 5.754 | 6.448 | 108.6422 | 1054.235 | 1499.9153 | 1421.6949 | 5.215 | 63.9714 | 1237.965 | 91.2241
[11 empty] | 1998-10-05 | 12:00 | 3005.0003 | 29.044 | 130.884 | 57.937 | 17.665 | 0 | 14.088 | 3.106 |  | 17.194 | 17.194 | 0.81936 | 0 | 12.8073 | 12.7906 | 8.6068 | 68.1387 | 0.18771 | 8.424 | 5.771 | 37.835 | 319.44 | 301.2101 | 1494.4462 | 1495.8102 | -0.091273 | 87.439 | 898.5102 | 95.7891 | 130.884 | 112.86 | 17.665 | 8.302 | 9.683 | 17.985 | 17.985 | 0.09226 | 0.46161 | 12.6106 | 12.5942 | 4.0412 | 100.1658 | 0.12573 | 5.771 | 5.771 | 18.3495 | 301.2101 | 582.3 | 543.7288 | 6.6239 | 93.9081 | 422.4694 | 95.6566 | 112.86 | 98.872 | 17.665 | 4.67 | 5.013 | 9.683 | 9.683 | 0.098009 | 0.48229 | 14.1873 | 14.1689 | 8.0477 | 80.1533 | 0.17677 | 5.771 | 5.771 | 33.2626 | 582.3 | 1040.585 | 1093.7711 | -5.1112 | 88.957 | 838.0356 | 96.0309 | 98.872 | 57.937 | 17.665 | 1.188 | 3.106 | 4.294 | 4.294 | 0.14805 | 0.27667 | 10.56 | 10.5463 | 11.1038 | 49.6357 | 0.21247 | 5.771 | 6.521 | 108.4637 | 1040.585 | 1494.4462 | 1397.1079 | 6.5133 | 63.9907 | 1218.8465 | 91.1011
[11 empty] | 1998-10-05 | 20:00 | 3013.0003 | 29.057 | 132.084 | 59.077 | 18.816 | 0 | 15.118 | 3.227 |  | 18.345 | 18.345 | 0.82409 | 0 | 13.7436 | 13.7205 | 8.8234 | 67.9411 | 0.20195 | 8.436 | 5.754 | 37.553 | 321.12 | 301.5365 | 1467.1001 | 1538.2586 | -4.8503 | 87.5461 | 919.8975 | 95.9177 | 132.084 | 114.51 | 18.816 | 9.377 | 8.375 | 17.752 | 17.752 | 0.087122 | 0.52822 | 14.2435 | 14.2196 | 4.4163 | 100.0647 | 0.1421 | 5.754 | 5.754 | 18.408 | 301.5365 | 579.6 | 618.539 | -6.7182 | 93.8953 | 460.0377 | 95.9986 | 114.51 | 100.29 | 18.816 | 4.67 | 3.705 | 8.375 | 8.375 | 0.080563 | 0.55761 | 14.1873 | 14.1635 | 8.9061 | 79.6779 | 0.17776 | 5.754 | 5.754 | 33.2874 | 579.6 | 1041.95 | 1268.2045 | -21.7145 | 88.9607 | 923.9022 | 96.3971 | 100.29 | 59.077 | 18.816 | 1.201 | 3.227 | 4.428 | 4.428 | 0.15316 | 0.27123 | 10.6756 | 10.6576 | 11.0735 | 49.794 | 0.21403 | 5.754 | 6.413 | 108.337 | 1041.95 | 1467.1001 | 1389.4149 | 5.2952 | 64.0717 | 1215.6825 | 91.0884
[11 empty] | 1998-10-06 | 4:00 | 3021 | 29.061 | 132.787 | 58.972 | 18.897 | 0 | 15.181 | 3.227 |  | 18.408 | 18.408 | 0.8247 | 0 | 13.8009 | 13.776 | 8.8444 | 68.1381 | 0.20218 | 8.209 | 5.751 | 38.4225 | 325.968 | 302.2627 | 1478.0383 | 1543.4646 | -4.4266 | 87.2884 | 922.8636 | 95.8366 | 132.787 | 115.005 | 18.897 | 9.44 | 8.309 | 17.749 | 17.749 | 0.086892 | 0.53186 | 14.3392 | 14.3134 | 4.4458 | 100.5532 | 0.14235 | 5.751 | 5.751 | 18.7395 | 302.2627 | 588.15 | 624.3784 | -6.1597 | 93.8003 | 463.3206 | 95.9554 | 115.005 | 100.882 | 18.897 | 4.67 | 3.639 | 8.309 | 8.309 | 0.079682 | 0.56204 | 14.1873 | 14.1618 | 9.1079 | 79.9386 | 0.17716 | 5.751 | 5.751 | 33.3537 | 588.15 | 1057.42 | 1300.131 | -22.9531 | 88.9653 | 944.1405 | 96.4673 | 100.882 | 58.972 | 18.897 | 1.201 | 3.227 | 4.428 | 4.428 | 0.15316 | 0.27123 | 10.6756 | 10.6563 | 11.2509 | 49.7791 | 0.21407 | 5.751 | 6.434 | 108.8438 | 1057.42 | 1478.0383 | 1410.4538 | 4.5726 | 63.9903 | 1233.9369 | 91.1791
[11 empty] | 1998-10-06 | 12:00 | 3029 | 29.401 | 131.273 | 58.102 | 18.88 | 0 | 15.258 | 3.105 |  | 18.363 | 18.363 | 0.83091 | 0 | 13.8709 | 13.7075 | 9.0792 | 66.7283 | 0.20542 | 8.494 | 5.761 | 34.075 | 292.992 | 296.7058 | 1374.7304 | 1587.2759 | -15.4609 | 88.5156 | 941.9908 | 96.3827 | 131.273 | 113.325 | 18.88 | 9.381 | 8.488 | 17.869 | 17.869 | 0.087889 | 0.52499 | 14.2496 | 14.0817 | 4.3381 | 99.0809 | 0.14212 | 5.761 | 5.761 | 17.2965 | 296.7058 | 530.1 | 605.5109 | -14.2258 | 94.1705 | 451.1083 | 96.1658 | 113.325 | 99.247 | 18.88 | 4.67 | 3.818 | 8.488 | 8.488 | 0.08207 | 0.55019 | 14.1873 | 14.0202 | 8.0148 | 79.3912 | 0.1766 | 5.761 | 5.761 | 32.7732 | 530.1 | 940.7125 | 1138.4071 | -21.0154 | 88.9543 | 834.2535 | 96.0716 | 99.247 | 58.102 | 18.88 | 1.213 | 3.105 | 4.318 | 4.318 | 0.14851 | 0.28092 | 10.7822 | 10.6552 | 9.987 | 49.8075 | 0.21393 | 5.761 | 6.469 | 105.2122 | 940.7125 | 1374.7304 | 1267.1093 | 7.8285 | 64.5399 | 1103.9109 | 90.4691
[11 empty] | 1998-10-06 | 20:00 | 3037 | 29.333 | 131.889 | 58.02 | 18.816 | 0 | 15.328 | 3.106 |  | 18.434 | 18.434 | 0.83151 | 0 | 13.9345 | 13.7981 | 9.12 | 67.0185 | 0.20588 | 8.429 | 5.741 | 33.9105 | 293.712 | 296.9261 | 1371.6918 | 1594.8987 | -16.2724 | 88.5795 | 945.9124 | 96.415 | 131.889 | 113.85 | 18.816 | 9.438 | 8.671 | 18.109 | 18.109 | 0.089299 | 0.52118 | 14.3362 | 14.1958 | 4.3157 | 99.7378 | 0.14233 | 5.741 | 5.741 | 17.4525 | 296.9261 | 532.8 | 601.1207 | -12.823 | 94.1223 | 449.0234 | 96.1132 | 113.85 | 99.6 | 18.816 | 4.67 | 4.001 | 8.671 | 8.671 | 0.084511 | 0.53858 | 14.1873 | 14.0484 | 7.9185 | 79.9905 | 0.17563 | 5.741 | 5.741 | 32.7676 | 532.8 | 947.0825 | 1116.4419 | -17.8822 | 88.9644 | 824.6209 | 96.0263 | 99.6 | 58.02 | 18.816 | 1.188 | 3.106 | 4.294 | 4.294 | 0.14805 | 0.27667 | 10.56 | 10.4566 | 10.0283 | 49.9657 | 0.20928 | 5.741 | 6.362 | 105.2438 | 947.0825 | 1371.6918 | 1269.0736 | 7.4811 | 64.5555 | 1108.078 | 90.5021
[11 empty] | 1998-10-07 | 4:00 | 3045 | 29.27 | 132.09 | 58.755 | 18.849 | 0 | 15.316 | 3.106 |  | 18.422 | 18.422 | 0.8314 | 0 | 13.9236 | 13.813 | 9.1386 | 67.4349 | 0.20483 | 6.896 | 5.743 | 37.553 | 319.92 | 301.2509 | 1467.1001 | 1601.5718 | -9.1658 | 87.5343 | 951.4113 | 96.0529 | 132.09 | 114.202 | 18.849 | 9.441 | 8.494 | 17.935 | 17.935 | 0.088129 | 0.5264 | 14.3408 | 14.2268 | 4.4003 | 99.8967 | 0.14241 | 5.743 | 5.743 | 18.408 | 301.2509 | 579.6 | 615.628 | -6.216 | 93.8895 | 458.4395 | 95.9846 | 114.202 | 100.32 | 18.849 | 4.655 | 3.839 | 8.494 | 8.494 | 0.08225 | 0.54803 | 14.1418 | 14.0294 | 8.7811 | 79.6309 | 0.17618 | 5.743 | 5.743 | 32.9286 | 579.6 | 1038.0825 | 1242.4693 | -19.6889 | 89.0694 | 911.0346 | 96.3856 | 100.32 | 58.755 | 18.849 | 1.194 | 3.106 | 4.3 | 4.3 | 0.14817 | 0.27767 | 10.6133 | 10.529 | 11.0876 | 49.6009 | 0.21227 | 5.743 | 6.36 | 108.0806 | 1038.0825 | 1467.1001 | 1395.5913 | 4.8742 | 64.1227 | 1216.8369 | 91.1179
[11 empty] | 1998-10-07 | 19:28 | 3060.4642 | 29.329 | 133.209 | 31.792 | 18.298 | 0 | 14.882 | 3.705 |  | 18.587 | 18.587 | 0.80067 | 0 | 13.5291 | 13.3982 | 8.2383 | 55.9642 | 0.23941 | 8.526 | 5.795 | 30.6205 | 319.248 | 304.4659 | 1338.8765 | 1404.4302 | -4.8962 | 89.9429 | 854.448 | 96.4163 | 133.209 | 114.36 | 18.298 | 9.021 | 8.727 | 17.748 | 17.748 | 0.088282 | 0.50828 | 13.7028 | 13.5702 | 4.3645 | 101.122 | 0.1342 | 5.795 | 5.795 | 16.731 | 304.4659 | 672.75 | 601.8942 | 10.5323 | 94.5048 | 453.1801 | 96.3081 | 114.36 | 100.335 | 18.298 | 4.641 | 4.086 | 8.727 | 8.727 | 0.085451 | 0.5318 | 14.0992 | 13.9628 | 10.0681 | 78.9814 | 0.17679 | 5.795 | 5.795 | 30.6139 | 672.75 | 791.4725 | 1402.1072 | -77.1517 | 89.945 | 1037.4286 | 97.0491 | 100.335 | 31.792 | 18.298 | 1.071 | 3.705 | 4.776 | 4.776 | 0.16968 | 0.22425 | 9.52 | 9.4279 | 7.6878 | 40.0777 | 0.23524 | 5.795 | 7.778 | 119.7763 | 791.4725 | 1338.8765 | 985.6389 | 26.3831 | 60.6602 | 888.5557 | 86.5201
[11 empty] | 1998-10-07 | 20:00 | 3060.9969 | 29.329 | 133.209 | 31.792 | 17.947 | 0 | 14.896 | 3.705 |  | 18.601 | 18.601 | 0.80082 | 0 | 13.5418 | 13.4108 | 8.3312 | 56.2223 | 0.23853 | 8.526 | 5.795 | 27.7065 | 319.248 | 304.4659 | 1338.8765 | 1417.1807 | -5.8485 | 90.9 | 860.8233 | 96.7814 | 133.209 | 114.36 | 17.947 | 9.021 | 8.727 | 17.748 | 17.748 | 0.088282 | 0.50828 | 13.7028 | 13.5702 | 4.3645 | 101.473 | 0.13373 | 5.795 | 5.795 | 16.731 | 304.4659 | 672.75 | 601.8942 | 10.5323 | 94.5048 | 453.1801 | 96.3081 | 114.36 | 93.525 | 17.947 | 4.655 | 4.072 | 8.727 | 8.727 | 0.085358 | 0.5334 | 14.1418 | 14.0049 | 10.0893 | 75.9062 | 0.1845 | 5.795 | 5.795 | 30.7666 | 672.75 | 839.02 | 1406.648 | -67.6537 | 89.8949 | 1039.699 | 97.0408 | 93.525 | 31.792 | 17.947 | 1.116 | 3.705 | 4.821 | 4.821 | 0.17058 | 0.23149 | 9.92 | 9.824 | 8.3475 | 36.364 | 0.27016 | 5.795 | 7.778 | 113.5354 | 839.02 | 1338.8765 | 1057.5465 | 21.0124 | 62.71 | 948.2833 | 88.0273
[11 empty] | 1998-10-07 | 20:01 | 3061.0161 | 29.329 | 133.209 | 31.792 | 18.78 | 0 | 14.863 | 3.705 |  | 18.568 | 18.568 | 0.80046 | 0 | 13.5118 | 13.3811 | 8.1952 | 55.5253 | 0.24099 | 8.526 | 5.795 | 31.819 | 319.248 | 304.4659 | 1338.8765 | 1398.2179 | -4.4322 | 89.5492 | 851.3419 | 96.2625 | 133.209 | 114.36 | 18.78 | 9.021 | 8.727 | 17.748 | 17.748 | 0.088282 | 0.50828 | 13.7028 | 13.5702 | 4.3645 | 100.64 | 0.13484 | 5.795 | 5.795 | 16.731 | 304.4659 | 672.75 | 601.8942 | 10.5323 | 94.5048 | 453.1801 | 96.3081 | 114.36 | 97.357 | 18.78 | 4.641 | 4.086 | 8.727 | 8.727 | 0.085451 | 0.5318 | 14.0992 | 13.9628 | 10.0494 | 77.0291 | 0.18127 | 5.795 | 5.795 | 31.8118 | 672.75 | 958.685 | 1400.7467 | -46.1113 | 89.5516 | 1036.7483 | 96.9316 | 97.357 | 31.792 | 18.78 | 1.071 | 3.705 | 4.776 | 4.776 | 0.16968 | 0.22425 | 9.52 | 9.4279 | 9.729 | 36.0655 | 0.26141 | 5.795 | 7.778 | 108.648 | 958.685 | 1338.8765 | 1204.4042 | 10.0437 | 64.3152 | 1081.5446 | 89.9544
[11 empty] | 1998-10-08 | 2:12 | 3067.1947 | 29.308 | 140.874 | 35.527 | 19.803 | 0 | 14.559 | 3.983 |  | 18.542 | 18.542 | 0.78519 | 0 | 13.2355 | 13.1155 | 7.4732 | 60.9243 | 0.21528 | 8.597 | 5.756 | 32.618 | 293.616 | 296.9098 | 1327.3303 | 1262.9715 | 4.8487 | 89.0142 | 779.9406 | 95.8179 | 140.874 | 120.682 | 19.803 | 9.861 | 9.567 | 19.428 | 19.428 | 0.096685 | 0.50757 | 14.9787 | 14.843 | 4.241 | 106.734 | 0.13907 | 5.756 | 5.756 | 17.043 | 296.9098 | 516.15 | 585.377 | -13.4122 | 94.2599 | 441.1434 | 96.1366 | 120.682 | 102.36 | 19.803 | 4.698 | 4.869 | 9.567 | 9.567 | 0.096275 | 0.49106 | 14.2724 | 14.1431 | 7.1801 | 84.5379 | 0.1673 | 5.756 | 5.756 | 31.8035 | 516.15 | 854.945 | 983.4862 | -15.035 | 89.2885 | 749.8181 | 95.7585 | 102.36 | 35.527 | 19.803 | 1.071 | 3.983 | 5.054 | 5.054 | 0.18081 | 0.21191 | 9.52 | 9.4337 | 8.5026 | 40.6379 | 0.23214 | 5.756 | 6.372 | 105.4483 | 854.945 | 1327.3303 | 1056.4793 | 20.4057 | 64.4847 | 955.7121 | 88.9665
[11 empty] | 1998-10-08 | 10:00 | 3075 | 29.384 | 133.806 | 59.085 | 18.336 | 0 | 13.194 | 3.165 |  | 16.359 | 16.359 | 0.80653 | 0 | 11.9945 | 11.8592 | 8.1015 | 70.008 | 0.1694 | 8.483 | 5.76 | 34.0515 | 292.272 | 296.7139 | 1408.7612 | 1391.6801 | 1.2125 | 88.5238 | 844.197 | 95.9664 | 133.806 | 115.132 | 18.336 | 8.482 | 9.923 | 18.405 | 18.405 | 0.094461 | 0.46085 | 12.8841 | 12.7386 | 3.9884 | 102.1446 | 0.12471 | 5.76 | 5.76 | 17.2965 | 296.7139 | 534.15 | 535.5549 | -0.26301 | 94.1706 | 416.1344 | 95.8435 | 115.132 | 100.65 | 18.336 | 4.712 | 5.211 | 9.923 | 9.923 | 0.10093 | 0.47486 | 14.3149 | 14.1534 | 7.2782 | 82.2768 | 0.17202 | 5.76 | 5.76 | 32.9351 | 534.15 | 952.77 | 987.3691 | -3.6314 | 88.9001 | 760.7595 | 95.6708 | 100.65 | 59.085 | 18.336 | 1.207 | 3.165 | 4.372 | 4.372 | 0.15079 | 0.27608 | 10.7289 | 10.6078 | 10.0845 | 51.447 | 0.20619 | 5.76 | 6.532 | 105.8198 | 952.77 | 1408.7612 | 1275.7617 | 9.4409 | 64.3361 | 1114.2659 | 90.5032
[11 empty] | 1998-10-08 | 18:00 | 3083 | 29.38 | 134.181 | 59.295 | 18.234 | 0 | 13.241 | 3.166 |  | 16.407 | 16.407 | 0.80703 | 0 | 12.0373 | 11.9028 | 8.1201 | 70.3839 | 0.16911 | 7.602 | 5.757 | 33.9575 | 292.896 | 296.6486 | 1405.1151 | 1395.2884 | 0.69935 | 88.553 | 845.9685 | 95.986 | 134.181 | 115.47 | 18.234 | 8.543 | 9.988 | 18.531 | 18.531 | 0.095098 | 0.46101 | 12.9767 | 12.8318 | 3.9902 | 102.6013 | 0.12506 | 5.757 | 5.757 | 17.16 | 296.6486 | 532.8 | 535.7026 | -0.54479 | 94.2154 | 416.1756 | 95.8767 | 115.47 | 100.687 | 18.234 | 4.698 | 5.29 | 9.988 | 9.988 | 0.10189 | 0.47036 | 14.2724 | 14.113 | 7.2242 | 82.6203 | 0.17082 | 5.757 | 5.757 | 32.5238 | 532.8 | 955.5 | 977.0906 | -2.2596 | 89.0362 | 754.9453 | 95.6919 | 100.687 | 59.295 | 18.234 | 1.22 | 3.166 | 4.386 | 4.386 | 0.15109 | 0.27816 | 10.8444 | 10.7233 | 10.1359 | 51.6211 | 0.20773 | 5.757 | 6.551 | 105.6557 | 955.5 | 1405.1151 | 1282.9827 | 8.692 | 64.3836 | 1119.2413 | 90.5601
[11 empty] | 1998-10-09 | 2:00 | 3091 | 29.333 | 134.596 | 59.67 | 18.207 | 0 | 13.254 | 3.106 |  | 16.36 | 16.36 | 0.81015 | 0 | 12.0491 | 11.9311 | 8.2556 | 70.6704 | 0.16883 | 8.416 | 5.748 | 33.464 | 293.76 | 296.9179 | 1392.9613 | 1421.135 | -2.0226 | 88.7295 | 859.0265 | 96.1044 | 134.596 | 115.935 | 18.207 | 8.542 | 10.037 | 18.579 | 18.579 | 0.095421 | 0.45977 | 12.9752 | 12.8481 | 3.9891 | 103.0694 | 0.12465 | 5.748 | 5.748 | 17.082 | 296.9179 | 536.4 | 535.0726 | 0.24747 | 94.2469 | 415.9953 | 95.8937 | 115.935 | 101.19 | 18.207 | 4.712 | 5.325 | 10.037 | 10.037 | 0.10245 | 0.46946 | 14.3149 | 14.1747 | 7.266 | 83.0895 | 0.1706 | 5.748 | 5.748 | 32.6701 | 536.4 | 958.685 | 982.1418 | -2.4468 | 88.9969 | 759.2709 | 95.6972 | 101.19 | 59.67 | 18.207 | 1.22 | 3.106 | 4.326 | 4.326 | 0.14869 | 0.28202 | 10.8444 | 10.7382 | 10.2081 | 52.0149 | 0.20645 | 5.748 | 6.486 | 105.4426 | 958.685 | 1392.9613 | 1293.8285 | 7.1167 | 64.4876 | 1126.2568 | 90.6378
[11 empty] | 1998-10-09 | 10:00 | 3099.0003 | 29.325 | 134.69 | 59.572 | 18.243 | 0 | 13.256 | 3.166 |  | 16.422 | 16.422 | 0.80721 | 0 | 12.0509 | 11.9357 | 8.1299 | 70.7581 | 0.16868 | 8.521 | 5.769 | 35.3675 | 302.544 | 298.1746 | 1440.3614 | 1398.5442 | 2.9032 | 88.1387 | 848.3594 | 95.8311 | 134.69 | 115.98 | 18.243 | 8.544 | 9.861 | 18.405 | 18.405 | 0.094254 | 0.46422 | 12.9782 | 12.8541 | 4.0209 | 103.0711 | 0.12471 | 5.769 | 5.769 | 17.628 | 298.1746 | 554.4 | 541.2523 | 2.3715 | 94.088 | 419.7134 | 95.8 | 115.98 | 101.227 | 18.243 | 4.712 | 5.149 | 9.861 | 9.861 | 0.1001 | 0.47784 | 14.3149 | 14.1781 | 7.6014 | 82.7591 | 0.17132 | 5.769 | 5.769 | 32.8882 | 554.4 | 985.075 | 1031.6507 | -4.7281 | 88.9702 | 793.0253 | 95.8528 | 101.227 | 59.572 | 18.243 | 1.226 | 3.166 | 4.392 | 4.392 | 0.15121 | 0.27914 | 10.8978 | 10.7936 | 10.487 | 51.6695 | 0.2089 | 5.769 | 6.584 | 106.488 | 985.075 | 1440.3614 | 1325.2985 | 7.9885 | 64.2867 | 1155.1868 | 90.7818
[11 empty] | 1998-10-09 | 18:00 | 3107 | 29.299 | 134.69 | 59.692 | 18.247 | 0 | 13.258 | 3.166 |  | 16.424 | 16.424 | 0.80723 | 0 | 12.0527 | 11.9467 | 8.1472 | 70.7968 | 0.16875 | 8.534 | 5.764 | 34.78 | 302.256 | 298.1174 | 1426.9921 | 1400.8742 | 1.8303 | 88.3335 | 849.4958 | 95.9058 | 134.69 | 116.07 | 18.247 | 8.546 | 10.036 | 18.582 | 18.582 | 0.095428 | 0.45991 | 12.9813 | 12.867 | 4.0008 | 103.1322 | 0.12476 | 5.764 | 5.764 | 17.511 | 298.1174 | 553.05 | 537.0635 | 2.8906 | 94.1261 | 417.5905 | 95.8067 | 116.07 | 101.467 | 18.247 | 4.712 | 5.324 | 10.036 | 10.036 | 0.10244 | 0.46951 | 14.3149 | 14.189 | 7.5007 | 83.0208 | 0.17091 | 5.764 | 5.764 | 33.0795 | 553.05 | 987.35 | 1013.2493 | -2.6231 | 88.9039 | 783.1496 | 95.7761 | 101.467 | 59.692 | 18.247 | 1.22 | 3.166 | 4.386 | 4.386 | 0.15109 | 0.27816 | 10.8444 | 10.749 | 10.5072 | 51.8253 | 0.20741 | 5.764 | 6.552 | 106.367 | 987.35 | 1426.9921 | 1326.8317 | 7.019 | 64.3204 | 1157.0909 | 90.8074
[11 empty] | 1998-10-10 | 0:00 | 3113 | 29.261 | 135.105 | 60 | 18.198 | 0 | 13.193 | 3.167 |  | 16.36 | 16.36 | 0.80642 | 0 | 11.9936 | 11.9015 | 8.1288 | 71.2257 | 0.1671 | 8.533 | 5.748 | 34.686 | 302.976 | 298.3622 | 1425.1691 | 1396.7773 | 1.9922 | 88.3745 | 847.5698 | 95.9076 | 135.105 | 116.167 | 18.198 | 8.48 | 9.803 | 18.283 | 18.283 | 0.093654 | 0.46382 | 12.881 | 12.782 | 4.0249 | 103.4131 | 0.1236 | 5.748 | 5.748 | 17.394 | 298.3622 | 552.15 | 541.4114 | 1.9449 | 94.1702 | 419.8868 | 95.8575 | 116.167 | 101.265 | 18.198 | 4.713 | 5.09 | 9.803 | 9.803 | 0.099323 | 0.48077 | 14.318 | 14.2079 | 7.5936 | 82.9244 | 0.17134 | 5.748 | 5.748 | 33.0942 | 552.15 | 990.535 | 1032.761 | -4.2629 | 88.908 | 792.4555 | 95.8238 | 101.265 | 60 | 18.198 | 1.22 | 3.167 | 4.387 | 4.387 | 0.15113 | 0.27809 | 10.8444 | 10.7611 | 10.5454 | 51.8891 | 0.20739 | 5.748 | 6.473 | 106.3066 | 990.535 | 1425.1691 | 1331.1598 | 6.5964 | 64.37 | 1160.8474 | 90.8423
[11 empty] | 1998-10-10 | 10:00 | 3123 | 29.376 | 134.415 | 59.55 | 18.324 | 0 | 13.257 | 3.166 |  | 16.423 | 16.423 | 0.80722 | 0 | 12.0518 | 11.9186 | 8.1447 | 70.5138 | 0.16903 | 8.284 | 5.744 | 33.558 | 293.904 | 296.8282 | 1395.3919 | 1399.22 | -0.27434 | 88.6945 | 848.0241 | 96.0428 | 134.415 | 115.762 | 18.324 | 8.545 | 10.031 | 18.576 | 18.576 | 0.095391 | 0.46 | 12.9797 | 12.8363 | 3.987 | 102.7775 | 0.12489 | 5.744 | 5.744 | 17.2185 | 296.8282 | 537.3 | 535.0162 | 0.42505 | 94.1992 | 415.9222 | 95.8602 | 115.762 | 101.122 | 18.324 | 4.712 | 5.319 | 10.031 | 10.031 | 0.10237 | 0.46974 | 14.3149 | 14.1567 | 7.2777 | 82.8403 | 0.17089 | 5.744 | 5.744 | 32.9351 | 537.3 | 960.05 | 984.1072 | -2.5058 | 88.9043 | 760.7036 | 95.6704 | 101.122 | 59.55 | 18.324 | 1.22 | 3.166 | 4.386 | 4.386 | 0.15109 | 0.27816 | 10.8444 | 10.7246 | 10.1955 | 51.8165 | 0.20697 | 5.744 | 6.441 | 105.2035 | 960.05 | 1395.3919 | 1289.4602 | 7.5915 | 64.5574 | 1124.7551 | 90.6465
[11 empty] | 1998-10-10 | 18:00 | 3131 | 29.384 | 134.469 | 59.512 | 18.24 | 0 | 13.255 | 3.166 |  | 16.421 | 16.421 | 0.8072 | 0 | 12.05 | 11.914 | 8.1441 | 70.6064 | 0.16874 | 8.498 | 5.746 | 33.5345 | 293.808 | 296.8118 | 1395.3919 | 1399.0674 | -0.26341 | 88.7018 | 847.9396 | 96.0452 | 134.469 | 115.635 | 18.24 | 8.543 | 10.168 | 18.711 | 18.711 | 0.096298 | 0.45658 | 12.9767 | 12.8302 | 3.9708 | 102.8412 | 0.12476 | 5.746 | 5.746 | 17.199 | 296.8118 | 536.85 | 531.7383 | 0.95216 | 94.2054 | 414.2751 | 95.8484 | 115.635 | 101.01 | 18.24 | 4.712 | 5.456 | 10.168 | 10.168 | 0.1042 | 0.46341 | 14.3149 | 14.1534 | 7.2198 | 82.8627 | 0.17081 | 5.746 | 5.746 | 32.6066 | 536.85 | 955.5 | 972.3329 | -1.7617 | 89.0144 | 754.5915 | 95.6789 | 101.01 | 59.512 | 18.24 | 1.201 | 3.166 | 4.367 | 4.367 | 0.15071 | 0.27502 | 10.6756 | 10.5551 | 10.1164 | 51.9046 | 0.20336 | 5.746 | 6.464 | 105.1488 | 955.5 | 1395.3919 | 1278.0748 | 8.4075 | 64.5739 | 1116.7874 | 90.5847
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A1: Catherine Hughes was not part of the EPA reviewing team. All comments from Catherine Hughes are lab verifications.
Note on S75: This time has been adjusted to reflect the plant was down from 8/23 until 9/1. It was assumed that the pilot ran for the remainder of 8/22, ran for approximately 8 hours on 8/23, and was started at approximately 7 am on 9/1.
Note on Z111: Reported as 1.61. Questionable value so changed to NR
Note on AA8: No cleaning events took place during this time
Note on AJ146: MTCw fluectuation is dur to the changes in PC. Records do not indicate why Pc changed during this time.
Note on DI183: Erroneous data points
Note on DI184: Erroneous data point
Note on DI185: Erroneous data point
Note on DS22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on DU33: Concentration reported as 2.68. This value was from the laboratory data collection sheet. The actual data output was not found, therefore concentration is questionable. Changed to NR
Note on DV22: Feed and Permeate TOC values lab verified. TOC analyzer was recalibrated and new standards prepared . This value falls within the expected range.
Note on DV27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands. TSC-ADM: reported residual was 8.7 mg/L
Note on DV33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on DV48: Lab verified.
Note on ED21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on ED43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on ED65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EM22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EO33: Reported as 41.63. Lab analysis error highly likely. Reported as NR
Note on EP22: Problems measuring TOC occurred during the pilot study. This TOC value is high for the feed water.
Note on EP27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands. TSC-ADM: reported residual was 1.0 mg/L
Note on EP33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on EP48: Lab verified
Note on EQ16: Concentrations for alkalinity, total hardness, calcium hardness, and turbidity were lab verified
Note on EQ18: Reported as 16.0. However, the calcium hardness in the permeate was 22.0. A laboratory collection error is suspected. Changed to NR
Note on EQ19: Reported as 16.0. However, the calcium hardness in the permeate was 16.0. A laboratory collection error is suspected. Changed to NR
Note on EX21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EX43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on EX65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FG22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FI22: Feed and Permeate concentrations were lab verified
Note on FI33: Reported as 61.28. However, given the low TOC value, it is unlikely a high concentration of CHCL3 would result. Changed to NR
Note on FI43: This value has been lab verified. The sample was delivered to the lab on 9/4/98 and analyzed 9/10/98. A concentration of 21.50 was found. However, due to the questionable value, changed to NR
Note on FJ22: Problems measuring TOC occurred during the pilot study. This TOC value is high for the feed water.Lab error or contamination could be the cause of the high value.
Note on FJ27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands. TSC-ADM: reported residual was 2.25 mg/L
Note on FJ33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on FJ48: Lab verified
Note on FR21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FR43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on FR65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GC22: Feed and permeate concentrations were lab verified
Note on GC26: Verified from laboratory notes. Possible record keeping error would explain the chlorine dose for the permeate being higher than the chlorine dose for the feed.
Note on GC37: Feed and permeate concentrationsLab verified
Note on GD27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands.
Note on GD33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GD48: Lab verified
Note on GE20: Lab Verified
Note on GL21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GL43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GL65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GU22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on GW22: Feed and permeate concetrations were lab verified
Note on GW26: Verified from laboratory notes. Possible record keeping error would explain the chlorine dose for the permeate being higher than the chlorine dose for the feed.
Note on GW33: Reported as 61.55. However, given the low TOC concentrations, this value is questionable. Changed to NR
Note on GX27: As recommended in the comments from Steve Allgeier, all chlrone residuals have been changed to BMRL because the chlorine dose was consistently too low to satisfy the ammonia and TOC demands. TSC-ADM: reported residual was 0.5 mg/L
Note on GX33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GX48: Lab verified
Note on HA20: Lab verified
Note on HF21: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HF43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HF65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HO3: Reviewer DJ: Changed "Week 20" to "Week 18"
Note on HO22: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HQ11: Reviewer DJ: Changed 9/30/98 to 9/18/98
Note on HQ22: Feed and Permeate concentrations were lab verified
Note on HQ33: Reported as 66.64. However, given the low TOC concenration, this value is questionable. Changed to NR
Note on HQ37: Feed and permeate concentrations were lab verified
Note on HR11: Reviewer DJ: Changed 9/30/98 to 9/18/98
Note on HR22: Problems measuring TOC occurred during the pilot study. This TOC value is high for the feed water.Lab error or contamination could be the cause of the high value.
Note on HR33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on HR48: Lab verified
Note on HS11: Reviewer DJ: Changed 9/30/98 to 9/18/98
Note on HZ3: Reviewer DJ: Changed "Week 20" to "Week 18"
Note on HZ43: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on HZ65: TSC_ADM: As noted in the Summary Report, there was some trouble with TOC analyses through the end of September.
Note on IB11: Reviewer DJ: Changed 9/16/98 to 9/18/98
Note on IB33: Reviewer DJ: Changed 9/16/98 to 9/18/98
Note on IB55: Reviewer DJ: Changed 9/16/98 to 9/18/98
Note on IC11: Reviewer DJ: Changed 9/16/98 to 9/18/98
Note on IC33: Reviewer DJ: Changed 9/16/98 to 9/18/98
Note on IC55: Reviewer DJ: Changed 9/16/98 to 9/18/98

## Sheet3. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2a: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 28 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Pompano Beach | Membrane manufacturer | FLUID SYSTEMS CORP. | Average yearly temperature of feed water, TavgoC (oC) | 29 | Alkalinity (mg/L as CaCO3) | 48 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.46117 | [6 empty] | System recovery during sample collection (decimal) | 0.83 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53066 | [6 empty] | System recovery during sample collection (decimal) | 0.78 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5113 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5172 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.47584 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5172 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4131618 | Membrane trade name | FLUID SYSTEMS | Temperature normalized MTCW (gfd/psi) | 0.12621 | Calcium Hardness (mg/L as CaCO3) | 250 | Cartridge filtration | 1 micron | Pilot - scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 18.54 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.55 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.45 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.26 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.58 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.5 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.44 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.02 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.8 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.47 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.44 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.02 |  |  |  |  | Capital Recovery Interest Rate (%) | 3
Water Industry Data Base Number (optional) |  | Membrane element model number | 2540 TFCS / 4921 TFCS |  |  | LSI | 0.3 | sulfuric acid addition | pH = 5.7, Dosage= 42 mg/L | Pilot - scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 18.54 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.54 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.45 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.45 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.58 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.58 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.44 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.44 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.44 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.44 |  |  |  |  | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.1 |  |  |  | 1998-10-11 | 2:00 | 3139.0003 | 29.18 | 135.454 | 60.382 | 18.21 | 0 | 14.439 | 3.227 |  | 17.666 | 17.666 | 0.81733 | 0 | 13.1264 | 13.0567 | 8.5566 | 71.1514 | 0.18351 | 8.593 | 5.751 | 35.4615 | 311.328 | 299.7821 | 1444.615 | 1482.4672 | -2.6202 | 88.1709 | 891.1246 | 96.0206 | 135.454 | 116.887 | 18.21 | 8.54 | 9.871 | 18.411 | 18.411 | 0.37723 | 0.46385 | 12.9722 | 12.9033 | 4.0424 | 103.9181 | 0.12417 | 5.751 | 5.751 | 17.6085 | 299.7821 | 567.45 | 543.9075 | 4.1488 | 94.1262 | 421.8448 | 95.8258 | 116.887 | 101.947 | 18.21 | 4.699 | 5.172 | 9.871 | 9.871 | 0.40129 | 0.47604 | 14.2754 | 14.1997 | 7.7689 | 83.4381 | 0.17018 | 5.751 | 5.751 | 33.2387 | 567.45 | 1017.6075 | 1052.8056 | -3.4589 | 88.9124 | 810.1278 | 95.8971 | 101.947 | 60.382 | 18.21 | 1.2 | 3.227 | 4.427 | 4.427 | 0.15314 | 0.27106 | 10.6667 | 10.6101 | 10.8003 | 52.1542 | 0.20344 | 5.751 | 6.483 | 106.9056 | 1017.6075 | 1444.615 | 1356.2633 | 6.1159 | 64.3389 | 1186.9354 | 90.9931 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Design system recovery, R (decimal) | 0.8 | Total iron (mg/L) | 0.3 |  |  |  | 1998-10-11 | 10:00 | 3147 | 29.282 | 134.643 | 59.82 | 18.201 | 0 | 14.395 | 3.165 |  | 17.56 | 17.56 | 0.81976 | 0 | 13.0864 | 12.9777 | 8.6227 | 70.4078 | 0.18432 | 8.439 | 5.767 | 34.545 | 301.488 | 297.9053 | 1419.6994 | 1495.7161 | -5.3544 | 88.404 | 896.8107 | 96.148 | 134.643 | 115.972 | 18.201 | 8.484 | 10.095 | 18.579 | 18.579 | 0.38246 | 0.45664 | 12.8871 | 12.7801 | 3.9847 | 103.1218 | 0.12393 | 5.767 | 5.767 | 17.3355 | 297.9053 | 550.35 | 533.7006 | 3.0252 | 94.1809 | 415.803 | 95.8308 | 115.972 | 101.182 | 18.201 | 4.698 | 5.397 | 10.095 | 10.095 | 0.41327 | 0.46538 | 14.2724 | 14.1539 | 7.4242 | 82.9518 | 0.17063 | 5.767 | 5.767 | 33.0703 | 550.35 | 978.9325 | 1000.6335 | -2.2168 | 88.899 | 775.4917 | 95.7356 | 101.182 | 59.82 | 18.201 | 1.213 | 3.165 | 4.378 | 4.378 | 0.15091 | 0.27707 | 10.7822 | 10.6927 | 10.4028 | 51.8972 | 0.20604 | 5.767 | 6.538 | 105.9408 | 978.9325 | 1419.6994 | 1313.5104 | 7.4797 | 64.4381 | 1146.2214 | 90.7574 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-10-11 | 18:00 | 3155 | 29.304 | 134.67 | 59.782 | 18.118 | 0 | 14.468 | 3.166 |  | 17.634 | 17.634 | 0.82046 | 0 | 13.1527 | 13.0351 | 8.6642 | 70.4438 | 0.18504 | 8.365 | 5.767 | 34.3335 | 302.208 | 298.093 | 1425.7766 | 1503.422 | -5.4458 | 88.4823 | 900.7575 | 96.1884 | 134.67 | 115.95 | 18.118 | 8.543 | 9.926 | 18.469 | 18.469 | 0.37874 | 0.46256 | 12.9767 | 12.8606 | 4.0141 | 103.1779 | 0.12465 | 5.767 | 5.767 | 17.4525 | 298.093 | 548.55 | 539.6315 | 1.6258 | 94.1453 | 418.8622 | 95.8334 | 115.95 | 101.257 | 18.118 | 4.712 | 5.214 | 9.926 | 9.926 | 0.40388 | 0.47471 | 14.3149 | 14.1869 | 7.4839 | 83.0016 | 0.17092 | 5.767 | 5.767 | 33.0777 | 548.55 | 983.0275 | 1014.393 | -3.1907 | 88.9036 | 781.4715 | 95.7673 | 101.257 | 59.782 | 18.118 | 1.213 | 3.166 | 4.379 | 4.379 | 0.15095 | 0.277 | 10.7822 | 10.6858 | 10.4497 | 51.9518 | 0.20569 | 5.767 | 6.562 | 106.0589 | 983.0275 | 1425.7766 | 1319.0234 | 7.4874 | 64.4209 | 1151.0254 | 90.7857 | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 (dup) | CF-sys-28 (dup) | CC-sys-28 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 (dup) | CI-s1-28 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25
|  | Membrane hydrophobicity | HYDRPHILIC | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | 0 |  |  |  | 1998-10-12 | 2:00 | 3163 | 29.265 | 134.898 | 59.94 | 18.226 | 0 | 14.459 | 3.167 |  | 17.626 | 17.626 | 0.82032 | 0 | 13.1445 | 13.042 | 8.651 | 70.542 | 0.18488 | 8.331 | 5.754 | 34.686 | 302.928 | 298.2154 | 1413.6228 | 1501.3638 | -6.2068 | 88.3688 | 899.7896 | 96.1451 | 134.898 | 116.272 | 18.226 | 8.541 | 9.928 | 18.469 | 18.469 | 0.37876 | 0.46245 | 12.9737 | 12.8724 | 4.0167 | 103.3423 | 0.12456 | 5.754 | 5.754 | 17.355 | 298.2154 | 551.7 | 539.8379 | 2.1501 | 94.1804 | 419.0266 | 95.8583 | 116.272 | 101.745 | 18.226 | 4.698 | 5.23 | 9.928 | 9.928 | 0.40436 | 0.47321 | 14.2724 | 14.161 | 7.5153 | 83.2672 | 0.17007 | 5.754 | 5.754 | 33.0933 | 551.7 | 986.2125 | 1017.5536 | -3.1779 | 88.9029 | 784.6268 | 95.7823 | 101.745 | 59.94 | 18.226 | 1.22 | 3.167 | 4.387 | 4.387 | 0.15113 | 0.27809 | 10.8444 | 10.7598 | 10.4975 | 52.119 | 0.20645 | 5.754 | 6.511 | 106.0013 | 986.2125 | 1413.6228 | 1325.2898 | 6.2487 | 64.4548 | 1155.7511 | 90.8284 | Sampling date | MM/DD/YY | 1998-10-13 | 1998-10-13 | 1998-10-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-13 | 1998-10-13 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-29 | 1998-10-29 | 1998-10-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-29 | 1998-10-29 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 7
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.1 |  |  |  | 1998-10-12 | 10:00 | 3171 | 29.27 | 135.313 | 60.037 | 18.262 | 0 | 14.478 | 3.106 |  | 17.584 | 17.584 | 0.82336 | 0 | 13.1618 | 13.0572 | 8.7788 | 70.6342 | 0.18486 | 8.283 | 5.768 | 34.404 | 301.44 | 297.9787 | 1416.6614 | 1526.5797 | -7.759 | 88.4542 | 912.2792 | 96.2288 | 135.313 | 116.512 | 18.262 | 8.546 | 9.983 | 18.529 | 18.529 | 0.3803 | 0.46122 | 12.9813 | 12.8781 | 4.0102 | 103.6403 | 0.12426 | 5.768 | 5.768 | 17.16 | 297.9787 | 549 | 538.3751 | 1.9353 | 94.2412 | 418.1769 | 95.8965 | 116.512 | 101.76 | 18.262 | 4.712 | 5.271 | 9.983 | 9.983 | 0.40692 | 0.472 | 14.3149 | 14.2011 | 7.4652 | 83.4088 | 0.17026 | 5.768 | 5.768 | 33.0814 | 549 | 979.8425 | 1010.2044 | -3.0987 | 88.8981 | 779.6022 | 95.7566 | 101.76 | 60.037 | 18.262 | 1.22 | 3.106 | 4.326 | 4.326 | 0.14869 | 0.28202 | 10.8444 | 10.7582 | 10.455 | 52.1815 | 0.20617 | 5.768 | 6.618 | 105.9696 | 979.8425 | 1416.6614 | 1323.0894 | 6.6051 | 64.4372 | 1151.466 | 90.797 | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:15 | 10:15 | 10:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:15 | 10:15 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 3391
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-10-12 | 18:00 | 3179 | 29.236 | 134.931 | 59.887 | 18.256 | 0 | 14.475 | 3.166 |  | 17.641 | 17.641 | 0.82053 | 0 | 13.1591 | 13.0676 | 8.6743 | 70.4787 | 0.18541 | 8.471 | 5.756 | 34.827 | 306.096 | 298.8029 | 1425.1691 | 1505.7046 | -5.6509 | 88.3445 | 902.2537 | 96.14 | 134.931 | 116.235 | 18.256 | 8.543 | 9.991 | 18.534 | 18.534 | 0.38047 | 0.46094 | 12.9767 | 12.8865 | 4.0172 | 103.3098 | 0.12474 | 5.756 | 5.756 | 17.394 | 298.8029 | 555.75 | 539.427 | 2.9371 | 94.1788 | 419.115 | 95.8498 | 116.235 | 101.647 | 18.256 | 4.712 | 5.279 | 9.991 | 9.991 | 0.40735 | 0.47162 | 14.3149 | 14.2154 | 7.5582 | 83.1268 | 0.17101 | 5.756 | 5.756 | 33.1586 | 555.75 | 998.4975 | 1022.2115 | -2.375 | 88.9028 | 788.9808 | 95.7973 | 101.647 | 59.887 | 18.256 | 1.22 | 3.166 | 4.386 | 4.386 | 0.15109 | 0.27816 | 10.8444 | 10.7691 | 10.6403 | 51.8707 | 0.20761 | 5.756 | 6.562 | 106.3613 | 998.4975 | 1425.1691 | 1342.2771 | 5.8163 | 64.4042 | 1170.3873 | 90.9123 | Operation time | hh.hh | 3409 | 3409 | 3409 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3409 | 3409 | --- | --- | --- | --- | Operation time | hh.hh | 3793 | 3793 | 3793 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3793 | 3793 | --- | --- | --- | --- | Operation time | hh.hh | 4081 | 4081 | 4081 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4081 | 4081 | --- | --- | --- | --- | Operation time | hh.hh | 4418 | 4418 | 4418 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4418 | 4418 | --- | --- | --- | --- | Operation time | hh.hh | 4729 | 4729 | 4729 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4729 | 4729 | --- | --- | --- | --- | Operation time | hh.hh | 4418 | 4418 | 4418 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4418 | 4418 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 267.13
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 8.9 |  |  |  | 1998-10-13 | 2:00 | 3187.0003 | 29.278 | 135.233 | 60.232 | 18.258 | 0 | 14.458 | 3.167 |  | 17.625 | 17.625 | 0.82031 | 0 | 13.1436 | 13.0361 | 8.6723 | 70.8022 | 0.18412 | 7.414 | 5.761 | 35.8845 | 313.968 | 300.0758 | 1445.2231 | 1506.1631 | -4.2167 | 88.0415 | 903.1195 | 96.0266 | 135.233 | 116.587 | 18.258 | 8.54 | 9.932 | 18.472 | 18.472 | 0.37886 | 0.46232 | 12.9722 | 12.866 | 4.038 | 103.614 | 0.12417 | 5.761 | 5.761 | 17.6865 | 300.0758 | 567.45 | 542.8875 | 4.3286 | 94.106 | 421.4816 | 95.8037 | 116.587 | 101.895 | 18.258 | 4.698 | 5.234 | 9.932 | 9.932 | 0.40457 | 0.47302 | 14.2724 | 14.1556 | 7.7394 | 83.2436 | 0.17005 | 5.761 | 5.761 | 33.2562 | 567.45 | 1021.93 | 1046.9385 | -2.4472 | 88.9174 | 807.1942 | 95.88 | 101.895 | 60.232 | 18.258 | 1.22 | 3.167 | 4.387 | 4.387 | 0.15113 | 0.27809 | 10.8444 | 10.7557 | 10.9114 | 51.8941 | 0.20726 | 5.761 | 6.572 | 107.0093 | 1021.93 | 1445.2231 | 1374.3781 | 4.902 | 64.3393 | 1198.1541 | 91.0688 | pH | --- | 5.39 | 5.6 | 6.12 | --- | --- | --- | --- | --- | pH | --- | 5.15 | 5.6 | --- | --- | --- | --- | pH | --- | 5.43 | 5.31 | 5.48 | --- | --- | --- | --- | --- | pH | --- | 5.4 | 5.31 | --- | --- | --- | --- | pH | --- | 5.35 | 5.86 | 6.12 | --- | --- | --- | --- | --- | pH | --- | 5.12 | 5.86 | --- | --- | --- | --- | pH | --- | 5.02 | 4.95 | 4.68 | --- | --- | --- | --- | --- | pH | --- | 4.89 | 4.95 | --- | --- | --- | --- | pH | --- | 4.72 | 4.85 | 5.7 | --- | --- | --- | --- | --- | pH | --- | 4.87 | 4.85 | --- | --- | --- | --- | pH | --- | 5.12 | 4.91 | 4.53 | --- | --- | --- | --- | --- | pH | --- | 4.85 | 4.91 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 25
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.82292 | Calcium (mg/L) | 252 |  |  |  | 1998-10-13 | 10:00 | 3195 | 29.287 | 135.032 | 59.842 | 18.303 | 0 | 14.467 | 3.167 |  | 17.634 | 17.634 | 0.8204 | 0 | 13.1518 | 13.0407 | 8.6548 | 70.4792 | 0.18503 | 8.377 | 5.768 | 34.451 | 300.624 | 297.995 | 1417.2689 | 1501.8762 | -5.9697 | 88.4391 | 899.9356 | 96.1718 | 135.032 | 116.257 | 18.303 | 8.547 | 9.988 | 18.535 | 18.535 | 0.38044 | 0.46113 | 12.9828 | 12.8731 | 4.0091 | 103.3324 | 0.12458 | 5.768 | 5.768 | 17.2185 | 297.995 | 549 | 538.2631 | 1.9557 | 94.2219 | 418.1291 | 95.882 | 116.257 | 101.572 | 18.303 | 4.712 | 5.276 | 9.988 | 9.988 | 0.40719 | 0.47177 | 14.3149 | 14.194 | 7.4633 | 83.1482 | 0.17071 | 5.768 | 5.768 | 33.0648 | 549 | 980.2975 | 1009.7822 | -3.0077 | 88.9042 | 779.3911 | 95.7576 | 101.572 | 59.842 | 18.303 | 1.208 | 3.167 | 4.375 | 4.375 | 0.15089 | 0.27611 | 10.7378 | 10.6471 | 10.4119 | 51.9921 | 0.20478 | 5.768 | 6.544 | 105.8717 | 980.2975 | 1417.2689 | 1313.8328 | 7.2983 | 64.472 | 1147.0652 | 90.7702 | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 79 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.9375 | Barium (mg/L) | 0.049 |  |  |  | 1998-10-13 | 18:00 | 3203 | 29.257 | 135.715 | 60.585 | 18.862 | 0 | 15.063 | 3.226 |  | 18.289 | 18.289 | 0.82361 | 0 | 13.6936 | 13.59 | 8.7959 | 70.4921 | 0.19279 | 8.462 | 5.762 | 34.31 | 302.112 | 298.0848 | 1403.2921 | 1529.7152 | -9.009 | 88.4899 | 913.9 | 96.2458 | 135.715 | 117.24 | 18.862 | 9.138 | 9.205 | 18.343 | 18.343 | 0.36744 | 0.49817 | 13.8805 | 13.7755 | 4.1999 | 103.4156 | 0.1332 | 5.762 | 5.762 | 17.4135 | 298.0848 | 548.1 | 576.7132 | -5.2204 | 94.1582 | 437.399 | 96.0189 | 117.24 | 102.517 | 18.862 | 4.712 | 4.493 | 9.205 | 9.205 | 0.36541 | 0.5119 | 14.3149 | 14.2066 | 7.8514 | 83.1651 | 0.17082 | 5.762 | 5.762 | 33.0446 | 548.1 | 981.89 | 1088.2605 | -10.8332 | 88.9144 | 818.1803 | 95.9612 | 102.517 | 60.585 | 18.862 | 1.213 | 3.226 | 4.439 | 4.439 | 0.15336 | 0.27326 | 10.7822 | 10.7006 | 10.408 | 52.281 | 0.20468 | 5.762 | 6.499 | 105.8026 | 981.89 | 1403.2921 | 1311.3054 | 6.5551 | 64.5059 | 1146.5977 | 90.7725 | Alkalinity | mg/L as CaCO3 | 18 | 42 | 160 | 151.3333 | 5.4167 | 57.1429 | 96.6667 | 81.3793 | Alkalinity | mg/L as CaCO3 | 12 | 42 | 67.6757 | 71.4286 | 54.8378 | 78.1173 | Alkalinity | mg/L as CaCO3 | 16 | 26 | 68 | 74.8235 | -10.0346 | 38.4615 | 50.4118 | 68.2614 | Alkalinity | mg/L as CaCO3 | 18 | 26 | 35.0452 | 30.7692 | 30.5226 | 41.0273 | Alkalinity | mg/L as CaCO3 | 14 | 26 | 156 | 68.5455 | 56.0606 | 46.1538 | 47.2727 | 70.3846 | Alkalinity | mg/L as CaCO3 | 18 | 26 | 34.37 | 30.7692 | 30.185 | 40.3678 | Alkalinity | mg/L as CaCO3 | 14 | NR | 180 | 14 | 92.2222 | 0 | 14 | 0 | Alkalinity | mg/L as CaCO3 | 14 | 14 | 14 | 0 | 14 | 0 | Alkalinity | mg/L as CaCO3 | 20 | 50 | 186 | 177.8947 | 4.3577 | 60 | 113.9474 | 82.448 | Alkalinity | mg/L as CaCO3 | 18 | 50 | 79.0504 | 64 | 64.5252 | 72.1039 | Alkalinity | mg/L as CaCO3 | 14 | NR | 200 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 14 | 16 | 18.1425 | #VALUE! | 17.0713 | 17.9908 | Electric Rate ($/kW-h) | 0.07
Mailing Address |  | Design flux, FW (gfd) | 17.9 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.875 | Strontium (mg/L) | 0.4 |  |  |  | 1998-10-14 | 2:00 | 3211 | 29.227 | 135.816 | 60.585 | 18.972 | 0 | 15.053 | 3.166 |  | 18.219 | 18.219 | 0.82623 | 0 | 13.6845 | 13.593 | 8.9196 | 70.3089 | 0.19333 | 8.39 | 5.753 | 34.216 | 302.784 | 298.3214 | 1390.5302 | 1554.0319 | -11.7582 | 88.5305 | 926.1766 | 96.3057 | 135.816 | 117.412 | 18.972 | 9.134 | 9.337 | 18.471 | 18.471 | 0.37091 | 0.4945 | 13.8744 | 13.7816 | 4.1848 | 103.4572 | 0.13321 | 5.753 | 5.753 | 17.2965 | 298.3214 | 547.2 | 573.2365 | -4.7581 | 94.2021 | 435.779 | 96.0309 | 117.412 | 102.562 | 18.972 | 4.712 | 4.625 | 9.337 | 9.337 | 0.37246 | 0.50466 | 14.3149 | 14.2192 | 7.7605 | 83.2545 | 0.17079 | 5.753 | 5.753 | 33.0584 | 547.2 | 981.6625 | 1071.0131 | -9.102 | 88.9185 | 809.1065 | 95.9142 | 102.562 | 60.585 | 18.972 | 1.207 | 3.166 | 4.373 | 4.373 | 0.15083 | 0.27601 | 10.7289 | 10.6571 | 10.4289 | 52.1726 | 0.20427 | 5.753 | 6.483 | 105.7363 | 981.6625 | 1390.5302 | 1315.599 | 5.3887 | 64.5562 | 1148.6307 | 90.7946 | Total dissolved solids | mg/L | 35.4 | 311 | 1330 | 1566.5111 | -17.7828 | 88.6174 | 938.7556 | 96.2291 | Total dissolved solids | mg/L | 23.7 | 311 | 556.8874 | 92.3794 | 433.9437 | 94.5385 | Total dissolved solids | mg/L | 46.7 | 353 | 1470 | 1848.4647 | -25.7459 | 86.7705 | 1100.7324 | 95.7574 | Total dissolved solids | mg/L | 41.5 | 353 | 705.1966 | 88.2436 | 529.0983 | 92.1565 | Total dissolved solids | mg/L | 41.2 | 295 | 1330 | 1194.8364 | 10.1627 | 86.0339 | 744.9182 | 94.4692 | Total dissolved solids | mg/L | 23.7 | 295 | 578.8491 | 91.9661 | 436.9246 | 94.5757 | Total dissolved solids | mg/L | 34 | 332 | 1260 | 1524 | -20.9524 | 89.759 | 928 | 96.3362 | Total dissolved solids | mg/L | 24 | 332 | 661.9477 | 92.7711 | 496.9739 | 95.1708 | Total dissolved solids | mg/L | 35.6 | 331 | 1360 | 1590.3368 | -16.9365 | 89.2447 | 960.6684 | 96.2942 | Total dissolved solids | mg/L | 25.4 | 331 | 608.4311 | 92.3263 | 469.7155 | 94.5925 | Total dissolved solids | mg/L | 47.2 | 332 | 1280 | 1471.2 | -14.9375 | 85.7831 | 901.6 | 94.7649 | Total dissolved solids | mg/L | 22.2 | 332 | 663.876 | 93.3133 | 497.938 | 95.5416 | Fuel Oil Rate ($/gal) | 0.89
|  | Net driving pressure at the design flux, NDP (psi) | 80 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.9375 | Reactive silica (mg/L as SiO2) | 6.29 |  |  |  | 1998-10-14 | 10:00 | 3219 | 29.1 | 135.976 | 60.817 | 18.82 | 0 | 15.002 | 3.226 |  | 18.228 | 18.228 | 0.82302 | 0 | 13.6382 | 13.5979 | 8.7824 | 70.7941 | 0.19208 | 8.329 | 5.746 | 35.109 | 307.2 | 299.2272 | 1413.6228 | 1527.4669 | -8.0534 | 88.2668 | 913.347 | 96.156 | 135.976 | 117.562 | 18.82 | 9.084 | 9.447 | 18.531 | 18.531 | 0.37318 | 0.49021 | 13.7985 | 13.7578 | 4.1736 | 103.7754 | 0.13257 | 5.746 | 5.746 | 17.3745 | 299.2272 | 559.8 | 570.2497 | -1.8667 | 94.1935 | 434.7385 | 96.0035 | 117.562 | 102.87 | 18.82 | 4.698 | 4.749 | 9.447 | 9.447 | 0.3787 | 0.4973 | 14.2724 | 14.2303 | 7.8713 | 83.5247 | 0.17037 | 5.746 | 5.746 | 33.1586 | 559.8 | 1002.365 | 1080.7857 | -7.8236 | 88.9186 | 820.2929 | 95.9577 | 102.87 | 60.817 | 18.82 | 1.22 | 3.226 | 4.446 | 4.446 | 0.1535 | 0.2744 | 10.8444 | 10.8124 | 10.6549 | 52.3686 | 0.20647 | 5.746 | 6.424 | 106.3094 | 1002.365 | 1413.6228 | 1341.2329 | 5.1209 | 64.472 | 1171.7989 | 90.9277 | Total hardness | mg/L as CaCO3 | 16 | 280 | 1740 | 1482.6667 | 14.7893 | 94.2857 | 881.3333 | 98.1846 | Total hardness | mg/L as CaCO3 | 12 | 280 | 509.3694 | 95.7143 | 394.6847 | 96.9596 | Total hardness | mg/L as CaCO3 | 18 | 310 | 1760 | 1735.6471 | 1.3837 | 94.1935 | 1022.8235 | 98.2402 | Total hardness | mg/L as CaCO3 | 14 | 310 | 644.6716 | 95.4839 | 477.3358 | 97.0671 | Total hardness | mg/L as CaCO3 | 14 | 308 | 1740 | 1350.3636 | 22.3929 | 95.4545 | 829.1818 | 98.3116 | Total hardness | mg/L as CaCO3 | 18 | 308 | 611.4141 | 94.1558 | 459.707 | 96.0845 | Total hardness | mg/L as CaCO3 | 14 | 300 | 1400 | 1444 | -3.1429 | 95.3333 | 872 | 98.3945 | Total hardness | mg/L as CaCO3 | 12 | 300 | 608.5226 | 96 | 454.2613 | 97.3583 | Total hardness | mg/L as CaCO3 | 18 | 288 | 1640 | 1439.0526 | 12.2529 | 93.75 | 863.5263 | 97.9155 | Total hardness | mg/L as CaCO3 | 18 | 288 | 533.1125 | 93.75 | 410.5563 | 95.6157 | Total hardness | mg/L as CaCO3 | 14 | 280 | 1480 | 1344 | 9.1892 | 95 | 812 | 98.2759 | Total hardness | mg/L as CaCO3 | 12 | 280 | 567.0974 | 95.7143 | 423.5487 | 97.1668 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 4.9375 | Turbidity (ntu) | 0.24 |  |  |  | 1998-10-14 | 18:00 | 3227 | 29.04 | 136.131 | 60.862 | 18.853 | 0 | 15.05 | 3.166 |  | 18.216 | 18.216 | 0.8262 | 0 | 13.6818 | 13.6657 | 8.9243 | 70.7192 | 0.19324 | 8.368 | 5.743 | 35.0855 | 307.968 | 299.3659 | 1413.6228 | 1555.6579 | -10.0476 | 88.2801 | 927.5119 | 96.2172 | 136.131 | 117.63 | 18.853 | 9.139 | 9.392 | 18.531 | 18.531 | 0.37244 | 0.49317 | 13.882 | 13.8656 | 4.1922 | 103.8353 | 0.13353 | 5.743 | 5.743 | 17.355 | 299.3659 | 559.35 | 573.7801 | -2.5798 | 94.2027 | 436.573 | 96.0247 | 117.63 | 102.892 | 18.853 | 4.698 | 4.694 | 9.392 | 9.392 | 0.37576 | 0.50021 | 14.2724 | 14.2555 | 7.8949 | 83.5131 | 0.1707 | 5.743 | 5.743 | 33.1743 | 559.35 | 1002.1375 | 1085.9741 | -8.3658 | 88.9185 | 822.6621 | 95.9674 | 102.892 | 60.862 | 18.853 | 1.213 | 3.166 | 4.379 | 4.379 | 0.15095 | 0.277 | 10.7822 | 10.7695 | 10.6738 | 52.3502 | 0.20572 | 5.743 | 6.385 | 106.3555 | 1002.1375 | 1413.6228 | 1345.3414 | 4.8302 | 64.4731 | 1173.7394 | 90.9387 | Calcium hardness | mg/L as CaCO3 | 14 | 276 | 1560 | 1469.5556 | 5.7977 | 94.9275 | 872.7778 | 98.3959 | Calcium hardness | mg/L as CaCO3 | 10 | 276 | 503.6577 | 96.3768 | 389.8288 | 97.4348 | Calcium hardness | mg/L as CaCO3 | 16 | 290 | 1620 | 1627.7647 | -0.4793 | 94.4828 | 958.8824 | 98.3314 | Calcium hardness | mg/L as CaCO3 | 12 | 290 | 604.3199 | 95.8621 | 447.16 | 97.3164 | Calcium hardness | mg/L as CaCO3 | 14 | 296 | 1560 | 1295.8182 | 16.9347 | 95.2703 | 795.9091 | 98.241 | Calcium hardness | mg/L as CaCO3 | 16 | 296 | 588.9515 | 94.5946 | 442.4758 | 96.384 | Calcium hardness | mg/L as CaCO3 | 14 | 290 | 1100 | 1394 | -26.7273 | 95.1724 | 842 | 98.3373 | Calcium hardness | mg/L as CaCO3 | 10 | 290 | 589.9525 | 96.5517 | 439.9762 | 97.7272 | Calcium hardness | mg/L as CaCO3 | 18 | 256 | 1460 | 1270.6316 | 12.9704 | 92.9688 | 763.3158 | 97.6419 | Calcium hardness | mg/L as CaCO3 | 16 | 256 | 473.8778 | 93.75 | 364.9389 | 95.6157 | Calcium hardness | mg/L as CaCO3 | 14 | 270 | 1220 | 1294 | -6.0656 | 94.8148 | 782 | 98.2097 | Calcium hardness | mg/L as CaCO3 | 10 | 270 | 548.5273 | 96.2963 | 409.2637 | 97.5566 | Current Process Water Rate ($/1000 gal) | 0.95
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Permeate flow rate from system, Qp-sys (gpm) | 19.75 | SDI | 2.5 |  |  |  | 1998-10-15 | 2:00 | 3235 | 29.261 | 135.38 | 60.217 | 18.9 | 0 | 15.068 | 3.167 |  | 18.235 | 18.235 | 0.82632 | 0 | 13.6982 | 13.5929 | 8.9112 | 69.9873 | 0.19422 | 8.292 | 5.732 | 31.678 | 284.88 | 295.4083 | 1335.838 | 1550.1884 | -16.0461 | 89.2765 | 922.7984 | 96.5672 | 135.38 | 116.88 | 18.9 | 9.135 | 9.397 | 18.532 | 18.532 | 0.37252 | 0.49293 | 13.8759 | 13.7693 | 4.1488 | 103.0812 | 0.13358 | 5.732 | 5.732 | 16.224 | 295.4083 | 515.25 | 566.8086 | -10.0065 | 94.5079 | 431.1085 | 96.2367 | 116.88 | 102 | 18.9 | 4.713 | 4.684 | 9.397 | 9.397 | 0.37563 | 0.50154 | 14.318 | 14.2079 | 7.2527 | 83.2873 | 0.17059 | 5.732 | 5.732 | 32.7318 | 515.25 | 921.6025 | 1000.7557 | -8.5886 | 88.9198 | 758.0028 | 95.6818 | 102 | 60.217 | 18.9 | 1.22 | 3.167 | 4.387 | 4.387 | 0.15113 | 0.27809 | 10.8444 | 10.7611 | 9.7532 | 52.4553 | 0.20515 | 5.732 | 6.343 | 103.801 | 921.6025 | 1335.838 | 1236.6381 | 7.426 | 64.8619 | 1079.1203 | 90.381 | Turbidity | ntu | 0.17 | 1.84 | 24.7 | 9.4478 | 61.7499 | 90.7609 | 5.6439 | 96.9879 | Turbidity | ntu | 0.158 | 1.84 | 3.2795 | 91.413 | 2.5598 | 93.8276 | Turbidity | ntu | 0.324 | 0.735 | 11.7 | 2.7416 | 76.5671 | 55.9184 | 1.7383 | 81.3614 | Turbidity | ntu | 0.473 | 0.735 | 1.0312 | 35.6463 | 0.88311 | 46.4396 | Turbidity | ntu | 0.356 | 2.45 | 24.7 | 9.8742 | 60.0236 | 85.4694 | 6.1621 | 94.2227 | Turbidity | ntu | 0.44 | 2.45 | 4.553 | 82.0408 | 3.5015 | 87.4339 | Turbidity | ntu | 0.239 | 2.12 | 24.3 | 9.644 | 60.3128 | 88.7264 | 5.882 | 95.9368 | Turbidity | ntu | 0.469 | 2.12 | 3.8886 | 77.8774 | 3.0043 | 84.3892 | Turbidity | ntu | 0.254 | 0.727 | 24.3 | 2.7435 | 88.71 | 65.0619 | 1.7352 | 85.3622 | Turbidity | ntu | 0.235 | 0.727 | 1.1736 | 67.6754 | 0.95032 | 75.2716 | Turbidity | ntu | 0.243 | 0.96 | 24.1 | 3.828 | 84.1162 | 74.6875 | 2.394 | 89.8496 | Turbidity | ntu | 0.189 | 0.96 | 1.7859 | 80.3125 | 1.373 | 86.2342 | Modifications to Existing Plant (% of construction costs) | 75
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | Feed flow rate to system, QF-sys (gpm) | 24.6875 | MFI |  |  |  |  | 1998-10-15 | 9:21 | 3242.3525 | 29.393 | 135.085 | 60.075 | 18.826 | 0 | 15.078 | 3.166 |  | 18.244 | 18.244 | 0.82646 | 0 | 13.7073 | 13.549 | 8.8884 | 69.8656 | 0.19393 | 8.318 | 5.757 | 31.8895 | 284.4 | 294.7637 | 1340.0915 | 1546.6957 | -15.4172 | 89.1813 | 920.7297 | 96.5365 | 135.085 | 116.722 | 18.826 | 9.14 | 9.271 | 18.411 | 18.411 | 0.36923 | 0.49644 | 13.8835 | 13.7232 | 4.1552 | 102.9223 | 0.13334 | 5.757 | 5.757 | 16.4385 | 294.7637 | 516.6 | 569.1561 | -10.1735 | 94.4232 | 431.9599 | 96.1944 | 116.722 | 101.76 | 18.826 | 4.712 | 4.559 | 9.271 | 9.271 | 0.36893 | 0.50825 | 14.3149 | 14.1496 | 7.3394 | 83.0756 | 0.17032 | 5.757 | 5.757 | 32.7216 | 516.6 | 915.915 | 1016.7173 | -11.0056 | 88.899 | 766.6587 | 95.7319 | 101.76 | 60.075 | 18.826 | 1.226 | 3.166 | 4.392 | 4.392 | 0.15121 | 0.27914 | 10.8978 | 10.7719 | 9.6931 | 52.3984 | 0.20558 | 5.757 | 6.454 | 103.8384 | 915.915 | 1340.0915 | 1230.3831 | 8.1866 | 64.7723 | 1073.149 | 90.324 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 21.7 | 24.7 | 27.2676 | #VALUE! | 25.9838 | 16.4864 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 15 | 29.5 | 45.8944 | #VALUE! | 37.6972 | 60.2092 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 2.61 | 68 | 136.4146 | 78.7805 | 102.2073 | 97.4464 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 2.86 | 14.9 | 27.798 | 80.8054 | 21.349 | 86.6036 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 4.53 | 14.9 | 24.3141 | 65.9398 | 19.6071 | 76.8961 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.55 | 19.8 | 39.3505 | 92.1717 | 29.5752 | 94.7591
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Concentrate-waste flow rate from system, QW-sys (gpm) | 4.9375 | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-10-15 | 21:00 | 3254 | 29.414 | 129.022 | 57.39 | 17.905 | 0 | 14.404 | 3.047 |  | 17.451 | 17.451 | 0.8254 | 0 | 13.0945 | 12.9353 | 8.8083 | 66.4927 | 0.19454 | 7.623 | 5.745 | 33.417 | 284.208 | 295.2859 | 1380.1995 | 1533.2117 | -11.0862 | 88.6832 | 914.2488 | 96.3449 | 129.022 | 110.872 | 17.905 | 8.541 | 9.333 | 17.874 | 17.874 | 0.36289 | 0.47784 | 12.9737 | 12.8159 | 4.0564 | 97.9856 | 0.13079 | 5.745 | 5.745 | 16.9845 | 295.2859 | 515.7 | 549.9706 | -6.6455 | 94.2481 | 422.6283 | 95.9812 | 110.872 | 96.945 | 17.905 | 4.669 | 4.664 | 9.333 | 9.333 | 0.37339 | 0.50027 | 14.1843 | 14.0118 | 7.2476 | 78.7559 | 0.17791 | 5.745 | 5.745 | 32.7005 | 515.7 | 922.285 | 999.2173 | -8.3415 | 88.9258 | 757.4587 | 95.6829 | 96.945 | 57.39 | 17.905 | 1.194 | 3.047 | 4.241 | 4.241 | 0.14581 | 0.28154 | 10.6133 | 10.4842 | 9.775 | 49.4875 | 0.21186 | 5.745 | 6.321 | 104.9328 | 922.285 | 1380.1995 | 1242.5733 | 9.9715 | 64.464 | 1082.4292 | 90.3058 | Total organic carbon | mg/L | NR | NR | 92.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.452 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | NR | 75 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | 12.3 | 68.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | 13.3 | 82.8 | 22.5 | 72.8261 | 12.7517 | 18.7 | 30.4813 | UV254 | cm-1 | BMRL | 0.483 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | 14.9 | 71.9 | 17.1368 | 76.1657 | 6.7669 | 15.2184 | 18.5198 | UV254 | cm-1 | BMRL | 0.495 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | 19.8 | 67.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.484 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Plant Name | Pompano Beach WTP | Total width of all membrane envelopes in the element, w (ft) | 14.4 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-10-16 | 5:00 | 3262.0003 | 29.227 | 130.007 | 58.125 | 18 | 0 | 14.356 | 3.047 |  | 17.403 | 17.403 | 0.82492 | 0 | 13.0509 | 12.9636 | 8.824 | 67.242 | 0.19279 | 8.708 | 5.75 | 33.746 | 291.696 | 296.6976 | 1400.2535 | 1535.5992 | -9.6658 | 88.6261 | 916.1484 | 96.3165 | 130.007 | 111.84 | 18 | 8.479 | 9.33 | 17.809 | 17.809 | 0.36198 | 0.47611 | 12.8795 | 12.7934 | 4.065 | 98.8585 | 0.12941 | 5.75 | 5.75 | 17.199 | 296.6976 | 530.55 | 550.7028 | -3.7985 | 94.2032 | 423.7002 | 95.9408 | 111.84 | 97.785 | 18 | 4.67 | 4.66 | 9.33 | 9.33 | 0.3732 | 0.50054 | 14.1873 | 14.0925 | 7.4763 | 79.3362 | 0.17763 | 5.75 | 5.75 | 32.4852 | 530.55 | 949.13 | 1029.6836 | -8.4871 | 89.0511 | 780.1168 | 95.8359 | 97.785 | 58.125 | 18 | 1.207 | 3.047 | 4.254 | 4.254 | 0.14607 | 0.28373 | 10.7289 | 10.6571 | 10.1075 | 49.8475 | 0.21379 | 5.75 | 6.355 | 105.48 | 949.13 | 1400.2535 | 1283.3228 | 8.3507 | 64.4487 | 1116.2264 | 90.5503 | UV254 | cm-1 | BMRL | 0.452 | 2.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 1.83 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.424 | 1.88 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 0.81356 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | NR | 2.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.495 | 2.06 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.2416 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.495 | 2.63 | 0.54616 | 79.2335 | 2.4242 | 0.52058 | 7.2187 | SUVA | L/(mg*m) | #VALUE! | 3.3221 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.484 | 2.53 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 2.4444 | --- | --- | --- | ---
Treatment Plant Category | CONV | Feed spacer thickness, T (ft) | 0.0029 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-10-16 | 13:00 | 3270 | 29.41 | 129.491 | 57.922 | 18.006 | 0 | 14.377 | 3.046 |  | 17.423 | 17.423 | 0.82517 | 0 | 13.07 | 12.9126 | 8.8117 | 66.8888 | 0.19305 | 8.594 | 5.763 | 33.088 | 284.256 | 295.343 | 1383.2381 | 1533.1765 | -10.8397 | 88.7968 | 914.2598 | 96.3809 | 129.491 | 111.397 | 18.006 | 8.481 | 9.499 | 17.98 | 17.98 | 0.36652 | 0.47169 | 12.8825 | 12.7273 | 4.024 | 98.414 | 0.12932 | 5.763 | 5.763 | 17.1405 | 295.343 | 516.6 | 543.7308 | -5.2518 | 94.1964 | 419.5369 | 95.9144 | 111.397 | 97.365 | 18.006 | 4.683 | 4.816 | 9.499 | 9.499 | 0.38187 | 0.493 | 14.2268 | 14.0555 | 7.1944 | 79.1806 | 0.17751 | 5.763 | 5.763 | 32.5183 | 516.6 | 919.555 | 987.3131 | -7.3686 | 88.9896 | 751.9566 | 95.6755 | 97.365 | 57.922 | 18.006 | 1.213 | 3.046 | 4.259 | 4.259 | 0.14615 | 0.28481 | 10.7822 | 10.6523 | 9.7711 | 49.8664 | 0.21362 | 5.763 | 6.453 | 104.6966 | 919.555 | 1383.2381 | 1244.0537 | 10.0622 | 64.5508 | 1081.8044 | 90.322 | SUVA | L/(mg*m) | NR | NR | 2.851 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | NR | 2.5067 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | 3.8316 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 3.7218 | 2.4879 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 3.3221 | 3.6579 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | 2.4444 | 3.7705 | --- | --- | --- | --- | ---
Process Train Name | Conventional train | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 16.4583 | [5 empty] | 1998-10-16 | 21:00 | 3278 | 29.363 | 129.256 | 57.87 | 17.95 | 0 | 14.415 | 3.047 |  | 17.462 | 17.462 | 0.82551 | 0 | 13.1045 | 12.9647 | 8.8416 | 66.7714 | 0.19417 | 8.551 | 5.737 | 32.994 | 285.84 | 295.7102 | 1369.2607 | 1538.59 | -12.3665 | 88.8425 | 917.1501 | 96.4026 | 129.256 | 111.232 | 17.95 | 8.538 | 9.27 | 17.808 | 17.808 | 0.36117 | 0.47945 | 12.9691 | 12.8307 | 4.0708 | 98.2232 | 0.13063 | 5.737 | 5.737 | 16.9845 | 295.7102 | 519.3 | 552.4266 | -6.3791 | 94.2564 | 424.0684 | 95.9949 | 111.232 | 97.2 | 17.95 | 4.67 | 4.6 | 9.27 | 9.27 | 0.37 | 0.50378 | 14.1873 | 14.0359 | 7.3368 | 78.9292 | 0.17783 | 5.737 | 5.737 | 32.6499 | 519.3 | 925.925 | 1013.3557 | -9.4425 | 88.9588 | 766.3278 | 95.7394 | 97.2 | 57.87 | 17.95 | 1.207 | 3.047 | 4.254 | 4.254 | 0.14607 | 0.28373 | 10.7289 | 10.6144 | 9.8391 | 49.7459 | 0.21337 | 5.737 | 6.219 | 104.6765 | 925.925 | 1369.2607 | 1251.244 | 8.619 | 64.6017 | 1088.5845 | 90.3842 | Bromide | mg/L | BMRL | BMRL | 1.44 | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | 3.93 | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | 0.72 | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
ICR Treatment Plant Identification Number | 1080 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 10.6979 | [5 empty] | 1998-10-17 | 5:00 | 3286 | 29.308 | 129.364 | 58.042 | 17.875 | 0 | 14.332 | 3.047 |  | 17.379 | 17.379 | 0.82467 | 0 | 13.0291 | 12.911 | 8.8058 | 67.0222 | 0.19264 | 8.516 | 5.739 | 34.545 | 295.056 | 297.2606 | 1411.1917 | 1532.9812 | -8.6303 | 88.3789 | 915.1209 | 96.2251 | 129.364 | 111.442 | 17.875 | 8.477 | 9.271 | 17.748 | 17.748 | 0.36038 | 0.47763 | 12.8765 | 12.7598 | 4.0818 | 98.4462 | 0.12961 | 5.739 | 5.739 | 17.1405 | 297.2606 | 538.65 | 553.3903 | -2.7365 | 94.2338 | 425.3255 | 95.97 | 111.442 | 97.567 | 17.875 | 4.655 | 4.616 | 9.271 | 9.271 | 0.37045 | 0.5021 | 14.1418 | 14.0136 | 7.6077 | 79.0218 | 0.17734 | 5.739 | 5.739 | 32.8937 | 538.65 | 960.96 | 1048.6794 | -9.1283 | 88.9344 | 793.6647 | 95.8555 | 97.567 | 58.042 | 17.875 | 1.2 | 3.047 | 4.247 | 4.247 | 0.14593 | 0.28255 | 10.6667 | 10.57 | 10.2358 | 49.6937 | 0.2127 | 5.739 | 6.265 | 105.7795 | 960.96 | 1411.1917 | 1297.7557 | 8.0383 | 64.4152 | 1129.3579 | 90.6337 | SDS-Cl2 dose | mg/L | 7.3 | 8 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 7 | 6.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.82 | 6.1 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 7.5 | 6.9 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 7.32 | 8.49 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 8 | 8.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4131618 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 5.7604 | [5 empty] | 1998-10-17 | 6:30 | 3287.5025 | 29.219 | 129.826 | 58.327 | 17.95 | 0 | 14.409 | 3.047 |  | 17.456 | 17.456 | 0.82545 | 0 | 13.0991 | 13.0146 | 8.8475 | 67.279 | 0.19344 | 8.503 | 5.74 | 34.169 | 295.056 | 297.1382 | 1411.1917 | 1540.6971 | -9.177 | 88.5006 | 918.9177 | 96.2816 | 129.826 | 111.712 | 17.95 | 8.539 | 9.332 | 17.871 | 17.871 | 0.36284 | 0.47781 | 12.9706 | 12.8869 | 4.0799 | 98.7391 | 0.13052 | 5.74 | 5.74 | 17.2185 | 297.1382 | 534.6 | 553.2714 | -3.4926 | 94.2052 | 425.2048 | 95.9505 | 111.712 | 97.815 | 17.95 | 4.67 | 4.662 | 9.332 | 9.332 | 0.37331 | 0.50043 | 14.1873 | 14.0958 | 7.5294 | 79.2841 | 0.17779 | 5.74 | 5.74 | 32.924 | 534.6 | 961.415 | 1037.1368 | -7.8761 | 88.9196 | 785.8684 | 95.8105 | 97.815 | 58.327 | 17.95 | 1.2 | 3.047 | 4.247 | 4.247 | 0.14593 | 0.28255 | 10.6667 | 10.5978 | 10.2418 | 49.8792 | 0.21247 | 5.74 | 6.292 | 105.7334 | 961.415 | 1411.1917 | 1298.4081 | 7.9921 | 64.4161 | 1129.9115 | 90.6423 | SDS-Free Cl2 residual | mg/L | 5.68 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 4.55 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 4.86 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 6.04 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 51 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 5 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 6.9 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-10-17 | 14:00 | 3295 | 29.41 | 129.337 | 57.66 | 17.925 | 0 | 14.356 | 3.046 |  | 17.402 | 17.402 | 0.82496 | 0 | 13.0509 | 12.8937 | 8.8016 | 66.7719 | 0.1931 | 8.734 | 5.757 | 33.135 | 284.448 | 295.3594 | 1373.5148 | 1531.2402 | -11.4833 | 88.7815 | 913.2998 | 96.3719 | 129.337 | 111.165 | 17.925 | 8.479 | 9.392 | 17.871 | 17.871 | 0.36364 | 0.47446 | 12.8795 | 12.7243 | 4.0372 | 98.2888 | 0.12946 | 5.757 | 5.757 | 17.199 | 295.3594 | 516.6 | 546.4796 | -5.7839 | 94.1769 | 420.9195 | 95.9139 | 111.165 | 97.117 | 17.925 | 4.67 | 4.722 | 9.392 | 9.392 | 0.37651 | 0.49723 | 14.1873 | 14.0164 | 7.2357 | 78.9803 | 0.17747 | 5.757 | 5.757 | 32.4438 | 516.6 | 921.375 | 995.4245 | -8.0369 | 89.0155 | 756.0123 | 95.7086 | 97.117 | 57.66 | 17.925 | 1.207 | 3.046 | 4.253 | 4.253 | 0.14603 | 0.2838 | 10.7289 | 10.5996 | 9.7861 | 49.6774 | 0.21337 | 5.757 | 6.403 | 104.5958 | 921.375 | 1373.5148 | 1245.0298 | 9.3545 | 64.5869 | 1083.2024 | 90.3438 | SDS-Cl2 demand | mg/L | 1.62 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.71 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.45 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.38 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.96 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.46 | NR | --- | 15.42 | --- | 53.0364 | 10.18 | 77.2102 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.32 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.32 | NR | --- | 27.9863 | --- | 77.5385 | 17.2432 | 91.5329 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.56 |  |  |  |  | SDS-Cl2 demand | mg/L | 1.1 | #VALUE! | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.32
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-10-17 | 22:00 | 3303 | 29.342 | 129.397 | 58.065 | 17.865 | 0 | 14.418 | 3.047 |  | 17.465 | 17.465 | 0.82554 | 0 | 13.1073 | 12.9754 | 8.8447 | 67.0213 | 0.1936 | 8.635 | 5.742 | 32.9235 | 286.656 | 295.6939 | 1368.6532 | 1539.0887 | -12.4528 | 88.8657 | 917.3913 | 96.4112 | 129.397 | 111.472 | 17.865 | 8.541 | 9.274 | 17.815 | 17.815 | 0.36132 | 0.47943 | 12.9737 | 12.8432 | 4.0711 | 98.4984 | 0.13039 | 5.742 | 5.742 | 16.9455 | 295.6939 | 518.85 | 552.4106 | -6.4683 | 94.2692 | 424.0522 | 96.0039 | 111.472 | 97.44 | 17.865 | 4.67 | 4.604 | 9.274 | 9.274 | 0.37021 | 0.50356 | 14.1873 | 14.0446 | 7.3272 | 79.2638 | 0.17719 | 5.742 | 5.742 | 32.694 | 518.85 | 925.47 | 1011.9752 | -9.3472 | 88.9433 | 765.4126 | 95.7286 | 97.44 | 58.065 | 17.865 | 1.207 | 3.047 | 4.254 | 4.254 | 0.14607 | 0.28373 | 10.7289 | 10.621 | 9.8349 | 50.0526 | 0.2122 | 5.742 | 6.306 | 104.567 | 925.47 | 1368.6532 | 1250.6521 | 8.6217 | 64.6367 | 1088.0611 | 90.3896 | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.34 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.18 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.08 |  |  |  |  | SDS-Chlorination temp. | oC | NR | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.43 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.33 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.43
State Approved Plant Capacity (MGD) | 18 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -8.4583 | [5 empty] | 1998-10-18 | 6:00 | 3311.0003 | 29.321 | 130 | 57.982 | 18.01 | 0 | 14.365 | 3.047 |  | 17.412 | 17.412 | 0.82501 | 0 | 13.0591 | 12.9358 | 8.8223 | 67.1587 | 0.19262 | 8.479 | 5.734 | 32.9 | 285.744 | 295.6858 | 1368.0457 | 1534.5822 | -12.1733 | 88.8733 | 915.134 | 96.4049 | 130 | 111.772 | 18.01 | 8.475 | 9.271 | 17.746 | 17.746 | 0.36036 | 0.47757 | 12.8734 | 12.7518 | 4.0626 | 98.8134 | 0.12905 | 5.734 | 5.734 | 16.8675 | 295.6858 | 518.85 | 550.5649 | -6.1125 | 94.2955 | 423.1253 | 96.0136 | 111.772 | 97.755 | 18.01 | 4.67 | 4.601 | 9.271 | 9.271 | 0.37005 | 0.50372 | 14.1873 | 14.0534 | 7.3302 | 79.4233 | 0.17694 | 5.734 | 5.734 | 32.5993 | 518.85 | 925.47 | 1012.3929 | -9.3923 | 88.975 | 765.6214 | 95.7421 | 97.755 | 57.982 | 18.01 | 1.22 | 3.047 | 4.267 | 4.267 | 0.14633 | 0.28592 | 10.8444 | 10.742 | 9.8525 | 50.006 | 0.21481 | 5.734 | 6.308 | 104.5642 | 925.47 | 1368.0457 | 1254.1556 | 8.325 | 64.6367 | 1089.8128 | 90.4053 | SDS-Chlorination pH | --- | 8.81 | 8.77 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 9.1 | 9.05 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.78 | 8.86 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.78 | 8.62 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.75 | 8.62 | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NA | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -6.6979 | [5 empty] | 1998-10-18 | 14:00 | 3319.0003 | 29.384 | 129.739 | 57.862 | 18.019 | 0 | 14.198 | 3.046 |  | 17.244 | 17.244 | 0.82336 | 0 | 12.9073 | 12.7616 | 8.7403 | 67.0412 | 0.19035 | 8.413 | 5.746 | 33.041 | 285.12 | 295.4654 | 1371.0843 | 1518.6769 | -10.7647 | 88.8173 | 907.0712 | 96.3574 | 129.739 | 111.57 | 18.019 | 8.478 | 9.394 | 17.872 | 17.872 | 0.36368 | 0.47437 | 12.878 | 12.7326 | 4.04 | 98.5955 | 0.12914 | 5.746 | 5.746 | 17.082 | 295.4654 | 516.15 | 546.704 | -5.9196 | 94.2186 | 421.0847 | 95.9433 | 111.57 | 97.545 | 18.019 | 4.52 | 4.874 | 9.394 | 9.394 | 0.38062 | 0.48116 | 13.7316 | 13.5767 | 7.0797 | 79.4588 | 0.17086 | 5.746 | 5.746 | 32.4585 | 516.15 | 922.9675 | 964.7108 | -4.5227 | 89.0144 | 740.4304 | 95.6163 | 97.545 | 57.862 | 18.019 | 1.2 | 3.046 | 4.246 | 4.246 | 0.14589 | 0.28262 | 10.6667 | 10.5463 | 9.7965 | 49.888 | 0.2114 | 5.746 | 6.362 | 104.5354 | 922.9675 | 1371.0843 | 1245.3964 | 9.167 | 64.6201 | 1084.182 | 90.3581 | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | NR | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -1.7604 | [5 empty] | 1998-10-18 | 22:00 | 3327 | 29.265 | 130.04 | 58.395 | 17.97 | 0 | 14.237 | 2.986 |  | 17.223 | 17.223 | 0.82663 | 0 | 12.9427 | 12.8417 | 8.9032 | 67.3443 | 0.19069 | 8.419 | 5.74 | 33.7695 | 293.472 | 296.869 | 1391.1377 | 1551.3053 | -11.5134 | 88.6248 | 924.0871 | 96.3456 | 130.04 | 112.057 | 17.97 | 8.477 | 9.274 | 17.751 | 17.751 | 0.36046 | 0.47755 | 12.8765 | 12.776 | 4.0732 | 99.0053 | 0.12904 | 5.74 | 5.74 | 17.316 | 296.869 | 531.45 | 552.3974 | -3.9415 | 94.1671 | 424.6332 | 95.9221 | 112.057 | 98.115 | 17.97 | 4.5 | 4.774 | 9.274 | 9.274 | 0.37475 | 0.48523 | 13.6709 | 13.5642 | 7.3413 | 79.7747 | 0.17003 | 5.74 | 5.74 | 32.487 | 531.45 | 949.585 | 1001.7754 | -5.4961 | 89.0568 | 766.6127 | 95.7623 | 98.115 | 58.395 | 17.97 | 1.26 | 2.986 | 4.246 | 4.246 | 0.14469 | 0.29675 | 11.2 | 11.1126 | 10.2244 | 50.0606 | 0.22198 | 5.74 | 6.314 | 105.2813 | 949.585 | 1391.1377 | 1305.8552 | 6.1304 | 64.5361 | 1127.7201 | 90.6642 | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-10-19 | 6:00 | 3335.0003 | 29.427 | 129.223 | 57.922 | 17.833 | 0 | 14.118 | 3.046 |  | 17.164 | 17.164 | 0.82254 | 0 | 12.8345 | 12.6736 | 8.725 | 67.0145 | 0.18912 | 8.375 | 5.74 | 31.6545 | 280.608 | 294.6576 | 1346.7762 | 1513.6588 | -12.3913 | 89.2572 | 904.1582 | 96.499 | 129.223 | 111.022 | 17.833 | 8.478 | 9.208 | 17.686 | 17.686 | 0.35872 | 0.47936 | 12.878 | 12.7165 | 4.0624 | 98.2271 | 0.12946 | 5.74 | 5.74 | 16.4775 | 294.6576 | 506.7 | 550.7839 | -8.7002 | 94.4079 | 422.7207 | 96.102 | 111.022 | 97.102 | 17.833 | 4.5 | 4.708 | 9.208 | 9.208 | 0.37123 | 0.48871 | 13.6709 | 13.4994 | 7.0116 | 79.2174 | 0.17041 | 5.74 | 5.74 | 32.2727 | 506.7 | 905.2225 | 960.1671 | -6.0697 | 89.0474 | 733.4335 | 95.5998 | 97.102 | 57.922 | 17.833 | 1.14 | 3.046 | 4.186 | 4.186 | 0.14469 | 0.27234 | 10.1333 | 10.0062 | 9.5158 | 50.1632 | 0.19947 | 5.74 | 6.355 | 103.6454 | 905.2225 | 1346.7762 | 1205.2218 | 10.5106 | 64.8251 | 1055.2221 | 90.1779 | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-10-13 | 1998-10-13 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-10-29 | 1998-10-29 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 26.126 | NR | --- | 262.4 | --- | 65.8084 | 167.32 | 85.2379 | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 24.7 | NR | --- | 270.1997 | --- | 63.9641 | 171.3498 | 84.7528 | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 25.31 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-10-19 | 14:00 | 3343 | 29.197 | 129.926 | 58.717 | 17.856 | 0 | 14.298 | 3.047 |  | 17.345 | 17.345 | 0.82433 | 0 | 12.9982 | 12.9227 | 8.8035 | 67.662 | 0.19099 | 8.403 | 5.743 | 33.8165 | 293.472 | 296.9016 | 1390.5302 | 1531.4243 | -10.1324 | 88.6102 | 914.163 | 96.3008 | 129.926 | 111.862 | 17.856 | 8.478 | 9.453 | 17.931 | 17.931 | 0.36525 | 0.47281 | 12.878 | 12.8032 | 4.0496 | 98.9884 | 0.12934 | 5.743 | 5.743 | 17.316 | 296.9016 | 535.5 | 547.6502 | -2.2689 | 94.1678 | 422.2759 | 95.8994 | 111.862 | 97.972 | 17.856 | 4.5 | 4.953 | 9.453 | 9.453 | 0.3843 | 0.47604 | 13.6709 | 13.5915 | 7.3147 | 79.7463 | 0.17043 | 5.743 | 5.743 | 32.5192 | 535.5 | 953.9075 | 992.4783 | -4.0435 | 89.0471 | 763.9891 | 95.7435 | 97.972 | 58.717 | 17.856 | 1.32 | 3.047 | 4.367 | 4.367 | 0.14833 | 0.30227 | 11.7333 | 11.6652 | 10.325 | 50.1635 | 0.23254 | 5.743 | 6.333 | 105.2352 | 953.9075 | 1390.5302 | 1321.5634 | 4.9598 | 64.5555 | 1137.7354 | 90.7505 | SDS-BDCM | mg/L | 8.12 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10.38 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10.38 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10.96 | NR | --- | 192.46 | --- | 78.2954 | 119.52 | 91.5412 | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10.11 | NR | --- | 200.9074 | --- | 76.7056 | 123.9787 | 91.1598 | Sampling time | hh:mm | 10:15 | 10:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | 10.76 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-10-19 | 15:09 | 3344.1444 | 29.227 | 129.926 | 58.417 | 17.883 | 0 | 14.239 | 3.046 |  | 17.285 | 17.285 | 0.82378 | 0 | 12.9445 | 12.858 | 8.7794 | 67.5091 | 0.19046 | 8.458 | 5.745 | 33.793 | 293.472 | 296.8608 | 1390.5302 | 1526.6121 | -9.7863 | 88.6166 | 911.7364 | 96.2936 | 129.926 | 111.862 | 17.883 | 8.479 | 9.266 | 17.745 | 17.745 | 0.36028 | 0.47782 | 12.8795 | 12.7934 | 4.075 | 98.936 | 0.12931 | 5.745 | 5.745 | 17.277 | 296.8608 | 531 | 552.6984 | -4.0863 | 94.1801 | 424.7796 | 95.9327 | 111.862 | 97.957 | 17.883 | 4.44 | 4.826 | 9.266 | 9.266 | 0.37592 | 0.47917 | 13.4886 | 13.3984 | 7.2764 | 79.7501 | 0.168 | 5.745 | 5.745 | 32.6168 | 531 | 953.68 | 989.5208 | -3.7582 | 89.0128 | 760.2604 | 95.7098 | 97.957 | 58.417 | 17.883 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.6549 | 10.3229 | 49.9811 | 0.23319 | 5.745 | 6.344 | 105.2294 | 953.68 | 1390.5302 | 1321.3605 | 4.9743 | 64.5526 | 1137.5202 | 90.7492 | SDS-DBCM | mg/L | 2.93 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3409 | 3409 | --- | --- | --- | --- | SDS-DBCM | mg/L | 4.46 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3793 | 3793 | --- | --- | --- | --- | SDS-DBCM | mg/L | 4.46 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4081 | 4081 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.75 | NR | --- | 22.76 | --- | 41.1628 | 15.68 | 67.7296 | Operation time | hh.hh | 4418 | 4418 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.06 | NR | --- | 20.2711 | --- | 32.4245 | 14.39 | 60.0418 | Operation time | hh.hh | 4729 | 4729 | --- | --- | --- | --- | SDS-DBCM | mg/L | 5.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4418 | 4418 | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-10-19 | 23:00 | 3352 | 29.206 | 129.779 | 58.357 | 17.857 | 0 | 14.18 | 3.046 |  | 17.226 | 17.226 | 0.82317 | 0 | 12.8909 | 12.8127 | 8.7594 | 67.4516 | 0.18995 | 8.381 | 5.727 | 33.793 | 294.336 | 297.024 | 1390.5302 | 1522.4395 | -9.4863 | 88.6228 | 909.7317 | 96.2854 | 129.779 | 111.832 | 17.857 | 8.48 | 9.331 | 17.811 | 17.811 | 0.36202 | 0.47611 | 12.881 | 12.8028 | 4.0686 | 98.8799 | 0.12948 | 5.727 | 5.727 | 17.277 | 297.024 | 535.5 | 551.2577 | -2.9426 | 94.1833 | 424.1408 | 95.9266 | 111.832 | 97.695 | 17.857 | 4.44 | 4.891 | 9.331 | 9.331 | 0.37939 | 0.47583 | 13.4886 | 13.4067 | 7.3073 | 79.5992 | 0.16843 | 5.727 | 5.727 | 32.8955 | 535.5 | 953.68 | 991.7592 | -3.9929 | 88.925 | 763.6296 | 95.6922 | 97.695 | 58.357 | 17.857 | 1.26 | 3.046 | 4.306 | 4.306 | 0.14709 | 0.29261 | 11.2 | 11.132 | 10.2399 | 49.9291 | 0.22296 | 5.727 | 6.232 | 105.1805 | 953.68 | 1390.5302 | 1304.668 | 6.1748 | 64.5886 | 1129.174 | 90.6852 | SDS-CHBr3 | mg/L | 0.22 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.12 | 5.8 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.56 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.22 | 5.32 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.56 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.2 | 5.92 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.615 | NR | --- | 29.08 | --- | 92.2581 | 17.64 | 97.2789 | pH | --- | 4.86 | 5.41 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.48 | NR | --- | -1.3429 | --- | -153.0864 | -0.54995 | 211.8289 | pH | --- | 4.7 | 5.51 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.68 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 4.71 | 4.96 | --- | --- | --- | ---
|  | Standard testing pH | 7.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 7.3125 | [5 empty] | 1998-10-20 | 7:00 | 3360.0003 | 29.338 | 129.169 | 57.742 | 17.866 | 0 | 14.298 | 3.047 |  | 17.345 | 17.345 | 0.82433 | 0 | 12.9982 | 12.869 | 8.8177 | 66.7718 | 0.19273 | 8.111 | 5.724 | 31.3255 | 280.752 | 294.8371 | 1337.053 | 1531.3613 | -14.5326 | 89.3753 | 913.0992 | 96.5693 | 129.169 | 111.12 | 17.866 | 8.478 | 9.267 | 17.745 | 17.745 | 0.36029 | 0.47777 | 12.878 | 12.75 | 4.0552 | 98.2233 | 0.12981 | 5.724 | 5.724 | 16.5945 | 294.8371 | 507.15 | 549.3899 | -8.3289 | 94.3716 | 422.1135 | 96.0687 | 111.12 | 97.162 | 17.866 | 4.5 | 4.767 | 9.267 | 9.267 | 0.37438 | 0.48559 | 13.6709 | 13.535 | 6.9856 | 79.2894 | 0.1707 | 5.724 | 5.724 | 32.5846 | 507.15 | 905.6775 | 955.135 | -5.4608 | 88.9483 | 731.1425 | 95.5433 | 97.162 | 57.742 | 17.866 | 1.32 | 3.047 | 4.367 | 4.367 | 0.14833 | 0.30227 | 11.7333 | 11.6167 | 9.7593 | 49.8267 | 0.23314 | 5.724 | 6.117 | 103.5014 | 905.6775 | 1337.053 | 1253.1906 | 6.2722 | 64.8954 | 1079.434 | 90.4115 | SDS-THM4 | mg/L | 11.27 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 15.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 15.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 43.451 | NR | --- | 506.7 | --- | 69.8024 | 320.16 | 87.3969 | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 40.35 | NR | --- | 490.0352 | --- | 66.1338 | 309.1686 | 85.9459 | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 42.55 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 80 - 350 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 1.1875 | [5 empty] | 1998-10-20 | 15:00 | 3368 | 29.512 | 129.256 | 57.802 | 17.958 | 0 | 14.364 | 3.046 |  | 17.41 | 17.41 | 0.82504 | 0 | 13.0582 | 12.862 | 8.8228 | 66.7482 | 0.1927 | 8.365 | 5.741 | 31.8895 | 280.128 | 294.6413 | 1351.6378 | 1533.6979 | -13.4696 | 89.1768 | 914.1696 | 96.5116 | 129.256 | 111.165 | 17.958 | 8.544 | 9.262 | 17.806 | 17.806 | 0.36104 | 0.47984 | 12.9782 | 12.7833 | 4.0592 | 98.1933 | 0.13019 | 5.741 | 5.741 | 16.848 | 294.6413 | 508.95 | 550.8997 | -8.2424 | 94.2819 | 422.7705 | 96.0149 | 111.165 | 97.102 | 17.958 | 4.5 | 4.762 | 9.262 | 9.262 | 0.37411 | 0.48586 | 13.6709 | 13.4655 | 7.0206 | 79.1549 | 0.17012 | 5.741 | 5.741 | 32.1641 | 508.95 | 899.7625 | 959.5036 | -6.6397 | 89.0836 | 734.2268 | 95.6193 | 97.102 | 57.802 | 17.958 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.5571 | 9.6876 | 49.8064 | 0.23204 | 5.741 | 6.289 | 103.5245 | 899.7625 | 1351.6378 | 1244.8164 | 7.9031 | 64.8642 | 1072.2895 | 90.3455 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 66 | 114.8294 | 57.1429 | 90.4147 | 80.0917 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 38 | 61.0526 | 30.7692 | 49.5263 | 63.6557 | SDS-MCAA* | mg/L | 10.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 58 | 97.3013 | 30.7692 | 77.6507 | 76.8193 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 14 | 52 | 91.9416 | 0 | 71.9708 | 80.5477 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 76 | 129.5346 | 60 | 102.7673 | 80.5386 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 12 | 20 | 28.4088 | #VALUE! | 24.2044 | 50.4222
|  | Acceptable range of operating pH values | 4 - 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 6.125 | [5 empty] | 1998-10-20 | 23:00 | 3376.0003 | 29.244 | 129.953 | 58.582 | 17.802 | 0 | 14.362 | 3.046 |  | 17.408 | 17.408 | 0.82502 | 0 | 13.0564 | 12.9625 | 8.8412 | 67.6243 | 0.19168 | 8.37 | 5.717 | 33.887 | 293.664 | 297.2117 | 1392.3533 | 1538.7971 | -10.5177 | 88.5984 | 918.0044 | 96.3086 | 129.953 | 111.982 | 17.802 | 8.542 | 9.201 | 17.743 | 17.743 | 0.35938 | 0.48143 | 12.9752 | 12.8819 | 4.0965 | 99.069 | 0.13003 | 5.717 | 5.717 | 17.433 | 297.2117 | 535.95 | 556.9519 | -3.9186 | 94.1345 | 427.0818 | 95.9181 | 111.982 | 98.01 | 17.802 | 4.5 | 4.701 | 9.201 | 9.201 | 0.37085 | 0.48908 | 13.6709 | 13.5726 | 7.4407 | 79.7533 | 0.17018 | 5.717 | 5.717 | 32.7345 | 535.95 | 954.59 | 1017.6496 | -6.6059 | 88.9861 | 776.7998 | 95.786 | 98.01 | 58.582 | 17.802 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.649 | 10.3357 | 50.1583 | 0.23225 | 5.717 | 6.152 | 105.0854 | 954.59 | 1392.3533 | 1322.7272 | 5.0006 | 64.6429 | 1138.6586 | 90.7711 | SDS-DCAA* | mg/L | 6.13 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 34.7 | 522 | 1017.7199 | 88.8424 | 769.8599 | 95.4927 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 46.7 | 649 | 1343.23 | 86.7705 | 996.115 | 95.3118 | SDS-DCAA* | mg/L | 5.24 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 41.7 | 500 | 950.2948 | 85.8644 | 725.1474 | 94.2494 | SDS-DCAA* | mg/L | 6.12 | NR | --- | 184.52 | --- | 85.3589 | 113.16 | 94.5917 | Total dissolved solids | mg/L | 38.1 | 577 | 1143.435 | 88.5241 | 860.2175 | 95.5709 | SDS-DCAA* | mg/L | 6.12 | NR | --- | 193.9095 | --- | 85.3589 | 117.8547 | 94.8072 | Total dissolved solids | mg/L | 34.7 | 575 | 1091.5132 | 89.5166 | 833.2566 | 95.8356 | SDS-DCAA* | mg/L | 5.74 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32.8 | 584 | 1163.3635 | 90.1205 | 873.6818 | 96.2458
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-10-21 | 7:00 | 3384.0003 | 29.257 | 129.993 | 58.417 | 17.89 | 0 | 14.12 | 3.046 |  | 17.166 | 17.166 | 0.82256 | 0 | 12.8364 | 12.7392 | 8.7356 | 67.5794 | 0.18851 | 7.395 | 5.712 | 32.571 | 286.704 | 295.8653 | 1358.93 | 1516.389 | -11.587 | 88.9913 | 906.1271 | 96.4055 | 129.993 | 112.027 | 17.89 | 8.54 | 9.268 | 17.808 | 17.808 | 0.36114 | 0.47956 | 12.9722 | 12.874 | 4.0788 | 99.0412 | 0.12999 | 5.712 | 5.712 | 16.6335 | 295.8653 | 519.3 | 553.1634 | -6.521 | 94.378 | 424.5144 | 96.0818 | 112.027 | 98.04 | 17.89 | 4.5 | 4.768 | 9.268 | 9.268 | 0.37443 | 0.48554 | 13.6709 | 13.5674 | 7.1613 | 79.9822 | 0.16963 | 5.712 | 5.712 | 32.7658 | 519.3 | 930.02 | 978.4871 | -5.2114 | 88.9254 | 748.8935 | 95.6248 | 98.04 | 58.417 | 17.89 | 1.08 | 3.046 | 4.126 | 4.126 | 0.14349 | 0.26175 | 9.6 | 9.5273 | 9.722 | 50.6165 | 0.18823 | 5.712 | 5.967 | 104.2157 | 930.02 | 1358.93 | 1222.82 | 10.016 | 64.776 | 1076.42 | 90.3183 | SDS-TCAA* | mg/L | 2.19 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 16 | 580 | 1153.7451 | 94.2857 | 866.8726 | 98.1543 | SDS-TCAA* | mg/L | 3.55 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 18 | 580 | 1227.7789 | 94.1935 | 903.8895 | 98.0086 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 16 | 1060 | 2085.7642 | 94.8052 | 1572.8821 | 98.9828 | SDS-TCAA* | mg/L | 1.44 | NR | --- | 133.24 | --- | 92.2887 | 80.82 | 97.2903 | Total hardness | mg/L as CaCO3 | 14 | 580 | 1174.9197 | 95.3333 | 877.4599 | 98.4045 | SDS-TCAA* | mg/L | 2.19 | NR | --- | 143.3347 | --- | 94.9296 | 85.8674 | 98.323 | Total hardness | mg/L as CaCO3 | 18 | 500 | 960.7799 | 93.75 | 730.3899 | 97.5356 | SDS-TCAA* | mg/L | 1.17 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 14 | 540 | 1092.8759 | 95 | 816.438 | 98.2852
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-10-21 | 15:00 | 3392.0003 | 29.38 | 130.248 | 58.44 | 18.031 | 0 | 14.301 | 3.045 |  | 17.346 | 17.346 | 0.82446 | 0 | 13.0009 | 12.8557 | 8.8032 | 67.5098 | 0.19043 | 8.282 | 5.739 | 32.7355 | 285.216 | 295.6531 | 1374.1223 | 1530.4593 | -11.3772 | 88.9277 | 913.0562 | 96.4147 | 130.248 | 112.11 | 18.031 | 8.481 | 9.321 | 17.802 | 17.802 | 0.36177 | 0.47641 | 12.8825 | 12.7386 | 4.0513 | 99.0967 | 0.12855 | 5.739 | 5.739 | 17.199 | 295.6531 | 517.05 | 549.0132 | -6.1818 | 94.1827 | 422.3332 | 95.9276 | 112.11 | 98.13 | 18.031 | 4.5 | 4.821 | 9.321 | 9.321 | 0.37726 | 0.48278 | 13.6709 | 13.5182 | 7.1037 | 79.9853 | 0.16901 | 5.739 | 5.739 | 32.7216 | 517.05 | 923.65 | 969.13 | -4.9239 | 88.9324 | 743.09 | 95.5965 | 98.13 | 58.44 | 18.031 | 1.32 | 3.045 | 4.365 | 4.365 | 0.14825 | 0.30241 | 11.7333 | 11.6023 | 9.9696 | 50.2844 | 0.23073 | 5.739 | 6.243 | 104.2877 | 923.65 | 1374.1223 | 1278.8415 | 6.9339 | 64.7263 | 1101.2458 | 90.53 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 14 | 550 | 1095.2613 | 94.9275 | 822.6307 | 98.2981 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 560 | 1187.0316 | 94.4828 | 873.5158 | 98.1683 | SDS-MBAA* | mg/L | 7.65 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 14 | 950 | 1869.6507 | 95.2703 | 1409.8253 | 99.007 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 14 | 530 | 1072.365 | 95.1724 | 801.1825 | 98.2526 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 480 | 921.6604 | 92.9688 | 700.8302 | 97.4316 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 12 | 490 | 992.4234 | 95.5556 | 741.2117 | 98.381
|  | Maximum permissible turbidity (ntu) | less than 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-10-21 | 23:00 | 3400.0003 | 29.325 | 129.853 | 58.222 | 17.979 | 0 | 14.298 | 3.046 |  | 17.344 | 17.344 | 0.82438 | 0 | 12.9982 | 12.8739 | 8.8112 | 67.2473 | 0.19144 | 8.241 | 5.716 | 32.618 | 287.376 | 295.8734 | 1370.4763 | 1531.601 | -11.7568 | 88.9757 | 913.7372 | 96.4303 | 129.853 | 111.69 | 17.979 | 8.478 | 9.202 | 17.68 | 17.68 | 0.35856 | 0.47952 | 12.878 | 12.7549 | 4.0728 | 98.7197 | 0.1292 | 5.716 | 5.716 | 17.043 | 295.8734 | 520.65 | 552.7659 | -6.1684 | 94.2398 | 424.3197 | 95.9835 | 111.69 | 97.65 | 17.979 | 4.5 | 4.702 | 9.202 | 9.202 | 0.37091 | 0.48902 | 13.6709 | 13.5402 | 7.2135 | 79.4775 | 0.17036 | 5.716 | 5.716 | 32.7667 | 520.65 | 930.2475 | 987.5736 | -6.1625 | 88.9254 | 754.1118 | 95.6549 | 97.65 | 58.222 | 17.979 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.6212 | 10.0488 | 49.9082 | 0.23285 | 5.716 | 6.07 | 104.3251 | 930.2475 | 1370.4763 | 1288.1653 | 6.006 | 64.74 | 1109.2064 | 90.5946 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.16 | 8.65 | 17.2867 | 91.3043 | 12.9683 | 98.7662 | SDS-DBAA* | mg/L | 2.67 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.638 | 2.94 | 5.5934 | 13.1973 | 4.2667 | 85.0469 | SDS-DBAA* | mg/L | 0.87 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.315 | 52.6 | 103.9717 | 87.1429 | 78.2859 | 99.5976 | SDS-DBAA* | mg/L | 0.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.309 | 2.43 | 4.6594 | 85.4245 | 3.5447 | 91.2827 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.233 | 6.55 | 12.5889 | 67.9505 | 9.5694 | 97.5652 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.19 | 2.37 | 4.6614 | 80.2083 | 3.5157 | 94.5957
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 1.1875 | [5 empty] | 1998-10-22 | 0:00 | 3401 | 29.346 | 129.853 | 58.2 | 17.979 | 0 | 14.358 | 3.046 |  | 17.404 | 17.404 | 0.82498 | 0 | 13.0527 | 12.9199 | 8.8944 | 67.1531 | 0.19239 | 7.709 | 5.708 | 32.618 | 296.736 | 297.5789 | 1390.5302 | 1546.5311 | -11.2188 | 89.0389 | 922.055 | 96.4625 | 129.853 | 111.69 | 17.979 | 8.478 | 9.328 | 17.806 | 17.806 | 0.36192 | 0.47613 | 12.878 | 12.7469 | 4.0802 | 98.7123 | 0.12913 | 5.708 | 5.708 | 17.043 | 297.5789 | 520.65 | 552.5513 | -6.1272 | 94.2728 | 425.0651 | 95.9905 | 111.69 | 97.65 | 17.979 | 4.62 | 4.708 | 9.328 | 9.328 | 0.37443 | 0.49528 | 14.0354 | 13.8926 | 7.2727 | 79.4183 | 0.17493 | 5.708 | 5.708 | 32.7667 | 520.65 | 930.2475 | 999.414 | -7.4353 | 88.9889 | 760.032 | 95.6888 | 97.65 | 58.2 | 17.979 | 1.26 | 3.046 | 4.306 | 4.306 | 0.14709 | 0.29261 | 11.2 | 11.086 | 9.9675 | 49.9785 | 0.22182 | 5.708 | 5.967 | 104.3251 | 930.2475 | 1390.5302 | 1271.8963 | 8.5316 | 64.942 | 1101.0719 | 90.5251 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 8.71 | 25.8 | 43.1853 | #VALUE! | 34.4926 | 74.7482 | SDS-BCAA* | mg/L | 2.61 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 17.7 | 26.3 | 36.2126 | #VALUE! | 31.2563 | 43.3714 | SDS-BCAA* | mg/L | 1.83 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.81 | 28.5 | 55.7063 | 93.4146 | 42.1032 | 98.0762 | SDS-BCAA* | mg/L | 0.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.88 | 26.3 | 53.0188 | 94.094 | 39.6594 | 97.7811 | SDS-BCAA* | mg/L | BMRL | NR | --- | 11.0263 | --- | 80 | 6.7632 | 92.607 | Total organic carbon | mg/L | 9.58 | 25.6 | 40.9147 | 27.9699 | 33.2574 | 71.1943 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 8.82 | 28.5 | 49.1855 | 55.4545 | 38.8428 | 77.2931
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-10-22 | 8:27 | 3409.4581 | 29.278 | 129.41 | 63.375 | 18.003 | 0 | 14.116 | 2.806 |  | 16.922 | 16.922 | 0.83418 | 0 | 12.8327 | 12.7277 | 9.2208 | 69.1687 | 0.18401 | 8.389 | 5.689 | 35.438 | 296.016 | 297.7421 | 1433.6768 | 1617.3017 | -12.808 | 88.0978 | 957.5219 | 96.299 | 129.41 | 111.772 | 18.003 | 8.416 | 9.03 | 17.446 | 17.446 | 0.35314 | 0.4824 | 12.7838 | 12.6792 | 4.1065 | 98.4815 | 0.12875 | 5.689 | 5.689 | 17.628 | 297.7421 | 546.75 | 558.8096 | -2.2057 | 94.0794 | 428.2759 | 95.884 | 111.772 | 98.43 | 18.003 | 4.5 | 4.53 | 9.03 | 9.03 | 0.36173 | 0.49834 | 13.6709 | 13.559 | 7.6871 | 79.4109 | 0.17074 | 5.689 | 5.689 | 33.143 | 546.75 | 985.3025 | 1056.9556 | -7.2722 | 88.8686 | 801.8528 | 95.8667 | 98.43 | 63.375 | 18.003 | 1.2 | 2.806 | 4.006 | 4.006 | 0.13629 | 0.29955 | 10.6667 | 10.5794 | 10.669 | 52.2305 | 0.20255 | 5.689 | 6.269 | 106.3498 | 985.3025 | 1433.6768 | 1361.1911 | 5.0559 | 64.2812 | 1173.2468 | 90.9354 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.006 | 0.87 | 1.7489 | 98.6726 | 1.3095 | 99.5418 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.005 | 0.708 | 1.5183 | 98.8208 | 1.1132 | 99.5508 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.003 | 0.879 | 1.7397 | #VALUE! | 1.3093 | 99.7709 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.931 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.927 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.935 | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 24.6875 | [5 empty] | 1998-10-22 | 16:00 | 3417.0003 | 29.282 | 129.678 | 58.185 | 17.928 | 0 | 14.24 | 3.046 |  | 17.286 | 17.286 | 0.82379 | 0 | 12.9455 | 12.838 | 8.7807 | 67.2228 | 0.19098 | 8.233 | 5.735 | 34.216 | 295.152 | 297.3096 | 1409.9767 | 1527.2679 | -8.3187 | 88.4915 | 912.2887 | 96.2494 | 129.678 | 111.577 | 17.928 | 8.48 | 9.199 | 17.679 | 17.679 | 0.3585 | 0.47967 | 12.881 | 12.7741 | 4.0905 | 98.609 | 0.12954 | 5.735 | 5.735 | 17.316 | 297.3096 | 535.05 | 555.4187 | -3.8069 | 94.1758 | 426.3642 | 95.9387 | 111.577 | 97.687 | 17.928 | 4.5 | 4.699 | 9.199 | 9.199 | 0.37075 | 0.48918 | 13.6709 | 13.5574 | 7.4308 | 79.2732 | 0.17102 | 5.735 | 5.735 | 32.568 | 535.05 | 961.6425 | 1016.2522 | -5.6788 | 89.0458 | 775.6511 | 95.8012 | 97.687 | 58.185 | 17.928 | 1.26 | 3.046 | 4.306 | 4.306 | 0.14709 | 0.29261 | 11.2 | 11.107 | 10.3287 | 49.6793 | 0.22357 | 5.735 | 6.156 | 105.791 | 961.6425 | 1409.9767 | 1315.6717 | 6.6884 | 64.4172 | 1138.6571 | 90.7091 | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.068886 | 3.3721 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.028249 | 2.692 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.37037 | 3.0842 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.5399 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.6211 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 3.2807 | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1998-10-23 | 0:00 | 3425 | 29.274 | 130.147 | 58.372 | 17.968 | 0 | 14.417 | 3.047 |  | 17.464 | 17.464 | 0.82553 | 0 | 13.1064 | 13.0006 | 8.8561 | 67.4354 | 0.19279 | 8.217 | 5.729 | 34.1455 | 295.008 | 297.2688 | 1399.646 | 1542.247 | -10.1884 | 88.5136 | 919.7579 | 96.2876 | 130.147 | 112.08 | 17.968 | 8.477 | 9.268 | 17.745 | 17.745 | 0.3603 | 0.47771 | 12.8765 | 12.7726 | 4.0815 | 99.064 | 0.12893 | 5.729 | 5.729 | 17.199 | 297.2688 | 534.15 | 553.4354 | -3.6105 | 94.2143 | 425.3521 | 95.9565 | 112.08 | 98.145 | 17.968 | 4.62 | 4.648 | 9.268 | 9.268 | 0.37123 | 0.49849 | 14.0354 | 13.9222 | 7.5101 | 79.6344 | 0.17483 | 5.729 | 5.729 | 32.4705 | 534.15 | 960.96 | 1032.8074 | -7.4766 | 89.0771 | 783.4787 | 95.8556 | 98.145 | 58.372 | 17.968 | 1.32 | 3.047 | 4.367 | 4.367 | 0.14833 | 0.30227 | 11.7333 | 11.6387 | 10.406 | 49.8845 | 0.23331 | 5.729 | 6.19 | 105.6269 | 960.96 | 1399.646 | 1331.5014 | 4.8687 | 64.4676 | 1146.2307 | 90.7848 | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | 2.62 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-10-23 | 8:36 | 3433.5953 | 29.231 | 134.489 | 60.712 | 18.346 | 0 | 14.72 | 3.106 |  | 17.826 | 17.826 | 0.82576 | 0 | 13.3818 | 13.2908 | 8.8965 | 70.358 | 0.1889 | 8.135 | 5.734 | 33.2055 | 295.68 | 297.228 | 1375.9459 | 1548.4872 | -12.5398 | 88.8283 | 922.8576 | 96.4019 | 134.489 | 116.55 | 18.346 | 8.78 | 9.386 | 18.166 | 18.166 | 0.36749 | 0.48332 | 13.3367 | 13.246 | 4.1166 | 103.0569 | 0.12853 | 5.734 | 5.734 | 16.7505 | 297.228 | 537.3 | 559.5967 | -4.1498 | 94.3644 | 428.4123 | 96.0901 | 116.55 | 101.865 | 18.346 | 4.56 | 4.826 | 9.386 | 9.386 | 0.37912 | 0.48583 | 13.8532 | 13.7589 | 7.4293 | 83.4322 | 0.16491 | 5.734 | 5.734 | 32.7437 | 537.3 | 968.0125 | 1014.0461 | -4.7555 | 88.9836 | 775.673 | 95.7787 | 101.865 | 60.712 | 18.346 | 1.38 | 3.106 | 4.486 | 4.486 | 0.1519 | 0.30762 | 12.2667 | 12.1832 | 10.5435 | 52.399 | 0.23251 | 5.734 | 6.245 | 105.3101 | 968.0125 | 1375.9459 | 1351.3124 | 1.7903 | 64.5693 | 1159.6624 | 90.9189 | SDS-HAA5 | mg/L | 8.32 | 0 | --- | -37.9022 | --- | #DIV/0! | -18.9511 | 143.9024 | [8 empty] | SDS-HAA5 | mg/L | 6.22 | 0 | --- | -30.3682 | --- | #DIV/0! | -15.1841 | 140.9639 | [8 empty] | SDS-HAA5 | mg/L | 24.16 | 0 | --- | -85.6582 | --- | #DIV/0! | -42.8291 | 156.4103 | [8 empty] | SDS-HAA5 | mg/L | 8.31 | 87.55 | --- | 404.51 | --- | 90.5083 | 246.03 | 96.6224 | [8 empty] | SDS-HAA5 | mg/L | 8.46 | 87.55 | --- | 424.7232 | --- | 90.337 | 256.1366 | 96.6971 | [8 empty] | SDS-HAA5 | mg/L | 6.91 | 0 | --- | -27.64 | --- | #DIV/0! | -13.82 | 150
|  | Field 3-2b: Manufacturer Reported Membrane Characteristics1 |  | maximum system recycle flow rates. | [6 empty] | 1998-10-23 | 16:00 | 3441 | 29.253 | 134.308 | 60.435 | 18.427 | 0 | 14.903 | 3.106 |  | 18.009 | 18.009 | 0.82753 | 0 | 13.5482 | 13.4472 | 8.967 | 69.9775 | 0.19217 | 7.24 | 5.729 | 33.323 | 294.144 | 297.1301 | 1378.3765 | 1562.9114 | -13.3879 | 88.785 | 930.0208 | 96.417 | 134.308 | 115.927 | 18.427 | 8.843 | 9.326 | 18.169 | 18.169 | 0.36673 | 0.48671 | 13.4324 | 13.3323 | 4.1314 | 102.5591 | 0.13 | 5.729 | 5.729 | 16.8675 | 297.1301 | 534.15 | 562.8777 | -5.3782 | 94.3232 | 430.0039 | 96.0774 | 115.927 | 101.46 | 18.427 | 4.62 | 4.706 | 9.326 | 9.326 | 0.37432 | 0.49539 | 14.0354 | 13.9309 | 7.4771 | 82.7894 | 0.16827 | 5.729 | 5.729 | 32.6241 | 534.15 | 965.055 | 1026.5107 | -6.3681 | 89.0203 | 780.3304 | 95.8192 | 101.46 | 60.435 | 18.427 | 1.44 | 3.106 | 4.546 | 4.546 | 0.1531 | 0.31676 | 12.8 | 12.7046 | 10.5921 | 51.9284 | 0.24466 | 5.729 | 6.203 | 105.1718 | 965.055 | 1378.3765 | 1363.713 | 1.0638 | 64.6041 | 1164.384 | 90.9676 | SDS-HAA6 | mg/L | 8.32 | 0 | --- | -37.9022 | --- | #DIV/0! | -18.9511 | 143.9024 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.83 | 0 | --- | -43.1112 | --- | #DIV/0! | -21.5556 | 140.9639 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 25.99 | 0 | --- | -92.1464 | --- | #DIV/0! | -46.0732 | 156.4103 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.31 | 90.05 | --- | 417.01 | --- | 90.7718 | 253.53 | 96.7223 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.96 | 90.05 | --- | 435.7495 | --- | 90.05 | 262.8997 | 96.5919 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 6.91 | 0 | --- | -27.64 | --- | #DIV/0! | -13.82 | 150 | Stage 3 Operating Parameters During Sample Collection
|  | General Information | [8 empty] | 1998-10-24 | 0:00 | 3449 | 29.24 | 134.663 | 60.87 | 18.43 | 0 | 14.777 | 3.106 |  | 17.883 | 17.883 | 0.82632 | 0 | 13.4336 | 13.3387 | 8.9203 | 70.4162 | 0.18943 | 8.317 | 5.723 | 33.2525 | 295.536 | 297.2606 | 1377.1609 | 1553.2968 | -12.7898 | 88.8137 | 925.2787 | 96.4062 | 134.663 | 116.625 | 18.43 | 8.777 | 9.461 | 18.238 | 18.238 | 0.36945 | 0.48125 | 13.3322 | 13.2379 | 4.1051 | 103.1089 | 0.12839 | 5.723 | 5.723 | 16.8285 | 297.2606 | 537.75 | 557.4184 | -3.6575 | 94.3388 | 427.3395 | 96.062 | 116.625 | 101.895 | 18.43 | 4.62 | 4.841 | 9.461 | 9.461 | 0.38153 | 0.48832 | 14.0354 | 13.9362 | 7.4608 | 83.3692 | 0.16716 | 5.723 | 5.723 | 32.6793 | 537.75 | 968.695 | 1019.7633 | -5.2719 | 89.0065 | 778.7567 | 95.8037 | 101.895 | 60.87 | 18.43 | 1.38 | 3.106 | 4.486 | 4.486 | 0.1519 | 0.30762 | 12.2667 | 12.18 | 10.5543 | 52.3982 | 0.23245 | 5.723 | 6.138 | 105.1142 | 968.695 | 1377.1609 | 1352.3851 | 1.7991 | 64.639 | 1160.54 | 90.9426 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.28 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.26 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.26 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.26 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.31 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 26
|  | Membrane manufacturer | FLUID SYSTEMS CORP. | Summary of the Stage and System Flow Rates | [6 empty] | 1998-10-24 | 7:43 | 3456.7122 | 29.21 | 134.549 | 60.63 | 18.477 | 0 | 14.478 | 3.167 |  | 17.645 | 17.645 | 0.82052 | 0 | 13.1618 | 13.0804 | 8.6888 | 70.4237 | 0.18574 | 8.178 | 5.719 | 32.806 | 295.728 | 297.2443 | 1375.9459 | 1506.1291 | -9.4614 | 88.9633 | 901.6867 | 96.3617 | 134.549 | 116.197 | 18.477 | 8.778 | 9.46 | 18.238 | 18.238 | 0.36944 | 0.4813 | 13.3337 | 13.2512 | 4.106 | 102.79 | 0.12891 | 5.719 | 5.719 | 16.77 | 297.2443 | 537.75 | 557.4984 | -3.6724 | 94.3582 | 427.3714 | 96.076 | 116.197 | 101.692 | 18.477 | 4.38 | 5.08 | 9.46 | 9.46 | 0.38787 | 0.463 | 13.3063 | 13.224 | 7.2307 | 83.2368 | 0.15887 | 5.719 | 5.719 | 32.499 | 537.75 | 968.0125 | 973.3798 | -0.55447 | 89.0666 | 755.5649 | 95.6987 | 101.692 | 60.63 | 18.477 | 1.32 | 3.167 | 4.487 | 4.487 | 0.15314 | 0.29418 | 11.7333 | 11.6607 | 10.4285 | 52.2555 | 0.22315 | 5.719 | 6.137 | 105.0106 | 968.0125 | 1375.9459 | 1327.7102 | 3.5056 | 64.672 | 1147.8613 | 90.8516 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.21 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.02 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.38 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.22 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.36 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.2
|  | Membrane trade name | FLUID SYSTEMS | Influent flow rate to stage 1, QI-s(1) (gpm) | 24.6875 | [5 empty] | 1998-10-24 | 15:00 | 3464 | 29.287 | 127.608 | 57.03 | 17.593 | 0 | 14.062 | 3.046 |  | 17.108 | 17.108 | 0.82195 | 0 | 12.7836 | 12.6756 | 8.699 | 66.027 | 0.19198 | 8.3 | 5.719 | 34.2395 | 294.384 | 297.1872 | 1402.0765 | 1511.0974 | -7.7757 | 88.4788 | 904.1423 | 96.213 | 127.608 | 109.837 | 17.593 | 8.362 | 9.084 | 17.446 | 17.446 | 0.35386 | 0.47931 | 12.7018 | 12.5945 | 4.0857 | 97.0438 | 0.12978 | 5.719 | 5.719 | 17.394 | 297.1872 | 535.5 | 554.7423 | -3.5933 | 94.1471 | 425.9648 | 95.9166 | 109.837 | 96.082 | 17.593 | 4.38 | 4.704 | 9.084 | 9.084 | 0.36781 | 0.48217 | 13.3063 | 13.1939 | 7.3724 | 77.9941 | 0.16917 | 5.719 | 5.719 | 32.4558 | 535.5 | 954.135 | 1003.8958 | -5.2153 | 89.079 | 769.6979 | 95.7833 | 96.082 | 57.03 | 17.593 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.6342 | 10.3271 | 48.6359 | 0.23921 | 5.719 | 6.07 | 105.3418 | 954.135 | 1402.0765 | 1321.964 | 5.7138 | 64.5537 | 1138.0495 | 90.7437 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.38 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 3.95 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 5.36 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.55 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.77 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.55
|  | Membrane element model number | 2540 TFCS / 4921 TFCS | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.875 | [5 empty] | 1998-10-24 | 23:00 | 3472 | 29.24 | 127.635 | 57.3 | 17.611 | 0 | 14.241 | 2.986 |  | 17.227 | 17.227 | 0.82667 | 0 | 12.9464 | 12.8548 | 8.9256 | 65.9309 | 0.19497 | 8.204 | 5.7 | 33.699 | 294.96 | 297.4075 | 1388.7072 | 1555.1011 | -11.9819 | 88.6691 | 926.2543 | 96.3618 | 127.635 | 109.83 | 17.611 | 8.361 | 9.267 | 17.628 | 17.628 | 0.35873 | 0.4743 | 12.7003 | 12.6105 | 4.067 | 97.0545 | 0.12993 | 5.7 | 5.7 | 17.1405 | 297.4075 | 534.15 | 550.2739 | -3.0186 | 94.2367 | 423.8407 | 95.9559 | 109.83 | 96.157 | 17.611 | 4.56 | 4.707 | 9.267 | 9.267 | 0.37278 | 0.49207 | 13.8532 | 13.7552 | 7.4496 | 77.9329 | 0.1765 | 5.7 | 5.7 | 32.2883 | 534.15 | 956.6375 | 1020.3385 | -6.6588 | 89.1434 | 777.2442 | 95.8458 | 96.157 | 57.3 | 17.611 | 1.32 | 2.986 | 4.306 | 4.306 | 0.14589 | 0.30655 | 11.7333 | 11.6504 | 10.3948 | 48.7227 | 0.23912 | 5.7 | 5.939 | 105.3216 | 956.6375 | 1388.7072 | 1332.9727 | 4.0134 | 64.5868 | 1144.8051 | 90.8 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Molecular weight cutoff (Daltons) | 200 | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 14.8125 | [5 empty] | 1998-10-25 | 0:00 | 3473 | 29.227 | 127.635 | 57.495 | 17.611 | 0 | 14.241 | 3.047 |  | 17.288 | 17.288 | 0.82375 | 0 | 12.9464 | 12.8598 | 8.7997 | 66.1543 | 0.19439 | 8.272 | 5.705 | 33.699 | 295.008 | 297.4075 | 1388.7072 | 1529.9225 | -10.1688 | 88.6691 | 913.665 | 96.3117 | 127.635 | 109.83 | 17.611 | 8.361 | 9.213 | 17.574 | 17.574 | 0.35729 | 0.47576 | 12.7003 | 12.6153 | 4.0744 | 97.0471 | 0.12999 | 5.705 | 5.705 | 17.1405 | 297.4075 | 534.15 | 551.756 | -3.2961 | 94.2367 | 424.5818 | 95.963 | 109.83 | 96.157 | 17.611 | 4.56 | 4.653 | 9.213 | 9.213 | 0.36989 | 0.49495 | 13.8532 | 13.7605 | 7.4778 | 77.9047 | 0.17663 | 5.705 | 5.705 | 32.2883 | 534.15 | 956.6375 | 1025.9809 | -7.2487 | 89.1434 | 780.0655 | 95.8608 | 96.157 | 57.495 | 17.611 | 1.32 | 3.047 | 4.367 | 4.367 | 0.14833 | 0.30227 | 11.7333 | 11.6549 | 10.3572 | 48.8578 | 0.23855 | 5.705 | 5.939 | 105.3216 | 956.6375 | 1388.7072 | 1325.4386 | 4.5559 | 64.5868 | 1141.0381 | 90.7697 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Influent flow rate to stage 2, QI-s(2) (gpm) | 14.8125 | [5 empty] | 1998-10-25 | 15:00 | 3488.0003 | 29.282 | 133.752 | 58.477 | 18.217 | 0 | 14.657 | 3.046 |  | 17.703 | 17.703 | 0.82794 | 0 | 13.3245 | 13.2139 | 8.9443 | 68.9532 | 0.19164 | 8.495 | 5.725 | 34.31 | 292.752 | 296.9179 | 1393.5688 | 1560.5569 | -11.9828 | 88.4446 | 928.7374 | 96.3057 | 133.752 | 115.297 | 18.217 | 8.717 | 9.268 | 17.985 | 17.985 | 0.36351 | 0.48468 | 13.241 | 13.1311 | 4.1144 | 102.1931 | 0.12849 | 5.725 | 5.725 | 17.082 | 296.9179 | 535.5 | 560.1171 | -4.597 | 94.2469 | 428.5175 | 96.0137 | 115.297 | 100.237 | 18.217 | 4.62 | 4.648 | 9.268 | 9.268 | 0.37123 | 0.49849 | 14.0354 | 13.9189 | 7.532 | 82.018 | 0.16971 | 5.725 | 5.725 | 32.3582 | 535.5 | 966.42 | 1035.6108 | -7.1595 | 89.102 | 785.5554 | 95.8808 | 100.237 | 58.477 | 18.217 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.6359 | 10.4709 | 50.6691 | 0.22965 | 5.725 | 6.226 | 105.8054 | 966.42 | 1393.5688 | 1339.3718 | 3.8891 | 64.3654 | 1152.8959 | 90.8226 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-22 | CI-s3-22 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-24 | CI-s3-24 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-26 | CI-s3-26 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-30 | CI-s3-30 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-28 | CI-s3-28 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-30 (dup) | CI-s3-30 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.9375 | [5 empty] | 1998-10-25 | 23:00 | 3496 | 29.253 | 134.502 | 57.405 | 18.076 | 0 | 14.419 | 3.047 |  | 17.466 | 17.466 | 0.82555 | 0 | 13.1082 | 13.0105 | 8.8002 | 69.0773 | 0.18835 | 8.623 | 5.705 | 35.391 | 292.464 | 296.8282 | 1420.915 | 1533.9999 | -7.9586 | 88.0769 | 915.414 | 96.1339 | 134.502 | 115.657 | 18.076 | 8.779 | 8.972 | 17.751 | 17.751 | 0.35644 | 0.49456 | 13.3352 | 13.2358 | 4.1649 | 102.8386 | 0.1287 | 5.705 | 5.705 | 17.16 | 296.8282 | 537.75 | 570.4803 | -6.0865 | 94.2189 | 433.6542 | 96.0429 | 115.657 | 99.607 | 18.076 | 4.5 | 4.472 | 8.972 | 8.972 | 0.35864 | 0.50156 | 13.6709 | 13.569 | 7.5921 | 81.9639 | 0.16555 | 5.705 | 5.705 | 32.6637 | 537.75 | 972.79 | 1045.9988 | -7.5256 | 88.9958 | 791.8744 | 95.8751 | 99.607 | 57.405 | 18.076 | 1.14 | 3.047 | 4.187 | 4.187 | 0.14473 | 0.27227 | 10.1333 | 10.0578 | 10.277 | 50.153 | 0.20054 | 5.705 | 6.114 | 107.0467 | 972.79 | 1420.915 | 1296.6979 | 8.742 | 63.9365 | 1134.7439 | 90.5664 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 649.0385 | 324.5192 |  |  |  | Sampling date | MM/DD/YY | 1998-10-13 | 1998-10-13 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 868.1672 | 434.0836 |  |  |  | Sampling date | MM/DD/YY | 1998-10-29 | 1998-10-29 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 223.5099 | 111.755 |  |  |  | Sampling date | MM/DD/YY | 1998-11-10 | 1998-11-10 | --- | --- | --- | --- | Qp/QT (THM4), % | 66.0663 | 104.6639 |  | Qp/QT (HAA5), % | 42.3397 | 76.4134 |  |  |  | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | --- | --- | --- | --- | Qp/QT (THM4), % | 66.354 | 108.7813 |  | Qp/QT (HAA5), % | 42.42 | 76.5584 |  |  |  | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 781.4761 | 390.7381 |  |  |  | Sampling date | MM/DD/YY | 1998-11-24 | 1998-11-24 | --- | --- | --- | ---
|  | Membrane hydrophobicity | HYDRPHILIC | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 9.875 | [5 empty] | 1998-10-26 | 7:00 | 3504.0003 | 29.223 | 136.117 | 56.377 | 17.827 | 0 | 14.238 | 2.987 |  | 17.225 | 17.225 | 0.82659 | 0 | 12.9436 | 12.8586 | 8.819 | 69.601 | 0.18475 | 7.759 | 5.707 | 36.143 | 291.504 | 296.8037 | 1440.9689 | 1539.2833 | -6.8228 | 87.8226 | 918.0435 | 96.063 | 136.117 | 116.257 | 17.827 | 8.718 | 8.968 | 17.686 | 17.686 | 0.35552 | 0.49293 | 13.2425 | 13.1555 | 4.1461 | 104.2139 | 0.12624 | 5.707 | 5.707 | 17.8035 | 296.8037 | 541.35 | 568.0262 | -4.9277 | 94.0016 | 432.4149 | 95.8828 | 116.257 | 99.06 | 17.827 | 4.44 | 4.528 | 8.968 | 8.968 | 0.36002 | 0.49509 | 13.4886 | 13.4 | 7.5831 | 82.2484 | 0.16292 | 5.707 | 5.707 | 32.5156 | 541.35 | 984.165 | 1040.2954 | -5.7034 | 89.0448 | 790.8227 | 95.8884 | 99.06 | 56.377 | 17.827 | 1.08 | 2.987 | 4.067 | 4.067 | 0.14113 | 0.26555 | 9.6 | 9.5369 | 10.3413 | 49.5502 | 0.19247 | 5.707 | 6.088 | 108.3658 | 984.165 | 1440.9689 | 1300.8249 | 9.7257 | 63.4891 | 1142.495 | 90.515 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 94.1297 | 62.3492 |  |  |  | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | 72 | NA |  | SDS-THM4b, mg/L | 92.3082 | 63.3415 |  |  |  | Sampling time | hh:mm | 10:15 | 10:15 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Influent flow rate to stage 3, QI-s(3) (gpm) | 9.875 | [5 empty] | 1998-10-29 | 8:52 | 3506 | 28.921 | 141.752 | 59.61 | 19.182 | 0 | 14.662 | 2.926 |  | 17.588 | 17.588 | 0.83364 | 0 | 13.3291 | 13.3603 | 8.8698 | 72.6292 | 0.18395 | 10.938 | 5.75 | 46.7885 | 312 | 299.8147 | 1673.716 | 1567.713 | 6.3334 | 84.3942 | 933.7639 | 94.9893 | 141.752 | 121.86 | 19.182 | 9.262 | 8.183 | 17.445 | 17.445 | 0.34183 | 0.53093 | 14.0689 | 14.1018 | 4.3575 | 108.2665 | 0.13025 | 5.75 | 5.75 | 21.5475 | 299.8147 | 583.65 | 614.7739 | -5.3326 | 92.8131 | 457.2943 | 95.288 | 121.86 | 103.312 | 19.182 | 4.38 | 3.803 | 8.183 | 8.183 | 0.31974 | 0.53526 | 13.3063 | 13.3374 | 8.6744 | 84.7296 | 0.15741 | 5.75 | 5.75 | 33.1927 | 583.65 | 1054.69 | 1217.624 | -15.4485 | 88.9289 | 900.637 | 96.3145 | 103.312 | 59.61 | 19.182 | 1.02 | 2.926 | 3.946 | 3.946 | 0.13749 | 0.25849 | 9.0667 | 9.0879 | 11.0275 | 51.2515 | 0.17732 | 5.75 | 6.326 | 115.6205 | 1054.69 | 1673.716 | 1382.0485 | 17.4263 | 61.436 | 1218.3692 | 90.5102 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 3409 | 3409 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 3793 | 3793 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 4081 | 4081 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 35.1991 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 4418 | 4418 | --- | --- | --- | --- | SDS-HAA5b, mg/L | 35.0707 | NA |  | SDS-HAA5b, mg/L | 54 | 27 |  |  |  | Operation time | hh.hh | 4729 | 4729 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 4418 | 4418 | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 4.9375 | [5 empty] | 1998-10-29 | 16:00 | 3513.0003 | 28.9 | 138.924 | 59.745 | 18.154 | 0 | 14.355 | 2.927 |  | 17.282 | 17.282 | 0.83063 | 0 | 13.05 | 13.0886 | 8.9157 | 72.2648 | 0.18112 | 9.343 | 5.716 | 42.0885 | 313.008 | 300.3533 | 1584.9923 | 1566.9713 | 1.137 | 85.987 | 933.6623 | 95.4921 | 138.924 | 119.407 | 18.154 | 8.895 | 8.55 | 17.445 | 17.445 | 0.34673 | 0.50989 | 13.5114 | 13.5514 | 4.2612 | 106.7503 | 0.12694 | 5.716 | 5.716 | 20.046 | 300.3533 | 579.15 | 591.9712 | -2.2138 | 93.3259 | 446.1622 | 95.507 | 119.407 | 101.437 | 18.154 | 4.44 | 4.11 | 8.55 | 8.55 | 0.33772 | 0.5193 | 13.4886 | 13.5285 | 8.4066 | 83.8614 | 0.16132 | 5.716 | 5.716 | 33.3206 | 579.15 | 1049.4575 | 1168.8052 | -11.3723 | 88.9062 | 873.9776 | 96.1875 | 101.437 | 59.745 | 18.154 | 1.02 | 2.927 | 3.947 | 3.947 | 0.13753 | 0.25842 | 9.0667 | 9.0935 | 11.004 | 51.433 | 0.1768 | 5.716 | 6.194 | 112.343 | 1049.4575 | 1584.9923 | 1376.0228 | 13.1843 | 62.5964 | 1212.7402 | 90.7364 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.41 | 6.04 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.44 | 5.63 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.25 | 5.5 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | NA |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 5.05 | 5.11 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | NA |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  |  |  | pH | --- | 4.98 | 5.6 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 4.93 | 5.19 | --- | --- | --- | ---
|  | Design Parameters |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 4.9375 | [5 empty] | 1998-10-30 | 0:00 | 3521 | 28.866 | 139.447 | 60.097 | 18.355 | 0 | 14.478 | 2.927 |  | 17.405 | 17.405 | 0.83183 | 0 | 13.1618 | 13.2141 | 9.0106 | 72.4064 | 0.1825 | 9.053 | 5.7 | 41.172 | 313.68 | 300.6062 | 1549.746 | 1583.8618 | -2.2014 | 86.3037 | 942.234 | 95.6304 | 139.447 | 120.187 | 18.355 | 9.018 | 8.493 | 17.511 | 17.511 | 0.34685 | 0.51499 | 13.6982 | 13.7526 | 4.3023 | 107.1597 | 0.12834 | 5.7 | 5.7 | 19.578 | 300.6062 | 581.85 | 599.0064 | -2.9486 | 93.4872 | 449.8063 | 95.6475 | 120.187 | 102.03 | 18.355 | 4.38 | 4.113 | 8.493 | 8.493 | 0.33628 | 0.51572 | 13.3063 | 13.3591 | 8.4055 | 84.348 | 0.15838 | 5.7 | 5.7 | 33.3491 | 581.85 | 1056.2825 | 1165.9575 | -10.3831 | 88.9061 | 873.9037 | 96.1839 | 102.03 | 60.097 | 18.355 | 1.08 | 2.927 | 4.007 | 4.007 | 0.13873 | 0.26953 | 9.6 | 9.6381 | 11.1882 | 51.5203 | 0.18707 | 5.7 | 5.963 | 111.721 | 1056.2825 | 1549.746 | 1404.8054 | 9.3525 | 62.8348 | 1230.5439 | 90.921 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | 3.2091 | NA |  | SDS-CDb, mg/L | 3.8307 | 2.938 |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | 3.1558 | NA |  | SDS-CDb, mg/L | 4.362 | 2.6415 |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-10-30 | 8:00 | 3529 | 28.959 | 135.387 | 36.255 | 17.502 | 0 | 12.882 | NR |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 11.7109 | 11.7251 | #VALUE! | #VALUE! | #VALUE! | 8.493 | 5.714 | 38.775 | 312.144 | 300.0514 | 1465.2765 | #VALUE! | #VALUE! | 87.0772 | #VALUE! | #VALUE! | 135.387 | 115.35 | 17.502 | 8.842 | 8.903 | 17.745 | 17.745 | 0.35544 | 0.49828 | 13.4309 | 13.4472 | 4.2013 | 103.6652 | 0.12972 | 5.714 | 5.714 | 19.3245 | 300.0514 | 558.45 | 578.8548 | -3.6538 | 93.5596 | 439.4531 | 95.6026 | 115.35 | 94.725 | 17.502 | 3.02 | 5.883 | 8.903 | 8.903 | 0.39444 | 0.33921 | 9.1747 | 9.1858 | 6.6129 | 80.9226 | 0.11351 | 5.714 | 5.714 | 32.2248 | 558.45 | 937.755 | 828.5843 | 11.6417 | 89.2602 | 693.5171 | 95.3534 | 94.725 | 36.255 | 17.502 | 1.02 | 3.983 | 5.003 | 5.003 | 0.17979 | 0.20388 | 9.0667 | 9.0777 | 9.3407 | 38.6473 | 0.23488 | 5.714 | 5.969 | 109.7107 | 937.755 | 1465.2765 | 1149.8075 | 21.5297 | 63.436 | 1043.7813 | 89.4891 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 22 | 122 | 160.1703 | 47.619 | 141.0852 | 84.4066 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 29 | 80 | 97.7543 | -11.5385 | 88.8771 | 67.3707 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 18 | 32 | 36.8543 | 30.7692 | 34.4271 | 47.7157 | TOCb, mg/L | 13.6447 | NA |  | TOCb, mg/L | 14.0955 | 13.4481 |  |  |  | Alkalinity | mg/L as CaCO3 | 12 | 26 | 31.1291 | 14.2857 | 28.5646 | 57.9899 | TOCb, mg/L | 12.7028 | NA |  | TOCb, mg/L | 12.9182 | 12.611 |  |  |  | Alkalinity | mg/L as CaCO3 | 26 | 130 | 171.478 | 48 | 150.739 | 82.7516 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 14 | 28 | 33.0149 | #VALUE! | 30.5075 | 54.1096
|  | Active membrane area of membrane element used, A (ft2) | 27 | System concentrate waste flow rate, QW-sys (gpm) | 4.9375 | [5 empty] | 1998-10-30 | 16:00 | 3537 | 28.934 | 138.04 | 57.112 | 18.229 | 0 | 14.477 | 3.166 |  | 17.643 | 17.643 | 0.82055 | 0 | 13.1609 | 13.1866 | 8.569 | 70.778 | 0.18631 | 8.944 | 5.714 | 39.621 | 312.192 | 300.3696 | 1510.2461 | 1492.6809 | 1.1631 | 86.8093 | 896.5252 | 95.5806 | 138.04 | 118.837 | 18.229 | 8.957 | 8.794 | 17.751 | 17.751 | 0.35406 | 0.50459 | 13.6056 | 13.6321 | 4.2455 | 105.964 | 0.12865 | 5.714 | 5.714 | 19.071 | 300.3696 | 575.55 | 586.8822 | -1.9689 | 93.6508 | 443.6259 | 95.7011 | 118.837 | 100.687 | 18.229 | 4.38 | 4.414 | 8.794 | 8.794 | 0.35234 | 0.49807 | 13.3063 | 13.3323 | 8.116 | 83.417 | 0.15983 | 5.714 | 5.714 | 33.0924 | 575.55 | 1021.7025 | 1113.8292 | -9.017 | 88.9828 | 844.6896 | 96.0823 | 100.687 | 57.112 | 18.229 | 1.14 | 3.166 | 4.306 | 4.306 | 0.14949 | 0.26475 | 10.1333 | 10.1531 | 10.7571 | 49.9134 | 0.20341 | 5.714 | 6.119 | 110.111 | 1021.7025 | 1510.2461 | 1349.9445 | 10.6143 | 63.3415 | 1185.8235 | 90.7144 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 105 | 980 | 1313.9905 | 66.2379 | 1146.9953 | 90.8456 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 124 | 890 | 1156.6621 | 64.8725 | 1023.3311 | 87.8827 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 107 | 1099 | 1442.9598 | 63.7288 | 1270.9799 | 91.5813 | UV254 b, cm-1 | #VALUE! | NA |  | UV254 b, cm-1 | #VALUE! | #VALUE! |  |  |  | Total dissolved solids | mg/L | 97.2 | 956 | 1270.6354 | 70.7229 | 1113.3177 | 91.2693 | UV254 b, cm-1 | 0.48704 | NA |  | UV254 b, cm-1 | 0.48991 | 0.48581 |  |  |  | Total dissolved solids | mg/L | 104 | 980 | 1329.3724 | 68.5801 | 1154.6862 | 90.9932 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 97.2 | 971 | 1284.003 | 70.7229 | 1127.5015 | 91.3792
|  | Design flux, FW (gfd) | 17.9 | System permeate flow rate, Qp-sys (gpm) | 19.75 | [5 empty] | 1998-10-31 | 0:00 | 3545 | 28.879 | 137.665 | 57.24 | 18.114 | 0 | 14.477 | 3.106 |  | 17.583 | 17.583 | 0.82335 | 0 | 13.1609 | 13.2081 | 8.7182 | 70.6203 | 0.18703 | 9.014 | 5.694 | 38.681 | 313.632 | 300.4512 | 1484.723 | 1520.5565 | -2.4135 | 87.1257 | 910.5039 | 95.7517 | 137.665 | 118.537 | 18.114 | 8.957 | 8.621 | 17.578 | 17.578 | 0.34945 | 0.50956 | 13.6056 | 13.6543 | 4.2791 | 105.7079 | 0.12917 | 5.694 | 5.694 | 18.837 | 300.4512 | 569.7 | 593.0412 | -4.0971 | 93.7304 | 446.7462 | 95.7835 | 118.537 | 100.702 | 18.114 | 4.38 | 4.241 | 8.621 | 8.621 | 0.34311 | 0.50806 | 13.3063 | 13.354 | 8.1366 | 83.3689 | 0.16018 | 5.694 | 5.694 | 33.12 | 569.7 | 1028.3 | 1123.8666 | -9.2936 | 88.9766 | 846.7833 | 96.0887 | 100.702 | 57.24 | 18.114 | 1.14 | 3.106 | 4.246 | 4.246 | 0.14709 | 0.26849 | 10.1333 | 10.1696 | 10.8738 | 49.9832 | 0.20346 | 5.694 | 5.912 | 109.5322 | 1028.3 | 1484.723 | 1365.5168 | 8.0289 | 63.5441 | 1196.9084 | 90.8487 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 54 | 1120 | 1526.8959 | 80.7143 | 1323.4479 | 95.9197 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 76 | 140 | 162.2799 | 75.4839 | 151.1399 | 49.7155 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 50 | 550 | 723.3668 | 83.7662 | 636.6834 | 92.1468 | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 44 | 1000 | 1350.2462 | 85.3333 | 1175.1231 | 96.2557 | Bromideb, mg/L | #VALUE! | NA |  | Bromideb, mg/L | #VALUE! | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 52 | 1070 | 1476.0059 | 81.9444 | 1273.0029 | 95.9152 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 44 | 980 | 1315.2836 | 84.2857 | 1147.6418 | 96.1661
|  | Net driving pressure at the design flux, NDP (psi) | 109 | System feed flow rate, QF-sys (gpm) | 24.6875 | [5 empty] | 1998-10-31 | 8:00 | 3553 | 28.93 | 137.517 | 57.757 | 18.238 | 0 | 14.358 | 3.166 |  | 17.524 | 17.524 | 0.81933 | 0 | 13.0527 | 13.0798 | 8.5604 | 70.8386 | 0.18464 | 8.905 | 5.713 | 37.9055 | 312.048 | 299.8882 | 1474.3922 | 1487.9952 | -0.92262 | 87.3601 | 893.9417 | 95.7597 | 137.517 | 118.425 | 18.238 | 8.898 | 8.613 | 17.511 | 17.511 | 0.34845 | 0.50814 | 13.5159 | 13.5439 | 4.2661 | 105.4669 | 0.12842 | 5.713 | 5.713 | 18.5835 | 299.8882 | 570.15 | 590.5011 | -3.5694 | 93.8032 | 445.1946 | 95.8258 | 118.425 | 100.905 | 18.238 | 4.38 | 4.233 | 8.613 | 8.613 | 0.34268 | 0.50853 | 13.3063 | 13.3339 | 8.1491 | 83.2779 | 0.16011 | 5.713 | 5.713 | 33.0906 | 570.15 | 1017.1525 | 1125.86 | -10.6874 | 88.9657 | 848.005 | 96.0978 | 100.905 | 57.757 | 18.238 | 1.08 | 3.166 | 4.246 | 4.246 | 0.14829 | 0.25436 | 9.6 | 9.6199 | 10.6317 | 50.4613 | 0.19064 | 5.713 | 6.081 | 108.8928 | 1017.1525 | 1474.3922 | 1326.9821 | 9.998 | 63.6889 | 1172.0673 | 90.7093 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 52 | 1080 | 1472.3912 | 81.1594 | 1276.1956 | 95.9254 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 69 | 128 | 148.5392 | 76.2069 | 138.2696 | 50.0975 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 46 | 520 | 684.3518 | 84.4595 | 602.1759 | 92.361 | Alkb, mg/L CaCO3 | 14 | NA |  | Alkb, mg/L CaCO3 | 14 | 14 |  |  |  | Calcium hardness | mg/L as CaCO3 | 42 | 870 | 1173.3514 | 85.5172 | 1021.6757 | 95.8891 | Alkb, mg/L CaCO3 | 30.0938 | NA |  | Alkb, mg/L CaCO3 | 37.274 | 27.0325 |  |  |  | Calcium hardness | mg/L as CaCO3 | 50 | 1020 | 1406.8622 | 80.4688 | 1213.4311 | 95.8795 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 42 | 820 | 1098.6866 | 84.4444 | 959.3433 | 95.622
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | [7 empty] | 1998-10-31 | 16:00 | 3561.0003 | 28.921 | 137.196 | 57.742 | 18.202 | 0 | 14.538 | 3.106 |  | 17.644 | 17.644 | 0.82396 | 0 | 13.2164 | 13.2473 | 8.7691 | 70.4979 | 0.18791 | 8.897 | 5.716 | 37.5765 | 312.24 | 300.1003 | 1467.7076 | 1528.8741 | -4.1675 | 87.4787 | 914.4872 | 95.891 | 137.196 | 118.335 | 18.202 | 8.958 | 8.667 | 17.625 | 17.625 | 0.35069 | 0.50826 | 13.6071 | 13.6389 | 4.2674 | 105.2961 | 0.12953 | 5.716 | 5.716 | 18.759 | 300.1003 | 572.85 | 590.8879 | -3.1488 | 93.7491 | 445.4941 | 95.7892 | 118.335 | 101.152 | 18.202 | 4.44 | 4.227 | 8.667 | 8.667 | 0.34396 | 0.51229 | 13.4886 | 13.5201 | 8.2323 | 83.3092 | 0.16229 | 5.716 | 5.716 | 33.0933 | 572.85 | 1013.9675 | 1139.8052 | -12.4104 | 88.9726 | 856.3276 | 96.1354 | 101.152 | 57.742 | 18.202 | 1.14 | 3.106 | 4.246 | 4.246 | 0.14709 | 0.26849 | 10.1333 | 10.157 | 10.7165 | 50.5285 | 0.20102 | 5.716 | 6.147 | 108.4867 | 1013.9675 | 1467.7076 | 1346.3075 | 8.2714 | 63.8498 | 1180.1375 | 90.8073 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.23 | 75.1 | 103.6781 | 87.5 | 89.3891 | 99.7427 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.22 | 1.12 | 1.4333 | 70.068 | 1.2767 | 82.7675 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.335 | 4.96 | 6.5636 | 86.3265 | 5.7618 | 94.1859 | T-Hdb, mg/L CaCO3 | 111.0505 | NA |  | T-Hdb, mg/L CaCO3 | 178.9084 | 81.4576 |  |  |  | Turbidity | ntu | 0.402 | 13.9 | 18.8452 | 81.0377 | 16.3726 | 97.5447 | T-Hdb, mg/L CaCO3 | 108.8443 | NA |  | T-Hdb, mg/L CaCO3 | 173.4659 | 81.2925 |  |  |  | Turbidity | ntu | 0.339 | 8.54 | 11.8108 | 53.37 | 10.1754 | 96.6684 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.401 | 16.3 | 21.9952 | 58.2292 | 19.1476 | 97.9057
|  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Calculate the Required System Influent Pressure | [6 empty] | 1998-11-01 | 0:00 | 3569.0003 | 28.879 | 137.102 | 58.41 | 18.21 | 0 | 14.355 | 3.167 |  | 17.522 | 17.522 | 0.81926 | 0 | 13.05 | 13.0968 | 8.6169 | 70.9291 | 0.18465 | 8.811 | 5.702 | 36.66 | 312.96 | 300.4675 | 1453.1227 | 1496.2228 | -2.966 | 87.799 | 898.3452 | 95.9192 | 137.102 | 118.492 | 18.21 | 8.895 | 8.733 | 17.628 | 17.628 | 0.35161 | 0.50459 | 13.5114 | 13.5598 | 4.26 | 105.327 | 0.12874 | 5.702 | 5.702 | 18.213 | 300.4675 | 570.15 | 587.958 | -3.1234 | 93.9384 | 444.2127 | 95.8999 | 118.492 | 101.7 | 18.21 | 4.44 | 4.293 | 8.733 | 8.733 | 0.34749 | 0.50842 | 13.4886 | 13.5369 | 8.1476 | 83.7384 | 0.16166 | 5.702 | 5.702 | 33.1044 | 570.15 | 1020.565 | 1125.585 | -10.2904 | 88.9824 | 847.8675 | 96.0956 | 101.7 | 58.41 | 18.21 | 1.02 | 3.167 | 4.187 | 4.187 | 0.14713 | 0.24361 | 9.0667 | 9.0992 | 10.5956 | 51.2494 | 0.17755 | 5.702 | 6.002 | 107.9654 | 1020.565 | 1453.1227 | 1314.4872 | 9.5405 | 64.0675 | 1167.5261 | 90.7526 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 3.17 | 50.6 | 68.7042 | #VALUE! | 59.6521 | 94.6859 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 13.2 | 71.5 | 91.7956 | #VALUE! | 81.6478 | 83.833 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 1.02 | 52 | 69.6765 | 91.7073 | 60.8382 | 98.3234 | Ca-Hdb, mg/L CaCO3 | 107.6571 | NA |  | Ca-Hdb, mg/L CaCO3 | 173.1424 | 79.0989 |  |  |  | Total organic carbon | mg/L | 5.09 | 54.3 | 72.3289 | 65.8389 | 63.3144 | 91.9608 | Ca-Hdb, mg/L CaCO3 | 98.0776 | NA |  | Ca-Hdb, mg/L CaCO3 | 155.0403 | 73.7911 |  |  |  | Total organic carbon | mg/L | 4.02 | 48.7 | 66.5196 | 69.7744 | 57.6098 | 93.022 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 3.1 | 42.5 | 56.6134 | 84.3434 | 49.5567 | 93.7445
|  | Maximum flow rate to the element, QI, max (gpm) | 8 | Osmotic pressure for stage 13, Dp1 (psi) | 2.8 | [5 empty] | 1998-11-01 | 8:00 | 3577.0003 | 28.951 | 137.216 | 58.807 | 18.295 | 0 | 14.658 | 3.166 |  | 17.824 | 17.824 | 0.82237 | 0 | 13.3255 | 13.3448 | 8.7341 | 70.9824 | 0.188 | 8.824 | 5.726 | 36.2605 | 312.048 | 299.7413 | 1433.0687 | 1519.609 | -6.0388 | 87.9027 | 909.6752 | 96.0139 | 137.216 | 118.702 | 18.295 | 8.958 | 8.727 | 17.685 | 17.685 | 0.35229 | 0.50653 | 13.6071 | 13.6268 | 4.2596 | 105.4044 | 0.12928 | 5.726 | 5.726 | 18.252 | 299.7413 | 566.55 | 588.6815 | -3.9064 | 93.9107 | 444.2114 | 95.8911 | 118.702 | 102.21 | 18.295 | 4.5 | 4.227 | 8.727 | 8.727 | 0.34557 | 0.51564 | 13.6709 | 13.6907 | 8.1739 | 83.9871 | 0.16301 | 5.726 | 5.726 | 33.1062 | 566.55 | 1009.19 | 1134.4462 | -12.4116 | 88.9551 | 850.4981 | 96.1074 | 102.21 | 58.807 | 18.295 | 1.2 | 3.166 | 4.366 | 4.366 | 0.15069 | 0.27485 | 10.6667 | 10.6821 | 10.7279 | 51.4856 | 0.20748 | 5.726 | 6.156 | 107.3174 | 1009.19 | 1433.0687 | 1351.0242 | 5.7251 | 64.1966 | 1180.1071 | 90.9061 | Notes: | [9 empty] | UV254 | cm-1 | 0.014 | 1.87 | 2.5784 | 96.9027 | 2.2242 | 99.3706 | Notes: | [9 empty] | UV254 | cm-1 | 0.041 | 1.75 | 2.3449 | 90.3302 | 2.0475 | 97.9975 | Notes: | [9 empty] | UV254 | cm-1 | 0.018 | 1.47 | 1.9735 | #VALUE! | 1.7217 | 98.9545 | Notes: | [9 empty] | UV254 | cm-1 | 0.03 | 1.43 | 1.9429 | 93.9394 | 1.6865 | 98.2211 | Notes: | [9 empty] | UV254 | cm-1 | 0.023 | 1.82 | 2.5367 | 95.3535 | 2.1783 | 98.9442 | Notes: | [9 empty] | UV254 | cm-1 | 0.019 | 1.75 | 2.3701 | 96.0744 | 2.06 | 99.0777
|  | Minimum flow rate to the element, QI, min (gpm) | 2 | Osmotic pressure for stage 23, Dp2 (psi) | 5 | [5 empty] | 1998-11-01 | 16:00 | 3585.0003 | 28.921 | 137.115 | 59.085 | 18.358 | 0 | 14 | 3.167 |  | 17.167 | 17.167 | 0.81552 | 0 | 12.7273 | 12.757 | 8.4766 | 71.2654 | 0.17901 | 8.771 | 5.735 | 35.908 | 311.376 | 299.9534 | 1434.2843 | 1467.1894 | -2.2942 | 88.0288 | 883.5714 | 95.936 | 137.115 | 118.395 | 18.358 | 8.896 | 8.73 | 17.626 | 17.626 | 0.35154 | 0.50471 | 13.5129 | 13.5445 | 4.2552 | 105.1418 | 0.12882 | 5.735 | 5.735 | 18.057 | 299.9534 | 567.45 | 587.2101 | -3.4823 | 93.9801 | 443.5818 | 95.9293 | 118.395 | 102.18 | 18.358 | 4.5 | 4.23 | 8.73 | 8.73 | 0.34573 | 0.51546 | 13.6709 | 13.7028 | 8.1859 | 83.7436 | 0.16363 | 5.735 | 5.735 | 33.0924 | 567.45 | 1010.1 | 1135.9155 | -12.4558 | 88.9675 | 851.6828 | 96.1145 | 102.18 | 59.085 | 18.358 | 1.2 | 3.167 | 4.367 | 4.367 | 0.15073 | 0.27479 | 10.6667 | 10.6916 | 10.7442 | 51.5303 | 0.20748 | 5.735 | 6.208 | 106.8106 | 1010.1 | 1434.2843 | 1352.3631 | 5.7116 | 64.391 | 1181.2316 | 90.9577 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.44164 | 3.6957 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.31061 | 2.4476 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 1.7647 | 2.8269 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.58939 | 2.6335 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.57214 | 3.7372 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.6129 | 4.1176 | --- | --- | --- | ---
|  | Total width of all membrane envelopes in the element, w (ft) | 19.2 | Osmotic pressure for stage 33, Dp3 (psi) | 9 | [5 empty] | 1998-11-02 | 0:00 | 3593.0003 | 28.862 | 136.941 | 59.325 | 18.376 | 0 | 15.195 | 3.166 |  | 18.361 | 18.361 | 0.82757 | 0 | 13.8136 | 13.8701 | 9.0082 | 70.7488 | 0.19605 | 8.731 | 5.715 | 35.344 | 312.768 | 300.3125 | 1409.9767 | 1572.0105 | -11.4919 | 88.2309 | 936.1615 | 96.2246 | 136.941 | 118.485 | 18.376 | 8.895 | 8.794 | 17.689 | 17.689 | 0.35323 | 0.50285 | 13.5114 | 13.5666 | 4.2536 | 105.0834 | 0.1291 | 5.715 | 5.715 | 17.823 | 300.3125 | 565.65 | 586.0464 | -3.6058 | 94.0652 | 443.1794 | 95.9784 | 118.485 | 102.682 | 18.376 | 4.5 | 4.294 | 8.794 | 8.794 | 0.34914 | 0.51171 | 13.6709 | 13.7268 | 8.1159 | 84.0916 | 0.16324 | 5.715 | 5.715 | 33.1044 | 565.65 | 1012.375 | 1123.7439 | -11.0008 | 88.9767 | 844.697 | 96.0809 | 102.682 | 59.325 | 18.376 | 1.8 | 3.166 | 4.966 | 4.966 | 0.1627 | 0.36246 | 16 | 16.0654 | 11.636 | 50.9915 | 0.31506 | 5.715 | 6.101 | 106.3382 | 1012.375 | 1409.9767 | 1527.4938 | -8.3347 | 64.5908 | 1269.9344 | 91.6265 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Feed spacer thickness, T (ft) | 0.0029 | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1998-11-02 | 5:04 | 3598.0725 | 28.836 | 136.606 | 59.632 | 18.268 | 0 | 14.535 | 3.227 |  | 17.762 | 17.762 | 0.81832 | 0 | 13.2136 | 13.2778 | 8.6368 | 71.2142 | 0.18645 | 8.714 | 5.715 | 34.827 | 313.44 | 300.4022 | 1407.5456 | 1496.6018 | -6.3271 | 88.4065 | 898.502 | 96.1239 | 136.606 | 118.162 | 18.268 | 8.895 | 8.92 | 17.815 | 17.815 | 0.3566 | 0.4993 | 13.5114 | 13.577 | 4.2371 | 104.8789 | 0.12945 | 5.715 | 5.715 | 17.667 | 300.4022 | 564.75 | 582.3451 | -3.1155 | 94.1189 | 441.3737 | 95.9973 | 118.162 | 102.547 | 18.268 | 4.5 | 4.42 | 8.92 | 8.92 | 0.35586 | 0.50448 | 13.6709 | 13.7373 | 8.0226 | 84.0639 | 0.16342 | 5.715 | 5.715 | 33.1145 | 564.75 | 1015.3325 | 1106.0079 | -8.9306 | 88.9766 | 835.3789 | 96.036 | 102.547 | 59.632 | 18.268 | 1.14 | 3.227 | 4.367 | 4.367 | 0.15194 | 0.26105 | 10.1333 | 10.1826 | 10.6987 | 52.1228 | 0.19536 | 5.715 | 6.109 | 106.0675 | 1015.3325 | 1407.5456 | 1336.5479 | 5.0441 | 64.6915 | 1175.9402 | 90.9802 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses in a single element, DPe (psi) | 6.7 | [5 empty] | 1998-11-02 | 13:00 | 3606 | 28.951 | 136.519 | 59.655 | 18.439 | 0 | 14.608 | 3.226 |  | 17.834 | 17.834 | 0.81911 | 0 | 13.28 | 13.2992 | 8.6526 | 70.9954 | 0.18733 | 8.663 | 5.736 | 34.78 | 310.704 | 299.8637 | 1405.1151 | 1500.2178 | -6.7683 | 88.4014 | 900.0407 | 96.1357 | 136.519 | 117.772 | 18.439 | 8.848 | 9.024 | 17.872 | 17.872 | 0.35874 | 0.49508 | 13.44 | 13.4595 | 4.2031 | 104.5034 | 0.12879 | 5.736 | 5.736 | 17.823 | 299.8637 | 560.7 | 576.4036 | -2.8007 | 94.0563 | 438.1336 | 95.9321 | 117.772 | 102.547 | 18.439 | 4.5 | 4.524 | 9.024 | 9.024 | 0.36141 | 0.49867 | 13.6709 | 13.6907 | 7.9004 | 83.8201 | 0.16333 | 5.736 | 5.736 | 33.0768 | 560.7 | 999.18 | 1085.5242 | -8.6415 | 88.9694 | 823.1121 | 95.9815 | 102.547 | 59.655 | 18.439 | 1.26 | 3.226 | 4.486 | 4.486 | 0.1543 | 0.28087 | 11.2 | 11.2162 | 10.6808 | 51.9812 | 0.21577 | 5.736 | 6.238 | 105.6038 | 999.18 | 1405.1151 | 1348.1899 | 4.0513 | 64.7827 | 1173.685 | 91.0024 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Design permeate pressure, Pp (psi) | 15 | [5 empty] | 1998-11-02 | 21:00 | 3614 | 28.904 | 136.09 | 59.662 | 18.454 | 0 | 14.778 | 3.227 |  | 18.005 | 18.005 | 0.82077 | 0 | 13.4345 | 13.4727 | 8.7385 | 70.6835 | 0.19061 | 8.687 | 5.709 | 34.5685 | 312.048 | 300.1982 | 1400.861 | 1516.6458 | -8.2653 | 88.4848 | 908.422 | 96.1947 | 136.09 | 117.57 | 18.454 | 8.898 | 8.853 | 17.751 | 17.751 | 0.35485 | 0.50127 | 13.5159 | 13.5544 | 4.2463 | 104.1297 | 0.13017 | 5.709 | 5.709 | 17.589 | 300.1982 | 562.95 | 584.244 | -3.7826 | 94.1409 | 442.2211 | 96.0226 | 117.57 | 102.532 | 18.454 | 4.5 | 4.353 | 8.853 | 8.853 | 0.35229 | 0.5083 | 13.6709 | 13.7097 | 8.0369 | 83.5601 | 0.16407 | 5.709 | 5.709 | 33.1237 | 562.95 | 1004.8675 | 1110.6685 | -10.5288 | 88.9661 | 836.8092 | 96.0417 | 102.532 | 59.662 | 18.454 | 1.38 | 3.227 | 4.607 | 4.607 | 0.15674 | 0.29954 | 12.2667 | 12.3015 | 10.9164 | 51.7266 | 0.23782 | 5.709 | 6.04 | 105.5261 | 1004.8675 | 1400.861 | 1389.4635 | 0.81361 | 64.8479 | 1197.1655 | 91.1853 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 45.2 | [5 empty] | 1998-11-03 | 5:00 | 3622 | 29.253 | 134.067 | 58.552 | 18.369 | 0 | 14.594 | 3.167 |  | 17.761 | 17.761 | 0.82169 | 0 | 13.2673 | 13.1684 | 8.7569 | 69.1836 | 0.19034 | 8.83 | 5.708 | 29.8685 | 281.184 | 294.9024 | 1290.2609 | 1516.2174 | -17.5125 | 89.8717 | 905.5599 | 96.7017 | 134.067 | 115.597 | 18.369 | 8.894 | 8.858 | 17.752 | 17.752 | 0.35493 | 0.50101 | 13.5099 | 13.4092 | 4.1894 | 102.2736 | 0.13111 | 5.708 | 5.708 | 15.99 | 294.9024 | 503.55 | 574.9483 | -14.179 | 94.5779 | 434.9254 | 96.3235 | 115.597 | 100.59 | 18.369 | 4.5 | 4.358 | 8.858 | 8.858 | 0.35255 | 0.50802 | 13.6709 | 13.569 | 7.1425 | 82.582 | 0.16431 | 5.708 | 5.708 | 32.4972 | 503.55 | 895.895 | 989.9515 | -10.4986 | 88.9804 | 746.7508 | 95.6482 | 100.59 | 58.552 | 18.369 | 1.2 | 3.167 | 4.367 | 4.367 | 0.15073 | 0.27479 | 10.6667 | 10.5872 | 9.4423 | 51.7597 | 0.20455 | 5.708 | 6.084 | 102.0586 | 895.895 | 1290.2609 | 1196.6856 | 7.2524 | 65.3924 | 1046.2903 | 90.2457 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Additional Information |  | Net driving pressure required for permeation, NDP (psi) | 118.8462 | [5 empty] | 1998-11-03 | 13:00 | 3630 | 28.959 | 136.184 | 59.925 | 18.345 | 0 | 14.421 | 3.226 |  | 17.647 | 17.647 | 0.81719 | 0 | 13.11 | 13.1259 | 8.5964 | 71.1131 | 0.18458 | 8.72 | 5.731 | 35.6025 | 319.344 | 301.3243 | 1426.9921 | 1489.1651 | -4.3569 | 88.1847 | 895.2447 | 96.0232 | 136.184 | 117.247 | 18.345 | 8.901 | 8.967 | 17.868 | 17.868 | 0.35793 | 0.49815 | 13.5205 | 13.5369 | 4.236 | 104.1345 | 0.12999 | 5.731 | 5.731 | 18.2325 | 301.3243 | 580.95 | 582.3325 | -0.23797 | 93.9492 | 441.8284 | 95.8734 | 117.247 | 102.21 | 18.345 | 4.5 | 4.467 | 8.967 | 8.967 | 0.35837 | 0.50184 | 13.6709 | 13.6875 | 8.2356 | 83.1479 | 0.16462 | 5.731 | 5.731 | 33.2598 | 580.95 | 1030.8025 | 1132.6862 | -9.8839 | 88.9621 | 856.8181 | 96.1182 | 102.21 | 59.925 | 18.345 | 1.02 | 3.226 | 4.246 | 4.246 | 0.14949 | 0.24023 | 9.0667 | 9.0777 | 10.7087 | 52.0138 | 0.17452 | 5.731 | 6.214 | 106.1136 | 1030.8025 | 1426.9921 | 1323.1716 | 7.2755 | 64.7843 | 1176.987 | 90.9843 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 1 | Flow weighted system pressure losses, Lsys (psi) | 61.4 | [5 empty] | 1998-11-03 | 21:00 | 3638 | 28.87 | 136.412 | 60.082 | 18.333 | 0 | 14.238 | 3.227 |  | 17.465 | 17.465 | 0.81523 | 0 | 12.9436 | 12.9935 | 8.5298 | 71.3842 | 0.18202 | 8.716 | 5.722 | 35.485 | 320.688 | 301.5365 | 1413.0148 | 1475.3949 | -4.4147 | 88.2319 | 888.4657 | 96.006 | 136.412 | 117.742 | 18.333 | 8.898 | 8.79 | 17.688 | 17.688 | 0.35317 | 0.50305 | 13.5159 | 13.568 | 4.2702 | 104.4738 | 0.12987 | 5.722 | 5.722 | 18.018 | 301.5365 | 579.15 | 588.5385 | -1.6211 | 94.0246 | 445.0375 | 95.9514 | 117.742 | 103.012 | 18.333 | 4.38 | 4.41 | 8.79 | 8.79 | 0.35213 | 0.49829 | 13.3063 | 13.3576 | 8.1696 | 83.8744 | 0.15926 | 5.722 | 5.722 | 33.2718 | 579.15 | 1033.76 | 1121.3147 | -8.4695 | 88.9659 | 850.2324 | 96.0867 | 103.012 | 60.082 | 18.333 | 0.96 | 3.227 | 4.187 | 4.187 | 0.14833 | 0.22928 | 8.5333 | 8.5662 | 10.6565 | 52.5575 | 0.16299 | 5.722 | 6.156 | 106.0963 | 1033.76 | 1413.0148 | 1309.7306 | 7.3095 | 64.8148 | 1171.7453 | 90.9454 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Required influent pressure to the system, PI (psi) | 195.2462 | [5 empty] | 1998-11-04 | 5:00 | 3646 | 28.832 | 136.177 | 42.69 | 18.016 | 0 | 14.236 | 3.983 |  | 18.219 | 18.219 | 0.78138 | 0 | 12.9418 | 13.0062 | 7.4511 | 63.9664 | 0.20333 | 8.616 | 5.732 | 34.1455 | 320.544 | 301.4875 | 1367.4377 | 1257.0188 | 8.0749 | 88.6743 | 779.2531 | 95.6182 | 136.177 | 116.76 | 18.016 | 8.896 | 9.338 | 18.234 | 18.234 | 0.36776 | 0.48788 | 13.5129 | 13.5802 | 4.1922 | 104.2603 | 0.13025 | 5.732 | 5.732 | 17.5305 | 301.4875 | 562.5 | 572.0039 | -1.6896 | 94.1853 | 436.7457 | 95.9861 | 116.76 | 99.892 | 18.016 | 4.38 | 4.958 | 9.338 | 9.338 | 0.38137 | 0.46905 | 13.3063 | 13.3726 | 7.6422 | 82.6678 | 0.16176 | 5.732 | 5.732 | 32.419 | 562.5 | 952.77 | 1030.7846 | -8.1882 | 89.247 | 796.6423 | 95.9305 | 99.892 | 42.69 | 18.016 | 0.96 | 3.983 | 4.943 | 4.943 | 0.17858 | 0.19421 | 8.5333 | 8.5758 | 9.493 | 43.782 | 0.19588 | 5.732 | 6.153 | 105.5722 | 952.77 | 1367.4377 | 1156.9653 | 15.3917 | 64.9829 | 1054.8677 | 89.9919 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Maximum element recovery (%) | NA | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-11-04 | 12:40 | 3653.6703 | 28.615 | 131.26 | 55.282 | 17.119 | 0 | 14.054 | 3.346 |  | 17.4 | 17.4 | 0.8077 | 0 | 12.7764 | 12.9226 | 8.3993 | 67.7527 | 0.19073 | 8.518 | 5.676 | 31.49 | 322.752 | 302.4259 | 1284.7912 | 1440.4216 | -12.1133 | 89.5875 | 871.4237 | 96.3864 | 131.26 | 114.09 | 17.119 | 8.654 | 8.077 | 16.731 | 16.731 | 0.33089 | 0.51724 | 13.1453 | 13.2958 | 4.3623 | 101.1937 | 0.13139 | 5.676 | 5.676 | 18.369 | 302.4259 | 572.4 | 606.7751 | -6.0054 | 93.9261 | 454.6005 | 95.9593 | 114.09 | 96.54 | 17.119 | 4.38 | 3.697 | 8.077 | 8.077 | 0.31409 | 0.54228 | 13.3063 | 13.4586 | 8.6056 | 79.5904 | 0.1691 | 5.676 | 5.676 | 31.9764 | 572.4 | 1006.6875 | 1212.6638 | -20.4608 | 89.4267 | 892.5319 | 96.4173 | 96.54 | 55.282 | 17.119 | 1.02 | 3.346 | 4.366 | 4.366 | 0.1543 | 0.23362 | 9.0667 | 9.1704 | 10.4567 | 48.3353 | 0.18973 | 5.676 | 6.477 | 99.3197 | 1006.6875 | 1284.7912 | 1283.291 | 0.11677 | 67.159 | 1144.9892 | 91.3257 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Variability of design flux (%) | 15 | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-11-04 | 20:00 | 3661 | 29.087 | 129.598 | 56.707 | 18.018 | 0 | 14.716 | 3.166 |  | 17.882 | 17.882 | 0.82295 | 0 | 13.3782 | 13.3438 | 8.8866 | 66.2479 | 0.20142 | 8.084 | 5.654 | 30.3855 | 294.144 | 297.7258 | 1292.0839 | 1540.3598 | -19.2151 | 89.7941 | 919.0428 | 96.6938 | 129.598 | 112.17 | 18.018 | 8.896 | 8.132 | 17.028 | 17.028 | 0.33559 | 0.52243 | 13.5129 | 13.4782 | 4.3551 | 98.5109 | 0.13682 | 5.654 | 5.654 | 16.2045 | 297.7258 | 522.45 | 605.6959 | -15.9338 | 94.5572 | 451.7108 | 96.4126 | 112.17 | 98.167 | 18.018 | 4.62 | 3.512 | 8.132 | 8.132 | 0.31062 | 0.56813 | 14.0354 | 13.9994 | 8.121 | 79.0295 | 0.17714 | 5.654 | 5.654 | 32.5662 | 522.45 | 914.3225 | 1166.8872 | -27.6231 | 89.0617 | 844.6686 | 96.1445 | 98.167 | 56.707 | 18.018 | 1.2 | 3.166 | 4.366 | 4.366 | 0.15069 | 0.27485 | 10.6667 | 10.6393 | 9.6576 | 49.7614 | 0.21381 | 5.654 | 5.172 | 102.4272 | 914.3225 | 1292.0839 | 1222.0529 | 5.42 | 65.5968 | 1068.1877 | 90.4111
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | [7 empty] | 1998-11-05 | 0:00 | 3665 | 29.134 | 128.56 | 56.422 | 18.045 | 0 | 14.299 | 3.166 |  | 17.465 | 17.465 | 0.81872 | 0 | 12.9991 | 12.9477 | 8.6962 | 65.7498 | 0.19692 | 7.936 | 5.653 | 30.785 | 294.048 | 297.685 | 1292.6914 | 1503.1185 | -16.2782 | 89.6585 | 900.4017 | 96.581 | 128.56 | 111.367 | 18.045 | 8.959 | 8.129 | 17.088 | 17.088 | 0.33635 | 0.52429 | 13.6086 | 13.5548 | 4.3611 | 97.5574 | 0.13894 | 5.653 | 5.653 | 16.5165 | 297.685 | 522.45 | 607.5617 | -16.2909 | 94.4517 | 452.6233 | 96.3509 | 111.367 | 97.297 | 18.045 | 4.26 | 3.869 | 8.129 | 8.129 | 0.32006 | 0.52405 | 12.9418 | 12.8906 | 7.5961 | 78.6909 | 0.16381 | 5.653 | 5.653 | 32.5487 | 522.45 | 916.37 | 1061.8606 | -15.8768 | 89.0661 | 792.1553 | 95.8911 | 97.297 | 56.422 | 18.045 | 1.08 | 3.166 | 4.246 | 4.246 | 0.14829 | 0.25436 | 9.6 | 9.5621 | 9.5266 | 49.2879 | 0.194 | 5.653 | 5.245 | 102.5222 | 916.37 | 1292.6914 | 1193.9934 | 7.6351 | 65.5602 | 1055.1817 | 90.2839
|  | (e.g., solute type and concentration) | [8 empty] | 1998-11-05 | 12:00 | 3677 | 29.163 | 127.729 | 58.252 | 17.79 | 0 | 13.995 | 3.046 |  | 17.041 | 17.041 | 0.82125 | 0 | 12.7227 | 12.6616 | 8.7604 | 66.4401 | 0.19057 | 7.654 | 5.676 | 32.007 | 295.776 | 297.6931 | 1341.3071 | 1518.4013 | -13.2031 | 89.2483 | 908.0472 | 96.4752 | 127.729 | 110.52 | 17.79 | 8.715 | 8.139 | 16.854 | 16.854 | 0.33336 | 0.51709 | 13.238 | 13.1743 | 4.3121 | 97.0224 | 0.13579 | 5.676 | 5.676 | 16.848 | 297.6931 | 526.05 | 598.4138 | -13.7561 | 94.3405 | 448.0534 | 96.2397 | 110.52 | 97.095 | 17.79 | 4.26 | 3.879 | 8.139 | 8.139 | 0.3206 | 0.52341 | 12.9418 | 12.8796 | 7.6421 | 78.3754 | 0.16433 | 5.676 | 5.676 | 32.7281 | 526.05 | 932.9775 | 1067.8266 | -14.4536 | 89.0061 | 796.9383 | 95.8933 | 97.095 | 58.252 | 17.79 | 1.02 | 3.046 | 4.066 | 4.066 | 0.14229 | 0.25086 | 9.0667 | 9.0231 | 9.6789 | 50.2046 | 0.17973 | 5.676 | 5.411 | 103.8989 | 932.9775 | 1341.3071 | 1210.6072 | 9.7442 | 65.0987 | 1071.7924 | 90.3061
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-11-05 | 20:00 | 3685.0003 | 29.117 | 127.441 | 58.125 | 17.779 | 0 | 14.061 | 2.986 |  | 17.047 | 17.047 | 0.82484 | 0 | 12.7827 | 12.7386 | 8.9467 | 66.0573 | 0.19284 | 8 | 5.646 | 31.0905 | 295.632 | 297.7992 | 1310.3149 | 1553.7239 | -18.5764 | 89.5599 | 925.7615 | 96.6416 | 127.441 | 110.28 | 17.779 | 8.781 | 8.431 | 17.212 | 17.212 | 0.34203 | 0.51017 | 13.3382 | 13.2922 | 4.28 | 96.8015 | 0.13731 | 5.646 | 5.646 | 16.3605 | 297.7992 | 529.2 | 590.9214 | -11.6632 | 94.5062 | 444.3603 | 96.3182 | 110.28 | 96.84 | 17.779 | 4.44 | 3.991 | 8.431 | 8.431 | 0.33137 | 0.52663 | 13.4886 | 13.442 | 7.7323 | 78.0487 | 0.17223 | 5.646 | 5.646 | 32.349 | 529.2 | 942.305 | 1081.9482 | -14.8193 | 89.1373 | 805.5741 | 95.9843 | 96.84 | 58.125 | 17.779 | 0.84 | 2.986 | 3.826 | 3.826 | 0.13629 | 0.21955 | 7.4667 | 7.4409 | 9.5687 | 50.1348 | 0.14842 | 5.646 | 5.277 | 103.4266 | 942.305 | 1310.3149 | 1178.2922 | 10.0756 | 65.2697 | 1060.2986 | 90.2455
|  | Standard testing recovery (%) | 10 | [7 empty] | 1998-11-06 | 0:00 | 3689 | 29.057 | 127.38 | 58.23 | 17.863 | 0 | 14.478 | 2.987 |  | 17.465 | 17.465 | 0.82897 | 0 | 13.1618 | 13.1397 | 9.1758 | 65.7662 | 0.19979 | 8.028 | 5.626 | 30.127 | 297.024 | 298.1501 | 1286.0068 | 1597.2589 | -24.203 | 89.8954 | 947.7045 | 96.8211 | 127.38 | 110.19 | 17.863 | 8.778 | 8.139 | 16.917 | 16.917 | 0.3342 | 0.51889 | 13.3337 | 13.3112 | 4.3471 | 96.5749 | 0.13783 | 5.626 | 5.626 | 15.7365 | 298.1501 | 531.9 | 602.7362 | -13.3176 | 94.722 | 450.4431 | 96.5064 | 110.19 | 96.757 | 17.863 | 4.5 | 3.639 | 8.139 | 8.139 | 0.31419 | 0.55289 | 13.6709 | 13.6479 | 8.0801 | 77.5304 | 0.17603 | 5.626 | 5.626 | 32.6066 | 531.9 | 950.2675 | 1149.3279 | -20.9478 | 89.0637 | 840.6139 | 96.1211 | 96.757 | 58.23 | 17.863 | 1.2 | 2.987 | 4.187 | 4.187 | 0.14353 | 0.2866 | 10.6667 | 10.6487 | 10.1776 | 49.4529 | 0.21533 | 5.626 | 5.034 | 102.7498 | 950.2675 | 1286.0068 | 1290.75 | -0.36884 | 65.5376 | 1120.5088 | 90.8301
|  | Standard testing pH | 7.5 | [7 empty] | 1998-11-06 | 12:00 | 3701 | 29.146 | 136.144 | 50.452 | 18.657 | 0 | 15.021 | 3.884 |  | 18.905 | 18.905 | 0.79455 | 0 | 13.6555 | 13.5967 | 7.8199 | 66.8211 | 0.20348 | 8.328 | 5.706 | 30.926 | 295.152 | 297.481 | 1304.2377 | 1328.3569 | -1.8493 | 89.604 | 812.9189 | 96.1957 | 136.144 | 117.637 | 18.657 | 9.321 | 8.718 | 18.039 | 18.039 | 0.35689 | 0.51671 | 14.1585 | 14.0975 | 4.3092 | 103.9243 | 0.13565 | 5.706 | 5.706 | 16.6725 | 297.481 | 519.3 | 597.7122 | -15.0996 | 94.3954 | 447.5966 | 96.2751 | 117.637 | 101.535 | 18.657 | 4.5 | 4.218 | 8.718 | 8.718 | 0.34509 | 0.51617 | 13.6709 | 13.612 | 7.4689 | 83.4601 | 0.1631 | 5.706 | 5.706 | 32.2267 | 519.3 | 886.34 | 1038.9373 | -17.2166 | 89.1668 | 779.1186 | 95.8637 | 101.535 | 50.452 | 18.657 | 1.2 | 3.884 | 5.084 | 5.084 | 0.17943 | 0.23603 | 10.6667 | 10.6207 | 9.0422 | 48.2943 | 0.21992 | 5.706 | 5.795 | 103.1098 | 886.34 | 1304.2377 | 1128.3267 | 13.4876 | 65.339 | 1007.3333 | 89.7641
|  | Acceptable range of operating pressures | 80 - 350 | [7 empty] | 1998-11-06 | 20:00 | 3709 | 29.074 | 136.271 | 50.61 | 18.619 | 0 | 15.021 | 3.885 |  | 18.906 | 18.906 | 0.79451 | 0 | 13.6555 | 13.6256 | 7.8269 | 66.9946 | 0.20338 | 8.469 | 5.704 | 30.6675 | 296.448 | 297.5054 | 1287.8298 | 1329.2101 | -3.2132 | 89.6918 | 813.3578 | 96.2295 | 136.271 | 117.87 | 18.619 | 9.321 | 8.961 | 18.282 | 18.282 | 0.36337 | 0.50985 | 14.1585 | 14.1275 | 4.2731 | 104.1784 | 0.13561 | 5.704 | 5.704 | 16.3995 | 297.5054 | 517.05 | 589.9046 | -14.0904 | 94.4877 | 443.705 | 96.304 | 117.87 | 101.88 | 18.619 | 4.5 | 4.461 | 8.961 | 8.961 | 0.35805 | 0.50218 | 13.6709 | 13.641 | 7.2934 | 83.9626 | 0.16247 | 5.704 | 5.704 | 32.2359 | 517.05 | 895.2125 | 1006.1026 | -12.387 | 89.1646 | 761.5763 | 95.7672 | 101.88 | 50.61 | 18.619 | 1.2 | 3.885 | 5.085 | 5.085 | 0.17947 | 0.23599 | 10.6667 | 10.6434 | 9.1442 | 48.4818 | 0.21953 | 5.704 | 5.855 | 103.1213 | 895.2125 | 1287.8298 | 1139.8739 | 11.4888 | 65.338 | 1017.5432 | 89.8657
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 1998-11-07 | 4:00 | 3717 | 29.053 | 136.392 | 50.707 | 18.64 | 0 | 15.019 | 3.886 |  | 18.905 | 18.905 | 0.79445 | 0 | 13.6536 | 13.6323 | 7.8357 | 67.0738 | 0.20324 | 8.022 | 5.69 | 30.5265 | 296.976 | 297.7339 | 1285.3993 | 1330.4638 | -3.5059 | 89.7471 | 814.0989 | 96.2503 | 136.392 | 118.027 | 18.64 | 9.319 | 8.667 | 17.986 | 17.986 | 0.3555 | 0.51813 | 14.1554 | 14.1333 | 4.3294 | 104.2401 | 0.13558 | 5.69 | 5.69 | 16.1655 | 297.7339 | 519.3 | 600.4841 | -15.6334 | 94.5705 | 449.109 | 96.4005 | 118.027 | 101.895 | 18.64 | 4.5 | 4.167 | 8.667 | 8.667 | 0.34236 | 0.51921 | 13.6709 | 13.6495 | 7.5004 | 83.8206 | 0.16284 | 5.69 | 5.69 | 32.246 | 519.3 | 897.9425 | 1045.2762 | -16.4079 | 89.1695 | 782.2881 | 95.878 | 101.895 | 50.707 | 18.64 | 1.2 | 3.886 | 5.086 | 5.086 | 0.17951 | 0.23594 | 10.6667 | 10.65 | 9.1754 | 48.4856 | 0.21965 | 5.69 | 5.739 | 103.127 | 897.9425 | 1285.3993 | 1143.3822 | 11.0485 | 65.3627 | 1020.6623 | 89.8961
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-11-07 | 12:00 | 3725 | 29.078 | 126.081 | 56.79 | 17.65 | 0 | 14.055 | 3.046 |  | 17.101 | 17.101 | 0.82188 | 0 | 12.7773 | 12.7478 | 8.7634 | 65.0221 | 0.19605 | 8.117 | 5.668 | 34.216 | 304.128 | 299.2027 | 1379.592 | 1521.9172 | -10.3165 | 88.5643 | 910.56 | 96.2423 | 126.081 | 108.945 | 17.65 | 8.655 | 8.304 | 16.959 | 16.959 | 0.33696 | 0.51035 | 13.1468 | 13.1166 | 4.2822 | 95.5808 | 0.13723 | 5.668 | 5.668 | 17.6865 | 299.2027 | 547.2 | 592.6183 | -8.3001 | 94.0888 | 445.9105 | 96.0336 | 108.945 | 95.37 | 17.65 | 4.2 | 4.104 | 8.304 | 8.304 | 0.331 | 0.50578 | 12.7595 | 12.7301 | 7.7752 | 76.7323 | 0.1659 | 5.668 | 5.668 | 32.8624 | 547.2 | 965.7375 | 1073.5689 | -11.1657 | 89.0167 | 810.3844 | 95.9448 | 95.37 | 56.79 | 17.65 | 1.2 | 3.046 | 4.246 | 4.246 | 0.14589 | 0.28262 | 10.6667 | 10.6421 | 10.3013 | 48.1287 | 0.22112 | 5.668 | 5.49 | 105.1315 | 965.7375 | 1379.592 | 1304.7812 | 5.4227 | 64.8628 | 1135.2594 | 90.7394
|  | Maximum permissible SDI | 5 | [7 empty] | 1998-11-07 | 17:15 | 3730.2522 | 29.044 | 127.394 | 68.175 | 18.153 | 0 | 14.416 | 2.748 |  | 17.164 | 17.164 | 0.8399 | 0 | 13.1055 | 13.0884 | 9.6074 | 70.0241 | 0.18691 | 8.112 | 5.663 | 34.0985 | 305.088 | 299.2762 | 1420.3075 | 1690.3974 | -19.0163 | 88.6063 | 994.8368 | 96.5725 | 127.394 | 110.88 | 18.153 | 8.656 | 8.13 | 16.786 | 16.786 | 0.33233 | 0.51567 | 13.1484 | 13.1313 | 4.3182 | 96.6658 | 0.13584 | 5.663 | 5.663 | 17.472 | 299.2762 | 549.9 | 599.3127 | -8.9858 | 94.1619 | 449.2944 | 96.1112 | 110.88 | 99.225 | 18.153 | 4.44 | 3.69 | 8.13 | 8.13 | 0.31531 | 0.54613 | 13.4886 | 13.4711 | 8.2786 | 78.6209 | 0.17134 | 5.663 | 5.663 | 33.0151 | 549.9 | 975.975 | 1171.8428 | -20.0689 | 88.9683 | 860.8714 | 96.1649 | 99.225 | 68.175 | 18.153 | 1.32 | 2.748 | 4.068 | 4.068 | 0.13637 | 0.32448 | 11.7333 | 11.7181 | 10.7958 | 54.7512 | 0.21402 | 5.663 | 5.496 | 105.4685 | 975.975 | 1420.3075 | 1394.1222 | 1.8436 | 64.7588 | 1185.0486 | 91.1001
|  | Maximum permissible turbidity (ntu) | less than 1 | [7 empty] | 1998-11-08 | 1:00 | 3738.0003 | 28.993 | 138.395 | 38.887 | 18.682 | 0 | 14.777 | 3.983 |  | 18.76 | 18.76 | 0.78769 | 0 | 13.4336 | 13.4364 | 7.6342 | 62.3248 | 0.21559 | 8.055 | 5.718 | 31.584 | 304.992 | 298.9824 | 1300.5916 | 1291.0352 | 0.73478 | 89.4362 | 795.0088 | 96.0272 | 138.395 | 119.032 | 18.682 | 9.437 | 9.145 | 18.582 | 18.582 | 0.36983 | 0.50786 | 14.3347 | 14.3376 | 4.2782 | 105.7533 | 0.13558 | 5.718 | 5.718 | 16.77 | 298.9824 | 529.65 | 590.2058 | -11.4332 | 94.391 | 444.5941 | 96.228 | 119.032 | 101.497 | 18.682 | 4.44 | 4.705 | 9.145 | 9.145 | 0.36947 | 0.48551 | 13.4886 | 13.4914 | 7.3251 | 84.2574 | 0.16012 | 5.718 | 5.718 | 31.9682 | 529.65 | 880.1975 | 999.3009 | -13.5314 | 89.3077 | 764.4754 | 95.8183 | 101.497 | 38.887 | 18.682 | 0.9 | 3.983 | 4.883 | 4.883 | 0.17738 | 0.18431 | 8 | 8.0017 | 8.6413 | 42.8687 | 0.18665 | 5.718 | 5.911 | 103.7894 | 880.1975 | 1300.5916 | 1055.6349 | 18.8343 | 65.2858 | 967.9162 | 89.277
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1998-11-08 | 9:00 | 3746 | 29.049 | 137.94 | 39 | 18.61 | 0 | 14.961 | 3.983 |  | 18.944 | 18.944 | 0.78975 | 0 | 13.6009 | 13.5812 | 7.6822 | 62.1778 | 0.21843 | 8.135 | 5.729 | 31.6545 | 303.6 | 298.5744 | 1302.4147 | 1301.1826 | 0.094595 | 89.3981 | 799.8785 | 96.0426 | 137.94 | 118.65 | 18.61 | 9.501 | 9.025 | 18.526 | 18.526 | 0.36748 | 0.51285 | 14.4319 | 14.411 | 4.3002 | 105.3848 | 0.13675 | 5.729 | 5.729 | 16.848 | 298.5744 | 526.5 | 595.1597 | -13.0408 | 94.3572 | 446.8671 | 96.2298 | 118.65 | 101.122 | 18.61 | 4.5 | 4.525 | 9.025 | 9.025 | 0.36146 | 0.49861 | 13.6709 | 13.6511 | 7.4046 | 83.8714 | 0.16276 | 5.729 | 5.729 | 31.9461 | 526.5 | 877.4675 | 1018.3216 | -16.0523 | 89.3005 | 772.4108 | 95.8641 | 101.122 | 39 | 18.61 | 0.96 | 3.983 | 4.943 | 4.943 | 0.17858 | 0.19421 | 8.5333 | 8.521 | 8.6679 | 42.7831 | 0.19917 | 5.729 | 6.065 | 103.9046 | 877.4675 | 1302.4147 | 1063.915 | 18.3121 | 65.1997 | 970.6912 | 89.2958
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-11-08 | 17:00 | 3754 | 28.998 | 137.819 | 38.602 | 18.673 | 0 | 14.777 | 3.983 |  | 18.76 | 18.76 | 0.78769 | 0 | 13.4336 | 13.4344 | 7.6071 | 61.9304 | 0.21693 | 7.961 | 5.723 | 29.939 | 290.736 | 296.3875 | 1268.9914 | 1284.9162 | -1.2549 | 89.8987 | 790.6519 | 96.2134 | 137.819 | 118.425 | 18.673 | 9.437 | 9.029 | 18.466 | 18.466 | 0.36673 | 0.51105 | 14.3347 | 14.3355 | 4.2669 | 105.1821 | 0.13629 | 5.723 | 5.723 | 16.146 | 296.3875 | 502.2 | 589.2925 | -17.3422 | 94.5524 | 442.84 | 96.354 | 118.425 | 100.777 | 18.673 | 4.56 | 4.469 | 9.029 | 9.029 | 0.36008 | 0.50504 | 13.8532 | 13.854 | 7.1044 | 83.8236 | 0.16528 | 5.723 | 5.723 | 31.7639 | 502.2 | 836.745 | 982.2153 | -17.3853 | 89.283 | 742.2077 | 95.7203 | 100.777 | 38.602 | 18.673 | 0.78 | 3.983 | 4.763 | 4.763 | 0.17498 | 0.16376 | 6.9333 | 6.9337 | 8.0589 | 42.9576 | 0.16141 | 5.723 | 5.937 | 102.7267 | 836.745 | 1268.9914 | 980.4895 | 22.7347 | 65.3404 | 908.6172 | 88.6942
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1998-11-09 | 0:00 | 3761 | 28.985 | 138.569 | 38.805 | 18.744 | 0 | 15.013 | 3.984 |  | 18.997 | 18.997 | 0.79028 | 0 | 13.6482 | 13.6542 | 7.6982 | 62.2448 | 0.21936 | 8.051 | 5.72 | 29.892 | 292.32 | 296.8037 | 1265.3453 | 1302.6132 | -2.9453 | 89.9287 | 799.7084 | 96.2621 | 138.569 | 119.115 | 18.744 | 9.493 | 9.146 | 18.639 | 18.639 | 0.3706 | 0.50931 | 14.4197 | 14.4261 | 4.259 | 105.839 | 0.1363 | 5.72 | 5.72 | 16.419 | 296.8037 | 505.8 | 587.8262 | -16.2171 | 94.4681 | 442.3149 | 96.2879 | 119.115 | 101.362 | 18.744 | 4.5 | 4.646 | 9.146 | 9.146 | 0.36792 | 0.49202 | 13.6709 | 13.6769 | 7.0356 | 84.4589 | 0.16194 | 5.72 | 5.72 | 31.7961 | 505.8 | 844.48 | 964.9084 | -14.2607 | 89.2872 | 735.3542 | 95.6761 | 101.362 | 38.805 | 18.744 | 1.02 | 3.984 | 5.004 | 5.004 | 0.17983 | 0.20384 | 9.0667 | 9.0707 | 8.3648 | 42.9747 | 0.21107 | 5.72 | 5.986 | 102.9254 | 844.48 | 1265.3453 | 1034.3358 | 18.2566 | 65.322 | 939.4079 | 89.0436
[11 empty] | 1998-11-09 | 9:00 | 3770.0003 | 29.027 | 138.831 | 46.732 | 18.885 | 0 | 15.2 | 3.983 |  | 19.183 | 19.183 | 0.79237 | 0 | 13.8182 | 13.8072 | 7.7359 | 66.1606 | 0.20869 | 8.116 | 5.721 | 30.832 | 293.328 | 296.8445 | 1292.0839 | 1312.0063 | -1.5419 | 89.6134 | 804.4254 | 96.1672 | 138.831 | 119.775 | 18.885 | 9.5 | 9.08 | 18.58 | 18.58 | 0.36893 | 0.5113 | 14.4304 | 14.4189 | 4.2695 | 106.1485 | 0.13584 | 5.721 | 5.721 | 16.536 | 296.8445 | 514.35 | 590.1188 | -14.731 | 94.4294 | 443.4816 | 96.2713 | 119.775 | 102.825 | 18.885 | 4.56 | 4.52 | 9.08 | 9.08 | 0.3628 | 0.5022 | 13.8532 | 13.8421 | 7.2557 | 85.1593 | 0.16254 | 5.721 | 5.721 | 32.0602 | 514.35 | 873.6 | 1000.9079 | -14.5728 | 89.1997 | 757.6289 | 95.7684 | 102.825 | 46.732 | 18.885 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.1252 | 8.8089 | 47.0846 | 0.21504 | 5.721 | 6.066 | 102.9917 | 873.6 | 1292.0839 | 1094.1608 | 15.3181 | 65.3045 | 983.8804 | 89.5321
[11 empty] | 1998-11-09 | 17:00 | 3778.0003 | 29.036 | 138.931 | 46.59 | 18.946 | 0 | 15.259 | 3.983 |  | 19.242 | 19.242 | 0.793 | 0 | 13.8718 | 13.8571 | 7.7595 | 66.055 | 0.20978 | 8.078 | 5.721 | 30.8555 | 294.144 | 296.9995 | 1292.0839 | 1316.6057 | -1.8979 | 89.6109 | 806.8026 | 96.1756 | 138.931 | 119.722 | 18.946 | 9.559 | 8.909 | 18.468 | 18.468 | 0.36516 | 0.5176 | 14.52 | 14.5046 | 4.3087 | 106.0718 | 0.13674 | 5.721 | 5.721 | 16.575 | 296.9995 | 514.8 | 597.8838 | -16.139 | 94.4192 | 447.4417 | 96.2956 | 119.722 | 102.937 | 18.946 | 4.62 | 4.289 | 8.909 | 8.909 | 0.35207 | 0.51858 | 14.0354 | 14.0205 | 7.4271 | 84.9564 | 0.16503 | 5.721 | 5.721 | 32.0767 | 514.8 | 873.3725 | 1034.777 | -18.4806 | 89.1997 | 774.7885 | 95.8599 | 102.937 | 46.59 | 18.946 | 1.08 | 3.983 | 5.063 | 5.063 | 0.18099 | 0.21331 | 9.6 | 9.5898 | 8.7483 | 47.0692 | 0.20374 | 5.721 | 6.028 | 102.9888 | 873.3725 | 1292.0839 | 1082.2639 | 16.2389 | 65.3236 | 977.8182 | 89.4675
[11 empty] | 1998-11-10 | 1:00 | 3786 | 29.002 | 139.259 | 46.747 | 19.045 | 0 | 15.077 | 3.983 |  | 19.06 | 19.06 | 0.79103 | 0 | 13.7064 | 13.7056 | 7.704 | 66.254 | 0.20686 | 8.179 | 5.71 | 30.785 | 294.144 | 297.1138 | 1290.8684 | 1305.2581 | -1.1147 | 89.6386 | 801.1859 | 96.1576 | 139.259 | 120.21 | 19.045 | 9.497 | 8.909 | 18.406 | 18.406 | 0.36433 | 0.51597 | 14.4258 | 14.425 | 4.3022 | 106.3873 | 0.13559 | 5.71 | 5.71 | 16.4775 | 297.1138 | 514.35 | 596.2722 | -15.9273 | 94.4541 | 446.693 | 96.3112 | 120.21 | 103.32 | 19.045 | 4.62 | 4.289 | 8.909 | 8.909 | 0.35207 | 0.51858 | 14.0354 | 14.0346 | 7.4202 | 85.2998 | 0.16453 | 5.71 | 5.71 | 32.0758 | 514.35 | 872.9175 | 1033.8433 | -18.4354 | 89.2042 | 774.0967 | 95.8564 | 103.32 | 46.747 | 19.045 | 0.96 | 3.983 | 4.943 | 4.943 | 0.17858 | 0.19421 | 8.5333 | 8.5328 | 8.6272 | 47.3613 | 0.18016 | 5.71 | 5.988 | 102.983 | 872.9175 | 1290.8684 | 1058.4905 | 18.0017 | 65.3389 | 965.704 | 89.336
[11 empty] | 1998-11-10 | 9:00 | 3794.0003 | 29.138 | 138.616 | 46.267 | 18.951 | 0 | 15.38 | 3.983 |  | 19.363 | 19.363 | 0.7943 | 0 | 13.9818 | 13.9249 | 7.7889 | 65.7016 | 0.21194 | 8.161 | 5.725 | 29.6805 | 285.936 | 295.4491 | 1272.6374 | 1321.691 | -3.8545 | 89.9541 | 808.5701 | 96.3293 | 138.616 | 119.52 | 18.951 | 9.5 | 9.08 | 18.58 | 18.58 | 0.36893 | 0.5113 | 14.4304 | 14.3716 | 4.2565 | 105.8605 | 0.13576 | 5.725 | 5.725 | 15.99 | 295.4491 | 499.5 | 587.8348 | -17.6846 | 94.5879 | 441.6419 | 96.3794 | 119.52 | 102.517 | 18.951 | 4.5 | 4.58 | 9.08 | 9.08 | 0.3644 | 0.49559 | 13.6709 | 13.6152 | 6.9724 | 85.0951 | 0.16 | 5.725 | 5.725 | 31.9516 | 499.5 | 846.5275 | 958.8816 | -13.2724 | 89.1854 | 729.1908 | 95.6182 | 102.517 | 46.267 | 18.951 | 1.38 | 3.983 | 5.363 | 5.363 | 0.18699 | 0.25732 | 12.2667 | 12.2167 | 8.7305 | 46.7105 | 0.26154 | 5.725 | 6.058 | 102.3926 | 846.5275 | 1272.6374 | 1104.3498 | 13.2235 | 65.3434 | 975.4386 | 89.5029
[11 empty] | 1998-11-10 | 17:00 | 3802.0003 | 29.142 | 134.201 | 62.482 | 18.843 | 0 | 15.139 | 3.046 |  | 18.185 | 18.185 | 0.8325 | 0 | 13.7627 | 13.7051 | 9.2256 | 70.2729 | 0.19503 | 8.206 | 5.7 | 31.2785 | 287.52 | 295.9958 | 1325.5072 | 1611.674 | -21.5892 | 89.4328 | 953.8349 | 96.7208 | 134.201 | 116.52 | 18.843 | 9.259 | 8.313 | 17.572 | 17.572 | 0.34526 | 0.52692 | 14.0643 | 14.0054 | 4.3494 | 102.1681 | 0.13708 | 5.7 | 5.7 | 16.6335 | 295.9958 | 515.25 | 607.149 | -17.8358 | 94.3805 | 451.5724 | 96.3165 | 116.52 | 102.292 | 18.843 | 4.56 | 3.753 | 8.313 | 8.313 | 0.32188 | 0.54854 | 13.8532 | 13.7951 | 7.7563 | 82.8067 | 0.16659 | 5.7 | 5.7 | 32.7474 | 515.25 | 917.735 | 1101.5042 | -20.0242 | 88.9365 | 808.3771 | 95.949 | 102.292 | 62.482 | 18.843 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.6842 | 9.9091 | 53.6349 | 0.21785 | 5.7 | 5.955 | 103.2998 | 917.735 | 1325.5072 | 1270.6747 | 4.1367 | 65.1009 | 1094.2049 | 90.5594
[11 empty] | 1998-11-11 | 1:00 | 3810 | 29.121 | 134.1 | 62.377 | 18.781 | 0 | 14.718 | 3.046 |  | 17.764 | 17.764 | 0.82853 | 0 | 13.38 | 13.3322 | 9.0481 | 70.4094 | 0.18935 | 8.213 | 5.684 | 31.2315 | 287.376 | 296.1101 | 1313.3529 | 1575.9797 | -19.9967 | 89.4527 | 936.0449 | 96.6635 | 134.1 | 116.205 | 18.781 | 9.258 | 8.253 | 17.511 | 17.511 | 0.34364 | 0.5287 | 14.0628 | 14.0126 | 4.3647 | 102.0068 | 0.13737 | 5.684 | 5.684 | 16.4775 | 296.1101 | 514.35 | 609.7946 | -18.5564 | 94.4353 | 452.9523 | 96.3622 | 116.205 | 102.067 | 18.781 | 4.5 | 3.753 | 8.253 | 8.253 | 0.32028 | 0.54526 | 13.6709 | 13.6221 | 7.7047 | 82.6503 | 0.16482 | 5.684 | 5.684 | 32.6646 | 514.35 | 920.6925 | 1091.9104 | -18.5966 | 88.9688 | 803.1302 | 95.9328 | 102.067 | 62.377 | 18.781 | 0.96 | 3.046 | 4.006 | 4.006 | 0.14109 | 0.23964 | 8.5333 | 8.5029 | 9.4633 | 53.9777 | 0.15753 | 5.684 | 5.77 | 103.1846 | 920.6925 | 1313.3529 | 1178.3444 | 10.2797 | 65.1533 | 1049.5184 | 90.1684
[11 empty] | 1998-11-11 | 9:00 | 3818.0003 | 29.185 | 137.102 | 32.917 | 18.576 | 0 | 14.895 | 3.982 |  | 18.877 | 18.877 | 0.78906 | 0 | 13.5409 | 13.4671 | 7.6328 | 58.8007 | 0.22903 | 8.187 | 5.73 | 29.6805 | 286.752 | 295.6042 | 1262.3067 | 1290.3136 | -2.2187 | 89.9594 | 792.9589 | 96.257 | 137.102 | 117.367 | 18.576 | 9.435 | 9.328 | 18.763 | 18.763 | 0.37468 | 0.50285 | 14.3316 | 14.2535 | 4.205 | 104.4535 | 0.13646 | 5.73 | 5.73 | 16.341 | 295.6042 | 495.9 | 578.0707 | -16.57 | 94.472 | 436.8374 | 96.2592 | 117.367 | 99.292 | 18.576 | 4.56 | 4.768 | 9.328 | 9.328 | 0.37603 | 0.48885 | 13.8532 | 13.7776 | 6.8638 | 82.8897 | 0.16622 | 5.73 | 5.73 | 31.5578 | 495.9 | 806.715 | 939.9856 | -16.5202 | 89.3243 | 717.9428 | 95.6044 | 99.292 | 32.917 | 18.576 | 0.9 | 3.982 | 4.882 | 4.882 | 0.17734 | 0.18435 | 8 | 7.9564 | 7.8367 | 39.6918 | 0.20045 | 5.73 | 6.045 | 102.6115 | 806.715 | 1262.3067 | 965.8544 | 23.485 | 65.2875 | 886.2847 | 88.4223
[11 empty] | 1998-11-11 | 17:00 | 3826.0003 | 29.151 | 138.938 | 47.317 | 19.042 | 0 | 15.319 | 3.983 |  | 19.302 | 19.302 | 0.79365 | 0 | 13.9264 | 13.8643 | 7.7695 | 66.316 | 0.20906 | 8.104 | 5.724 | 30.08 | 287.568 | 295.8816 | 1272.0299 | 1318.18 | -3.6281 | 89.8338 | 807.0308 | 96.2728 | 138.938 | 119.625 | 19.042 | 9.559 | 8.844 | 18.403 | 18.403 | 0.36343 | 0.51943 | 14.52 | 14.4553 | 4.3064 | 105.9331 | 0.13646 | 5.724 | 5.724 | 16.3215 | 295.8816 | 503.55 | 598.043 | -18.7654 | 94.4838 | 446.9623 | 96.3483 | 119.625 | 102.885 | 19.042 | 4.62 | 4.224 | 8.844 | 8.844 | 0.34861 | 0.52239 | 14.0354 | 13.9729 | 7.2941 | 84.9189 | 0.16454 | 5.724 | 5.724 | 32.0142 | 503.55 | 854.035 | 1019.2923 | -19.3502 | 89.1801 | 761.4212 | 95.7955 | 102.885 | 47.317 | 19.042 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0882 | 8.5916 | 47.4674 | 0.21253 | 5.724 | 6.044 | 102.4387 | 854.035 | 1272.0299 | 1069.1542 | 15.949 | 65.3785 | 961.5946 | 89.347
[11 empty] | 1998-11-12 | 1:00 | 3834 | 29.138 | 138.723 | 47.34 | 19.041 | 0 | 15.378 | 3.983 |  | 19.361 | 19.361 | 0.79428 | 0 | 13.98 | 13.9231 | 7.7946 | 66.1959 | 0.21033 | 8.145 | 5.724 | 29.986 | 287.328 | 295.9714 | 1270.8144 | 1322.9166 | -4.0999 | 89.8686 | 809.444 | 96.2955 | 138.723 | 119.475 | 19.041 | 9.558 | 8.91 | 18.468 | 18.468 | 0.36517 | 0.51754 | 14.5185 | 14.4594 | 4.2985 | 105.7595 | 0.13672 | 5.724 | 5.724 | 16.185 | 295.9714 | 502.65 | 596.1058 | -18.5926 | 94.5316 | 446.0386 | 96.3714 | 119.475 | 102.66 | 19.041 | 4.62 | 4.29 | 8.91 | 8.91 | 0.35213 | 0.51852 | 14.0354 | 13.9783 | 7.2406 | 84.7859 | 0.16487 | 5.724 | 5.724 | 32.0114 | 502.65 | 853.3525 | 1009.4916 | -18.2971 | 89.1843 | 756.0708 | 95.7661 | 102.66 | 47.34 | 19.041 | 1.2 | 3.983 | 5.183 | 5.183 | 0.18339 | 0.23153 | 10.6667 | 10.6232 | 8.6399 | 47.3191 | 0.2245 | 5.724 | 6.002 | 102.479 | 853.3525 | 1270.8144 | 1079.576 | 15.0485 | 65.3754 | 966.4642 | 89.3965
[11 empty] | 1998-11-12 | 9:00 | 3842 | 28.832 | 139.715 | 47.955 | 18.994 | 0 | 15.258 | 3.983 |  | 19.241 | 19.241 | 0.79299 | 0 | 13.8709 | 13.94 | 7.7838 | 67.0572 | 0.20788 | 8.044 | 5.748 | 32.9235 | 311.28 | 299.9126 | 1335.2299 | 1322.6895 | 0.93919 | 89.0223 | 811.3011 | 95.9419 | 139.715 | 120.622 | 18.994 | 9.498 | 8.782 | 18.28 | 18.28 | 0.36096 | 0.51958 | 14.4273 | 14.4992 | 4.3548 | 106.8197 | 0.13573 | 5.748 | 5.748 | 17.277 | 299.9126 | 546.75 | 605.5917 | -10.7621 | 94.2393 | 452.7522 | 96.184 | 120.622 | 103.695 | 18.994 | 4.56 | 4.222 | 8.782 | 8.782 | 0.3469 | 0.51924 | 13.8532 | 13.9221 | 7.9213 | 85.2432 | 0.16332 | 5.748 | 5.748 | 32.3886 | 546.75 | 933.4325 | 1102.2896 | -18.0899 | 89.2007 | 824.5198 | 96.0718 | 103.695 | 47.955 | 18.994 | 1.2 | 3.983 | 5.183 | 5.183 | 0.18339 | 0.23153 | 10.6667 | 10.7198 | 9.5353 | 47.2957 | 0.22665 | 5.748 | 6.105 | 104.7398 | 933.4325 | 1335.2299 | 1183.1014 | 11.3934 | 65.0766 | 1058.2669 | 90.1027
[11 empty] | 1998-11-12 | 17:00 | 3850 | 28.866 | 139.688 | 47.925 | 19.008 | 0 | 15.137 | 3.982 |  | 19.119 | 19.119 | 0.79173 | 0 | 13.7609 | 13.8155 | 7.7431 | 67.0554 | 0.20603 | 8.092 | 5.743 | 32.9705 | 312.048 | 299.9126 | 1336.4455 | 1314.6548 | 1.6305 | 89.0066 | 807.2837 | 95.9159 | 139.688 | 120.592 | 19.008 | 9.497 | 9.031 | 18.528 | 18.528 | 0.36759 | 0.51258 | 14.4258 | 14.4831 | 4.3119 | 106.8201 | 0.13558 | 5.743 | 5.743 | 17.316 | 299.9126 | 547.2 | 597.0913 | -9.1176 | 94.2263 | 448.502 | 96.1391 | 120.592 | 103.755 | 19.008 | 4.56 | 4.471 | 9.031 | 9.031 | 0.36018 | 0.50493 | 13.8532 | 13.9081 | 7.7734 | 85.3921 | 0.16287 | 5.743 | 5.743 | 32.3886 | 547.2 | 933.8875 | 1072.2593 | -14.8167 | 89.2007 | 809.7296 | 96.0001 | 103.755 | 47.925 | 19.008 | 1.08 | 3.982 | 5.062 | 5.062 | 0.18095 | 0.21335 | 9.6 | 9.6381 | 9.4155 | 47.4165 | 0.20326 | 5.743 | 6.081 | 104.7744 | 933.8875 | 1336.4455 | 1158.76 | 13.2954 | 65.065 | 1046.3237 | 89.9864
[11 empty] | 1998-11-13 | 1:00 | 3858.0003 | 29.057 | 138.342 | 47.212 | 18.946 | 0 | 15.257 | 3.983 |  | 19.24 | 19.24 | 0.79298 | 0 | 13.87 | 13.8467 | 7.7622 | 66.0688 | 0.20958 | 7.871 | 5.748 | 29.563 | 288.192 | 295.8245 | 1268.9914 | 1315.747 | -3.6845 | 90.0066 | 805.7857 | 96.3312 | 138.342 | 119.235 | 18.946 | 9.497 | 10.715 | 20.212 | 20.212 | 0.41251 | 0.46987 | 14.4258 | 14.4015 | 4.0359 | 105.8066 | 0.13611 | 5.748 | 5.748 | 16.1655 | 295.8245 | 502.2 | 543.6939 | -8.2624 | 94.5354 | 419.7592 | 96.1489 | 119.235 | 102.382 | 18.946 | 4.56 | 6.155 | 10.715 | 10.715 | 0.45003 | 0.42557 | 13.8532 | 13.8298 | 6.4438 | 85.4187 | 0.16191 | 5.748 | 5.748 | 31.9948 | 502.2 | 853.125 | 850.5567 | 0.30105 | 89.1845 | 676.3784 | 95.2697 | 102.382 | 47.212 | 18.946 | 1.2 | 3.983 | 5.183 | 5.183 | 0.18339 | 0.23153 | 10.6667 | 10.6487 | 8.6373 | 47.2137 | 0.22554 | 5.748 | 6.14 | 102.4762 | 853.125 | 1268.9914 | 1079.2808 | 14.9497 | 65.3591 | 966.2029 | 89.3939
[11 empty] | 1998-11-13 | 9:00 | 3866 | 29.142 | 138.884 | 47.362 | 19.074 | 0 | 15.316 | 3.983 |  | 19.299 | 19.299 | 0.79362 | 0 | 13.9236 | 13.8653 | 7.7644 | 66.2846 | 0.20918 | 8.09 | 5.729 | 30.033 | 286.656 | 295.6939 | 1271.4224 | 1317.2512 | -3.6045 | 89.8432 | 806.4726 | 96.276 | 138.884 | 119.7 | 19.074 | 9.556 | 8.85 | 18.406 | 18.406 | 0.36355 | 0.51918 | 14.5154 | 14.4546 | 4.3038 | 105.9142 | 0.13648 | 5.729 | 5.729 | 16.2045 | 295.6939 | 502.65 | 597.4793 | -18.8659 | 94.5198 | 446.5866 | 96.3715 | 119.7 | 102.682 | 19.074 | 4.62 | 4.23 | 8.85 | 8.85 | 0.34893 | 0.52203 | 14.0354 | 13.9767 | 7.2765 | 84.8405 | 0.16474 | 5.729 | 5.729 | 32.0123 | 502.65 | 853.58 | 1016.6798 | -19.1077 | 89.1738 | 759.6649 | 95.786 | 102.682 | 47.362 | 19.074 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0909 | 8.5864 | 47.3616 | 0.21306 | 5.729 | 6.05 | 102.433 | 853.58 | 1271.4224 | 1068.5706 | 15.9547 | 65.3584 | 961.0753 | 89.3418
[11 empty] | 1998-11-13 | 17:00 | 3874 | 29.142 | 138.931 | 47.46 | 19.071 | 0 | 14.954 | 3.983 |  | 18.937 | 18.937 | 0.78967 | 0 | 13.5945 | 13.5376 | 7.6519 | 66.4726 | 0.20366 | 8.306 | 5.716 | 30.0565 | 288.288 | 296.004 | 1271.4224 | 1294.4923 | -1.8145 | 89.8459 | 795.2482 | 96.2205 | 138.931 | 119.872 | 19.071 | 9.614 | 8.792 | 18.406 | 18.406 | 0.36277 | 0.52233 | 14.6035 | 14.5424 | 4.3269 | 106.0036 | 0.13719 | 5.716 | 5.716 | 16.263 | 296.004 | 503.1 | 601.8991 | -19.6381 | 94.5058 | 448.9516 | 96.3776 | 119.872 | 102.735 | 19.071 | 4.2 | 4.592 | 8.792 | 8.792 | 0.35704 | 0.47771 | 12.7595 | 12.706 | 6.8652 | 85.3673 | 0.14884 | 5.716 | 5.716 | 32.0123 | 503.1 | 857.9025 | 933.9729 | -8.867 | 89.1852 | 718.5364 | 95.5448 | 102.735 | 47.46 | 19.071 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0909 | 8.6352 | 47.3913 | 0.21293 | 5.716 | 5.967 | 102.4877 | 857.9025 | 1271.4224 | 1074.1146 | 15.5187 | 65.3763 | 966.0086 | 89.3906
[11 empty] | 1998-11-14 | 1:00 | 3882.0003 | 29.129 | 138.656 | 47.22 | 19.057 | 0 | 15.379 | 3.983 |  | 19.362 | 19.362 | 0.79429 | 0 | 13.9809 | 13.9277 | 7.8001 | 66.0809 | 0.21077 | 8.429 | 5.715 | 29.939 | 288.096 | 296.1019 | 1268.9914 | 1323.7995 | -4.319 | 89.889 | 809.9507 | 96.3036 | 138.656 | 119.587 | 19.057 | 9.559 | 9.144 | 18.703 | 18.703 | 0.37143 | 0.51109 | 14.52 | 14.4647 | 4.2632 | 105.8013 | 0.13672 | 5.715 | 5.715 | 16.1265 | 296.1019 | 506.25 | 588.784 | -16.303 | 94.5537 | 442.443 | 96.3551 | 119.587 | 102.57 | 19.057 | 4.62 | 4.524 | 9.144 | 9.144 | 0.36461 | 0.50525 | 14.0354 | 13.982 | 7.1637 | 84.8578 | 0.16477 | 5.715 | 5.715 | 32.0261 | 506.25 | 856.765 | 990.537 | -15.6136 | 89.1841 | 748.3935 | 95.7207 | 102.57 | 47.22 | 19.057 | 1.2 | 3.983 | 5.183 | 5.183 | 0.18339 | 0.23153 | 10.6667 | 10.6261 | 8.6792 | 47.1588 | 0.22533 | 5.715 | 5.91 | 102.4704 | 856.765 | 1268.9914 | 1084.0192 | 14.5763 | 65.3935 | 970.3921 | 89.4403
[11 empty] | 1998-11-14 | 11:00 | 3892 | 29.219 | 138.161 | 44.842 | 18.93 | 0 | 14.962 | 3.983 |  | 18.945 | 18.945 | 0.78976 | 0 | 13.6018 | 13.5141 | 7.6402 | 64.9313 | 0.20813 | 8.436 | 5.739 | 30.221 | 286.128 | 295.6694 | 1275.676 | 1292.8172 | -1.3437 | 89.7788 | 794.2433 | 96.195 | 138.161 | 118.875 | 18.93 | 9.562 | 9.5 | 19.062 | 19.062 | 0.38097 | 0.50163 | 14.5246 | 14.4308 | 4.1961 | 105.3919 | 0.13693 | 5.739 | 5.739 | 16.536 | 295.6694 | 500.85 | 576.6246 | -15.1292 | 94.4073 | 436.147 | 96.2086 | 118.875 | 101.715 | 18.93 | 4.26 | 5.24 | 9.5 | 9.5 | 0.39321 | 0.44842 | 12.9418 | 12.8583 | 6.5954 | 84.7696 | 0.15168 | 5.739 | 5.739 | 31.9231 | 500.85 | 844.025 | 882.0768 | -4.5084 | 89.2031 | 691.4634 | 95.3833 | 101.715 | 44.842 | 18.93 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0679 | 8.4769 | 45.8716 | 0.21948 | 5.739 | 6.038 | 102.4589 | 844.025 | 1275.676 | 1056.2734 | 17.1989 | 65.3468 | 950.1492 | 89.2165
[11 empty] | 1998-11-14 | 19:00 | 3900 | 29.151 | 138.228 | 44.925 | 18.955 | 0 | 15.38 | 3.983 |  | 19.363 | 19.363 | 0.7943 | 0 | 13.9818 | 13.9196 | 7.7948 | 64.8267 | 0.21472 | 8.401 | 5.72 | 30.033 | 288.288 | 296.004 | 1271.4224 | 1323.0273 | -4.0588 | 89.8539 | 809.5157 | 96.29 | 138.228 | 119.167 | 18.955 | 9.56 | 8.786 | 18.346 | 18.346 | 0.36189 | 0.52109 | 14.5215 | 14.4568 | 4.3196 | 105.4229 | 0.13713 | 5.72 | 5.72 | 16.2435 | 296.004 | 503.1 | 600.4099 | -19.3421 | 94.5124 | 448.207 | 96.3759 | 119.167 | 102.03 | 18.955 | 4.62 | 4.166 | 8.786 | 8.786 | 0.34551 | 0.52584 | 14.0354 | 13.9729 | 7.324 | 84.3195 | 0.16571 | 5.72 | 5.72 | 31.947 | 503.1 | 849.94 | 1025.598 | -20.6671 | 89.2072 | 764.349 | 95.8204 | 102.03 | 44.925 | 18.955 | 1.2 | 3.983 | 5.183 | 5.183 | 0.18339 | 0.23153 | 10.6667 | 10.6192 | 8.6 | 45.9225 | 0.23124 | 5.72 | 5.978 | 102.5309 | 849.94 | 1271.4224 | 1075.1197 | 15.4396 | 65.3617 | 962.5299 | 89.3478
[11 empty] | 1998-11-15 | 3:00 | 3908 | 29.112 | 138.516 | 45.022 | 18.982 | 0 | 14.774 | 3.983 |  | 18.757 | 18.757 | 0.78765 | 0 | 13.4309 | 13.3865 | 7.5999 | 65.1871 | 0.20536 | 8.42 | 5.711 | 29.986 | 289.056 | 296.2162 | 1270.2069 | 1283.7342 | -1.065 | 89.877 | 789.9752 | 96.2042 | 138.516 | 119.22 | 18.982 | 9.494 | 8.972 | 18.466 | 18.466 | 0.36597 | 0.51413 | 14.4213 | 14.3736 | 4.2819 | 105.6041 | 0.13611 | 5.711 | 5.711 | 16.185 | 296.2162 | 503.55 | 592.5398 | -17.6725 | 94.5361 | 444.378 | 96.3578 | 119.22 | 102.007 | 18.982 | 4.2 | 4.772 | 8.972 | 8.972 | 0.36664 | 0.46812 | 12.7595 | 12.7173 | 6.7912 | 84.8403 | 0.1499 | 5.711 | 5.711 | 31.9617 | 503.55 | 853.125 | 918.6109 | -7.676 | 89.21 | 711.0805 | 95.5052 | 102.007 | 45.022 | 18.982 | 1.08 | 3.983 | 5.063 | 5.063 | 0.18099 | 0.21331 | 9.6 | 9.5683 | 8.5236 | 46.0089 | 0.20797 | 5.711 | 5.838 | 102.528 | 853.125 | 1270.2069 | 1056.6512 | 16.8127 | 65.3874 | 954.8881 | 89.2628
[11 empty] | 1998-11-15 | 11:00 | 3916 | 29.223 | 138.221 | 44.82 | 18.87 | 0 | 15.262 | 3.983 |  | 19.245 | 19.245 | 0.79304 | 0 | 13.8745 | 13.7834 | 7.7418 | 64.9087 | 0.21235 | 8.402 | 5.734 | 30.3385 | 286.272 | 295.8408 | 1277.4991 | 1313.1886 | -2.7937 | 89.745 | 804.5147 | 96.229 | 138.221 | 118.822 | 18.87 | 9.562 | 8.966 | 18.528 | 18.528 | 0.36672 | 0.51608 | 14.5246 | 14.4291 | 4.2815 | 105.37 | 0.13694 | 5.734 | 5.734 | 16.5945 | 295.8408 | 505.8 | 593.6495 | -17.3684 | 94.3907 | 444.7452 | 96.2688 | 118.822 | 101.662 | 18.87 | 4.56 | 4.406 | 8.966 | 8.966 | 0.35672 | 0.50859 | 13.8532 | 13.7622 | 7.191 | 84.181 | 0.16348 | 5.734 | 5.734 | 31.9231 | 505.8 | 844.48 | 996.24 | -17.9708 | 89.2094 | 751.02 | 95.7494 | 101.662 | 44.82 | 18.87 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0668 | 8.482 | 45.889 | 0.21937 | 5.734 | 6.015 | 102.4675 | 844.48 | 1277.4991 | 1056.8562 | 17.2715 | 65.364 | 950.6681 | 89.2215
[11 empty] | 1998-11-15 | 19:00 | 3924 | 29.168 | 138.342 | 44.955 | 18.868 | 0 | 15.259 | 3.983 |  | 19.242 | 19.242 | 0.793 | 0 | 13.8718 | 13.8031 | 7.7578 | 65.0227 | 0.21228 | 8.464 | 5.715 | 30.0565 | 288.336 | 296.1427 | 1270.8144 | 1315.5275 | -3.5185 | 89.8507 | 805.8351 | 96.2701 | 138.342 | 118.687 | 18.868 | 9.559 | 9.086 | 18.645 | 18.645 | 0.36988 | 0.51268 | 14.52 | 14.4481 | 4.271 | 105.3755 | 0.13711 | 5.715 | 5.715 | 16.263 | 296.1427 | 503.1 | 590.5924 | -17.3907 | 94.5084 | 443.3676 | 96.3319 | 118.687 | 101.595 | 18.868 | 4.56 | 4.526 | 9.086 | 9.086 | 0.36312 | 0.50187 | 13.8532 | 13.7845 | 7.085 | 84.188 | 0.16374 | 5.715 | 5.715 | 31.9479 | 503.1 | 849.7125 | 977.7914 | -15.0732 | 89.212 | 740.4457 | 95.6853 | 101.595 | 44.955 | 18.868 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0831 | 8.5409 | 45.8661 | 0.21984 | 5.715 | 5.967 | 102.5453 | 849.7125 | 1270.8144 | 1063.564 | 16.3085 | 65.373 | 956.6383 | 89.2807
[11 empty] | 1998-11-16 | 0:00 | 3929 | 29.159 | 138.167 | 44.947 | 19.023 | 0 | 15.26 | 3.983 |  | 19.243 | 19.243 | 0.79302 | 0 | 13.8727 | 13.8077 | 7.7583 | 64.7757 | 0.21316 | 8.386 | 5.714 | 30.033 | 288.336 | 296.1264 | 1270.8144 | 1315.6055 | -3.5246 | 89.858 | 805.866 | 96.2732 | 138.167 | 119.047 | 19.023 | 9.56 | 8.903 | 18.463 | 18.463 | 0.36501 | 0.51779 | 14.5215 | 14.4534 | 4.3018 | 105.2822 | 0.13728 | 5.714 | 5.714 | 16.224 | 296.1264 | 502.65 | 596.6843 | -18.7077 | 94.5213 | 446.4053 | 96.3656 | 119.047 | 102.052 | 19.023 | 4.56 | 4.343 | 8.903 | 8.903 | 0.35336 | 0.51219 | 13.8532 | 13.7882 | 7.1781 | 84.3484 | 0.16347 | 5.714 | 5.714 | 31.947 | 502.65 | 851.305 | 996.8719 | -17.0993 | 89.2117 | 749.7609 | 95.739 | 102.052 | 44.947 | 19.023 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.0858 | 8.5593 | 45.9172 | 0.21965 | 5.714 | 5.921 | 102.5338 | 851.305 | 1270.8144 | 1065.6156 | 16.147 | 65.375 | 958.4603 | 89.3022
[11 empty] | 1998-11-16 | 11:00 | 3940 | 28.84 | 139.159 | 45.502 | 18.886 | 0 | 15.077 | 3.983 |  | 19.06 | 19.06 | 0.79103 | 0 | 13.7064 | 13.7713 | 7.7302 | 65.7143 | 0.20956 | 8.41 | 5.732 | 32.9705 | 312.96 | 300.2064 | 1336.4455 | 1311.7845 | 1.8453 | 89.0174 | 805.9955 | 95.9093 | 139.159 | 120.06 | 18.886 | 9.497 | 8.971 | 18.468 | 18.468 | 0.36599 | 0.51424 | 14.4258 | 14.4942 | 4.3263 | 106.3972 | 0.13623 | 5.732 | 5.732 | 17.316 | 300.2064 | 546.75 | 599.6836 | -9.6815 | 94.232 | 449.945 | 96.1515 | 120.06 | 103.02 | 18.886 | 4.56 | 4.411 | 8.971 | 8.971 | 0.35698 | 0.5083 | 13.8532 | 13.9188 | 7.8033 | 84.8507 | 0.16404 | 5.732 | 5.732 | 32.3233 | 546.75 | 929.3375 | 1078.5536 | -16.0562 | 89.233 | 812.6518 | 96.0225 | 103.02 | 45.502 | 18.886 | 1.02 | 3.983 | 5.003 | 5.003 | 0.17979 | 0.20388 | 9.0667 | 9.1096 | 9.2997 | 46.0753 | 0.19771 | 5.732 | 6.092 | 104.9242 | 929.3375 | 1336.4455 | 1140.4602 | 14.6647 | 65.0493 | 1034.8988 | 89.8614
[11 empty] | 1998-11-16 | 19:00 | 3948 | 28.836 | 139.521 | 51.757 | 19.066 | 0 | 15.377 | 3.944 |  | 19.321 | 19.321 | 0.79587 | 0 | 13.9791 | 14.047 | 7.8749 | 68.6981 | 0.20447 | 8.377 | 5.7 | 33.3465 | 312.96 | 300.3451 | 1346.1687 | 1341.3283 | 0.35957 | 88.8973 | 820.8367 | 95.9375 | 139.521 | 120.562 | 19.066 | 9.557 | 8.723 | 18.28 | 18.28 | 0.36017 | 0.52281 | 14.517 | 14.5875 | 4.3813 | 106.5942 | 0.13685 | 5.7 | 5.7 | 17.277 | 300.3451 | 554.4 | 610.4772 | -10.1149 | 94.2476 | 455.4112 | 96.2063 | 120.562 | 104.1 | 19.066 | 4.62 | 4.103 | 8.723 | 8.723 | 0.34215 | 0.52963 | 14.0354 | 14.1036 | 8.1557 | 85.1093 | 0.16571 | 5.7 | 5.7 | 32.6002 | 554.4 | 957.32 | 1141.9494 | -19.2861 | 89.1458 | 848.1747 | 96.1564 | 104.1 | 51.757 | 19.066 | 1.2 | 3.944 | 5.144 | 5.144 | 0.18183 | 0.23328 | 10.6667 | 10.7185 | 9.8207 | 49.0418 | 0.21856 | 5.7 | 5.817 | 104.9213 | 957.32 | 1346.1687 | 1216.6705 | 9.6198 | 65.0664 | 1086.9953 | 90.3476
[11 empty] | 1998-11-17 | 3:00 | 3956 | 28.866 | 138.154 | 51.037 | 17.971 | 0 | 14.477 | 3.885 |  | 18.362 | 18.362 | 0.78842 | 0 | 13.1609 | 13.2131 | 7.6381 | 68.9864 | 0.19153 | 8.401 | 5.722 | 33.6755 | 312.768 | 300.443 | 1376.5534 | 1294.5212 | 5.9592 | 88.7914 | 797.4821 | 95.7773 | 138.154 | 119.077 | 17.971 | 8.597 | 9.983 | 18.58 | 18.58 | 0.38098 | 0.4627 | 13.0587 | 13.1106 | 4.0532 | 106.5913 | 0.123 | 5.722 | 5.722 | 17.121 | 300.443 | 555.3 | 544.4298 | 1.9575 | 94.3014 | 422.4364 | 95.9471 | 119.077 | 102.697 | 17.971 | 4.62 | 5.363 | 9.983 | 9.983 | 0.40938 | 0.46279 | 14.0354 | 14.0911 | 7.4778 | 85.4382 | 0.16493 | 5.722 | 5.722 | 32.6453 | 555.3 | 964.6 | 1005.5452 | -4.2448 | 89.1343 | 780.4226 | 95.817 | 102.697 | 51.037 | 17.971 | 1.26 | 3.885 | 5.145 | 5.145 | 0.18067 | 0.2449 | 11.2 | 11.2444 | 9.9827 | 48.9133 | 0.22989 | 5.722 | 5.874 | 105.6211 | 964.6 | 1376.5534 | 1243.1877 | 9.6884 | 64.8449 | 1103.8939 | 90.4319
[11 empty] | 1998-11-17 | 11:00 | 3964.0003 | 29.151 | 137.591 | 50.452 | 18.169 | 0 | 14.422 | 3.884 |  | 18.306 | 18.306 | 0.78783 | 0 | 13.1109 | 13.0525 | 7.5775 | 68.275 | 0.19118 | 8.434 | 5.736 | 30.691 | 286.992 | 295.955 | 1308.4918 | 1280.9288 | 2.1065 | 89.6298 | 788.4419 | 96.1074 | 137.591 | 118.372 | 18.169 | 8.602 | 9.977 | 18.579 | 18.579 | 0.38089 | 0.463 | 13.0663 | 13.0081 | 3.9993 | 105.8132 | 0.12293 | 5.736 | 5.736 | 16.497 | 295.955 | 508.95 | 536.899 | -5.4915 | 94.4258 | 416.427 | 96.0384 | 118.372 | 102.007 | 18.169 | 4.62 | 5.357 | 9.977 | 9.977 | 0.40906 | 0.46307 | 14.0354 | 13.9729 | 6.8231 | 85.1974 | 0.16401 | 5.736 | 5.736 | 32.2156 | 508.95 | 876.1025 | 920.0967 | -5.0216 | 89.1147 | 714.5233 | 95.4913 | 102.007 | 50.452 | 18.169 | 1.2 | 3.884 | 5.084 | 5.084 | 0.17943 | 0.23603 | 10.6667 | 10.6192 | 8.9262 | 49.1343 | 0.21613 | 5.736 | 5.965 | 102.9254 | 876.1025 | 1308.4918 | 1114.9832 | 14.7887 | 65.2226 | 995.5428 | 89.6614
[11 empty] | 1998-11-17 | 19:00 | 3972 | 29.121 | 137.618 | 50.565 | 18.063 | 0 | 14.473 | 3.884 |  | 18.357 | 18.357 | 0.78842 | 0 | 13.1573 | 13.1103 | 7.6068 | 68.4217 | 0.19161 | 8.17 | 5.72 | 30.456 | 288.288 | 296.1346 | 1303.0222 | 1286.1361 | 1.2959 | 89.7155 | 791.1353 | 96.1503 | 137.618 | 118.425 | 18.063 | 8.653 | 9.813 | 18.466 | 18.466 | 0.37719 | 0.46859 | 13.1438 | 13.0969 | 4.0329 | 105.9256 | 0.12364 | 5.72 | 5.72 | 16.2435 | 296.1346 | 510.75 | 542.9395 | -6.3024 | 94.5148 | 419.5371 | 96.1282 | 118.425 | 102.105 | 18.063 | 4.62 | 5.193 | 9.813 | 9.813 | 0.40031 | 0.4708 | 14.0354 | 13.9853 | 6.9139 | 85.2881 | 0.16398 | 5.72 | 5.72 | 32.2258 | 510.75 | 881.5625 | 936.4735 | -6.2288 | 89.1179 | 723.6117 | 95.5465 | 102.105 | 50.565 | 18.063 | 1.2 | 3.884 | 5.084 | 5.084 | 0.17943 | 0.23603 | 10.6667 | 10.6286 | 8.989 | 49.283 | 0.21566 | 5.72 | 5.953 | 102.9427 | 881.5625 | 1303.0222 | 1122.1247 | 13.8829 | 65.2379 | 1001.8436 | 89.7247
[11 empty] | 1998-11-18 | 11:00 | 3988 | 29.24 | 133.692 | 62.445 | 19.12 | 0 | 15.195 | 2.985 |  | 18.18 | 18.18 | 0.83581 | 0 | 13.8136 | 13.716 | 9.3516 | 69.5969 | 0.19708 | 8.485 | 5.716 | 32.3125 | 286.896 | 296.0938 | 1351.0303 | 1638.8597 | -21.3044 | 89.0871 | 967.4767 | 96.6601 | 133.692 | 115.38 | 19.12 | 9.375 | 8.302 | 17.677 | 17.677 | 0.34651 | 0.53035 | 14.2405 | 14.1398 | 4.3694 | 101.0466 | 0.13993 | 5.716 | 5.716 | 16.8285 | 296.0938 | 520.65 | 611.4529 | -17.4403 | 94.3165 | 453.7733 | 96.2914 | 115.38 | 101.437 | 19.12 | 4.5 | 3.802 | 8.302 | 8.302 | 0.32289 | 0.54204 | 13.6709 | 13.5742 | 7.768 | 81.5205 | 0.16651 | 5.716 | 5.716 | 32.6462 | 520.65 | 923.65 | 1098.2452 | -18.9027 | 88.9744 | 809.4476 | 95.9669 | 101.437 | 62.445 | 19.12 | 1.32 | 2.985 | 4.305 | 4.305 | 0.14585 | 0.30662 | 11.7333 | 11.6504 | 10.0102 | 52.8108 | 0.22061 | 5.716 | 5.737 | 103.8845 | 923.65 | 1351.0303 | 1286.1594 | 4.8016 | 64.915 | 1104.9047 | 90.5979
[11 empty] | 1998-11-18 | 19:00 | 3996 | 29.176 | 133.33 | 62.647 | 19.017 | 0 | 15.259 | 2.985 |  | 18.244 | 18.244 | 0.83638 | 0 | 13.8718 | 13.7998 | 9.4078 | 69.5637 | 0.19838 | 8.421 | 5.698 | 31.725 | 288.384 | 296.2896 | 1336.4455 | 1648.7155 | -23.3657 | 89.2926 | 972.5025 | 96.7378 | 133.33 | 115.785 | 19.017 | 9.319 | 8.249 | 17.568 | 17.568 | 0.34435 | 0.53045 | 14.1554 | 14.082 | 4.3762 | 101.1643 | 0.1392 | 5.698 | 5.698 | 16.6335 | 296.2896 | 522.9 | 612.2206 | -17.0818 | 94.3861 | 454.2551 | 96.3383 | 115.785 | 101.91 | 19.017 | 4.5 | 3.749 | 8.249 | 8.249 | 0.32006 | 0.54552 | 13.6709 | 13.6 | 7.8474 | 81.9831 | 0.16589 | 5.698 | 5.698 | 32.487 | 522.9 | 933.66 | 1111.5525 | -19.0532 | 89.0354 | 817.2263 | 96.0247 | 101.91 | 62.647 | 19.017 | 1.44 | 2.985 | 4.425 | 4.425 | 0.14825 | 0.32542 | 12.8 | 12.7336 | 10.3008 | 52.9607 | 0.24043 | 5.698 | 5.741 | 103.7578 | 933.66 | 1336.4455 | 1334.0148 | 0.18187 | 64.981 | 1133.8374 | 90.849
[11 empty] | 1998-11-19 | 12:00 | 4013.0003 | 29.261 | 134.496 | 47.452 | 18.909 | 0 | 15.036 | 3.982 |  | 19.018 | 19.018 | 0.79062 | 0 | 13.6691 | 13.564 | 7.6331 | 64.4319 | 0.21052 | 8.733 | 5.736 | 31.5135 | 286.08 | 295.8163 | 1307.8838 | 1293.8216 | 1.0752 | 89.3469 | 794.819 | 96.0351 | 134.496 | 115.545 | 18.909 | 9.436 | 8.664 | 18.1 | 18.1 | 0.35698 | 0.52133 | 14.3332 | 14.223 | 4.3085 | 101.803 | 0.13971 | 5.736 | 5.736 | 16.8675 | 295.8163 | 505.8 | 599.6207 | -18.549 | 94.298 | 447.7185 | 96.2326 | 115.545 | 99.487 | 18.909 | 4.5 | 4.164 | 8.664 | 8.664 | 0.3422 | 0.51939 | 13.6709 | 13.5658 | 7.2973 | 81.3097 | 0.16684 | 5.736 | 5.736 | 32.0583 | 505.8 | 859.95 | 1017.7687 | -18.3521 | 89.1628 | 761.7843 | 95.7917 | 99.487 | 47.452 | 18.909 | 1.1 | 3.982 | 5.082 | 5.082 | 0.18135 | 0.21645 | 9.7778 | 9.7026 | 8.6102 | 45.9503 | 0.21115 | 5.736 | 5.775 | 103.4237 | 859.95 | 1307.8838 | 1068.9352 | 18.2699 | 65.0379 | 964.4426 | 89.2763
[11 empty] | 1998-11-19 | 20:00 | 4021 | 28.879 | 134.931 | 47.722 | 18.81 | 0 | 15.077 | 3.943 |  | 19.02 | 19.02 | 0.79269 | 0 | 13.7064 | 13.7555 | 7.7416 | 64.7749 | 0.21236 | 8.574 | 5.695 | 31.725 | 295.152 | 297.587 | 1314.5684 | 1314.1739 | 0.030013 | 89.3393 | 805.8805 | 96.0633 | 134.931 | 116.205 | 18.81 | 9.437 | 8.603 | 18.04 | 18.04 | 0.35537 | 0.52312 | 14.3347 | 14.386 | 4.3559 | 102.4021 | 0.14049 | 5.695 | 5.695 | 16.2825 | 297.587 | 522.9 | 606.1621 | -15.9231 | 94.5285 | 451.8746 | 96.3967 | 116.205 | 100.185 | 18.81 | 4.5 | 4.103 | 8.603 | 8.603 | 0.33895 | 0.52307 | 13.6709 | 13.7199 | 7.5973 | 81.7877 | 0.16775 | 5.695 | 5.695 | 32.2377 | 522.9 | 897.9425 | 1061.038 | -18.1632 | 89.167 | 791.969 | 95.9294 | 100.185 | 47.722 | 18.81 | 1.14 | 3.943 | 5.083 | 5.083 | 0.18059 | 0.22428 | 10.1333 | 10.1696 | 9.0871 | 46.0564 | 0.22081 | 5.695 | 5.477 | 104.0083 | 897.9425 | 1314.5684 | 1127.4847 | 14.2316 | 65.0494 | 1012.7136 | 89.7297
[11 empty] | 1998-11-20 | 4:00 | 4029 | 28.828 | 135.172 | 47.805 | 18.735 | 0 | 14.832 | 3.983 |  | 18.815 | 18.815 | 0.78831 | 0 | 13.4836 | 13.5524 | 7.6171 | 65.1364 | 0.20806 | 8.48 | 5.681 | 31.2785 | 293.328 | 297.432 | 1303.0222 | 1288.5414 | 1.1113 | 89.4838 | 792.9867 | 96.0556 | 135.172 | 116.775 | 18.735 | 9.372 | 8.665 | 18.037 | 18.037 | 0.35616 | 0.5196 | 14.2359 | 14.3085 | 4.3331 | 102.9054 | 0.13905 | 5.681 | 5.681 | 16.2045 | 297.432 | 522.45 | 601.6056 | -15.1508 | 94.5519 | 449.5188 | 96.3951 | 116.775 | 100.2 | 18.735 | 4.5 | 4.165 | 8.665 | 8.665 | 0.34226 | 0.51933 | 13.6709 | 13.7406 | 7.5508 | 82.2017 | 0.16716 | 5.681 | 5.681 | 32.2083 | 522.45 | 893.3925 | 1052.1229 | -17.7672 | 89.1712 | 787.2865 | 95.909 | 100.2 | 47.805 | 18.735 | 0.96 | 3.983 | 4.943 | 4.943 | 0.17858 | 0.19421 | 8.5333 | 8.5768 | 8.8497 | 46.4178 | 0.18477 | 5.681 | 5.387 | 103.5994 | 893.3925 | 1303.0222 | 1083.7519 | 16.8278 | 65.1687 | 988.5722 | 89.5203
[11 empty] | 1998-11-20 | 12:00 | 4037.0003 | 28.887 | 135.199 | 47.782 | 18.81 | 0 | 14.955 | 3.942 |  | 18.897 | 18.897 | 0.7914 | 0 | 13.5955 | 13.6409 | 7.6903 | 64.9902 | 0.20989 | 6.992 | 5.707 | 31.5135 | 292.176 | 296.9832 | 1309.0993 | 1304.1114 | 0.38102 | 89.3888 | 800.5473 | 96.0635 | 135.199 | 116.302 | 18.81 | 9.375 | 8.724 | 18.099 | 18.099 | 0.35777 | 0.51798 | 14.2405 | 14.2882 | 4.3107 | 102.6298 | 0.13922 | 5.707 | 5.707 | 16.575 | 296.9832 | 521.1 | 598.3159 | -14.8179 | 94.4189 | 447.6496 | 96.2973 | 116.302 | 100.185 | 18.81 | 4.44 | 4.284 | 8.724 | 8.724 | 0.34701 | 0.50894 | 13.4886 | 13.5337 | 7.423 | 82.0105 | 0.16502 | 5.707 | 5.707 | 32.1687 | 521.1 | 880.1975 | 1027.8355 | -16.7733 | 89.1682 | 774.4678 | 95.8463 | 100.185 | 47.782 | 18.81 | 1.14 | 3.942 | 5.082 | 5.082 | 0.18055 | 0.22432 | 10.1333 | 10.1672 | 8.8897 | 46.2838 | 0.21967 | 5.707 | 5.662 | 103.5302 | 880.1975 | 1309.0993 | 1104.8045 | 15.6058 | 65.1394 | 992.501 | 89.5688
[11 empty] | 1998-11-20 | 20:00 | 4045 | 28.73 | 135.682 | 48.03 | 18.751 | 0 | 14.897 | 3.982 |  | 18.879 | 18.879 | 0.78908 | 0 | 13.5427 | 13.6512 | 7.6552 | 65.4498 | 0.20858 | 6.98 | 5.716 | 33.3935 | 310.416 | 300.0758 | 1357.715 | 1297.7571 | 4.4161 | 88.8716 | 798.9165 | 95.8202 | 135.682 | 116.887 | 18.751 | 9.377 | 8.897 | 18.274 | 18.274 | 0.36241 | 0.51313 | 14.2435 | 14.3577 | 4.3174 | 103.2161 | 0.1391 | 5.716 | 5.716 | 17.3355 | 300.0758 | 551.25 | 598.0702 | -8.4935 | 94.223 | 449.073 | 96.1397 | 116.887 | 100.762 | 18.751 | 4.44 | 4.457 | 8.897 | 8.897 | 0.35624 | 0.49904 | 13.4886 | 13.5967 | 7.772 | 82.3015 | 0.16521 | 5.716 | 5.716 | 32.4548 | 551.25 | 941.85 | 1068.0664 | -13.4009 | 89.1845 | 809.6582 | 95.9915 | 100.762 | 48.03 | 18.751 | 1.08 | 3.982 | 5.062 | 5.062 | 0.18095 | 0.21335 | 9.6 | 9.6769 | 9.4996 | 46.1454 | 0.20971 | 5.716 | 5.791 | 105.3274 | 941.85 | 1357.715 | 1168.7321 | 13.9192 | 64.8998 | 1055.291 | 90.0191
[11 empty] | 1998-11-21 | 4:00 | 4053 | 28.675 | 135.735 | 48.15 | 18.708 | 0 | 14.896 | 3.944 |  | 18.84 | 18.84 | 0.79066 | 0 | 13.5418 | 13.6725 | 7.714 | 65.5205 | 0.20868 | 6.986 | 5.689 | 33.2055 | 310.992 | 300.2717 | 1343.7376 | 1308.9476 | 2.589 | 88.9415 | 804.6096 | 95.8731 | 135.735 | 117.067 | 18.708 | 9.316 | 8.787 | 18.103 | 18.103 | 0.35866 | 0.51461 | 14.1509 | 14.2875 | 4.3385 | 103.3545 | 0.13824 | 5.689 | 5.689 | 16.731 | 300.2717 | 549.45 | 600.8822 | -9.3607 | 94.428 | 450.577 | 96.2868 | 117.067 | 100.942 | 18.708 | 4.44 | 4.347 | 8.787 | 8.787 | 0.35037 | 0.50529 | 13.4886 | 13.6188 | 7.8101 | 82.4864 | 0.1651 | 5.689 | 5.689 | 32.4659 | 549.45 | 943.8975 | 1077.4945 | -14.1538 | 89.1878 | 813.4723 | 96.009 | 100.942 | 48.15 | 18.708 | 1.14 | 3.944 | 5.084 | 5.084 | 0.18063 | 0.22423 | 10.1333 | 10.2311 | 9.5995 | 46.2385 | 0.22127 | 5.689 | 5.482 | 105.1603 | 943.8975 | 1343.7376 | 1186.3317 | 11.714 | 64.9783 | 1065.1146 | 90.1269
[11 empty] | 1998-11-21 | 12:00 | 4061 | 28.802 | 135.615 | 48.112 | 18.735 | 0 | 14.837 | 3.883 |  | 18.72 | 18.72 | 0.79257 | 0 | 13.4882 | 13.5674 | 7.7457 | 65.3828 | 0.20751 | 7.003 | 5.72 | 33.605 | 309.12 | 299.7331 | 1352.2453 | 1316.6126 | 2.6351 | 88.7884 | 808.1728 | 95.8419 | 135.615 | 116.79 | 18.735 | 9.377 | 8.722 | 18.099 | 18.099 | 0.35774 | 0.51809 | 14.2435 | 14.3272 | 4.3435 | 103.124 | 0.13893 | 5.72 | 5.72 | 17.238 | 299.7331 | 549 | 603.4429 | -9.9167 | 94.2489 | 451.588 | 96.1828 | 116.79 | 100.837 | 18.735 | 4.5 | 4.222 | 8.722 | 8.722 | 0.3453 | 0.51594 | 13.6709 | 13.7511 | 7.9186 | 82.1599 | 0.16737 | 5.72 | 5.72 | 32.4282 | 549 | 931.84 | 1099.5858 | -18.0016 | 89.181 | 824.2929 | 96.0659 | 100.837 | 48.112 | 18.735 | 0.96 | 3.883 | 4.843 | 4.843 | 0.17458 | 0.19822 | 8.5333 | 8.5834 | 9.2905 | 46.449 | 0.18479 | 5.72 | 5.775 | 105.0019 | 931.84 | 1352.2453 | 1136.2604 | 15.9723 | 64.9682 | 1034.0502 | 89.8456
[11 empty] | 1998-11-22 | 2:36 | 4075.5939 | 28.709 | 131.025 | 54.975 | 18.255 | 0 | 14.477 | 3.406 |  | 17.883 | 17.883 | 0.80954 | 0 | 13.1609 | 13.2746 | 8.314 | 66.431 | 0.19983 | 7.001 | 5.68 | 34.1455 | 310.272 | 300.1738 | 1377.769 | 1430.911 | -3.8571 | 88.6248 | 865.5424 | 96.055 | 131.025 | 113.01 | 18.255 | 9.017 | 8.423 | 17.44 | 17.44 | 0.34497 | 0.51703 | 13.6967 | 13.815 | 4.3441 | 99.4184 | 0.13896 | 5.68 | 5.68 | 17.2185 | 300.1738 | 554.4 | 603.0834 | -8.7813 | 94.2638 | 451.6286 | 96.1875 | 113.01 | 98.625 | 18.255 | 4.32 | 4.103 | 8.423 | 8.423 | 0.33415 | 0.51288 | 13.1241 | 13.2374 | 7.962 | 79.6005 | 0.1663 | 5.68 | 5.68 | 32.7952 | 554.4 | 973.0175 | 1103.5915 | -13.4195 | 89.0746 | 828.9957 | 96.044 | 98.625 | 54.975 | 18.255 | 1.14 | 3.406 | 4.546 | 4.546 | 0.1591 | 0.25077 | 10.1333 | 10.2209 | 10.1273 | 48.4177 | 0.2111 | 5.68 | 5.487 | 105.4742 | 973.0175 | 1377.769 | 1263.3872 | 8.302 | 64.8623 | 1118.2024 | 90.5675
[11 empty] | 1998-11-22 | 4:00 | 4077 | 28.726 | 130.891 | 54.712 | 18.267 | 0 | 14.838 | 3.345 |  | 18.183 | 18.183 | 0.81604 | 0 | 13.4891 | 13.5988 | 8.5601 | 65.9744 | 0.20612 | 6.91 | 5.673 | 34.169 | 310.368 | 300.1819 | 1367.4377 | 1480.1818 | -8.2449 | 88.6172 | 890.1819 | 96.1616 | 130.891 | 112.995 | 18.267 | 9.078 | 8.305 | 17.383 | 17.383 | 0.34263 | 0.52223 | 13.7894 | 13.9015 | 4.3761 | 99.2999 | 0.14 | 5.673 | 5.673 | 17.2185 | 300.1819 | 555.3 | 609.4826 | -9.7574 | 94.264 | 454.8322 | 96.2143 | 112.995 | 98.505 | 18.267 | 4.32 | 3.985 | 8.305 | 8.305 | 0.32785 | 0.52017 | 13.1241 | 13.2308 | 8.0572 | 79.4258 | 0.16658 | 5.673 | 5.673 | 32.7962 | 555.3 | 973.245 | 1121.7283 | -15.2565 | 89.0746 | 838.5141 | 96.0888 | 98.505 | 54.712 | 18.267 | 1.44 | 3.345 | 4.785 | 4.785 | 0.16266 | 0.30094 | 12.8 | 12.9041 | 10.5456 | 47.7959 | 0.26998 | 5.673 | 5.399 | 105.4742 | 973.245 | 1367.4377 | 1346.8145 | 1.5082 | 64.8632 | 1160.0297 | 90.9076
[11 empty] | 1998-11-22 | 12:00 | 4085 | 28.798 | 130.523 | 54.802 | 18.208 | 0 | 14.837 | 3.405 |  | 18.242 | 18.242 | 0.81334 | 0 | 13.4882 | 13.569 | 8.4396 | 66.0149 | 0.20554 | 6.952 | 5.696 | 34.31 | 308.064 | 299.8147 | 1381.415 | 1456.7291 | -5.452 | 88.5563 | 878.2719 | 96.0935 | 130.523 | 112.8 | 18.208 | 9.077 | 8.305 | 17.382 | 17.382 | 0.34262 | 0.52221 | 13.7878 | 13.8704 | 4.3673 | 99.0862 | 0.13998 | 5.696 | 5.696 | 17.4135 | 299.8147 | 551.7 | 608.4668 | -10.2894 | 94.1919 | 454.1408 | 96.1656 | 112.8 | 98.302 | 18.208 | 4.32 | 3.985 | 8.305 | 8.305 | 0.32785 | 0.52017 | 13.1241 | 13.2026 | 8.0021 | 79.3409 | 0.1664 | 5.696 | 5.696 | 32.7676 | 551.7 | 964.8275 | 1114.2565 | -15.4876 | 89.0707 | 832.9783 | 96.0662 | 98.302 | 54.802 | 18.208 | 1.44 | 3.405 | 4.845 | 4.845 | 0.16506 | 0.29721 | 12.8 | 12.8767 | 10.4116 | 47.9324 | 0.26864 | 5.696 | 5.633 | 105.3965 | 964.8275 | 1381.415 | 1328.2873 | 3.8459 | 64.8461 | 1146.5574 | 90.8076
[11 empty] | 1998-11-22 | 20:00 | 4093 | 28.764 | 130.878 | 54.855 | 18.193 | 0 | 14.537 | 3.345 |  | 17.882 | 17.882 | 0.81294 | 0 | 13.2155 | 13.308 | 8.4316 | 66.2419 | 0.2009 | 6.949 | 5.689 | 34.169 | 309.552 | 299.9045 | 1368.0457 | 1454.7615 | -6.3387 | 88.6067 | 877.333 | 96.1054 | 130.878 | 113.047 | 18.193 | 9.017 | 8.551 | 17.568 | 17.568 | 0.34838 | 0.51326 | 13.6967 | 13.7926 | 4.3164 | 99.4531 | 0.13868 | 5.689 | 5.689 | 17.277 | 299.9045 | 554.85 | 597.9342 | -7.765 | 94.2392 | 448.9193 | 96.1514 | 113.047 | 98.572 | 18.193 | 4.32 | 4.231 | 8.551 | 8.551 | 0.34098 | 0.5052 | 13.1241 | 13.2159 | 7.886 | 79.7305 | 0.16576 | 5.689 | 5.689 | 32.7796 | 554.85 | 965.965 | 1087.9023 | -12.6234 | 89.07 | 821.3761 | 96.0092 | 98.572 | 54.855 | 18.193 | 1.2 | 3.345 | 4.545 | 4.545 | 0.15786 | 0.26403 | 10.6667 | 10.7413 | 10.1501 | 48.3704 | 0.22206 | 5.689 | 5.577 | 105.3274 | 965.965 | 1368.0457 | 1274.7139 | 6.8223 | 64.8797 | 1120.3395 | 90.5986
[11 empty] | 1998-11-23 | 4:00 | 4101.0003 | 28.726 | 131.521 | 55.08 | 18.397 | 0 | 14.478 | 3.345 |  | 17.823 | 17.823 | 0.81232 | 0 | 13.1618 | 13.2689 | 8.4087 | 66.4948 | 0.19955 | 6.896 | 5.708 | 34.122 | 309.456 | 299.8718 | 1366.8302 | 1450.1039 | -6.0925 | 88.6211 | 874.9879 | 96.1003 | 131.521 | 113.19 | 18.397 | 9.018 | 8.662 | 17.68 | 17.68 | 0.35135 | 0.51007 | 13.6982 | 13.8096 | 4.2985 | 99.66 | 0.13857 | 5.708 | 5.708 | 17.1795 | 299.8718 | 553.95 | 594.1826 | -7.2629 | 94.2711 | 447.0272 | 96.1569 | 113.19 | 98.97 | 18.397 | 4.32 | 4.342 | 8.662 | 8.662 | 0.3469 | 0.49873 | 13.1241 | 13.2308 | 7.8044 | 79.8786 | 0.16564 | 5.708 | 5.708 | 32.7778 | 553.95 | 964.6 | 1072.4816 | -11.1841 | 89.0694 | 813.2158 | 95.9694 | 98.97 | 55.08 | 18.397 | 1.14 | 3.345 | 4.485 | 4.485 | 0.15666 | 0.25418 | 10.1333 | 10.2157 | 10.0577 | 48.5703 | 0.21033 | 5.708 | 5.586 | 105.2669 | 964.6 | 1366.8302 | 1257.4669 | 8.0012 | 64.896 | 1111.0334 | 90.5253
[11 empty] | 1998-11-23 | 12:00 | 4109 | 28.798 | 130.871 | 54.81 | 18.28 | 0 | 14.478 | 3.405 |  | 17.883 | 17.883 | 0.8096 | 0 | 13.1618 | 13.2406 | 8.2946 | 66.2659 | 0.19981 | 6.92 | 5.701 | 34.357 | 307.536 | 299.7005 | 1371.6918 | 1427.9363 | -4.1004 | 88.5362 | 863.8184 | 96.0227 | 130.871 | 113.017 | 18.28 | 9.018 | 8.658 | 17.676 | 17.676 | 0.35125 | 0.51018 | 13.6982 | 13.7803 | 4.2918 | 99.3722 | 0.13867 | 5.701 | 5.701 | 17.4915 | 299.7005 | 552.15 | 593.6437 | -7.5149 | 94.1637 | 446.6721 | 96.084 | 113.017 | 98.565 | 18.28 | 4.32 | 4.338 | 8.658 | 8.658 | 0.34669 | 0.49896 | 13.1241 | 13.2026 | 7.7803 | 79.7307 | 0.16559 | 5.701 | 5.701 | 32.7419 | 552.15 | 961.6425 | 1069.4029 | -11.2059 | 89.0751 | 810.7764 | 95.9617 | 98.565 | 54.81 | 18.28 | 1.14 | 3.405 | 4.545 | 4.545 | 0.15906 | 0.25083 | 10.1333 | 10.194 | 9.9999 | 48.4076 | 0.21059 | 5.701 | 5.697 | 105.048 | 961.6425 | 1371.6918 | 1248.4318 | 8.986 | 64.949 | 1105.0372 | 90.4937
[11 empty] | 1998-11-23 | 20:00 | 4117.0003 | 28.768 | 130.657 | 54.577 | 18.298 | 0 | 14.598 | 3.406 |  | 18.004 | 18.004 | 0.81082 | 0 | 13.2709 | 13.3622 | 8.3697 | 65.9493 | 0.20261 | 6.894 | 5.656 | 33.7695 | 308.688 | 300.0677 | 1357.715 | 1441.4126 | -6.1646 | 88.746 | 870.7401 | 96.1217 | 130.657 | 112.83 | 18.298 | 9.078 | 8.302 | 17.38 | 17.38 | 0.34255 | 0.52232 | 13.7894 | 13.8843 | 4.3789 | 99.0666 | 0.14015 | 5.656 | 5.656 | 16.965 | 300.0677 | 554.85 | 609.6324 | -9.8734 | 94.3463 | 454.85 | 96.2702 | 112.83 | 98.385 | 18.298 | 4.32 | 3.982 | 8.302 | 8.302 | 0.32769 | 0.52036 | 13.1241 | 13.2144 | 8.0524 | 79.2571 | 0.16673 | 5.656 | 5.656 | 32.7962 | 554.85 | 969.3775 | 1121.2168 | -15.6636 | 89.0704 | 838.0334 | 96.0865 | 98.385 | 54.577 | 18.298 | 1.2 | 3.406 | 4.606 | 4.606 | 0.1603 | 0.26053 | 10.6667 | 10.7401 | 10.1686 | 48.0144 | 0.22368 | 5.656 | 5.2 | 104.8205 | 969.3775 | 1357.715 | 1273.9777 | 6.1675 | 65.0677 | 1121.6776 | 90.655
[11 empty] | 1998-11-24 | 4:00 | 4125.0003 | 28.764 | 130.087 | 54.24 | 18.298 | 0 | 14.357 | 3.285 |  | 17.642 | 17.642 | 0.8138 | 0 | 13.0518 | 13.1432 | 8.5142 | 65.3513 | 0.20112 | 6.928 | 5.595 | 29.4925 | 287.136 | 296.7955 | 1258.0531 | 1465.0358 | -16.4526 | 90.063 | 880.9157 | 96.6521 | 130.087 | 111.885 | 18.298 | 9.077 | 8.372 | 17.449 | 17.449 | 0.34441 | 0.5202 | 13.7878 | 13.8844 | 4.3511 | 98.3369 | 0.14119 | 5.595 | 5.595 | 14.6445 | 296.7955 | 521.55 | 602.7063 | -15.5606 | 95.0658 | 449.7509 | 96.7439 | 111.885 | 97.365 | 18.298 | 4.26 | 4.112 | 8.372 | 8.372 | 0.33303 | 0.50884 | 12.9418 | 13.0324 | 7.4226 | 78.9044 | 0.16517 | 5.595 | 5.595 | 32.579 | 521.55 | 924.105 | 1028.1201 | -11.2558 | 89.0231 | 774.8351 | 95.7954 | 97.365 | 54.24 | 18.298 | 1.02 | 3.285 | 4.305 | 4.305 | 0.15186 | 0.23693 | 9.0667 | 9.1301 | 9.4873 | 48.0172 | 0.19014 | 5.595 | 4.691 | 102.8765 | 924.105 | 1258.0531 | 1179.0983 | 6.276 | 65.3376 | 1051.6017 | 90.2172
[11 empty] | 1998-11-24 | 12:00 | 4133.0003 | 28.794 | 130.844 | 54.847 | 18.298 | 0 | 14.535 | 3.345 |  | 17.88 | 17.88 | 0.81292 | 0 | 13.2136 | 13.2943 | 8.4551 | 66.0924 | 0.20115 | 6.897 | 5.638 | 30.7615 | 291.504 | 297.2606 | 1290.8684 | 1455.2771 | -12.7363 | 89.6517 | 876.2689 | 96.4895 | 130.844 | 113.04 | 18.298 | 9.015 | 8.427 | 17.442 | 17.442 | 0.34505 | 0.51686 | 13.6937 | 13.7773 | 4.3148 | 99.3292 | 0.1387 | 5.638 | 5.638 | 16.146 | 297.2606 | 522 | 597.9903 | -14.5575 | 94.5684 | 447.6254 | 96.393 | 113.04 | 98.572 | 18.298 | 4.32 | 4.107 | 8.427 | 8.427 | 0.33436 | 0.51264 | 13.1241 | 13.2042 | 7.4699 | 80.0381 | 0.16497 | 5.638 | 5.638 | 32.4668 | 522 | 912.5025 | 1036.9217 | -13.6349 | 89.078 | 779.4609 | 95.8347 | 98.572 | 54.847 | 18.298 | 1.2 | 3.345 | 4.545 | 4.545 | 0.15786 | 0.26403 | 10.6667 | 10.7318 | 9.5497 | 48.8618 | 0.21964 | 5.638 | 5.51 | 102.7757 | 912.5025 | 1290.8684 | 1202.9875 | 6.8079 | 65.4257 | 1057.745 | 90.2835
[11 empty] | 1998-11-24 | 20:00 | 4141 | 28.789 | 130.436 | 54.645 | 18.291 | 0 | 14.534 | 3.346 |  | 17.88 | 17.88 | 0.81286 | 0 | 13.2127 | 13.2954 | 8.4666 | 65.7829 | 0.20211 | 6.938 | 5.641 | 30.2915 | 291.36 | 297.2198 | 1278.7146 | 1456.6749 | -13.9171 | 89.8084 | 876.9473 | 96.5458 | 130.436 | 112.74 | 18.291 | 9.014 | 8.555 | 17.569 | 17.569 | 0.34845 | 0.51306 | 13.6922 | 13.7778 | 4.2981 | 98.9989 | 0.13917 | 5.641 | 5.641 | 15.717 | 297.2198 | 525.6 | 593.8261 | -12.9806 | 94.712 | 445.523 | 96.4722 | 112.74 | 98.347 | 18.291 | 4.32 | 4.235 | 8.555 | 8.555 | 0.34119 | 0.50497 | 13.1241 | 13.2062 | 7.4463 | 79.8062 | 0.16548 | 5.641 | 5.641 | 32.4815 | 525.6 | 915.915 | 1028.6158 | -12.3047 | 89.0716 | 777.1079 | 95.8202 | 98.347 | 54.645 | 18.291 | 1.2 | 3.346 | 4.546 | 4.546 | 0.1579 | 0.26397 | 10.6667 | 10.7334 | 9.5909 | 48.6141 | 0.22079 | 5.641 | 5.23 | 102.6576 | 915.915 | 1278.7146 | 1207.5793 | 5.563 | 65.4607 | 1061.7472 | 90.3313
[11 empty] | 1998-11-25 | 4:00 | 4149 | 28.794 | 130.529 | 54.892 | 18.375 | 0 | 14.417 | 3.285 |  | 17.702 | 17.702 | 0.81443 | 0 | 13.1064 | 13.1864 | 8.5402 | 65.7953 | 0.20042 | 6.897 | 5.627 | 29.892 | 291.456 | 297.2443 | 1268.9914 | 1470.5833 | -15.886 | 89.9436 | 883.9138 | 96.6182 | 130.529 | 112.912 | 18.375 | 9.077 | 8.366 | 17.443 | 17.443 | 0.34425 | 0.52038 | 13.7878 | 13.8721 | 4.3422 | 99.0033 | 0.14012 | 5.627 | 5.627 | 15.7365 | 297.2443 | 524.7 | 602.6766 | -14.8612 | 94.7059 | 449.9605 | 96.5027 | 112.912 | 98.302 | 18.375 | 4.26 | 4.106 | 8.366 | 8.366 | 0.33271 | 0.5092 | 12.9418 | 13.0208 | 7.4751 | 79.7569 | 0.16326 | 5.627 | 5.627 | 32.5156 | 524.7 | 920.2375 | 1035.3444 | -12.5084 | 89.061 | 780.0222 | 95.8315 | 98.302 | 54.892 | 18.375 | 1.08 | 3.285 | 4.365 | 4.365 | 0.15306 | 0.24742 | 9.6 | 9.6586 | 9.5261 | 48.6959 | 0.19835 | 5.627 | 5.119 | 102.1162 | 920.2375 | 1268.9914 | 1189.2089 | 6.2871 | 65.6457 | 1054.7232 | 90.3182
[11 empty] | 1998-11-25 | 12:00 | 4157 | 28.904 | 131.173 | 55.057 | 18.136 | 0 | 14.474 | 3.405 |  | 17.879 | 17.879 | 0.80955 | 0 | 13.1582 | 13.1956 | 8.2766 | 66.7024 | 0.19783 | 6.889 | 5.762 | 31.349 | 290.112 | 296.1672 | 1306.0607 | 1421.8584 | -8.8662 | 89.4151 | 859.0128 | 96.3506 | 131.173 | 113.325 | 18.136 | 9.014 | 8.249 | 17.263 | 17.263 | 0.34028 | 0.52216 | 13.6922 | 13.7311 | 4.3217 | 99.7913 | 0.1376 | 5.762 | 5.762 | 16.692 | 296.1672 | 515.7 | 601.5605 | -16.6493 | 94.364 | 448.8639 | 96.2813 | 113.325 | 98.925 | 18.136 | 4.44 | 3.809 | 8.249 | 8.249 | 0.32166 | 0.53825 | 13.4886 | 13.5269 | 7.6497 | 80.3393 | 0.16837 | 5.762 | 5.762 | 32.407 | 515.7 | 898.3975 | 1079.0555 | -20.1089 | 89.0579 | 797.3777 | 95.9358 | 98.925 | 55.057 | 18.136 | 1.02 | 3.405 | 4.425 | 4.425 | 0.15666 | 0.23051 | 9.0667 | 9.0924 | 9.1433 | 49.7117 | 0.1829 | 5.762 | 6.121 | 103.1789 | 898.3975 | 1306.0607 | 1136.6128 | 12.974 | 65.1619 | 1017.5051 | 89.8596
[11 empty] | 1998-11-25 | 20:00 | 4165 | 28.998 | 131.374 | 55.065 | 18.231 | 0 | 14.598 | 3.345 |  | 17.943 | 17.943 | 0.81358 | 0 | 13.2709 | 13.2717 | 8.44 | 66.5485 | 0.19943 | 6.764 | 5.764 | 32.0305 | 296.688 | 297.2688 | 1334.0149 | 1454.802 | -9.0544 | 89.2251 | 876.0354 | 96.3437 | 131.374 | 113.557 | 18.231 | 9.078 | 8.242 | 17.32 | 17.32 | 0.34095 | 0.52413 | 13.7894 | 13.7902 | 4.3434 | 99.8911 | 0.13805 | 5.764 | 5.764 | 17.1795 | 297.2688 | 522.45 | 605.768 | -15.9476 | 94.2209 | 451.5184 | 96.1952 | 113.557 | 98.82 | 18.231 | 4.32 | 3.922 | 8.242 | 8.242 | 0.32449 | 0.52414 | 13.1241 | 13.1248 | 7.5978 | 80.3597 | 0.16333 | 5.764 | 5.764 | 32.5008 | 522.45 | 916.825 | 1062.1186 | -15.8475 | 89.0669 | 792.2843 | 95.8978 | 98.82 | 55.065 | 18.231 | 1.2 | 3.345 | 4.545 | 4.545 | 0.15786 | 0.26403 | 10.6667 | 10.6673 | 9.5874 | 49.1241 | 0.21715 | 5.764 | 6.115 | 103.8989 | 916.825 | 1334.0149 | 1208.4577 | 9.412 | 65.0488 | 1062.6413 | 90.2226
[11 empty] | 1998-11-26 | 4:00 | 4173 | 28.989 | 135.648 | 42.502 | 18.55 | 0 | 14.832 | 3.983 |  | 18.815 | 18.815 | 0.78831 | 0 | 13.4836 | 13.488 | 7.6225 | 62.9025 | 0.21443 | 6.804 | 5.768 | 30.738 | 295.632 | 297.0811 | 1289.6528 | 1288.8966 | 0.058637 | 89.6533 | 792.9889 | 96.1238 | 135.648 | 116.767 | 18.55 | 9.372 | 8.731 | 18.103 | 18.103 | 0.35792 | 0.5177 | 14.2359 | 14.2406 | 4.3133 | 103.3442 | 0.1378 | 5.768 | 5.768 | 16.3995 | 297.0811 | 513.45 | 598.3694 | -16.539 | 94.4798 | 447.7253 | 96.3372 | 116.767 | 99.952 | 18.55 | 4.44 | 4.291 | 8.731 | 8.731 | 0.34738 | 0.50853 | 13.4886 | 13.493 | 7.306 | 82.5035 | 0.16354 | 5.768 | 5.768 | 31.959 | 513.45 | 864.045 | 1011.6603 | -17.0842 | 89.2423 | 762.5551 | 95.809 | 99.952 | 42.502 | 18.55 | 1.02 | 3.983 | 5.003 | 5.003 | 0.17979 | 0.20388 | 9.0667 | 9.0696 | 8.5795 | 44.0975 | 0.20567 | 5.768 | 6.113 | 103.4842 | 864.045 | 1289.6528 | 1058.8158 | 17.8992 | 65.1664 | 961.4304 | 89.2364
[11 empty] | 1998-11-26 | 12:00 | 4181 | 29.163 | 135.032 | 42.127 | 18.529 | 0 | 14.833 | 3.982 |  | 18.815 | 18.815 | 0.78836 | 0 | 13.4845 | 13.4197 | 7.6083 | 62.4422 | 0.21491 | 6.239 | 5.771 | 30.9965 | 294.48 | 296.7874 | 1284.7912 | 1286.8617 | -0.16115 | 89.556 | 791.8245 | 96.0854 | 135.032 | 115.867 | 18.529 | 9.373 | 8.723 | 18.096 | 18.096 | 0.35772 | 0.51796 | 14.2375 | 14.169 | 4.31 | 102.6105 | 0.13809 | 5.771 | 5.771 | 16.419 | 296.7874 | 512.1 | 598.0476 | -16.7834 | 94.4678 | 447.4175 | 96.3303 | 115.867 | 99.315 | 18.529 | 4.44 | 4.283 | 8.723 | 8.723 | 0.34695 | 0.509 | 13.4886 | 13.4238 | 7.2905 | 81.7715 | 0.16416 | 5.771 | 5.771 | 31.9341 | 512.1 | 859.04 | 1009.8671 | -17.5576 | 89.2401 | 760.9836 | 95.8036 | 99.315 | 42.127 | 18.529 | 1.02 | 3.982 | 5.002 | 5.002 | 0.17975 | 0.20392 | 9.0667 | 9.0231 | 8.5251 | 43.6669 | 0.20663 | 5.771 | 6.124 | 103.32 | 859.04 | 1284.7912 | 1052.6197 | 18.0708 | 65.1872 | 955.8299 | 89.1905
[11 empty] | 1998-11-26 | 20:00 | 4189 | 29.074 | 135.226 | 42.127 | 18.583 | 0 | 14.65 | 3.982 |  | 18.632 | 18.632 | 0.78628 | 0 | 13.3182 | 13.2891 | 7.5609 | 62.5326 | 0.21251 | 6.221 | 5.756 | 30.4325 | 293.376 | 296.7058 | 1281.1451 | 1276.3399 | 0.37507 | 89.7432 | 786.5228 | 96.1308 | 135.226 | 116.197 | 18.583 | 9.37 | 8.792 | 18.162 | 18.162 | 0.35952 | 0.51591 | 14.2329 | 14.2018 | 4.2988 | 102.8297 | 0.13811 | 5.756 | 5.756 | 16.263 | 296.7058 | 510.75 | 595.5853 | -16.6099 | 94.5188 | 446.1455 | 96.3548 | 116.197 | 99.615 | 18.583 | 4.26 | 4.532 | 8.792 | 8.792 | 0.35544 | 0.48453 | 12.9418 | 12.9135 | 7.0386 | 82.2844 | 0.15694 | 5.756 | 5.756 | 31.9304 | 510.75 | 857.4475 | 960.8319 | -12.0572 | 89.2383 | 735.791 | 95.6604 | 99.615 | 42.127 | 18.583 | 1.02 | 3.982 | 5.002 | 5.002 | 0.17975 | 0.20392 | 9.0667 | 9.0469 | 8.5074 | 43.7806 | 0.20664 | 5.756 | 6.13 | 103.297 | 857.4475 | 1281.1451 | 1050.6252 | 17.9933 | 65.1854 | 954.0363 | 89.1726
[11 empty] | 1998-11-27 | 4:00 | 4197 | 29.176 | 138.375 | 43.185 | 19.092 | 0 | 15.192 | 3.983 |  | 19.175 | 19.175 | 0.79228 | 0 | 13.8109 | 13.7392 | 7.7368 | 63.9512 | 0.21484 | 5.905 | 5.763 | 28.6465 | 283.824 | 294.78 | 1245.8988 | 1309.8692 | -5.1345 | 90.2821 | 802.3246 | 96.4296 | 138.375 | 119.017 | 19.092 | 9.612 | 9.025 | 18.637 | 18.637 | 0.36896 | 0.51575 | 14.6005 | 14.5247 | 4.2758 | 105.3282 | 0.1379 | 5.763 | 5.763 | 15.7755 | 294.78 | 489.6 | 591.9314 | -20.901 | 94.6484 | 443.3557 | 96.4418 | 119.017 | 101.797 | 19.092 | 4.56 | 4.465 | 9.025 | 9.025 | 0.35986 | 0.50526 | 13.8532 | 13.7813 | 6.916 | 84.399 | 0.16329 | 5.763 | 5.763 | 31.7796 | 489.6 | 828.3275 | 957.1613 | -15.5535 | 89.2192 | 723.3807 | 95.6068 | 101.797 | 43.185 | 19.092 | 1.02 | 3.983 | 5.003 | 5.003 | 0.17979 | 0.20388 | 9.0667 | 9.0196 | 8.1926 | 45.2064 | 0.19952 | 5.763 | 6.188 | 102.0643 | 828.3275 | 1245.8988 | 1014.3151 | 18.5877 | 65.3761 | 921.3213 | 88.922
[11 empty] | 1998-11-27 | 12:00 | 4205 | 29.338 | 141.162 | 46.905 | 19.374 | 0 | 15.56 | 3.981 |  | 19.541 | 19.541 | 0.79627 | 0 | 14.1455 | 14.0048 | 7.8385 | 66.821 | 0.20959 | 6.958 | 5.787 | 29.046 | 281.904 | 294.372 | 1254.407 | 1331.4161 | -6.1391 | 90.1329 | 812.894 | 96.4268 | 141.162 | 121.545 | 19.374 | 9.74 | 9.136 | 18.876 | 18.876 | 0.37363 | 0.516 | 14.7949 | 14.6479 | 4.2692 | 107.7103 | 0.13599 | 5.787 | 5.787 | 15.8925 | 294.372 | 493.2 | 591.2624 | -19.8829 | 94.6012 | 442.8172 | 96.411 | 121.545 | 103.792 | 19.374 | 4.62 | 4.516 | 9.136 | 9.136 | 0.36419 | 0.50569 | 14.0354 | 13.8959 | 6.9725 | 86.322 | 0.16098 | 5.787 | 5.787 | 31.9056 | 493.2 | 834.2425 | 965.1177 | -15.6879 | 89.1615 | 729.1588 | 95.6243 | 103.792 | 46.905 | 19.374 | 1.2 | 3.981 | 5.181 | 5.181 | 0.18331 | 0.23162 | 10.6667 | 10.5606 | 8.4265 | 47.548 | 0.2221 | 5.787 | 6.296 | 101.9606 | 834.2425 | 1254.407 | 1054.9755 | 15.8985 | 65.3633 | 944.609 | 89.206
[11 empty] | 1998-11-27 | 20:00 | 4213 | 29.117 | 141.377 | 47.565 | 19.294 | 0 | 15.553 | 3.983 |  | 19.536 | 19.536 | 0.79612 | 0 | 14.1391 | 14.0903 | 7.8694 | 67.3076 | 0.20934 | 7.007 | 5.77 | 30.0095 | 294.144 | 296.5507 | 1269.5989 | 1337.353 | -5.3367 | 89.8805 | 816.9519 | 96.3267 | 141.377 | 121.927 | 19.294 | 9.733 | 9.507 | 19.24 | 19.24 | 0.38343 | 0.50587 | 14.7843 | 14.7333 | 4.2438 | 108.1142 | 0.13628 | 5.77 | 5.77 | 15.8535 | 296.5507 | 514.35 | 583.9207 | -13.5259 | 94.654 | 440.2357 | 96.3989 | 121.927 | 104.655 | 19.294 | 4.62 | 4.887 | 9.507 | 9.507 | 0.38398 | 0.48596 | 14.0354 | 13.987 | 7.1019 | 86.8951 | 0.16096 | 5.77 | 5.77 | 32.1089 | 514.35 | 877.0125 | 970.244 | -10.6306 | 89.1725 | 742.297 | 95.6744 | 104.655 | 47.565 | 19.294 | 1.2 | 3.983 | 5.183 | 5.183 | 0.18339 | 0.23153 | 10.6667 | 10.6298 | 8.9045 | 47.9115 | 0.22186 | 5.77 | 6.303 | 103.1386 | 877.0125 | 1269.5989 | 1110.1656 | 12.5578 | 65.2206 | 993.589 | 89.6196
[11 empty] | 1998-11-28 | 0:00 | 4217 | 29.066 | 141.089 | 47.587 | 19.308 | 0 | 15.13 | 3.982 |  | 19.112 | 19.112 | 0.79165 | 0 | 13.7545 | 13.7277 | 7.7359 | 67.2941 | 0.204 | 6.501 | 5.771 | 29.8685 | 293.904 | 296.6405 | 1267.7758 | 1310.2668 | -3.3516 | 89.9311 | 803.4536 | 96.2825 | 141.089 | 121.695 | 19.308 | 9.67 | 9.269 | 18.939 | 18.939 | 0.37624 | 0.51059 | 14.6886 | 14.66 | 4.2755 | 107.8085 | 0.13598 | 5.771 | 5.771 | 15.6585 | 296.6405 | 513 | 589.7784 | -14.9666 | 94.7214 | 443.2095 | 96.467 | 121.695 | 104.422 | 19.308 | 4.26 | 5.009 | 9.269 | 9.269 | 0.38089 | 0.4596 | 12.9418 | 12.9165 | 6.8539 | 86.8966 | 0.14864 | 5.771 | 5.771 | 32.1052 | 513 | 879.7425 | 921.9862 | -4.8018 | 89.1771 | 717.4931 | 95.5254 | 104.422 | 47.587 | 19.308 | 1.2 | 3.982 | 5.182 | 5.182 | 0.18335 | 0.23157 | 10.6667 | 10.6459 | 8.9363 | 47.7602 | 0.2229 | 5.771 | 6.274 | 103.127 | 879.7425 | 1267.7758 | 1113.7803 | 12.1469 | 65.235 | 996.7614 | 89.6538
[11 empty] | 1998-11-28 | 12:00 | 4229 | 29.159 | 137.015 | 45.78 | 18.724 | 0 | 15.319 | 3.982 |  | 19.301 | 19.301 | 0.79369 | 0 | 13.9264 | 13.8611 | 7.7677 | 64.9058 | 0.21356 | 6.904 | 5.785 | 30.7145 | 292.992 | 296.412 | 1288.4378 | 1318.5667 | -2.3384 | 89.6379 | 807.4893 | 96.1963 | 137.015 | 117.742 | 18.724 | 9.499 | 8.723 | 18.222 | 18.222 | 0.3594 | 0.52129 | 14.4289 | 14.3612 | 4.322 | 104.3325 | 0.13765 | 5.785 | 5.785 | 16.575 | 296.412 | 513.45 | 601.1434 | -17.0792 | 94.4081 | 448.7777 | 96.3066 | 117.742 | 101.085 | 18.724 | 4.62 | 4.103 | 8.723 | 8.723 | 0.34215 | 0.52963 | 14.0354 | 13.9696 | 7.5243 | 83.1652 | 0.16797 | 5.785 | 5.785 | 32.0519 | 513.45 | 868.8225 | 1055.5069 | -21.4871 | 89.1867 | 784.4784 | 95.9142 | 101.085 | 45.78 | 18.724 | 1.2 | 3.982 | 5.182 | 5.182 | 0.18335 | 0.23157 | 10.6667 | 10.6167 | 8.8094 | 45.8991 | 0.2313 | 5.785 | 6.231 | 103.2394 | 868.8225 | 1288.4378 | 1099.5357 | 14.6613 | 65.1703 | 984.1791 | 89.5101
[11 empty] | 1998-11-28 | 20:00 | 4237 | 29.087 | 131.226 | 43.89 | 18.105 | 0 | 14.716 | 3.983 |  | 18.699 | 18.699 | 0.78699 | 0 | 13.3782 | 13.3438 | 7.5631 | 61.8899 | 0.21561 | 6.853 | 5.758 | 31.208 | 294.144 | 296.8282 | 1301.8072 | 1278.2156 | 1.8122 | 89.4862 | 787.5219 | 96.0372 | 131.226 | 112.507 | 18.105 | 9.076 | 8.544 | 17.62 | 17.62 | 0.34898 | 0.5151 | 13.7863 | 13.7509 | 4.2869 | 99.4746 | 0.13824 | 5.758 | 5.758 | 16.848 | 296.8282 | 510.3 | 594.2415 | -16.4494 | 94.324 | 445.5349 | 96.2185 | 112.507 | 96.772 | 18.105 | 4.5 | 4.044 | 8.544 | 8.544 | 0.3358 | 0.52669 | 13.6709 | 13.6358 | 7.4441 | 79.0904 | 0.17241 | 5.758 | 5.758 | 32.0068 | 510.3 | 866.32 | 1042.5254 | -20.3395 | 89.2171 | 776.4127 | 95.8776 | 96.772 | 43.89 | 18.105 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.1073 | 8.7176 | 43.5084 | 0.23231 | 5.758 | 6.177 | 103.6944 | 866.32 | 1301.8072 | 1084.596 | 16.6854 | 65.0658 | 975.458 | 89.3697
[11 empty] | 1998-11-29 | 4:00 | 4245 | 29.036 | 138.402 | 34.845 | 18.777 | 0 | 14.834 | 3.983 |  | 18.817 | 18.817 | 0.78833 | 0 | 13.4855 | 13.4711 | 7.6394 | 60.2071 | 0.22375 | 6.789 | 5.776 | 29.8685 | 294.72 | 296.7792 | 1266.5608 | 1290.8423 | -1.9171 | 89.9358 | 793.8107 | 96.2373 | 138.402 | 118.522 | 18.777 | 9.494 | 9.44 | 18.934 | 18.934 | 0.37846 | 0.50143 | 14.4213 | 14.4059 | 4.2196 | 105.4654 | 0.13659 | 5.776 | 5.776 | 16.0095 | 296.7792 | 504.9 | 579.155 | -14.7069 | 94.6056 | 437.9671 | 96.3446 | 118.522 | 100.402 | 18.777 | 4.32 | 5.12 | 9.44 | 9.44 | 0.38841 | 0.45763 | 13.1241 | 13.1101 | 6.7281 | 83.9569 | 0.15615 | 5.776 | 5.776 | 31.7124 | 504.9 | 839.475 | 904.152 | -7.7045 | 89.3145 | 704.526 | 95.4988 | 100.402 | 34.845 | 18.777 | 1.02 | 3.983 | 5.003 | 5.003 | 0.17979 | 0.20388 | 9.0667 | 9.057 | 8.3018 | 40.5447 | 0.22338 | 5.776 | 6.273 | 103.5274 | 839.475 | 1266.5608 | 1027.9426 | 18.8399 | 65.1164 | 933.7088 | 88.9122
[11 empty] | 1998-11-29 | 12:00 | 4253 | 29.01 | 131.963 | NR | 17.787 | 0 | 14.676 | 3.982 |  | 18.658 | 18.658 | 0.78658 | 0 | 13.3418 | 13.3379 | 7.5764 | #VALUE! | #VALUE! | 6.763 | 5.772 | 32.0775 | 306.096 | 298.5907 | 1313.3529 | 1280.8479 | 2.475 | 89.257 | 789.7193 | 95.9381 | 131.963 | 112.567 | 17.787 | 9.076 | 9.089 | 18.165 | 18.165 | 0.36352 | 0.49964 | 13.7863 | 13.7823 | 4.223 | 100.255 | 0.13747 | 5.772 | 5.772 | 16.926 | 298.5907 | 522.45 | 579.8526 | -10.9872 | 94.3314 | 439.2216 | 96.1464 | 112.567 | 94.77 | 17.787 | 4.5 | 4.589 | 9.089 | 9.089 | 0.36488 | 0.4951 | 13.6709 | 13.6668 | 7.3139 | 78.5676 | 0.17395 | 5.772 | 5.772 | 31.6848 | 522.45 | 849.485 | 1003.6972 | -18.1536 | 89.3886 | 763.0736 | 95.8477 | 94.77 | 28.552 | 17.787 | 1.1 | 3.982 | 5.082 | 5.082 | 0.18135 | 0.21645 | 9.7778 | 9.7749 | 8.4683 | 35.4057 | 0.27608 | 5.772 | 6.305 | 105.4253 | 849.485 | 1313.3529 | 1055.0264 | 19.6692 | 64.6924 | 952.2557 | 88.9289
[11 empty] | 1998-11-29 | 20:00 | 4261 | 28.981 | 134.898 | 55.545 | 18.697 | 0 | 14.835 | 3.525 |  | 18.36 | 18.36 | 0.80801 | 0 | 13.4864 | 13.4939 | 8.2484 | 68.2761 | 0.19764 | 6.878 | 5.761 | 32.853 | 306 | 298.5662 | 1344.9532 | 1416.8232 | -5.3437 | 88.9964 | 857.6947 | 96.1696 | 134.898 | 116.49 | 18.697 | 9.255 | 8.725 | 17.98 | 17.98 | 0.3562 | 0.51474 | 14.0582 | 14.0661 | 4.3116 | 102.6854 | 0.13698 | 5.761 | 5.761 | 16.8285 | 298.5662 | 537.75 | 597.4181 | -11.0959 | 94.3636 | 447.9922 | 96.2436 | 116.49 | 101.782 | 18.697 | 4.44 | 4.285 | 8.725 | 8.725 | 0.34706 | 0.50888 | 13.4886 | 13.4962 | 7.6678 | 82.7712 | 0.16305 | 5.761 | 5.761 | 32.6526 | 537.75 | 948.675 | 1061.1181 | -11.8526 | 89.0635 | 799.434 | 95.9155 | 101.782 | 55.545 | 18.697 | 1.14 | 3.525 | 4.665 | 4.665 | 0.16386 | 0.24437 | 10.1333 | 10.139 | 9.7996 | 50.1669 | 0.20211 | 5.761 | 6.327 | 105.1171 | 948.675 | 1344.9532 | 1221.4852 | 9.1801 | 64.7927 | 1085.0801 | 90.3125
[11 empty] | 1998-11-30 | 4:00 | 4269.0003 | 29.066 | 134.938 | 55.342 | 18.627 | 0 | 14.897 | 3.465 |  | 18.362 | 18.362 | 0.8113 | 0 | 13.5427 | 13.5163 | 8.3627 | 68.1503 | 0.19833 | 6.281 | 5.761 | 31.161 | 294.048 | 296.6731 | 1312.7454 | 1438.1837 | -9.5554 | 89.4965 | 867.4284 | 96.4077 | 134.938 | 116.565 | 18.627 | 9.317 | 8.548 | 17.865 | 17.865 | 0.3523 | 0.52152 | 14.1524 | 14.1248 | 4.3293 | 102.7952 | 0.13741 | 5.761 | 5.761 | 16.458 | 296.6731 | 517.95 | 602.0971 | -16.2462 | 94.4525 | 449.3851 | 96.3377 | 116.565 | 101.295 | 18.627 | 4.44 | 4.108 | 8.548 | 8.548 | 0.33762 | 0.51942 | 13.4886 | 13.4623 | 7.4784 | 82.8246 | 0.16254 | 5.761 | 5.761 | 32.4668 | 517.95 | 908.4075 | 1042.6689 | -14.7799 | 89.0564 | 780.3095 | 95.8392 | 101.295 | 55.342 | 18.627 | 1.14 | 3.465 | 4.605 | 4.605 | 0.16146 | 0.24756 | 10.1333 | 10.1136 | 9.3692 | 50.3223 | 0.20098 | 5.761 | 6.339 | 103.8384 | 908.4075 | 1312.7454 | 1173.1142 | 10.6366 | 64.9991 | 1040.7609 | 90.0228
[11 empty] | 1998-11-30 | 12:00 | 4277.0003 | 29.095 | 134.69 | 55.282 | 18.78 | 0 | 14.961 | 3.464 |  | 18.425 | 18.425 | 0.81199 | 0 | 13.6009 | 13.5628 | 8.3811 | 67.8249 | 0.19997 | 6.906 | 5.765 | 31.349 | 294.336 | 296.616 | 1315.784 | 1442.3029 | -9.6155 | 89.4311 | 869.4595 | 96.3944 | 134.69 | 116.347 | 18.78 | 9.321 | 8.538 | 17.859 | 17.859 | 0.35209 | 0.52192 | 14.1585 | 14.1188 | 4.3266 | 102.4119 | 0.13786 | 5.765 | 5.765 | 16.731 | 296.616 | 519.75 | 602.1686 | -15.8574 | 94.3594 | 449.3923 | 96.277 | 116.347 | 101.22 | 18.78 | 4.44 | 4.098 | 8.538 | 8.538 | 0.33708 | 0.52003 | 13.4886 | 13.4508 | 7.5125 | 82.491 | 0.16306 | 5.765 | 5.765 | 32.4723 | 519.75 | 910.2275 | 1047.6936 | -15.1024 | 89.0524 | 783.7218 | 95.8567 | 101.22 | 55.282 | 18.78 | 1.2 | 3.464 | 4.664 | 4.664 | 0.16262 | 0.25729 | 10.6667 | 10.6368 | 9.461 | 50.01 | 0.21269 | 5.765 | 6.359 | 103.8096 | 910.2275 | 1315.784 | 1189.587 | 9.591 | 65.002 | 1049.9073 | 90.1125
[11 empty] | 1998-11-30 | 20:00 | 4285 | 29.07 | 134.375 | 55.065 | 18.628 | 0 | 14.897 | 3.525 |  | 18.422 | 18.422 | 0.80865 | 0 | 13.5427 | 13.5147 | 8.2679 | 67.8241 | 0.19926 | 6.438 | 5.753 | 31.255 | 294.24 | 296.8445 | 1313.3529 | 1419.252 | -8.0633 | 89.4709 | 858.0482 | 96.3574 | 134.375 | 116.242 | 18.628 | 9.317 | 8.665 | 17.982 | 17.982 | 0.35542 | 0.51813 | 14.1524 | 14.1232 | 4.3092 | 102.3713 | 0.13796 | 5.753 | 5.753 | 16.5945 | 296.8445 | 522.45 | 598.1819 | -14.4955 | 94.4097 | 447.5132 | 96.2918 | 116.242 | 101.077 | 18.628 | 4.5 | 4.165 | 8.665 | 8.665 | 0.34226 | 0.51933 | 13.6709 | 13.6426 | 7.5468 | 82.4847 | 0.1654 | 5.753 | 5.753 | 32.4686 | 522.45 | 913.4125 | 1051.8416 | -15.1552 | 89.0621 | 787.1458 | 95.8751 | 101.077 | 55.065 | 18.628 | 1.08 | 3.525 | 4.605 | 4.605 | 0.16266 | 0.23453 | 9.6 | 9.5802 | 9.3369 | 50.1061 | 0.1912 | 5.753 | 6.304 | 103.7549 | 913.4125 | 1313.3529 | 1161.4778 | 11.5639 | 65.0474 | 1037.4452 | 89.999
[11 empty] | 1998-12-01 | 4:00 | 4293 | 29.049 | 134.77 | 55.2 | 18.696 | 0 | 15.077 | 3.526 |  | 18.603 | 18.603 | 0.81046 | 0 | 13.7064 | 13.6865 | 8.3416 | 67.9474 | 0.20143 | 6.225 | 5.771 | 31.0905 | 295.536 | 296.9179 | 1310.3149 | 1433.5827 | -9.4075 | 89.5289 | 865.2503 | 96.4068 | 134.77 | 116.437 | 18.696 | 9.317 | 8.489 | 17.806 | 17.806 | 0.35073 | 0.52325 | 14.1524 | 14.1319 | 4.3452 | 102.5623 | 0.13779 | 5.771 | 5.771 | 16.3605 | 296.9179 | 521.1 | 604.8403 | -16.0699 | 94.4899 | 450.8791 | 96.3714 | 116.437 | 101.415 | 18.696 | 4.5 | 3.989 | 8.489 | 8.489 | 0.33287 | 0.5301 | 13.6709 | 13.6511 | 7.6423 | 82.5877 | 0.16529 | 5.771 | 5.771 | 32.4797 | 521.1 | 915.2325 | 1072.3137 | -17.163 | 89.0611 | 796.7068 | 95.9233 | 101.415 | 55.2 | 18.696 | 1.26 | 3.526 | 4.786 | 4.786 | 0.1663 | 0.26327 | 11.2 | 11.1838 | 9.5639 | 50.0476 | 0.22346 | 5.771 | 6.285 | 103.824 | 915.2325 | 1310.3149 | 1205.1856 | 8.0232 | 65.0328 | 1060.2091 | 90.2072
[11 empty] | 1998-12-01 | 12:00 | 4301 | 29.138 | 134.945 | 54.81 | 18.879 | 0 | 14.78 | 3.524 |  | 18.304 | 18.304 | 0.80747 | 0 | 13.4364 | 13.3817 | 8.1862 | 67.8123 | 0.19733 | 6.917 | 5.773 | 30.9965 | 285.936 | 295.3186 | 1306.6682 | 1403.9111 | -7.442 | 89.504 | 849.6148 | 96.3517 | 134.945 | 115.92 | 18.879 | 9.32 | 8.606 | 17.926 | 17.926 | 0.35389 | 0.51992 | 14.157 | 14.0993 | 4.2998 | 102.2537 | 0.13789 | 5.773 | 5.773 | 16.38 | 295.3186 | 508.05 | 597.3994 | -17.5867 | 94.4534 | 446.359 | 96.3303 | 115.92 | 100.687 | 18.879 | 4.44 | 4.166 | 8.606 | 8.606 | 0.34071 | 0.51592 | 13.4886 | 13.4337 | 7.2923 | 82.1322 | 0.16356 | 5.773 | 5.773 | 32.327 | 508.05 | 882.9275 | 1015.0616 | -14.9655 | 89.0535 | 761.5558 | 95.7551 | 100.687 | 54.81 | 18.879 | 1.02 | 3.524 | 4.544 | 4.544 | 0.16142 | 0.22447 | 9.0667 | 9.0298 | 8.9267 | 49.9428 | 0.1808 | 5.773 | 6.313 | 103.1098 | 882.9275 | 1306.6682 | 1108.6409 | 15.1551 | 65.0852 | 995.7842 | 89.6454
[11 empty] | 1998-12-01 | 20:00 | 4309 | 29.095 | 134.663 | 55.117 | 18.678 | 0 | 15.015 | 3.465 |  | 18.48 | 18.48 | 0.8125 | 0 | 13.65 | 13.6117 | 8.3897 | 67.8223 | 0.2007 | 6.238 | 5.769 | 30.7145 | 288.912 | 295.6531 | 1301.1991 | 1443.7205 | -10.9531 | 89.6113 | 869.6868 | 96.4683 | 134.663 | 116.182 | 18.678 | 9.315 | 8.79 | 18.105 | 18.105 | 0.35873 | 0.5145 | 14.1494 | 14.1097 | 4.2767 | 102.4678 | 0.1377 | 5.769 | 5.769 | 16.107 | 295.6531 | 509.85 | 591.8957 | -16.0921 | 94.5521 | 443.7744 | 96.3705 | 116.182 | 101.062 | 18.678 | 4.44 | 4.35 | 8.79 | 8.79 | 0.35053 | 0.50512 | 13.4886 | 13.4508 | 7.2116 | 82.7324 | 0.16258 | 5.769 | 5.769 | 32.3674 | 509.85 | 892.4825 | 997.2115 | -11.7346 | 89.0522 | 753.5308 | 95.7046 | 101.062 | 55.117 | 18.678 | 1.26 | 3.465 | 4.725 | 4.725 | 0.16386 | 0.26667 | 11.2 | 11.1686 | 9.3269 | 50.0846 | 0.22299 | 5.769 | 6.339 | 103.2826 | 892.4825 | 1301.1991 | 1179.4643 | 9.3556 | 65.0663 | 1035.9734 | 90.0304
[11 empty] | 1998-12-02 | 0:00 | 4313 | 28.913 | 135.012 | 55.357 | 18.816 | 0 | 15.078 | 3.526 |  | 18.604 | 18.604 | 0.81047 | 0 | 13.7073 | 13.7426 | 8.3173 | 68.0512 | 0.20194 | 6.194 | 5.755 | 31.1845 | 291.456 | 296.2243 | 1300.5916 | 1429.5965 | -9.9189 | 89.4727 | 862.9104 | 96.3861 | 135.012 | 116.587 | 18.816 | 9.318 | 8.61 | 17.928 | 17.928 | 0.35397 | 0.51975 | 14.1539 | 14.1904 | 4.3172 | 102.6663 | 0.13822 | 5.755 | 5.755 | 16.0875 | 296.2243 | 517.95 | 599.3968 | -15.7248 | 94.5691 | 447.8106 | 96.4075 | 116.587 | 101.692 | 18.816 | 4.5 | 4.11 | 8.61 | 8.61 | 0.33932 | 0.52265 | 13.6709 | 13.7061 | 7.5128 | 82.8107 | 0.16551 | 5.755 | 5.755 | 32.4502 | 517.95 | 904.3125 | 1049.5191 | -16.0571 | 89.0454 | 783.7345 | 95.8595 | 101.692 | 55.357 | 18.816 | 1.26 | 3.526 | 4.786 | 4.786 | 0.1663 | 0.26327 | 11.2 | 11.2288 | 9.4367 | 50.2718 | 0.22336 | 5.755 | 6.279 | 103.6886 | 904.3125 | 1300.5916 | 1190.4118 | 8.4715 | 64.9966 | 1047.3621 | 90.1
[11 empty] | 1998-12-02 | 12:00 | 4325 | 28.883 | 134.918 | 55.132 | 18.661 | 0 | 14.899 | 3.525 |  | 18.424 | 18.424 | 0.80867 | 0 | 13.5445 | 13.5915 | 8.2538 | 68.1102 | 0.19955 | 6.214 | 5.755 | 30.926 | 290.112 | 296.0366 | 1304.8452 | 1416.5709 | -8.5624 | 89.5533 | 856.3038 | 96.3884 | 134.918 | 116.565 | 18.661 | 9.319 | 8.543 | 17.862 | 17.862 | 0.35219 | 0.52172 | 14.1554 | 14.2045 | 4.3222 | 102.7583 | 0.13823 | 5.755 | 5.755 | 16.3605 | 296.0366 | 515.7 | 601.1171 | -16.5633 | 94.4735 | 448.5768 | 96.3528 | 116.565 | 101.4 | 18.661 | 4.44 | 4.103 | 8.543 | 8.543 | 0.33735 | 0.51972 | 13.4886 | 13.5353 | 7.4474 | 82.8741 | 0.16332 | 5.755 | 5.755 | 32.4392 | 515.7 | 898.8525 | 1038.6534 | -15.5533 | 89.0422 | 777.1767 | 95.826 | 101.4 | 55.132 | 18.661 | 1.14 | 3.525 | 4.665 | 4.665 | 0.16386 | 0.24437 | 10.1333 | 10.1684 | 9.2383 | 50.3667 | 0.20189 | 5.755 | 6.284 | 103.6138 | 898.8525 | 1304.8452 | 1156.0361 | 11.4043 | 64.9997 | 1027.4443 | 89.9154
[11 empty] | 1998-12-02 | 20:00 | 4333.0003 | 28.747 | 135.548 | 55.41 | 18.699 | 0 | 15.016 | 3.585 |  | 18.601 | 18.601 | 0.80727 | 0 | 13.6509 | 13.7534 | 8.2183 | 68.5617 | 0.2006 | 6.276 | 5.777 | 30.8085 | 291.6 | 296.4038 | 1301.8072 | 1408.8668 | -8.2239 | 89.6059 | 852.6353 | 96.3867 | 135.548 | 116.857 | 18.699 | 9.256 | 8.609 | 17.865 | 17.865 | 0.35311 | 0.51811 | 14.0597 | 14.1653 | 4.3089 | 103.1946 | 0.13727 | 5.777 | 5.777 | 16.1655 | 296.4038 | 517.95 | 597.7032 | -15.3979 | 94.5461 | 447.0535 | 96.384 | 116.857 | 101.782 | 18.699 | 4.44 | 4.169 | 8.609 | 8.609 | 0.34087 | 0.51574 | 13.4886 | 13.5899 | 7.4405 | 83.18 | 0.16338 | 5.777 | 5.777 | 32.4346 | 517.95 | 908.8625 | 1035.0256 | -13.8814 | 89.0573 | 776.4878 | 95.8229 | 101.782 | 55.41 | 18.699 | 1.32 | 3.585 | 4.905 | 4.905 | 0.16986 | 0.26911 | 11.7333 | 11.8214 | 9.5352 | 50.3618 | 0.23473 | 5.777 | 6.265 | 103.5907 | 908.8625 | 1301.8072 | 1205.3642 | 7.4084 | 65.0508 | 1057.1134 | 90.2006
[11 empty] | 1998-12-03 | 4:00 | 4341.0003 | 28.73 | 135.501 | 55.537 | 18.76 | 0 | 14.956 | 3.524 |  | 18.48 | 18.48 | 0.80931 | 0 | 13.5964 | 13.7053 | 8.2987 | 68.4603 | 0.20019 | 6.307 | 5.776 | 30.691 | 292.272 | 296.5018 | 1300.5916 | 1424.6135 | -9.5358 | 89.649 | 860.5576 | 96.4336 | 135.501 | 117.202 | 18.76 | 9.256 | 8.61 | 17.866 | 17.866 | 0.35314 | 0.51808 | 14.0597 | 14.1724 | 4.312 | 103.2795 | 0.13722 | 5.776 | 5.776 | 16.0485 | 296.5018 | 517.5 | 597.9972 | -15.555 | 94.5874 | 447.2495 | 96.4117 | 117.202 | 101.97 | 18.76 | 4.44 | 4.17 | 8.61 | 8.61 | 0.34092 | 0.51568 | 13.4886 | 13.5967 | 7.4328 | 83.3932 | 0.16304 | 5.776 | 5.776 | 32.4484 | 517.5 | 907.725 | 1033.9578 | -13.9065 | 89.0563 | 775.7289 | 95.817 | 101.97 | 55.537 | 18.76 | 1.26 | 3.524 | 4.784 | 4.784 | 0.16622 | 0.26338 | 11.2 | 11.2897 | 9.4785 | 50.515 | 0.22349 | 5.776 | 6.286 | 103.631 | 907.725 | 1300.5916 | 1195.2274 | 8.1013 | 65.0488 | 1051.4762 | 90.1442
[11 empty] | 1998-12-03 | 12:00 | 4349.0003 | 28.84 | 134.945 | 55.162 | 18.741 | 0 | 14.897 | 3.525 |  | 18.422 | 18.422 | 0.80865 | 0 | 13.5427 | 13.6069 | 8.2396 | 68.0729 | 0.19989 | 6.489 | 5.767 | 31.3255 | 290.064 | 296.004 | 1304.2377 | 1414.5616 | -8.4589 | 89.4172 | 855.2828 | 96.3374 | 134.945 | 116.25 | 18.741 | 9.257 | 8.605 | 17.862 | 17.862 | 0.35302 | 0.51825 | 14.0613 | 14.1279 | 4.3015 | 102.555 | 0.13776 | 5.767 | 5.767 | 16.302 | 296.004 | 515.25 | 596.899 | -15.8465 | 94.4926 | 446.4515 | 96.3485 | 116.25 | 101.01 | 18.741 | 4.44 | 4.165 | 8.605 | 8.605 | 0.34066 | 0.51598 | 13.4886 | 13.5526 | 7.4016 | 82.4874 | 0.1643 | 5.767 | 5.767 | 32.4383 | 515.25 | 902.0375 | 1029.94 | -14.1793 | 89.0413 | 772.595 | 95.8014 | 101.01 | 55.162 | 18.741 | 1.2 | 3.525 | 4.725 | 4.725 | 0.16506 | 0.25397 | 10.6667 | 10.7172 | 9.3439 | 50.0011 | 0.21434 | 5.767 | 6.245 | 103.5562 | 902.0375 | 1304.2377 | 1173.8609 | 9.9964 | 65.0153 | 1037.9492 | 90.023
[11 empty] | 1998-12-03 | 20:00 | 4357.0003 | 28.879 | 134.884 | 55.32 | 18.654 | 0 | 14.838 | 3.525 |  | 18.363 | 18.363 | 0.80804 | 0 | 13.4891 | 13.5374 | 8.2398 | 68.2082 | 0.19847 | 6.301 | 5.766 | 29.986 | 285.696 | 295.3838 | 1280.5376 | 1412.5393 | -10.3083 | 89.8485 | 853.9616 | 96.4886 | 134.884 | 116.805 | 18.654 | 9.258 | 8.548 | 17.806 | 17.806 | 0.35151 | 0.51994 | 14.0628 | 14.1132 | 4.309 | 102.8815 | 0.13718 | 5.766 | 5.766 | 15.8535 | 295.3838 | 506.25 | 598.1321 | -18.1495 | 94.6329 | 446.758 | 96.4514 | 116.805 | 101.362 | 18.654 | 4.44 | 4.108 | 8.548 | 8.548 | 0.33762 | 0.51942 | 13.4886 | 13.5369 | 7.3002 | 83.1293 | 0.16284 | 5.766 | 5.766 | 32.338 | 506.25 | 884.975 | 1018.4626 | -15.0838 | 89.0522 | 762.3563 | 95.7582 | 101.362 | 55.32 | 18.654 | 1.14 | 3.525 | 4.665 | 4.665 | 0.16386 | 0.24437 | 10.1333 | 10.1696 | 9.0862 | 50.6008 | 0.20098 | 5.766 | 6.291 | 102.8333 | 884.975 | 1280.5376 | 1137.923 | 11.1371 | 65.1866 | 1011.449 | 89.8331
[11 empty] | 1998-12-04 | 0:00 | 4361 | 28.874 | 135.012 | 55.552 | 18.727 | 0 | 14.957 | 3.525 |  | 18.482 | 18.482 | 0.80927 | 0 | 13.5973 | 13.648 | 8.2858 | 68.2692 | 0.19991 | 6.287 | 5.771 | 29.5395 | 283.92 | 294.9758 | 1279.9301 | 1421.2542 | -11.0415 | 89.9858 | 858.115 | 96.5576 | 135.012 | 116.55 | 18.727 | 9.257 | 8.551 | 17.808 | 17.808 | 0.35158 | 0.51982 | 14.0613 | 14.1137 | 4.303 | 102.751 | 0.13736 | 5.771 | 5.771 | 15.795 | 294.9758 | 502.2 | 597.2068 | -18.9181 | 94.6453 | 446.0913 | 96.4592 | 116.55 | 101.4 | 18.727 | 4.68 | 3.871 | 8.551 | 8.551 | 0.33137 | 0.5473 | 14.2177 | 14.2708 | 7.5392 | 82.7088 | 0.17254 | 5.771 | 5.771 | 32.3205 | 502.2 | 880.6525 | 1070.2796 | -21.5326 | 89.043 | 786.2398 | 95.8892 | 101.4 | 55.552 | 18.727 | 1.02 | 3.525 | 4.545 | 4.545 | 0.16146 | 0.22442 | 9.0667 | 9.1005 | 8.9049 | 50.8441 | 0.17899 | 5.771 | 6.315 | 102.7123 | 880.6525 | 1279.9301 | 1105.7586 | 13.6079 | 65.1794 | 993.2055 | 89.6585
[11 empty] | 1998-12-04 | 12:00 | 4373 | 29.078 | 138.208 | 43.417 | 18.292 | 0 | 14.294 | 3.982 |  | 18.276 | 18.276 | 0.78212 | 0 | 12.9945 | 12.9646 | 7.4011 | 65.1194 | 0.19909 | 6.861 | 5.797 | 28.9285 | 277.488 | 293.7437 | 1263.5222 | 1244.3384 | 1.5183 | 90.1518 | 769.041 | 96.2384 | 138.208 | 118.537 | 18.292 | 8.894 | 9.989 | 18.883 | 18.883 | 0.3851 | 0.47101 | 13.5099 | 13.4788 | 4.0225 | 106.058 | 0.12709 | 5.797 | 5.797 | 15.405 | 293.7437 | 488.25 | 541.5707 | -10.9208 | 94.7556 | 417.6572 | 96.3116 | 118.537 | 101.22 | 18.292 | 4.5 | 5.489 | 9.989 | 9.989 | 0.4129 | 0.4505 | 13.6709 | 13.6394 | 6.4352 | 85.1513 | 0.16018 | 5.797 | 5.797 | 31.821 | 488.25 | 823.55 | 862.4403 | -4.7223 | 89.1671 | 675.3452 | 95.2882 | 101.22 | 43.417 | 18.292 | 0.9 | 3.982 | 4.882 | 4.882 | 0.17734 | 0.18435 | 8 | 7.9816 | 8.0242 | 46.0023 | 0.1735 | 5.797 | 6.249 | 102.6029 | 823.55 | 1263.5222 | 986.4964 | 21.9249 | 65.0706 | 905.0232 | 88.663
[11 empty] | 1998-12-04 | 20:00 | 4381 | 29.044 | 138.409 | 43.845 | 18.288 | 0 | 14.358 | 3.982 |  | 18.34 | 18.34 | 0.78288 | 0 | 13.0527 | 13.0358 | 7.4373 | 65.4017 | 0.19932 | 6.844 | 5.79 | 28.7405 | 278.928 | 294.0864 | 1248.9374 | 1250.8509 | -0.15322 | 90.2272 | 772.4687 | 96.2794 | 138.409 | 118.935 | 18.288 | 8.838 | 10.347 | 19.185 | 19.185 | 0.3939 | 0.46067 | 13.4248 | 13.4074 | 3.9801 | 106.4039 | 0.126 | 5.79 | 5.79 | 15.1905 | 294.0864 | 486.9 | 532.3083 | -9.326 | 94.8347 | 413.1973 | 96.3237 | 118.935 | 101.452 | 18.288 | 4.56 | 5.787 | 10.347 | 10.347 | 0.4304 | 0.44071 | 13.8532 | 13.8352 | 6.3436 | 85.5619 | 0.1617 | 5.79 | 5.79 | 31.832 | 486.9 | 829.2375 | 845.4813 | -1.9589 | 89.176 | 666.1907 | 95.2218 | 101.452 | 43.845 | 18.288 | 0.96 | 3.982 | 4.942 | 4.942 | 0.17854 | 0.19425 | 8.5333 | 8.5222 | 8.1436 | 46.2169 | 0.1844 | 5.79 | 6.33 | 102.479 | 829.2375 | 1248.9374 | 1004.448 | 19.5758 | 65.1534 | 916.8427 | 88.8226
[11 empty] | 1998-12-05 | 4:00 | 4389 | 29.027 | 138.817 | 43.777 | 18.339 | 0 | 14.832 | 3.983 |  | 18.815 | 18.815 | 0.78831 | 0 | 13.4836 | 13.4729 | 7.6074 | 65.3506 | 0.20616 | 6.976 | 5.785 | 28.247 | 278.784 | 294.0619 | 1247.7218 | 1283.9105 | -2.9004 | 90.3942 | 788.9862 | 96.4198 | 138.817 | 119.07 | 18.339 | 8.892 | 9.81 | 18.702 | 18.702 | 0.3803 | 0.47546 | 13.5068 | 13.4961 | 4.0534 | 106.5511 | 0.12666 | 5.785 | 5.785 | 15.132 | 294.0619 | 486 | 546.8901 | -12.5288 | 94.8541 | 420.476 | 96.4012 | 119.07 | 101.76 | 18.339 | 4.68 | 5.13 | 9.81 | 9.81 | 0.39854 | 0.47706 | 14.2177 | 14.2064 | 6.6134 | 85.4626 | 0.16623 | 5.785 | 5.785 | 31.8302 | 486 | 828.7825 | 900.3304 | -8.6329 | 89.1757 | 693.1652 | 95.408 | 101.76 | 43.777 | 18.339 | 1.26 | 3.983 | 5.243 | 5.243 | 0.18459 | 0.24032 | 11.2 | 11.1911 | 8.4125 | 46.017 | 0.24319 | 5.785 | 6.327 | 102.4214 | 828.7825 | 1247.7218 | 1058.5628 | 15.1604 | 65.1701 | 943.6727 | 89.1465
[11 empty] | 1998-12-05 | 12:00 | 4397 | 28.993 | 133.96 | 61.417 | 17.967 | 0 | 14.237 | 3.046 |  | 17.283 | 17.283 | 0.82376 | 0 | 12.9427 | 12.9454 | 8.8368 | 70.8847 | 0.18263 | 6.918 | 5.78 | 33.793 | 306.144 | 298.607 | 1400.861 | 1536.3475 | -9.6717 | 88.6831 | 917.4773 | 96.3167 | 133.96 | 115.605 | 17.967 | 8.537 | 9.203 | 17.74 | 17.74 | 0.35937 | 0.48123 | 12.9676 | 12.9703 | 4.123 | 102.6925 | 0.1263 | 5.78 | 5.78 | 16.9455 | 298.607 | 550.8 | 559.8854 | -1.6495 | 94.3252 | 429.2462 | 96.0523 | 115.605 | 101.362 | 17.967 | 4.5 | 4.703 | 9.203 | 9.203 | 0.37096 | 0.48897 | 13.6709 | 13.6737 | 7.6534 | 82.8631 | 0.16502 | 5.78 | 5.78 | 33.1228 | 550.8 | 993.265 | 1046.1323 | -5.3226 | 88.9076 | 798.4661 | 95.8517 | 101.362 | 61.417 | 17.967 | 1.2 | 3.046 | 4.246 | 4.246 | 0.14589 | 0.28262 | 10.6667 | 10.6689 | 10.6186 | 52.8039 | 0.20205 | 5.78 | 6.432 | 106.151 | 993.265 | 1400.861 | 1342.7518 | 4.1481 | 64.4513 | 1168.0084 | 90.9118
[11 empty] | 1998-12-05 | 20:00 | 4405 | 28.964 | 133.571 | 61.507 | 17.905 | 0 | 14.357 | 3.046 |  | 17.403 | 17.403 | 0.82497 | 0 | 13.0518 | 13.0657 | 8.895 | 70.739 | 0.1847 | 7.077 | 5.769 | 33.746 | 306.096 | 298.7376 | 1399.646 | 1547.7476 | -10.5814 | 88.7038 | 923.2426 | 96.3448 | 133.571 | 115.635 | 17.905 | 8.537 | 9.143 | 17.68 | 17.68 | 0.35777 | 0.48286 | 12.9676 | 12.9814 | 4.1286 | 102.5694 | 0.12656 | 5.769 | 5.769 | 17.277 | 298.7376 | 550.35 | 561.5429 | -2.0338 | 94.2167 | 430.1403 | 95.9834 | 115.635 | 101.25 | 17.905 | 4.5 | 4.643 | 9.143 | 9.143 | 0.36776 | 0.49218 | 13.6709 | 13.6854 | 7.6788 | 82.8587 | 0.16517 | 5.769 | 5.769 | 33.1218 | 550.35 | 993.0375 | 1051.648 | -5.9021 | 88.9127 | 800.999 | 95.8649 | 101.25 | 61.507 | 17.905 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.7458 | 10.7932 | 52.6803 | 0.22296 | 5.769 | 6.355 | 105.9322 | 993.0375 | 1399.646 | 1377.4692 | 1.5845 | 64.5401 | 1185.2534 | 91.0625
[11 empty] | 1998-12-06 | 4:00 | 4413.0003 | 28.972 | 133.571 | 61.507 | 17.919 | 0 | 14.418 | 3.046 |  | 17.464 | 17.464 | 0.82558 | 0 | 13.1073 | 13.1181 | 8.9233 | 70.6967 | 0.18555 | 7.025 | 5.772 | 33.652 | 305.904 | 298.6968 | 1398.4304 | 1553.2654 | -11.0721 | 88.7337 | 925.9811 | 96.3658 | 133.571 | 115.545 | 17.919 | 8.538 | 9.204 | 17.742 | 17.742 | 0.35941 | 0.48123 | 12.9691 | 12.9799 | 4.1215 | 102.5175 | 0.12661 | 5.772 | 5.772 | 17.1405 | 298.6968 | 549.9 | 559.8797 | -1.8148 | 94.2616 | 429.2883 | 96.0072 | 115.545 | 101.415 | 17.919 | 4.56 | 4.644 | 9.204 | 9.204 | 0.36941 | 0.49544 | 13.8532 | 13.8646 | 7.705 | 82.856 | 0.16733 | 5.772 | 5.772 | 33.12 | 549.9 | 992.1275 | 1057.3326 | -6.5722 | 88.9118 | 803.6163 | 95.8786 | 101.415 | 61.507 | 17.919 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.743 | 10.7835 | 52.7585 | 0.22258 | 5.772 | 6.363 | 105.8198 | 992.1275 | 1398.4304 | 1376.2136 | 1.5887 | 64.5728 | 1184.1705 | 91.0638
[11 empty] | 1998-12-06 | 12:00 | 4421 | 29.087 | 133.323 | 61.05 | 17.943 | 0 | 14.356 | 3.045 |  | 17.401 | 17.401 | 0.82501 | 0 | 13.0509 | 13.0174 | 8.872 | 70.3715 | 0.18498 | 7.019 | 5.773 | 32.2185 | 294.48 | 296.4773 | 1360.1455 | 1542.3555 | -13.3964 | 89.1329 | 919.4164 | 96.4958 | 133.323 | 114.93 | 17.943 | 8.476 | 9.26 | 17.736 | 17.736 | 0.36008 | 0.4779 | 12.8749 | 12.8419 | 4.0775 | 102.106 | 0.12577 | 5.773 | 5.773 | 16.7505 | 296.4773 | 532.35 | 552.5209 | -3.789 | 94.3502 | 424.4991 | 96.0541 | 114.93 | 100.59 | 17.943 | 4.56 | 4.7 | 9.26 | 9.26 | 0.3724 | 0.49244 | 13.8532 | 13.8176 | 7.4174 | 82.3996 | 0.16769 | 5.773 | 5.773 | 32.8983 | 532.35 | 946.6275 | 1016.9244 | -7.426 | 88.9036 | 774.6372 | 95.7531 | 100.59 | 61.05 | 17.943 | 1.32 | 3.045 | 4.365 | 4.365 | 0.14825 | 0.30241 | 11.7333 | 11.7032 | 10.2474 | 52.6296 | 0.22237 | 5.773 | 6.35 | 104.4288 | 946.6275 | 1360.1455 | 1311.7186 | 3.5604 | 64.7768 | 1129.173 | 90.7517
[11 empty] | 1998-12-06 | 20:00 | 4429.0003 | 29.066 | 133.645 | 61.372 | 18.04 | 0 | 14.355 | 3.046 |  | 17.401 | 17.401 | 0.82495 | 0 | 13.05 | 13.0246 | 8.8876 | 70.5809 | 0.18453 | 7.002 | 5.761 | 32.0305 | 294.96 | 296.8282 | 1355.8919 | 1544.7502 | -13.9287 | 89.2091 | 920.7892 | 96.5214 | 133.645 | 115.44 | 18.04 | 8.535 | 9.142 | 17.677 | 17.677 | 0.35772 | 0.48283 | 12.9646 | 12.9393 | 4.1116 | 102.3909 | 0.12637 | 5.761 | 5.761 | 16.5165 | 296.8282 | 530.1 | 558.528 | -5.3628 | 94.4357 | 427.6781 | 96.1381 | 115.44 | 101.25 | 18.04 | 4.5 | 4.642 | 9.142 | 9.142 | 0.36771 | 0.49223 | 13.6709 | 13.6442 | 7.3879 | 82.9171 | 0.16455 | 5.761 | 5.761 | 32.4999 | 530.1 | 952.5425 | 1012.4784 | -6.2922 | 89.0509 | 771.2892 | 95.7863 | 101.25 | 61.372 | 18.04 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.7105 | 10.3191 | 52.9519 | 0.22115 | 5.761 | 6.415 | 104.4058 | 952.5425 | 1355.8919 | 1320.087 | 2.6407 | 64.8262 | 1136.3147 | 90.8119
[11 empty] | 1998-12-07 | 4:00 | 4437 | 29.036 | 133.437 | 61.282 | 17.872 | 0 | 14.416 | 3.046 |  | 17.462 | 17.462 | 0.82556 | 0 | 13.1055 | 13.0915 | 8.9146 | 70.5729 | 0.1855 | 6.961 | 5.755 | 31.9835 | 294.864 | 296.7955 | 1355.2839 | 1550.0884 | -14.3737 | 89.2237 | 923.442 | 96.5365 | 133.437 | 115.2 | 17.872 | 8.536 | 9.267 | 17.803 | 17.803 | 0.36106 | 0.47947 | 12.9661 | 12.9523 | 4.0953 | 102.3512 | 0.12655 | 5.755 | 5.755 | 16.3995 | 296.7955 | 529.65 | 555.0733 | -4.8 | 94.4745 | 425.9344 | 96.1498 | 115.2 | 101.047 | 17.872 | 4.5 | 4.767 | 9.267 | 9.267 | 0.37438 | 0.48559 | 13.6709 | 13.6563 | 7.3185 | 82.933 | 0.16467 | 5.755 | 5.755 | 32.4659 | 529.65 | 952.0875 | 998.9868 | -4.9259 | 89.0612 | 764.3184 | 95.7523 | 101.047 | 61.282 | 17.872 | 1.38 | 3.046 | 4.426 | 4.426 | 0.14949 | 0.31179 | 12.2667 | 12.2536 | 10.3972 | 52.8953 | 0.23166 | 5.755 | 6.451 | 104.3942 | 952.0875 | 1355.2839 | 1336.1376 | 1.4127 | 64.8262 | 1144.1126 | 90.8755
[11 empty] | 1998-12-07 | 12:00 | 4445 | 29.036 | 133.384 | 61.132 | 17.902 | 0 | 14.393 | 3.046 |  | 17.439 | 17.439 | 0.82533 | 0 | 13.0845 | 13.0706 | 8.8736 | 70.4824 | 0.18545 | 6.761 | 5.76 | 32.571 | 294.336 | 296.461 | 1369.2607 | 1543.3973 | -12.7176 | 89.0134 | 919.9291 | 96.4594 | 133.384 | 115.275 | 17.902 | 8.473 | 9.327 | 17.8 | 17.8 | 0.36182 | 0.47601 | 12.8704 | 12.8567 | 4.069 | 102.3585 | 0.1256 | 5.76 | 5.76 | 16.653 | 296.461 | 531.45 | 550.6491 | -3.6126 | 94.3827 | 423.555 | 96.0683 | 115.275 | 101.002 | 17.902 | 4.56 | 4.767 | 9.327 | 9.327 | 0.37598 | 0.4889 | 13.8532 | 13.8384 | 7.3754 | 82.8611 | 0.16701 | 5.76 | 5.76 | 32.5367 | 531.45 | 950.04 | 1008.6987 | -6.1743 | 89.025 | 770.0744 | 95.7749 | 101.002 | 61.132 | 17.902 | 1.36 | 3.046 | 4.406 | 4.406 | 0.14909 | 0.30867 | 12.0889 | 12.076 | 10.344 | 52.821 | 0.22862 | 5.76 | 6.509 | 104.423 | 950.04 | 1369.2607 | 1327.5971 | 3.0428 | 64.7768 | 1138.8186 | 90.8306
[11 empty] | 1998-12-07 | 20:00 | 4453.0003 | 28.968 | 133.759 | 61.327 | 17.934 | 0 | 14.294 | 3.046 |  | 17.34 | 17.34 | 0.82434 | 0 | 12.9945 | 13.0068 | 8.8652 | 70.7438 | 0.18386 | 6.92 | 5.764 | 32.054 | 295.776 | 296.975 | 1363.7916 | 1540.1731 | -12.9332 | 89.2065 | 918.5741 | 96.5105 | 133.759 | 115.672 | 17.934 | 8.534 | 9.394 | 17.928 | 17.928 | 0.36443 | 0.47602 | 12.963 | 12.9753 | 4.0782 | 102.7033 | 0.12634 | 5.764 | 5.764 | 16.536 | 296.975 | 531 | 551.7405 | -3.9059 | 94.4319 | 424.3578 | 96.1033 | 115.672 | 101.422 | 17.934 | 4.56 | 4.834 | 9.394 | 9.394 | 0.37955 | 0.48542 | 13.8532 | 13.8663 | 7.3326 | 83.2804 | 0.1665 | 5.764 | 5.764 | 32.7446 | 531 | 956.6375 | 1001.0133 | -4.6387 | 88.9739 | 766.0067 | 95.7253 | 101.422 | 61.327 | 17.934 | 1.2 | 3.046 | 4.246 | 4.246 | 0.14589 | 0.28262 | 10.6667 | 10.6768 | 10.1998 | 53.2407 | 0.20054 | 5.764 | 6.453 | 104.5066 | 956.6375 | 1363.7916 | 1292.3424 | 5.239 | 64.8096 | 1124.49 | 90.7063
[11 empty] | 1998-12-08 | 4:00 | 4461 | 28.942 | 134.094 | 61.612 | 17.994 | 0 | 14.293 | 3.047 |  | 17.34 | 17.34 | 0.82428 | 0 | 12.9936 | 13.0159 | 8.8548 | 71.0042 | 0.18331 | 6.428 | 5.755 | 32.4065 | 296.544 | 297.0893 | 1355.2839 | 1538.6748 | -13.5315 | 89.092 | 917.882 | 96.4694 | 134.094 | 115.875 | 17.994 | 8.473 | 9.207 | 17.68 | 17.68 | 0.35862 | 0.47924 | 12.8704 | 12.8925 | 4.0931 | 102.8974 | 0.12529 | 5.755 | 5.755 | 16.77 | 297.0893 | 533.7 | 555.061 | -4.0024 | 94.3552 | 426.0751 | 96.0641 | 115.875 | 101.737 | 17.994 | 4.5 | 4.707 | 9.207 | 9.207 | 0.37117 | 0.48876 | 13.6709 | 13.6943 | 7.4037 | 83.4083 | 0.16418 | 5.755 | 5.755 | 32.7768 | 533.7 | 955.955 | 1012.594 | -5.9249 | 88.9673 | 773.147 | 95.7606 | 101.737 | 61.612 | 17.994 | 1.32 | 3.047 | 4.367 | 4.367 | 0.14833 | 0.30227 | 11.7333 | 11.7535 | 10.3595 | 53.321 | 0.22043 | 5.755 | 6.413 | 104.4461 | 955.955 | 1355.2839 | 1324.8397 | 2.2463 | 64.8435 | 1140.3974 | 90.8413
[11 empty] | 1998-12-08 | 12:00 | 4469 | 29.074 | 133.323 | 60.907 | 17.938 | 0 | 14.359 | 3.046 |  | 17.405 | 17.405 | 0.82499 | 0 | 13.0536 | 13.0251 | 8.8716 | 70.3054 | 0.18526 | 6.46 | 5.748 | 31.302 | 287.472 | 295.5715 | 1337.053 | 1541.3516 | -15.2798 | 89.4097 | 918.4615 | 96.5919 | 133.323 | 115.147 | 17.938 | 8.539 | 9.263 | 17.802 | 17.802 | 0.361 | 0.47967 | 12.9706 | 12.9423 | 4.0802 | 102.2168 | 0.12662 | 5.748 | 5.748 | 16.2825 | 295.5715 | 519.3 | 553.0312 | -6.4955 | 94.4912 | 424.3014 | 96.1625 | 115.147 | 100.837 | 17.938 | 4.5 | 4.763 | 9.263 | 9.263 | 0.37416 | 0.4858 | 13.6709 | 13.641 | 7.1644 | 82.8896 | 0.16457 | 5.748 | 5.748 | 32.7161 | 519.3 | 930.02 | 979.016 | -5.2683 | 88.9312 | 749.158 | 95.6329 | 100.837 | 60.907 | 17.938 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.7077 | 10.0536 | 52.8804 | 0.2214 | 5.748 | 6.32 | 103.703 | 930.02 | 1337.053 | 1288.1088 | 3.6606 | 64.9144 | 1109.0644 | 90.6495
[11 empty] | 1998-12-08 | 13:29 | 4470.4819 | 29.104 | 133.377 | 60.847 | 18.033 | 0 | 14.415 | 3.046 |  | 17.461 | 17.461 | 0.82555 | 0 | 13.1045 | 13.0643 | 8.9003 | 70.1787 | 0.18616 | 6.481 | 5.743 | 31.302 | 288.288 | 295.7021 | 1336.4455 | 1546.9585 | -15.7517 | 89.4143 | 921.3303 | 96.6025 | 133.377 | 115.02 | 18.033 | 8.535 | 9.141 | 17.676 | 17.676 | 0.35769 | 0.48286 | 12.9646 | 12.9248 | 4.0992 | 102.0663 | 0.12663 | 5.743 | 5.743 | 16.2435 | 295.7021 | 518.85 | 556.634 | -7.2823 | 94.5068 | 426.1681 | 96.1885 | 115.02 | 101.025 | 18.033 | 4.56 | 4.581 | 9.141 | 9.141 | 0.36605 | 0.49885 | 13.8532 | 13.8106 | 7.2809 | 82.7086 | 0.16698 | 5.743 | 5.743 | 32.7143 | 518.85 | 929.565 | 1002.7572 | -7.8738 | 88.9367 | 760.8036 | 95.7 | 101.025 | 60.847 | 18.033 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.6973 | 10.048 | 52.855 | 0.22131 | 5.743 | 6.357 | 103.7059 | 929.565 | 1336.4455 | 1287.4553 | 3.6657 | 64.9289 | 1108.5102 | 90.6446
[11 empty] | 1998-12-08 | 21:00 | 4478 | 29.061 | 133.491 | 61.267 | 18.043 | 0 | 14.417 | 3.046 |  | 17.463 | 17.463 | 0.82557 | 0 | 13.1064 | 13.0828 | 8.9079 | 70.4281 | 0.18576 | 6.352 | 5.761 | 31.208 | 289.008 | 295.8082 | 1334.6224 | 1548.1852 | -16.0017 | 89.4499 | 921.9967 | 96.6152 | 133.491 | 115.477 | 18.043 | 8.537 | 9.206 | 17.743 | 17.743 | 0.35945 | 0.48115 | 12.9676 | 12.9442 | 4.0927 | 102.3483 | 0.12647 | 5.761 | 5.761 | 16.185 | 295.8082 | 517.95 | 555.1111 | -7.1747 | 94.5285 | 425.4596 | 96.1959 | 115.477 | 101.085 | 18.043 | 4.56 | 4.646 | 9.206 | 9.206 | 0.36952 | 0.49533 | 13.8532 | 13.8282 | 7.2329 | 83.0051 | 0.16659 | 5.761 | 5.761 | 32.7612 | 517.95 | 932.75 | 994.1577 | -6.5835 | 88.9248 | 756.0538 | 95.6668 | 101.085 | 61.267 | 18.043 | 1.32 | 3.046 | 4.366 | 4.366 | 0.14829 | 0.30234 | 11.7333 | 11.7122 | 10.0863 | 53.0467 | 0.22079 | 5.761 | 6.352 | 103.7462 | 932.75 | 1334.6224 | 1292.0031 | 3.1934 | 64.9279 | 1112.3766 | 90.6735
[11 empty] | 1998-12-09 | 5:00 | 4486.0003 | 29.04 | 138.469 | 42.825 | 18.124 | 0 | 14.479 | 3.982 |  | 18.461 | 18.461 | 0.7843 | 0 | 13.1627 | 13.1472 | 7.5046 | 65.0184 | 0.20221 | 6.357 | 5.76 | 29.4455 | 289.632 | 295.751 | 1266.5608 | 1264.0679 | 0.19682 | 90.0438 | 779.9095 | 96.2245 | 138.469 | 118.912 | 18.124 | 8.839 | 10.161 | 19 | 19 | 0.38895 | 0.46521 | 13.4263 | 13.4105 | 4.0195 | 106.547 | 0.12586 | 5.76 | 5.76 | 15.639 | 295.751 | 505.35 | 539.419 | -6.7417 | 94.7121 | 417.585 | 96.2549 | 118.912 | 101.52 | 18.124 | 4.62 | 5.541 | 10.161 | 10.161 | 0.41887 | 0.45468 | 14.0354 | 14.0189 | 6.7077 | 85.3843 | 0.16419 | 5.76 | 5.76 | 31.9415 | 505.35 | 855.6275 | 900.0707 | -5.1942 | 89.1999 | 702.7103 | 95.4545 | 101.52 | 42.825 | 18.124 | 1.02 | 3.982 | 5.002 | 5.002 | 0.17975 | 0.20392 | 9.0667 | 9.056 | 8.4923 | 45.5562 | 0.19879 | 5.76 | 6.31 | 102.816 | 855.6275 | 1266.5608 | 1048.4622 | 17.2198 | 65.2356 | 952.0448 | 89.2005
[11 empty] | 1998-12-09 | 13:00 | 4494 | 29.138 | 138.744 | 45 | 18.339 | 0 | 14.354 | 3.982 |  | 18.336 | 18.336 | 0.78283 | 0 | 13.0491 | 12.996 | 7.4344 | 66.0986 | 0.19661 | 6.355 | 5.776 | 29.751 | 287.664 | 295.0411 | 1284.7912 | 1251.3381 | 2.6038 | 89.9163 | 773.1896 | 96.1522 | 138.744 | 118.927 | 18.339 | 8.894 | 10.105 | 18.999 | 18.999 | 0.38819 | 0.46813 | 13.5099 | 13.4549 | 4.0174 | 106.4791 | 0.12636 | 5.776 | 5.776 | 16.068 | 295.0411 | 508.05 | 540.5816 | -6.4032 | 94.554 | 417.8114 | 96.1542 | 118.927 | 101.797 | 18.339 | 4.62 | 5.485 | 10.105 | 10.105 | 0.41588 | 0.4572 | 14.0354 | 13.9783 | 6.7653 | 85.2577 | 0.16395 | 5.776 | 5.776 | 32.004 | 508.05 | 859.2675 | 909.0222 | -5.7904 | 89.1527 | 708.5361 | 95.4831 | 101.797 | 45 | 18.339 | 0.84 | 3.982 | 4.822 | 4.822 | 0.17614 | 0.1742 | 7.4667 | 7.4363 | 8.3624 | 46.6971 | 0.15924 | 5.776 | 6.376 | 102.8102 | 859.2675 | 1284.7912 | 1018.8416 | 20.6998 | 65.1539 | 939.0546 | 89.0517
[11 empty] | 1998-12-09 | 21:00 | 4502 | 29.078 | 138.824 | 44.925 | 18.346 | 0 | 14.597 | 3.983 |  | 18.58 | 18.58 | 0.78563 | 0 | 13.27 | 13.2394 | 7.5383 | 65.9902 | 0.20063 | 6.36 | 5.755 | 29.516 | 289.008 | 295.6613 | 1280.5376 | 1271.0373 | 0.7419 | 90.017 | 783.3493 | 96.2321 | 138.824 | 119.19 | 18.346 | 8.837 | 10.099 | 18.936 | 18.936 | 0.38727 | 0.46668 | 13.4233 | 13.3924 | 4.0228 | 106.6382 | 0.12559 | 5.755 | 5.755 | 15.8145 | 295.6613 | 506.25 | 540.5376 | -6.7729 | 94.6511 | 418.0994 | 96.2175 | 119.19 | 101.917 | 18.346 | 4.62 | 5.479 | 10.099 | 10.099 | 0.41556 | 0.45747 | 14.0354 | 14.0031 | 6.7416 | 85.4659 | 0.16384 | 5.755 | 5.755 | 32.0261 | 506.25 | 861.9975 | 906.1249 | -5.1192 | 89.168 | 706.1874 | 95.4649 | 101.917 | 44.925 | 18.346 | 1.14 | 3.983 | 5.123 | 5.123 | 0.18219 | 0.22253 | 10.1333 | 10.11 | 8.6775 | 46.3975 | 0.2179 | 5.755 | 6.372 | 102.8822 | 861.9975 | 1280.5376 | 1079.2688 | 15.7175 | 65.2027 | 970.6331 | 89.4005
[11 empty] | 1998-12-10 | 5:00 | 4510 | 29.036 | 139.058 | 45.232 | 18.228 | 0 | 14.652 | 3.982 |  | 18.634 | 18.634 | 0.7863 | 0 | 13.32 | 13.3058 | 7.5795 | 66.3375 | 0.20058 | 6.328 | 5.755 | 29.892 | 295.68 | 296.7955 | 1290.2609 | 1278.8825 | 0.88187 | 89.9284 | 787.839 | 96.2058 | 139.058 | 119.37 | 18.228 | 8.892 | 9.75 | 18.642 | 18.642 | 0.3787 | 0.47699 | 13.5068 | 13.4925 | 4.0928 | 106.8932 | 0.12622 | 5.755 | 5.755 | 15.6975 | 296.7955 | 517.5 | 553.1569 | -6.8902 | 94.711 | 424.9762 | 96.3063 | 119.37 | 102.21 | 18.228 | 4.62 | 5.13 | 9.75 | 9.75 | 0.39694 | 0.47385 | 14.0354 | 14.0205 | 7.0394 | 85.5226 | 0.16394 | 5.755 | 5.755 | 32.1227 | 517.5 | 884.065 | 954.6234 | -7.9811 | 89.1768 | 736.0617 | 95.6359 | 102.21 | 45.232 | 18.228 | 1.14 | 3.982 | 5.122 | 5.122 | 0.18215 | 0.22257 | 10.1333 | 10.1226 | 8.9243 | 46.5687 | 0.21737 | 5.755 | 6.4 | 103.3805 | 884.065 | 1290.2609 | 1107.5658 | 14.1595 | 65.1678 | 995.8154 | 89.6185
[11 empty] | 1998-12-10 | 13:00 | 4518 | 29.032 | 139.025 | 45.15 | 18.274 | 0 | 14.497 | 3.981 |  | 18.478 | 18.478 | 0.78455 | 0 | 13.1791 | 13.1666 | 7.5116 | 66.3019 | 0.19859 | 6.488 | 5.776 | 31.772 | 304.56 | 298.0685 | 1327.9378 | 1267.7997 | 4.5287 | 89.3407 | 782.9341 | 95.9419 | 139.025 | 119.392 | 18.274 | 8.837 | 10.094 | 18.931 | 18.931 | 0.38714 | 0.4668 | 13.4233 | 13.4106 | 4.0502 | 106.8843 | 0.12547 | 5.776 | 5.776 | 16.3605 | 298.0685 | 535.5 | 544.6955 | -1.7172 | 94.5112 | 421.382 | 96.1174 | 119.392 | 102.322 | 18.274 | 4.52 | 5.574 | 10.094 | 10.094 | 0.41797 | 0.44779 | 13.7316 | 13.7187 | 7.0723 | 85.5107 | 0.16043 | 5.776 | 5.776 | 32.2929 | 535.5 | 914.3225 | 943.5545 | -3.1971 | 89.1659 | 739.5273 | 95.6333 | 102.322 | 45.15 | 18.274 | 1.14 | 3.981 | 5.121 | 5.121 | 0.18211 | 0.22261 | 10.1333 | 10.1238 | 9.2574 | 46.2046 | 0.21911 | 5.776 | 6.44 | 104.5296 | 914.3225 | 1327.9378 | 1146.215 | 13.6846 | 64.931 | 1030.2687 | 89.8541
[11 empty] | 1998-12-10 | 21:00 | 4526 | 28.993 | 139.172 | 45.367 | 18.277 | 0 | 14.475 | 3.982 |  | 18.457 | 18.457 | 0.78426 | 0 | 13.1591 | 13.1618 | 7.5215 | 66.471 | 0.19801 | 6.456 | 5.764 | 31.631 | 306.048 | 298.5826 | 1320.6456 | 1268.9803 | 3.9121 | 89.4063 | 783.7814 | 95.9643 | 139.172 | 119.97 | 18.277 | 8.895 | 9.927 | 18.822 | 18.822 | 0.38346 | 0.47259 | 13.5114 | 13.5142 | 4.0889 | 107.2051 | 0.12606 | 5.764 | 5.764 | 16.2045 | 298.5826 | 538.2 | 551.6049 | -2.4907 | 94.5729 | 425.0937 | 96.188 | 119.97 | 102.517 | 18.277 | 4.62 | 5.307 | 9.927 | 9.927 | 0.40639 | 0.4654 | 14.0354 | 14.0383 | 7.2612 | 85.7053 | 0.1638 | 5.764 | 5.764 | 32.2883 | 538.2 | 917.0525 | 978.6206 | -6.7137 | 89.1861 | 758.4103 | 95.7426 | 102.517 | 45.367 | 18.277 | 0.96 | 3.982 | 4.942 | 4.942 | 0.17854 | 0.19425 | 8.5333 | 8.5351 | 9.1048 | 46.5602 | 0.18331 | 5.764 | 6.404 | 104.5152 | 917.0525 | 1320.6456 | 1112.943 | 15.7274 | 64.9962 | 1014.9977 | 89.7029
[11 empty] | 1998-12-11 | 5:00 | 4534.0003 | 28.887 | 139.688 | 45.675 | 18.223 | 0 | 14.536 | 3.983 |  | 18.519 | 18.519 | 0.78492 | 0 | 13.2145 | 13.2588 | 7.5579 | 66.9006 | 0.19819 | 6.44 | 5.761 | 32.477 | 314.592 | 300.035 | 1346.1687 | 1276.4909 | 5.176 | 89.1756 | 788.263 | 95.8799 | 139.688 | 119.94 | 18.223 | 8.836 | 9.984 | 18.82 | 18.82 | 0.38419 | 0.4695 | 13.4218 | 13.4667 | 4.0898 | 107.5012 | 0.12527 | 5.761 | 5.761 | 16.5165 | 300.035 | 554.4 | 550.9535 | 0.62166 | 94.4951 | 425.4943 | 96.1183 | 119.94 | 102.787 | 18.223 | 4.62 | 5.364 | 9.984 | 9.984 | 0.40943 | 0.46274 | 14.0354 | 14.0824 | 7.4675 | 85.673 | 0.16437 | 5.761 | 5.761 | 32.4355 | 554.4 | 944.8075 | 1003.9667 | -6.2615 | 89.1894 | 779.1834 | 95.8372 | 102.787 | 45.675 | 18.223 | 1.08 | 3.983 | 5.063 | 5.063 | 0.18099 | 0.21331 | 9.6 | 9.6321 | 9.533 | 46.475 | 0.20725 | 5.761 | 6.429 | 105.3216 | 944.8075 | 1346.1687 | 1172.4361 | 12.9057 | 64.8969 | 1058.6218 | 90.0511
[11 empty] | 1998-12-11 | 13:00 | 4542.0003 | 28.934 | 139.581 | 45.517 | 18.279 | 0 | 14.538 | 3.982 |  | 18.52 | 18.52 | 0.78499 | 0 | 13.2164 | 13.2422 | 7.55 | 66.72 | 0.19847 | 6.404 | 5.773 | 32.5945 | 313.872 | 299.8066 | 1348.5992 | 1275.3789 | 5.4294 | 89.1282 | 787.5927 | 95.8615 | 139.581 | 120.15 | 18.279 | 8.838 | 10.095 | 18.933 | 18.933 | 0.38718 | 0.4668 | 13.4248 | 13.451 | 4.0705 | 107.516 | 0.12511 | 5.773 | 5.773 | 16.692 | 299.8066 | 551.7 | 547.6685 | 0.73074 | 94.4324 | 423.7375 | 96.0608 | 120.15 | 102.937 | 18.279 | 4.62 | 5.475 | 10.095 | 10.095 | 0.41535 | 0.45765 | 14.0354 | 14.0629 | 7.3837 | 85.8808 | 0.16375 | 5.773 | 5.773 | 32.4226 | 551.7 | 942.305 | 989.8847 | -5.0493 | 89.1855 | 770.7924 | 95.7936 | 102.937 | 45.517 | 18.279 | 1.08 | 3.982 | 5.062 | 5.062 | 0.18095 | 0.21335 | 9.6 | 9.6187 | 9.5053 | 46.4427 | 0.20711 | 5.773 | 6.46 | 105.287 | 942.305 | 1348.5992 | 1169.3214 | 13.2936 | 64.8817 | 1055.8132 | 90.0279
[11 empty] | 1998-12-11 | 21:00 | 4550 | 28.879 | 139.601 | 45.517 | 18.249 | 0 | 14.476 | 3.983 |  | 18.459 | 18.459 | 0.78422 | 0 | 13.16 | 13.2072 | 7.5379 | 66.7721 | 0.19779 | 6.393 | 5.806 | 32.4535 | 314.496 | 300.0187 | 1340.0915 | 1272.4702 | 5.046 | 89.1828 | 786.2444 | 95.8723 | 139.601 | 120.022 | 18.249 | 8.836 | 9.986 | 18.822 | 18.822 | 0.38425 | 0.46945 | 13.4218 | 13.4699 | 4.0896 | 107.4729 | 0.12533 | 5.806 | 5.806 | 16.497 | 300.0187 | 553.95 | 550.8897 | 0.55244 | 94.5013 | 425.4542 | 96.1225 | 120.022 | 102.862 | 18.249 | 4.38 | 5.606 | 9.986 | 9.986 | 0.41594 | 0.43861 | 13.3063 | 13.354 | 7.2525 | 85.9405 | 0.15539 | 5.806 | 5.806 | 32.4346 | 553.95 | 944.58 | 961.413 | -1.7821 | 89.1891 | 757.6815 | 95.7192 | 102.862 | 45.517 | 18.249 | 1.26 | 3.983 | 5.243 | 5.243 | 0.18459 | 0.24032 | 11.2 | 11.2401 | 9.7201 | 46.2204 | 0.24319 | 5.806 | 6.478 | 105.3187 | 944.58 | 1340.0915 | 1210.0757 | 9.702 | 64.896 | 1077.3278 | 90.2241
[11 empty] | 1998-12-12 | 0:00 | 4553 | 28.862 | 139.802 | 45.622 | 18.171 | 0 | 14.652 | 3.982 |  | 18.634 | 18.634 | 0.7863 | 0 | 13.32 | 13.3744 | 7.5943 | 66.9467 | 0.19978 | 6.399 | 5.803 | 32.4535 | 315.36 | 299.88 | 1334.0149 | 1283.8913 | 3.7573 | 89.1778 | 791.8857 | 95.9017 | 139.802 | 120.285 | 18.171 | 8.892 | 9.864 | 18.756 | 18.756 | 0.38174 | 0.47409 | 13.5068 | 13.562 | 4.1106 | 107.7619 | 0.12585 | 5.803 | 5.803 | 16.536 | 299.88 | 554.4 | 555.3032 | -0.16292 | 94.4858 | 427.5916 | 96.1328 | 120.285 | 102.922 | 18.171 | 4.62 | 5.244 | 9.864 | 9.864 | 0.40303 | 0.46837 | 14.0354 | 14.0928 | 7.5189 | 85.9136 | 0.16403 | 5.803 | 5.803 | 32.4346 | 554.4 | 944.8075 | 1014.2551 | -7.3504 | 89.1841 | 784.3276 | 95.8647 | 102.922 | 45.622 | 18.171 | 1.14 | 3.982 | 5.122 | 5.122 | 0.18215 | 0.22257 | 10.1333 | 10.1748 | 9.5965 | 46.5045 | 0.21879 | 5.803 | 6.505 | 105.3216 | 944.8075 | 1334.0149 | 1185.1425 | 11.1597 | 64.8788 | 1064.975 | 90.1104
[11 empty] | 1998-12-12 | 13:00 | 4566 | 29.163 | 139.038 | 45.015 | 18.348 | 0 | 14.653 | 3.982 |  | 18.635 | 18.635 | 0.78632 | 0 | 13.3209 | 13.2569 | 7.5551 | 66.1234 | 0.20049 | 6.401 | 5.799 | 28.3645 | 282.336 | 294.3965 | 1250.1529 | 1273.3434 | -1.855 | 90.3652 | 783.8699 | 96.3815 | 139.038 | 119.272 | 18.348 | 8.893 | 9.929 | 18.822 | 18.822 | 0.38349 | 0.47248 | 13.5084 | 13.4434 | 4.0419 | 106.7651 | 0.12592 | 5.799 | 5.799 | 15.2295 | 294.3965 | 495 | 544.4349 | -9.9869 | 94.8269 | 419.4157 | 96.3689 | 119.272 | 102.105 | 18.348 | 4.62 | 5.309 | 9.929 | 9.929 | 0.40649 | 0.4653 | 14.0354 | 13.968 | 6.6458 | 85.6947 | 0.163 | 5.799 | 5.799 | 31.9148 | 495 | 837.655 | 897.9862 | -7.2024 | 89.1592 | 696.4931 | 95.4178 | 102.105 | 45.015 | 18.348 | 1.14 | 3.982 | 5.122 | 5.122 | 0.18215 | 0.22257 | 10.1333 | 10.0846 | 8.408 | 46.804 | 0.21547 | 5.799 | 6.544 | 102.1363 | 837.655 | 1250.1529 | 1048.2254 | 16.1522 | 65.3065 | 942.9402 | 89.1683
[11 empty] | 1998-12-12 | 21:00 | 4574 | 29.214 | 138.971 | 45.097 | 18.226 | 0 | 14.536 | 3.983 |  | 18.519 | 18.519 | 0.78492 | 0 | 13.2145 | 13.1312 | 7.5191 | 66.2889 | 0.19809 | 6.398 | 5.79 | 28.341 | 283.152 | 294.527 | 1248.9374 | 1265.9758 | -1.3642 | 90.3775 | 780.2514 | 96.3677 | 138.971 | 119.077 | 18.226 | 8.836 | 10.095 | 18.931 | 18.931 | 0.38715 | 0.46675 | 13.4218 | 13.3371 | 4.0108 | 106.7872 | 0.12489 | 5.79 | 5.79 | 15.5415 | 294.527 | 494.55 | 538.7188 | -8.9311 | 94.7232 | 416.6229 | 96.2696 | 119.077 | 101.85 | 18.226 | 4.62 | 5.475 | 10.095 | 10.095 | 0.41535 | 0.45765 | 14.0354 | 13.9469 | 6.5783 | 85.6592 | 0.16282 | 5.79 | 5.79 | 31.913 | 494.55 | 841.295 | 884.9396 | -5.1878 | 89.1647 | 689.7448 | 95.3732 | 101.85 | 45.097 | 18.226 | 1.08 | 3.983 | 5.063 | 5.063 | 0.18099 | 0.21331 | 9.6 | 9.5395 | 8.3933 | 46.8542 | 0.2036 | 5.79 | 6.552 | 102.1709 | 841.295 | 1248.9374 | 1041.7103 | 16.5923 | 65.3102 | 941.5026 | 89.1481
[11 empty] | 1998-12-13 | 5:00 | 4582.0003 | 29.24 | 138.476 | 44.707 | 18.444 | 0 | 14.715 | 3.982 |  | 18.697 | 18.697 | 0.78702 | 0 | 13.3773 | 13.2827 | 7.5685 | 65.579 | 0.20255 | 6.152 | 5.785 | 28.7405 | 283.056 | 294.5189 | 1248.9374 | 1276.6708 | -2.2206 | 90.2415 | 785.5948 | 96.3416 | 138.476 | 119.145 | 18.444 | 8.895 | 9.924 | 18.819 | 18.819 | 0.38338 | 0.47266 | 13.5114 | 13.4159 | 4.0406 | 106.3259 | 0.12618 | 5.785 | 5.785 | 15.5025 | 294.5189 | 494.55 | 544.6046 | -10.1212 | 94.7363 | 419.5617 | 96.3051 | 119.145 | 102.097 | 18.444 | 4.62 | 5.304 | 9.924 | 9.924 | 0.40623 | 0.46554 | 14.0354 | 13.9362 | 6.6413 | 85.5357 | 0.16293 | 5.785 | 5.785 | 31.912 | 494.55 | 841.0675 | 897.5265 | -6.7128 | 89.1647 | 696.0383 | 95.4152 | 102.097 | 44.707 | 18.444 | 1.2 | 3.982 | 5.182 | 5.182 | 0.18335 | 0.23157 | 10.6667 | 10.5913 | 8.5018 | 46.4562 | 0.22798 | 5.785 | 6.529 | 102.2141 | 841.0675 | 1248.9374 | 1063.7255 | 14.8296 | 65.2946 | 952.3965 | 89.2677
[11 empty] | 1998-12-13 | 13:00 | 4590.0003 | 29.304 | 138.931 | 44.242 | 18.36 | 0 | 14.716 | 3.982 |  | 18.698 | 18.698 | 0.78704 | 0 | 13.3782 | 13.2585 | 7.5282 | 65.6983 | 0.20181 | 6.2 | 5.792 | 29.6805 | 280.944 | 294.0293 | 1272.0299 | 1270.9647 | 0.083747 | 89.9056 | 782.497 | 96.207 | 138.931 | 119.287 | 18.36 | 8.956 | 9.804 | 18.76 | 18.76 | 0.38099 | 0.4774 | 13.6041 | 13.4824 | 4.0538 | 106.6952 | 0.12636 | 5.792 | 5.792 | 15.756 | 294.0293 | 492.75 | 548.2332 | -11.2599 | 94.6414 | 421.1313 | 96.2586 | 119.287 | 101.535 | 18.36 | 4.62 | 5.184 | 9.804 | 9.804 | 0.39983 | 0.47124 | 14.0354 | 13.9099 | 6.662 | 85.389 | 0.1629 | 5.792 | 5.792 | 31.9028 | 492.75 | 839.2475 | 903.4587 | -7.651 | 89.1498 | 698.1043 | 95.4301 | 101.535 | 44.242 | 18.36 | 1.14 | 3.982 | 5.122 | 5.122 | 0.18215 | 0.22257 | 10.1333 | 10.0427 | 8.4215 | 46.107 | 0.21781 | 5.792 | 6.551 | 102.551 | 839.2475 | 1272.0299 | 1050.1551 | 17.4426 | 65.1222 | 944.7013 | 89.1446
[11 empty] | 1998-12-14 | 16:00 | 4617 | 28.836 | 135.085 | 59.985 | 18.708 | 0 | 15.069 | 3.105 |  | 18.174 | 18.174 | 0.82915 | 0 | 13.6991 | 13.7657 | 9.0184 | 69.8086 | 0.19719 | 6.392 | 5.805 | 36.9185 | 315.792 | 300.1085 | 1440.3614 | 1577.4063 | -9.5146 | 87.6983 | 938.7574 | 96.0673 | 135.085 | 116.917 | 18.708 | 9.429 | 8.014 | 17.443 | 17.443 | 0.33955 | 0.54056 | 14.3225 | 14.3921 | 4.4854 | 102.8076 | 0.13999 | 5.805 | 5.805 | 17.706 | 300.1085 | 568.8 | 632.3736 | -11.1768 | 94.1001 | 466.2411 | 96.2024 | 116.917 | 101.887 | 18.708 | 4.38 | 3.634 | 8.014 | 8.014 | 0.31073 | 0.54654 | 13.3063 | 13.371 | 8.5846 | 82.1094 | 0.16284 | 5.805 | 5.805 | 33.1485 | 568.8 | 1023.0675 | 1214.4119 | -18.703 | 88.9545 | 891.6059 | 96.2822 | 101.887 | 59.985 | 18.708 | 1.26 | 3.105 | 4.365 | 4.365 | 0.14945 | 0.28866 | 11.2 | 11.2544 | 11.0033 | 51.2247 | 0.21971 | 5.805 | 6.6 | 108.3312 | 1023.0675 | 1440.3614 | 1394.2648 | 3.2003 | 63.9027 | 1208.6662 | 91.0371
[11 empty] | 1998-12-15 | 0:00 | 4625 | 28.76 | 135.528 | 60.352 | 18.685 | 0 | 15.013 | 3.106 |  | 18.119 | 18.119 | 0.82858 | 0 | 13.6482 | 13.7453 | 9.0215 | 70.2335 | 0.19571 | 6.744 | 5.785 | 36.2605 | 318.096 | 300.2962 | 1423.9535 | 1576.5252 | -10.7147 | 87.9251 | 938.4107 | 96.136 | 135.528 | 117.412 | 18.685 | 9.433 | 8.136 | 17.569 | 17.569 | 0.34286 | 0.53691 | 14.3286 | 14.4306 | 4.4684 | 103.3166 | 0.13967 | 5.785 | 5.785 | 17.433 | 300.2962 | 570.6 | 628.2519 | -10.1037 | 94.1947 | 464.274 | 96.2451 | 117.412 | 102.412 | 18.685 | 4.38 | 3.756 | 8.136 | 8.136 | 0.31724 | 0.53835 | 13.3063 | 13.4011 | 8.5078 | 82.7192 | 0.16201 | 5.785 | 5.785 | 33.1743 | 570.6 | 1028.755 | 1197.3105 | -16.3844 | 88.9528 | 883.9553 | 96.2471 | 102.412 | 60.352 | 18.685 | 1.2 | 3.106 | 4.306 | 4.306 | 0.14829 | 0.27868 | 10.6667 | 10.7426 | 10.9848 | 51.7122 | 0.20774 | 5.785 | 6.613 | 108.1181 | 1028.755 | 1423.9535 | 1384.4422 | 2.7748 | 63.9962 | 1206.5986 | 91.0394
[11 empty] | 1998-12-15 | 8:00 | 4633 | 28.772 | 135.628 | 60.63 | 18.756 | 0 | 15.011 | 3.167 |  | 18.178 | 18.178 | 0.82578 | 0 | 13.6464 | 13.7386 | 8.9304 | 70.4426 | 0.19503 | 6.753 | 5.767 | 35.438 | 317.184 | 300.443 | 1413.0148 | 1556.5184 | -10.1558 | 88.2048 | 928.4807 | 96.1832 | 135.628 | 117.63 | 18.756 | 9.371 | 8.201 | 17.572 | 17.572 | 0.34376 | 0.53329 | 14.2344 | 14.3307 | 4.4467 | 103.4263 | 0.13856 | 5.767 | 5.767 | 17.4525 | 300.443 | 566.55 | 623.8066 | -10.1062 | 94.1911 | 462.1248 | 96.2234 | 117.63 | 102.832 | 18.756 | 4.38 | 3.821 | 8.201 | 8.201 | 0.3207 | 0.53408 | 13.3063 | 13.3963 | 8.3911 | 83.0839 | 0.16124 | 5.767 | 5.767 | 33.1577 | 566.55 | 1024.8875 | 1177.9759 | -14.9371 | 88.9637 | 872.2629 | 96.1987 | 102.832 | 60.63 | 18.756 | 1.26 | 3.167 | 4.427 | 4.427 | 0.15194 | 0.28462 | 11.2 | 11.2757 | 10.9968 | 51.9782 | 0.21693 | 5.767 | 6.602 | 107.6659 | 1024.8875 | 1413.0148 | 1389.8067 | 1.6424 | 64.1643 | 1207.3471 | 91.0824
[11 empty] | 1998-12-15 | 20:00 | 4645 | 28.764 | 134.717 | 60.45 | 18.49 | 0 | 14.832 | 3.106 |  | 17.938 | 17.938 | 0.82685 | 0 | 13.4836 | 13.578 | 8.9844 | 70.1091 | 0.19367 | 6.989 | 5.751 | 35.1325 | 316.608 | 300.3451 | 1404.5071 | 1566.808 | -11.5557 | 88.3026 | 933.5765 | 96.2368 | 134.717 | 116.61 | 18.49 | 9.252 | 8.317 | 17.569 | 17.569 | 0.34527 | 0.52661 | 14.0537 | 14.1521 | 4.4 | 102.7735 | 0.1377 | 5.751 | 5.751 | 17.6085 | 300.3451 | 567.9 | 614.8671 | -8.2703 | 94.1372 | 457.6061 | 96.152 | 116.61 | 101.992 | 18.49 | 4.38 | 3.937 | 8.317 | 8.317 | 0.32689 | 0.52663 | 13.3063 | 13.3995 | 8.7864 | 82.0246 | 0.16336 | 5.751 | 5.751 | 3.3178 | 567.9 | 1022.1575 | 1196.0102 | -17.0084 | 98.8953 | 881.9551 | 99.6238 | 101.992 | 60.45 | 18.49 | 1.2 | 3.106 | 4.306 | 4.306 | 0.14829 | 0.27868 | 10.6667 | 10.7413 | 11.202 | 51.529 | 0.20845 | 5.751 | 6.531 | 83.3146 | 1022.1575 | 1404.5071 | 1384.8785 | 1.3975 | 72.2604 | 1203.518 | 93.0774
[11 empty] | 1998-12-16 | 4:00 | 4653 | 28.696 | 134.931 | 61.26 | 18.417 | 0 | 14.711 | 3.107 |  | 17.818 | 17.818 | 0.82563 | 0 | 13.3736 | 13.4944 | 8.9595 | 70.719 | 0.19082 | 7.142 | 5.745 | 34.4745 | 317.856 | 300.541 | 1388.0997 | 1560.3104 | -12.4062 | 88.5292 | 930.4257 | 96.2948 | 134.931 | 117.277 | 18.417 | 9.251 | 8.435 | 17.686 | 17.686 | 0.34841 | 0.52307 | 14.0522 | 14.179 | 4.3851 | 103.3019 | 0.13726 | 5.745 | 5.745 | 17.3355 | 300.541 | 565.2 | 611.1437 | -8.1287 | 94.2319 | 455.8423 | 96.197 | 117.277 | 102.592 | 18.417 | 4.38 | 4.055 | 8.435 | 8.435 | 0.33319 | 0.51926 | 13.3063 | 13.4264 | 8.6534 | 82.8641 | 0.16203 | 5.745 | 5.745 | 3.3172 | 565.2 | 1027.39 | 1172.1165 | -14.0868 | 98.8962 | 868.6583 | 99.6181 | 102.592 | 61.26 | 18.417 | 1.08 | 3.107 | 4.187 | 4.187 | 0.14593 | 0.25794 | 9.6 | 9.6867 | 11.0846 | 52.4244 | 0.18477 | 5.745 | 6.533 | 83.057 | 1027.39 | 1388.0997 | 1355.6422 | 2.3383 | 72.3642 | 1191.5161 | 93.0293
[11 empty] | 1998-12-16 | 12:00 | 4661 | 28.751 | 133.263 | 49.14 | 18.238 | 0 | 14.471 | 3.763 |  | 18.234 | 18.234 | 0.79363 | 0 | 13.1555 | 13.2526 | 7.7707 | 65.1928 | 0.20328 | 7.171 | 5.741 | 33.9105 | 316.224 | 299.7739 | 1372.2993 | 1322.1788 | 3.6523 | 88.688 | 810.9764 | 95.8186 | 133.263 | 114.757 | 18.238 | 9.131 | 8.485 | 17.616 | 17.616 | 0.34814 | 0.51834 | 13.8699 | 13.9723 | 4.345 | 101.427 | 0.13776 | 5.741 | 5.741 | 17.277 | 299.7739 | 556.2 | 603.7786 | -8.5542 | 94.2367 | 451.7762 | 96.1758 | 114.757 | 99.307 | 18.238 | 4.32 | 4.165 | 8.485 | 8.485 | 0.33746 | 0.50913 | 13.1241 | 13.221 | 8.3971 | 80.3969 | 0.16445 | 5.741 | 5.741 | 3.2542 | 556.2 | 958.685 | 1129.7236 | -17.841 | 98.9144 | 842.9618 | 99.614 | 99.307 | 49.14 | 18.238 | 1.02 | 3.763 | 4.783 | 4.783 | 0.17098 | 0.21326 | 9.0667 | 9.1336 | 9.9494 | 46.0361 | 0.1984 | 5.741 | 6.509 | 82.4925 | 958.685 | 1372.2993 | 1196.186 | 12.8334 | 72.4818 | 1077.4355 | 92.3436
[11 empty] | 1998-12-16 | 20:00 | 4669 | 28.692 | 132.827 | 48.982 | 18.156 | 0 | 14.233 | 3.824 |  | 18.057 | 18.057 | 0.78823 | 0 | 12.9391 | 13.0574 | 7.6311 | 65.1174 | 0.20052 | 7.123 | 5.742 | 33.699 | 317.088 | 300.4267 | 1368.6532 | 1293.1923 | 5.5135 | 88.783 | 796.8095 | 95.7708 | 132.827 | 114.637 | 18.156 | 9.073 | 8.61 | 17.683 | 17.683 | 0.3507 | 0.51309 | 13.7818 | 13.9078 | 4.321 | 101.255 | 0.13735 | 5.742 | 5.742 | 17.433 | 300.4267 | 554.4 | 598.6383 | -7.9795 | 94.1973 | 449.5325 | 96.122 | 114.637 | 99.142 | 18.156 | 4.32 | 4.29 | 8.61 | 8.61 | 0.34412 | 0.50174 | 13.1241 | 13.2441 | 8.2865 | 80.447 | 0.16463 | 5.742 | 5.742 | 3.2536 | 554.4 | 964.3725 | 1109.4006 | -15.0386 | 98.917 | 831.9003 | 99.6089 | 99.142 | 48.982 | 18.156 | 0.84 | 3.824 | 4.664 | 4.664 | 0.16982 | 0.1801 | 7.4667 | 7.535 | 9.7872 | 46.1188 | 0.16338 | 5.742 | 6.462 | 82.5082 | 964.3725 | 1368.6532 | 1158.0875 | 15.3849 | 72.5363 | 1061.23 | 92.2252
[11 empty] | 1998-12-17 | 0:21 | 4673.3508 | 28.687 | 139.166 | 51.217 | 18.934 | 0 | 14.773 | 3.825 |  | 18.598 | 18.598 | 0.79433 | 0 | 13.43 | 13.5548 | 7.8235 | 68.434 | 0.19807 | 7.069 | 5.734 | 33.605 | 316.944 | 300.5165 | 1328 | 1331.3879 | -0.25512 | 88.8176 | 815.9522 | 95.8815 | 139.166 | 120.135 | 18.934 | 9.253 | 8.558 | 17.811 | 17.811 | 0.35171 | 0.51951 | 14.0552 | 14.1858 | 4.3684 | 106.3481 | 0.13339 | 5.734 | 5.734 | 16.965 | 300.5165 | 553.05 | 607.0953 | -9.7722 | 94.3547 | 453.8059 | 96.2616 | 120.135 | 103.995 | 18.934 | 4.5 | 4.058 | 8.558 | 8.558 | 0.33655 | 0.52582 | 13.6709 | 13.798 | 8.5463 | 84.5847 | 0.16313 | 5.734 | 5.734 | 3.2549 | 553.05 | 963.4625 | 1162.7292 | -20.6823 | 98.9169 | 857.8896 | 99.6206 | #REF! | 51.217 | 18.934 | 1.02 | 3.825 | 4.845 | 4.845 | 0.17346 | 0.21053 | 9.0667 | 9.1509 | 9.9838 | #REF! | #REF! | 5.734 | 6.41 | 82.5373 | 963.4625 | 1328 | 1198.3759 | 9.7609 | 72.5349 | 1080.9192 | 92.3642
[11 empty] | 1998-12-17 | 16:00 | 4689 | 28.755 | 138.328 | 49.11 | 18.783 | 0 | 15.128 | 3.982 |  | 19.11 | 19.11 | 0.79163 | 0 | 13.7527 | 13.8527 | 7.7481 | 67.1879 | 0.20618 | 7.008 | 5.746 | 32.7355 | 314.208 | 299.9534 | 1396 | 1315.14 | 5.7923 | 89.0865 | 807.5467 | 95.9463 | 138.328 | 119.407 | 18.783 | 9.428 | 8.848 | 18.276 | 18.276 | 0.36178 | 0.51587 | 14.321 | 14.4251 | 4.3373 | 105.7472 | 0.13641 | 5.746 | 5.746 | 16.9845 | 299.9534 | 553.05 | 601.4714 | -8.7553 | 94.3376 | 450.7124 | 96.2316 | 119.407 | 102.922 | 18.783 | 4.56 | 4.288 | 8.848 | 8.848 | 0.35042 | 0.51537 | 13.8532 | 13.9539 | 8.4214 | 83.9601 | 0.1662 | 5.746 | 5.746 | 3.2512 | 553.05 | 955.2725 | 1137.7241 | -19.0994 | 98.9161 | 845.3871 | 99.6154 | #REF! | 49.11 | 18.783 | 1.14 | 3.982 | 5.122 | 5.122 | 0.18215 | 0.22257 | 10.1333 | 10.207 | 9.9821 | #REF! | #REF! | 5.746 | 6.548 | 82.0602 | 955.2725 | 1396 | 1205.263 | 13.6631 | 72.6424 | 1080.2677 | 92.4037
[11 empty] | 1998-12-18 | 0:00 | 4697 | 28.692 | 138.543 | 49.215 | 18.838 | 0 | 15.009 | 3.983 |  | 18.992 | 18.992 | 0.79028 | 0 | 13.6445 | 13.7693 | 7.7175 | 67.3235 | 0.20453 | 7.012 | 5.745 | 32.571 | 315.552 | 300.1574 | 1451.52 | 1308.4941 | 9.8535 | 89.1487 | 804.3258 | 95.9505 | 138.543 | 119.685 | 18.838 | 9.429 | 8.973 | 18.402 | 18.402 | 0.36513 | 0.51239 | 14.3225 | 14.4535 | 4.3228 | 105.9532 | 0.13641 | 5.745 | 5.745 | 16.77 | 300.1574 | 550.8 | 597.9464 | -8.5596 | 94.4129 | 449.0519 | 96.2655 | 119.685 | 103.23 | 18.838 | 4.294 | 4.679 | 8.973 | 8.973 | 0.36419 | 0.47855 | 13.0451 | 13.1644 | 7.9879 | 84.6316 | 0.15555 | 5.745 | 5.745 | 3.2522 | 550.8 | 957.0925 | 1053.2942 | -10.0515 | 98.9165 | 802.0471 | 99.5945 | #REF! | 49.215 | 18.838 | 1.286 | 3.983 | 5.269 | 5.269 | 0.18511 | 0.24407 | 11.4311 | 11.5357 | 10.1623 | #REF! | #REF! | 5.745 | 6.551 | 82.1184 | 957.0925 | 1451.52 | 1239.5973 | 14.6001 | 72.6416 | 1098.3449 | 92.5234
[11 empty] | 1998-12-18 | 8:00 | 4705 | 28.687 | 135.601 | 48.232 | 18.447 | 0 | 14.8 | 3.984 |  | 18.784 | 18.784 | 0.7879 | 0 | 13.4545 | 13.5796 | 7.6358 | 65.8337 | 0.20627 | 6.958 | 5.741 | 32.9 | 316.224 | 300.1248 | 1428.3 | 1292.8274 | 9.4849 | 89.0379 | 796.4761 | 95.8693 | 135.601 | 116.97 | 18.447 | 9.252 | 8.797 | 18.049 | 18.049 | 0.35808 | 0.5126 | 14.0537 | 14.1843 | 4.3197 | 103.5188 | 0.13702 | 5.741 | 5.741 | 17.0235 | 300.1248 | 549.9 | 597.8687 | -8.7232 | 94.3279 | 448.9968 | 96.2085 | 116.97 | 100.837 | 18.447 | 4.267 | 4.53 | 8.797 | 8.797 | 0.35552 | 0.48505 | 12.963 | 13.0835 | 8.0411 | 82.4154 | 0.15875 | 5.741 | 5.741 | 3.2486 | 549.9 | 952.5425 | 1064.8142 | -11.7865 | 98.9176 | 807.3571 | 99.5976 | #REF! | 48.232 | 18.447 | 1.281 | 3.984 | 5.265 | 5.265 | 0.18505 | 0.2433 | 11.3867 | 11.4925 | 10.1027 | #REF! | #REF! | 5.741 | 6.425 | 82.199 | 952.5425 | 1428.3 | 1232.3894 | 13.7163 | 72.6117 | 1092.4659 | 92.4758
[11 empty] | 1998-12-18 | 16:00 | 4713 | 28.764 | 135.28 | 47.985 | 18.478 | 0 | 14.8 | 3.942 |  | 18.742 | 18.742 | 0.78967 | 0 | 13.4545 | 13.5487 | 7.6719 | 65.4826 | 0.20691 | 5.772 | 5.752 | 33.2055 | 312.624 | 299.8474 | 1435.86 | 1300.9381 | 9.3966 | 88.9259 | 800.3927 | 95.8513 | 135.28 | 116.55 | 18.478 | 9.252 | 8.725 | 17.977 | 17.977 | 0.35616 | 0.51466 | 14.0537 | 14.1521 | 4.3266 | 103.1104 | 0.13725 | 5.752 | 5.752 | 17.1015 | 299.8474 | 549.45 | 599.6714 | -9.1403 | 94.2966 | 449.7594 | 96.1976 | 116.55 | 100.522 | 18.478 | 4.267 | 4.458 | 8.725 | 8.725 | 0.35167 | 0.48905 | 12.963 | 13.0538 | 8.076 | 81.982 | 0.15923 | 5.752 | 5.752 | 3.2464 | 549.45 | 947.765 | 1072.2519 | -13.1348 | 98.9173 | 810.8509 | 99.5996 | #REF! | 47.985 | 18.478 | 1.281 | 3.942 | 5.223 | 5.223 | 0.18337 | 0.24526 | 11.3867 | 11.4664 | 10.064 | #REF! | #REF! | 5.752 | 6.45 | 82.0266 | 947.765 | 1435.86 | 1229.0971 | 14.3999 | 72.6439 | 1088.431 | 92.4638
[11 empty] | 1998-12-19 | 0:00 | 4721 | 28.747 | 135.206 | 48.03 | 18.483 | 0 | 14.797 | 3.982 |  | 18.779 | 18.779 | 0.78795 | 0 | 13.4518 | 13.5528 | 7.6208 | 65.5142 | 0.20687 | 6.228 | 5.744 | 33.182 | 312.864 | 299.831 | 1433.7 | 1290.6914 | 9.9748 | 88.9331 | 795.2612 | 95.8275 | 135.206 | 116.49 | 18.483 | 9.253 | 8.723 | 17.976 | 17.976 | 0.35612 | 0.51474 | 14.0552 | 14.1607 | 4.328 | 103.037 | 0.13743 | 5.744 | 5.744 | 17.0235 | 299.831 | 549.45 | 599.8217 | -9.1677 | 94.3223 | 449.8263 | 96.2155 | 116.49 | 100.68 | 18.483 | 4.267 | 4.456 | 8.723 | 8.723 | 0.35157 | 0.48917 | 12.963 | 13.0603 | 8.0772 | 82.0248 | 0.15922 | 5.744 | 5.744 | 3.2464 | 549.45 | 947.5375 | 1072.4865 | -13.1867 | 98.9173 | 810.9683 | 99.5997 | #REF! | 48.03 | 18.483 | 1.277 | 3.982 | 5.259 | 5.259 | 0.18489 | 0.24282 | 11.3511 | 11.4363 | 10.0425 | #REF! | #REF! | 5.744 | 6.485 | 82.0602 | 947.5375 | 1433.7 | 1225.0901 | 14.5505 | 72.6312 | 1086.3138 | 92.446
[11 empty] | 1998-12-19 | 8:00 | 4729 | 28.777 | 135.353 | 48.105 | 18.468 | 0 | 14.808 | 3.982 |  | 18.79 | 18.79 | 0.78808 | 0 | 13.4618 | 13.5508 | 7.6194 | 65.6416 | 0.20644 | 5.768 | 5.748 | 33.229 | 312.672 | 299.7005 | 1426.68 | 1290.6371 | 9.5356 | 88.9126 | 795.1688 | 95.8211 | 135.353 | 116.61 | 18.468 | 9.255 | 8.842 | 18.097 | 18.097 | 0.35932 | 0.51141 | 14.0582 | 14.1512 | 4.3053 | 103.2082 | 0.13711 | 5.748 | 5.748 | 17.082 | 299.7005 | 549.9 | 595.5198 | -8.296 | 94.3003 | 447.6101 | 96.1837 | 116.61 | 100.395 | 18.468 | 4.267 | 4.575 | 8.842 | 8.842 | 0.35792 | 0.48258 | 12.963 | 13.0488 | 8.0158 | 82.0187 | 0.1591 | 5.748 | 5.748 | 3.2466 | 549.9 | 944.125 | 1059.7514 | -12.2469 | 98.9167 | 804.8257 | 99.5966 | #REF! | 48.105 | 18.468 | 1.286 | 3.982 | 5.268 | 5.268 | 0.18507 | 0.24412 | 11.4311 | 11.5067 | 10.0131 | #REF! | #REF! | 5.748 | 6.514 | 82.0266 | 944.125 | 1426.68 | 1222.5425 | 14.3086 | 72.6305 | 1083.3338 | 92.4283
[11 empty] | 1998-12-19 | 16:00 | 4737.0003 | 28.823 | 135.273 | 47.94 | 18.393 | 0 | 14.815 | 3.942 |  | 18.757 | 18.757 | 0.78984 | 0 | 13.4682 | 13.5388 | 7.6656 | 65.5479 | 0.20655 | 5.471 | 5.758 | 33.37 | 311.856 | 299.6189 | 1429.92 | 1300.2473 | 9.0685 | 88.8625 | 799.9331 | 95.8284 | 135.273 | 116.407 | 18.393 | 9.257 | 8.779 | 18.036 | 18.036 | 0.35766 | 0.51325 | 14.0613 | 14.135 | 4.312 | 103.135 | 0.13705 | 5.758 | 5.758 | 17.277 | 299.6189 | 550.8 | 597.3337 | -8.4484 | 94.2337 | 448.4763 | 96.1476 | 116.407 | 100.387 | 18.393 | 4.267 | 4.512 | 8.779 | 8.779 | 0.35456 | 0.48605 | 12.963 | 13.031 | 8.0647 | 81.9393 | 0.15903 | 5.758 | 5.758 | 3.2453 | 550.8 | 941.395 | 1068.6227 | -13.5148 | 98.9169 | 809.7113 | 99.5992 | #REF! | 47.94 | 18.393 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.5358 | 10.0009 | #REF! | #REF! | 5.758 | 6.556 | 82.0243 | 941.395 | 1429.92 | 1222.8378 | 14.4821 | 72.6238 | 1082.1164 | 92.42
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[22 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [16 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [15 empty] | 0 | 0 | 0 | #DIV/0! | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on A1: Catherine Hughes was not part of the EPA reviewing team. All comments from Catherine Hughes are lab verifications.
Note on S56: Pilot not operating from 10/26 until 10/29. No productivity readings were collected.
Note on S57: Pilot assumed to start up again at 7 am of 10/29
Note on V97: No reason can be given for the sudden drop in Pc. Sensor error is possible.
Note on V149: Questionable data. Changed to NR
Note on Z60: Waste flow reported as 3.98. Sensor error is mostly likeky responsible. Being reported as NR.
Note on AA8: No cleaning events took place during this time
Note on AJ58: Slight decrease in MTCw is the result of an increase in NDP. Because the change is so minor, the MTCw is still being reported.
Note on AJ97: Increase in MTCw is the result of a higher NDP. NDP decreased due to an decrease in Pc. Because consectutuve data is at normal levels, the sensor error is unlikely.
Note on DU22: TOC concentration was measured at 12.4 mg/L, aunusually high concentration for the permeate. Lab or sampling error are possible causes of this concnetration. Therefore, it is being reported as NR
Note on DU26: chlorine doses were increased in Quarter 4. Free chlorine residual was measured.
Note on DU33: Value reported as 35.01. This seems high for permeate. Analyticla error likely. Chnaged to NR
Note on DV22: TOC concentration was measured at 24.7 mg/L, aunusually high concentration for the permeate. Lab or sampling error are possible causes of this concnetration. Therefore, it is being reported as NR
Note on DV33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on EO33: Value reported as 39.06. This seems high for permeate. Chnaged to NR
Note on EO39: Lab verified as 37.8. Sample was analyzed on 11/2. Value changed to NR due to unusually high concentration.
Note on EP23: Lab verified
Note on EP33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on FI22: Reported as 14.7. Questionable, so changed to NR
Note on FI33: Reported as 39.36. Questionable value, changed to NR
Note on FI38: All HAA concentrations Lab verified.
Note on FI40: Lab verified as 28.6. However, changed to NR because concentration is unexpectedly high.
Note on FJ33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GC16: Lab data sheets report alkalinity as 14.0. Original lab analysis sheets are not available. Because these results are consistent with weeks 22 and 24, the alkalinity is being reported.
Note on GC22: Sampling error most likely reason for discrepancy
Note on GC23: Incorrectly reported as 0.483. Actually BMRL
Note on GD16: Laboratory Data collection sheets list feed alkalinity as 14.0. However, no actual experimental data sheets are available. Value is being reported as NR, because it is highly unlikely the feed and permeate hardness are the same.
Note on GD27: TSC_ADM: Reviewer changed reported residual of 0.4 mg/L to BMRL, since it was unlikely that the reported residual was actually a measured free chlorine residual based on the reported feed TOC, SDS incubation time and SDS pH.
Note on GD33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GW22: Lab verified. Sampling reason most likely reason for unusually high value Changed to NR
Note on GW23: Lab verified. Value is consistent with other permeate data.
Note on GX33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on HO3: Reviewer DJ: Changed "Week 30" to "Week 28."
Note on HQ11: Reviewer DJ: Changed date from 12/24/98 to 11/24/98
Note on HQ16: Lab data sheets report alkalinity as 14.0. Original lab analysis sheets are not available. Because these results are consistent with weeks 22 and 24, the alkalinity is being reported.
Note on HQ22: This value was originally 8.61. This concentration is high for permeate, indicating possible lab error or contamination. It is being reported as NR
Note on HQ23: Lab verified. Value is consistent with other permeate data.
Note on HR11: Reviewer DJ: Changed date from 12/24/98 to 11/24/98
Note on HR16: Laboratory Data collection sheets list feed alkalinity as 16.0. However, no actual experimental data sheets are available. Value is being reported as NR, because it is highly unlikely the feed and permeate hardness are so similar.
Note on HR22: The feed TOC was within the expected range of values. This value was lab verified.
Note on HR33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on HS11: Reviewer DJ: Changed date from 12/24/98 to 11/24/98
Note on HZ3: Reviewer DJ: Changed "Week 30" to "Week 28."

## Sheet4. Weeks 31-40
FIELD-SET 4: PILOT-SCALE MEMBRANE RESULTS: WEEKS 31-40 (FILE: mempilot.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2a: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: 3-Stage Membrane Pilot System Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-7: System And Stage Water Quality For Week 32 | [9 empty] | Field 4-7: System And Stage Water Quality For Week 32 (continued) | [7 empty] | Field 4-8: System And Stage Water Quality For Week 34 | [9 empty] | Field 4-8: System And Stage Water Quality For Week 34 (continued) | [7 empty] | Field 4-9: System And Stage Water Quality For Week 36 | [9 empty] | Field 4-9: System And Stage Water Quality For Week 36 (continued) | [7 empty] | Field 4-10: System And Stage Water Quality For Week 38 | [9 empty] | Field 4-10: System And Stage Water Quality For Week 38 (continued) | [7 empty] | Field 4-11: System And Stage Water Quality For Week 40 | [9 empty] | Field 4-11: System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 40 | [9 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | Stage 3 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | City of Pompano Beach | Membrane manufacturer | FLUID SYSTEMS CORP. | Average yearly temperature of feed water, TavgoC (oC) | 29 | Alkalinity (mg/L as CaCO3) | 48 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  | STAGE 3 |  |  |  | System recovery during sample collection (decimal) | 0.79 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.79 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.49462 | [6 empty] | System recovery during sample collection (decimal) | 0.8 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 | [6 empty] | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.47012 | [6 empty] | System recovery during sample collection (decimal) | [9 empty] | Stage 1 recovery during sample collection (decimal) | [5 empty] | Cost Parameter | Parameter value
Public Water System Identification Number | FL4131618 | Membrane trade name | FLUID SYSTEMS | Temperature normalized MTCW (gfd/psi) | 0.12621 | Calcium Hardness (mg/L as CaCO3) | 250 | Cartridge filtration | 1 micron | Pilot - scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 17.97 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.25 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.67 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.31 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.2 | [6 empty] | System feed flow rate during sample collection (gpm) | 18.22 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 9.11 | [6 empty] | System feed flow rate during sample collection (gpm) | 17.74 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 8.34 | [6 empty] | System feed flow rate during sample collection (gpm) | [9 empty] | Stage 1 permeate flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Interest Rate (%) | 3
Water Industry Data Base Number (optional) |  | Membrane element model number | 2540 TFCS / 4921 TFCS |  |  | LSI | 0.3 | sulfuric acid addition | pH = 5.7, Dosage= 42 mg/L | Pilot - scale |  | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 17.97 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.73 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.67 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.67 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.6 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.6 | [6 empty] | System influent flow rate during sample collection (gpm) | 18.22 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 18.22 | [6 empty] | System influent flow rate during sample collection (gpm) | 17.74 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 17.74 | [6 empty] | System influent flow rate during sample collection (gpm) | [9 empty] | Stage 1 influent flow rate during sample collection (gpm) | [5 empty] | Capital Recovery Period (years) | 30
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0.1 |  |  |  | 1998-12-20 | 0:00 | 4745 | 28.789 | 135.172 | 48.157 | 18.483 | 0 | 14.819 | 3.943 |  | 18.762 | 18.762 | 0.78984 | 0 | 13.4718 | 13.5561 | 7.6672 | 65.5143 | 0.20692 | 5.461 | 5.75 | 33.276 | 311.904 | 299.5781 | 1430.46 | 1300.4227 | 9.0906 | 88.8924 | 800.0004 | 95.8405 | 135.172 | 116.437 | 18.483 | 9.253 | 8.846 | 18.099 | 18.099 | 0.3594 | 0.51124 | 14.0552 | 14.1431 | 4.3012 | 103.0203 | 0.13728 | 5.75 | 5.75 | 17.16 | 299.5781 | 549.9 | 594.9901 | -8.1997 | 94.2719 | 447.2841 | 96.1635 | 116.437 | 100.335 | 18.483 | 4.28 | 4.566 | 8.846 | 8.846 | 0.35778 | 0.48383 | 13.0025 | 13.0839 | 8.0286 | 81.8744 | 0.1598 | 5.75 | 5.75 | 3.2451 | 549.9 | 940.485 | 1062.3141 | -12.9539 | 98.9168 | 806.1071 | 99.5974 | 100.335 | 48.157 | 18.483 | 1.286 | 3.943 | 5.229 | 5.229 | 0.18351 | 0.24594 | 11.4311 | 11.5026 | 9.9845 | 45.7785 | 0.25127 | 5.75 | 6.553 | 82.031 | 940.485 | 1430.46 | 1220.4677 | 14.6801 | 72.6178 | 1080.4764 | 92.4079 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Design system recovery, R (decimal) | 0.8 | Total iron (mg/L) | 0.3 |  |  |  | 1998-12-20 | 8:00 | 4753 | 28.806 | 135.293 | 47.617 | 18.462 | 0 | 14.806 | 3.982 |  | 18.788 | 18.788 | 0.78806 | 0 | 13.46 | 13.5374 | 7.6113 | 65.3817 | 0.20705 | 5.602 | 5.734 | 32.0775 | 303.504 | 298.2888 | 1385.64 | 1288.1242 | 7.0376 | 89.2462 | 793.2065 | 95.956 | 135.293 | 116.025 | 18.462 | 9.253 | 8.846 | 18.099 | 18.099 | 0.3594 | 0.51124 | 14.0552 | 14.136 | 4.2914 | 102.9056 | 0.13737 | 5.734 | 5.734 | 16.5165 | 298.2888 | 534.6 | 593.0253 | -10.9288 | 94.4629 | 445.6571 | 96.2939 | 116.025 | 100.185 | 18.462 | 4.267 | 4.579 | 8.846 | 8.846 | 0.35813 | 0.48236 | 12.963 | 13.0376 | 7.7895 | 81.8535 | 0.15928 | 5.734 | 5.734 | 3.2321 | 534.6 | 912.9575 | 1029.762 | -12.7941 | 98.9164 | 782.181 | 99.5868 | 100.185 | 47.617 | 18.462 | 1.286 | 3.982 | 5.268 | 5.268 | 0.18507 | 0.24412 | 11.4311 | 11.4969 | 9.6597 | 45.7793 | 0.25114 | 5.734 | 6.443 | 81.2874 | 912.9575 | 1385.64 | 1181.5481 | 14.7291 | 72.7488 | 1047.2528 | 92.238 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Design average system flux, FW (gfd) | 15 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-12-20 | 16:00 | 4761.0003 | 28.798 | 134.811 | 47.557 | 18.495 | 0 | 14.89 | 3.982 |  | 18.872 | 18.872 | 0.789 | 0 | 13.5364 | 13.6174 | 7.6159 | 65.0731 | 0.20926 | 5.544 | 5.728 | 30.4795 | 288.384 | 295.8734 | 1331.1 | 1288.2682 | 3.2178 | 89.6985 | 792.0708 | 96.1519 | 134.811 | 115.882 | 18.495 | 9.318 | 8.658 | 17.976 | 17.976 | 0.35525 | 0.51836 | 14.1539 | 14.2387 | 4.3052 | 102.5463 | 0.13885 | 5.728 | 5.728 | 15.9705 | 295.8734 | 507.6 | 597.1134 | -17.6346 | 94.6023 | 446.4934 | 96.4231 | 115.882 | 99.81 | 18.495 | 4.281 | 4.377 | 8.658 | 8.658 | 0.34773 | 0.49446 | 13.0056 | 13.0835 | 7.5105 | 81.8405 | 0.15987 | 5.728 | 5.728 | 3.2112 | 507.6 | 869.7325 | 1000.9262 | -15.0844 | 98.9147 | 754.2631 | 99.5743 | 99.81 | 47.557 | 18.495 | 1.291 | 3.982 | 5.273 | 5.273 | 0.18517 | 0.24483 | 11.4756 | 11.5443 | 9.1735 | 46.015 | 0.25088 | 5.728 | 6.42 | 80.3466 | 869.7325 | 1331.1 | 1125.6585 | 15.434 | 72.8443 | 997.6955 | 91.9468 | Parameter | Units | Cp-sys-32 | CF-sys-32 | CC-sys-32 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-32 | CI-s1-32 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-34 | CF-sys-34 | CC-sys-34 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-34 | CI-s1-34 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-36 | CF-sys-36 | CC-sys-36 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-36 | CI-s1-36 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-38 | CF-sys-38 | CC-sys-38 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-38 | CI-s1-38 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 | CF-sys-40 | CC-sys-40 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 | CI-s1-40 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 (dup) | CF-sys-40 (dup) | CC-sys-40 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 (dup) | CI-s1-40 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25
|  | Membrane hydrophobicity | HYDRPHILIC | Number of elements per pressure vessel, Ne | 6 | Total aluminum (mg/L) | 0 |  |  |  | 1998-12-21 | 0:00 | 4769 | 28.692 | 134.851 | 47.647 | 18.502 | 0 | 14.824 | 3.942 |  | 18.766 | 18.766 | 0.78994 | 0 | 13.4764 | 13.5996 | 7.6522 | 65.0948 | 0.20892 | 6.099 | 5.728 | 30.4325 | 289.92 | 296.1101 | 1330.02 | 1295.198 | 2.6182 | 89.7226 | 795.654 | 96.1752 | 134.851 | 116.032 | 18.502 | 9.252 | 8.788 | 18.04 | 18.04 | 0.35784 | 0.51286 | 14.0537 | 14.1822 | 4.2778 | 102.6617 | 0.13815 | 5.728 | 5.728 | 15.8535 | 296.1101 | 510.75 | 591.164 | -15.7443 | 94.6461 | 443.637 | 96.4265 | 116.032 | 99.945 | 18.502 | 4.281 | 4.507 | 8.788 | 8.788 | 0.35466 | 0.48714 | 13.0056 | 13.1245 | 7.4858 | 82.0007 | 0.16005 | 5.728 | 5.728 | 3.2125 | 510.75 | 873.145 | 992.8374 | -13.7082 | 98.9151 | 751.7937 | 99.5727 | 99.945 | 47.647 | 18.502 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.5805 | 9.2258 | 46.0682 | 0.25138 | 5.728 | 6.392 | 80.3757 | 873.145 | 1330.02 | 1132.7759 | 14.8302 | 72.8561 | 1002.9605 | 91.9862 | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-06 | 1999-01-06 | 1999-01-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-06 | 1999-01-06 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-04 | 1999-02-04 | 1999-02-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-04 | 1999-02-04 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  |  | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY |  |  | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 7
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.1 |  |  |  | 1998-12-21 | 8:00 | 4777.0003 | 28.853 | 134.549 | 47.355 | 18.468 | 0 | 14.812 | 3.942 |  | 18.754 | 18.754 | 0.7898 | 0 | 13.4655 | 13.5241 | 7.6401 | 64.8439 | 0.20856 | 5.829 | 5.732 | 29.986 | 286.944 | 295.3838 | 1306.8 | 1292.6118 | 1.0857 | 89.8485 | 793.9978 | 96.2234 | 134.549 | 115.762 | 18.468 | 9.254 | 8.72 | 17.974 | 17.974 | 0.35605 | 0.51485 | 14.0567 | 14.1179 | 4.2791 | 102.4084 | 0.13786 | 5.732 | 5.732 | 15.8145 | 295.3838 | 502.65 | 592.0736 | -17.7904 | 94.6461 | 443.7287 | 96.436 | 115.762 | 99.75 | 18.468 | 4.267 | 4.453 | 8.72 | 8.72 | 0.35141 | 0.48933 | 12.963 | 13.0195 | 7.3874 | 81.9006 | 0.15897 | 5.732 | 5.732 | 3.2044 | 502.65 | 861.0875 | 981.234 | -13.9529 | 98.9152 | 741.942 | 99.5681 | 99.75 | 47.355 | 18.468 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.5255 | 9.0896 | 45.9949 | 0.25058 | 5.732 | 6.431 | 80.024 | 861.0875 | 1306.8 | 1116.8848 | 14.5328 | 72.9085 | 988.9862 | 91.9085 | Sampling time | hh:mm | 8:00 | 8:00 | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | 14:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 2:00 | 2:00 | 2:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 2:00 | 2:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm |  |  |  | --- | --- | --- | --- | --- | Sampling time | hh:mm |  |  | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 3391
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-12-21 | 16:00 | 4785 | 28.964 | 134.663 | 47.467 | 18.538 | 0 | 14.88 | 3.942 |  | 18.822 | 18.822 | 0.79056 | 0 | 13.5273 | 13.5417 | 7.6617 | 64.8653 | 0.20877 | 5.977 | 5.738 | 30.08 | 286.704 | 295.4328 | 1313.28 | 1297.0689 | 1.2344 | 89.8183 | 796.2509 | 96.2223 | 134.663 | 115.807 | 18.538 | 9.313 | 8.664 | 17.977 | 17.977 | 0.35534 | 0.51805 | 14.1463 | 14.1614 | 4.2966 | 102.4004 | 0.13829 | 5.738 | 5.738 | 15.9705 | 295.4328 | 503.55 | 595.829 | -18.3257 | 94.5942 | 445.6309 | 96.4162 | 115.807 | 99.795 | 18.538 | 4.281 | 4.383 | 8.664 | 8.664 | 0.34805 | 0.49411 | 13.0056 | 13.0194 | 7.447 | 81.816 | 0.15913 | 5.738 | 5.738 | 3.2046 | 503.55 | 861.9975 | 992.2515 | -15.1107 | 98.9153 | 747.9007 | 99.5715 | 99.795 | 47.467 | 18.538 | 1.286 | 3.942 | 5.228 | 5.228 | 0.18347 | 0.24598 | 11.4311 | 11.4433 | 9.0948 | 45.9982 | 0.24878 | 5.738 | 6.47 | 80.0666 | 861.9975 | 1313.28 | 1117.0871 | 14.9392 | 72.8986 | 989.5423 | 91.9087 | Operation time | hh.hh | 5063 | 5063 | 5063 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5063 | 5063 | --- | --- | --- | --- | Operation time | hh.hh | 5454 | 5454 | 5454 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5454 | 5454 | --- | --- | --- | --- | Operation time | hh.hh | 5875 | 5875 | 5875 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5875 | 5875 | --- | --- | --- | --- | Operation time | hh.hh | 6137 | 6137 | 6137 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6137 | 6137 | --- | --- | --- | --- | Operation time | hh.hh | 6574 | 6574 | 6574 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6574 | 6574 | --- | --- | --- | --- | Operation time | hh.hh |  |  |  | --- | --- | --- | --- | --- | Operation time | hh.hh |  |  | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 267.13
E-Mail Address (optional) |  | Design Parameters |  | Number of parallel pressure vessels in stage 3, Nv-s(3) | 1 | Sulfate (mg/L) | 8.9 |  |  |  | 1998-12-22 | 0:00 | 4793 | 28.964 | 134.744 | 47.617 | 18.552 | 0 | 14.875 | 3.942 |  | 18.817 | 18.817 | 0.79051 | 0 | 13.5227 | 13.5371 | 7.666 | 64.9625 | 0.20838 | 6.108 | 5.737 | 29.9625 | 287.232 | 295.5226 | 1313.28 | 1297.6042 | 1.1936 | 89.8612 | 796.5634 | 96.2385 | 134.744 | 115.725 | 18.552 | 9.317 | 8.72 | 18.037 | 18.037 | 0.35689 | 0.51655 | 14.1524 | 14.1675 | 4.2917 | 102.3908 | 0.13837 | 5.737 | 5.737 | 15.795 | 295.5226 | 502.2 | 594.4012 | -18.3595 | 94.6552 | 444.9619 | 96.4503 | 115.725 | 99.697 | 18.552 | 4.267 | 4.453 | 8.72 | 8.72 | 0.35141 | 0.48933 | 12.963 | 12.9768 | 7.3807 | 81.7783 | 0.15868 | 5.737 | 5.737 | 3.2058 | 502.2 | 862.68 | 980.3514 | -13.6402 | 98.9152 | 741.2757 | 99.5675 | 99.697 | 47.617 | 18.552 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4878 | 9.1069 | 45.9981 | 0.24974 | 5.737 | 6.441 | 80.1338 | 862.68 | 1313.28 | 1118.9629 | 14.7963 | 72.884 | 990.8215 | 91.9124 | pH | --- | 4.85 | 5.5 | 4.89 | --- | --- | --- | --- | --- | pH | --- | 4.7 | 5.5 | --- | --- | --- | --- | pH | --- | 5.5 | 5.51 | 5.62 | --- | --- | --- | --- | --- | pH | --- | 4.92 | 5.51 | --- | --- | --- | --- | pH | --- | 4.68 | 5.55 | 5.9 | --- | --- | --- | --- | --- | pH | --- | 4.8 | 5.55 | --- | --- | --- | --- | pH | --- | 4.9 | 5.29 | 5.5 | --- | --- | --- | --- | --- | pH | --- | 4.8 | 5.9 | --- | --- | --- | --- | pH | --- | 5.69 | 5.97 | 6.14 | --- | --- | --- | --- | --- | pH | --- | 5.83 | 5.97 | --- | --- | --- | --- | pH | --- |  |  |  | --- | --- | --- | --- | --- | pH | --- |  |  | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 25
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4" x 40" | Permeate flow rate per element, Qp-e (gpm) | 0.82292 | Calcium (mg/L) | 252 |  |  |  | 1998-12-22 | 8:00 | 4801 | 28.985 | 134.67 | 47.43 | 18.498 | 0 | 14.811 | 3.942 |  | 18.753 | 18.753 | 0.78979 | 0 | 13.4645 | 13.4705 | 7.6445 | 64.9075 | 0.20753 | 6.054 | 5.729 | 29.9625 | 287.28 | 295.5226 | 1310.04 | 1293.2927 | 1.2784 | 89.8612 | 794.4076 | 96.2283 | 134.67 | 115.68 | 18.498 | 9.253 | 8.849 | 18.102 | 18.102 | 0.35948 | 0.51116 | 14.0552 | 14.0614 | 4.2547 | 102.4223 | 0.13729 | 5.729 | 5.729 | 16.1265 | 295.5226 | 502.2 | 587.6744 | -17.02 | 94.5431 | 441.5985 | 96.3482 | 115.68 | 99.555 | 18.498 | 4.267 | 4.582 | 8.849 | 8.849 | 0.35829 | 0.4822 | 12.963 | 12.9688 | 7.3134 | 81.8061 | 0.15853 | 5.729 | 5.729 | 3.2059 | 502.2 | 861.0875 | 966.8896 | -12.287 | 98.9152 | 734.5448 | 99.5635 | 99.555 | 47.43 | 18.498 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4806 | 9.0883 | 45.9062 | 0.25009 | 5.729 | 6.429 | 80.1405 | 861.0875 | 1310.04 | 1116.8467 | 14.7471 | 72.8818 | 988.9671 | 91.8965 | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC | 29 | 29 | 29 | --- | --- | --- | --- | --- | Temperature | oC | 29 | 29 | --- | --- | --- | --- | Temperature | oC |  |  |  | --- | --- | --- | --- | --- | Temperature | oC |  |  | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 50
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 79 | Permeate flow rate per pressure vessel, Qp-v (gpm) | 4.9375 | Barium (mg/L) | 0.049 |  |  |  | 1998-12-22 | 16:00 | 4809 | 29.023 | 134.523 | 47.497 | 18.6 | 0 | 14.823 | 3.942 |  | 18.765 | 18.765 | 0.78993 | 0 | 13.4755 | 13.4663 | 7.6355 | 64.7745 | 0.20789 | 6.558 | 5.725 | 30.456 | 287.424 | 295.5634 | 1315.98 | 1292.4397 | 1.7888 | 89.6956 | 794.0015 | 96.1642 | 134.523 | 115.522 | 18.6 | 9.252 | 8.908 | 18.16 | 18.16 | 0.36104 | 0.50947 | 14.0537 | 14.0441 | 4.2434 | 102.1791 | 0.13745 | 5.725 | 5.725 | 16.263 | 295.5634 | 503.1 | 585.6495 | -16.4082 | 94.4976 | 440.6064 | 96.309 | 115.522 | 99.562 | 18.6 | 4.28 | 4.628 | 8.908 | 8.908 | 0.36109 | 0.48047 | 13.0025 | 12.9937 | 7.3105 | 81.6315 | 0.15917 | 5.725 | 5.725 | 3.2061 | 503.1 | 861.5425 | 965.4046 | -12.0554 | 98.9153 | 734.2523 | 99.5634 | 99.562 | 47.497 | 18.6 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4678 | 9.0931 | 45.8364 | 0.25019 | 5.725 | 6.432 | 80.183 | 861.5425 | 1315.98 | 1117.4367 | 15.0871 | 72.8711 | 989.4896 | 91.8965 | Alkalinity | mg/L as CaCO3 | 20 | 48 | 158 | 153.3333 | 2.9536 | 58.3333 | 100.6667 | 80.1325 | Alkalinity | mg/L as CaCO3 | 16 | 48 | 82.9057 | 66.6667 | 65.4528 | 75.5549 | Alkalinity | mg/L as CaCO3 | NR | NR | 32 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 14 | 74 | 140.8182 | #VALUE! | 107.4091 | 86.9657 | Alkalinity | mg/L as CaCO3 | 18 | 52 | 160 | 179.9048 | -12.4405 | 65.3846 | 115.9524 | 84.4764 | Alkalinity | mg/L as CaCO3 | 14 | 52 | 89.1915 | 73.0769 | 70.5957 | 80.1688 | Alkalinity | mg/L as CaCO3 | 16 | 54 | 160 | 206 | -28.75 | 70.3704 | 130 | 87.6923 | Alkalinity | mg/L as CaCO3 | 14 | 160 | 306 | 74.0741 | 233 | 93.9914 | Alkalinity | mg/L as CaCO3 | 12 | 36 | 88 | 145.3333 | -65.1515 | 66.6667 | 90.6667 | 86.7647 | Alkalinity | mg/L as CaCO3 | 18 | 36 | 51.9702 | 50 | 43.9851 | 59.0771 | Alkalinity | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Electric Rate ($/kW-h) | 0.07
Mailing Address |  | Design flux, FW (gfd) | 17.9 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.875 | Strontium (mg/L) | 0.4 |  |  |  | 1998-12-23 | 0:00 | 4817 | 28.998 | 134.851 | 47.49 | 18.529 | 0 | 14.887 | 3.942 |  | 18.829 | 18.829 | 0.79064 | 0 | 13.5336 | 13.5344 | 7.663 | 64.9785 | 0.20829 | 6.801 | 5.721 | 30.3385 | 288.048 | 295.6531 | 1315.98 | 1297.6163 | 1.3954 | 89.7385 | 796.6347 | 96.1917 | 134.851 | 115.717 | 18.529 | 9.315 | 8.787 | 18.102 | 18.102 | 0.35865 | 0.51458 | 14.1494 | 14.1502 | 4.2769 | 102.4781 | 0.13808 | 5.721 | 5.721 | 16.1265 | 295.6531 | 505.8 | 591.9762 | -17.0376 | 94.5455 | 443.8146 | 96.3664 | 115.717 | 99.63 | 18.529 | 4.281 | 4.506 | 8.787 | 8.787 | 0.35461 | 0.4872 | 13.0056 | 13.0063 | 7.4134 | 81.7311 | 0.15914 | 5.721 | 5.721 | 3.2074 | 505.8 | 868.14 | 983.2964 | -13.2647 | 98.9151 | 744.5482 | 99.5692 | 99.63 | 47.49 | 18.529 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4762 | 9.17 | 45.861 | 0.25024 | 5.721 | 6.401 | 80.1718 | 868.14 | 1315.98 | 1126.1986 | 14.4213 | 72.8831 | 997.1693 | 91.9601 | Total dissolved solids | mg/L | 33.2 | 326 | 1160 | 1427.4857 | -23.0591 | 89.816 | 876.7429 | 96.2133 | Total dissolved solids | mg/L | 25.9 | 326 | 653.3496 | 92.0552 | 489.6748 | 94.7108 | Total dissolved solids | mg/L | 37.1 | 384 | 1270 | 1862.8895 | -46.6842 | 90.3385 | 1123.4447 | 96.6977 | Total dissolved solids | mg/L | 29.7 | 384 | 778.5614 | 92.2656 | 581.2807 | 94.8906 | Total dissolved solids | mg/L | 36.2 | 378 | 1330 | 1663.819 | -25.0992 | 90.4233 | 1020.9095 | 96.4541 | Total dissolved solids | mg/L | 28.9 | 378 | 719.6723 | 92.3545 | 548.8362 | 94.7343 | Total dissolved solids | mg/L | 36.3 | 376 | 1330 | 1734.8 | -30.4361 | 90.3457 | 1055.4 | 96.5605 | Total dissolved solids | mg/L | 28.9 | 2780 | 5531.1 | 92.3138 | 4155.55 | 99.3045 | Total dissolved solids | mg/L | 39.2 | NR | 1500 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 33 | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fuel Oil Rate ($/gal) | 0.89
|  | Net driving pressure at the design flux, NDP (psi) | 80 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.9375 | Reactive silica (mg/L as SiO2) | 6.29 |  |  |  | 1998-12-23 | 8:00 | 4825.0003 | 28.972 | 134.65 | 47.595 | 18.487 | 0 | 14.884 | 3.943 |  | 18.827 | 18.827 | 0.79057 | 0 | 13.5309 | 13.5421 | 7.6654 | 64.9701 | 0.20844 | 6.813 | 5.729 | 30.315 | 288.048 | 295.7918 | 1315.98 | 1297.9114 | 1.373 | 89.7512 | 796.8516 | 96.1957 | 134.65 | 115.777 | 18.487 | 9.313 | 8.664 | 17.977 | 17.977 | 0.35534 | 0.51805 | 14.1463 | 14.158 | 4.3003 | 102.4262 | 0.13823 | 5.729 | 5.729 | 16.0875 | 295.7918 | 505.8 | 596.4482 | -17.9217 | 94.5612 | 446.12 | 96.3939 | 115.777 | 99.697 | 18.487 | 4.28 | 4.384 | 8.664 | 8.664 | 0.34807 | 0.494 | 13.0025 | 13.0133 | 7.4793 | 81.7707 | 0.15914 | 5.729 | 5.729 | 3.2074 | 505.8 | 867.9125 | 996.4698 | -14.8122 | 98.9157 | 751.1349 | 99.573 | 99.697 | 47.595 | 18.487 | 1.291 | 3.943 | 5.234 | 5.234 | 0.18361 | 0.24666 | 11.4756 | 11.4851 | 9.1666 | 45.9924 | 0.24972 | 5.729 | 6.376 | 80.2077 | 867.9125 | 1315.98 | 1125.8194 | 14.4501 | 72.8837 | 996.866 | 91.954 | Total hardness | mg/L as CaCO3 | 18 | 320 | 1280 | 1456.0952 | -13.7574 | 94.375 | 888.0476 | 97.9731 | Total hardness | mg/L as CaCO3 | 18 | 320 | 649.4222 | 94.375 | 484.7111 | 96.2864 | Total hardness | mg/L as CaCO3 | 20 | 340 | 1700 | 1704.2105 | -0.24768 | 94.1176 | 1022.1053 | 98.0433 | Total hardness | mg/L as CaCO3 | 12 | 340 | 705.2727 | 96.4706 | 522.6364 | 97.7039 | Total hardness | mg/L as CaCO3 | 14 | 288 | 1240 | 1318.7619 | -6.3518 | 95.1389 | 803.381 | 98.2574 | Total hardness | mg/L as CaCO3 | 10 | 288 | 560.0851 | 96.5278 | 424.0426 | 97.6417 | Total hardness | mg/L as CaCO3 | 16 | 290 | 1240 | 1386 | -11.7742 | 94.4828 | 838 | 98.0907 | Total hardness | mg/L as CaCO3 | 10 | 1240 | 2470 | 96.5517 | 1855 | 99.4609 | Total hardness | mg/L as CaCO3 | 18 | 320 | 1680 | 1695.7778 | -0.93915 | 94.375 | 1007.8889 | 98.2141 | Total hardness | mg/L as CaCO3 | 16 | 320 | 589.7191 | 95 | 454.8596 | 96.4824 | Total hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 4.9375 | Turbidity (ntu) | 0.24 |  |  |  | 1998-12-23 | 16:00 | 4833.0003 | 29.027 | 134.409 | 47.505 | 18.469 | 0 | 14.886 | 3.942 |  | 18.828 | 18.828 | 0.79063 | 0 | 13.5327 | 13.5219 | 7.6579 | 64.8301 | 0.20858 | 6.887 | 5.732 | 30.362 | 287.232 | 295.5144 | 1318.14 | 1296.7977 | 1.6191 | 89.7257 | 796.156 | 96.1864 | 134.409 | 115.62 | 18.469 | 9.314 | 8.783 | 18.097 | 18.097 | 0.35853 | 0.51467 | 14.1478 | 14.1366 | 4.275 | 102.2705 | 0.13823 | 5.732 | 5.732 | 16.146 | 295.5144 | 506.25 | 591.7728 | -16.8934 | 94.5363 | 443.6436 | 96.3606 | 115.62 | 99.577 | 18.469 | 4.281 | 4.502 | 8.783 | 8.783 | 0.3544 | 0.48742 | 13.0056 | 12.9952 | 7.4222 | 81.7073 | 0.15905 | 5.732 | 5.732 | 3.2075 | 506.25 | 864.955 | 984.5985 | -13.8323 | 98.9146 | 745.4243 | 99.5697 | 99.577 | 47.505 | 18.469 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4664 | 9.1329 | 45.9391 | 0.2496 | 5.732 | 6.378 | 80.1763 | 864.955 | 1318.14 | 1121.969 | 14.8824 | 72.8689 | 993.462 | 91.9296 | Calcium hardness | mg/L as CaCO3 | 16 | 310 | 1260 | 1416 | -12.381 | 94.8387 | 863 | 98.146 | Calcium hardness | mg/L as CaCO3 | 16 | 310 | 630.6958 | 94.8387 | 470.3479 | 96.5983 | Calcium hardness | mg/L as CaCO3 | 18 | 328 | 1400 | 1649.5789 | -17.8271 | 94.5122 | 988.7895 | 98.1796 | Calcium hardness | mg/L as CaCO3 | 12 | 328 | 679.9091 | 96.3415 | 503.9545 | 97.6188 | Calcium hardness | mg/L as CaCO3 | 14 | 276 | 1100 | 1261.619 | -14.6926 | 94.9275 | 768.8095 | 98.179 | Calcium hardness | mg/L as CaCO3 | 10 | 276 | 536.3404 | 96.3768 | 406.1702 | 97.538 | Calcium hardness | mg/L as CaCO3 | 14 | 278 | 1100 | 1334 | -21.2727 | 94.964 | 806 | 98.263 | Calcium hardness | mg/L as CaCO3 | 10 | 1100 | 2190 | 96.4029 | 1645 | 99.3921 | Calcium hardness | mg/L as CaCO3 | 18 | 300 | 1500 | 1584.6667 | -5.6444 | 94 | 942.3333 | 98.0898 | Calcium hardness | mg/L as CaCO3 | 12 | 300 | 555.5234 | 96 | 427.7617 | 97.1947 | Calcium hardness | mg/L as CaCO3 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Current Process Water Rate ($/1000 gal) | 0.95
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Permeate flow rate from system, Qp-sys (gpm) | 19.75 | SDI | 2.5 |  |  |  | 1998-12-24 | 0:00 | 4841 | 28.845 | 134.904 | 47.617 | 18.441 | 0 | 14.813 | 3.943 |  | 18.756 | 18.756 | 0.78977 | 0 | 13.4664 | 13.5282 | 7.6498 | 65.1697 | 0.20758 | 6.69 | 5.715 | 30.7615 | 292.368 | 296.5262 | 1340.82 | 1294.947 | 3.4213 | 89.626 | 795.7366 | 96.1342 | 134.904 | 116.197 | 18.441 | 9.255 | 8.784 | 18.039 | 18.039 | 0.35777 | 0.51306 | 14.0582 | 14.1228 | 4.2809 | 102.8286 | 0.13734 | 5.715 | 5.715 | 16.146 | 296.5262 | 514.35 | 591.9405 | -15.0852 | 94.555 | 444.2334 | 96.3654 | 116.197 | 100.012 | 18.441 | 4.267 | 4.517 | 8.784 | 8.784 | 0.35482 | 0.48577 | 12.963 | 13.0226 | 7.5255 | 82.138 | 0.15855 | 5.715 | 5.715 | 3.2172 | 514.35 | 884.52 | 997.1934 | -12.7384 | 98.915 | 755.7717 | 99.5743 | 100.012 | 47.617 | 18.441 | 1.291 | 3.943 | 5.234 | 5.234 | 0.18361 | 0.24666 | 11.4756 | 11.5283 | 9.3551 | 46.0184 | 0.25051 | 5.715 | 6.327 | 80.6131 | 884.52 | 1340.82 | 1147.7317 | 14.4008 | 72.8142 | 1016.1259 | 92.0666 | Turbidity | ntu | 0.07 | 0.138 | 63 | 0.39381 | 99.3749 | 49.2754 | 0.2659 | 73.6748 | Turbidity | ntu | 0.261 | 0.138 | 0.0038314 | -89.1304 | 0.070916 | -268.0427 | Turbidity | ntu | 0.59 | 6.08 | 56 | 29.4847 | 47.3487 | 90.2961 | 17.7824 | 96.6821 | Turbidity | ntu | 0.396 | 6.08 | 12.4099 | 93.4868 | 9.245 | 95.7166 | Turbidity | ntu | 0.932 | 1.88 | 26 | 5.4463 | 79.0527 | 50.4255 | 3.6631 | 74.5574 | Turbidity | ntu | 0.485 | 1.88 | 3.2453 | 74.2021 | 2.5627 | 81.0743 | Turbidity | ntu | 0.14 | 1.89 | 26 | 8.89 | 65.8077 | 92.5926 | 5.39 | 97.4026 | Turbidity | ntu | 0.48 | 26 | 51.52 | 74.6032 | 38.76 | 98.7616 | Turbidity | ntu | 0.15 | 1.35 | 37.5 | 6.8167 | 81.8222 | 88.8889 | 4.0833 | 96.3265 | Turbidity | ntu | 0.1 | 1.35 | 2.459 | 92.5926 | 1.9045 | 94.7493 | Turbidity | ntu |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Modifications to Existing Plant (% of construction costs) | 75
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 16 | Feed flow rate to system, QF-sys (gpm) | 24.6875 | MFI |  |  |  |  | 1998-12-24 | 8:00 | 4849 | 28.781 | 134.851 | 47.715 | 18.474 | 0 | 14.81 | 3.943 |  | 18.753 | 18.753 | 0.78974 | 0 | 13.4636 | 13.5511 | 7.6396 | 65.1694 | 0.20794 | 6.848 | 5.709 | 30.8085 | 290.736 | 296.257 | 1468.8 | 1293.2876 | 11.9494 | 89.6008 | 794.7723 | 96.1236 | 134.851 | 116.145 | 18.474 | 9.252 | 8.721 | 17.973 | 17.973 | 0.35605 | 0.51477 | 14.0537 | 14.1449 | 4.2863 | 102.7377 | 0.13768 | 5.709 | 5.709 | 16.185 | 296.257 | 514.8 | 593.3818 | -15.2645 | 94.5368 | 444.8194 | 96.3614 | 116.145 | 99.915 | 18.474 | 4.267 | 4.454 | 8.721 | 8.721 | 0.35146 | 0.48928 | 12.963 | 13.0472 | 7.5664 | 81.9896 | 0.15913 | 5.709 | 5.709 | 3.2159 | 514.8 | 877.24 | 1004.9054 | -14.5531 | 98.9145 | 759.8527 | 99.5768 | 99.915 | 47.715 | 18.474 | 1.291 | 3.943 | 5.234 | 5.234 | 0.18361 | 0.24666 | 11.4756 | 11.5501 | 9.2718 | 46.0692 | 0.25071 | 5.709 | 6.292 | 80.4944 | 877.24 | 1468.8 | 1138.107 | 22.5145 | 72.8295 | 1007.6735 | 92.0119 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 3.95 | 15.7 | 28.5169 | 74.8408 | 22.1085 | 82.1335 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.94 | 4.82 | 8.0273 | #VALUE! | 6.4236 | 69.799 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 13.9 | 37.9 | 61.3894 | #VALUE! | 49.6447 | 72.001 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.39 | 191 | 380.61 | 87.2477 | 285.805 | 99.5137 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Concentrate-waste flow rate from system, QW-sys (gpm) | 4.9375 | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-12-24 | 16:00 | 4857 | 28.772 | 136.432 | 57.855 | 18.805 | 0 | 14.958 | 3.405 |  | 18.363 | 18.363 | 0.81457 | 0 | 13.5982 | 13.6901 | 8.4705 | 69.868 | 0.19594 | 6.856 | 5.708 | 31.302 | 290.88 | 296.2978 | 1471.5 | 1460.4113 | 0.75356 | 89.4356 | 878.3545 | 96.4363 | 136.432 | 117.847 | 18.805 | 9.373 | 8.55 | 17.923 | 17.923 | 0.3531 | 0.52296 | 14.2375 | 14.3337 | 4.3401 | 103.9944 | 0.13783 | 5.708 | 5.708 | 15.951 | 296.2978 | 522 | 603.6299 | -15.6379 | 94.6166 | 449.9639 | 96.455 | 117.847 | 102.697 | 18.805 | 4.28 | 4.27 | 8.55 | 8.55 | 0.34199 | 0.50058 | 13.0025 | 13.0905 | 7.7872 | 83.6798 | 0.15644 | 5.708 | 5.708 | 3.2601 | 522 | 921.6025 | 1041.9547 | -13.059 | 98.8997 | 781.9774 | 99.5831 | 102.697 | 57.855 | 18.805 | 1.305 | 3.405 | 4.71 | 4.71 | 0.16236 | 0.27707 | 11.6 | 11.6784 | 10.0206 | 51.4504 | 0.22698 | 5.708 | 6.344 | 80.687 | 921.6025 | 1471.5 | 1243.8917 | 15.4678 | 72.7683 | 1082.7471 | 92.5479 | Total organic carbon | mg/L | BMRL | 15.7 | 75.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.531 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | NR | 97.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.508 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | NR | NR | 191 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.581 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.35 | 10.9 | 191 | 49.1 | 74.2932 | 87.6147 | 30 | 95.5 | UV254 | cm-1 | BMRL | 2.62 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.01 | 13 | 84 | 72.1767 | 14.0754 | 99.9231 | 42.5883 | 99.9765 | UV254 | cm-1 | 0.001 | NR | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Plant Name | Pompano Beach WTP | Total width of all membrane envelopes in the element, w (ft) | 14.4 |  |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-12-25 | 0:00 | 4865 | 28.734 | 136.358 | 58.065 | 18.898 | 0 | 14.959 | 3.284 |  | 18.243 | 18.243 | 0.81999 | 0 | 13.5991 | 13.7064 | 8.6945 | 69.619 | 0.19688 | 6.846 | 5.716 | 31.2785 | 291.648 | 296.5507 | 1474.2 | 1504.8964 | -2.0822 | 89.4526 | 900.7235 | 96.5274 | 136.358 | 118.02 | 18.898 | 9.37 | 8.664 | 18.034 | 18.034 | 0.3561 | 0.51957 | 14.2329 | 14.3453 | 4.3194 | 103.9716 | 0.13797 | 5.716 | 5.716 | 16.2045 | 296.5507 | 522.9 | 599.7414 | -14.6952 | 94.5357 | 448.1461 | 96.3841 | 118.02 | 102.75 | 18.898 | 4.293 | 4.371 | 8.664 | 8.664 | 0.34773 | 0.4955 | 13.042 | 13.145 | 7.7482 | 83.7388 | 0.15698 | 5.716 | 5.716 | 3.2599 | 522.9 | 925.015 | 1033.2672 | -11.7027 | 98.9007 | 778.0836 | 99.581 | 102.75 | 58.065 | 18.898 | 1.296 | 3.284 | 4.58 | 4.58 | 0.15734 | 0.28297 | 11.52 | 11.6109 | 10.1092 | 51.4003 | 0.22589 | 5.716 | 6.214 | 80.6938 | 925.015 | 1474.2 | 1258.2185 | 14.6508 | 72.7892 | 1091.6168 | 92.6079 | UV254 | cm-1 | 0.009 | 0.531 | 2.6 | 2.4947 | 4.0495 | 98.3051 | 1.5129 | 99.4051 | SUVA | L/(mg*m) | #VALUE! | 3.3822 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | NR | 2.57 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 10.5394 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.581 | 2.62 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 1.533 | --- | --- | --- | --- | UV254 | cm-1 | 0.015 | 0.501 | 2.62 | 2.445 | 6.6794 | 97.006 | 1.473 | 98.9817 | SUVA | L/(mg*m) | #VALUE! | 1.3717 | --- | --- | --- | --- | UV254 | cm-1 | 0.003 | NR | 3.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | #VALUE! | --- | --- | --- | --- | UV254 | cm-1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
Treatment Plant Category | CONV | Feed spacer thickness, T (ft) | 0.0029 | Calculate the Feed Flow Rates at the End of Each Stage |  |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-12-25 | 8:00 | 4873.0003 | 28.747 | 134.127 | 41.032 | 18.253 | 0 | 14.784 | 3.983 |  | 18.767 | 18.767 | 0.78777 | 0 | 13.44 | 13.5409 | 7.5974 | 61.7291 | 0.21936 | 6.84 | 5.755 | 30.3385 | 292.272 | 296.363 | 1377.54 | 1283.7863 | 6.8059 | 89.7631 | 790.0747 | 96.16 | 134.127 | 115.17 | 18.253 | 9.254 | 8.78 | 18.034 | 18.034 | 0.35765 | 0.51314 | 14.0567 | 14.1622 | 4.2807 | 102.1148 | 0.13869 | 5.755 | 5.755 | 16.029 | 296.363 | 509.4 | 591.8313 | -16.182 | 94.5914 | 444.0972 | 96.3907 | 115.17 | 98.452 | 18.253 | 4.254 | 4.526 | 8.78 | 8.78 | 0.35496 | 0.48451 | 12.9235 | 13.0206 | 7.441 | 81.117 | 0.16052 | 5.755 | 5.755 | 3.191 | 509.4 | 858.13 | 985.1872 | -14.8063 | 98.9233 | 747.2936 | 99.573 | 98.452 | 41.032 | 18.253 | 1.276 | 3.983 | 5.259 | 5.259 | 0.18491 | 0.24263 | 11.3422 | 11.4274 | 9.022 | 42.467 | 0.26909 | 5.755 | 6.113 | 80.4899 | 858.13 | 1377.54 | 1107.256 | 19.6208 | 72.8408 | 982.693 | 91.8093 | SUVA | L/(mg*m) | #VALUE! | 3.3822 | 3.4346 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | 2.644 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | 1.3717 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 1.1111 | 4.5963 | 1.3717 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | 30 | #VALUE! | 3.7262 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | #DIV/0! | --- | --- | --- | --- | ---
Process Train Name | Conventional train | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 16.4583 | [5 empty] | 1998-12-25 | 16:00 | 4881 | 28.794 | 134.683 | 41.212 | 18.354 | 0 | 14.726 | 3.981 |  | 18.707 | 18.707 | 0.78719 | 0 | 13.3873 | 13.469 | 7.575 | 62.0185 | 0.21718 | 6.845 | 5.753 | 30.456 | 290.88 | 296.2896 | 1379.16 | 1279.6269 | 7.2169 | 89.7209 | 787.9582 | 96.1348 | 134.683 | 115.327 | 18.354 | 9.191 | 9.028 | 18.219 | 18.219 | 0.36343 | 0.50447 | 13.961 | 14.0463 | 4.2251 | 102.4259 | 0.13714 | 5.753 | 5.753 | 16.302 | 296.2896 | 509.85 | 581.3324 | -14.0203 | 94.498 | 438.811 | 96.285 | 115.327 | 98.625 | 18.354 | 4.254 | 4.774 | 9.028 | 9.028 | 0.36819 | 0.4712 | 12.9235 | 13.0025 | 7.3239 | 81.2981 | 0.15994 | 5.753 | 5.753 | 3.1915 | 509.85 | 857.675 | 961.3216 | -12.0846 | 98.9229 | 735.5858 | 99.5661 | 98.625 | 41.212 | 18.354 | 1.281 | 3.981 | 5.262 | 5.262 | 0.18493 | 0.24344 | 11.3867 | 11.4562 | 9.0222 | 42.5423 | 0.26929 | 5.753 | 6.205 | 80.4989 | 857.675 | 1379.16 | 1107.7535 | 19.6791 | 72.831 | 982.7143 | 91.8085 | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
ICR Treatment Plant Identification Number | 1080 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 10.6979 | [5 empty] | 1998-12-26 | 0:00 | 4889 | 28.726 | 135.507 | 50.902 | 18.574 | 0 | 14.882 | 3.763 |  | 18.645 | 18.645 | 0.79818 | 0 | 13.5291 | 13.6391 | 7.9122 | 66.7183 | 0.20443 | 6.814 | 5.731 | 30.785 | 292.368 | 296.5262 | 1374.84 | 1347.4859 | 1.9896 | 89.6181 | 822.0061 | 96.2549 | 135.507 | 116.767 | 18.574 | 9.319 | 8.655 | 17.974 | 17.974 | 0.35518 | 0.51847 | 14.1554 | 14.2706 | 4.3139 | 103.2491 | 0.13821 | 5.731 | 5.731 | 16.107 | 296.5262 | 517.95 | 598.4589 | -15.5438 | 94.5681 | 447.4926 | 96.4006 | 116.767 | 100.957 | 18.574 | 4.267 | 4.388 | 8.655 | 8.655 | 0.34794 | 0.49301 | 12.963 | 13.0685 | 7.6499 | 82.6381 | 0.15814 | 5.731 | 5.731 | 3.2286 | 517.95 | 892.255 | 1018.4778 | -14.1465 | 98.9112 | 768.2139 | 99.5797 | 100.957 | 50.902 | 18.574 | 1.296 | 3.763 | 5.059 | 5.059 | 0.1765 | 0.25618 | 11.52 | 11.6137 | 9.5146 | 47.8409 | 0.24276 | 5.731 | 6.174 | 80.5661 | 892.255 | 1374.84 | 1171.8056 | 14.7679 | 72.83 | 1032.0303 | 92.1934 | SDS-Cl2 dose | mg/L | 7.1 | 7.8 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 8.5 | 10.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 8.6 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 8.6 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 8 | 8.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection
PWSID Number of Plant (if assigned) | FL4131618 |  |  | Feed flow rate at the end of stage 3, (QF-s(3))end (gpm) | 5.7604 | [5 empty] | 1998-12-26 | 8:00 | 4897 | 28.713 | 135.179 | 50.947 | 18.501 | 0 | 14.819 | 3.763 |  | 18.582 | 18.582 | 0.79749 | 0 | 13.4718 | 13.5866 | 7.8913 | 66.6707 | 0.20379 | 6.772 | 5.758 | 30.691 | 293.04 | 296.4773 | 1381.32 | 1343.1653 | 2.7622 | 89.6481 | 819.8213 | 96.2564 | 135.179 | 116.602 | 18.501 | 9.256 | 8.78 | 18.036 | 18.036 | 0.35768 | 0.5132 | 14.0597 | 14.1795 | 4.2836 | 103.1059 | 0.13752 | 5.758 | 5.758 | 15.9705 | 296.4773 | 517.5 | 592.1915 | -14.4331 | 94.6132 | 444.3344 | 96.4057 | 116.602 | 100.867 | 18.501 | 4.267 | 4.513 | 8.78 | 8.78 | 0.35461 | 0.48599 | 12.963 | 13.0735 | 7.5739 | 82.6596 | 0.15816 | 5.758 | 5.758 | 3.2284 | 517.5 | 895.44 | 1003.7391 | -12.0945 | 98.9111 | 760.6195 | 99.5756 | 100.867 | 50.947 | 18.501 | 1.296 | 3.763 | 5.059 | 5.059 | 0.1765 | 0.25618 | 11.52 | 11.6181 | 9.5518 | 47.8542 | 0.24278 | 5.758 | 6.161 | 80.5818 | 895.44 | 1381.32 | 1176.0821 | 14.8581 | 72.8203 | 1035.7611 | 92.22 | SDS-Free Cl2 residual | mg/L | 6.15 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 8 | BMRL | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.51 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 8 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.50562 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 8 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47104 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.5 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47273 |  |  |  |  | SDS-Free Cl2 residual | mg/L |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal)
Historical Minimum Water Temperature (oC) | 20 | Additional Information |  |  |  | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-12-26 | 16:00 | 4905.0003 | 28.768 | 135.072 | 50.632 | 18.511 | 0 | 14.818 | 3.823 |  | 18.641 | 18.641 | 0.79491 | 0 | 13.4709 | 13.5636 | 7.7967 | 66.5443 | 0.20383 | 6.849 | 5.762 | 30.973 | 291.888 | 296.3467 | 1382.4 | 1324.9389 | 4.1566 | 89.5484 | 810.6428 | 96.1792 | 135.072 | 116.415 | 18.511 | 9.255 | 8.779 | 18.034 | 18.034 | 0.35764 | 0.5132 | 14.0582 | 14.155 | 4.2748 | 102.9577 | 0.13748 | 5.762 | 5.762 | 16.419 | 296.3467 | 516.6 | 591.4522 | -14.4894 | 94.4595 | 443.8995 | 96.3012 | 116.415 | 100.59 | 18.511 | 4.267 | 4.512 | 8.779 | 8.779 | 0.35456 | 0.48605 | 12.963 | 13.0522 | 7.5612 | 82.4303 | 0.15834 | 5.762 | 5.762 | 3.2277 | 516.6 | 890.89 | 1002.0963 | -12.4826 | 98.9108 | 759.3482 | 99.5749 | 100.59 | 50.632 | 18.511 | 1.296 | 3.823 | 5.119 | 5.119 | 0.1789 | 0.25317 | 11.52 | 11.5993 | 9.4769 | 47.6231 | 0.24356 | 5.762 | 6.208 | 80.5504 | 890.89 | 1382.4 | 1165.5958 | 15.6832 | 72.8189 | 1028.2429 | 92.1662 | SDS-Cl2 demand | mg/L | 0.95 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.29 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.25 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.5 |  |  |  |  | SDS-Cl2 demand | mg/L | 0.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 6.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 4.42 |  |  |  |  | SDS-Cl2 demand | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! |  |  | Stage 2 permeate flow rate during sample collection (gpm)
Historical Average Water Temperature (oC) | 25 | Design cross-flow velocity (fps) | 1 | Calculate the Minimum Recycle Flow Rates for Each Stage1 |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-12-27 | 0:00 | 4913 | 28.743 | 135.568 | 51.097 | 18.528 | 0 | 14.814 | 3.763 |  | 18.577 | 18.577 | 0.79744 | 0 | 13.4673 | 13.57 | 7.8852 | 66.9193 | 0.20278 | 6.739 | 5.779 | 30.7145 | 292.224 | 296.3549 | 1373.22 | 1342.1153 | 2.2651 | 89.6359 | 819.2351 | 96.2508 | 135.568 | 117.015 | 18.528 | 9.256 | 8.604 | 17.86 | 17.86 | 0.35298 | 0.51825 | 14.0597 | 14.167 | 4.3111 | 103.4524 | 0.13694 | 5.779 | 5.779 | 16.029 | 296.3549 | 517.5 | 597.9235 | -15.5408 | 94.5913 | 447.1392 | 96.4152 | 117.015 | 101.152 | 18.528 | 4.281 | 4.323 | 8.604 | 8.604 | 0.34485 | 0.49756 | 13.0056 | 13.1047 | 7.6891 | 82.8664 | 0.15814 | 5.779 | 5.779 | 3.2285 | 517.5 | 895.6675 | 1026.7751 | -14.638 | 98.9106 | 772.1376 | 99.5819 | 101.152 | 51.097 | 18.528 | 1.277 | 3.763 | 5.04 | 5.04 | 0.17612 | 0.25337 | 11.3511 | 11.4377 | 9.5346 | 48.0619 | 0.23798 | 5.779 | 6.198 | 80.5235 | 895.6675 | 1373.22 | 1172.2922 | 14.6319 | 72.8287 | 1033.9799 | 92.2123 | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.72 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.36 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.9 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.15 |  |  |  |  | SDS-Chlorination temp. | oC | 24 | 24 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 9.35 |  |  |  |  | SDS-Chlorination temp. | oC |  |  | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm)
State Approved Plant Capacity (MGD) | 18 | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | -8.4583 | [5 empty] | 1998-12-27 | 8:00 | 4921.0003 | 28.713 | 135.956 | 50.88 | 18.681 | 0 | 14.813 | 3.764 |  | 18.577 | 18.577 | 0.79738 | 0 | 13.4664 | 13.5811 | 7.8933 | 66.8437 | 0.20318 | 6.747 | 5.768 | 30.644 | 292.896 | 296.616 | 1379.7 | 1343.3331 | 2.6359 | 89.6688 | 819.9746 | 96.2628 | 135.956 | 117.255 | 18.681 | 9.255 | 8.782 | 18.037 | 18.037 | 0.35772 | 0.51311 | 14.0582 | 14.178 | 4.2859 | 103.6386 | 0.1368 | 5.768 | 5.768 | 15.9315 | 296.616 | 516.6 | 592.4182 | -14.6764 | 94.6289 | 444.5171 | 96.416 | 117.255 | 101.325 | 18.681 | 4.267 | 4.515 | 8.782 | 8.782 | 0.35472 | 0.48588 | 12.963 | 13.0735 | 7.5596 | 83.0494 | 0.15742 | 5.768 | 5.768 | 3.2283 | 516.6 | 896.1225 | 1001.7732 | -11.7898 | 98.9116 | 759.1866 | 99.5748 | 101.325 | 50.88 | 18.681 | 1.291 | 3.764 | 5.055 | 5.055 | 0.17644 | 0.25539 | 11.4756 | 11.5733 | 9.5543 | 47.8672 | 0.24178 | 5.768 | 6.108 | 80.5571 | 896.1225 | 1379.7 | 1175.8502 | 14.7749 | 72.8413 | 1035.9863 | 92.2241 | SDS-Chlorination pH | --- | 8.8 | 8.75 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | NR | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.65 | 8.5 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- |  |  | --- | --- | --- | --- | --- | ---
|  | Maximum element recovery (%) | NA | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | -6.6979 | [5 empty] | 1998-12-27 | 16:00 | 4929 | 28.738 | 135.219 | 50.805 | 18.507 | 0 | 14.886 | 3.763 |  | 18.649 | 18.649 | 0.79822 | 0 | 13.5327 | 13.6379 | 7.9102 | 66.5948 | 0.20479 | 6.758 | 5.764 | 30.785 | 292.368 | 296.412 | 1380.24 | 1347.2022 | 2.3936 | 89.6141 | 821.8071 | 96.254 | 135.219 | 116.602 | 18.507 | 9.315 | 8.661 | 17.976 | 17.976 | 0.35529 | 0.51819 | 14.1494 | 14.2594 | 4.3098 | 103.0937 | 0.13831 | 5.764 | 5.764 | 16.146 | 296.412 | 515.7 | 597.8411 | -15.9281 | 94.5529 | 447.1266 | 96.3889 | 116.602 | 100.882 | 18.507 | 4.28 | 4.381 | 8.661 | 8.661 | 0.34791 | 0.49417 | 13.0025 | 13.1036 | 7.628 | 82.607 | 0.15863 | 5.764 | 5.764 | 3.2287 | 515.7 | 896.5775 | 1016.3567 | -13.3596 | 98.9107 | 766.0283 | 99.5785 | 100.882 | 50.805 | 18.507 | 1.291 | 3.763 | 5.054 | 5.054 | 0.1764 | 0.25544 | 11.4756 | 11.5648 | 9.5603 | 47.7762 | 0.24206 | 5.764 | 6.215 | 80.5302 | 896.5775 | 1380.24 | 1176.5448 | 14.758 | 72.8317 | 1036.5612 | 92.231 | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 72 | 72 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours |  |  | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters
|  | Variability of design flux (%) | 15 | Minimum recycle flow rate for stage 3, (QR-s(3))min (gpm) | -1.7604 | [5 empty] | 1998-12-28 | 0:00 | 4937 | 28.747 | 135.574 | 50.865 | 18.586 | 0 | 14.83 | 3.823 |  | 18.653 | 18.653 | 0.79505 | 0 | 13.4818 | 13.583 | 7.8119 | 66.8216 | 0.20327 | 6.776 | 5.753 | 30.8085 | 292.416 | 296.5589 | 1449.36 | 1327.4451 | 8.4116 | 89.6113 | 812.002 | 96.2059 | 135.574 | 116.82 | 18.586 | 9.254 | 8.666 | 17.92 | 17.92 | 0.35461 | 0.51641 | 14.0567 | 14.1622 | 4.3001 | 103.3109 | 0.13708 | 5.753 | 5.753 | 16.224 | 296.5589 | 517.95 | 595.9149 | -15.0526 | 94.5292 | 446.2369 | 96.3643 | 116.82 | 100.995 | 18.586 | 4.28 | 4.386 | 8.666 | 8.666 | 0.34818 | 0.49388 | 13.0025 | 13.1001 | 7.6586 | 82.6629 | 0.15848 | 5.753 | 5.753 | 3.2288 | 517.95 | 892.9375 | 1020.2315 | -14.2556 | 98.9112 | 769.0907 | 99.5802 | 100.995 | 50.865 | 18.586 | 1.296 | 3.823 | 5.119 | 5.119 | 0.1789 | 0.25317 | 11.52 | 11.6065 | 9.5011 | 47.8429 | 0.2426 | 5.753 | 6.216 | 80.5347 | 892.9375 | 1449.36 | 1168.3427 | 19.3891 | 72.8436 | 1030.6401 | 92.186 | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-32 | CI-s2-32 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-34 | CI-s2-34 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-36 | CI-s2-36 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-38 | CI-s2-38 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-40 | CI-s2-40 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Parameter | Units | Cp-s2-40 (dup) | CI-s2-40 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | 1: A negative minimum recycle flow rate indicates that recycle is not required to | [6 empty] | 1998-12-28 | 8:00 | 4945.0003 | 28.755 | 135.916 | 50.992 | 18.619 | 0 | 14.867 | 3.763 |  | 18.63 | 18.63 | 0.79801 | 0 | 13.5155 | 13.6137 | 7.9021 | 66.9329 | 0.20339 | 6.787 | 5.758 | 30.8085 | 291.6 | 296.3875 | 1460.7 | 1345.647 | 7.8766 | 89.6053 | 821.0172 | 96.2475 | 135.916 | 117.045 | 18.619 | 9.314 | 8.657 | 17.971 | 17.971 | 0.35517 | 0.51828 | 14.1478 | 14.2507 | 4.3103 | 103.5512 | 0.13762 | 5.758 | 5.758 | 16.1265 | 296.3875 | 517.95 | 597.9182 | -15.4394 | 94.559 | 447.1529 | 96.3935 | 117.045 | 101.152 | 18.619 | 4.267 | 4.39 | 8.657 | 8.657 | 0.34805 | 0.4929 | 12.963 | 13.0573 | 7.6487 | 82.8308 | 0.15764 | 5.758 | 5.758 | 3.2286 | 517.95 | 892.71 | 1018.2499 | -14.0628 | 98.9107 | 768.0999 | 99.5797 | 101.152 | 50.992 | 18.619 | 1.286 | 3.763 | 5.049 | 5.049 | 0.1763 | 0.2547 | 11.4311 | 11.5142 | 9.51 | 47.943 | 0.24016 | 5.758 | 6.203 | 80.4966 | 892.71 | 1460.7 | 1170.2828 | 19.8821 | 72.8407 | 1031.4964 | 92.1961 | SDS-CHCl3 | mg/L | 27.96 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 37.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-06 | 1999-01-06 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 27.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 27.53 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-02-04 | 1999-02-04 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 25.39 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | (e.g., solute type and concentration) |  | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-12-28 | 11:00 | 4947.9956 | 28.768 | 135.722 | 56.475 | 18.714 | 0 | 14.912 | 3.464 |  | 18.376 | 18.376 | 0.81149 | 0 | 13.5564 | 13.6496 | 8.3521 | 69.0324 | 0.19773 | 6.776 | 5.765 | 31.396 | 291.888 | 296.3386 | 1462.86 | 1436.8765 | 1.7762 | 89.4054 | 866.6075 | 96.3771 | 135.722 | 117.127 | 18.714 | 9.319 | 8.652 | 17.971 | 17.971 | 0.3551 | 0.51856 | 14.1554 | 14.2528 | 4.3124 | 103.3981 | 0.13784 | 5.765 | 5.765 | 16.0485 | 296.3386 | 520.2 | 598.2367 | -15.0013 | 94.5844 | 447.2877 | 96.412 | 117.127 | 102.15 | 18.714 | 4.293 | 4.359 | 8.652 | 8.652 | 0.34709 | 0.49619 | 13.042 | 13.1318 | 7.7151 | 83.2094 | 0.15782 | 5.765 | 5.765 | 3.2522 | 520.2 | 910.6825 | 1029.3206 | -13.0274 | 98.9025 | 774.7603 | 99.5802 | 102.15 | 56.475 | 18.714 | 1.3 | 3.464 | 4.764 | 4.764 | 0.16462 | 0.27288 | 11.5556 | 11.6351 | 9.8581 | 50.7404 | 0.22931 | 5.765 | 6.273 | 80.6288 | 910.6825 | 1462.86 | 1222.1923 | 16.4519 | 72.7917 | 1066.4374 | 92.4394 | SDS-BDCM | mg/L | 9.35 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 16.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 16.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 9.99 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 2:00 | 2:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 14.16 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1998-12-28 | 18:00 | 4955 | 28.704 | 136.486 | 56.707 | 18.852 | 0 | 14.948 | 3.464 |  | 18.412 | 18.412 | 0.81186 | 0 | 13.5891 | 13.7085 | 8.3817 | 69.3628 | 0.19763 | 6.576 | 5.751 | 31.255 | 293.28 | 296.6976 | 1432.08 | 1442.1468 | -0.70295 | 89.4657 | 869.4222 | 96.4051 | 136.486 | 117.78 | 18.852 | 9.369 | 8.488 | 17.857 | 17.857 | 0.35139 | 0.52467 | 14.2314 | 14.3565 | 4.3527 | 103.9283 | 0.13814 | 5.751 | 5.751 | 16.224 | 296.6976 | 522.45 | 606.2826 | -16.046 | 94.5318 | 451.4901 | 96.4066 | 117.78 | 102.855 | 18.852 | 4.293 | 4.195 | 8.488 | 8.488 | 0.33834 | 0.50577 | 13.042 | 13.1566 | 7.8485 | 83.617 | 0.15734 | 5.751 | 5.751 | 3.2566 | 522.45 | 920.92 | 1053.7723 | -14.426 | 98.9024 | 788.1112 | 99.5868 | 102.855 | 56.707 | 18.852 | 1.286 | 3.464 | 4.75 | 4.75 | 0.16434 | 0.27074 | 11.4311 | 11.5316 | 9.9619 | 50.9671 | 0.22626 | 5.751 | 6.204 | 80.6915 | 920.92 | 1432.08 | 1232.8524 | 13.9118 | 72.8034 | 1076.8862 | 92.507 | SDS-DBCM | mg/L | 3.654 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5063 | 5063 | --- | --- | --- | --- | SDS-DBCM | mg/L | 4.13 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5454 | 5454 | --- | --- | --- | --- | SDS-DBCM | mg/L | 11.836 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5875 | 5875 | --- | --- | --- | --- | SDS-DBCM | mg/L | 0.717 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6137 | 6137 | --- | --- | --- | --- | SDS-DBCM | mg/L | 10.22 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6574 | 6574 | --- | --- | --- | --- | SDS-DBCM | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  | Standard testing recovery (%) | 10 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-12-29 | 2:00 | 4963 | 28.726 | 136.439 | 56.73 | 18.732 | 0 | 14.938 | 3.465 |  | 18.403 | 18.403 | 0.81172 | 0 | 13.58 | 13.6904 | 8.3784 | 69.4741 | 0.19706 | 6.718 | 5.734 | 31.1375 | 294 | 296.6486 | 1436.4 | 1441.2967 | -0.3409 | 89.5036 | 868.9727 | 96.4167 | 136.439 | 118.26 | 18.732 | 9.367 | 8.667 | 18.034 | 18.034 | 0.35614 | 0.51941 | 14.2284 | 14.3441 | 4.322 | 104.2955 | 0.13753 | 5.734 | 5.734 | 16.068 | 296.6486 | 521.55 | 599.8907 | -15.0207 | 94.5835 | 448.2697 | 96.4156 | 118.26 | 102.742 | 18.732 | 4.28 | 4.387 | 8.667 | 8.667 | 0.34823 | 0.49383 | 13.0025 | 13.1083 | 7.7112 | 84.0578 | 0.15594 | 5.734 | 5.734 | 3.2562 | 521.55 | 923.65 | 1027.2024 | -11.2112 | 98.9023 | 774.3762 | 99.5795 | 102.742 | 56.73 | 18.732 | 1.291 | 3.465 | 4.756 | 4.756 | 0.16448 | 0.27145 | 11.4756 | 11.5689 | 10.0005 | 51.0035 | 0.22683 | 5.734 | 6.126 | 80.6445 | 923.65 | 1436.4 | 1237.7395 | 13.8304 | 72.8148 | 1080.6948 | 92.5377 | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 4.94 | 5.62 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.18 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 4.94 | 5.02 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1.008 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 4.76 | 5.19 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.198 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 4.76 | 5.19 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 0.98 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.58 | 6.23 | --- | --- | --- | --- | SDS-CHBr3 | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | pH | --- |  |  | --- | --- | --- | ---
|  | Standard testing pH | 7.5 | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 7.3125 | [5 empty] | 1998-12-29 | 10:00 | 4971 | 28.908 | 136.211 | 56.632 | 18.703 | 0 | 14.951 | 3.464 |  | 18.415 | 18.415 | 0.81189 | 0 | 13.5918 | 13.6288 | 8.3934 | 69.3251 | 0.19659 | 6.737 | 5.728 | 30.268 | 290.496 | 296.0448 | 1438.56 | 1443.1663 | -0.3202 | 89.7759 | 869.6056 | 96.5193 | 136.211 | 117.87 | 18.703 | 9.371 | 8.554 | 17.925 | 17.925 | 0.35318 | 0.52279 | 14.2344 | 14.2732 | 4.334 | 104.0035 | 0.13724 | 5.728 | 5.728 | 16.029 | 296.0448 | 517.05 | 602.8052 | -16.5855 | 94.5856 | 449.425 | 96.4334 | 117.87 | 102.285 | 18.703 | 4.28 | 4.274 | 8.554 | 8.554 | 0.3422 | 0.50035 | 13.0025 | 13.0379 | 7.7106 | 83.6639 | 0.15584 | 5.728 | 5.728 | 3.248 | 517.05 | 907.4975 | 1031.5733 | -13.6723 | 98.9029 | 774.3117 | 99.5805 | 102.285 | 56.632 | 18.703 | 1.3 | 3.464 | 4.764 | 4.764 | 0.16462 | 0.27288 | 11.5556 | 11.587 | 9.8243 | 50.9312 | 0.2275 | 5.728 | 6.148 | 80.2883 | 907.4975 | 1438.56 | 1217.9397 | 15.3362 | 72.8797 | 1062.7186 | 92.445 | SDS-THM4 | mg/L | 40.964 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 58.41 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 56.744 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 38.435 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 50.75 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-THM4 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Temperature | oC |  |  | --- | --- | --- | ---
|  | Acceptable range of operating pressures | 80 - 350 | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 1.1875 | [5 empty] | 1998-12-29 | 18:00 | 4979 | 28.981 | 136.164 | 56.527 | 18.756 | 0 | 14.954 | 3.405 |  | 18.359 | 18.359 | 0.81453 | 0 | 13.5945 | 13.6022 | 8.4824 | 69.1071 | 0.19683 | 6.924 | 5.743 | 30.4325 | 289.104 | 295.849 | 1318.68 | 1461.4988 | -10.8304 | 89.7135 | 878.6739 | 96.5365 | 136.164 | 117.51 | 18.756 | 9.374 | 8.596 | 17.97 | 17.97 | 0.35434 | 0.52165 | 14.239 | 14.247 | 4.3206 | 103.7604 | 0.13731 | 5.743 | 5.743 | 16.2435 | 295.849 | 515.25 | 600.7607 | -16.596 | 94.5095 | 448.3048 | 96.3767 | 117.51 | 102.112 | 18.756 | 4.28 | 4.316 | 8.596 | 8.596 | 0.34445 | 0.49791 | 13.0025 | 13.0098 | 7.6587 | 83.3963 | 0.156 | 5.743 | 5.743 | 3.247 | 515.25 | 905.2225 | 1022.9824 | -13.0089 | 98.9025 | 769.1162 | 99.5778 | 102.112 | 56.527 | 18.756 | 1.3 | 3.405 | 4.705 | 4.705 | 0.16226 | 0.2763 | 11.5556 | 11.562 | 9.8245 | 50.739 | 0.22787 | 5.743 | 6.267 | 80.2592 | 905.2225 | 1318.68 | 1220.1865 | 7.4691 | 72.8716 | 1062.7045 | 92.4476 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 76 | 130.2302 | 58.3333 | 103.1151 | 80.6042 | SDS-MCAA* | mg/L | 2.56 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 20 | 20 | #VALUE! | 20 | 0 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 116 | 218.2727 | 69.2308 | 167.1364 | 90.427 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 116 | 205.0496 | 70.3704 | 160.5248 | 90.0327 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 20 | 52 | 80.6897 | 44.4444 | 66.3448 | 69.8545 | SDS-MCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Acceptable range of operating pH values | 4 - 11 | Maximum recycle flow rate for stage 3, (QR-s(3))max (gpm) | 6.125 | [5 empty] | 1998-12-30 | 2:00 | 4987 | 28.968 | 136.171 | 56.685 | 18.906 | 0 | 14.969 | 3.464 |  | 18.433 | 18.433 | 0.81208 | 0 | 13.6082 | 13.6211 | 8.402 | 69.12 | 0.19706 | 6.834 | 5.726 | 30.221 | 289.584 | 296.053 | 1325.7 | 1444.7939 | -8.9835 | 89.792 | 870.4234 | 96.528 | 136.171 | 117.78 | 18.906 | 9.371 | 8.603 | 17.974 | 17.974 | 0.35449 | 0.52136 | 14.2344 | 14.2479 | 4.3257 | 103.7438 | 0.13734 | 5.726 | 5.726 | 16.0095 | 296.053 | 513 | 601.0962 | -17.1728 | 94.5924 | 448.5746 | 96.431 | 117.78 | 102.42 | 18.906 | 4.293 | 4.31 | 8.603 | 8.603 | 0.34447 | 0.49901 | 13.042 | 13.0544 | 7.6362 | 83.5578 | 0.15623 | 5.726 | 5.726 | 3.248 | 513 | 907.4975 | 1020.7414 | -12.4787 | 98.9029 | 766.8707 | 99.5765 | 102.42 | 56.685 | 18.906 | 1.305 | 3.464 | 4.769 | 4.769 | 0.16472 | 0.27364 | 11.6 | 11.611 | 9.8304 | 50.8161 | 0.22849 | 5.726 | 6.259 | 80.2816 | 907.4975 | 1325.7 | 1219.1363 | 8.0383 | 72.8827 | 1063.3169 | 92.4499 | SDS-DCAA* | mg/L | 3.33 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32.4 | 561 | 1072.8948 | 90.0613 | 816.9474 | 96.034 | SDS-DCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 32.4 | 605 | 1197.1046 | 91.5625 | 901.0523 | 96.4042 | SDS-DCAA* | mg/L | 6.62 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 37.5 | 1050 | 2085.5114 | 90.0794 | 1567.7557 | 97.608 | SDS-DCAA* | mg/L | 5.92 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 37.5 | 1005 | 1866.5548 | 90.0266 | 1435.7774 | 97.3882 | SDS-DCAA* | mg/L | 2.58 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 58 | 639 | 1159.8966 | #VALUE! | 899.4483 | 93.5516 | SDS-DCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1998-12-30 | 15:00 | 5000 | 28.951 | 133.196 | 47.752 | 18.57 | 0 | 14.969 | 3.883 |  | 18.852 | 18.852 | 0.79403 | 0 | 13.6082 | 13.6279 | 7.7568 | 64.1472 | 0.21245 | 6.787 | 5.771 | 31.0905 | 290.448 | 296.053 | 1332.72 | 1317.4856 | 1.1431 | 89.4983 | 806.7693 | 96.1463 | 133.196 | 114.487 | 18.57 | 9.429 | 8.491 | 17.92 | 17.92 | 0.35227 | 0.52617 | 14.3225 | 14.3433 | 4.3499 | 100.9216 | 0.14212 | 5.771 | 5.771 | 16.3605 | 296.053 | 509.4 | 606.643 | -19.0897 | 94.4738 | 451.348 | 96.3752 | 114.487 | 98.677 | 18.57 | 4.254 | 4.237 | 8.491 | 8.491 | 0.33954 | 0.501 | 12.9235 | 12.9423 | 7.603 | 80.409 | 0.16096 | 5.771 | 5.771 | 3.2088 | 509.4 | 871.78 | 1017.6222 | -16.7292 | 98.9161 | 763.5111 | 99.5797 | 98.677 | 47.752 | 18.57 | 1.286 | 3.883 | 5.169 | 5.169 | 0.18111 | 0.24879 | 11.4311 | 11.4477 | 9.2205 | 45.424 | 0.25202 | 5.771 | 6.223 | 80.7229 | 871.78 | 1332.72 | 1133.768 | 14.9283 | 72.7336 | 1002.774 | 91.95 | SDS-TCAA* | mg/L | 1.01 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 550 | 1059.377 | 92.5 | 804.6885 | 97.0175 | SDS-TCAA* | mg/L | NR | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 24 | 600 | 1195.6204 | 92.9412 | 897.8102 | 97.3268 | SDS-TCAA* | mg/L | 1.73 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 20 | 1010 | 2022.5 | 93.0556 | 1516.25 | 98.681 | SDS-TCAA* | mg/L | 2.51 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 20 | 1010 | 1891.5909 | 93.1034 | 1450.7955 | 98.6214 | SDS-TCAA* | mg/L | 26 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 18 | 650 | 1216.6207 | 94.375 | 933.3103 | 98.0714 | SDS-TCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible SDI | 5 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-12-30 | 23:00 | 5008.0003 | 28.887 | 133.585 | 47.947 | 18.546 | 0 | 14.91 | 3.885 |  | 18.795 | 18.795 | 0.7933 | 0 | 13.5545 | 13.5999 | 7.7581 | 64.4619 | 0.21098 | 7.002 | 5.751 | 30.4795 | 291.792 | 296.2651 | 1345.14 | 1316.3072 | 2.1435 | 89.7121 | 806.2862 | 96.2198 | 133.585 | 114.982 | 18.546 | 9.365 | 8.675 | 18.04 | 18.04 | 0.35633 | 0.51912 | 14.2253 | 14.2729 | 4.3129 | 101.4246 | 0.14072 | 5.751 | 5.751 | 16.1655 | 296.2651 | 507.15 | 598.6436 | -18.0407 | 94.5436 | 447.4543 | 96.3872 | 114.982 | 99.075 | 18.546 | 4.254 | 4.421 | 8.675 | 8.675 | 0.34935 | 0.49037 | 12.9235 | 12.9668 | 7.4639 | 81.0186 | 0.16005 | 5.751 | 5.751 | 3.2098 | 507.15 | 877.4675 | 992.0542 | -13.0588 | 98.9166 | 749.6021 | 99.5718 | 99.075 | 47.947 | 18.546 | 1.291 | 3.885 | 5.176 | 5.176 | 0.18129 | 0.24942 | 11.4756 | 11.5139 | 9.292 | 45.673 | 0.2521 | 5.751 | 6.139 | 80.6624 | 877.4675 | 1345.14 | 1142.2488 | 15.0833 | 72.7736 | 1009.8582 | 92.0125 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 550 | 1065.1874 | 94.1935 | 807.5937 | 97.7712 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 520 | 1039.0998 | 94.5122 | 779.5499 | 97.691 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 970 | 1943.6364 | 93.4783 | 1456.8182 | 98.7644 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 18 | 970 | 1817.7521 | 93.5252 | 1393.876 | 98.7086 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 16 | 540 | 1009.7931 | 94.6667 | 774.8966 | 97.9352 | SDS-MBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum permissible turbidity (ntu) | less than 1 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 0 | [5 empty] | 1998-12-31 | 7:00 | 5016 | 28.896 | 139.809 | 50.43 | 19.296 | 0 | 15.237 | 3.983 |  | 19.22 | 19.22 | 0.79277 | 0 | 13.8518 | 13.8945 | 7.7665 | 68.057 | 0.20416 | 6.959 | 5.745 | 29.5865 | 291.648 | 296.2243 | 1342.98 | 1316.2495 | 1.9904 | 90.0121 | 806.2369 | 96.3303 | 139.809 | 120.622 | 19.296 | 9.668 | 8.857 | 18.525 | 18.525 | 0.36523 | 0.52189 | 14.6856 | 14.7308 | 4.336 | 106.5835 | 0.13821 | 5.745 | 5.745 | 15.717 | 296.2243 | 510.3 | 602.4166 | -18.0515 | 94.6942 | 449.3204 | 96.5021 | 120.622 | 103.815 | 19.296 | 4.293 | 4.564 | 8.857 | 8.857 | 0.35802 | 0.4847 | 13.042 | 13.0822 | 7.4557 | 85.4668 | 0.15307 | 5.745 | 5.745 | 3.216 | 510.3 | 884.52 | 987.2745 | -11.617 | 98.9143 | 748.7872 | 99.5705 | 103.815 | 50.43 | 19.296 | 1.276 | 3.983 | 5.259 | 5.259 | 0.18491 | 0.24263 | 11.3422 | 11.3771 | 9.33 | 48.4965 | 0.2346 | 5.745 | 6.21 | 80.3376 | 884.52 | 1342.98 | 1142.1491 | 14.9541 | 72.8795 | 1013.3346 | 92.072 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.07 | 0.547 | 1.0089 | 49.2754 | 0.77796 | 91.0021 | SDS-DBAA* | mg/L | 2.33 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.182 | 4.7 | 9.3719 | 97.0066 | 7.0359 | 97.4133 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.827 | 41.8 | 83.7042 | 56.0106 | 62.7521 | 98.6821 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.827 | 41.8 | 78.2863 | 56.2434 | 60.0431 | 98.6227 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.08 | 2.5 | 4.6697 | 94.0741 | 3.5848 | 97.7684 | SDS-DBAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | Maximum system recycle flow rate, (QR-sys)max (gpm) | 1.1875 | [5 empty] | 1998-12-31 | 15:00 | 5024.0003 | 28.964 | 139.42 | 50.047 | 19.173 | 0 | 15.267 | 3.942 |  | 19.209 | 19.209 | 0.79478 | 0 | 13.8791 | 13.8939 | 7.8114 | 67.7491 | 0.20508 | 6.422 | 5.752 | 29.939 | 289.776 | 295.955 | 1341.9 | 1326.2105 | 1.1692 | 89.8839 | 811.0828 | 96.3088 | 139.42 | 120.18 | 19.173 | 9.669 | 9.085 | 18.754 | 18.754 | 0.37132 | 0.51557 | 14.6871 | 14.7027 | 4.2921 | 106.3349 | 0.13827 | 5.752 | 5.752 | 15.8145 | 295.955 | 510.3 | 594.1035 | -16.4224 | 94.6565 | 445.0293 | 96.4464 | 120.18 | 103.485 | 19.173 | 4.307 | 4.778 | 9.085 | 9.085 | 0.36981 | 0.47408 | 13.0846 | 13.0985 | 7.3563 | 85.3032 | 0.15355 | 5.752 | 5.752 | 3.2156 | 510.3 | 876.5575 | 967.3977 | -10.3633 | 98.9135 | 738.8488 | 99.5648 | 103.485 | 50.047 | 19.173 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4878 | 9.267 | 48.326 | 0.23771 | 5.752 | 6.252 | 80.2547 | 876.5575 | 1341.9 | 1137.3457 | 15.2436 | 72.8828 | 1006.9516 | 92.0299 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 14.8 | 35.8 | 56.1363 | 5.7325 | 45.9682 | 67.8038 | SDS-BCAA* | mg/L | 7.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.93 | 45.7 | 90.9609 | #VALUE! | 68.3305 | 97.1755 | SDS-BCAA* | mg/L | 1.17 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.23 | 71.5 | 143.367 | #VALUE! | 107.4335 | 98.8551 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.23 | 71.5 | 134.0751 | 88.7156 | 102.7876 | 98.8034 | SDS-BCAA* | mg/L | 11 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 1.5 | 30 | 55.5517 | 88.4615 | 42.7759 | 96.4933 | SDS-BCAA* | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | 1: All of the information requested in this field may not be available, but values for all of the Design |  | Design system recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1998-12-31 | 23:00 | 5032 | 28.951 | 139.387 | 50.227 | 19.155 | 0 | 15.271 | 3.943 |  | 19.214 | 19.214 | 0.79479 | 0 | 13.8827 | 13.9028 | 7.8174 | 67.8346 | 0.20495 | 6.889 | 5.744 | 29.845 | 290.448 | 296.0611 | 1347.3 | 1327.1 | 1.4993 | 89.9193 | 811.5806 | 96.3226 | 139.387 | 120.33 | 19.155 | 9.668 | 9.151 | 18.819 | 18.819 | 0.37307 | 0.51374 | 14.6856 | 14.7069 | 4.2852 | 106.4183 | 0.1382 | 5.744 | 5.744 | 15.6585 | 296.0611 | 508.95 | 592.3055 | -16.3779 | 94.7111 | 444.1833 | 96.4748 | 120.33 | 103.545 | 19.155 | 4.307 | 4.844 | 9.151 | 9.151 | 0.37334 | 0.47066 | 13.0846 | 13.1035 | 7.3057 | 85.4768 | 0.1533 | 5.744 | 5.744 | 3.2169 | 508.95 | 879.7425 | 958.6182 | -8.9658 | 98.9134 | 733.7841 | 99.5616 | 103.545 | 50.227 | 19.155 | 1.296 | 3.943 | 5.239 | 5.239 | 0.18371 | 0.24738 | 11.52 | 11.5367 | 9.3093 | 48.4217 | 0.23825 | 5.744 | 6.215 | 80.2054 | 879.7425 | 1347.3 | 1142.5373 | 15.198 | 72.9092 | 1011.1399 | 92.0678 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 1.01 | 1.9794 | 98.3051 | 1.4947 | 99.3979 | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.982 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 1.22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.03 | 1.11 | 2.0783 | #VALUE! | 1.5941 | 98.1181 | SDS-TBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | System influent flow rate, QI-sys (gpm) | 24.6875 | [5 empty] | 1999-01-01 | 10:00 | 5043 | 28.955 | 139.474 | 50.055 | 19.17 | 0 | 15.256 | 3.982 |  | 19.238 | 19.238 | 0.79301 | 0 | 13.8691 | 13.8876 | 7.7614 | 67.8331 | 0.20473 | 6.799 | 5.736 | 29.845 | 290.496 | 296.0448 | 1344.06 | 1315.9203 | 2.0936 | 89.9188 | 805.9825 | 96.2971 | 139.474 | 120.307 | 19.17 | 9.672 | 8.964 | 18.636 | 18.636 | 0.36813 | 0.519 | 14.6916 | 14.7112 | 4.3162 | 106.4043 | 0.13826 | 5.736 | 5.736 | 15.678 | 296.0448 | 509.4 | 598.5557 | -17.5021 | 94.7042 | 447.3002 | 96.495 | 120.307 | 103.635 | 19.17 | 4.293 | 4.671 | 8.964 | 8.964 | 0.36373 | 0.47892 | 13.042 | 13.0594 | 7.3879 | 85.4131 | 0.1529 | 5.736 | 5.736 | 3.217 | 509.4 | 879.7425 | 974.6202 | -10.7847 | 98.9134 | 742.0101 | 99.5665 | 103.635 | 50.055 | 19.17 | 1.291 | 3.982 | 5.273 | 5.273 | 0.18517 | 0.24483 | 11.4756 | 11.4908 | 9.2916 | 48.3834 | 0.2375 | 5.736 | 6.198 | 80.1965 | 879.7425 | 1344.06 | 1138.9625 | 15.2596 | 72.9107 | 1009.3525 | 92.0547 | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 0.060811 | 2.8212 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 2.15 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 2.1488 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 1.7063 | --- | --- | --- | --- | SDS-CDBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | #VALUE! | 1.7063 | --- | --- | --- | --- | SDS-CDBAA | mg/L | 13.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | 2 | 3.7 | --- | --- | --- | --- | SDS-CDBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  |  |  | Recycle ratio, r | 0 | [5 empty] | 1999-01-01 | 15:00 | 5048.0003 | 28.976 | 140.017 | 50.22 | 19.324 | 0 | 15.269 | 3.942 |  | 19.211 | 19.211 | 0.79481 | 0 | 13.8809 | 13.8908 | 7.8071 | 67.9874 | 0.20431 | 6.805 | 5.748 | 29.986 | 289.104 | 295.8326 | 1331.1 | 1325.5669 | 0.41568 | 89.8639 | 810.6998 | 96.3012 | 140.017 | 120.57 | 19.324 | 9.671 | 8.962 | 18.633 | 18.633 | 0.36807 | 0.51903 | 14.6901 | 14.7006 | 4.3101 | 106.6594 | 0.13783 | 5.748 | 5.748 | 15.873 | 295.8326 | 510.75 | 597.9404 | -17.0711 | 94.6345 | 446.8865 | 96.4481 | 120.57 | 103.987 | 19.324 | 4.307 | 4.655 | 8.962 | 8.962 | 0.36325 | 0.48058 | 13.0846 | 13.0938 | 7.4233 | 85.5312 | 0.15309 | 5.748 | 5.748 | 3.2158 | 510.75 | 877.0125 | 980.3418 | -11.782 | 98.913 | 745.5459 | 99.5687 | 103.987 | 50.22 | 19.324 | 1.291 | 3.942 | 5.233 | 5.233 | 0.18357 | 0.2467 | 11.4756 | 11.4837 | 9.2731 | 48.5064 | 0.23675 | 5.748 | 6.317 | 80.1786 | 877.0125 | 1331.1 | 1137.9746 | 14.5087 | 72.8973 | 1007.4936 | 92.0418 | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 16.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L |  |  | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1999-01-01 | 23:00 | 5056 | 28.959 | 139.427 | 50.287 | 19.132 | 0 | 15.273 | 3.982 |  | 19.255 | 19.255 | 0.7932 | 0 | 13.8845 | 13.9014 | 7.7621 | 67.9629 | 0.20454 | 6.762 | 5.776 | 29.892 | 289.632 | 295.9224 | 1343.52 | 1316.2846 | 2.0272 | 89.8987 | 806.1035 | 96.2918 | 139.427 | 120.322 | 19.132 | 9.67 | 8.729 | 18.399 | 18.399 | 0.36184 | 0.52557 | 14.6886 | 14.7064 | 4.3541 | 106.3884 | 0.13823 | 5.776 | 5.776 | 15.717 | 295.9224 | 509.4 | 606.3344 | -19.0291 | 94.6888 | 451.1284 | 96.5161 | 120.322 | 103.567 | 19.132 | 4.307 | 4.422 | 8.729 | 8.729 | 0.35082 | 0.49341 | 13.0846 | 13.1004 | 7.5269 | 85.2856 | 0.15361 | 5.776 | 5.776 | 3.2171 | 509.4 | 879.7425 | 1002.419 | -13.9446 | 98.9129 | 755.9095 | 99.5744 | 103.567 | 50.287 | 19.132 | 1.296 | 3.982 | 5.278 | 5.278 | 0.18527 | 0.24555 | 11.52 | 11.534 | 9.2964 | 48.4986 | 0.23782 | 5.776 | 6.324 | 80.2077 | 879.7425 | 1343.52 | 1139.9628 | 15.151 | 72.8957 | 1009.8526 | 92.0575 | SDS-HAA5 | mg/L | 4.34 | 0 | --- | -16.3267 | --- | #DIV/0! | -8.1633 | 153.1646 | [8 empty] | SDS-HAA5 | mg/L | 4.89 | 0 | --- | -20.8468 | --- | #DIV/0! | -10.4234 | 146.9136 | [8 empty] | SDS-HAA5 | mg/L | 8.35 | 0 | --- | -31.4119 | --- | #DIV/0! | -15.706 | 153.1646 | [8 empty] | SDS-HAA5 | mg/L | 8.43 | 0 | --- | -33.72 | --- | #DIV/0! | -16.86 | 150 | [8 empty] | SDS-HAA5 | mg/L | 28.58 | 0 | --- | -130.1978 | --- | #DIV/0! | -65.0989 | 143.9024 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Field 4-2b: Manufacturer Reported Membrane Characteristics1 |  | maximum system recycle flow rates. | [6 empty] | 1999-01-02 | 18:00 | 5075 | 28.985 | 135.97 | 54.495 | 17.932 | 0 | 14.143 | 3.524 |  | 17.667 | 17.667 | 0.80053 | 0 | 12.8573 | 12.863 | 7.9566 | 69.3439 | 0.1855 | 6.786 | 5.782 | 31.1845 | 289.872 | 295.8163 | 1437.48 | 1357.873 | 5.538 | 89.4582 | 826.8447 | 96.2285 | 135.97 | 116.932 | 17.932 | 8.536 | 9.921 | 18.457 | 18.457 | 0.37851 | 0.46248 | 12.9661 | 12.9718 | 3.9996 | 104.5194 | 0.12411 | 5.782 | 5.782 | 16.1655 | 295.8163 | 518.4 | 536.4271 | -3.4774 | 94.5353 | 416.1217 | 96.1152 | 116.932 | 101.28 | 17.932 | 4.307 | 5.614 | 9.921 | 9.921 | 0.41442 | 0.43413 | 13.0846 | 13.0904 | 7.1276 | 84.0464 | 0.15575 | 5.782 | 5.782 | 3.2483 | 518.4 | 908.4075 | 913.6188 | -0.57367 | 98.9019 | 716.0094 | 99.5463 | 101.28 | 54.495 | 17.932 | 1.3 | 3.524 | 4.824 | 4.824 | 0.16702 | 0.26949 | 11.5556 | 11.5607 | 9.8011 | 50.1544 | 0.2305 | 5.782 | 6.418 | 80.9245 | 908.4075 | 1437.48 | 1213.6651 | 15.5699 | 72.6437 | 1061.0363 | 92.3731 | SDS-HAA6 | mg/L | 4.34 | 0 | --- | -16.3267 | --- | #DIV/0! | -8.1633 | 153.1646 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 12.09 | 0 | --- | -51.5416 | --- | #DIV/0! | -25.7708 | 146.9136 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 9.52 | 0 | --- | -35.8133 | --- | #DIV/0! | -17.9067 | 153.1646 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 8.43 | 0 | --- | -33.72 | --- | #DIV/0! | -16.86 | 150 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 39.58 | 0 | --- | -180.3089 | --- | #DIV/0! | -90.1544 | 143.9024 | Stage 3 Operating Parameters During Sample Collection | [7 empty] | SDS-HAA6 | mg/L | 0 | 0 | --- | 0 | --- | #DIV/0! | #DIV/0! | #DIV/0! | Stage 3 Operating Parameters During Sample Collection
|  | General Information | [8 empty] | 1999-01-03 | 2:00 | 5083.0003 | 29.002 | 136.023 | 54.547 | 17.898 | 0 | 14.078 | 3.524 |  | 17.602 | 17.602 | 0.7998 | 0 | 12.7982 | 12.7974 | 7.9416 | 69.4454 | 0.18428 | 6.756 | 5.771 | 30.8555 | 289.008 | 295.8 | 1437.48 | 1354.2247 | 5.7918 | 89.5688 | 825.0124 | 96.26 | 136.023 | 117.105 | 17.898 | 8.471 | 9.86 | 18.331 | 18.331 | 0.37602 | 0.46211 | 12.8673 | 12.8666 | 3.9981 | 104.6679 | 0.12293 | 5.771 | 5.771 | 16.1265 | 295.8 | 518.4 | 536.0753 | -3.4096 | 94.5482 | 415.9376 | 96.1229 | 117.105 | 101.287 | 17.898 | 4.307 | 5.553 | 9.86 | 9.86 | 0.41116 | 0.43682 | 13.0846 | 13.0838 | 7.1493 | 84.1487 | 0.15548 | 5.771 | 5.771 | 3.2483 | 518.4 | 908.635 | 917.9603 | -1.0263 | 98.9018 | 718.1801 | 99.5477 | 101.287 | 54.547 | 17.898 | 1.3 | 3.524 | 4.824 | 4.824 | 0.16702 | 0.26949 | 11.5556 | 11.5549 | 9.8057 | 50.2133 | 0.23012 | 5.771 | 6.427 | 80.7654 | 908.635 | 1437.48 | 1214.0352 | 15.5442 | 72.6959 | 1061.3351 | 92.3902 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.25 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.27 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.25333 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.25813 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal) | 0.29545 |  |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | Stage 3 recovery during sample collection (decimal)
|  | Membrane manufacturer | FLUID SYSTEMS CORP. | Summary of the Stage and System Flow Rates | [6 empty] | 1999-01-03 | 10:00 | 5091 | 28.896 | 136.244 | 54.772 | 17.832 | 0 | 14.062 | 3.644 |  | 17.706 | 17.706 | 0.79419 | 0 | 12.7836 | 12.823 | 7.7679 | 69.9081 | 0.18343 | 6.938 | 5.774 | 32.3595 | 299.04 | 297.5218 | 1471.5 | 1320.7687 | 10.2434 | 89.1237 | 809.1452 | 96.0008 | 136.244 | 117.517 | 17.832 | 8.469 | 9.928 | 18.397 | 18.397 | 0.3778 | 0.46035 | 12.8643 | 12.9039 | 4.0103 | 105.0382 | 0.12285 | 5.774 | 5.774 | 16.3995 | 297.5218 | 533.7 | 537.3308 | -0.68031 | 94.488 | 417.4263 | 96.0713 | 117.517 | 101.722 | 17.832 | 4.293 | 5.635 | 9.928 | 9.928 | 0.41516 | 0.43241 | 13.042 | 13.0822 | 7.3249 | 84.4626 | 0.15489 | 5.774 | 5.774 | 3.2628 | 533.7 | 939.8025 | 937.8113 | 0.21188 | 98.9033 | 735.7556 | 99.5565 | 101.722 | 54.772 | 17.832 | 1.3 | 3.644 | 4.944 | 4.944 | 0.17182 | 0.26294 | 11.5556 | 11.5911 | 10.1158 | 50.2992 | 0.23044 | 5.774 | 6.375 | 81.3523 | 939.8025 | 1471.5 | 1246.0553 | 15.3207 | 72.6567 | 1092.9289 | 92.5565 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.29 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.3 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.14 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.27 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm) | 1.3 |  |  |  |  | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | Stage 3 permeate flow rate during sample collection (gpm)
|  | Membrane trade name | FLUID SYSTEMS | Influent flow rate to stage 1, QI-s(1) (gpm) | 24.6875 | [5 empty] | 1999-01-03 | 18:00 | 5099 | 28.84 | 136.573 | 54.892 | 17.868 | 0 | 13.983 | 3.584 |  | 17.567 | 17.567 | 0.79598 | 0 | 12.7118 | 12.7721 | 7.8604 | 70.0041 | 0.18245 | 6.851 | 5.761 | 32.947 | 309.216 | 299.3333 | 1535.76 | 1338.6411 | 12.8353 | 88.9932 | 818.9872 | 95.9771 | 136.573 | 117.607 | 17.868 | 8.409 | 9.748 | 18.157 | 18.157 | 0.3722 | 0.46313 | 12.7732 | 12.8337 | 4.0419 | 105.1801 | 0.12202 | 5.761 | 5.761 | 16.9455 | 299.3333 | 554.85 | 542.9318 | 2.148 | 94.3389 | 421.1326 | 95.9762 | 117.607 | 101.985 | 17.868 | 4.293 | 5.455 | 9.748 | 9.748 | 0.40556 | 0.4404 | 13.042 | 13.1039 | 7.6861 | 84.2419 | 0.15555 | 5.761 | 5.761 | 3.2811 | 554.85 | 977.1125 | 988.9261 | -1.209 | 98.9039 | 771.8881 | 99.5749 | 101.985 | 54.892 | 17.868 | 1.281 | 3.584 | 4.865 | 4.865 | 0.16904 | 0.26331 | 11.3867 | 11.4406 | 10.5522 | 50.0183 | 0.22873 | 5.761 | 6.367 | 81.8765 | 977.1125 | 1535.76 | 1297.0894 | 15.5409 | 72.6471 | 1137.101 | 92.7995 | [12 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.45 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.88 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.5 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.92 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm) | 4.4 | [16 empty] | Stage 3 influent flow rate during sample collection (gpm)
|  | Membrane element model number | 2540 TFCS / 4921 TFCS | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 9.875 | [5 empty] | 1999-01-04 | 2:00 | 5107 | 28.743 | 137.464 | 55.29 | 17.977 | 0 | 14.064 | 3.585 |  | 17.649 | 17.649 | 0.79687 | 0 | 12.7855 | 12.883 | 7.8978 | 70.5022 | 0.18273 | 6.881 | 5.76 | 32.242 | 307.296 | 298.9253 | 1526.04 | 1345.1271 | 11.8551 | 89.214 | 822.0262 | 96.0777 | 137.464 | 118.635 | 17.977 | 8.471 | 9.925 | 18.396 | 18.396 | 0.37775 | 0.46048 | 12.8673 | 12.9655 | 4.0329 | 106.0396 | 0.12227 | 5.76 | 5.76 | 16.263 | 298.9253 | 548.55 | 540.1779 | 1.5262 | 94.5595 | 419.5516 | 96.1237 | 118.635 | 102.907 | 17.977 | 4.293 | 5.632 | 9.925 | 9.925 | 0.415 | 0.43254 | 13.042 | 13.1415 | 7.5309 | 85.2631 | 0.15413 | 5.76 | 5.76 | 3.2772 | 548.55 | 970.7425 | 964.1849 | 0.67552 | 98.9037 | 756.3675 | 99.5667 | 102.907 | 55.29 | 17.977 | 1.3 | 3.585 | 4.885 | 4.885 | 0.16946 | 0.26612 | 11.5556 | 11.6437 | 10.5019 | 50.6196 | 0.23002 | 5.76 | 6.371 | 81.7398 | 970.7425 | 1526.04 | 1293.1145 | 15.2634 | 72.6554 | 1131.9285 | 92.7787 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs
|  | Molecular weight cutoff (Daltons) | 200 | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 14.8125 | [5 empty] | 1999-01-04 | 10:00 | 5115.0003 | 28.619 | 137.558 | 55.62 | 17.743 | 0 | 14.061 | 3.586 |  | 17.647 | 17.647 | 0.79679 | 0 | 12.7827 | 12.9275 | 7.9122 | 70.9338 | 0.18225 | 6.944 | 5.763 | 33.276 | 317.856 | 300.5328 | 1562.76 | 1348.4686 | 13.7124 | 88.9277 | 824.5007 | 95.9641 | 137.558 | 118.815 | 17.743 | 8.471 | 9.931 | 18.402 | 18.402 | 0.37791 | 0.46033 | 12.8673 | 13.0131 | 4.0495 | 106.394 | 0.12231 | 5.763 | 5.763 | 16.653 | 300.5328 | 561.6 | 542.6782 | 3.3693 | 94.4588 | 421.6055 | 96.0501 | 118.815 | 103.012 | 17.743 | 4.294 | 5.637 | 9.931 | 9.931 | 0.4153 | 0.43238 | 13.0451 | 13.1928 | 7.7096 | 85.4609 | 0.15437 | 5.763 | 5.763 | 3.291 | 561.6 | 1003.9575 | 986.8934 | 1.6997 | 98.9049 | 774.2467 | 99.5749 | 103.012 | 55.62 | 17.743 | 1.296 | 3.586 | 4.882 | 4.882 | 0.16942 | 0.26546 | 11.52 | 11.6505 | 10.8791 | 50.6939 | 0.22982 | 5.763 | 6.409 | 82.5462 | 1003.9575 | 1562.76 | 1336.9606 | 14.4488 | 72.5334 | 1170.459 | 92.9475 |  | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters | [8 empty] | THM4 Controls |  |  |  | HAA5 Controls |  |  |  |  | Stage 3 Permeate and Influent Water Quality Parameters
|  | Membrane material (e.g., PVD, polyamide, etc.) | POLYAMIDE | Influent flow rate to stage 2, QI-s(2) (gpm) | 14.8125 | [5 empty] | 1999-01-04 | 18:00 | 5123 | 28.619 | 137.477 | 55.642 | 17.82 | 0 | 14.06 | 3.586 |  | 17.646 | 17.646 | 0.79678 | 0 | 12.7818 | 12.9266 | 7.9098 | 70.8297 | 0.1825 | 5.575 | 5.75 | 33.182 | 316.848 | 300.3696 | 1569.78 | 1347.9596 | 14.1307 | 88.9529 | 824.1646 | 95.9739 | 137.477 | 118.83 | 17.82 | 8.471 | 9.758 | 18.229 | 18.229 | 0.3733 | 0.4647 | 12.8673 | 13.0131 | 4.0692 | 106.2643 | 0.12246 | 5.75 | 5.75 | 16.614 | 300.3696 | 560.7 | 546.7002 | 2.4968 | 94.4688 | 423.5349 | 96.0773 | 118.83 | 103.035 | 17.82 | 4.294 | 5.464 | 9.758 | 9.758 | 0.40607 | 0.44005 | 13.0451 | 13.1928 | 7.7644 | 85.3481 | 0.15458 | 5.75 | 5.75 | 3.2907 | 560.7 | 1003.0475 | 998.7519 | 0.42825 | 98.9045 | 779.726 | 99.578 | 103.035 | 55.642 | 17.82 | 1.295 | 3.586 | 4.881 | 4.881 | 0.1694 | 0.26531 | 11.5111 | 11.6415 | 10.8686 | 50.6499 | 0.22984 | 5.75 | 6.292 | 82.4186 | 1003.0475 | 1569.78 | 1335.5111 | 14.9237 | 72.561 | 1169.2793 | 92.9513 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-32 | CI-s3-32 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-34 | CI-s3-34 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-36 | CI-s3-36 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-38 | CI-s3-38 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-40 | CI-s3-40 | CC(calc) | RF (%) | CB | RB (%) |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 |  |  |  | Parameter | Units | Cp-s3-40 (dup) | CI-s3-40 (dup) | CC(calc) | RF (%) | CB | RB (%)
|  | Membrane construction (e.g., thin-film composite) | THIN - FILM COMPOSIT | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 4.9375 | [5 empty] | 1999-01-05 | 2:00 | 5131.0003 | 28.56 | 137.538 | 55.687 | 17.778 | 0 | 14.065 | 3.587 |  | 17.652 | 17.652 | 0.79679 | 0 | 12.7864 | 12.9537 | 7.9239 | 70.9106 | 0.18268 | 5.591 | 5.736 | 33.1115 | 317.52 | 300.7613 | 1576.26 | 1350.2439 | 14.3388 | 88.9908 | 825.5026 | 95.9889 | 137.538 | 118.852 | 17.778 | 8.471 | 9.875 | 18.346 | 18.346 | 0.37642 | 0.46174 | 12.8673 | 13.0358 | 4.0566 | 106.3604 | 0.12256 | 5.736 | 5.736 | 16.8675 | 300.7613 | 563.85 | 544.2918 | 3.4687 | 94.3917 | 422.5266 | 96.0079 | 118.852 | 103.065 | 17.778 | 4.294 | 5.581 | 9.875 | 9.875 | 0.41231 | 0.43484 | 13.0451 | 13.2158 | 7.762 | 85.4185 | 0.15472 | 5.736 | 5.736 | 3.2919 | 563.85 | 1009.8725 | 995.1412 | 1.4587 | 98.9055 | 779.4956 | 99.5777 | 103.065 | 55.687 | 17.778 | 1.3 | 3.587 | 4.887 | 4.887 | 0.16954 | 0.26601 | 11.5556 | 11.7068 | 10.9548 | 50.6432 | 0.23116 | 5.736 | 6.049 | 82.4477 | 1009.8725 | 1576.26 | 1345.9897 | 14.6087 | 72.587 | 1177.9311 | 93.0006 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 1244.2396 | 622.1198 |  |  |  | Sampling date | MM/DD/YY | 1998-12-21 | 1998-12-21 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 1104.2945 | 552.1472 |  |  |  | Sampling date | MM/DD/YY | 1999-01-06 | 1999-01-06 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 646.7066 | 323.3533 |  |  |  | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 640.5694 | 320.2847 |  |  |  | Sampling date | MM/DD/YY | 1999-02-04 | 1999-02-04 | --- | --- | --- | --- | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | 188.9433 | 94.4717 |  |  |  | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | Qp/QT (THM4), % | #DIV/0! | #DIV/0! |  | Qp/QT (HAA5), % | #DIV/0! | #DIV/0! |  |  |  | Sampling date | MM/DD/YY |  |  | --- | --- | --- | ---
|  | Membrane hydrophobicity | HYDRPHILIC | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 9.875 | [5 empty] | 1999-01-05 | 15:10 | 5144.1681 | 28.573 | 132.432 | 53.64 | 18.81 | 0 | 14.985 | 3.526 |  | 18.511 | 18.511 | 0.80952 | 0 | 13.6227 | 13.7958 | 8.3853 | 65.8407 | 0.20953 | 6.141 | 5.611 | 27.8475 | 284.784 | 296.1835 | 1371.6 | 1436.5736 | -4.7371 | 90.5979 | 866.3785 | 96.7858 | 132.432 | 114.307 | 18.81 | 9.489 | 8.079 | 17.568 | 17.568 | 0.34208 | 0.54013 | 14.4137 | 14.5967 | 4.4746 | 100.0849 | 0.14584 | 5.611 | 5.611 | 14.274 | 296.1835 | 525.6 | 627.2937 | -19.3481 | 95.1807 | 461.7386 | 96.9086 | 114.307 | 99.645 | 18.81 | 4.215 | 3.864 | 8.079 | 8.079 | 0.3186 | 0.52172 | 12.8051 | 12.9677 | 8.0737 | 80.0923 | 0.16191 | 5.611 | 5.611 | 3.1728 | 525.6 | 939.575 | 1095.4837 | -16.5935 | 98.9288 | 810.5419 | 99.6086 | 99.645 | 53.64 | 18.81 | 1.281 | 3.526 | 4.807 | 4.807 | 0.16672 | 0.26649 | 11.3867 | 11.5313 | 10.171 | 47.6615 | 0.24194 | 5.611 | 8.163 | 78.8323 | 939.575 | 1371.6 | 1252.2838 | 8.699 | 73.384 | 1095.9294 | 92.8068 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 8:00 | 8:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | NA |  |  |  | Sampling time | hh:mm | 2:00 | 2:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | NA | #VALUE! |  |  |  | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  | SDS-THM4b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Sampling time | hh:mm |  |  | --- | --- | --- | ---
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | NEGATIVE | Influent flow rate to stage 3, QI-s(3) (gpm) | 9.875 | [5 empty] | 1999-01-05 | 23:00 | 5152 | 28.585 | 132.023 | 53.092 | 18.6 | 0 | 14.928 | 3.466 |  | 18.394 | 18.394 | 0.81157 | 0 | 13.5709 | 13.7384 | 8.4527 | 65.5048 | 0.20973 | 6.279 | 5.658 | 27.636 | 285.216 | 295.6776 | 1393.2 | 1450.128 | -4.0861 | 90.6533 | 872.9028 | 96.834 | 132.023 | 113.925 | 18.6 | 9.366 | 8.377 | 17.743 | 17.743 | 0.34839 | 0.52787 | 14.2268 | 14.4024 | 4.3844 | 99.9896 | 0.14404 | 5.658 | 5.658 | 14.4495 | 295.6776 | 504 | 610.1079 | -21.0531 | 95.1131 | 452.8927 | 96.8095 | 113.925 | 98.857 | 18.6 | 4.267 | 4.11 | 8.377 | 8.377 | 0.33311 | 0.50937 | 12.963 | 13.123 | 7.6072 | 80.1838 | 0.16366 | 5.658 | 5.658 | 3.2266 | 504 | 894.075 | 1023.9027 | -14.5209 | 98.9087 | 763.9513 | 99.5776 | 98.857 | 53.092 | 18.6 | 1.295 | 3.466 | 4.761 | 4.761 | 0.1646 | 0.272 | 11.5111 | 11.6532 | 9.6719 | 47.7026 | 0.24429 | 5.658 | 5.684 | 79.128 | 894.075 | 1393.2 | 1198.5633 | 13.9705 | 73.2384 | 1046.3191 | 92.4375 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 5063 | 5063 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 5454 | 5454 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 5875 | 5875 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | NA |  |  |  | Operation time | hh.hh | 6137 | 6137 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | NA | 27 |  |  |  | Operation time | hh.hh | 6574 | 6574 | --- | --- | --- | --- | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  | SDS-HAA5b, mg/L | #DIV/0! | #DIV/0! |  |  |  | Operation time | hh.hh |  |  | --- | --- | --- | ---
|  |  |  | Permeate flow rate from stage 3, Qp-s(3) (gpm) | 4.9375 | [5 empty] | 1999-01-06 | 7:00 | 5160.0003 | 28.556 | 133.216 | 54.33 | 18.535 | 0 | 14.884 | 3.527 |  | 18.411 | 18.411 | 0.80843 | 0 | 13.5309 | 13.7097 | 8.39 | 66.848 | 0.20509 | 5.296 | 5.658 | 29.657 | 307.2 | 299.4312 | 1472.04 | 1437.8829 | 2.3204 | 90.0956 | 868.6571 | 96.5859 | 133.216 | 115.222 | 18.535 | 9.367 | 8.319 | 17.686 | 17.686 | 0.34686 | 0.52963 | 14.2284 | 14.4163 | 4.4332 | 101.2508 | 0.14238 | 5.658 | 5.658 | 15.795 | 299.4312 | 540 | 618.7989 | -14.5924 | 94.725 | 459.1151 | 96.5597 | 115.222 | 100.32 | 18.535 | 4.241 | 4.078 | 8.319 | 8.319 | 0.33071 | 0.5098 | 12.8841 | 13.0543 | 8.1584 | 81.0776 | 0.16101 | 5.658 | 5.658 | 3.2574 | 540 | 961.415 | 1098.1965 | -14.2271 | 98.9121 | 819.0982 | 99.6023 | 100.32 | 54.33 | 18.535 | 1.276 | 3.527 | 4.803 | 4.803 | 0.16666 | 0.26567 | 11.3422 | 11.4921 | 10.4119 | 48.3781 | 0.23755 | 5.658 | 5.644 | 79.7149 | 961.415 | 1472.04 | 1280.397 | 13.0189 | 73.3779 | 1120.906 | 92.8884 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 4.97 | 5.8 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.05 | 4.87 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.15 | 5.92 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | NA |  |  |  | pH | --- | 5.15 | 5.92 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | NA | #VALUE! |  |  |  | pH | --- | 5.81 | 6.27 | --- | --- | --- | --- | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  | SDS-TOXb, mg Cl- /L | #DIV/0! | #DIV/0! |  |  |  | pH | --- |  |  | --- | --- | --- | ---
|  | Design Parameters |  | Concentrate flow rate from stage 3, QC-s(3) (gpm) | 4.9375 | [5 empty] | 1999-01-06 | 15:00 | 5168 | 28.717 | 132.961 | 53.88 | 18.559 | 0 | 14.859 | 3.584 |  | 18.443 | 18.443 | 0.80567 | 0 | 13.5082 | 13.6217 | 8.1731 | 66.6884 | 0.20426 | 6.217 | 5.752 | 33.1115 | 306.432 | 299.0803 | 1473.66 | 1401.7675 | 4.8785 | 88.9289 | 850.4239 | 96.1065 | 132.961 | 114.937 | 18.559 | 9.309 | 8.361 | 17.67 | 17.67 | 0.34721 | 0.52683 | 14.1403 | 14.259 | 4.3911 | 100.9989 | 0.14118 | 5.752 | 5.752 | 17.004 | 299.0803 | 540.45 | 613.1395 | -13.4498 | 94.3146 | 456.1099 | 96.272 | 114.937 | 100.035 | 18.559 | 4.254 | 4.107 | 8.361 | 8.361 | 0.3326 | 0.50879 | 12.9235 | 13.0321 | 8.154 | 80.773 | 0.16134 | 5.752 | 5.752 | 3.2608 | 540.45 | 950.95 | 1096.8665 | -15.3443 | 98.9097 | 818.6583 | 99.6017 | 100.035 | 53.88 | 18.559 | 1.296 | 3.584 | 4.88 | 4.88 | 0.16934 | 0.26557 | 11.52 | 11.6168 | 10.2636 | 48.1349 | 0.24134 | 5.752 | 6.635 | 81.7421 | 950.95 | 1473.66 | 1265.2618 | 14.1415 | 72.6689 | 1108.1059 | 92.6233 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | NA |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | NA | #VALUE! |  |  |  | Temperature | oC | 29 | 29 | --- | --- | --- | --- | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  | SDS-CDb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Temperature | oC |  |  | --- | --- | --- | ---
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 2.5" x 40" | System concentrate recycle flow rate, QR-sys (gpm) | 0 | [5 empty] | 1999-01-06 | 23:00 | 5176.0003 | 28.683 | 133.149 | 53.857 | 18.517 | 0 | 14.857 | 3.585 |  | 18.442 | 18.442 | 0.80561 | 0 | 13.5064 | 13.6335 | 8.1936 | 66.7924 | 0.20412 | 6.306 | 5.743 | 34.6155 | 320.592 | 301.3243 | 1423.44 | 1406.6222 | 1.1815 | 88.5122 | 853.9733 | 95.9465 | 133.149 | 114.96 | 18.517 | 9.312 | 8.362 | 17.674 | 17.674 | 0.34727 | 0.52688 | 14.1448 | 14.278 | 4.4187 | 101.1188 | 0.1412 | 5.743 | 5.743 | 17.4915 | 301.3243 | 563.4 | 617.4032 | -9.5852 | 94.1951 | 459.3637 | 96.1922 | 114.96 | 99.99 | 18.517 | 4.254 | 4.108 | 8.362 | 8.362 | 0.33265 | 0.50873 | 12.9235 | 13.0452 | 8.5014 | 80.4566 | 0.16214 | 5.743 | 5.743 | 3.2766 | 563.4 | 988.9425 | 1143.4304 | -15.6215 | 98.9126 | 853.4152 | 99.6161 | 99.99 | 53.857 | 18.517 | 1.291 | 3.585 | 4.876 | 4.876 | 0.16928 | 0.26477 | 11.4756 | 11.5836 | 10.6955 | 47.711 | 0.24279 | 5.743 | 6.476 | 82.5888 | 988.9425 | 1423.44 | 1315.331 | 7.5949 | 72.5914 | 1152.1367 | 92.8317 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 128 | 168.8228 | 41.6667 | 148.4114 | 81.1335 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 18 | 32 | 37.0838 | #VALUE! | 34.5419 | 47.8894 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 132 | 167.2857 | 46.1538 | 149.6429 | 81.2888 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | NA |  |  |  | Alkalinity | mg/L as CaCO3 | 28 | 132 | 168.1863 | 48.1481 | 150.0932 | 81.3449 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | 0.72813 |  |  |  | Alkalinity | mg/L as CaCO3 | 26 | 76 | 96.9677 | 27.7778 | 86.4839 | 69.9366 | TOCb, mg/L | #DIV/0! | #DIV/0! |  | TOCb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Alkalinity | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Active membrane area of membrane element used, A (ft2) | 27 | System concentrate waste flow rate, QW-sys (gpm) | 4.9375 | [5 empty] | 1999-01-07 | 7:00 | 5184 | 28.479 | 132.747 | 53.527 | 18.499 | 0 | 14.787 | 3.526 |  | 18.313 | 18.313 | 0.80746 | 0 | 13.4427 | 13.6513 | 8.2433 | 66.3947 | 0.20561 | 6.364 | 5.691 | 31.1845 | 294.912 | 297.3667 | 1412.64 | 1413.6561 | -0.071932 | 89.5131 | 855.5114 | 96.3549 | 132.747 | 114.48 | 18.499 | 9.251 | 8.489 | 17.74 | 17.74 | 0.34985 | 0.52148 | 14.0522 | 14.2702 | 4.3469 | 100.7676 | 0.14162 | 5.691 | 5.691 | 15.99 | 297.3667 | 521.55 | 604.0007 | -15.8088 | 94.6228 | 450.6837 | 96.4521 | 114.48 | 99.51 | 18.499 | 4.255 | 4.234 | 8.489 | 8.489 | 0.3394 | 0.50124 | 12.9266 | 13.1272 | 7.7874 | 80.7086 | 0.16265 | 5.691 | 5.691 | 3.2436 | 521.55 | 920.01 | 1042.4271 | -13.3061 | 98.9092 | 781.9885 | 99.5852 | 99.51 | 53.527 | 18.499 | 1.281 | 3.526 | 4.807 | 4.807 | 0.16672 | 0.26649 | 11.3867 | 11.5634 | 9.9155 | 48.104 | 0.24038 | 5.691 | 5.881 | 80.8864 | 920.01 | 1412.64 | 1224.8646 | 13.2925 | 72.7991 | 1072.4373 | 92.4577 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 25.9 | 931 | 1300.487 | 92.0552 | 1115.7435 | 97.6787 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 104 | 990 | 1311.7318 | 72.9167 | 1150.8659 | 90.9633 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 122 | 1040 | 1351.4643 | 67.7249 | 1195.7321 | 89.797 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | NA |  |  |  | Total dissolved solids | mg/L | 122 | 1004 | 1310.8877 | 67.5532 | 1157.4438 | 89.4595 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! |  |  |  | Total dissolved solids | mg/L | 42.4 | 1110 | 1557.7032 | #VALUE! | 1333.8516 | 96.8212 | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  | UV254 b, cm-1 | #DIV/0! | #DIV/0! |  |  |  | Total dissolved solids | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Design flux, FW (gfd) | 17.9 | System permeate flow rate, Qp-sys (gpm) | 19.75 | [5 empty] | 1999-01-07 | 12:27 | 5189.4503 | 28.585 | 132.6 | 53.362 | 18.498 | 0 | 14.494 | 3.465 |  | 17.959 | 17.959 | 0.80706 | 0 | 13.1764 | 13.339 | 8.196 | 66.287 | 0.20123 | 6.46 | 5.735 | 31.584 | 292.416 | 296.6976 | 1315.784 | 1405.6605 | -6.8306 | 89.3548 | 851.1791 | 96.2894 | 132.6 | 114.427 | 18.498 | 8.949 | 8.721 | 17.67 | 17.67 | 0.35201 | 0.50645 | 13.5934 | 13.7612 | 4.2349 | 100.7806 | 0.13655 | 5.735 | 5.735 | 16.809 | 296.6976 | 522.45 | 583.9035 | -11.7626 | 94.3346 | 440.3006 | 96.1824 | 114.427 | 99.172 | 18.498 | 4.254 | 4.467 | 8.721 | 8.721 | 0.35181 | 0.48779 | 12.9235 | 13.0831 | 7.6644 | 80.6371 | 0.16225 | 5.735 | 5.735 | 3.2401 | 522.45 | 904.54 | 1016.9025 | -12.4221 | 98.908 | 769.6762 | 99.579 | 99.172 | 53.362 | 18.498 | 1.291 | 3.465 | 4.756 | 4.756 | 0.16448 | 0.27145 | 11.4756 | 11.6172 | 9.772 | 47.997 | 0.24204 | 5.735 | 6.203 | 80.7923 | 904.54 | 1315.784 | 1211.4544 | 7.9291 | 72.7695 | 1057.9972 | 92.3637 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 58 | 980 | 1356.3861 | 81.875 | 1168.193 | 95.0351 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 48 | 1050 | 1413.8547 | 85.8824 | 1231.9274 | 96.1037 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 28 | 1000 | 1329.7857 | 90.2778 | 1164.8929 | 97.5963 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | NA |  |  |  | Total hardness | mg/L as CaCO3 | 48 | 1000 | 1331.2438 | 83.4483 | 1165.6219 | 95.882 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! |  |  |  | Total hardness | mg/L as CaCO3 | 70 | 1040 | 1446.7742 | 78.125 | 1243.3871 | 94.3702 | Bromideb, mg/L | #DIV/0! | #DIV/0! |  | Bromideb, mg/L | #DIV/0! | #DIV/0! |  |  |  | Total hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Net driving pressure at the design flux, NDP (psi) | 109 | System feed flow rate, QF-sys (gpm) | 24.6875 | [5 empty] | 1999-01-07 | 20:00 | 5197 | 28.547 | 132.868 | 53.617 | 18.486 | 0 | 14.795 | 3.584 |  | 18.379 | 18.379 | 0.80499 | 0 | 13.45 | 13.6313 | 8.1332 | 66.6233 | 0.2046 | 6.238 | 5.741 | 31.443 | 293.712 | 296.8853 | 1368.7186 | 1392.6494 | -1.7484 | 89.409 | 844.7673 | 96.2779 | 132.868 | 114.577 | 18.486 | 9.25 | 8.426 | 17.676 | 17.676 | 0.34815 | 0.52331 | 14.0506 | 14.24 | 4.3459 | 100.8906 | 0.14114 | 5.741 | 5.741 | 16.302 | 296.8853 | 520.65 | 604.9075 | -16.1831 | 94.509 | 450.8964 | 96.3845 | 114.577 | 99.682 | 18.486 | 4.254 | 4.172 | 8.426 | 8.426 | 0.33607 | 0.50487 | 12.9235 | 13.0978 | 7.812 | 80.8315 | 0.16204 | 5.741 | 5.741 | 3.2413 | 520.65 | 910.91 | 1048.2283 | -15.0749 | 98.9082 | 784.4392 | 99.5868 | 99.682 | 53.617 | 18.486 | 1.291 | 3.584 | 4.875 | 4.875 | 0.16924 | 0.26482 | 11.4756 | 11.6302 | 9.7945 | 48.369 | 0.24045 | 5.741 | 6.245 | 80.9402 | 910.91 | 1368.7186 | 1209.8751 | 11.6053 | 72.7369 | 1060.3926 | 92.367 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 58 | 880 | 1215.5633 | 81.2903 | 1047.7816 | 94.4645 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 48 | 1000 | 1345.6983 | 85.3659 | 1172.8492 | 95.9074 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 26 | 940 | 1250.1071 | 90.5797 | 1095.0536 | 97.6257 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | NA |  |  |  | Calcium hardness | mg/L as CaCO3 | 48 | 940 | 1250.3671 | 82.7338 | 1095.1836 | 95.6172 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | NA | 13.3268 |  |  |  | Calcium hardness | mg/L as CaCO3 | 68 | 1020 | 1419.2258 | 77.3333 | 1219.6129 | 94.4245 | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Alkb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Calcium hardness | mg/L as CaCO3 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.13 | [7 empty] | 1999-01-08 | 4:00 | 5205.0003 | 28.543 | 132.821 | 53.625 | 18.496 | 0 | 14.783 | 3.525 |  | 18.308 | 18.308 | 0.80746 | 0 | 13.4391 | 13.6219 | 8.2217 | 66.5053 | 0.20482 | 6.016 | 5.741 | 31.4195 | 292.848 | 296.9016 | 1369.3282 | 1410.2695 | -2.9899 | 89.4175 | 853.5856 | 96.3191 | 132.821 | 114.48 | 18.496 | 9.251 | 8.42 | 17.671 | 17.671 | 0.34801 | 0.52351 | 14.0522 | 14.2433 | 4.3481 | 100.8064 | 0.14129 | 5.741 | 5.741 | 16.263 | 296.9016 | 520.65 | 605.2374 | -16.2465 | 94.5224 | 451.0695 | 96.3946 | 114.48 | 99.442 | 18.496 | 4.241 | 4.179 | 8.42 | 8.42 | 0.3361 | 0.50368 | 12.8841 | 13.0593 | 7.7995 | 80.6655 | 0.16189 | 5.741 | 5.741 | 3.2413 | 520.65 | 910.6825 | 1045.735 | -14.8298 | 98.9083 | 783.1925 | 99.5861 | 99.442 | 53.625 | 18.496 | 1.291 | 3.525 | 4.816 | 4.816 | 0.16688 | 0.26806 | 11.4756 | 11.6316 | 9.8172 | 48.2203 | 0.24122 | 5.741 | 6.261 | 80.9088 | 910.6825 | 1369.3282 | 1214.5798 | 11.301 | 72.749 | 1062.6311 | 92.386 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.318 | 25.2 | 35.3575 | -130.4348 | 30.2788 | 98.9498 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.74 | 25.5 | 34.4911 | 87.8289 | 29.9955 | 97.533 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.403 | 27.4 | 36.5597 | 78.5638 | 31.9798 | 98.7398 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Turbidity | ntu | 0.403 | 27.4 | 36.7935 | 78.6772 | 32.0967 | 98.7444 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | NA | 34.6956 |  |  |  | Turbidity | ntu | 0.01 | 30.8 | 43.7119 | 99.2593 | 37.256 | 99.9732 | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | T-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Turbidity | ntu |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Temperature at which the MTCW was determined, ToC (oC) | 30 | Calculate the Required System Influent Pressure | [6 empty] | 1999-01-08 | 12:00 | 5213 | 28.602 | 133.102 | 53.617 | 18.484 | 0 | 14.793 | 3.524 |  | 18.317 | 18.317 | 0.80761 | 0 | 13.4482 | 13.6073 | 8.2139 | 66.6616 | 0.20413 | 6.002 | 5.756 | 31.6545 | 292.416 | 296.7139 | 1377.2565 | 1409.3768 | -2.3322 | 89.3316 | 853.0454 | 96.2892 | 133.102 | 114.517 | 18.484 | 9.253 | 8.474 | 17.727 | 17.727 | 0.34947 | 0.52197 | 14.0552 | 14.2215 | 4.3308 | 100.9947 | 0.14081 | 5.756 | 5.756 | 16.575 | 296.7139 | 518.85 | 602.6055 | -16.1425 | 94.4138 | 449.6597 | 96.3139 | 114.517 | 99.322 | 18.484 | 4.254 | 4.22 | 8.474 | 8.474 | 0.33863 | 0.50201 | 12.9235 | 13.0765 | 7.7549 | 80.6806 | 0.16208 | 5.756 | 5.756 | 3.2404 | 518.85 | 905.2225 | 1038.6138 | -14.7357 | 98.9079 | 778.7319 | 99.5839 | 99.322 | 53.617 | 18.484 | 1.286 | 3.524 | 4.81 | 4.81 | 0.16674 | 0.26736 | 11.4311 | 11.5664 | 9.7474 | 48.2381 | 0.23978 | 5.756 | 6.317 | 80.8931 | 905.2225 | 1377.2565 | 1206.0419 | 12.4316 | 72.737 | 1055.6322 | 92.337 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 12.5 | 50.6 | 66.1535 | 20.3822 | 58.3767 | 78.5874 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 28.6 | 77.1 | 94.7117 | #VALUE! | 85.9059 | 66.7077 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 17.4 | 175 | 228.4714 | #VALUE! | 201.7357 | 91.3749 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | NA |  |  |  | Total organic carbon | mg/L | 17.4 | 175 | 229.8362 | -59.633 | 202.4181 | 91.4039 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | NA | 33.5899 |  |  |  | Total organic carbon | mg/L | 1.5 | 58 | 81.6935 | 88.4615 | 69.8468 | 97.8524 | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #DIV/0! |  |  |  | Total organic carbon | mg/L |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Maximum flow rate to the element, QI, max (gpm) | 8 | Osmotic pressure for stage 13, Dp1 (psi) | 2.8 | [5 empty] | 1999-01-08 | 20:00 | 5221.0003 | 28.573 | 132.888 | 53.55 | 18.502 | 0 | 14.815 | 3.524 |  | 18.339 | 18.339 | 0.80784 | 0 | 13.4682 | 13.6392 | 8.2274 | 66.4896 | 0.20513 | 6.791 | 5.75 | 31.6075 | 293.28 | 296.8363 | 1372.3776 | 1411.8661 | -2.8774 | 89.3519 | 854.3512 | 96.3004 | 132.888 | 114.502 | 18.502 | 9.252 | 8.355 | 17.607 | 17.607 | 0.34629 | 0.52547 | 14.0537 | 14.2322 | 4.3553 | 100.8377 | 0.14114 | 5.75 | 5.75 | 16.5165 | 296.8363 | 520.65 | 607.2515 | -16.6333 | 94.4358 | 452.0439 | 96.3463 | 114.502 | 99.465 | 18.502 | 4.267 | 4.088 | 8.355 | 8.355 | 0.33193 | 0.51071 | 12.963 | 13.1277 | 7.8744 | 80.6071 | 0.16286 | 5.75 | 5.75 | 3.2418 | 520.65 | 908.635 | 1060.7138 | -16.7371 | 98.9079 | 790.6819 | 99.59 | 99.465 | 53.55 | 18.502 | 1.296 | 3.524 | 4.82 | 4.82 | 0.16694 | 0.26888 | 11.52 | 11.6663 | 9.7991 | 48.2064 | 0.24201 | 5.75 | 6.276 | 80.9222 | 908.635 | 1372.3776 | 1213.0379 | 11.6105 | 72.7384 | 1060.8364 | 92.3718 | Notes: | [9 empty] | UV254 | cm-1 | 0.02 | 1.72 | 2.414 | 96.2335 | 2.067 | 99.0324 | Notes: | [9 empty] | UV254 | cm-1 | BMRL | 1.91 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Notes: | [9 empty] | UV254 | cm-1 | 0.11 | 2.33 | 3.0832 | 81.0671 | 2.7066 | 95.9359 | Notes: | [9 empty] | UV254 | cm-1 | 0.11 | 2.33 | 3.1024 | 78.0439 | 2.7162 | 95.9503 | Notes: | [9 empty] | UV254 | cm-1 | 0.033 | 2.31 | 3.2649 | #VALUE! | 2.7874 | 98.8161 | Notes: | [9 empty] | UV254 | cm-1 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Minimum flow rate to the element, QI, min (gpm) | 2 | Osmotic pressure for stage 23, Dp2 (psi) | 5 | [5 empty] | 1999-01-09 | 14:00 | 5239 | 28.632 | 134.08 | 51.15 | 18.261 | 0 | 14.712 | 3.703 |  | 18.415 | 18.415 | 0.79891 | 0 | 13.3745 | 13.5208 | 7.9027 | 66.4513 | 0.20347 | 7.044 | 5.794 | 32.148 | 291.792 | 296.7629 | 1387.0143 | 1348.0764 | 2.8073 | 89.1671 | 822.4197 | 96.091 | 134.08 | 115.23 | 18.261 | 9.012 | 8.956 | 17.968 | 17.968 | 0.35912 | 0.50156 | 13.6891 | 13.8388 | 4.2101 | 102.1839 | 0.13543 | 5.794 | 5.794 | 16.6725 | 296.7629 | 523.8 | 578.6046 | -10.4629 | 94.3819 | 437.6837 | 96.1907 | 115.23 | 99.727 | 18.261 | 4.5 | 4.456 | 8.956 | 8.956 | 0.35778 | 0.50246 | 13.6709 | 13.8204 | 7.8342 | 81.3833 | 0.16982 | 5.794 | 5.794 | 3.2356 | 523.8 | 905.905 | 1049.5046 | -15.8515 | 98.9097 | 786.6523 | 99.5887 | 99.727 | 51.15 | 18.261 | 1.2 | 3.703 | 4.903 | 4.903 | 0.17218 | 0.24475 | 10.6667 | 10.7833 | 9.5823 | 47.5952 | 0.22656 | 5.794 | 6.408 | 81.2918 | 905.905 | 1387.0143 | 1173.1304 | 15.4205 | 72.6071 | 1039.5177 | 92.1799 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.16 | 3.3992 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #VALUE! | 2.4773 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.63218 | 1.3314 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 0.63218 | 1.3314 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | 2.2 | 3.9828 | --- | --- | --- | --- | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [9 empty] | SUVA | L/(mg*m) | #DIV/0! | #DIV/0! | --- | --- | --- | ---
|  | Total width of all membrane envelopes in the element, w (ft) | 19.2 | Osmotic pressure for stage 33, Dp3 (psi) | 9 | [5 empty] | 1999-01-09 | 22:00 | 5247 | 28.598 | 134.275 | 51.202 | 18.336 | 0 | 14.652 | 3.704 |  | 18.356 | 18.356 | 0.79821 | 0 | 13.32 | 13.4792 | 7.889 | 66.5135 | 0.20265 | 6.976 | 5.774 | 32.054 | 293.28 | 296.975 | 1383.9649 | 1344.9294 | 2.8206 | 89.2065 | 820.9522 | 96.0955 | 134.275 | 115.552 | 18.336 | 9.012 | 9.019 | 18.031 | 18.031 | 0.3608 | 0.49981 | 13.6891 | 13.8527 | 4.2055 | 102.372 | 0.13532 | 5.774 | 5.774 | 16.536 | 296.975 | 522.45 | 577.1964 | -10.4788 | 94.4319 | 437.0857 | 96.2168 | 115.552 | 99.93 | 18.336 | 4.44 | 4.579 | 9.019 | 9.019 | 0.36275 | 0.49229 | 13.4886 | 13.6498 | 7.7094 | 81.6956 | 0.16708 | 5.774 | 5.774 | 3.237 | 522.45 | 908.8625 | 1025.9018 | -12.8776 | 98.91 | 774.1759 | 99.5819 | 99.93 | 51.202 | 18.336 | 1.2 | 3.704 | 4.904 | 4.904 | 0.17222 | 0.2447 | 10.6667 | 10.7942 | 9.6168 | 47.6132 | 0.22671 | 5.774 | 6.365 | 81.2426 | 908.8625 | 1383.9649 | 1176.9899 | 14.9552 | 72.6433 | 1042.9262 | 92.2101 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs.
|  | Feed spacer thickness, T (ft) | 0.0029 | Pressure losses due to stage hardware, DPs (psi) | 5 | [5 empty] | 1999-01-10 | 6:00 | 5255 | 28.547 | 134.342 | 51.39 | 18.229 | 0 | 14.651 | 3.764 |  | 18.415 | 18.415 | 0.7956 | 0 | 13.3191 | 13.4986 | 7.8295 | 66.8075 | 0.20205 | 6.917 | 5.757 | 31.396 | 294.432 | 297.1464 | 1377.8662 | 1331.5537 | 3.3612 | 89.4342 | 814.3501 | 96.1447 | 134.342 | 115.755 | 18.229 | 9.071 | 8.963 | 18.034 | 18.034 | 0.36009 | 0.50299 | 13.7787 | 13.9645 | 4.2313 | 102.5882 | 0.13612 | 5.757 | 5.757 | 16.185 | 297.1464 | 523.8 | 581.4933 | -11.0144 | 94.5532 | 439.3198 | 96.3159 | 115.755 | 100.125 | 18.229 | 4.44 | 4.523 | 8.963 | 8.963 | 0.35976 | 0.49537 | 13.4886 | 13.6704 | 7.7607 | 81.9503 | 0.16681 | 5.757 | 5.757 | 3.2378 | 523.8 | 912.275 | 1034.8095 | -13.4317 | 98.9104 | 779.3047 | 99.5845 | 100.125 | 51.39 | 18.229 | 1.14 | 3.764 | 4.904 | 4.904 | 0.17342 | 0.23246 | 10.1333 | 10.2699 | 9.569 | 47.9595 | 0.21414 | 5.757 | 6.306 | 81.2224 | 912.275 | 1377.8662 | 1163.9753 | 15.5233 | 72.6659 | 1038.1252 | 92.176 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5.
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | Pressure losses in a single element, DPe (psi) | 6.7 | [5 empty] | 1999-01-10 | 18:19 | 5267.3133 | 28.607 | 134.167 | 51.135 | 18.352 | 0 | 14.532 | 3.705 |  | 18.237 | 18.237 | 0.79684 | 0 | 13.2109 | 13.3653 | 7.8719 | 66.4271 | 0.2012 | 6.954 | 5.741 | 29.281 | 282.576 | 295.1227 | 1323.5897 | 1337.825 | -1.0755 | 90.0784 | 816.4739 | 96.4137 | 134.167 | 115.485 | 18.352 | 9.012 | 8.908 | 17.92 | 17.92 | 0.35784 | 0.5029 | 13.6891 | 13.8491 | 4.21 | 102.264 | 0.13542 | 5.741 | 5.741 | 15.5415 | 295.1227 | 499.5 | 577.968 | -15.7093 | 94.7339 | 436.5454 | 96.4399 | 115.485 | 99.84 | 18.352 | 4.44 | 4.468 | 8.908 | 8.908 | 0.35682 | 0.49843 | 13.4886 | 13.6462 | 7.4287 | 81.8818 | 0.16666 | 5.741 | 5.741 | 3.2149 | 499.5 | 869.96 | 992.6749 | -14.1058 | 98.9106 | 746.0875 | 99.5691 | 99.84 | 51.135 | 18.352 | 1.08 | 3.705 | 4.785 | 4.785 | 0.16986 | 0.22571 | 9.6 | 9.7122 | 9.0515 | 48.084 | 0.20198 | 5.741 | 6.191 | 79.9568 | 869.96 | 1323.5897 | 1100.2443 | 16.8742 | 72.9073 | 985.1022 | 91.8834 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters.
|  | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Design permeate pressure, Pp (psi) | 15 | [5 empty] | 1999-01-10 | 22:00 | 5271.0003 | 28.611 | 134.228 | 51.21 | 18.273 | 0 | 14.652 | 3.645 |  | 18.297 | 18.297 | 0.80079 | 0 | 13.32 | 13.474 | 8.0133 | 66.4327 | 0.20282 | 7.008 | 5.745 | 29.093 | 283.92 | 295.3267 | 1319.9301 | 1365.5205 | -3.454 | 90.1489 | 830.4236 | 96.4966 | 134.228 | 115.65 | 18.273 | 9.072 | 8.908 | 17.98 | 17.98 | 0.35864 | 0.50456 | 13.7803 | 13.9396 | 4.2258 | 102.4402 | 0.13608 | 5.745 | 5.745 | 15.327 | 295.3267 | 501.75 | 580.4814 | -15.6914 | 94.8102 | 437.904 | 96.4999 | 115.65 | 100.05 | 18.273 | 4.44 | 4.468 | 8.908 | 8.908 | 0.35682 | 0.49843 | 13.4886 | 13.6446 | 7.4624 | 82.1146 | 0.16617 | 5.745 | 5.745 | 3.2159 | 501.75 | 876.1025 | 997.1599 | -13.8177 | 98.9111 | 749.455 | 99.5709 | 100.05 | 51.21 | 18.273 | 1.14 | 3.645 | 4.785 | 4.785 | 0.16866 | 0.23824 | 10.1333 | 10.2505 | 9.2058 | 48.1512 | 0.21288 | 5.745 | 6.196 | 80.0173 | 876.1025 | 1319.9301 | 1125.0839 | 14.7619 | 72.9055 | 1000.5932 | 92.003 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design.
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 45.2 | [5 empty] | 1999-01-11 | 6:00 | 5279 | 28.632 | 134.054 | 51.082 | 18.283 | 0 | 14.656 | 3.646 |  | 18.302 | 18.302 | 0.80079 | 0 | 13.3236 | 13.4694 | 8.0189 | 66.2661 | 0.20326 | 6.996 | 5.697 | 29.0225 | 283.776 | 295.441 | 1318.7108 | 1366.3759 | -3.6145 | 90.1765 | 830.9085 | 96.5071 | 134.054 | 115.402 | 18.283 | 9.076 | 8.906 | 17.982 | 17.982 | 0.35864 | 0.50473 | 13.7863 | 13.9371 | 4.2299 | 102.2151 | 0.13635 | 5.697 | 5.697 | 15.2295 | 295.441 | 501.3 | 581.0012 | -15.8989 | 94.8452 | 438.2211 | 96.5247 | 115.402 | 99.832 | 18.283 | 4.5 | 4.406 | 8.906 | 8.906 | 0.35512 | 0.50528 | 13.6709 | 13.8204 | 7.5244 | 81.8096 | 0.16893 | 5.697 | 5.697 | 3.2173 | 501.3 | 879.2875 | 1010.009 | -14.8668 | 98.911 | 755.6545 | 99.5742 | 99.832 | 51.082 | 18.283 | 1.08 | 3.646 | 4.726 | 4.726 | 0.1675 | 0.22852 | 9.6 | 9.705 | 9.1775 | 47.9965 | 0.2022 | 5.697 | 5.919 | 79.9299 | 879.2875 | 1318.7108 | 1116.0692 | 15.3666 | 72.9456 | 997.6784 | 91.9884 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
|  | Additional Information |  | Net driving pressure required for permeation, NDP (psi) | 118.8462 | [5 empty] | 1999-01-11 | 14:00 | 5287 | 28.675 | 134.121 | 51.195 | 17.332 | 0 | 14.589 | 3.704 |  | 18.293 | 18.293 | 0.79752 | 0 | 13.2627 | 13.3908 | 7.906 | 67.42 | 0.19862 | 6.716 | 5.766 | 34.028 | 313.44 | 300.2798 | 1435.1926 | 1348.9699 | 6.0077 | 88.6679 | 824.6249 | 95.8735 | 134.121 | 115.447 | 17.332 | 9.069 | 9.024 | 18.093 | 18.093 | 0.36169 | 0.50124 | 13.7757 | 13.9087 | 4.255 | 103.197 | 0.13478 | 5.766 | 5.766 | 17.082 | 300.2798 | 557.1 | 584.8899 | -4.9883 | 94.3113 | 442.5849 | 96.1404 | 115.447 | 100.08 | 17.332 | 4.44 | 4.584 | 9.024 | 9.024 | 0.36301 | 0.49202 | 13.4886 | 13.6188 | 8.2204 | 82.2111 | 0.16566 | 5.766 | 5.766 | 3.2709 | 557.1 | 975.52 | 1093.5314 | -12.0973 | 98.9107 | 825.3157 | 99.6037 | 100.08 | 51.195 | 17.332 | 1.08 | 3.704 | 4.784 | 4.784 | 0.16982 | 0.22575 | 9.6 | 9.6927 | 10.2339 | 48.0716 | 0.20163 | 5.766 | 6.391 | 82.3446 | 975.52 | 1435.1926 | 1235.9491 | 13.8827 | 72.5774 | 1105.7346 | 92.5529 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
|  | Design cross-flow velocity (fps) | 1 | Flow weighted system pressure losses, Lsys (psi) | 61.4 | [5 empty] | 1999-01-11 | 22:00 | 5295 | 28.628 | 134.918 | 51.727 | 18.172 | 0 | 14.59 | 3.704 |  | 18.294 | 18.294 | 0.79753 | 0 | 13.2636 | 13.4103 | 7.9171 | 67.2334 | 0.19946 | 7.076 | 5.754 | 33.887 | 314.064 | 300.5002 | 1432.1437 | 1350.6854 | 5.6879 | 88.7231 | 825.5928 | 95.8954 | 134.918 | 116.182 | 18.172 | 9.01 | 9.086 | 18.096 | 18.096 | 0.36256 | 0.4979 | 13.6861 | 13.8374 | 4.2368 | 103.1412 | 0.13416 | 5.754 | 5.754 | 17.2575 | 300.5002 | 559.8 | 581.3736 | -3.8538 | 94.2571 | 440.9369 | 96.0862 | 116.182 | 100.552 | 18.172 | 4.38 | 4.706 | 9.086 | 9.086 | 0.36792 | 0.48206 | 13.3063 | 13.4535 | 8.1552 | 82.0398 | 0.16399 | 5.754 | 5.754 | 3.2672 | 559.8 | 978.0225 | 1077.78 | -10.1999 | 98.9127 | 818.79 | 99.601 | 100.552 | 51.727 | 18.172 | 1.2 | 3.704 | 4.904 | 4.904 | 0.17222 | 0.2447 | 10.6667 | 10.7846 | 10.4069 | 47.5606 | 0.22676 | 5.754 | 6.356 | 82.4074 | 978.0225 | 1432.1437 | 1268.1786 | 11.4489 | 72.5766 | 1123.1005 | 92.6625 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
|  | Required influent flow to permeate flow rate ratio, QI:Qp | 5:1 | Required influent pressure to the system, PI (psi) | 195.2462 | [5 empty] | 1999-01-12 | 6:00 | 5303.0003 | 28.619 | 134.516 | 51.652 | 18.165 | 0 | 14.586 | 3.763 |  | 18.349 | 18.349 | 0.79492 | 0 | 13.26 | 13.4102 | 7.8367 | 67.0823 | 0.19991 | 6.996 | 5.744 | 33.887 | 314.064 | 300.6144 | 1432.7534 | 1334.4932 | 6.8581 | 88.7274 | 817.5538 | 95.8551 | 134.516 | 115.965 | 18.165 | 8.946 | 8.97 | 17.916 | 17.916 | 0.35861 | 0.49933 | 13.5889 | 13.7428 | 4.2469 | 102.8286 | 0.13365 | 5.744 | 5.744 | 17.238 | 300.6144 | 559.8 | 583.2326 | -4.1859 | 94.2657 | 441.9235 | 96.0993 | 115.965 | 100.41 | 18.165 | 4.44 | 4.53 | 8.97 | 8.97 | 0.36013 | 0.49498 | 13.4886 | 13.6414 | 8.2927 | 81.7298 | 0.16691 | 5.744 | 5.744 | 3.2689 | 559.8 | 978.0225 | 1105.2742 | -13.0111 | 98.9126 | 832.5371 | 99.6074 | 100.41 | 51.652 | 18.165 | 1.2 | 3.763 | 4.963 | 4.963 | 0.17458 | 0.24179 | 10.6667 | 10.7875 | 10.3842 | 47.4818 | 0.22719 | 5.744 | 6.331 | 82.4074 | 978.0225 | 1432.7534 | 1263.6292 | 11.8041 | 72.587 | 1120.8259 | 92.6476 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
|  | Maximum element recovery (%) | NA | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1999-01-12 | 14:00 | 5311 | 28.713 | 134.543 | 51.615 | 18.225 | 0 | 14.592 | 3.703 |  | 18.295 | 18.295 | 0.79759 | 0 | 13.2655 | 13.3785 | 7.9023 | 66.9517 | 0.19982 | 6.964 | 5.764 | 34.122 | 312.72 | 300.1656 | 1437.0226 | 1348.534 | 6.1578 | 88.6323 | 824.3498 | 95.8607 | 134.543 | 115.807 | 18.225 | 9.012 | 9.018 | 18.03 | 18.03 | 0.36077 | 0.49983 | 13.6891 | 13.8057 | 4.2439 | 102.7061 | 0.13442 | 5.764 | 5.764 | 17.1795 | 300.1656 | 558 | 582.9634 | -4.4737 | 94.2767 | 441.5645 | 96.1094 | 115.807 | 100.35 | 18.225 | 4.44 | 4.578 | 9.018 | 9.018 | 0.36269 | 0.49235 | 13.4886 | 13.6035 | 8.2374 | 81.6161 | 0.16668 | 5.764 | 5.764 | 3.2679 | 558 | 968.24 | 1096.0101 | -13.1961 | 98.9113 | 827.0051 | 99.6048 | 100.35 | 51.615 | 18.225 | 1.14 | 3.703 | 4.843 | 4.843 | 0.17098 | 0.23539 | 10.1333 | 10.2197 | 10.2225 | 47.535 | 0.21499 | 5.764 | 6.379 | 82.3514 | 968.24 | 1437.0226 | 1240.9683 | 13.6431 | 72.5647 | 1104.6042 | 92.5447 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
|  | Variability of design flux (%) | 15 | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1999-01-12 | 22:00 | 5319 | 28.641 | 134.529 | 51.832 | 18.144 | 0 | 14.592 | 3.644 |  | 18.236 | 18.236 | 0.80018 | 0 | 13.2655 | 13.407 | 8.0027 | 67.0338 | 0.2 | 6.95 | 5.752 | 33.981 | 314.256 | 300.541 | 1434.5829 | 1367.9512 | 4.6447 | 88.6934 | 834.2461 | 95.9267 | 134.529 | 116.122 | 18.144 | 9.012 | 8.91 | 17.922 | 17.922 | 0.35789 | 0.50285 | 13.6891 | 13.8352 | 4.2637 | 102.9178 | 0.13443 | 5.752 | 5.752 | 17.3745 | 300.541 | 560.7 | 586.9491 | -4.6815 | 94.2189 | 443.745 | 96.0846 | 116.122 | 100.612 | 18.144 | 4.44 | 4.47 | 8.91 | 8.91 | 0.35693 | 0.49832 | 13.4886 | 13.6325 | 8.3428 | 81.8802 | 0.16649 | 5.752 | 5.752 | 3.2691 | 560.7 | 975.065 | 1114.3897 | -14.2888 | 98.9123 | 837.5449 | 99.6097 | 100.612 | 51.832 | 18.144 | 1.14 | 3.644 | 4.784 | 4.784 | 0.16862 | 0.23829 | 10.1333 | 10.2414 | 10.3228 | 47.7552 | 0.21446 | 5.752 | 6.347 | 82.4141 | 975.065 | 1434.5829 | 1254.3246 | 12.5652 | 72.5781 | 1114.6948 | 92.6066
|  | Rejection of reference solute and conditions of test | 500mg/L NaCl 85% CI | [7 empty] | 1999-01-13 | 6:00 | 5327 | 28.662 | 134.73 | 51.862 | 18.157 | 0 | 14.53 | 3.704 |  | 18.234 | 18.234 | 0.79686 | 0 | 13.2091 | 13.3417 | 7.8907 | 67.2483 | 0.19839 | 6.919 | 5.749 | 33.934 | 313.344 | 300.3859 | 1434.5829 | 1345.6198 | 6.2013 | 88.7032 | 823.0029 | 95.8768 | 134.73 | 116.205 | 18.157 | 9.01 | 9.024 | 18.034 | 18.034 | 0.3609 | 0.49961 | 13.6861 | 13.8235 | 4.2436 | 103.0669 | 0.13412 | 5.749 | 5.749 | 17.3355 | 300.3859 | 556.65 | 582.9972 | -4.7332 | 94.2289 | 441.6916 | 96.0752 | 116.205 | 100.65 | 18.157 | 4.44 | 4.584 | 9.024 | 9.024 | 0.36301 | 0.49202 | 13.4886 | 13.624 | 8.2138 | 82.0567 | 0.16603 | 5.749 | 5.749 | 3.269 | 556.65 | 974.8375 | 1092.6473 | -12.0851 | 98.9117 | 824.6486 | 99.6036 | 100.65 | 51.862 | 18.157 | 1.08 | 3.704 | 4.784 | 4.784 | 0.16982 | 0.22575 | 9.6 | 9.6964 | 10.2258 | 47.8732 | 0.20254 | 5.749 | 6.346 | 82.3715 | 974.8375 | 1434.5829 | 1235.0598 | 13.9081 | 72.5781 | 1104.9486 | 92.5452
|  | (e.g., solute type and concentration) | [8 empty] | 1999-01-13 | 14:00 | 5335 | 28.815 | 134.59 | 51.3 | 18.325 | 0 | 14.592 | 3.703 |  | 18.295 | 18.295 | 0.79759 | 0 | 13.2655 | 13.3382 | 7.8916 | 66.7284 | 0.19989 | 7.046 | 5.762 | 32.947 | 303.648 | 298.6315 | 1408.3594 | 1345.5849 | 4.4573 | 88.9673 | 822.1082 | 95.9924 | 134.59 | 115.83 | 18.325 | 9.012 | 9.015 | 18.027 | 18.027 | 0.36069 | 0.49992 | 13.6891 | 13.7642 | 4.2242 | 102.6608 | 0.13407 | 5.762 | 5.762 | 16.9845 | 298.6315 | 543.6 | 580.1848 | -6.7301 | 94.3126 | 439.4082 | 96.1347 | 115.83 | 100.162 | 18.325 | 4.44 | 4.575 | 9.015 | 9.015 | 0.36253 | 0.49251 | 13.4886 | 13.5626 | 8.0255 | 81.6455 | 0.16612 | 5.762 | 5.762 | 3.2536 | 543.6 | 941.395 | 1068.0018 | -13.4488 | 98.9105 | 805.8009 | 99.5962 | 100.162 | 51.3 | 18.325 | 1.14 | 3.703 | 4.843 | 4.843 | 0.17098 | 0.23539 | 10.1333 | 10.1889 | 9.9204 | 47.4856 | 0.21457 | 5.762 | 6.397 | 81.6861 | 941.395 | 1408.3594 | 1206.0637 | 14.3639 | 72.6465 | 1073.7293 | 92.3923
|  | Variability of rejection of reference solute (%) | 10 | [7 empty] | 1999-01-13 | 22:00 | 5343 | 28.781 | 134.576 | 51.697 | 18.214 | 0 | 14.653 | 3.704 |  | 18.357 | 18.357 | 0.79822 | 0 | 13.3209 | 13.4074 | 7.9279 | 66.9946 | 0.20013 | 6.981 | 5.75 | 32.7355 | 305.664 | 298.9498 | 1401.651 | 1352.0916 | 3.5358 | 89.0498 | 825.5207 | 96.0346 | 134.576 | 115.897 | 18.214 | 9.013 | 9.021 | 18.034 | 18.034 | 0.36086 | 0.49978 | 13.6906 | 13.7795 | 4.2329 | 102.7896 | 0.13406 | 5.75 | 5.75 | 16.6725 | 298.9498 | 544.95 | 580.9767 | -6.611 | 94.423 | 439.9632 | 96.2105 | 115.897 | 100.125 | 18.214 | 4.44 | 4.581 | 9.021 | 9.021 | 0.36285 | 0.49218 | 13.4886 | 13.5762 | 8.0421 | 81.7549 | 0.16606 | 5.75 | 5.75 | 3.2544 | 544.95 | 946.855 | 1069.9726 | -13.0028 | 98.9114 | 807.4613 | 99.597 | 100.125 | 51.697 | 18.214 | 1.2 | 3.704 | 4.904 | 4.904 | 0.17222 | 0.2447 | 10.6667 | 10.7359 | 10.053 | 47.644 | 0.22534 | 5.75 | 6.322 | 81.7018 | 946.855 | 1401.651 | 1227.1422 | 12.4502 | 72.6704 | 1086.9986 | 92.4837
|  | Standard testing recovery (%) | 10 | [7 empty] | 1999-01-14 | 6:00 | 5351 | 28.551 | 134.744 | 51.757 | 18.166 | 0 | 14.469 | 3.644 |  | 18.113 | 18.113 | 0.79882 | 0 | 13.1536 | 13.3294 | 7.9564 | 67.1281 | 0.19857 | 6.932 | 5.725 | 33.1585 | 308.352 | 299.676 | 1413.2378 | 1357.9202 | 3.9142 | 88.9352 | 828.7981 | 95.9992 | 134.744 | 116.347 | 18.166 | 9.009 | 8.964 | 17.973 | 17.973 | 0.35929 | 0.50125 | 13.6846 | 13.8674 | 4.2524 | 103.1271 | 0.13447 | 5.725 | 5.725 | 16.653 | 299.676 | 549 | 584.1198 | -6.397 | 94.443 | 441.8979 | 96.2315 | 116.347 | 100.552 | 18.166 | 4.44 | 4.524 | 8.964 | 8.964 | 0.35981 | 0.49531 | 13.4886 | 13.6688 | 8.1354 | 82.1481 | 0.16639 | 5.725 | 5.725 | 3.2609 | 549 | 963.0075 | 1084.606 | -12.6269 | 98.9118 | 816.803 | 99.6008 | 100.552 | 51.757 | 18.166 | 1.02 | 3.644 | 4.664 | 4.664 | 0.16622 | 0.2187 | 9.0667 | 9.1878 | 10.0429 | 47.9456 | 0.19163 | 5.725 | 6.296 | 82.0176 | 963.0075 | 1413.2378 | 1209.6073 | 14.4088 | 72.6312 | 1086.3074 | 92.4499
|  | Standard testing pH | 7.5 | [7 empty] | 1999-01-14 | 14:00 | 5359 | 28.624 | 134.616 | 51.667 | 18.234 | 0 | 14.472 | 3.643 |  | 18.115 | 18.115 | 0.7989 | 0 | 13.1564 | 13.3034 | 7.9447 | 66.9628 | 0.19867 | 6.969 | 5.748 | 33.276 | 306.912 | 299.317 | 1416.8974 | 1356.178 | 4.2854 | 88.8827 | 827.7475 | 95.9799 | 134.616 | 115.972 | 18.234 | 8.952 | 9.019 | 17.971 | 17.971 | 0.36 | 0.49814 | 13.598 | 13.7499 | 4.226 | 102.834 | 0.13371 | 5.748 | 5.748 | 16.887 | 299.317 | 550.8 | 579.6488 | -5.2376 | 94.3582 | 439.4829 | 96.1575 | 115.972 | 100.425 | 18.234 | 4.44 | 4.579 | 9.019 | 9.019 | 0.36275 | 0.49229 | 13.4886 | 13.6394 | 8.13 | 81.8345 | 0.16667 | 5.748 | 5.748 | 3.2615 | 550.8 | 952.5425 | 1081.7174 | -13.5611 | 98.9104 | 816.2587 | 99.6004 | 100.425 | 51.667 | 18.234 | 1.08 | 3.643 | 4.723 | 4.723 | 0.16738 | 0.22867 | 9.6 | 9.7073 | 9.9959 | 47.8161 | 0.20301 | 5.748 | 6.316 | 81.9952 | 952.5425 | 1416.8974 | 1210.624 | 14.5581 | 72.6059 | 1081.5833 | 92.419
|  | Acceptable range of operating pressures | 80 - 350 | [7 empty] | 1999-01-14 | 22:00 | 5367.0003 | 28.59 | 134.435 | 51.66 | 18.202 | 0 | 14.652 | 3.643 |  | 18.295 | 18.295 | 0.80087 | 0 | 13.32 | 13.4824 | 8.0202 | 66.8253 | 0.20176 | 6.905 | 5.736 | 33.2055 | 308.112 | 299.5699 | 1415.0678 | 1370.8769 | 3.1229 | 88.9156 | 835.2234 | 96.0244 | 134.435 | 115.95 | 18.202 | 9.012 | 8.905 | 17.917 | 17.917 | 0.35776 | 0.50299 | 13.6891 | 13.856 | 4.2593 | 102.7312 | 0.13488 | 5.736 | 5.736 | 16.7505 | 299.5699 | 549.9 | 585.7876 | -6.5262 | 94.4085 | 442.6788 | 96.2161 | 115.95 | 100.447 | 18.202 | 4.44 | 4.465 | 8.905 | 8.905 | 0.35666 | 0.4986 | 13.4886 | 13.6531 | 8.1843 | 81.8122 | 0.16688 | 5.736 | 5.736 | 3.2612 | 549.9 | 955.7275 | 1093.4781 | -14.4132 | 98.9114 | 821.689 | 99.6031 | 100.447 | 51.66 | 18.202 | 1.2 | 3.643 | 4.843 | 4.843 | 0.16978 | 0.24778 | 10.6667 | 10.7967 | 10.176 | 47.6755 | 0.22646 | 5.736 | 6.287 | 82.0243 | 955.7275 | 1415.0678 | 1243.5243 | 12.1226 | 72.6193 | 1099.6259 | 92.5407
|  | Acceptable range of operating pH values | 4 - 11 | [7 empty] | 1999-01-15 | 6:00 | 5375 | 28.662 | 134.569 | 51.81 | 18.256 | 0 | 14.471 | 3.704 |  | 18.175 | 18.175 | 0.7962 | 0 | 13.1555 | 13.2875 | 7.8685 | 67.065 | 0.19813 | 6.913 | 5.757 | 33.9575 | 313.392 | 300.3778 | 1433.9732 | 1341.2437 | 6.4666 | 88.6951 | 820.8107 | 95.8629 | 134.569 | 116.295 | 18.256 | 9.011 | 8.962 | 17.973 | 17.973 | 0.35926 | 0.50136 | 13.6876 | 13.825 | 4.2543 | 102.9217 | 0.13433 | 5.757 | 5.757 | 17.277 | 300.3778 | 556.65 | 585.0264 | -5.0977 | 94.2482 | 442.7021 | 96.0974 | 116.295 | 100.492 | 18.256 | 4.44 | 4.522 | 8.962 | 8.962 | 0.3597 | 0.49543 | 13.4886 | 13.624 | 8.2506 | 81.8869 | 0.16638 | 5.757 | 5.757 | 3.2675 | 556.65 | 974.61 | 1099.9977 | -12.8654 | 98.9122 | 828.3239 | 99.6055 | 100.492 | 51.81 | 18.256 | 1.02 | 3.704 | 4.724 | 4.724 | 0.16862 | 0.21592 | 9.0667 | 9.1577 | 10.1513 | 47.7437 | 0.19181 | 5.757 | 6.32 | 82.3334 | 974.61 | 1433.9732 | 1220.3233 | 14.8992 | 72.59 | 1097.4667 | 92.4979
|  | Typical pressure drop across a single element (psi) | 2 | [7 empty] | 1999-01-15 | 14:00 | 5383 | 28.789 | 134.174 | 51.442 | 18.196 | 0 | 14.535 | 3.703 |  | 18.238 | 18.238 | 0.79696 | 0 | 13.2136 | 13.2963 | 7.8702 | 66.7418 | 0.19922 | 6.862 | 5.764 | 34.3335 | 311.472 | 299.9861 | 1443.1208 | 1342.7245 | 6.9569 | 88.555 | 821.3553 | 95.8199 | 134.174 | 115.537 | 18.196 | 9.015 | 8.95 | 17.965 | 17.965 | 0.359 | 0.50181 | 13.6937 | 13.7793 | 4.2483 | 102.4112 | 0.13455 | 5.764 | 5.764 | 17.4525 | 299.9861 | 556.2 | 584.5716 | -5.101 | 94.1822 | 442.2788 | 96.054 | 115.537 | 100.132 | 18.196 | 4.38 | 4.57 | 8.95 | 8.95 | 0.36066 | 0.48939 | 13.3063 | 13.3896 | 8.1791 | 81.4594 | 0.16437 | 5.764 | 5.764 | 3.267 | 556.2 | 962.78 | 1086.1445 | -12.8134 | 98.9109 | 821.1723 | 99.6022 | 100.132 | 51.442 | 18.196 | 1.14 | 3.703 | 4.843 | 4.843 | 0.17098 | 0.23539 | 10.1333 | 10.1967 | 10.1611 | 47.4299 | 0.21499 | 5.764 | 6.387 | 82.2125 | 962.78 | 1443.1208 | 1233.8702 | 14.4999 | 72.5946 | 1098.3251 | 92.5147
|  | Maximum permissible SDI | 5 | [7 empty] | 1999-01-15 | 22:00 | 5391 | 28.811 | 133.772 | 50.865 | 18.367 | 0 | 14.715 | 3.644 |  | 18.359 | 18.359 | 0.80151 | 0 | 13.3773 | 13.4522 | 8.0129 | 65.9386 | 0.20401 | 7.146 | 5.707 | 29.516 | 281.28 | 294.9269 | 1329.0782 | 1366.6945 | -2.8302 | 89.9921 | 830.8107 | 96.4473 | 133.772 | 115.005 | 18.367 | 9.015 | 8.904 | 17.919 | 17.919 | 0.35777 | 0.5031 | 13.6937 | 13.7704 | 4.2103 | 101.8112 | 0.13525 | 5.707 | 5.707 | 15.405 | 294.9269 | 497.7 | 577.9334 | -16.1208 | 94.7767 | 436.4301 | 96.4702 | 115.005 | 99.412 | 18.367 | 4.5 | 4.404 | 8.904 | 8.904 | 0.35501 | 0.50539 | 13.6709 | 13.7475 | 7.4712 | 81.3703 | 0.16895 | 5.707 | 5.707 | 3.2139 | 497.7 | 864.2725 | 1002.9651 | -16.0473 | 98.9103 | 750.3325 | 99.5717 | 99.412 | 50.865 | 18.367 | 1.2 | 3.644 | 4.844 | 4.844 | 0.16982 | 0.24773 | 10.6667 | 10.7264 | 9.138 | 47.6335 | 0.22519 | 5.707 | 6.087 | 79.6611 | 864.2725 | 1329.0782 | 1122.6517 | 15.5316 | 72.9895 | 993.4621 | 91.9815
|  | Maximum permissible turbidity (ntu) | less than 1 | [7 empty] | 1999-01-16 | 6:00 | 5399 | 28.819 | 134.054 | 51.112 | 18.322 | 0 | 14.652 | 3.644 |  | 18.296 | 18.296 | 0.80083 | 0 | 13.32 | 13.3915 | 7.9967 | 66.2643 | 0.20209 | 7.095 | 5.709 | 29.375 | 281.04 | 295.0085 | 1326.0289 | 1363.0825 | -2.7943 | 90.0427 | 829.0455 | 96.4568 | 134.054 | 115.095 | 18.322 | 9.012 | 9.148 | 18.16 | 18.16 | 0.36424 | 0.49626 | 13.6891 | 13.7625 | 4.1706 | 102.0819 | 0.13482 | 5.709 | 5.709 | 15.5805 | 295.0085 | 497.25 | 570.2823 | -14.6872 | 94.7186 | 432.6454 | 96.3988 | 115.095 | 99.36 | 18.322 | 4.44 | 4.708 | 9.148 | 9.148 | 0.36963 | 0.48535 | 13.4886 | 13.561 | 7.2699 | 81.6356 | 0.16612 | 5.709 | 5.709 | 3.2152 | 497.25 | 867.23 | 963.1622 | -11.0619 | 98.9101 | 730.2061 | 99.5597 | 99.36 | 51.112 | 18.322 | 1.2 | 3.644 | 4.844 | 4.844 | 0.16982 | 0.24773 | 10.6667 | 10.7239 | 9.1726 | 47.7414 | 0.22462 | 5.709 | 6.033 | 79.6477 | 867.23 | 1326.0289 | 1126.5875 | 15.0405 | 73.0016 | 996.9088 | 92.0105
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | [7 empty] | 1999-01-16 | 14:00 | 5407 | 28.862 | 134.65 | 56.925 | 18.532 | 0 | 14.834 | 3.344 |  | 18.178 | 18.178 | 0.81604 | 0 | 13.4855 | 13.5406 | 8.5429 | 68.7126 | 0.19706 | 7.125 | 5.729 | 30.785 | 288.96 | 296.257 | 1372.9878 | 1473.8918 | -7.3492 | 89.6087 | 885.0744 | 96.5218 | 134.65 | 116.325 | 18.532 | 9.074 | 9.017 | 18.091 | 18.091 | 0.36157 | 0.50158 | 13.7833 | 13.8396 | 4.2099 | 102.7456 | 0.1347 | 5.729 | 5.729 | 16.185 | 296.257 | 518.4 | 578.0994 | -11.5161 | 94.5368 | 437.1782 | 96.2978 | 116.325 | 101.385 | 18.532 | 4.5 | 4.517 | 9.017 | 9.017 | 0.36104 | 0.49906 | 13.6709 | 13.7268 | 7.7175 | 82.6055 | 0.16617 | 5.729 | 5.729 | 3.2549 | 518.4 | 913.185 | 1031.6064 | -12.9679 | 98.9013 | 775.0032 | 99.58 | 101.385 | 56.925 | 18.532 | 1.26 | 3.344 | 4.604 | 4.604 | 0.15902 | 0.27368 | 11.2 | 11.2458 | 9.8962 | 50.7268 | 0.22169 | 5.729 | 6.288 | 80.4518 | 913.185 | 1372.9878 | 1226.9541 | 10.6362 | 72.8439 | 1070.0695 | 92.4816
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1999-01-16 | 22:00 | 5415 | 28.883 | 134.817 | 56.857 | 18.553 | 0 | 14.775 | 3.345 |  | 18.12 | 18.12 | 0.8154 | 0 | 13.4318 | 13.4784 | 8.5096 | 68.7744 | 0.19598 | 7.007 | 5.723 | 31.161 | 289.776 | 296.3794 | 1371.7679 | 1467.8596 | -7.0049 | 89.4861 | 882.1195 | 96.4675 | 134.817 | 116.52 | 18.553 | 9.075 | 8.844 | 17.919 | 17.919 | 0.35697 | 0.50645 | 13.7848 | 13.8326 | 4.2404 | 102.8751 | 0.13446 | 5.723 | 5.723 | 16.1265 | 296.3794 | 521.55 | 583.9523 | -11.9648 | 94.5588 | 440.1658 | 96.3363 | 116.52 | 101.505 | 18.553 | 4.5 | 4.344 | 8.844 | 8.844 | 0.35181 | 0.50882 | 13.6709 | 13.7182 | 7.8675 | 82.592 | 0.1661 | 5.723 | 5.723 | 3.2564 | 521.55 | 916.1425 | 1058.4563 | -15.534 | 98.9013 | 790.0032 | 99.5878 | 101.505 | 56.857 | 18.553 | 1.2 | 3.345 | 4.545 | 4.545 | 0.15786 | 0.26403 | 10.6667 | 10.7036 | 9.8555 | 50.7725 | 0.21082 | 5.723 | 6.238 | 80.4877 | 916.1425 | 1371.7679 | 1215.929 | 11.3604 | 72.843 | 1066.0357 | 92.4498
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. | [8 empty] | 1999-01-17 | 6:00 | 5423 | 28.874 | 135.286 | 50.43 | 18.445 | 0 | 14.772 | 3.763 |  | 18.535 | 18.535 | 0.79698 | 0 | 13.4291 | 13.4792 | 7.8704 | 66.5426 | 0.20256 | 6.964 | 5.699 | 30.7145 | 289.68 | 296.3549 | 1349.2035 | 1339.1504 | 0.74511 | 89.6359 | 817.7527 | 96.244 | 135.286 | 116.49 | 18.445 | 9.072 | 9.024 | 18.096 | 18.096 | 0.36173 | 0.50133 | 13.7803 | 13.8317 | 4.2121 | 103.2309 | 0.13399 | 5.699 | 5.699 | 16.0485 | 296.3549 | 513.9 | 578.1523 | -12.5029 | 94.5847 | 437.2536 | 96.3297 | 116.49 | 100.485 | 18.445 | 4.5 | 4.524 | 9.024 | 9.024 | 0.36141 | 0.49867 | 13.6709 | 13.7219 | 7.6466 | 82.3959 | 0.16654 | 5.699 | 5.699 | 3.2252 | 513.9 | 887.705 | 1021.8656 | -15.1132 | 98.9117 | 767.8828 | 99.58 | 100.485 | 50.43 | 18.445 | 1.2 | 3.763 | 4.963 | 4.963 | 0.17458 | 0.24179 | 10.6667 | 10.7065 | 9.3621 | 47.6504 | 0.22469 | 5.699 | 6.186 | 80.2458 | 887.705 | 1349.2035 | 1145.1993 | 15.1203 | 72.9224 | 1016.4522 | 92.1053
[11 empty] | 1999-01-17 | 14:00 | 5431 | 28.849 | 135.34 | 50.557 | 18.405 | 0 | 14.713 | 3.763 |  | 18.476 | 18.476 | 0.79633 | 0 | 13.3755 | 13.4353 | 7.8445 | 66.699 | 0.20143 | 7.075 | 5.724 | 31.7015 | 295.104 | 297.1709 | 1374.8173 | 1335.1329 | 2.8865 | 89.3322 | 816.1519 | 96.1157 | 135.34 | 116.407 | 18.405 | 9.073 | 9.141 | 18.214 | 18.214 | 0.36487 | 0.49813 | 13.7818 | 13.8434 | 4.1979 | 103.2706 | 0.13405 | 5.724 | 5.724 | 16.614 | 297.1709 | 527.4 | 575.6407 | -9.1469 | 94.4093 | 436.4058 | 96.193 | 116.407 | 100.59 | 18.405 | 4.56 | 4.581 | 9.141 | 9.141 | 0.36605 | 0.49885 | 13.8532 | 13.9151 | 7.8505 | 82.243 | 0.1692 | 5.724 | 5.724 | 3.2355 | 527.4 | 905.2225 | 1049.1616 | -15.901 | 98.9112 | 788.2808 | 99.5895 | 100.59 | 50.557 | 18.405 | 1.08 | 3.763 | 4.843 | 4.843 | 0.17218 | 0.223 | 9.6 | 9.6429 | 9.4276 | 47.7409 | 0.20199 | 5.724 | 6.344 | 80.7722 | 905.2225 | 1374.8173 | 1141.8439 | 16.9458 | 72.8196 | 1023.5332 | 92.1085
[11 empty] | 1999-01-17 | 22:00 | 5439.0003 | 28.802 | 135.434 | 50.715 | 18.37 | 0 | 14.65 | 3.763 |  | 18.413 | 18.413 | 0.79563 | 0 | 13.3182 | 13.3964 | 7.8327 | 66.8718 | 0.20033 | 6.93 | 5.715 | 31.584 | 296.592 | 297.4075 | 1372.3776 | 1332.3038 | 2.92 | 89.3802 | 814.8556 | 96.124 | 135.434 | 116.655 | 18.37 | 9.13 | 8.966 | 18.096 | 18.096 | 0.36096 | 0.50453 | 13.8684 | 13.9498 | 4.2393 | 103.4352 | 0.13486 | 5.715 | 5.715 | 16.497 | 297.4075 | 526.5 | 583.4563 | -10.8179 | 94.4531 | 440.4319 | 96.2544 | 116.655 | 100.815 | 18.37 | 4.5 | 4.466 | 8.966 | 8.966 | 0.35832 | 0.5019 | 13.6709 | 13.7511 | 7.8689 | 82.4961 | 0.16669 | 5.715 | 5.715 | 3.2368 | 526.5 | 912.275 | 1053.7468 | -15.5076 | 98.9116 | 790.1234 | 99.5903 | 100.815 | 50.715 | 18.37 | 1.02 | 3.763 | 4.783 | 4.783 | 0.17098 | 0.21326 | 9.0667 | 9.1199 | 9.4416 | 47.9534 | 0.19018 | 5.715 | 6.301 | 80.8058 | 912.275 | 1372.3776 | 1137.6533 | 17.1035 | 72.83 | 1024.9642 | 92.1162
[11 empty] | 1999-01-18 | 6:00 | 5447 | 28.815 | 135.239 | 50.52 | 18.372 | 0 | 14.588 | 3.763 |  | 18.351 | 18.351 | 0.79494 | 0 | 13.2618 | 13.3345 | 7.8144 | 66.6931 | 0.19994 | 6.91 | 5.725 | 31.584 | 296.592 | 297.5299 | 1372.3776 | 1328.5209 | 3.1957 | 89.3846 | 813.0254 | 96.1153 | 135.239 | 116.602 | 18.372 | 9.128 | 9.14 | 18.268 | 18.268 | 0.36557 | 0.49967 | 13.8653 | 13.9413 | 4.2148 | 103.3337 | 0.13492 | 5.725 | 5.725 | 16.419 | 297.5299 | 526.05 | 578.2718 | -9.9271 | 94.4816 | 437.9008 | 96.2505 | 116.602 | 100.59 | 18.372 | 4.44 | 4.7 | 9.14 | 9.14 | 0.3692 | 0.48578 | 13.4886 | 13.5626 | 7.6976 | 82.5264 | 0.16434 | 5.725 | 5.725 | 3.2368 | 526.05 | 912.0475 | 1019.9416 | -11.8299 | 98.9121 | 772.9958 | 99.5813 | 100.59 | 50.52 | 18.372 | 1.02 | 3.763 | 4.783 | 4.783 | 0.17098 | 0.21326 | 9.0667 | 9.1164 | 9.4391 | 47.7439 | 0.19094 | 5.725 | 6.274 | 80.8013 | 912.0475 | 1372.3776 | 1137.3654 | 17.1245 | 72.8426 | 1024.7064 | 92.1147
[11 empty] | 1999-01-18 | 14:00 | 5455.0003 | 28.738 | 135.494 | 50.475 | 18.4 | 0 | 14.776 | 3.822 |  | 18.598 | 18.598 | 0.79449 | 0 | 13.4327 | 13.5372 | 7.7849 | 66.7996 | 0.20265 | 6.973 | 5.727 | 31.349 | 291.84 | 296.771 | 1365.6692 | 1322.9029 | 3.1315 | 89.4366 | 809.837 | 96.129 | 135.494 | 116.437 | 18.4 | 9.076 | 9.012 | 18.088 | 18.088 | 0.36146 | 0.50177 | 13.7863 | 13.8935 | 4.2161 | 103.3494 | 0.13443 | 5.727 | 5.727 | 16.3605 | 296.771 | 520.2 | 579.173 | -11.3366 | 94.4872 | 437.972 | 96.2645 | 116.437 | 100.515 | 18.4 | 4.5 | 4.512 | 9.012 | 9.012 | 0.36077 | 0.49933 | 13.6709 | 13.7772 | 7.7477 | 82.3283 | 0.16734 | 5.727 | 5.727 | 3.2309 | 520.2 | 898.17 | 1035.7942 | -15.3227 | 98.9113 | 777.9971 | 99.5847 | 100.515 | 50.475 | 18.4 | 1.2 | 3.822 | 5.022 | 5.022 | 0.17694 | 0.23895 | 10.6667 | 10.7496 | 9.4594 | 47.6356 | 0.22566 | 5.727 | 6.247 | 80.584 | 898.17 | 1365.6692 | 1154.8689 | 15.4357 | 72.8464 | 1026.5195 | 92.1498
[11 empty] | 1999-01-18 | 22:00 | 5463 | 28.7 | 135.487 | 50.572 | 18.321 | 0 | 14.654 | 3.763 |  | 18.417 | 18.417 | 0.79568 | 0 | 13.3218 | 13.4405 | 7.8329 | 66.8756 | 0.20098 | 6.902 | 5.716 | 31.1845 | 293.28 | 296.9669 | 1362.0101 | 1331.9855 | 2.2044 | 89.499 | 814.4762 | 96.1712 | 135.487 | 116.662 | 18.321 | 9.074 | 9.019 | 18.093 | 18.093 | 0.36162 | 0.50152 | 13.7833 | 13.9061 | 4.2209 | 103.5326 | 0.13432 | 5.716 | 5.716 | 16.146 | 296.9669 | 522.45 | 579.5003 | -10.9198 | 94.563 | 438.2336 | 96.3157 | 116.662 | 100.575 | 18.321 | 4.5 | 4.519 | 9.019 | 9.019 | 0.36114 | 0.49895 | 13.6709 | 13.7927 | 7.7774 | 82.5201 | 0.16714 | 5.716 | 5.716 | 3.2321 | 522.45 | 904.7675 | 1039.4849 | -14.8897 | 98.9116 | 780.9675 | 99.5861 | 100.575 | 50.572 | 18.321 | 1.08 | 3.763 | 4.843 | 4.843 | 0.17218 | 0.223 | 9.6 | 9.6855 | 9.4235 | 47.829 | 0.2025 | 5.716 | 6.177 | 80.6758 | 904.7675 | 1362.0101 | 1141.286 | 16.2058 | 72.8334 | 1023.0267 | 92.114
[11 empty] | 1999-01-19 | 6:00 | 5471 | 28.662 | 135.313 | 50.52 | 18.282 | 0 | 14.712 | 3.823 |  | 18.535 | 18.535 | 0.79374 | 0 | 13.3745 | 13.5088 | 7.7824 | 66.8521 | 0.20207 | 6.876 | 5.736 | 31.0435 | 293.712 | 297.1872 | 1358.3511 | 1321.3845 | 2.7214 | 89.5542 | 809.2858 | 96.1641 | 135.313 | 116.647 | 18.282 | 9.072 | 8.899 | 17.971 | 17.971 | 0.3584 | 0.50481 | 13.7803 | 13.9186 | 4.2465 | 103.4515 | 0.13454 | 5.736 | 5.736 | 15.912 | 297.1872 | 524.7 | 583.9305 | -11.2885 | 94.6458 | 440.5588 | 96.3882 | 116.647 | 100.702 | 18.282 | 4.5 | 4.399 | 8.899 | 8.899 | 0.35474 | 0.50567 | 13.6709 | 13.8082 | 7.8819 | 82.5106 | 0.16735 | 5.736 | 5.736 | 3.2332 | 524.7 | 902.9475 | 1058.1396 | -17.1873 | 98.9121 | 791.4198 | 99.5915 | 100.702 | 50.52 | 18.282 | 1.14 | 3.823 | 4.963 | 4.963 | 0.17578 | 0.2297 | 10.1333 | 10.2351 | 9.4487 | 47.8803 | 0.21376 | 5.736 | 6.12 | 80.6758 | 902.9475 | 1358.3511 | 1148.1449 | 15.4751 | 72.8535 | 1025.5462 | 92.1334
[11 empty] | 1999-01-19 | 14:00 | 5479 | 28.7 | 135.729 | 50.977 | 18.373 | 0 | 14.654 | 3.762 |  | 18.416 | 18.416 | 0.79572 | 0 | 13.3218 | 13.4405 | 7.8428 | 67.1372 | 0.20019 | 6.885 | 5.767 | 32.994 | 306.192 | 299.064 | 1407.7492 | 1335.4781 | 5.1338 | 88.9676 | 817.271 | 95.9629 | 135.729 | 116.932 | 18.373 | 9.074 | 9.017 | 18.091 | 18.091 | 0.36157 | 0.50158 | 13.7833 | 13.9061 | 4.2454 | 103.7121 | 0.13408 | 5.767 | 5.767 | 16.6335 | 299.064 | 547.65 | 583.2799 | -6.506 | 94.4381 | 441.1719 | 96.2297 | 116.932 | 101.175 | 18.373 | 4.5 | 4.517 | 9.017 | 9.017 | 0.36104 | 0.49906 | 13.6709 | 13.7927 | 8.1557 | 82.5248 | 0.16713 | 5.767 | 5.767 | 3.2537 | 547.65 | 945.945 | 1089.9975 | -15.2284 | 98.912 | 818.8237 | 99.6026 | 101.175 | 50.977 | 18.373 | 1.08 | 3.762 | 4.842 | 4.842 | 0.17214 | 0.22305 | 9.6 | 9.6855 | 9.8842 | 47.8188 | 0.20255 | 5.767 | 6.308 | 81.592 | 945.945 | 1407.7492 | 1194.0846 | 15.1777 | 72.7175 | 1070.0148 | 92.3747
[11 empty] | 1999-01-19 | 22:00 | 5487 | 28.624 | 135.923 | 50.79 | 18.289 | 0 | 14.593 | 3.823 |  | 18.416 | 18.416 | 0.79241 | 0 | 13.2664 | 13.4146 | 7.7493 | 67.3182 | 0.19927 | 6.837 | 5.752 | 32.8295 | 307.584 | 299.2598 | 1393.1131 | 1316.2669 | 5.5161 | 89.0298 | 807.7634 | 95.9358 | 135.923 | 117.15 | 18.289 | 9.073 | 9.023 | 18.096 | 18.096 | 0.36172 | 0.50138 | 13.7818 | 13.9358 | 4.2458 | 104.0017 | 0.134 | 5.752 | 5.752 | 16.731 | 299.2598 | 545.4 | 583.3543 | -6.959 | 94.4092 | 441.3071 | 96.2088 | 117.15 | 101.085 | 18.289 | 4.5 | 4.523 | 9.023 | 9.023 | 0.36136 | 0.49873 | 13.6709 | 13.8237 | 8.1184 | 82.7101 | 0.16713 | 5.752 | 5.752 | 3.2547 | 545.4 | 947.9925 | 1084.7884 | -14.4301 | 98.9124 | 815.0942 | 99.6007 | 101.085 | 50.79 | 18.289 | 1.02 | 3.823 | 4.843 | 4.843 | 0.17338 | 0.21061 | 9.0667 | 9.168 | 9.8194 | 47.8291 | 0.19168 | 5.752 | 6.25 | 81.6323 | 947.9925 | 1393.1131 | 1179.1427 | 15.3591 | 72.7219 | 1063.5676 | 92.3247
[11 empty] | 1999-01-20 | 0:00 | 5489 | 28.645 | 136.244 | 51.15 | 18.366 | 0 | 14.775 | 3.823 |  | 18.598 | 18.598 | 0.79444 | 0 | 13.4318 | 13.5735 | 7.8139 | 67.5171 | 0.20104 | 7.046 | 5.747 | 32.7825 | 306.672 | 299.2517 | 1403.4805 | 1329.0927 | 5.3002 | 89.0452 | 814.1722 | 95.9735 | 136.244 | 117.262 | 18.366 | 9.075 | 9.019 | 18.094 | 18.094 | 0.36164 | 0.50155 | 13.7848 | 13.9302 | 4.2469 | 104.1401 | 0.13376 | 5.747 | 5.747 | 16.7115 | 299.2517 | 545.4 | 583.5462 | -6.9942 | 94.4156 | 441.3989 | 96.214 | 117.262 | 101.295 | 18.366 | 4.5 | 4.519 | 9.019 | 9.019 | 0.36114 | 0.49895 | 13.6709 | 13.8151 | 8.1208 | 82.7917 | 0.16687 | 5.747 | 5.747 | 3.255 | 545.4 | 947.765 | 1085.2656 | -14.5079 | 98.9123 | 815.3328 | 99.6008 | 101.295 | 51.15 | 18.366 | 1.2 | 3.823 | 5.023 | 5.023 | 0.17698 | 0.2389 | 10.6667 | 10.7792 | 10.0211 | 47.8354 | 0.22534 | 5.747 | 6.224 | 81.592 | 947.765 | 1403.4805 | 1219.6477 | 13.0984 | 72.7347 | 1083.7064 | 92.471
[11 empty] | 1999-01-20 | 14:00 | 5503 | 28.772 | 135.601 | 50.902 | 18.364 | 0 | 14.652 | 3.822 |  | 18.474 | 18.474 | 0.79311 | 0 | 13.32 | 13.4101 | 7.7582 | 67.1293 | 0.19976 | 7.034 | 5.789 | 33.8165 | 309.6 | 299.7984 | 1426.045 | 1319.4653 | 7.4738 | 88.7203 | 809.6318 | 95.8232 | 135.601 | 116.82 | 18.364 | 9.072 | 9.081 | 18.153 | 18.153 | 0.36325 | 0.49975 | 13.7803 | 13.8734 | 4.2408 | 103.6057 | 0.13391 | 5.789 | 5.789 | 16.9845 | 299.7984 | 555.3 | 582.332 | -4.868 | 94.3347 | 441.0652 | 96.1492 | 116.82 | 101.092 | 18.364 | 4.5 | 4.581 | 9.081 | 9.081 | 0.36445 | 0.49554 | 13.6709 | 13.7633 | 8.2318 | 82.3602 | 0.16711 | 5.789 | 5.789 | 3.2618 | 555.3 | 957.775 | 1097.5772 | -14.5966 | 98.912 | 826.4386 | 99.6053 | 101.092 | 50.902 | 18.364 | 1.08 | 3.822 | 4.902 | 4.902 | 0.17454 | 0.22032 | 9.6 | 9.6649 | 9.995 | 47.638 | 0.20288 | 5.789 | 6.245 | 82.0086 | 957.775 | 1426.045 | 1205.2443 | 15.4834 | 72.6454 | 1081.5097 | 92.4172
[11 empty] | 1999-01-20 | 22:00 | 5511.0003 | 28.649 | 135.956 | 51.165 | 18.291 | 0 | 14.774 | 3.883 |  | 18.657 | 18.657 | 0.79187 | 0 | 13.4309 | 13.571 | 7.7486 | 67.5209 | 0.20099 | 7.025 | 5.763 | 34.4745 | 319.536 | 301.4467 | 1437.0226 | 1317.22 | 8.3369 | 88.5637 | 809.3334 | 95.7404 | 135.956 | 117.112 | 18.291 | 9.074 | 9.082 | 18.156 | 18.156 | 0.36331 | 0.49978 | 13.7833 | 13.927 | 4.2642 | 103.9788 | 0.13394 | 5.763 | 5.763 | 17.082 | 301.4467 | 573.3 | 585.561 | -2.1387 | 94.3333 | 443.5038 | 96.1484 | 117.112 | 101.385 | 18.291 | 4.5 | 4.582 | 9.082 | 9.082 | 0.36451 | 0.49549 | 13.6709 | 13.8135 | 8.4993 | 82.4582 | 0.16752 | 5.763 | 5.763 | 3.2776 | 573.3 | 991.9 | 1133.1212 | -14.2374 | 98.9127 | 853.2106 | 99.6159 | 101.385 | 51.165 | 18.291 | 1.2 | 3.883 | 5.083 | 5.083 | 0.17939 | 0.23608 | 10.6667 | 10.7779 | 10.4978 | 47.4862 | 0.22697 | 5.763 | 6.149 | 82.6202 | 991.9 | 1437.0226 | 1272.9033 | 11.4208 | 72.5921 | 1132.4016 | 92.704
[11 empty] | 1999-01-21 | 6:00 | 5519 | 28.607 | 136.231 | 51.247 | 18.3 | 0 | 14.775 | 3.823 |  | 18.598 | 18.598 | 0.79444 | 0 | 13.4318 | 13.5888 | 7.8388 | 67.6002 | 0.20102 | 6.968 | 5.752 | 34.357 | 320.928 | 301.6752 | 1433.363 | 1334.7975 | 6.8765 | 88.6113 | 818.2363 | 95.8011 | 136.231 | 117.457 | 18.3 | 9.075 | 9.019 | 18.094 | 18.094 | 0.36164 | 0.50155 | 13.7848 | 13.9459 | 4.2748 | 104.2692 | 0.13375 | 5.752 | 5.752 | 17.277 | 301.6752 | 572.4 | 587.8393 | -2.6973 | 94.273 | 444.7572 | 96.1154 | 117.457 | 102.15 | 18.3 | 4.5 | 4.519 | 9.019 | 9.019 | 0.36114 | 0.49895 | 13.6709 | 13.8306 | 8.5249 | 82.9786 | 0.16668 | 5.752 | 5.752 | 3.2772 | 572.4 | 994.63 | 1139.1299 | -14.528 | 98.9137 | 855.765 | 99.617 | 102.15 | 51.247 | 18.3 | 1.2 | 3.823 | 5.023 | 5.023 | 0.17698 | 0.2389 | 10.6667 | 10.7913 | 10.5516 | 47.8469 | 0.22554 | 5.752 | 6.044 | 82.6112 | 994.63 | 1433.363 | 1280.9032 | 10.6365 | 72.6158 | 1137.7666 | 92.7392
[11 empty] | 1999-01-21 | 14:00 | 5527.0003 | 28.726 | 135.595 | 50.865 | 18.361 | 0 | 14.655 | 3.821 |  | 18.476 | 18.476 | 0.79319 | 0 | 13.3227 | 13.4311 | 7.7789 | 67.0901 | 0.20019 | 6.978 | 5.768 | 34.6155 | 318.048 | 301.2264 | 1450.4395 | 1323.7814 | 8.7324 | 88.5085 | 812.5039 | 95.7397 | 135.595 | 116.865 | 18.361 | 9.075 | 9.078 | 18.153 | 18.153 | 0.36321 | 0.49992 | 13.7848 | 13.8969 | 4.2585 | 103.6105 | 0.13413 | 5.768 | 5.768 | 17.2965 | 301.2264 | 571.05 | 585.0625 | -2.4538 | 94.258 | 443.1444 | 96.0969 | 116.865 | 101.122 | 18.361 | 4.44 | 4.638 | 9.078 | 9.078 | 0.36589 | 0.48909 | 13.4886 | 13.5983 | 8.3954 | 82.2371 | 0.16535 | 5.768 | 5.768 | 3.2764 | 571.05 | 985.53 | 1114.5849 | -13.095 | 98.9123 | 842.8174 | 99.6113 | 101.122 | 50.865 | 18.361 | 1.14 | 3.821 | 4.961 | 4.961 | 0.1757 | 0.22979 | 10.1333 | 10.2157 | 10.3772 | 47.2553 | 0.21618 | 5.768 | 6.131 | 82.5171 | 985.53 | 1450.4395 | 1254.945 | 13.4783 | 72.6063 | 1120.2375 | 92.634
[11 empty] | 1999-01-21 | 22:00 | 5535.0003 | 28.815 | 135.729 | 50.722 | 18.369 | 0 | 14.708 | 3.823 |  | 18.531 | 18.531 | 0.7937 | 0 | 13.3709 | 13.4442 | 7.7995 | 67.057 | 0.20049 | 6.88 | 5.761 | 33.2525 | 311.76 | 300.0269 | 1415.6775 | 1326.372 | 6.3083 | 88.9168 | 813.1995 | 95.9109 | 135.729 | 116.895 | 18.369 | 9.128 | 9.088 | 18.216 | 18.216 | 0.36419 | 0.5011 | 13.8653 | 13.9413 | 4.2486 | 103.6944 | 0.13445 | 5.761 | 5.761 | 17.199 | 300.0269 | 554.4 | 584.0996 | -5.3571 | 94.2675 | 442.0632 | 96.1094 | 116.895 | 101.122 | 18.369 | 4.44 | 4.648 | 9.088 | 9.088 | 0.36643 | 0.48856 | 13.4886 | 13.5626 | 8.1438 | 82.4957 | 0.1644 | 5.761 | 5.761 | 3.2614 | 554.4 | 960.7325 | 1080.8749 | -12.5053 | 98.913 | 817.6375 | 99.6011 | 101.122 | 50.722 | 18.369 | 1.14 | 3.823 | 4.963 | 4.963 | 0.17578 | 0.2297 | 10.1333 | 10.1889 | 10.0985 | 47.4545 | 0.21471 | 5.761 | 6.152 | 81.9123 | 960.7325 | 1415.6775 | 1222.7924 | 13.6249 | 72.6983 | 1091.7625 | 92.4972
[11 empty] | 1999-01-22 | 6:00 | 5543 | 28.794 | 135.822 | 50.925 | 18.303 | 0 | 14.532 | 3.823 |  | 18.355 | 18.355 | 0.79172 | 0 | 13.2109 | 13.2916 | 7.7432 | 67.3273 | 0.19742 | 6.961 | 5.755 | 33.182 | 311.76 | 300.133 | 1414.4576 | 1314.8678 | 7.0408 | 88.9442 | 807.5004 | 95.8908 | 135.822 | 116.865 | 18.303 | 9.072 | 9.025 | 18.097 | 18.097 | 0.36176 | 0.5013 | 13.7803 | 13.8644 | 4.2534 | 103.7871 | 0.13359 | 5.755 | 5.755 | 17.0625 | 300.133 | 553.5 | 584.6776 | -5.6328 | 94.315 | 442.4053 | 96.1432 | 116.865 | 100.957 | 18.303 | 4.5 | 4.525 | 9.025 | 9.025 | 0.36146 | 0.49861 | 13.6709 | 13.7544 | 8.2384 | 82.3696 | 0.16698 | 5.755 | 5.755 | 3.2627 | 553.5 | 963.4625 | 1100.6973 | -14.2439 | 98.9129 | 827.0987 | 99.6055 | 100.957 | 50.925 | 18.303 | 0.96 | 3.823 | 4.783 | 4.783 | 0.17218 | 0.20071 | 8.5333 | 8.5855 | 9.922 | 47.716 | 0.17993 | 5.755 | 6.147 | 81.9437 | 963.4625 | 1414.4576 | 1184.8222 | 16.2349 | 72.6975 | 1074.1423 | 92.3712
[11 empty] | 1999-01-22 | 14:00 | 5551.0003 | 28.874 | 135.641 | 50.917 | 18.297 | 0 | 14.715 | 3.822 |  | 18.537 | 18.537 | 0.79382 | 0 | 13.3773 | 13.4272 | 7.7927 | 67.1893 | 0.19984 | 6.51 | 5.772 | 33.37 | 310.416 | 299.7821 | 1419.3365 | 1325.4895 | 6.612 | 88.8686 | 812.6358 | 95.8936 | 135.641 | 116.647 | 18.297 | 9.075 | 9.076 | 18.151 | 18.151 | 0.36316 | 0.49997 | 13.7848 | 13.8362 | 4.2418 | 103.6052 | 0.13355 | 5.772 | 5.772 | 16.9845 | 299.7821 | 555.3 | 582.5485 | -4.907 | 94.3344 | 441.1653 | 96.1501 | 116.647 | 100.8 | 18.297 | 4.5 | 4.576 | 9.076 | 9.076 | 0.36419 | 0.49581 | 13.6709 | 13.7219 | 8.2347 | 82.1918 | 0.16695 | 5.772 | 5.772 | 3.2618 | 555.3 | 957.775 | 1098.1698 | -14.6584 | 98.912 | 826.7349 | 99.6055 | 100.8 | 50.917 | 18.297 | 1.14 | 3.822 | 4.962 | 4.962 | 0.17574 | 0.22975 | 10.1333 | 10.1711 | 10.0647 | 47.4968 | 0.21414 | 5.772 | 6.269 | 81.9258 | 957.775 | 1419.3365 | 1219.0173 | 14.1136 | 72.6716 | 1088.3962 | 92.4728
[11 empty] | 1999-01-22 | 22:00 | 5559.0003 | 28.836 | 135.849 | 51.007 | 18.354 | 0 | 14.713 | 3.763 |  | 18.476 | 18.476 | 0.79633 | 0 | 13.3755 | 13.4405 | 7.8785 | 67.1955 | 0.20002 | 6.943 | 5.763 | 33.2525 | 311.952 | 299.8718 | 1415.6775 | 1342.3301 | 5.1811 | 88.9111 | 821.101 | 95.9503 | 135.849 | 117.112 | 18.354 | 9.073 | 9.192 | 18.265 | 18.265 | 0.36623 | 0.49674 | 13.7818 | 13.8487 | 4.2224 | 103.9041 | 0.13328 | 5.763 | 5.763 | 17.16 | 299.8718 | 554.4 | 578.9237 | -4.4235 | 94.2776 | 439.3978 | 96.0947 | 117.112 | 101.07 | 18.354 | 4.5 | 4.692 | 9.192 | 9.192 | 0.37037 | 0.48956 | 13.6709 | 13.7373 | 8.1543 | 82.5827 | 0.16635 | 5.763 | 5.763 | 3.2631 | 554.4 | 960.505 | 1082.984 | -12.7515 | 98.9118 | 818.692 | 99.6014 | 101.07 | 51.007 | 18.354 | 1.14 | 3.763 | 4.903 | 4.903 | 0.17338 | 0.23251 | 10.1333 | 10.1826 | 10.1163 | 47.5682 | 0.21406 | 5.763 | 6.264 | 81.9504 | 960.505 | 1415.6775 | 1226.6629 | 13.3515 | 72.6715 | 1093.584 | 92.5063
[11 empty] | 1999-01-23 | 6:00 | 5567 | 28.836 | 135.869 | 50.985 | 18.295 | 0 | 14.767 | 3.762 |  | 18.529 | 18.529 | 0.79697 | 0 | 13.4245 | 13.4898 | 7.9036 | 67.2284 | 0.20066 | 6.905 | 5.755 | 33.229 | 311.904 | 300.0024 | 1415.6775 | 1347.1695 | 4.8392 | 88.9238 | 823.586 | 95.9653 | 135.869 | 116.857 | 18.295 | 9.127 | 9.089 | 18.216 | 18.216 | 0.3642 | 0.50104 | 13.8638 | 13.9312 | 4.2488 | 103.8192 | 0.13419 | 5.755 | 5.755 | 17.1405 | 300.0024 | 554.4 | 584.0469 | -5.3476 | 94.2865 | 442.0247 | 96.1223 | 116.857 | 101.07 | 18.295 | 4.5 | 4.589 | 9.089 | 9.089 | 0.36488 | 0.4951 | 13.6709 | 13.7373 | 8.2136 | 82.4549 | 0.1666 | 5.755 | 5.755 | 3.263 | 554.4 | 963.9175 | 1094.8482 | -13.5832 | 98.9124 | 824.6241 | 99.6043 | 101.07 | 50.985 | 18.295 | 1.14 | 3.762 | 4.902 | 4.902 | 0.17334 | 0.23256 | 10.1333 | 10.1826 | 10.156 | 47.5765 | 0.21403 | 5.755 | 6.25 | 81.9482 | 963.9175 | 1415.6775 | 1231.1809 | 13.0324 | 72.6842 | 1097.5492 | 92.5335
[11 empty] | 1999-01-23 | 14:00 | 5575 | 28.921 | 135.675 | 50.887 | 18.37 | 0 | 14.768 | 3.761 |  | 18.529 | 18.529 | 0.79702 | 0 | 13.4255 | 13.4568 | 7.8778 | 67.0332 | 0.20075 | 6.946 | 5.767 | 33.8165 | 310.464 | 299.6597 | 1419.3365 | 1343.5236 | 5.3414 | 88.715 | 821.5916 | 95.884 | 135.675 | 116.932 | 18.37 | 9.128 | 9.025 | 18.153 | 18.153 | 0.36251 | 0.50284 | 13.8653 | 13.8977 | 4.2554 | 103.6781 | 0.13405 | 5.767 | 5.767 | 17.043 | 299.6597 | 555.75 | 585.5018 | -5.3534 | 94.3125 | 442.5807 | 96.1492 | 116.932 | 100.995 | 18.37 | 4.5 | 4.525 | 9.025 | 9.025 | 0.36146 | 0.49861 | 13.6709 | 13.7028 | 8.2721 | 82.3214 | 0.16646 | 5.767 | 5.767 | 3.2619 | 555.75 | 958.0025 | 1105.1857 | -15.3636 | 98.9115 | 830.4679 | 99.6072 | 100.995 | 50.887 | 18.37 | 1.14 | 3.761 | 4.901 | 4.901 | 0.1733 | 0.23261 | 10.1333 | 10.157 | 10.0885 | 47.4825 | 0.21391 | 5.767 | 6.309 | 81.9258 | 958.0025 | 1419.3365 | 1223.5509 | 13.7942 | 72.6604 | 1090.7767 | 92.4892
[11 empty] | 1999-01-23 | 22:00 | 5583 | 28.887 | 135.802 | 51.015 | 18.328 | 0 | 14.714 | 3.823 |  | 18.537 | 18.537 | 0.79376 | 0 | 13.3764 | 13.4211 | 7.7966 | 67.2839 | 0.19947 | 6.93 | 5.766 | 33.2525 | 311.856 | 299.8555 | 1416.2872 | 1325.9598 | 6.3778 | 88.9105 | 812.9077 | 95.9094 | 135.802 | 116.872 | 18.328 | 9.074 | 9.016 | 18.09 | 18.09 | 0.36154 | 0.5016 | 13.7833 | 13.8294 | 4.2498 | 103.7592 | 0.13328 | 5.766 | 5.766 | 17.1405 | 299.8555 | 553.95 | 584.3892 | -5.4949 | 94.2837 | 442.1224 | 96.1231 | 116.872 | 101.13 | 18.328 | 4.5 | 4.516 | 9.016 | 9.016 | 0.36098 | 0.49911 | 13.6709 | 13.7166 | 8.2506 | 82.4224 | 0.16642 | 5.766 | 5.766 | 3.263 | 553.95 | 960.05 | 1102.686 | -14.8571 | 98.9118 | 828.318 | 99.6061 | 101.13 | 51.015 | 18.328 | 1.14 | 3.823 | 4.963 | 4.963 | 0.17578 | 0.2297 | 10.1333 | 10.1672 | 10.0902 | 47.6543 | 0.21335 | 5.766 | 6.288 | 81.9504 | 960.05 | 1416.2872 | 1221.895 | 13.7255 | 72.67 | 1090.9725 | 92.4883
[11 empty] | 1999-01-24 | 6:00 | 5591.0003 | 28.853 | 135.615 | 50.85 | 18.319 | 0 | 14.473 | 3.762 |  | 18.235 | 18.235 | 0.79369 | 0 | 13.1573 | 13.2146 | 7.7998 | 67.1137 | 0.1969 | 6.877 | 5.764 | 33.2055 | 311.808 | 299.9942 | 1415.0678 | 1326.3721 | 6.268 | 88.9313 | 813.1832 | 95.9166 | 135.615 | 116.887 | 18.319 | 9.073 | 8.897 | 17.97 | 17.97 | 0.35836 | 0.5049 | 13.7818 | 13.8418 | 4.2711 | 103.6609 | 0.13353 | 5.764 | 5.764 | 17.121 | 299.9942 | 553.95 | 588.4633 | -6.2304 | 94.2929 | 444.2288 | 96.1459 | 116.887 | 100.965 | 18.319 | 4.5 | 4.397 | 8.897 | 8.897 | 0.35464 | 0.50579 | 13.6709 | 13.7304 | 8.3248 | 82.2822 | 0.16687 | 5.764 | 5.764 | 3.2617 | 553.95 | 963.69 | 1117.5382 | -15.9645 | 98.9128 | 835.7441 | 99.6097 | 100.965 | 50.85 | 18.319 | 0.9 | 3.762 | 4.662 | 4.662 | 0.16854 | 0.19305 | 8 | 8.0348 | 9.8722 | 47.7163 | 0.16839 | 5.764 | 6.274 | 81.9459 | 963.69 | 1415.0678 | 1174.6336 | 16.991 | 72.6842 | 1069.1618 | 92.3355
[11 empty] | 1999-01-24 | 14:00 | 5599 | 28.832 | 135.883 | 50.902 | 18.249 | 0 | 14.712 | 3.763 |  | 18.475 | 18.475 | 0.79632 | 0 | 13.3745 | 13.4411 | 7.8749 | 67.2686 | 0.19981 | 6.89 | 5.779 | 33.605 | 312.576 | 300.1166 | 1413.2378 | 1342.083 | 5.0349 | 88.8027 | 821.0998 | 95.9073 | 135.883 | 117 | 18.249 | 9.072 | 9.021 | 18.093 | 18.093 | 0.36165 | 0.50141 | 13.7803 | 13.8489 | 4.2541 | 103.9384 | 0.13324 | 5.779 | 5.779 | 17.043 | 300.1166 | 557.1 | 584.7906 | -4.9705 | 94.3212 | 442.4536 | 96.1481 | 117 | 101.182 | 18.249 | 4.5 | 4.521 | 9.021 | 9.021 | 0.36125 | 0.49884 | 13.6709 | 13.7389 | 8.2947 | 82.5473 | 0.16644 | 5.779 | 5.779 | 3.2628 | 557.1 | 967.5575 | 1108.3647 | -14.5528 | 98.9128 | 832.7323 | 99.6082 | 101.182 | 50.902 | 18.249 | 1.14 | 3.763 | 4.903 | 4.903 | 0.17338 | 0.23251 | 10.1333 | 10.1838 | 10.1971 | 47.5959 | 0.21396 | 5.779 | 6.21 | 81.9862 | 967.5575 | 1413.2378 | 1235.8411 | 12.5525 | 72.6819 | 1101.6993 | 92.5582
[11 empty] | 1999-01-24 | 22:00 | 5607 | 28.781 | 135.675 | 50.73 | 18.414 | 0 | 14.769 | 3.823 |  | 18.592 | 18.592 | 0.79437 | 0 | 13.4264 | 13.5136 | 7.8274 | 66.9611 | 0.20181 | 7.082 | 5.736 | 31.067 | 299.376 | 298.0685 | 1357.7414 | 1329.5476 | 2.0765 | 89.5772 | 813.8081 | 96.1825 | 135.675 | 116.887 | 18.414 | 9.129 | 9.144 | 18.273 | 18.273 | 0.36569 | 0.49959 | 13.8668 | 13.9569 | 4.2292 | 103.6378 | 0.13467 | 5.736 | 5.736 | 15.9705 | 298.0685 | 532.35 | 579.7037 | -8.8952 | 94.642 | 438.8861 | 96.3611 | 116.887 | 100.882 | 18.414 | 4.5 | 4.644 | 9.144 | 9.144 | 0.36781 | 0.49213 | 13.6709 | 13.7597 | 7.8546 | 82.6159 | 0.16655 | 5.736 | 5.736 | 3.2413 | 532.35 | 918.8725 | 1045.0523 | -13.732 | 98.9126 | 788.7011 | 99.589 | 100.882 | 50.73 | 18.414 | 1.14 | 3.823 | 4.963 | 4.963 | 0.17578 | 0.2297 | 10.1333 | 10.1991 | 9.6322 | 47.7598 | 0.21355 | 5.736 | 5.994 | 80.6355 | 918.8725 | 1357.7414 | 1168.8307 | 13.9136 | 72.9473 | 1043.8516 | 92.2752
[11 empty] | 1999-01-25 | 6:00 | 5615 | 28.777 | 135.621 | 50.715 | 18.309 | 0 | 14.712 | 3.763 |  | 18.475 | 18.475 | 0.79632 | 0 | 13.3745 | 13.463 | 7.9005 | 66.9585 | 0.20106 | 6.992 | 5.74 | 30.456 | 299.328 | 297.8318 | 1354.0824 | 1343.1769 | 0.80538 | 89.7741 | 820.5044 | 96.2881 | 135.621 | 116.835 | 18.309 | 9.072 | 9.09 | 18.162 | 18.162 | 0.36349 | 0.4995 | 13.7803 | 13.8714 | 4.2289 | 103.6901 | 0.13378 | 5.74 | 5.74 | 15.717 | 297.8318 | 526.5 | 579.388 | -10.0452 | 94.7229 | 438.6099 | 96.4166 | 116.835 | 100.987 | 18.309 | 4.5 | 4.59 | 9.09 | 9.09 | 0.36493 | 0.49505 | 13.6709 | 13.7613 | 7.7976 | 82.8044 | 0.16619 | 5.74 | 5.74 | 3.2374 | 526.5 | 920.6925 | 1039.5026 | -12.9044 | 98.913 | 783.0013 | 99.5865 | 100.987 | 50.715 | 18.309 | 1.14 | 3.763 | 4.903 | 4.903 | 0.17338 | 0.23251 | 10.1333 | 10.2003 | 9.6732 | 47.8688 | 0.21309 | 5.74 | 6.054 | 80.6243 | 920.6925 | 1354.0824 | 1175.191 | 13.2113 | 72.9296 | 1047.9417 | 92.3064
[11 empty] | 1999-01-25 | 14:00 | 5623 | 28.734 | 135.749 | 50.662 | 18.342 | 0 | 14.716 | 3.762 |  | 18.478 | 18.478 | 0.79641 | 0 | 13.3782 | 13.4838 | 7.8552 | 67.0083 | 0.20123 | 7.039 | 5.745 | 30.8085 | 290.688 | 296.5589 | 1352.2523 | 1336.1077 | 1.1939 | 89.6113 | 816.3333 | 96.226 | 135.749 | 116.76 | 18.342 | 9.076 | 9.072 | 18.148 | 18.148 | 0.36307 | 0.50011 | 13.7863 | 13.8952 | 4.2112 | 103.7013 | 0.13399 | 5.745 | 5.745 | 15.8535 | 296.5589 | 518.4 | 577.388 | -11.3789 | 94.6542 | 436.9735 | 96.372 | 116.76 | 100.635 | 18.342 | 4.5 | 4.572 | 9.072 | 9.072 | 0.36397 | 0.49603 | 13.6709 | 13.7788 | 7.687 | 82.6685 | 0.16668 | 5.745 | 5.745 | 3.2289 | 518.4 | 897.0325 | 1025.4581 | -14.3167 | 98.9112 | 771.9291 | 99.5817 | 100.635 | 50.662 | 18.342 | 1.14 | 3.762 | 4.902 | 4.902 | 0.17334 | 0.23256 | 10.1333 | 10.2133 | 9.4043 | 47.9022 | 0.21321 | 5.745 | 6.129 | 80.3398 | 897.0325 | 1352.2523 | 1144.5151 | 15.3623 | 72.9093 | 1020.7738 | 92.1295
[11 empty] | 1999-01-25 | 22:00 | 5631.0003 | 28.709 | 135.353 | 50.452 | 18.331 | 0 | 14.711 | 3.822 |  | 18.533 | 18.533 | 0.79377 | 0 | 13.3736 | 13.4892 | 7.7865 | 66.785 | 0.20198 | 7.021 | 5.728 | 30.6675 | 292.176 | 296.9179 | 1348.5933 | 1321.7243 | 1.9924 | 89.6714 | 809.3211 | 96.2107 | 135.353 | 116.377 | 18.331 | 9.071 | 9.083 | 18.154 | 18.154 | 0.36329 | 0.49967 | 13.7787 | 13.8978 | 4.2118 | 103.3222 | 0.13451 | 5.728 | 5.728 | 16.0095 | 296.9179 | 521.1 | 577.4552 | -10.8147 | 94.6081 | 437.1866 | 96.3381 | 116.377 | 100.44 | 18.331 | 4.44 | 4.643 | 9.083 | 9.083 | 0.36616 | 0.48883 | 13.4886 | 13.6051 | 7.6548 | 82.4227 | 0.16507 | 5.728 | 5.728 | 3.23 | 521.1 | 903.4025 | 1016.3278 | -12.5 | 98.9121 | 768.7139 | 99.5798 | 100.44 | 50.452 | 18.331 | 1.2 | 3.822 | 5.022 | 5.022 | 0.17694 | 0.23895 | 10.6667 | 10.7588 | 9.5215 | 47.5935 | 0.22606 | 5.728 | 6.009 | 80.4429 | 903.4025 | 1348.5933 | 1161.7886 | 13.8518 | 72.9074 | 1032.5955 | 92.2096
[11 empty] | 1999-01-26 | 6:00 | 5639 | 28.743 | 135.327 | 50.385 | 18.376 | 0 | 14.712 | 3.823 |  | 18.535 | 18.535 | 0.79374 | 0 | 13.3745 | 13.4765 | 7.78 | 66.7 | 0.20205 | 6.817 | 5.731 | 29.8215 | 287.088 | 295.8816 | 1337.0065 | 1319.7571 | 1.2901 | 89.9211 | 807.8194 | 96.3084 | 135.327 | 116.422 | 18.376 | 9.072 | 9.148 | 18.22 | 18.22 | 0.36504 | 0.49791 | 13.7803 | 13.8853 | 4.1926 | 103.3059 | 0.13441 | 5.731 | 5.731 | 15.6 | 295.8816 | 508.95 | 573.8347 | -12.7487 | 94.7276 | 434.8581 | 96.4126 | 116.422 | 100.53 | 18.376 | 4.5 | 4.648 | 9.148 | 9.148 | 0.36803 | 0.49191 | 13.6709 | 13.7751 | 7.5054 | 82.5946 | 0.16678 | 5.731 | 5.731 | 3.2201 | 508.95 | 882.9275 | 998.5766 | -13.0984 | 98.9117 | 753.7633 | 99.5728 | 100.53 | 50.385 | 18.376 | 1.14 | 3.823 | 4.963 | 4.963 | 0.17578 | 0.2297 | 10.1333 | 10.2106 | 9.2277 | 47.8538 | 0.21337 | 5.731 | 6.032 | 79.8851 | 882.9275 | 1337.0065 | 1122.3908 | 16.052 | 73.001 | 1002.6592 | 92.0327
[11 empty] | 1999-01-26 | 14:00 | 5647 | 28.866 | 135.246 | 50.415 | 18.327 | 0 | 14.716 | 3.703 |  | 18.419 | 18.419 | 0.79896 | 0 | 13.3782 | 13.4313 | 7.9522 | 66.5513 | 0.20182 | 6.46 | 5.745 | 31.208 | 296.448 | 297.432 | 1362.6203 | 1355.4262 | 0.52797 | 89.5075 | 826.4291 | 96.2238 | 135.246 | 116.49 | 18.327 | 9.076 | 9.137 | 18.213 | 18.213 | 0.3648 | 0.49833 | 13.7863 | 13.841 | 4.2093 | 103.3317 | 0.13395 | 5.745 | 5.745 | 16.185 | 297.432 | 526.5 | 576.8014 | -9.5539 | 94.5584 | 437.1167 | 96.2973 | 116.49 | 100.62 | 18.327 | 4.5 | 4.637 | 9.137 | 9.137 | 0.36744 | 0.4925 | 13.6709 | 13.7251 | 7.7717 | 82.4563 | 0.16645 | 5.745 | 5.745 | 3.2354 | 526.5 | 912.9575 | 1034.3048 | -13.2917 | 98.9122 | 780.4024 | 99.5854 | 100.62 | 50.415 | 18.327 | 1.14 | 3.703 | 4.843 | 4.843 | 0.17098 | 0.23539 | 10.1333 | 10.1735 | 9.606 | 47.5845 | 0.2138 | 5.745 | 6.142 | 80.4966 | 912.9575 | 1362.6203 | 1169.2376 | 14.192 | 72.9361 | 1041.0976 | 92.2681
[11 empty] | 1999-01-26 | 14:45 | 5647.7533 | 28.862 | 135.246 | 50.535 | 18.327 | 0 | 14.656 | 3.822 |  | 18.478 | 18.478 | 0.79316 | 0 | 13.3236 | 13.3781 | 7.7704 | 66.7931 | 0.20029 | 7.003 | 5.742 | 31.208 | 296.64 | 297.5626 | 1362.0101 | 1318.9368 | 3.1625 | 89.5121 | 808.2497 | 96.1388 | 135.246 | 116.49 | 18.327 | 9.076 | 9.017 | 18.093 | 18.093 | 0.3616 | 0.50163 | 13.7863 | 13.8427 | 4.2299 | 103.3111 | 0.13399 | 5.742 | 5.742 | 16.185 | 297.5626 | 526.5 | 580.7812 | -10.3098 | 94.5608 | 439.1719 | 96.3147 | 116.49 | 100.62 | 18.327 | 4.5 | 4.517 | 9.017 | 9.017 | 0.36104 | 0.49906 | 13.6709 | 13.7268 | 7.8391 | 82.3889 | 0.16661 | 5.742 | 5.742 | 3.2354 | 526.5 | 912.9575 | 1047.7953 | -14.7693 | 98.9127 | 787.1476 | 99.589 | 100.62 | 50.535 | 18.327 | 1.08 | 3.822 | 4.902 | 4.902 | 0.17454 | 0.22032 | 9.6 | 9.6392 | 9.5008 | 47.7497 | 0.20187 | 5.742 | 6.131 | 80.4966 | 912.9575 | 1362.0101 | 1148.1898 | 15.6989 | 72.948 | 1030.5736 | 92.1891
[11 empty] | 1999-01-26 | 22:00 | 5655.0003 | 28.862 | 135.253 | 50.332 | 18.115 | 0 | 14.454 | 3.763 |  | 18.217 | 18.217 | 0.79343 | 0 | 13.14 | 13.1937 | 7.7842 | 66.8933 | 0.19723 | 7.147 | 5.75 | 31.1375 | 296.544 | 297.6686 | 1370.5481 | 1321.4372 | 3.5833 | 89.5395 | 809.5529 | 96.1537 | 135.253 | 116.482 | 18.115 | 8.892 | 9.199 | 18.091 | 18.091 | 0.364 | 0.49152 | 13.5068 | 13.562 | 4.1767 | 103.5758 | 0.13094 | 5.75 | 5.75 | 16.0875 | 297.6686 | 529.65 | 569.8525 | -7.5904 | 94.5955 | 433.7606 | 96.2912 | 116.482 | 100.597 | 18.115 | 4.266 | 4.933 | 9.199 | 9.199 | 0.37699 | 0.46375 | 12.96 | 13.013 | 7.5403 | 82.8842 | 0.157 | 5.75 | 5.75 | 3.2383 | 529.65 | 915.6875 | 984.8846 | -7.5568 | 98.9121 | 757.2673 | 99.5724 | 100.597 | 50.332 | 18.115 | 1.296 | 3.763 | 5.059 | 5.059 | 0.1765 | 0.25618 | 11.52 | 11.5671 | 9.7875 | 47.562 | 0.2432 | 5.75 | 6.111 | 80.7206 | 915.6875 | 1370.5481 | 1203.2551 | 12.2063 | 72.8824 | 1059.4713 | 92.381
[11 empty] | 1999-01-27 | 6:00 | 5663 | 28.866 | 135.018 | 50.4 | 18.027 | 0 | 14.403 | 3.762 |  | 18.165 | 18.165 | 0.7929 | 0 | 13.0936 | 13.1456 | 7.7674 | 66.9146 | 0.19645 | 6.985 | 5.741 | 31.114 | 296.4 | 297.6442 | 1369.3282 | 1318.0678 | 3.7435 | 89.5466 | 807.856 | 96.1486 | 135.018 | 116.295 | 18.027 | 8.831 | 9.142 | 17.973 | 17.973 | 0.36166 | 0.49135 | 13.4142 | 13.4674 | 4.1766 | 103.4529 | 0.13018 | 5.741 | 5.741 | 16.0095 | 297.6442 | 529.2 | 569.6979 | -7.6527 | 94.6213 | 433.6711 | 96.3084 | 116.295 | 100.282 | 18.027 | 4.28 | 4.862 | 9.142 | 9.142 | 0.37358 | 0.46817 | 13.0025 | 13.0541 | 7.5747 | 82.6868 | 0.15787 | 5.741 | 5.741 | 3.2366 | 529.2 | 911.5925 | 992.2036 | -8.8429 | 98.9126 | 760.7018 | 99.5745 | 100.282 | 50.4 | 18.027 | 1.292 | 3.762 | 5.054 | 5.054 | 0.17638 | 0.25564 | 11.4844 | 11.53 | 9.7364 | 47.5776 | 0.24234 | 5.741 | 6.11 | 80.6378 | 911.5925 | 1369.3282 | 1196.9709 | 12.587 | 72.908 | 1054.2817 | 92.3514
[11 empty] | 1999-01-27 | 14:00 | 5671 | 28.925 | 135.601 | 50.752 | 18.109 | 0 | 14.447 | 3.761 |  | 18.208 | 18.208 | 0.79344 | 0 | 13.1336 | 13.1628 | 7.787 | 67.2805 | 0.19564 | 6.969 | 5.78 | 34.6155 | 318.912 | 301.2346 | 1451.0491 | 1325.3892 | 8.6599 | 88.5088 | 813.3119 | 95.7439 | 135.601 | 116.692 | 18.109 | 8.885 | 9.265 | 18.15 | 18.15 | 0.36567 | 0.48953 | 13.4962 | 13.5262 | 4.2003 | 103.8372 | 0.13026 | 5.78 | 5.78 | 17.3355 | 301.2346 | 571.05 | 573.4896 | -0.42722 | 94.2452 | 437.3621 | 96.0364 | 116.692 | 100.905 | 18.109 | 4.28 | 4.985 | 9.265 | 9.265 | 0.38014 | 0.46195 | 13.0025 | 13.0314 | 8.1151 | 82.5744 | 0.15781 | 5.78 | 5.78 | 3.2765 | 571.05 | 989.3975 | 1058.5266 | -6.987 | 98.9123 | 814.7883 | 99.5979 | 100.905 | 50.752 | 18.109 | 1.282 | 3.761 | 5.043 | 5.043 | 0.17614 | 0.25421 | 11.3956 | 11.4208 | 10.6126 | 47.1069 | 0.24245 | 5.78 | 6.297 | 82.6739 | 989.3975 | 1451.0491 | 1298.4695 | 10.5151 | 72.555 | 1143.9335 | 92.7728
[11 empty] | 1999-01-27 | 22:00 | 5679.0003 | 28.794 | 136.037 | 50.902 | 18.102 | 0 | 14.459 | 3.763 |  | 18.222 | 18.222 | 0.79349 | 0 | 13.1445 | 13.2248 | 7.7835 | 67.584 | 0.19568 | 7.061 | 5.769 | 33.2525 | 310.224 | 299.7005 | 1414.4576 | 1323.5037 | 6.4303 | 88.9048 | 811.6021 | 95.9029 | 136.037 | 117.24 | 18.102 | 8.887 | 9.266 | 18.153 | 18.153 | 0.36572 | 0.48956 | 13.4992 | 13.5817 | 4.1861 | 104.3504 | 0.13015 | 5.769 | 5.769 | 16.77 | 299.7005 | 553.5 | 571.0585 | -3.1723 | 94.4044 | 435.3795 | 96.1482 | 117.24 | 101.175 | 18.102 | 4.28 | 4.986 | 9.266 | 9.266 | 0.38019 | 0.4619 | 13.0025 | 13.0819 | 7.864 | 83.2415 | 0.15716 | 5.769 | 5.769 | 3.2613 | 553.5 | 959.8225 | 1025.8268 | -6.8767 | 98.9118 | 789.6634 | 99.587 | 101.175 | 50.902 | 18.102 | 1.292 | 3.763 | 5.055 | 5.055 | 0.17642 | 0.25559 | 11.4844 | 11.5546 | 10.2854 | 47.6511 | 0.24248 | 5.769 | 6.2 | 81.984 | 959.8225 | 1414.4576 | 1261.2223 | 10.8335 | 72.6447 | 1110.5224 | 92.6175
[11 empty] | 1999-01-28 | 0:00 | 5681 | 28.764 | 136.043 | 50.865 | 18.097 | 0 | 14.471 | 3.762 |  | 18.233 | 18.233 | 0.79367 | 0 | 13.1555 | 13.2475 | 7.7941 | 67.5629 | 0.19608 | 7.036 | 5.766 | 33.229 | 310.992 | 299.8474 | 1414.4576 | 1325.428 | 6.2943 | 88.918 | 812.6377 | 95.911 | 136.043 | 116.992 | 18.097 | 8.887 | 9.266 | 18.153 | 18.153 | 0.36572 | 0.48956 | 13.4992 | 13.5937 | 4.1883 | 104.2322 | 0.13042 | 5.766 | 5.766 | 16.77 | 299.8474 | 553.95 | 571.3462 | -3.1404 | 94.4072 | 435.5968 | 96.1501 | 116.992 | 100.905 | 18.097 | 4.292 | 4.974 | 9.266 | 9.266 | 0.37987 | 0.4632 | 13.039 | 13.1303 | 7.8828 | 82.9687 | 0.15826 | 5.766 | 5.766 | 3.2629 | 553.95 | 963.69 | 1029.1308 | -6.7906 | 98.9118 | 791.5404 | 99.5878 | 100.905 | 50.865 | 18.097 | 1.292 | 3.762 | 5.054 | 5.054 | 0.17638 | 0.25564 | 11.4844 | 11.5648 | 10.3311 | 47.4569 | 0.24369 | 5.766 | 6.174 | 81.9862 | 963.69 | 1414.4576 | 1266.4974 | 10.4606 | 72.6573 | 1115.0937 | 92.6476
[11 empty] | 1999-01-28 | 11:18 | 5692.2961 | 28.789 | 134.402 | NR | 18.325 | 0 | 15.168 | 3.98 |  | 19.148 | 19.148 | 0.79215 | 0 | 13.7891 | 13.8754 | 7.6901 | #VALUE! | #VALUE! | 7.195 | 5.807 | 34.7095 | 309.552 | 299.3822 | 1474.2232 | 1308.0647 | 11.2709 | 88.4063 | 803.7235 | 95.6814 | 134.402 | 114.472 | 18.325 | 9.671 | 9.199 | 18.87 | 18.87 | 0.37439 | 0.51251 | 14.6901 | 14.782 | 4.2965 | 101.8155 | 0.14518 | 5.807 | 5.807 | 17.7645 | 299.3822 | 535.95 | 595.4498 | -11.1017 | 94.0663 | 447.416 | 96.0295 | 114.472 | 95.617 | 18.325 | 4.253 | 4.946 | 9.199 | 9.199 | 0.37734 | 0.46233 | 12.9205 | 13.0013 | 7.6182 | 79.1013 | 0.16436 | 5.807 | 5.807 | 3.1866 | 535.95 | 890.89 | 994.0662 | -11.5813 | 98.9356 | 765.0081 | 99.5835 | 95.617 | 20.107 | 18.325 | 1.244 | 3.98 | 5.224 | 5.224 | 0.18415 | 0.23813 | 11.0578 | 11.127 | 9.2627 | 30.2743 | 0.36754 | 5.807 | 5.517 | 89.815 | 890.89 | 1474.2232 | 1141.2762 | 22.5846 | 69.9999 | 1016.0831 | 91.1607
[11 empty] | 1999-01-28 | 11:18 | 5692.3042 | 28.789 | 134.402 | NR | 19.186 | 0 | 15.233 | 3.98 |  | 19.213 | 19.213 | 0.79285 | 0 | 13.8482 | 13.9348 | 7.7111 | #VALUE! | #VALUE! | 7.195 | 5.807 | 34.733 | 309.552 | 299.3822 | 1474.2232 | 1312.2973 | 10.9838 | 88.3984 | 805.8398 | 95.6898 | 134.402 | 114.472 | 19.186 | 9.671 | 9.199 | 18.87 | 18.87 | 0.37439 | 0.51251 | 14.6901 | 14.782 | 4.2965 | 100.9545 | 0.14642 | 5.807 | 5.807 | 17.7645 | 299.3822 | 535.95 | 595.4498 | -11.1017 | 94.0663 | 447.416 | 96.0295 | 114.472 | 103.275 | 19.186 | 4.266 | 4.933 | 9.199 | 9.199 | 0.37699 | 0.46375 | 12.96 | 13.0411 | 7.631 | 82.0565 | 0.15893 | 5.807 | 5.807 | 3.2079 | 535.95 | 886.1125 | 996.659 | -12.4754 | 98.9285 | 766.3045 | 99.5814 | 103.275 | 20.107 | 19.186 | 1.296 | 3.98 | 5.276 | 5.276 | 0.18519 | 0.24564 | 11.52 | 11.5921 | 9.2119 | 33.2931 | 0.34818 | 5.807 | 5.517 | 93.9075 | 886.1125 | 1474.2232 | 1144.0767 | 22.3946 | 68.6329 | 1015.0946 | 90.7489
[11 empty] | 1999-01-28 | 19:00 | 5700 | 28.777 | 137.249 | 51.615 | 18.933 | 0 | 15.13 | 3.883 |  | 19.013 | 19.013 | 0.79577 | 0 | 13.7545 | 13.8455 | 7.8403 | 67.6587 | 0.20464 | 6.912 | 5.798 | 33.6285 | 310.992 | 299.5618 | 1426.045 | 1335.7632 | 6.3309 | 88.7741 | 817.6625 | 95.8872 | 137.249 | 118.38 | 18.933 | 9.555 | 8.773 | 18.328 | 18.328 | 0.36148 | 0.52133 | 14.5139 | 14.6099 | 4.3625 | 104.519 | 0.13978 | 5.798 | 5.798 | 17.121 | 299.5618 | 551.7 | 607.1785 | -10.0559 | 94.2847 | 453.3701 | 96.2236 | 118.38 | 102.45 | 18.933 | 4.279 | 4.494 | 8.773 | 8.773 | 0.35392 | 0.48775 | 12.9995 | 13.0855 | 8.0954 | 83.3866 | 0.15693 | 5.798 | 5.798 | 3.2597 | 551.7 | 960.05 | 1073.9021 | -11.859 | 98.9119 | 812.8011 | 99.599 | 102.45 | 51.615 | 18.933 | 1.296 | 3.883 | 5.179 | 5.179 | 0.18131 | 0.25024 | 11.52 | 11.5962 | 10.2413 | 47.8582 | 0.2423 | 5.798 | 6.162 | 82.3827 | 960.05 | 1426.045 | 1252.9825 | 12.1358 | 72.4989 | 1106.5162 | 92.5548
[11 empty] | 1999-01-29 | 3:00 | 5708 | 28.717 | 137.678 | 51.75 | 18.868 | 0 | 15.118 | 3.823 |  | 18.941 | 18.941 | 0.79816 | 0 | 13.7436 | 13.8591 | 7.9165 | 67.9295 | 0.20402 | 6.856 | 5.771 | 33.229 | 307.536 | 299.1293 | 1403.4805 | 1350.6282 | 3.7658 | 88.8914 | 824.8787 | 95.9717 | 137.678 | 118.695 | 18.868 | 9.552 | 8.716 | 18.268 | 18.268 | 0.35992 | 0.52288 | 14.5094 | 14.6312 | 4.3708 | 104.9477 | 0.13941 | 5.771 | 5.771 | 16.77 | 299.1293 | 545.85 | 608.5712 | -11.4906 | 94.3937 | 453.8502 | 96.3049 | 118.695 | 102.607 | 18.868 | 4.279 | 4.437 | 8.716 | 8.716 | 0.35087 | 0.49094 | 12.9995 | 13.1087 | 8.0423 | 83.7407 | 0.15654 | 5.771 | 5.771 | 3.2563 | 545.85 | 950.95 | 1069.1221 | -12.4267 | 98.9114 | 807.486 | 99.5967 | 102.607 | 51.75 | 18.868 | 1.287 | 3.823 | 5.11 | 5.11 | 0.17872 | 0.25186 | 11.44 | 11.5361 | 10.1523 | 48.1582 | 0.23955 | 5.771 | 6.098 | 81.984 | 950.95 | 1403.4805 | 1243.4845 | 11.3999 | 72.5925 | 1097.2172 | 92.528
[11 empty] | 1999-01-29 | 11:00 | 5716 | 28.764 | 137.377 | 42.157 | 18.183 | 0 | 14.513 | 3.981 |  | 18.494 | 18.494 | 0.78474 | 0 | 13.1936 | 13.286 | 7.5021 | 64.0819 | 0.20733 | 6.931 | 5.783 | 33.0175 | 305.376 | 298.7866 | 1408.3594 | 1267.6653 | 9.9899 | 88.9495 | 783.2259 | 95.7844 | 137.377 | 117.885 | 18.183 | 8.952 | 9.67 | 18.622 | 18.622 | 0.37736 | 0.48072 | 13.598 | 13.6932 | 4.127 | 105.321 | 0.13001 | 5.783 | 5.783 | 16.6725 | 298.7866 | 540 | 559.9536 | -3.6951 | 94.4199 | 429.3701 | 96.117 | 117.885 | 100.575 | 18.183 | 4.279 | 5.391 | 9.67 | 9.67 | 0.40177 | 0.4425 | 12.9995 | 13.0905 | 7.4981 | 83.5489 | 0.15668 | 5.783 | 5.783 | 3.2227 | 540 | 913.8675 | 966.0564 | -5.7108 | 98.9214 | 753.0282 | 99.572 | 100.575 | 42.157 | 18.183 | 1.282 | 3.981 | 5.263 | 5.263 | 0.18495 | 0.24359 | 11.3956 | 11.4753 | 9.6567 | 43.5263 | 0.26364 | 5.783 | 6.17 | 82.1229 | 913.8675 | 1408.3594 | 1181.7139 | 16.0929 | 72.5145 | 1047.7907 | 92.1623
[11 empty] | 1999-01-29 | 19:00 | 5724.0003 | 28.717 | 133.799 | 49.725 | 17.956 | 0 | 14.268 | 3.822 |  | 18.09 | 18.09 | 0.78872 | 0 | 12.9709 | 13.0799 | 7.6094 | 66.1966 | 0.19759 | 6.83 | 5.753 | 33.699 | 307.68 | 299.1538 | 1433.363 | 1290.1293 | 9.9928 | 88.7352 | 794.6415 | 95.7592 | 133.799 | 115.012 | 17.956 | 8.71 | 9.261 | 17.971 | 17.971 | 0.36323 | 0.48467 | 13.2304 | 13.3415 | 4.1454 | 102.3041 | 0.13041 | 5.753 | 5.753 | 17.199 | 299.1538 | 546.75 | 564.3331 | -3.2159 | 94.2508 | 431.7434 | 96.0164 | 115.012 | 99.337 | 17.956 | 4.266 | 4.995 | 9.261 | 9.261 | 0.3803 | 0.46064 | 12.96 | 13.0689 | 7.7558 | 81.4627 | 0.16043 | 5.753 | 5.753 | 3.255 | 546.75 | 952.77 | 1010.9241 | -6.1037 | 98.9119 | 778.8371 | 99.5821 | 99.337 | 49.725 | 17.956 | 1.292 | 3.822 | 5.114 | 5.114 | 0.17878 | 0.25264 | 11.4844 | 11.5809 | 10.1763 | 46.3987 | 0.2496 | 5.753 | 6.107 | 82.2685 | 952.77 | 1433.363 | 1247.0369 | 12.9992 | 72.4996 | 1099.9034 | 92.5204
[11 empty] | 1999-01-30 | 3:00 | 5732 | 28.726 | 133.672 | 49.935 | 17.8 | 0 | 14.271 | 3.762 |  | 18.033 | 18.033 | 0.79138 | 0 | 12.9736 | 13.0791 | 7.6951 | 66.3084 | 0.19725 | 6.847 | 5.745 | 33.605 | 307.584 | 299.2517 | 1425.4353 | 1306.972 | 8.3107 | 88.7703 | 803.1118 | 95.8157 | 133.672 | 114.765 | 17.8 | 8.708 | 9.322 | 18.03 | 18.03 | 0.36483 | 0.48297 | 13.2273 | 13.3349 | 4.1402 | 102.2783 | 0.13038 | 5.745 | 5.745 | 17.043 | 299.2517 | 549.45 | 562.8725 | -2.4429 | 94.3048 | 431.0621 | 96.0463 | 114.765 | 99.06 | 17.8 | 4.266 | 5.056 | 9.322 | 9.322 | 0.38355 | 0.45763 | 12.96 | 13.0654 | 7.7662 | 81.3463 | 0.16061 | 5.745 | 5.745 | 3.2562 | 549.45 | 947.5375 | 1010.301 | -6.6239 | 98.9119 | 779.8755 | 99.5825 | 99.06 | 49.935 | 17.8 | 1.297 | 3.762 | 5.059 | 5.059 | 0.17648 | 0.25637 | 11.5289 | 11.6226 | 10.1453 | 46.5522 | 0.24967 | 5.745 | 6.072 | 82.1811 | 947.5375 | 1425.4353 | 1245.8807 | 12.5965 | 72.5378 | 1096.7091 | 92.5066
[11 empty] | 1999-01-30 | 11:00 | 5740 | 28.794 | 133.457 | 49.777 | 17.913 | 0 | 14.267 | 3.822 |  | 18.089 | 18.089 | 0.78871 | 0 | 12.97 | 13.0492 | 7.5987 | 66.1053 | 0.1974 | 6.883 | 5.756 | 33.8165 | 305.328 | 298.909 | 1429.704 | 1288.4626 | 9.8791 | 88.6867 | 793.6858 | 95.7393 | 133.457 | 114.78 | 17.913 | 8.709 | 9.381 | 18.09 | 18.09 | 0.36641 | 0.48143 | 13.2289 | 13.3097 | 4.1282 | 102.0773 | 0.13039 | 5.756 | 5.756 | 16.965 | 298.909 | 547.2 | 560.6561 | -2.4591 | 94.3244 | 429.7825 | 96.0527 | 114.78 | 99.397 | 17.913 | 4.266 | 5.115 | 9.381 | 9.381 | 0.3867 | 0.45475 | 12.96 | 13.0392 | 7.7078 | 81.4677 | 0.16005 | 5.756 | 5.756 | 3.2536 | 547.2 | 941.85 | 1000.8609 | -6.2654 | 98.9115 | 774.0304 | 99.5797 | 99.397 | 49.777 | 17.913 | 1.292 | 3.822 | 5.114 | 5.114 | 0.17878 | 0.25264 | 11.4844 | 11.5546 | 10.0513 | 46.6227 | 0.24783 | 5.756 | 6.17 | 82.0445 | 941.85 | 1429.704 | 1232.5012 | 13.7933 | 72.552 | 1087.1756 | 92.4534
[11 empty] | 1999-01-30 | 19:00 | 5748 | 28.76 | 133.638 | 49.89 | 17.794 | 0 | 14.256 | 3.763 |  | 18.019 | 18.019 | 0.79116 | 0 | 12.96 | 13.0523 | 7.6831 | 66.2869 | 0.19691 | 6.896 | 5.75 | 33.6755 | 307.632 | 299.1374 | 1426.045 | 1304.8311 | 8.5 | 88.7425 | 801.9843 | 95.801 | 133.638 | 114.72 | 17.794 | 8.713 | 9.381 | 18.094 | 18.094 | 0.36647 | 0.48154 | 13.2349 | 13.3292 | 4.1347 | 102.2503 | 0.13036 | 5.75 | 5.75 | 16.7895 | 299.1374 | 545.85 | 561.38 | -2.8451 | 94.3874 | 430.2587 | 96.0978 | 114.72 | 99.18 | 17.794 | 4.266 | 5.115 | 9.381 | 9.381 | 0.3867 | 0.45475 | 12.96 | 13.0523 | 7.6886 | 81.4674 | 0.16021 | 5.75 | 5.75 | 3.2548 | 545.85 | 948.22 | 998.384 | -5.2903 | 98.9119 | 772.117 | 99.5785 | 99.18 | 49.89 | 17.794 | 1.277 | 3.763 | 5.04 | 5.04 | 0.17612 | 0.25337 | 11.3511 | 11.4319 | 10.1312 | 46.6098 | 0.24527 | 5.75 | 6.124 | 82.0669 | 948.22 | 1426.045 | 1242.155 | 12.8951 | 72.5655 | 1095.1875 | 92.5066
[11 empty] | 1999-01-31 | 3:00 | 5756 | 28.721 | 133.899 | 49.882 | 17.829 | 0 | 14.269 | 3.823 |  | 18.092 | 18.092 | 0.78869 | 0 | 12.9718 | 13.0792 | 7.6135 | 66.448 | 0.19683 | 6.869 | 5.736 | 33.6285 | 307.584 | 299.2598 | 1425.4353 | 1290.7047 | 9.4519 | 88.7628 | 794.9823 | 95.7699 | 133.899 | 115.005 | 17.829 | 8.711 | 9.379 | 18.09 | 18.09 | 0.36639 | 0.48154 | 13.2319 | 13.3415 | 4.1367 | 102.4863 | 0.13018 | 5.736 | 5.736 | 16.77 | 299.2598 | 545.85 | 561.6299 | -2.8909 | 94.3962 | 430.4449 | 96.104 | 115.005 | 99.27 | 17.829 | 4.266 | 5.113 | 9.379 | 9.379 | 0.38659 | 0.45485 | 12.96 | 13.0673 | 7.6895 | 81.619 | 0.1601 | 5.736 | 5.736 | 3.2547 | 545.85 | 948.9025 | 998.5611 | -5.2333 | 98.9124 | 772.2055 | 99.5785 | 99.27 | 49.882 | 17.829 | 1.292 | 3.823 | 5.115 | 5.115 | 0.17882 | 0.25259 | 11.4844 | 11.5795 | 10.1336 | 46.6134 | 0.24842 | 5.736 | 6.06 | 82.0243 | 948.9025 | 1425.4353 | 1241.8679 | 12.878 | 72.5909 | 1095.3852 | 92.5118
[11 empty] | 1999-01-31 | 11:00 | 5764.0003 | 28.781 | 133.678 | 49.807 | 17.776 | 0 | 14.272 | 3.703 |  | 17.975 | 17.975 | 0.79399 | 0 | 12.9745 | 13.0588 | 7.7719 | 66.1946 | 0.19728 | 6.86 | 5.751 | 33.417 | 305.664 | 298.9334 | 1430.3137 | 1322.2795 | 7.5532 | 88.8213 | 810.6065 | 95.8775 | 133.678 | 114.69 | 17.776 | 8.714 | 9.313 | 18.027 | 18.027 | 0.36467 | 0.48339 | 13.2365 | 13.3224 | 4.138 | 102.27 | 0.13027 | 5.751 | 5.751 | 17.0235 | 298.9334 | 547.65 | 562.7113 | -2.7502 | 94.3053 | 430.8224 | 96.0486 | 114.69 | 99.067 | 17.776 | 4.266 | 5.047 | 9.313 | 9.313 | 0.38307 | 0.45807 | 12.96 | 13.0442 | 7.7447 | 81.3578 | 0.16033 | 5.751 | 5.751 | 3.2538 | 547.65 | 942.305 | 1007.8034 | -6.9509 | 98.9115 | 777.7267 | 99.5816 | 99.067 | 49.807 | 17.776 | 1.292 | 3.703 | 4.995 | 4.995 | 0.17402 | 0.25866 | 11.4844 | 11.559 | 10.1047 | 46.5563 | 0.24828 | 5.751 | 6.146 | 81.928 | 942.305 | 1430.3137 | 1242.4959 | 13.1312 | 72.5932 | 1092.4005 | 92.5002
[11 empty] | 1999-01-31 | 19:00 | 5772.0003 | 28.828 | 133.705 | 49.71 | 17.863 | 0 | 14.261 | 3.762 |  | 18.023 | 18.023 | 0.79127 | 0 | 12.9645 | 13.0306 | 7.6935 | 66.151 | 0.19698 | 6.604 | 5.739 | 32.853 | 304.32 | 298.5662 | 1405.31 | 1305.8327 | 7.0787 | 88.9964 | 802.1995 | 95.9046 | 133.705 | 114.795 | 17.863 | 8.712 | 9.382 | 18.094 | 18.094 | 0.36648 | 0.48149 | 13.2334 | 13.3009 | 4.1255 | 102.2615 | 0.13007 | 5.739 | 5.739 | 16.8285 | 298.5662 | 538.65 | 560.1841 | -3.9978 | 94.3636 | 429.3752 | 96.0807 | 114.795 | 98.985 | 17.863 | 4.267 | 5.115 | 9.382 | 9.382 | 0.38673 | 0.45481 | 12.963 | 13.0291 | 7.5872 | 81.4398 | 0.15998 | 5.739 | 5.739 | 3.2467 | 538.65 | 932.295 | 985.2905 | -5.6844 | 98.9126 | 761.9702 | 99.5739 | 98.985 | 49.71 | 17.863 | 1.282 | 3.762 | 5.044 | 5.044 | 0.17618 | 0.25416 | 11.3956 | 11.4536 | 9.9569 | 46.5276 | 0.24617 | 5.739 | 6.112 | 81.5562 | 932.295 | 1405.31 | 1222.2065 | 13.0294 | 72.6841 | 1077.2508 | 92.4292
[11 empty] | 1999-02-01 | 3:00 | 5780 | 28.904 | 133.504 | 49.8 | 17.895 | 0 | 14.329 | 3.763 |  | 18.092 | 18.092 | 0.79201 | 0 | 13.0264 | 13.0634 | 7.7179 | 66.0391 | 0.19781 | 6.842 | 5.738 | 32.712 | 304.272 | 298.4846 | 1401.0408 | 1310.5113 | 6.4616 | 89.0406 | 804.4979 | 95.9339 | 133.504 | 114.832 | 17.895 | 8.771 | 9.388 | 18.159 | 18.159 | 0.36743 | 0.48301 | 13.323 | 13.3609 | 4.1354 | 102.1376 | 0.13081 | 5.738 | 5.738 | 16.614 | 298.4846 | 536.4 | 561.8301 | -4.7409 | 94.4339 | 430.1574 | 96.1377 | 114.832 | 99.112 | 17.895 | 4.266 | 5.122 | 9.388 | 9.388 | 0.38707 | 0.45441 | 12.96 | 12.9968 | 7.5518 | 81.5252 | 0.15942 | 5.738 | 5.738 | 3.2478 | 536.4 | 938.4375 | 980.4506 | -4.4769 | 98.9119 | 758.4253 | 99.5718 | 99.112 | 49.8 | 17.895 | 1.292 | 3.763 | 5.055 | 5.055 | 0.17642 | 0.25559 | 11.4844 | 11.5171 | 10.0396 | 46.5214 | 0.24757 | 5.738 | 6.081 | 81.5786 | 938.4375 | 1401.0408 | 1232.6341 | 12.0201 | 72.6691 | 1085.5358 | 92.4849
[11 empty] | 1999-02-01 | 16:00 | 5793 | 28.768 | 133.725 | 49.875 | 17.85 | 0 | 14.26 | 3.823 |  | 18.083 | 18.083 | 0.78859 | 0 | 12.9636 | 13.0528 | 7.5973 | 66.3527 | 0.19672 | 6.886 | 5.768 | 33.2055 | 303.264 | 298.3786 | 1414.4576 | 1287.4886 | 8.9765 | 88.8714 | 792.9336 | 95.8123 | 133.725 | 114.975 | 17.85 | 8.707 | 9.449 | 18.156 | 18.156 | 0.3682 | 0.47957 | 13.2258 | 13.3168 | 4.1141 | 102.3859 | 0.13007 | 5.768 | 5.768 | 16.731 | 298.3786 | 537.3 | 557.9092 | -3.8357 | 94.3927 | 428.1439 | 96.0922 | 114.975 | 99.277 | 17.85 | 4.266 | 5.183 | 9.449 | 9.449 | 0.39033 | 0.45148 | 12.96 | 13.0492 | 7.5383 | 81.7377 | 0.15965 | 5.768 | 5.768 | 3.2482 | 537.3 | 935.7075 | 976.865 | -4.3985 | 98.9114 | 757.0825 | 99.571 | 99.277 | 49.875 | 17.85 | 1.287 | 3.823 | 5.11 | 5.11 | 0.17872 | 0.25186 | 11.44 | 11.5187 | 9.9738 | 46.7522 | 0.24638 | 5.768 | 6.161 | 82.0243 | 935.7075 | 1414.4576 | 1223.0971 | 13.5289 | 72.51 | 1079.4023 | 92.4009
[11 empty] | 1999-02-02 | 0:00 | 5801 | 28.747 | 133.444 | 49.747 | 17.884 | 0 | 14.27 | 3.762 |  | 18.032 | 18.032 | 0.79137 | 0 | 12.9727 | 13.0701 | 7.6855 | 66.026 | 0.19795 | 6.922 | 5.75 | 33.2055 | 303.264 | 298.5336 | 1413.848 | 1304.9749 | 7.7005 | 88.8771 | 801.7542 | 95.8584 | 133.444 | 114.81 | 17.884 | 8.708 | 9.262 | 17.97 | 17.97 | 0.36323 | 0.48459 | 13.2273 | 13.3266 | 4.1428 | 102.1002 | 0.13052 | 5.75 | 5.75 | 16.731 | 298.5336 | 541.35 | 563.4804 | -4.088 | 94.3956 | 431.007 | 96.1182 | 114.81 | 99.067 | 17.884 | 4.266 | 4.996 | 9.262 | 9.262 | 0.38035 | 0.46059 | 12.96 | 13.0573 | 7.6784 | 81.3761 | 0.16046 | 5.75 | 5.75 | 3.2482 | 541.35 | 935.48 | 1000.8261 | -6.9853 | 98.912 | 771.088 | 99.5788 | 99.067 | 49.747 | 17.884 | 1.296 | 3.762 | 5.058 | 5.058 | 0.17646 | 0.25623 | 11.52 | 11.6065 | 10.0065 | 46.5165 | 0.24951 | 5.75 | 6.085 | 81.8653 | 935.48 | 1413.848 | 1229.5482 | 13.0353 | 72.5775 | 1082.5141 | 92.4375
[11 empty] | 1999-02-02 | 10:26 | 5811.4314 | 28.777 | 136.171 | 56.677 | 19.05 | 0 | 15.126 | 3.404 |  | 18.53 | 18.53 | 0.8163 | 0 | 13.7509 | 13.8418 | 8.529 | 68.845 | 0.20106 | 6.88 | 5.769 | 33.699 | 302.64 | 298.4275 | 1427.2648 | 1474.7741 | -3.3287 | 88.7078 | 886.6008 | 96.1991 | 136.171 | 117.502 | 19.05 | 9.555 | 8.413 | 17.968 | 17.968 | 0.35187 | 0.53178 | 14.5139 | 14.6099 | 4.4148 | 103.3717 | 0.14133 | 5.769 | 5.769 | 16.848 | 298.4275 | 542.25 | 618.2293 | -14.0119 | 94.3544 | 458.3284 | 96.324 | 117.502 | 102.412 | 19.05 | 4.279 | 4.134 | 8.413 | 8.413 | 0.33471 | 0.50862 | 12.9995 | 13.0855 | 8.1792 | 82.7278 | 0.15817 | 5.769 | 5.769 | 3.2745 | 542.25 | 956.41 | 1100.1301 | -15.027 | 98.9028 | 821.19 | 99.6013 | 102.412 | 56.677 | 19.05 | 1.292 | 3.404 | 4.696 | 4.696 | 0.16206 | 0.27513 | 11.4844 | 11.5604 | 10.4018 | 50.0927 | 0.23078 | 5.769 | 6.339 | 82.1475 | 956.41 | 1427.2648 | 1288.2394 | 9.7407 | 72.4732 | 1122.3247 | 92.6806
[11 empty] | 1999-02-02 | 18:00 | 5819 | 28.874 | 135.367 | 52.117 | 18.912 | 0 | 15.064 | 3.762 |  | 18.826 | 18.826 | 0.80017 | 0 | 13.6945 | 13.7456 | 7.945 | 66.885 | 0.20551 | 6.898 | 5.747 | 31.1375 | 288.096 | 295.7837 | 1360.7903 | 1355.494 | 0.38921 | 89.4729 | 825.6388 | 96.2287 | 135.367 | 116.445 | 18.912 | 9.488 | 8.543 | 18.031 | 18.031 | 0.35445 | 0.5262 | 14.4122 | 14.4659 | 4.3507 | 102.6433 | 0.14093 | 5.747 | 5.747 | 16.0485 | 295.7837 | 509.85 | 606.4623 | -18.9492 | 94.5742 | 451.123 | 96.4425 | 116.445 | 100.725 | 18.912 | 4.28 | 4.263 | 8.543 | 8.543 | 0.34162 | 0.50099 | 13.0025 | 13.051 | 7.6094 | 82.0636 | 0.15904 | 5.747 | 5.747 | 3.227 | 509.85 | 887.9325 | 1018.4933 | -14.7039 | 98.909 | 764.1717 | 99.5777 | 100.725 | 52.117 | 18.912 | 1.296 | 3.762 | 5.058 | 5.058 | 0.17646 | 0.25623 | 11.52 | 11.563 | 9.4644 | 48.0446 | 0.24067 | 5.747 | 6.198 | 80.5616 | 887.9325 | 1360.7903 | 1166.0698 | 14.3094 | 72.7633 | 1027.0012 | 92.1556
[11 empty] | 1999-02-03 | 2:00 | 5827 | 28.849 | 135.675 | 52.23 | 18.969 | 0 | 15.115 | 3.703 |  | 18.818 | 18.818 | 0.80322 | 0 | 13.7409 | 13.8024 | 8.0699 | 66.9136 | 0.20627 | 6.881 | 5.736 | 30.6675 | 288.816 | 296.0448 | 1348.5933 | 1379.2686 | -2.2746 | 89.6409 | 837.6567 | 96.3389 | 135.675 | 116.985 | 18.969 | 9.553 | 8.664 | 18.217 | 18.217 | 0.35854 | 0.5244 | 14.5109 | 14.5758 | 4.3439 | 103.0171 | 0.14149 | 5.736 | 5.736 | 16.029 | 296.0448 | 513 | 604.7926 | -17.8933 | 94.5856 | 450.4187 | 96.4413 | 116.985 | 101.085 | 18.969 | 4.266 | 4.398 | 8.664 | 8.664 | 0.34845 | 0.49238 | 12.96 | 13.018 | 7.5701 | 82.4959 | 0.1578 | 5.736 | 5.736 | 3.2284 | 513 | 891.5725 | 1007.4715 | -12.9994 | 98.9095 | 760.2358 | 99.5753 | 101.085 | 52.23 | 18.969 | 1.296 | 3.703 | 4.999 | 4.999 | 0.1741 | 0.25925 | 11.52 | 11.5715 | 9.5303 | 48.1582 | 0.24028 | 5.736 | 6.033 | 80.481 | 891.5725 | 1348.5933 | 1175.4436 | 12.8393 | 72.8146 | 1033.508 | 92.2128
[11 empty] | 1999-02-03 | 18:00 | 5843 | 28.981 | 136.62 | 49.477 | 18.447 | 0 | 14.667 | 3.584 |  | 18.251 | 18.251 | 0.80363 | 0 | 13.3336 | 13.3411 | 8.0632 | 66.5383 | 0.2005 | 7.09 | 5.748 | 30.409 | 283.968 | 295.1064 | 1363.23 | 1378.3421 | -1.1086 | 89.6956 | 836.7243 | 96.3657 | 136.62 | 117.585 | 18.447 | 9.074 | 9.316 | 18.39 | 18.39 | 0.36955 | 0.49342 | 13.7833 | 13.791 | 4.1522 | 104.5033 | 0.13197 | 5.748 | 5.748 | 15.873 | 295.1064 | 510.75 | 567.0862 | -11.0301 | 94.6213 | 431.0963 | 96.318 | 117.585 | 102.232 | 18.447 | 4.306 | 5.01 | 9.316 | 9.316 | 0.38217 | 0.46222 | 13.0815 | 13.0889 | 7.2562 | 84.2053 | 0.15544 | 5.748 | 5.748 | 3.2305 | 510.75 | 904.7675 | 946.9534 | -4.6626 | 98.9053 | 728.8517 | 99.5568 | 102.232 | 49.477 | 18.447 | 1.287 | 3.584 | 4.871 | 4.871 | 0.16916 | 0.26422 | 11.44 | 11.4464 | 9.7124 | 47.6951 | 0.23999 | 5.748 | 6.265 | 81.3635 | 904.7675 | 1363.23 | 1200.4486 | 11.9409 | 72.4291 | 1052.608 | 92.2703
[11 empty] | 1999-02-04 | 2:00 | 5851.0003 | 28.947 | 136.419 | 49.672 | 18.364 | 0 | 14.649 | 3.643 |  | 18.292 | 18.292 | 0.80084 | 0 | 13.3173 | 13.3382 | 7.9749 | 66.7066 | 0.19995 | 6.934 | 5.734 | 30.2915 | 284.592 | 295.188 | 1360.1806 | 1360.373 | -0.014141 | 89.7382 | 827.7805 | 96.3406 | 136.419 | 117.72 | 18.364 | 9.071 | 9.146 | 18.217 | 18.217 | 0.36497 | 0.49794 | 13.7787 | 13.8003 | 4.1812 | 104.5243 | 0.13203 | 5.734 | 5.734 | 15.678 | 295.188 | 509.4 | 572.4059 | -12.3687 | 94.6888 | 433.797 | 96.3859 | 117.72 | 102.27 | 18.364 | 4.306 | 4.84 | 9.146 | 9.146 | 0.3731 | 0.47081 | 13.0815 | 13.102 | 7.3133 | 84.3177 | 0.15539 | 5.734 | 5.734 | 3.2304 | 509.4 | 903.8575 | 959.7236 | -6.1809 | 98.9056 | 734.5618 | 99.5602 | 102.27 | 49.672 | 18.364 | 1.272 | 3.643 | 4.915 | 4.915 | 0.17122 | 0.2588 | 11.3067 | 11.3244 | 9.6624 | 47.9446 | 0.2362 | 5.734 | 6.149 | 81.2358 | 903.8575 | 1360.1806 | 1191.0864 | 12.4318 | 72.48 | 1047.4719 | 92.2446
[11 empty] | 1999-02-04 | 10:00 | 5859 | 29.053 | 132.801 | 58.057 | 18.255 | 0 | 14.42 | 3.164 |  | 17.584 | 17.584 | 0.82006 | 0 | 13.1091 | 13.0886 | 8.6533 | 68.5207 | 0.19102 | 6.888 | 5.741 | 30.973 | 282.576 | 294.8942 | 1377.2565 | 1497.7211 | -8.7467 | 89.4969 | 896.3077 | 96.5444 | 132.801 | 114.292 | 18.255 | 8.835 | 9.013 | 17.848 | 17.848 | 0.35828 | 0.49501 | 13.4203 | 13.3992 | 4.1496 | 101.1419 | 0.13248 | 5.741 | 5.741 | 16.419 | 294.8942 | 508.5 | 567.8698 | -11.6755 | 94.4322 | 431.382 | 96.1939 | 114.292 | 99.682 | 18.255 | 4.279 | 4.734 | 9.013 | 9.013 | 0.36672 | 0.47476 | 12.9995 | 12.9791 | 7.3359 | 81.3961 | 0.15946 | 5.741 | 5.741 | 3.2539 | 508.5 | 898.8525 | 965.1852 | -7.3797 | 98.8966 | 736.8426 | 99.5584 | 99.682 | 58.057 | 18.255 | 1.306 | 3.164 | 4.47 | 4.47 | 0.15274 | 0.29217 | 11.6089 | 11.5907 | 9.8742 | 50.7403 | 0.22843 | 5.741 | 6.301 | 80.3555 | 898.8525 | 1377.2565 | 1236.7024 | 10.2054 | 72.7511 | 1067.7774 | 92.4745
[11 empty] | 1999-02-04 | 18:00 | 5867 | 28.862 | 133.859 | 58.957 | 18.154 | 0 | 14.407 | 3.165 |  | 17.572 | 17.572 | 0.81988 | 0 | 13.0973 | 13.1508 | 8.6785 | 69.5755 | 0.18901 | 6.945 | 5.746 | 34.9915 | 312.048 | 299.9045 | 1471.1744 | 1505.7817 | -2.3524 | 88.3325 | 902.8431 | 96.1243 | 133.859 | 115.537 | 18.154 | 8.835 | 8.959 | 17.794 | 17.794 | 0.35684 | 0.49652 | 13.4203 | 13.4751 | 4.2146 | 102.3294 | 0.13168 | 5.746 | 5.746 | 17.628 | 299.9045 | 562.95 | 578.274 | -2.7221 | 94.1221 | 439.0892 | 95.9853 | 115.537 | 100.935 | 18.154 | 4.266 | 4.693 | 8.959 | 8.959 | 0.36419 | 0.47617 | 12.96 | 13.013 | 8.14 | 81.942 | 0.15881 | 5.746 | 5.746 | 3.3089 | 562.95 | 1004.8675 | 1071.6713 | -6.648 | 98.8967 | 817.3106 | 99.5952 | 100.935 | 58.957 | 18.154 | 1.306 | 3.165 | 4.471 | 4.471 | 0.15278 | 0.2921 | 11.6089 | 11.6563 | 11.1242 | 50.6678 | 0.23005 | 5.746 | 6.304 | 82.7098 | 1004.8675 | 1471.1744 | 1385.385 | 5.8314 | 72.4213 | 1195.1263 | 93.0794
[11 empty] | 1999-02-05 | 2:00 | 5875 | 28.925 | 133.497 | 58.56 | 18.184 | 0 | 14.399 | 3.165 |  | 17.564 | 17.564 | 0.8198 | 0 | 13.09 | 13.1191 | 8.6822 | 69.1623 | 0.18969 | 7.003 | 5.728 | 31.9365 | 295.536 | 297.0648 | 1402.2607 | 1503.252 | -7.202 | 89.2493 | 900.1584 | 96.4521 | 133.497 | 115.162 | 18.184 | 8.832 | 9.024 | 17.856 | 17.856 | 0.35853 | 0.49462 | 13.4157 | 13.4455 | 4.1761 | 101.9694 | 0.13186 | 5.728 | 5.728 | 16.6725 | 297.0648 | 529.2 | 571.4913 | -7.9916 | 94.3876 | 434.2781 | 96.1609 | 115.162 | 100.372 | 18.184 | 4.266 | 4.758 | 9.024 | 9.024 | 0.36765 | 0.47274 | 12.96 | 12.9888 | 7.6169 | 81.9661 | 0.15847 | 5.728 | 5.728 | 3.2758 | 529.2 | 944.8075 | 1000.7412 | -5.9201 | 98.8973 | 764.9706 | 99.5718 | 100.372 | 58.56 | 18.184 | 1.301 | 3.165 | 4.466 | 4.466 | 0.15268 | 0.29131 | 11.5644 | 11.5901 | 10.4125 | 50.8695 | 0.22784 | 5.728 | 6.185 | 81.0768 | 944.8075 | 1402.2607 | 1299.8513 | 7.3032 | 72.7074 | 1122.3294 | 92.776
[11 empty] | 1999-02-05 | 3:09 | 5876.1486 | 28.921 | 133.41 | 58.567 | 18.148 | 0 | 14.414 | 3.165 |  | 17.579 | 17.579 | 0.81996 | 0 | 13.1036 | 13.1343 | 8.6898 | 69.1507 | 0.18994 | 6.992 | 5.732 | 31.8895 | 295.536 | 297.0566 | 1402.2607 | 1504.6772 | -7.3037 | 89.2648 | 900.8669 | 96.4601 | 133.41 | 115.05 | 18.148 | 8.833 | 9.084 | 17.917 | 17.917 | 0.36014 | 0.493 | 13.4172 | 13.4486 | 4.1676 | 101.9144 | 0.13196 | 5.732 | 5.732 | 16.6335 | 297.0566 | 528.75 | 569.7314 | -7.7506 | 94.4006 | 433.394 | 96.162 | 115.05 | 100.417 | 18.148 | 4.28 | 4.804 | 9.084 | 9.084 | 0.37048 | 0.47116 | 13.0025 | 13.0329 | 7.5955 | 81.99 | 0.15896 | 5.732 | 5.732 | 3.2773 | 528.75 | 947.0825 | 996.9063 | -5.2608 | 98.8967 | 762.8282 | 99.5704 | 100.417 | 58.567 | 18.148 | 1.301 | 3.165 | 4.466 | 4.466 | 0.15268 | 0.29131 | 11.5644 | 11.5915 | 10.4399 | 50.9041 | 0.22771 | 5.732 | 6.196 | 81.079 | 947.0825 | 1402.2607 | 1303.0605 | 7.0743 | 72.7059 | 1125.0715 | 92.7934
[11 empty] | 1999-02-05 | 11:00 | 5884 | 29.044 | 133.437 | 58.462 | 18.214 | 0 | 14.425 | 3.164 |  | 17.589 | 17.589 | 0.82011 | 0 | 13.1136 | 13.0966 | 8.6598 | 69.0757 | 0.1896 | 6.916 | 5.75 | 32.618 | 293.76 | 296.6731 | 1410.7986 | 1500.5275 | -6.3601 | 89.0054 | 898.6003 | 96.3701 | 133.437 | 115.102 | 18.214 | 8.839 | 9.125 | 17.964 | 17.964 | 0.36132 | 0.49204 | 13.4263 | 13.4089 | 4.155 | 101.9005 | 0.13159 | 5.75 | 5.75 | 16.7505 | 296.6731 | 528.75 | 567.8223 | -7.3896 | 94.3539 | 432.2477 | 96.1248 | 115.102 | 100.155 | 18.214 | 4.28 | 4.845 | 9.125 | 9.125 | 0.37267 | 0.46904 | 13.0025 | 12.9856 | 7.5758 | 81.8387 | 0.15867 | 5.75 | 5.75 | 3.2705 | 528.75 | 935.7075 | 992.9507 | -6.1176 | 98.8976 | 760.8503 | 99.5702 | 100.155 | 58.462 | 18.214 | 1.306 | 3.164 | 4.47 | 4.47 | 0.15274 | 0.29217 | 11.6089 | 11.5938 | 10.3115 | 50.783 | 0.2283 | 5.75 | 6.292 | 80.9603 | 935.7075 | 1410.7986 | 1288.5203 | 8.6673 | 72.7106 | 1112.1139 | 92.7201
[11 empty] | 1999-02-05 | 19:00 | 5892 | 28.955 | 133.377 | 58.62 | 18.177 | 0 | 14.353 | 3.165 |  | 17.518 | 17.518 | 0.81933 | 0 | 13.0482 | 13.0655 | 8.658 | 69.1635 | 0.18891 | 6.875 | 5.729 | 31.9835 | 294.864 | 296.9587 | 1403.4805 | 1498.5983 | -6.7773 | 89.2296 | 897.7785 | 96.4375 | 133.377 | 115.102 | 18.177 | 8.773 | 9.086 | 17.859 | 17.859 | 0.3594 | 0.49124 | 13.3261 | 13.3438 | 4.1595 | 101.903 | 0.13095 | 5.729 | 5.729 | 16.4385 | 296.9587 | 529.65 | 567.8154 | -7.2058 | 94.4644 | 432.3871 | 96.1982 | 115.102 | 100.47 | 18.177 | 4.279 | 4.807 | 9.086 | 9.086 | 0.37061 | 0.47094 | 12.9995 | 13.0168 | 7.6066 | 82.0024 | 0.15874 | 5.729 | 5.729 | 3.2711 | 529.65 | 943.8975 | 998.2116 | -5.7542 | 98.8985 | 763.9308 | 99.5718 | 100.47 | 58.62 | 18.177 | 1.301 | 3.165 | 4.466 | 4.466 | 0.15268 | 0.29131 | 11.5644 | 11.5798 | 10.4024 | 50.9656 | 0.22721 | 5.729 | 6.226 | 81.0029 | 943.8975 | 1403.4805 | 1298.5976 | 7.4731 | 72.7225 | 1121.2476 | 92.7756
[11 empty] | 1999-02-06 | 3:00 | 5900.0003 | 28.934 | 133.618 | 58.59 | 18.126 | 0 | 14.42 | 3.165 |  | 17.585 | 17.585 | 0.82002 | 0 | 13.1091 | 13.1347 | 8.6915 | 69.2865 | 0.18957 | 6.799 | 5.712 | 31.9365 | 295.68 | 297.0811 | 1402.8703 | 1505.1018 | -7.2873 | 89.2499 | 901.0915 | 96.4558 | 133.618 | 115.2 | 18.126 | 8.834 | 9.137 | 17.971 | 17.971 | 0.36157 | 0.49157 | 13.4187 | 13.4449 | 4.164 | 102.119 | 0.13166 | 5.712 | 5.712 | 16.38 | 297.0811 | 529.2 | 568.4737 | -7.4213 | 94.4864 | 432.7774 | 96.2151 | 115.2 | 100.552 | 18.126 | 4.28 | 4.857 | 9.137 | 9.137 | 0.37331 | 0.46843 | 13.0025 | 13.0279 | 7.5766 | 82.1734 | 0.15854 | 5.712 | 5.712 | 3.2693 | 529.2 | 947.5375 | 992.6514 | -4.7612 | 98.8995 | 760.9257 | 99.5704 | 100.552 | 58.59 | 18.126 | 1.306 | 3.165 | 4.471 | 4.471 | 0.15278 | 0.2921 | 11.6089 | 11.6316 | 10.4537 | 50.9913 | 0.22811 | 5.712 | 6.135 | 80.9581 | 947.5375 | 1402.8703 | 1305.1213 | 6.9678 | 72.7488 | 1126.3294 | 92.8122
[11 empty] | 1999-02-06 | 11:00 | 5908 | 29.006 | 133.518 | 58.417 | 18.151 | 0 | 14.358 | 3.164 |  | 17.522 | 17.522 | 0.81943 | 0 | 13.0527 | 13.0504 | 8.6476 | 69.1689 | 0.18867 | 6.863 | 5.746 | 32.242 | 293.616 | 296.7792 | 1409.5787 | 1497.2296 | -6.2182 | 89.136 | 897.0044 | 96.4056 | 133.518 | 115.057 | 18.151 | 8.773 | 9.078 | 17.851 | 17.851 | 0.35918 | 0.49146 | 13.3261 | 13.3237 | 4.1534 | 101.9831 | 0.13065 | 5.746 | 5.746 | 16.7505 | 296.7792 | 529.65 | 567.3996 | -7.1273 | 94.3559 | 432.0894 | 96.1234 | 115.057 | 100.35 | 18.151 | 4.279 | 4.799 | 9.078 | 9.078 | 0.37019 | 0.47136 | 12.9995 | 12.9972 | 7.6106 | 81.9419 | 0.15861 | 5.746 | 5.746 | 3.262 | 529.65 | 938.8925 | 999.0007 | -6.402 | 98.9009 | 764.3254 | 99.5732 | 100.35 | 58.417 | 18.151 | 1.306 | 3.164 | 4.47 | 4.47 | 0.15274 | 0.29217 | 11.6089 | 11.6068 | 10.351 | 50.8815 | 0.22811 | 5.746 | 6.25 | 80.873 | 938.8925 | 1409.5787 | 1293.0561 | 8.2665 | 72.7498 | 1115.9743 | 92.7532
[11 empty] | 1999-02-06 | 19:00 | 5916 | 28.951 | 133.658 | 58.432 | 18.193 | 0 | 14.394 | 3.165 |  | 17.559 | 17.559 | 0.81975 | 0 | 13.0855 | 13.1044 | 8.6797 | 69.1723 | 0.18945 | 6.769 | 5.723 | 31.9835 | 294.864 | 297.0974 | 1393.1131 | 1502.8005 | -7.8735 | 89.2347 | 899.9489 | 96.4461 | 133.658 | 115.447 | 18.193 | 8.832 | 8.962 | 17.794 | 17.794 | 0.35688 | 0.49635 | 13.4157 | 13.4351 | 4.1889 | 102.1706 | 0.1315 | 5.723 | 5.723 | 16.4775 | 297.0974 | 530.1 | 573.6468 | -8.2148 | 94.4538 | 435.3721 | 96.2153 | 115.447 | 100.702 | 18.193 | 4.28 | 4.682 | 8.962 | 8.962 | 0.36397 | 0.47757 | 13.0025 | 13.0214 | 7.6764 | 82.2051 | 0.1584 | 5.723 | 5.723 | 3.2613 | 530.1 | 947.9925 | 1011.7039 | -6.7207 | 98.9023 | 770.902 | 99.5769 | 100.702 | 58.432 | 18.193 | 1.282 | 3.165 | 4.447 | 4.447 | 0.1523 | 0.28828 | 11.3956 | 11.4121 | 10.4282 | 50.9458 | 0.224 | 5.723 | 6.187 | 80.8035 | 947.9925 | 1393.1131 | 1299.252 | 6.7375 | 72.8024 | 1123.6222 | 92.8087
[11 empty] | 1999-02-07 | 3:00 | 5924 | 28.908 | 134.409 | 57.277 | 18.127 | 0 | 14.4 | 3.105 |  | 17.505 | 17.505 | 0.82262 | 0 | 13.0909 | 13.1266 | 8.7736 | 68.9424 | 0.1904 | 6.517 | 5.754 | 32.6415 | 294.432 | 296.9995 | 1399.8209 | 1523.0077 | -8.8002 | 89.0096 | 910.0036 | 96.413 | 134.409 | 116.025 | 18.127 | 8.833 | 8.901 | 17.734 | 17.734 | 0.35526 | 0.49808 | 13.4172 | 13.4538 | 4.1965 | 102.8935 | 0.13075 | 5.754 | 5.754 | 16.5165 | 296.9995 | 531.45 | 575.3398 | -8.2585 | 94.4389 | 436.1696 | 96.2133 | 116.025 | 100.8 | 18.127 | 4.266 | 4.635 | 8.901 | 8.901 | 0.36109 | 0.47927 | 12.96 | 12.9953 | 7.7128 | 82.5727 | 0.15738 | 5.754 | 5.754 | 3.2476 | 531.45 | 957.775 | 1017.6013 | -6.2464 | 98.9065 | 774.5257 | 99.5807 | 100.8 | 57.277 | 18.127 | 1.301 | 3.105 | 4.406 | 4.406 | 0.15027 | 0.29528 | 11.5644 | 11.5959 | 10.5972 | 50.3143 | 0.23047 | 5.754 | 6.229 | 81.6144 | 957.775 | 1399.8209 | 1324.8877 | 5.3531 | 72.5204 | 1141.3314 | 92.8492
[11 empty] | 1999-02-07 | 11:00 | 5932 | 29.04 | 135.4 | 56.07 | 18.177 | 0 | 14.453 | 3.104 |  | 17.557 | 17.557 | 0.8232 | 0 | 13.1391 | 13.1236 | 8.7238 | 68.8342 | 0.19065 | 6.978 | 5.758 | 34.404 | 292.08 | 296.5262 | 1443.7305 | 1517.0329 | -5.0773 | 88.3977 | 906.7796 | 96.2059 | 135.4 | 116.925 | 18.177 | 8.895 | 8.83 | 17.725 | 17.725 | 0.3542 | 0.50183 | 13.5114 | 13.4954 | 4.2037 | 103.7818 | 0.13004 | 5.758 | 5.758 | 16.965 | 296.5262 | 537.3 | 578.1454 | -7.602 | 94.2788 | 437.3358 | 96.1208 | 116.925 | 100.162 | 18.177 | 4.266 | 4.564 | 8.83 | 8.83 | 0.3573 | 0.48313 | 12.96 | 12.9447 | 7.8366 | 82.5299 | 0.15685 | 5.758 | 5.758 | 3.2395 | 537.3 | 955.7275 | 1036.4898 | -8.4503 | 98.9075 | 786.8949 | 99.5883 | 100.162 | 56.07 | 18.177 | 1.292 | 3.104 | 4.396 | 4.396 | 0.15005 | 0.2939 | 11.4844 | 11.4709 | 10.5491 | 49.3899 | 0.23225 | 5.758 | 6.393 | 82.5418 | 955.7275 | 1443.7305 | 1319.1798 | 8.627 | 72.1638 | 1137.4537 | 92.7433
[11 empty] | 1999-02-07 | 19:00 | 5940 | 28.972 | 139.4 | 56.115 | 17.761 | 0 | 14.257 | 3.104 |  | 17.361 | 17.361 | 0.82121 | 0 | 12.9609 | 12.9716 | 8.6562 | 71.3403 | 0.18183 | 6.931 | 5.73 | 34.0985 | 292.416 | 296.6813 | 1437.6323 | 1502.7517 | -4.5296 | 88.5067 | 899.7165 | 96.2101 | 139.4 | 121.012 | 17.761 | 8.712 | 8.848 | 17.56 | 17.56 | 0.35223 | 0.49613 | 13.2334 | 13.2444 | 4.1766 | 108.2684 | 0.12233 | 5.73 | 5.73 | 16.809 | 296.6813 | 534.15 | 572.2517 | -7.1332 | 94.3343 | 434.4665 | 96.1311 | 121.012 | 102.502 | 17.761 | 4.253 | 4.595 | 8.848 | 8.848 | 0.35861 | 0.48067 | 12.9205 | 12.9312 | 7.7663 | 86.2297 | 0.14996 | 5.73 | 5.73 | 3.2255 | 534.15 | 960.2775 | 1025.5584 | -6.7981 | 98.9128 | 779.8542 | 99.5864 | 102.502 | 56.115 | 17.761 | 1.292 | 3.104 | 4.396 | 4.396 | 0.15005 | 0.2939 | 11.4844 | 11.494 | 10.5964 | 50.9511 | 0.22559 | 5.73 | 6.339 | 83.1757 | 960.2775 | 1437.6323 | 1325.3598 | 7.8095 | 71.9646 | 1142.8187 | 92.7219
[11 empty] | 1999-02-07 | 20:00 | 5941.0025 | 28.981 | 136.868 | 59.445 | 17.631 | 0 | 14.375 | 3.703 |  | 18.078 | 18.078 | 0.79517 | 0 | 13.0682 | 13.0755 | 7.7221 | 72.8034 | 0.1796 | 6.879 | 5.739 | 34.122 | 292.416 | 296.6894 | 1449.2196 | 1315.973 | 9.1944 | 88.4991 | 806.3312 | 95.7682 | 136.868 | 118.837 | 17.631 | 8.835 | 9.021 | 17.856 | 17.856 | 0.35849 | 0.49479 | 13.4203 | 13.4278 | 4.1737 | 106.0478 | 0.12662 | 5.739 | 5.739 | 16.5165 | 296.6894 | 534.6 | 571.0856 | -6.8248 | 94.4331 | 433.8875 | 96.1934 | 118.837 | 101.167 | 17.631 | 4.253 | 4.768 | 9.021 | 9.021 | 0.36784 | 0.47146 | 12.9205 | 12.9278 | 7.684 | 84.687 | 0.15265 | 5.739 | 5.739 | 3.2039 | 534.6 | 952.9975 | 1008.5991 | -5.8344 | 98.9201 | 771.5995 | 99.5848 | 101.167 | 59.445 | 17.631 | 1.287 | 3.703 | 4.99 | 4.99 | 0.17392 | 0.25792 | 11.44 | 11.4464 | 10.2051 | 52.4699 | 0.21815 | 5.739 | 6.341 | 83.5744 | 952.9975 | 1449.2196 | 1255.1707 | 13.3899 | 71.831 | 1104.0841 | 92.4304
[11 empty] | 1999-02-09 | 8:32 | 5977.5325 | 28.777 | 139.28 | 59.25 | 18.189 | 0 | 14.612 | 2.926 |  | 17.538 | 17.538 | 0.83316 | 0 | 13.2836 | 13.3715 | 9.3203 | 71.7557 | 0.18635 | 7.681 | 5.758 | 33.6285 | 310.224 | 300.1574 | 1404.6998 | 1631.1625 | -16.1218 | 88.7964 | 965.66 | 96.5176 | 139.28 | 123.427 | 18.189 | 9.129 | 8.904 | 18.033 | 18.033 | 0.35929 | 0.50624 | 13.8668 | 13.9585 | 4.2943 | 108.8702 | 0.12821 | 5.758 | 5.758 | 16.263 | 300.1574 | 621.9 | 591.2258 | 4.9323 | 94.5818 | 445.6916 | 96.3511 | 123.427 | 100.672 | 18.189 | 4.239 | 4.665 | 8.904 | 8.904 | 0.36197 | 0.47608 | 12.878 | 12.9631 | 8.9985 | 84.862 | 0.15276 | 5.758 | 5.758 | 3.1672 | 621.9 | 1011.6925 | 1184.1312 | -17.0446 | 98.9448 | 903.0156 | 99.6493 | 100.672 | 59.25 | 18.189 | 1.244 | 2.926 | 4.17 | 4.17 | 0.14197 | 0.29832 | 11.0578 | 11.1309 | 11.2553 | 50.5167 | 0.22034 | 5.758 | 7.44 | 83.4781 | 1011.6925 | 1404.6998 | 1406.3264 | -0.11579 | 72.1886 | 1209.0094 | 93.0953
[11 empty] | 1999-02-09 | 16:00 | 5985 | 28.832 | 134.06 | 66.982 | 17.709 | 0 | 14.237 | 2.506 |  | 16.743 | 16.743 | 0.85033 | 0 | 12.9427 | 13.0072 | 9.9447 | 72.8673 | 0.1785 | 7.267 | 5.769 | 40.8195 | 310.32 | 299.7576 | 1622.4181 | 1770.8277 | -9.1474 | 86.3825 | 1035.2927 | 96.0572 | 134.06 | 116.745 | 17.709 | 8.71 | 8.357 | 17.067 | 17.067 | 0.33911 | 0.51034 | 13.2304 | 13.2962 | 4.2814 | 103.4121 | 0.12858 | 5.769 | 5.769 | 18.291 | 299.7576 | 586.8 | 593.1134 | -1.0759 | 93.8981 | 446.4355 | 95.9029 | 116.745 | 101.137 | 17.709 | 4.24 | 4.117 | 8.357 | 8.357 | 0.33276 | 0.50736 | 12.881 | 12.9451 | 8.8412 | 82.3908 | 0.15712 | 5.769 | 5.769 | 3.1979 | 586.8 | 1112.475 | 1187.8378 | -6.7743 | 98.9332 | 887.3189 | 99.6396 | 101.137 | 66.982 | 17.709 | 1.287 | 2.506 | 3.793 | 3.793 | 0.12603 | 0.33931 | 11.44 | 11.497 | 12.8764 | 53.4741 | 0.215 | 5.769 | 6.783 | 87.9245 | 1112.475 | 1622.4181 | 1638.6508 | -1.0005 | 70.6681 | 1375.5629 | 93.6081
[11 empty] | 1999-02-09 | 20:37 | 5989.6136 | 28.517 | 127.936 | NR | 16.936 | 0 | 14.994 | 3.982 |  | 18.976 | 18.976 | 0.79016 | 0 | 13.6309 | 13.8269 | 7.8032 | #VALUE! | #VALUE! | 7.678 | 5.784 | 29.8685 | 313.44 | 300.5573 | 1305.9036 | 1319.8209 | -1.0657 | 90.0623 | 810.1891 | 96.3134 | 127.936 | 111.27 | 16.936 | 9.607 | 8.547 | 18.154 | 18.154 | 0.35614 | 0.52919 | 14.5929 | 14.8027 | 4.4352 | 98.2318 | 0.15069 | 5.784 | 5.784 | 16.614 | 300.5573 | 580.95 | 619.7152 | -6.6727 | 94.4723 | 460.1363 | 96.3893 | 111.27 | 92.617 | 16.936 | 4.187 | 4.36 | 8.547 | 8.547 | 0.34431 | 0.48988 | 12.72 | 12.9029 | 8.5533 | 76.4542 | 0.16877 | 5.784 | 5.784 | 3.0886 | 580.95 | 871.0975 | 1135.8825 | -30.3967 | 98.9724 | 858.4162 | 99.6402 | 92.617 | 37.08 | 16.936 | 1.2 | 3.982 | 5.182 | 5.182 | 0.18335 | 0.23157 | 10.6667 | 10.82 | 9.1017 | 38.8108 | 0.27879 | 5.784 | 6.343 | 80.1091 | 871.0975 | 1305.9036 | 1109.4667 | 15.0422 | 73.3465 | 990.2821 | 91.9105
[11 empty] | 1999-02-10 | 5:00 | 5998 | 28.764 | 141.357 | 44.205 | 18.174 | 0 | 14.575 | 3.981 |  | 18.556 | 18.556 | 0.78546 | 0 | 13.25 | 13.3428 | 7.48 | 67.127 | 0.19877 | 7.009 | 5.755 | 33.9575 | 301.44 | 298.2154 | 1311.1 | 1265.7005 | 3.4627 | 88.6131 | 781.9579 | 95.6574 | 141.357 | 121.927 | 18.174 | 9.01 | 9.617 | 18.627 | 18.627 | 0.37672 | 0.48371 | 13.6861 | 13.7819 | 4.1394 | 109.3286 | 0.12606 | 5.755 | 5.755 | 16.3215 | 298.2154 | 540.45 | 562.3168 | -4.046 | 94.5269 | 430.2661 | 96.2066 | 121.927 | 102.045 | 18.174 | 4.293 | 5.324 | 9.617 | 9.617 | 0.39857 | 0.4464 | 13.042 | 13.1333 | 7.538 | 86.274 | 0.15223 | 5.755 | 5.755 | 3.2382 | 540.45 | 946.855 | 973.63 | -2.8278 | 98.9141 | 757.04 | 99.5723 | 102.045 | 44.205 | 18.174 | 1.272 | 3.981 | 5.253 | 5.253 | 0.18475 | 0.24215 | 11.3067 | 11.3858 | 10.0094 | 44.9416 | 0.25335 | 5.755 | 6.096 | 83.7962 | 946.855 | #REF! | 1222.6176 | #REF! | 71.9008 | 1084.7363 | 92.275
[11 empty] | 1999-02-10 | 13:00 | 6006.0006 | 28.84 | 142.107 | 50.625 | 18.48 | 0 | 14.595 | 3.821 |  | 18.416 | 18.416 | 0.79252 | 0 | 13.2682 | 13.3311 | 7.696 | 70.19 | 0.18993 | 7.099 | 5.792 | 33.464 | 300.384 | 297.9461 | 1388 | 1308.1832 | 5.7505 | 88.7684 | 803.0646 | 95.833 | 142.107 | 122.64 | 18.48 | 9.011 | 9.736 | 18.747 | 18.747 | 0.37991 | 0.48066 | 13.6876 | 13.7525 | 4.1132 | 109.7803 | 0.12527 | 5.792 | 5.792 | 16.7505 | 297.9461 | 544.05 | 558.2022 | -2.6013 | 94.378 | 428.0741 | 96.087 | 122.64 | 104.34 | 18.48 | 4.292 | 5.444 | 9.736 | 9.736 | 0.40495 | 0.44084 | 13.039 | 13.1008 | 7.5398 | 87.4702 | 0.14977 | 5.792 | 5.792 | 3.2506 | 544.05 | 950.495 | 970.4113 | -2.0954 | 98.909 | 757.2306 | 99.5707 | 104.34 | 50.625 | 18.48 | 1.292 | 3.821 | 5.113 | 5.113 | 0.17874 | 0.25269 | 11.4844 | 11.5389 | 10.1443 | 48.8582 | 0.23617 | 5.792 | 6.387 | 82.7658 | 950.495 | #REF! | 1243.9015 | #REF! | 72.2212 | 1097.1982 | 92.4566
[11 empty] | 1999-02-10 | 21:00 | 6014 | 28.819 | 141.182 | 51.397 | 18.402 | 0 | 14.607 | 3.883 |  | 18.49 | 18.49 | 0.78999 | 0 | 13.2791 | 13.3503 | 7.6496 | 70.2379 | 0.19007 | 7.262 | 5.769 | 32.9 | 302.64 | 298.4275 | 1391.1 | 1297.2842 | 6.744 | 88.9755 | 797.8559 | 95.8764 | 141.182 | 121.777 | 18.402 | 9.009 | 9.678 | 18.687 | 18.687 | 0.37834 | 0.4821 | 13.6846 | 13.758 | 4.1309 | 108.9466 | 0.12628 | 5.769 | 5.769 | 16.536 | 298.4275 | 542.7 | 560.833 | -3.3413 | 94.459 | 429.6303 | 96.1511 | 121.777 | 104.242 | 18.402 | 4.306 | 5.372 | 9.678 | 9.678 | 0.40148 | 0.44493 | 13.0815 | 13.1517 | 7.5565 | 87.051 | 0.15108 | 5.769 | 5.769 | 3.2533 | 542.7 | 956.6375 | 975.1009 | -1.93 | 98.9099 | 758.9004 | 99.5713 | 104.242 | 51.397 | 18.402 | 1.292 | 3.883 | 5.175 | 5.175 | 0.18123 | 0.24966 | 11.4844 | 11.5461 | 10.1979 | 49.2196 | 0.23458 | 5.769 | 6.278 | 82.3088 | 956.6375 | #REF! | 1247.555 | #REF! | 72.4192 | 1102.0963 | 92.5316
[11 empty] | 1999-02-11 | 5:00 | 6022 | 28.789 | 137.035 | 50.047 | 17.961 | 0 | 14.282 | 3.823 |  | 18.105 | 18.105 | 0.78884 | 0 | 12.9836 | 13.0649 | 7.6266 | 67.9534 | 0.19226 | 7.244 | 5.741 | 32.7355 | 304.032 | 298.6642 | 1511.46 | 1292.123 | 14.5116 | 89.0394 | 795.3936 | 95.8844 | 137.035 | 117.742 | 17.961 | 8.71 | 9.62 | 18.33 | 18.33 | 0.3728 | 0.47518 | 13.2304 | 13.3132 | 4.0962 | 105.3313 | 0.12639 | 5.741 | 5.741 | 16.692 | 298.6642 | 540.9 | 553.9633 | -2.4151 | 94.4111 | 426.3137 | 96.0846 | 117.742 | 101.332 | 17.961 | 4.28 | 5.34 | 9.62 | 9.62 | 0.39908 | 0.44491 | 13.0025 | 13.0839 | 7.5311 | 84.0449 | 0.15568 | 5.741 | 5.741 | 3.2496 | 540.9 | 947.31 | 971.8258 | -2.5879 | 98.9119 | 756.3629 | 99.5704 | 101.332 | 50.047 | 17.961 | 1.292 | 3.823 | 5.115 | 5.115 | 0.17882 | 0.25259 | 11.4844 | 11.5563 | 10.1164 | 47.6121 | 0.24272 | 5.741 | 6.147 | 81.9056 | 947.31 | 1511.46 | 1239.7773 | 17.9749 | 72.576 | 1093.5436 | 92.5101
[11 empty] | 1999-02-11 | 13:00 | 6030.0003 | 28.959 | 136.171 | 50.077 | 17.952 | 0 | 14.296 | 3.761 |  | 18.057 | 18.057 | 0.79172 | 0 | 12.9964 | 13.0121 | 7.703 | 67.469 | 0.19286 | 7.258 | 5.775 | 31.772 | 296.112 | 297.3422 | 1550.88 | 1306.8057 | 15.7378 | 89.3147 | 802.074 | 96.0388 | 136.171 | 117.052 | 17.952 | 8.712 | 9.672 | 18.384 | 18.384 | 0.37422 | 0.47389 | 13.2334 | 13.2495 | 4.0753 | 104.5842 | 0.12669 | 5.775 | 5.775 | 16.3605 | 297.3422 | 527.85 | 550.435 | -4.2787 | 94.4978 | 423.8886 | 96.1404 | 117.052 | 100.665 | 17.952 | 4.292 | 5.38 | 9.672 | 9.672 | 0.40153 | 0.44376 | 13.039 | 13.0548 | 7.3387 | 83.5678 | 0.15622 | 5.775 | 5.775 | 3.2375 | 527.85 | 918.4175 | 946.3699 | -3.0435 | 98.9112 | 737.1099 | 99.5608 | 100.665 | 50.077 | 17.952 | 1.292 | 3.761 | 5.053 | 5.053 | 0.17634 | 0.25569 | 11.4844 | 11.4984 | 9.8132 | 47.6058 | 0.24153 | 5.775 | 6.298 | 80.9424 | 918.4175 | 1550.88 | 1206.1117 | 22.2305 | 72.778 | 1062.2646 | 92.3802
[11 empty] | 1999-02-11 | 21:00 | 6038 | 28.955 | 136.687 | 50.355 | 18.016 | 0 | 14.289 | 3.882 |  | 18.171 | 18.171 | 0.78636 | 0 | 12.99 | 13.0073 | 7.5503 | 67.9547 | 0.19141 | 7.215 | 5.766 | 31.584 | 297.456 | 297.3994 | 1550.1 | 1275.8217 | 17.6942 | 89.3799 | 786.6105 | 95.9848 | 136.687 | 117.382 | 18.016 | 8.71 | 9.557 | 18.267 | 18.267 | 0.37112 | 0.47682 | 13.2304 | 13.248 | 4.0939 | 104.9246 | 0.12626 | 5.766 | 5.766 | 16.1655 | 297.3994 | 530.1 | 553.7085 | -4.4536 | 94.5644 | 425.554 | 96.2013 | 117.382 | 101.145 | 18.016 | 4.292 | 5.265 | 9.557 | 9.557 | 0.3954 | 0.44909 | 13.039 | 13.0563 | 7.4161 | 83.8314 | 0.15575 | 5.766 | 5.766 | 3.2386 | 530.1 | 920.465 | 959.5946 | -4.2511 | 98.911 | 744.8473 | 99.5652 | 101.145 | 50.355 | 18.016 | 1.287 | 3.882 | 5.169 | 5.169 | 0.18109 | 0.24898 | 11.44 | 11.4552 | 9.788 | 47.946 | 0.23892 | 5.766 | 6.301 | 80.8438 | 920.465 | #VALUE! | 1198.8247 | #VALUE! | 72.8164 | 1059.6449 | 92.3707
[11 empty] | 1999-02-12 | 0:00 | 6041 | 28.879 | 136.76 | 50.4 | 17.977 | 0 | 14.284 | 3.884 |  | 18.168 | 18.168 | 0.78622 | 0 | 12.9855 | 13.032 | 7.5679 | 68.0351 | 0.19155 | 7.185 | 5.768 | 31.0435 | 298.896 | 297.6278 | 1498 | 1278.0322 | 14.6841 | 89.5697 | 787.83 | 96.0596 | 136.76 | 117.645 | 17.977 | 8.712 | 9.679 | 18.391 | 18.391 | 0.3744 | 0.47371 | 13.2334 | 13.2808 | 4.0791 | 105.1464 | 0.12631 | 5.768 | 5.768 | 16.3215 | 297.6278 | 528.75 | 550.8297 | -4.1758 | 94.5161 | 424.2288 | 96.1527 | 117.645 | 101.542 | 17.977 | 4.28 | 5.399 | 9.679 | 9.679 | 0.40223 | 0.44219 | 13.0025 | 13.0491 | 7.3381 | 84.2784 | 0.15483 | 5.768 | 5.768 | 3.238 | 528.75 | 926.835 | 945.344 | -1.997 | 98.9121 | 737.047 | 99.5607 | 101.542 | 50.4 | 17.977 | 1.292 | 3.884 | 5.176 | 5.176 | 0.18127 | 0.24961 | 11.4844 | 11.5256 | 9.8671 | 48.1269 | 0.23948 | 5.768 | 6.271 | 80.8326 | 926.835 | #REF! | 1208.2549 | #REF! | 72.841 | 1067.545 | 92.4282
[11 empty] | 1999-02-12 | 13:00 | 6054.0003 | 29.002 | 131.702 | 48.15 | 17.763 | 0 | 14.322 | 3.761 |  | 18.083 | 18.083 | 0.79201 | 0 | 13.02 | 13.0192 | 7.6718 | 64.4912 | 0.20188 | 7.197 | 5.776 | 33.041 | 296.16 | 297.2198 | 1468 | 1303.2207 | 11.2247 | 88.8833 | 800.2203 | 95.871 | 131.702 | 113.092 | 17.763 | 8.773 | 9.075 | 17.848 | 17.848 | 0.3591 | 0.49154 | 13.3261 | 13.3253 | 4.1549 | 100.4791 | 0.13262 | 5.776 | 5.776 | 17.121 | 297.2198 | 528.3 | 567.9975 | -7.5142 | 94.2396 | 432.6087 | 96.0424 | 113.092 | 97.425 | 17.763 | 4.253 | 4.822 | 9.075 | 9.075 | 0.37072 | 0.46865 | 12.9205 | 12.9197 | 7.5662 | 79.9293 | 0.16164 | 5.776 | 5.776 | 3.2309 | 528.3 | 906.1325 | 991.4105 | -9.4112 | 98.9129 | 759.8552 | 99.5748 | 97.425 | 48.15 | 17.763 | 1.296 | 3.761 | 5.057 | 5.057 | 0.17642 | 0.25628 | 11.52 | 11.5193 | 9.6658 | 45.3587 | 0.25396 | 5.776 | 6.185 | 81.6166 | 906.1325 | #REF! | 1190.2518 | #REF! | 72.54 | 1048.1921 | 92.2136
[11 empty] | 1999-02-12 | 21:00 | 6062 | 28.951 | 131.956 | 48.382 | 17.779 | 0 | 14.318 | 3.822 |  | 18.14 | 18.14 | 0.78931 | 0 | 13.0164 | 13.0352 | 7.6073 | 64.7827 | 0.20121 | 7.447 | 5.764 | 32.9 | 298.416 | 297.6768 | 1398 | 1289.5853 | 7.755 | 88.9477 | 793.631 | 95.8545 | 131.956 | 113.1 | 17.779 | 8.772 | 9.144 | 17.916 | 17.916 | 0.36093 | 0.48962 | 13.3246 | 13.3439 | 4.1544 | 100.5946 | 0.13265 | 5.764 | 5.764 | 16.9065 | 297.6768 | 526.5 | 567.0247 | -7.697 | 94.3205 | 432.3507 | 96.0896 | 113.1 | 97.507 | 17.779 | 4.254 | 4.89 | 9.144 | 9.144 | 0.37438 | 0.46522 | 12.9235 | 12.9423 | 7.5087 | 80.0158 | 0.16175 | 5.764 | 5.764 | 3.2322 | 526.5 | 909.09 | 981.7109 | -7.9883 | 98.9142 | 754.1054 | 99.5714 | 97.507 | 48.382 | 17.779 | 1.292 | 3.822 | 5.114 | 5.114 | 0.17878 | 0.25264 | 11.4844 | 11.5011 | 9.6758 | 45.4897 | 0.25283 | 5.764 | 6.04 | 81.4061 | 909.09 | #REF! | 1188.8827 | #REF! | 72.6529 | 1048.9863 | 92.2395
[11 empty] | 1999-02-13 | 5:00 | 6070 | 28.913 | 136.285 | 50.302 | 18.231 | 0 | 14.524 | 3.823 |  | 18.347 | 18.347 | 0.79163 | 0 | 13.2036 | 13.2376 | 7.7097 | 67.3528 | 0.19654 | 7.08 | 5.76 | 31.8895 | 298.848 | 297.7829 | 1375 | 1307.9413 | 4.877 | 89.291 | 802.8621 | 96.028 | 136.285 | 117.292 | 18.231 | 8.948 | 9.271 | 18.219 | 18.219 | 0.36667 | 0.49114 | 13.5919 | 13.6269 | 4.1729 | 104.3846 | 0.13055 | 5.76 | 5.76 | 16.3215 | 297.7829 | 528.3 | 569.4382 | -7.7869 | 94.519 | 433.6105 | 96.2359 | 117.292 | 101.077 | 18.231 | 4.28 | 4.991 | 9.271 | 9.271 | 0.38046 | 0.46165 | 13.0025 | 13.036 | 7.5019 | 83.4516 | 0.15621 | 5.76 | 5.76 | 3.238 | 528.3 | 918.8725 | 978.5635 | -6.4961 | 98.9126 | 753.4318 | 99.5702 | 101.077 | 50.302 | 18.231 | 1.296 | 3.823 | 5.119 | 5.119 | 0.1789 | 0.25317 | 11.52 | 11.5497 | 9.7968 | 47.6617 | 0.24233 | 5.76 | 6.122 | 81.1843 | 918.8725 | #REF! | 1202.8495 | #REF! | 72.7371 | 1060.861 | 92.3473
[11 empty] | 1999-02-13 | 13:00 | 6078 | 28.951 | 136.224 | 49.987 | 18.277 | 0 | 14.516 | 3.882 |  | 18.398 | 18.398 | 0.789 | 0 | 13.1964 | 13.2155 | 7.6126 | 67.2159 | 0.19661 | 7.435 | 5.765 | 32.0305 | 297.552 | 297.3096 | 1374.8 | 1289.2703 | 6.2212 | 89.2266 | 793.2899 | 95.9623 | 136.224 | 117.067 | 18.277 | 8.95 | 9.263 | 18.213 | 18.213 | 0.36648 | 0.49141 | 13.5949 | 13.6146 | 4.163 | 104.2055 | 0.13065 | 5.765 | 5.765 | 16.614 | 297.3096 | 526.5 | 568.5204 | -7.9811 | 94.4119 | 432.915 | 96.1623 | 117.067 | 100.935 | 18.277 | 4.279 | 4.984 | 9.263 | 9.263 | 0.38006 | 0.46195 | 12.9995 | 13.0183 | 7.4789 | 83.2451 | 0.15639 | 5.765 | 5.765 | 3.2371 | 526.5 | 913.185 | 975.746 | -6.8509 | 98.9112 | 751.123 | 99.569 | 100.935 | 49.987 | 18.277 | 1.287 | 3.882 | 5.169 | 5.169 | 0.18109 | 0.24898 | 11.44 | 11.4566 | 9.7002 | 47.4838 | 0.24127 | 5.765 | 6.181 | 81.097 | 913.185 | #REF! | 1189.0473 | #REF! | 72.7231 | 1051.1161 | 92.2847
[11 empty] | 1999-02-18 | 11:04 | 6092.0739 | 28.908 | 137.002 | 55.297 | 17.956 | 0 | 14.908 | 2.864 |  | 17.772 | 17.772 | 0.83885 | 0 | 13.5527 | 13.5896 | 9.22 | 68.9735 | 0.19703 | 7.95 | 5.77 | 43.4515 | 307.152 | 299.3741 | 1567.9 | 1631.5297 | -4.0583 | 85.4859 | 965.4519 | 95.4994 | 137.002 | 110.895 | 17.956 | 9.43 | 7.874 | 17.304 | 17.304 | 0.33583 | 0.54496 | 14.3241 | 14.3631 | 4.4703 | 101.5222 | 0.14148 | 5.77 | 5.77 | 19.773 | 299.3741 | 575.55 | 634.2278 | -10.1951 | 93.3952 | 466.8009 | 95.7641 | 110.895 | 93.675 | 17.956 | 4.201 | 3.673 | 7.874 | 7.874 | 0.30803 | 0.53353 | 12.7625 | 12.7973 | 8.9947 | 75.3343 | 0.16987 | 5.77 | 5.77 | 3.3215 | 575.55 | 1042.1775 | 1230.0373 | -18.0257 | 98.8905 | 902.7937 | 99.6321 | 93.675 | 55.297 | 17.956 | 1.277 | 2.864 | 4.141 | 4.141 | 0.14015 | 0.30838 | 11.3511 | 11.382 | 11.6741 | 44.8559 | 0.25375 | 5.77 | 6.726 | 87.5818 | 1042.1775 | #REF! | 1467.8125 | #REF! | 70.745 | 1254.995 | 93.0213
[11 empty] | 1999-02-18 | 19:00 | 6100 | 28.866 | 137.886 | 55.927 | 18.049 | 0 | 14.694 | 2.865 |  | 17.559 | 17.559 | 0.83684 | 0 | 13.3582 | 13.4112 | 9.1709 | 69.6866 | 0.19245 | 7.846 | 5.748 | 42.4645 | 308.64 | 299.7576 | 1675.8 | 1619.3614 | 3.3679 | 85.8337 | 959.5595 | 95.5746 | 137.886 | 111.915 | 18.049 | 9.249 | 7.879 | 17.128 | 17.128 | 0.33355 | 0.53999 | 14.0491 | 14.1049 | 4.445 | 102.4065 | 0.13773 | 5.748 | 5.748 | 19.656 | 299.7576 | 574.65 | 628.5632 | -9.3819 | 93.4427 | 464.1604 | 95.7653 | 111.915 | 94.567 | 18.049 | 4.187 | 3.692 | 7.879 | 7.879 | 0.30867 | 0.53141 | 12.72 | 12.7705 | 8.9538 | 76.2382 | 0.16751 | 5.748 | 5.748 | 3.2682 | 574.65 | 1036.945 | 1222.639 | -17.9078 | 98.9097 | 898.6445 | 99.6363 | 94.567 | 55.927 | 18.049 | 1.258 | 2.865 | 4.123 | 4.123 | 0.13981 | 0.30512 | 11.1822 | 11.2266 | 11.5863 | 45.6117 | 0.24613 | 5.748 | 6.467 | 86.8963 | 1036.945 | #REF! | 1454.1042 | #REF! | 71.0111 | 1245.5246 | 93.0233
[11 empty] | 1999-02-19 | 0:00 | 6105 | 28.819 | 138.208 | 56.28 | 18.001 | 0 | 14.714 | 2.866 |  | 17.58 | 17.58 | 0.83697 | 0 | 13.3764 | 13.4481 | 9.2152 | 70.0278 | 0.19204 | 7.656 | 5.741 | 41.4775 | 310.032 | 299.8229 | 1576.6 | 1626.1641 | -3.1437 | 86.166 | 962.9935 | 95.6929 | 138.208 | 112.417 | 18.001 | 9.25 | 7.886 | 17.136 | 17.136 | 0.33375 | 0.5398 | 14.0506 | 14.126 | 4.4538 | 102.8577 | 0.13734 | 5.741 | 5.741 | 19.0905 | 299.8229 | 576.9 | 629.1121 | -9.0505 | 93.6327 | 464.4675 | 95.8898 | 112.417 | 95.01 | 18.001 | 4.187 | 3.699 | 7.886 | 7.886 | 0.30905 | 0.53094 | 12.72 | 12.7882 | 8.9826 | 76.7299 | 0.16667 | 5.741 | 5.741 | 3.2855 | 576.9 | 1038.9925 | 1226.19 | -18.0172 | 98.9042 | 901.545 | 99.6356 | 95.01 | 56.28 | 18.001 | 1.277 | 2.866 | 4.143 | 4.143 | 0.14023 | 0.30823 | 11.3511 | 11.412 | 11.6456 | 45.9984 | 0.2481 | 5.741 | 6.386 | 86.6051 | 1038.9925 | #REF! | 1463.3465 | #REF! | 71.1146 | 1251.1695 | 93.0781
[11 empty] | 1999-02-19 | 11:00 | 6116.0003 | 28.913 | 143.186 | 58.56 | 18.618 | 0 | 15.06 | 2.925 |  | 17.985 | 17.985 | 0.83736 | 0 | 13.6909 | 13.7262 | 9.2606 | 72.9944 | 0.18804 | 7.476 | 5.784 | 40.185 | 307.296 | 299.268 | 1546,7 | 1633.2133 | #VALUE! | 86.5722 | 966.2406 | 95.8411 | 143.186 | 116.895 | 18.618 | 9.556 | 8.231 | 17.787 | 17.787 | 0.34703 | 0.53725 | 14.5154 | 14.5528 | 4.4319 | 106.9906 | 0.13602 | 5.784 | 5.784 | 18.8565 | 299.268 | 572.4 | 624.8192 | -9.1578 | 93.6991 | 462.0436 | 95.9189 | 116.895 | 98.677 | 18.618 | 4.227 | 4.004 | 8.231 | 8.231 | 0.32639 | 0.51355 | 12.8415 | 12.8746 | 8.6947 | 80.4733 | 0.15999 | 5.784 | 5.784 | 3.3178 | 572.4 | 1031.2575 | 1173.1768 | -13.7618 | 98.8914 | 872.7884 | 99.6199 | 98.677 | 58.56 | 18.618 | 1.277 | 2.925 | 4.202 | 4.202 | 0.14259 | 0.3039 | 11.3511 | 11.3803 | 11.5197 | 48.4808 | 0.23474 | 5.784 | 6.553 | 85.6957 | 1031.2575 | #REF! | 1444.072 | #REF! | 71.3649 | 1237.6648 | 93.076
[11 empty] | 1999-02-19 | 19:00 | 6124 | 28.879 | 143.212 | 58.98 | 18.604 | 0 | 15.066 | 2.926 |  | 17.992 | 17.992 | 0.83737 | 0 | 13.6964 | 13.7454 | 9.2959 | 73.1961 | 0.18779 | 7.388 | 5.766 | 39.5505 | 309.504 | 299.6107 | 1547.8 | 1638.6631 | -5.8705 | 86.7994 | 969.1369 | 95.919 | 143.212 | 117.03 | 18.604 | 9.552 | 7.942 | 17.494 | 17.494 | 0.33927 | 0.54602 | 14.5094 | 14.5614 | 4.4999 | 107.0171 | 0.13607 | 5.766 | 5.766 | 18.603 | 299.6107 | 574.65 | 637.5842 | -10.9518 | 93.7909 | 468.5975 | 96.0301 | 117.03 | 99 | 18.604 | 4.227 | 3.715 | 7.942 | 7.942 | 0.31097 | 0.53223 | 12.8415 | 12.8875 | 8.9636 | 80.4474 | 0.1602 | 5.766 | 5.766 | 3.3253 | 574.65 | 1044.68 | 1224.7144 | -17.2335 | 98.8901 | 899.6822 | 99.6304 | 99 | 58.98 | 18.604 | 1.287 | 2.926 | 4.213 | 4.213 | 0.14283 | 0.30548 | 11.44 | 11.481 | 11.6997 | 48.6863 | 0.23582 | 5.766 | 6.557 | 85.633 | 1044.68 | #REF! | 1466.5165 | #REF! | 71.4186 | 1255.5982 | 93.1799
[11 empty] | 1999-02-20 | 1:46 | 6130.7644 | 28.789 | 129.678 | 57.427 | 16.813 | 0 | 14.433 | NR |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 13.1209 | 13.203 | 9.3 | 67.4395 | 0.19578 | 7.993 | 5.345 | 38.07 | 310.752 | 314.3722 | 1523 | #VALUE! | #VALUE! | 87.8901 | #VALUE! | #VALUE! | 129.678 | 99.202 | 16.813 | 9.072 | 6.024 | 15.096 | 15.096 | 0.2817 | 0.60095 | 13.7803 | 13.8665 | 5.1899 | 92.4371 | 0.15001 | 5.345 | 5.345 | 18.3105 | 314.3722 | 552.15 | 760.2339 | -37.6861 | 94.1755 | 537.3031 | 96.5921 | 99.202 | 79.297 | 16.813 | 4.161 | 1.863 | 6.024 | 6.024 | 0.2104 | 0.69074 | 12.641 | 12.7201 | 11.6198 | 60.8167 | 0.20915 | 5.345 | 5.345 | 3.2022 | 552.15 | 938.665 | 1778.2217 | -89.4416 | 98.9814 | 1165.1859 | 99.7252 | 79.297 | 57.427 | 16.813 | 1.2 | -0.01 | 1.19 | 1.19 | 0.023609 | 1.0084 | 10.6667 | 10.7334 | -504.0488 | 555.5978 | 0.019319 | 5.345 | 6.507 | 84.345 | 938.665 | #REF! | -101579.7398 | #REF! | 73.1703 | -50320.5374 | 100.1676
[11 empty] | 1999-02-20 | 9:00 | 6138 | 28.832 | 143.032 | 46.462 | 18.507 | 0 | 15.113 | 3.643 |  | 18.756 | 18.756 | 0.80577 | 0 | 13.7391 | 13.8075 | 8.0265 | 68.2135 | 0.20242 | 7.631 | 5.779 | 38.1405 | 310.896 | 299.2272 | 1499.2274 | 1382.3464 | 7.7961 | 87.2537 | 840.7868 | 95.4637 | 143.032 | 116.31 | 18.507 | 9.609 | 8.419 | 18.028 | 18.028 | 0.35275 | 0.533 | 14.5959 | 14.6686 | 4.412 | 106.752 | 0.13741 | 5.779 | 5.779 | 18.33 | 299.2272 | 564.75 | 619.8284 | -9.7527 | 93.8742 | 459.5278 | 96.0111 | 116.31 | 96.607 | 18.507 | 4.227 | 4.192 | 8.419 | 8.419 | 0.33642 | 0.50208 | 12.8415 | 12.9054 | 8.4458 | 79.5057 | 0.16232 | 5.779 | 5.779 | 3.261 | 564.75 | 987.1225 | 1130.927 | -14.568 | 98.9102 | 847.8385 | 99.6154 | 96.607 | 46.462 | 18.507 | 1.277 | 3.643 | 4.92 | 4.92 | 0.17132 | 0.25955 | 11.3511 | 11.4076 | 10.6002 | 42.4273 | 0.26887 | 5.779 | 6.625 | 85.185 | 987.1225 | 1499.2274 | 1303.2834 | 13.0697 | 71.5317 | 1145.203 | 92.5616
[11 empty] | 1999-02-20 | 17:00 | 6146.0003 | 28.84 | 143.655 | 53.19 | 18.702 | 0 | 15.195 | 3.224 |  | 18.419 | 18.419 | 0.82496 | 0 | 13.8136 | 13.8791 | 8.7855 | 70.935 | 0.19566 | 7.558 | 5.774 | 37.835 | 309.312 | 299.5781 | 1502.2768 | 1533.1966 | -2.0582 | 87.3706 | 916.3873 | 95.8713 | 143.655 | 117.337 | 18.702 | 9.668 | 8.249 | 17.917 | 17.917 | 0.34901 | 0.5396 | 14.6856 | 14.7552 | 4.4631 | 107.3309 | 0.13747 | 5.774 | 5.774 | 18.174 | 299.5781 | 569.7 | 629.3895 | -10.4774 | 93.9335 | 464.4838 | 96.0873 | 117.337 | 98.542 | 18.702 | 4.24 | 4.009 | 8.249 | 8.249 | 0.327 | 0.514 | 12.881 | 12.9421 | 8.6593 | 80.5782 | 0.16062 | 5.774 | 5.774 | 3.2924 | 569.7 | 1015.56 | 1168.7442 | -15.0837 | 98.901 | 869.2221 | 99.6212 | 98.542 | 53.19 | 18.702 | 1.287 | 3.224 | 4.511 | 4.511 | 0.15476 | 0.2853 | 11.44 | 11.4942 | 11.1664 | 45.9976 | 0.24989 | 5.774 | 6.565 | 84.7168 | 1015.56 | 1502.2768 | 1387.1466 | 7.6637 | 71.7213 | 1201.3533 | 92.9482
[11 empty] | 1999-02-21 | 1:02 | 6154.0294 | 28.777 | 137.249 | 41.632 | 17.319 | 0 | 14.962 | 3.585 |  | 18.547 | 18.547 | 0.80671 | 0 | 13.6018 | 13.6918 | 8.1632 | 63.9583 | 0.21407 | 7.518 | 5.703 | 35.8375 | 312.096 | 300.2962 | 1494.3485 | 1404.0146 | 6.045 | 88.0659 | 852.1554 | 95.7945 | 137.249 | 110.527 | 17.319 | 9.548 | 7.234 | 16.782 | 16.782 | 0.32033 | 0.56894 | 14.5033 | 14.5992 | 4.695 | 101.874 | 0.14331 | 5.703 | 5.703 | 17.4525 | 300.2962 | 598.05 | 673.6154 | -12.6353 | 94.1882 | 486.9558 | 96.416 | 110.527 | 89.175 | 17.319 | 4.214 | 3.02 | 7.234 | 7.234 | 0.27354 | 0.58253 | 12.802 | 12.8867 | 10.0983 | 72.4337 | 0.17791 | 5.703 | 5.703 | 3.2229 | 598.05 | 937.5275 | 1428.0505 | -52.3209 | 98.9268 | 1013.0503 | 99.6819 | 89.175 | 41.632 | 17.319 | 1.2 | 3.585 | 4.785 | 4.785 | 0.16746 | 0.25078 | 10.6667 | 10.7372 | 9.9787 | 38.1058 | 0.28177 | 5.703 | 6.147 | 82.7187 | 937.5275 | 1494.3485 | 1223.656 | 18.1144 | 72.4543 | 1080.5917 | 92.3451
[11 empty] | 1999-02-21 | 9:00 | 6162.0003 | 28.789 | 139.99 | 62.595 | 18.49 | 0 | 14.872 | 2.806 |  | 17.678 | 17.678 | 0.84127 | 0 | 13.52 | 13.6046 | 9.5733 | 73.2292 | 0.18578 | 7.412 | 5.734 | 37.2005 | 311.568 | 299.4802 | 1496.7882 | 1689.5811 | -12.8804 | 87.5783 | 994.5306 | 96.2595 | 139.99 | 115.597 | 18.49 | 9.432 | 7.941 | 17.373 | 17.373 | 0.33764 | 0.54291 | 14.3271 | 14.4167 | 4.488 | 104.8155 | 0.13754 | 5.734 | 5.734 | 17.901 | 299.4802 | 575.55 | 633.9285 | -10.1431 | 94.0226 | 466.7044 | 96.1644 | 115.597 | 98.932 | 18.49 | 4.24 | 3.701 | 7.941 | 7.941 | 0.31057 | 0.53394 | 12.881 | 12.9616 | 8.9997 | 79.7748 | 0.16248 | 5.734 | 5.734 | 3.3489 | 575.55 | 1062.1975 | 1231.0844 | -15.8998 | 98.8818 | 903.3172 | 99.6293 | 98.932 | 62.595 | 18.49 | 1.2 | 2.806 | 4.006 | 4.006 | 0.13629 | 0.29955 | 10.6667 | 10.7334 | 11.8689 | 50.4046 | 0.21294 | 5.734 | 6.395 | 84.3875 | 1062.1975 | 1496.7882 | 1480.3629 | 1.0974 | 71.822 | 1271.2802 | 93.362
[11 empty] | 1999-02-21 | 23:00 | 6176.0003 | 28.734 | 140.13 | 62.865 | 18.583 | 0 | 14.958 | 2.868 |  | 17.826 | 17.826 | 0.83911 | 0 | 13.5982 | 13.7055 | 9.5329 | 73.3816 | 0.18677 | 7.293 | 5.694 | 36.1665 | 313.008 | 300.4022 | 1471.1744 | 1678.5188 | -14.0938 | 87.9606 | 989.4605 | 96.3448 | 140.13 | 116.062 | 18.583 | 9.427 | 7.95 | 17.377 | 17.377 | 0.33782 | 0.5425 | 14.3195 | 14.4325 | 4.503 | 105.01 | 0.13744 | 5.694 | 5.694 | 17.706 | 300.4022 | 577.8 | 635.6195 | -10.0068 | 94.1059 | 468.0109 | 96.2168 | 116.062 | 99.862 | 18.583 | 4.24 | 3.71 | 7.95 | 7.95 | 0.31105 | 0.53333 | 12.881 | 12.9827 | 9.0271 | 80.3519 | 0.16157 | 5.694 | 5.694 | 3.346 | 577.8 | 1067.43 | 1234.3188 | -15.6346 | 98.8861 | 906.0594 | 99.6307 | 99.862 | 62.865 | 18.583 | 1.291 | 2.868 | 4.159 | 4.159 | 0.14059 | 0.31041 | 11.4756 | 11.5661 | 12.052 | 50.7285 | 0.228 | 5.694 | 6.095 | 83.6506 | 1067.43 | 1471.1744 | 1510.268 | -2.6573 | 72.1538 | 1288.849 | 93.5097
[11 empty] | 1999-02-22 | 7:00 | 6184 | 28.641 | 139.615 | 63.63 | 18.618 | 0 | 14.965 | 2.868 |  | 17.833 | 17.833 | 0.83917 | 0 | 13.6045 | 13.7497 | 9.6267 | 73.3778 | 0.18738 | 7.395 | 5.621 | 34.31 | 314.16 | 301.055 | 1424.2154 | 1692.9098 | -18.8661 | 88.6034 | 996.9824 | 96.5586 | 139.615 | 115.92 | 18.618 | 9.429 | 8.079 | 17.508 | 17.508 | 0.34128 | 0.53855 | 14.3225 | 14.4753 | 4.5009 | 104.6486 | 0.13832 | 5.621 | 5.621 | 16.8285 | 301.055 | 576 | 632.7758 | -9.8569 | 94.4102 | 466.9154 | 96.3958 | 115.92 | 100.2 | 18.618 | 4.254 | 3.825 | 8.079 | 8.079 | 0.31756 | 0.52655 | 12.9235 | 13.0614 | 8.911 | 80.531 | 0.16219 | 5.621 | 5.621 | 3.341 | 576 | 1077.44 | 1212.8867 | -12.5712 | 98.8902 | 894.4433 | 99.6265 | 100.2 | 63.63 | 18.618 | 1.282 | 2.868 | 4.15 | 4.15 | 0.14041 | 0.30892 | 11.3956 | 11.5171 | 12.1761 | 51.1209 | 0.22529 | 5.621 | 5.145 | 82.2506 | 1077.44 | 1424.2154 | 1522.2911 | -6.8863 | 72.6792 | 1299.8655 | 93.6724
[11 empty] | 1999-02-22 | 16:00 | 6193 | 28.768 | 138.181 | 57.982 | 17.448 | 0 | 13.886 | 3.105 |  | 16.991 | 16.991 | 0.81726 | 0 | 12.6236 | 12.7105 | 8.5876 | 72.0459 | 0.17642 | 7.299 | 5.707 | 34.6625 | 311.52 | 300.035 | 1452.2684 | 1486.8186 | -2.3791 | 88.4472 | 893.4268 | 96.1203 | 138.181 | 114.345 | 17.448 | 8.35 | 9.387 | 17.737 | 17.737 | 0.36178 | 0.47077 | 12.6835 | 12.7708 | 4.0866 | 104.7284 | 0.12194 | 5.707 | 5.707 | 17.1795 | 300.035 | 567 | 551.643 | 2.7085 | 94.2742 | 425.839 | 95.9657 | 114.345 | 98.767 | 17.448 | 4.24 | 5.147 | 9.387 | 9.387 | 0.38771 | 0.45169 | 12.881 | 12.9696 | 7.9586 | 81.1494 | 0.15982 | 5.707 | 5.707 | 3.3127 | 567 | 1025.115 | 1031.3548 | -0.60869 | 98.8959 | 799.1774 | 99.5855 | 98.767 | 57.982 | 17.448 | 1.296 | 3.105 | 4.401 | 4.401 | 0.15017 | 0.29448 | 11.52 | 11.5993 | 11.3974 | 49.5291 | 0.23419 | 5.707 | 6.202 | 82.1632 | 1025.115 | 1452.2684 | 1418.6949 | 2.3118 | 72.6155 | 1221.9049 | 93.2758
[11 empty] | 1999-02-23 | 0:00 | 6201 | 28.696 | 137.986 | 58.44 | 17.568 | 0 | 13.957 | 3.047 |  | 17.004 | 17.004 | 0.82081 | 0 | 12.6882 | 12.8027 | 8.7692 | 71.8758 | 0.17812 | 7.251 | 5.651 | 33.981 | 313.392 | 300.5002 | 1435.8028 | 1521.3101 | -5.9554 | 88.6919 | 910.9051 | 96.2695 | 137.986 | 114.795 | 17.568 | 8.407 | 9.398 | 17.805 | 17.805 | 0.36284 | 0.47217 | 12.7701 | 12.8854 | 4.1041 | 104.7184 | 0.12305 | 5.651 | 5.651 | 16.926 | 300.5002 | 568.35 | 554.172 | 2.4946 | 94.3674 | 427.3361 | 96.0392 | 114.795 | 99.412 | 17.568 | 4.254 | 5.144 | 9.398 | 9.398 | 0.38793 | 0.45265 | 12.9235 | 13.0402 | 7.9867 | 81.5488 | 0.15991 | 5.651 | 5.651 | 3.3168 | 568.35 | 1030.3475 | 1035.6228 | -0.51199 | 98.8962 | 801.9864 | 99.5864 | 99.412 | 58.44 | 17.568 | 1.296 | 3.047 | 4.343 | 4.343 | 0.14785 | 0.29841 | 11.52 | 11.624 | 11.5006 | 49.8574 | 0.23314 | 5.651 | 5.675 | 81.9795 | 1030.3475 | 1435.8028 | 1433.7229 | 0.14486 | 72.719 | 1232.0352 | 93.346
[11 empty] | 1999-02-23 | 8:00 | 6209 | 28.717 | 137.584 | 58.74 | 17.557 | 0 | 13.9 | 3.106 |  | 17.006 | 17.006 | 0.81736 | 0 | 12.6364 | 12.7425 | 8.6565 | 71.9485 | 0.17711 | 7.239 | 5.632 | 33.135 | 311.76 | 300.5083 | 1414.4576 | 1497.0599 | -5.8399 | 88.9737 | 898.7841 | 96.3134 | 137.584 | 114.592 | 17.557 | 8.354 | 9.388 | 17.742 | 17.742 | 0.36186 | 0.47086 | 12.6896 | 12.7962 | 4.1026 | 104.4284 | 0.12254 | 5.632 | 5.632 | 16.575 | 300.5083 | 568.35 | 553.1691 | 2.6711 | 94.4843 | 426.8387 | 96.1168 | 114.592 | 99.547 | 17.557 | 4.254 | 5.134 | 9.388 | 9.388 | 0.38739 | 0.45313 | 12.9235 | 13.0321 | 7.9912 | 81.5213 | 0.15986 | 5.632 | 5.632 | 3.3184 | 568.35 | 1034.4425 | 1036.5316 | -0.20195 | 98.8957 | 802.4408 | 99.5865 | 99.547 | 58.74 | 17.557 | 1.292 | 3.106 | 4.398 | 4.398 | 0.15013 | 0.29377 | 11.4844 | 11.5809 | 11.5142 | 50.0723 | 0.23128 | 5.632 | 5.237 | 81.2717 | 1034.4425 | 1414.4576 | 1430.9321 | -1.1647 | 72.9553 | 1232.6873 | 93.407
[11 empty] | 1999-02-23 | 16:00 | 6217.0003 | 28.777 | 137.497 | 58.972 | 17.58 | 0 | 13.909 | 3.165 |  | 17.074 | 17.074 | 0.81463 | 0 | 12.6445 | 12.7282 | 8.4953 | 72.1592 | 0.17639 | 7.182 | 5.715 | 33.9575 | 309.936 | 299.6597 | 1444.3407 | 1467.3221 | -1.5911 | 88.668 | 883.4909 | 96.1564 | 137.497 | 114.892 | 17.58 | 8.352 | 9.384 | 17.736 | 17.736 | 0.36173 | 0.47091 | 12.6866 | 12.7705 | 4.0847 | 104.5298 | 0.12217 | 5.715 | 5.715 | 16.9845 | 299.6597 | 560.7 | 551.2478 | 1.6858 | 94.3321 | 425.4537 | 96.0079 | 114.892 | 100.005 | 17.58 | 4.266 | 5.118 | 9.384 | 9.384 | 0.38686 | 0.4546 | 12.96 | 13.0457 | 7.8969 | 81.9716 | 0.15915 | 5.715 | 5.715 | 3.3099 | 560.7 | 1011.01 | 1025.3007 | -1.4135 | 98.8955 | 793.0003 | 99.5826 | 100.005 | 58.972 | 17.58 | 1.291 | 3.165 | 4.456 | 4.456 | 0.15248 | 0.28972 | 11.4756 | 11.5514 | 11.1898 | 50.7187 | 0.22776 | 5.715 | 6.283 | 81.5853 | 1011.01 | 1444.3407 | 1390.1213 | 3.7539 | 72.774 | 1200.5657 | 93.2044
[11 empty] | 1999-02-24 | 0:00 | 6225 | 28.721 | 137.31 | 59.01 | 17.62 | 0 | 13.968 | 3.166 |  | 17.134 | 17.134 | 0.81522 | 0 | 12.6982 | 12.8033 | 8.5353 | 72.0047 | 0.17781 | 7.101 | 5.695 | 33.7695 | 311.28 | 300.0024 | 1440.6817 | 1474.589 | -2.3536 | 88.7436 | 887.2957 | 96.1941 | 137.31 | 114.99 | 17.62 | 8.405 | 9.395 | 17.8 | 17.8 | 0.36273 | 0.47219 | 12.7671 | 12.8728 | 4.0945 | 104.4355 | 0.12326 | 5.695 | 5.695 | 17.1015 | 300.0024 | 562.5 | 553.0926 | 1.6724 | 94.2995 | 426.5475 | 95.9907 | 114.99 | 100.275 | 17.62 | 4.267 | 5.128 | 9.395 | 9.395 | 0.38742 | 0.45418 | 12.963 | 13.0704 | 7.9184 | 82.0941 | 0.15921 | 5.695 | 5.695 | 3.3126 | 562.5 | 1020.7925 | 1027.7989 | -0.68637 | 98.8958 | 795.1495 | 99.5834 | 100.275 | 59.01 | 17.62 | 1.296 | 3.166 | 4.462 | 4.462 | 0.15262 | 0.29045 | 11.52 | 11.6154 | 11.3118 | 50.7107 | 0.22905 | 5.695 | 6.187 | 81.8026 | 1020.7925 | 1440.6817 | 1405.1674 | 2.4651 | 72.7327 | 1212.98 | 93.2561
[11 empty] | 1999-02-24 | 8:00 | 6233 | 28.811 | 139.347 | 54.637 | 17.724 | 0 | 14.097 | 3.525 |  | 17.622 | 17.622 | 0.79997 | 0 | 12.8155 | 12.8872 | 7.9895 | 71.2785 | 0.1808 | 7.158 | 5.688 | 33.3465 | 307.776 | 299.7005 | 1418.7269 | 1364.8897 | 3.7948 | 88.8734 | 832.2951 | 95.9934 | 139.347 | 116.632 | 17.724 | 8.534 | 9.566 | 18.1 | 18.1 | 0.36901 | 0.47149 | 12.963 | 13.0357 | 4.0919 | 106.1736 | 0.12278 | 5.688 | 5.688 | 16.731 | 299.7005 | 553.95 | 552.1426 | 0.32627 | 94.4174 | 425.9216 | 96.0718 | 116.632 | 100.927 | 17.724 | 4.267 | 5.299 | 9.566 | 9.566 | 0.39654 | 0.44606 | 12.963 | 13.0357 | 7.7238 | 83.3317 | 0.15643 | 5.688 | 5.688 | 3.285 | 553.95 | 988.9425 | 997.371 | -0.85227 | 98.9039 | 775.6605 | 99.5765 | 100.927 | 54.637 | 17.724 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5845 | 10.7439 | 49.3141 | 0.23491 | 5.688 | 6.054 | 81.3904 | 988.9425 | 1418.7269 | 1322.6127 | 6.7747 | 72.8428 | 1155.7776 | 92.958
[11 empty] | 1999-02-24 | 16:52 | 6241.8722 | 28.777 | 139.065 | 54.577 | 17.715 | 0 | 14.086 | 3.524 |  | 17.61 | 17.61 | 0.79989 | 0 | 12.8055 | 12.8901 | 7.9818 | 71.1242 | 0.18123 | 6.912 | 5.734 | 33.229 | 308.4 | 299.4149 | 1426.045 | 1363.403 | 4.3927 | 88.902 | 831.409 | 96.0033 | 139.065 | 116.512 | 17.715 | 8.533 | 9.681 | 18.214 | 18.214 | 0.37207 | 0.46849 | 12.9615 | 13.0472 | 4.0771 | 105.9964 | 0.12309 | 5.734 | 5.734 | 16.419 | 299.4149 | 545.85 | 548.8523 | -0.55003 | 94.5163 | 424.1336 | 96.1288 | 116.512 | 100.845 | 17.715 | 4.266 | 5.415 | 9.681 | 9.681 | 0.40271 | 0.44066 | 12.96 | 13.0457 | 7.5629 | 83.4006 | 0.15642 | 5.734 | 5.734 | 3.2826 | 545.85 | 983.9375 | 973.2909 | 1.082 | 98.9037 | 759.5705 | 99.5678 | 100.845 | 54.577 | 17.715 | 1.287 | 3.524 | 4.811 | 4.811 | 0.16676 | 0.26751 | 11.44 | 11.5157 | 10.6726 | 49.3234 | 0.23347 | 5.734 | 6.498 | 81.4755 | 983.9375 | 1426.045 | 1313.5256 | 7.8903 | 72.7884 | 1148.7316 | 92.9073
[11 empty] | 1999-02-25 | 0:00 | 6249 | 28.751 | 139.347 | 54.832 | 17.791 | 0 | 14.093 | 3.585 |  | 17.678 | 17.678 | 0.79721 | 0 | 12.8118 | 12.9065 | 7.9064 | 71.3921 | 0.18078 | 7.098 | 5.716 | 32.9705 | 311.328 | 299.5781 | 1419.9467 | 1347.6396 | 5.0922 | 88.9944 | 823.6089 | 95.9968 | 139.347 | 116.902 | 17.791 | 8.53 | 9.696 | 18.226 | 18.226 | 0.37243 | 0.46801 | 12.957 | 13.0527 | 4.0718 | 106.2617 | 0.12284 | 5.716 | 5.716 | 16.7895 | 299.5781 | 554.85 | 548.3597 | 1.1697 | 94.3956 | 423.9689 | 96.0399 | 116.902 | 101.212 | 17.791 | 4.267 | 5.429 | 9.696 | 9.696 | 0.40348 | 0.44008 | 12.963 | 13.0588 | 7.6832 | 83.5828 | 0.15624 | 5.716 | 5.716 | 3.2833 | 554.85 | 989.17 | 988.3617 | 0.081713 | 98.904 | 771.6059 | 99.5745 | 101.212 | 54.832 | 17.791 | 1.296 | 3.585 | 4.881 | 4.881 | 0.16938 | 0.26552 | 11.52 | 11.6051 | 10.7165 | 49.5145 | 0.23438 | 5.716 | 6.427 | 81.5674 | 989.17 | 1419.9467 | 1317.2741 | 7.2307 | 72.7726 | 1153.222 | 92.927
[11 empty] | 1999-02-25 | 8:00 | 6257.0003 | 28.789 | 139.159 | 54.585 | 17.815 | 0 | 14.168 | 3.525 |  | 17.693 | 17.693 | 0.80077 | 0 | 12.88 | 12.9606 | 8.0255 | 71.0315 | 0.18246 | 7.097 | 5.71 | 32.8765 | 308.64 | 299.5373 | 1418.1167 | 1371.3245 | 3.2996 | 89.0242 | 835.4309 | 96.0647 | 139.159 | 116.872 | 17.815 | 8.592 | 9.633 | 18.225 | 18.225 | 0.37157 | 0.47144 | 13.0511 | 13.1328 | 4.0898 | 106.1107 | 0.12377 | 5.71 | 5.71 | 16.692 | 299.5373 | 553.95 | 551.8166 | 0.38513 | 94.4274 | 425.6769 | 96.0787 | 116.872 | 101.077 | 17.815 | 4.28 | 5.353 | 9.633 | 9.633 | 0.39977 | 0.44431 | 13.0025 | 13.0839 | 7.7081 | 83.4514 | 0.15678 | 5.71 | 5.71 | 3.2848 | 553.95 | 992.1275 | 994.2353 | -0.21245 | 98.9034 | 774.0926 | 99.5757 | 101.077 | 54.585 | 17.815 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5921 | 10.779 | 49.237 | 0.23543 | 5.71 | 6.303 | 81.6099 | 992.1275 | 1418.1167 | 1326.888 | 6.4331 | 72.7547 | 1159.5078 | 92.9617
[11 empty] | 1999-02-25 | 16:00 | 6265 | 28.828 | 138.857 | 54.667 | 17.779 | 0 | 14.095 | 3.524 |  | 17.619 | 17.619 | 0.79999 | 0 | 12.8136 | 12.8789 | 7.9866 | 70.9964 | 0.1814 | 7.094 | 5.731 | 33.1585 | 308.304 | 299.3904 | 1425.4353 | 1364.2425 | 4.2929 | 88.9247 | 831.8164 | 96.0137 | 138.857 | 116.707 | 17.779 | 8.533 | 9.684 | 18.217 | 18.217 | 0.37215 | 0.46841 | 12.9615 | 13.0276 | 4.0722 | 105.9308 | 0.12298 | 5.731 | 5.731 | 16.7115 | 299.3904 | 557.1 | 548.4713 | 1.5489 | 94.4182 | 423.9308 | 96.058 | 116.707 | 100.927 | 17.779 | 4.28 | 5.404 | 9.684 | 9.684 | 0.40249 | 0.44197 | 13.0025 | 13.0688 | 7.7313 | 83.3067 | 0.15688 | 5.731 | 5.731 | 3.2824 | 557.1 | 983.255 | 995.7268 | -1.2684 | 98.9036 | 776.4134 | 99.5772 | 100.927 | 54.667 | 17.779 | 1.282 | 3.524 | 4.806 | 4.806 | 0.16666 | 0.26675 | 11.3956 | 11.4536 | 10.6582 | 49.3598 | 0.23204 | 5.731 | 6.448 | 81.4666 | 983.255 | 1425.4353 | 1311.3177 | 8.0058 | 72.7892 | 1147.2863 | 92.8992
[11 empty] | 1999-02-26 | 0:00 | 6273 | 28.73 | 139.293 | 54.862 | 17.833 | 0 | 14.164 | 3.586 |  | 17.75 | 17.75 | 0.79797 | 0 | 12.8764 | 12.9795 | 7.932 | 71.3125 | 0.18201 | 7.075 | 5.714 | 32.9705 | 311.376 | 299.6026 | 1415.0678 | 1352.7471 | 4.4041 | 88.9953 | 826.1749 | 96.0093 | 139.293 | 117.247 | 17.833 | 8.593 | 9.572 | 18.165 | 18.165 | 0.36996 | 0.47305 | 13.0527 | 13.1572 | 4.097 | 106.34 | 0.12373 | 5.714 | 5.714 | 16.8285 | 299.6026 | 555.3 | 553.4552 | 0.33222 | 94.3831 | 426.5289 | 96.0545 | 117.247 | 101.595 | 17.833 | 4.28 | 5.292 | 9.572 | 9.572 | 0.39652 | 0.44714 | 13.0025 | 13.1067 | 7.7524 | 83.8356 | 0.15634 | 5.714 | 5.714 | 3.285 | 555.3 | 989.17 | 1001.7521 | -1.272 | 98.9036 | 778.526 | 99.5781 | 101.595 | 54.862 | 17.833 | 1.291 | 3.586 | 4.877 | 4.877 | 0.16932 | 0.26471 | 11.4756 | 11.5675 | 10.7093 | 49.6862 | 0.23281 | 5.714 | 6.377 | 81.6077 | 989.17 | 1415.0678 | 1315.9026 | 7.0078 | 72.7614 | 1152.5363 | 92.9193
[11 empty] | 1999-02-26 | 8:00 | 6281.0003 | 28.828 | 138.677 | 54.622 | 17.754 | 0 | 14.168 | 3.526 |  | 17.694 | 17.694 | 0.80072 | 0 | 12.88 | 12.9457 | 8.0069 | 70.8886 | 0.18262 | 7.045 | 5.711 | 33.2995 | 307.776 | 299.3904 | 1418.1167 | 1368.5838 | 3.4929 | 88.8776 | 833.9871 | 96.0072 | 138.677 | 116.722 | 17.754 | 8.592 | 9.57 | 18.162 | 18.162 | 0.36989 | 0.47308 | 13.0511 | 13.1177 | 4.0963 | 105.8492 | 0.12393 | 5.711 | 5.711 | 16.6725 | 299.3904 | 553.95 | 553.2161 | 0.13248 | 94.4312 | 426.3033 | 96.0891 | 116.722 | 100.98 | 17.754 | 4.28 | 5.29 | 9.57 | 9.57 | 0.39641 | 0.44723 | 13.0025 | 13.0688 | 7.7343 | 83.3627 | 0.15677 | 5.711 | 5.711 | 3.2848 | 553.95 | 988.26 | 999.4788 | -1.1352 | 98.9028 | 776.7144 | 99.5771 | 100.98 | 54.622 | 17.754 | 1.296 | 3.526 | 4.822 | 4.822 | 0.16702 | 0.26877 | 11.52 | 11.5787 | 10.7327 | 49.3143 | 0.23479 | 5.711 | 6.192 | 81.6077 | 988.26 | 1418.1167 | 1321.5049 | 6.8127 | 72.7421 | 1154.8824 | 92.9337
[11 empty] | 1999-02-26 | 16:00 | 6289.0003 | 28.734 | 138.784 | 54.6 | 17.841 | 0 | 14.164 | 3.584 |  | 17.748 | 17.748 | 0.79806 | 0 | 12.8764 | 12.978 | 7.926 | 70.925 | 0.18298 | 6.685 | 5.723 | 33.2055 | 308.352 | 299.5373 | 1424.8251 | 1352.0829 | 5.1053 | 88.9144 | 825.8101 | 95.979 | 138.784 | 116.812 | 17.841 | 8.592 | 9.741 | 18.333 | 18.333 | 0.37446 | 0.46866 | 13.0511 | 13.1542 | 4.0759 | 105.8811 | 0.12424 | 5.723 | 5.723 | 16.692 | 299.5373 | 557.1 | 549.0195 | 1.4505 | 94.4274 | 424.2784 | 96.0658 | 116.812 | 100.995 | 17.841 | 4.28 | 5.461 | 9.741 | 9.741 | 0.40553 | 0.43938 | 13.0025 | 13.1052 | 7.7084 | 83.3541 | 0.15722 | 5.723 | 5.723 | 3.2839 | 557.1 | 987.1225 | 991.1474 | -0.40774 | 98.9037 | 774.1237 | 99.5758 | 100.995 | 54.6 | 17.841 | 1.292 | 3.584 | 4.876 | 4.876 | 0.16926 | 0.26497 | 11.4844 | 11.5751 | 10.688 | 49.2685 | 0.23494 | 5.723 | 6.372 | 81.5472 | 987.1225 | 1424.8251 | 1313.5743 | 7.808 | 72.7756 | 1150.3484 | 92.9111
[11 empty] | 1999-02-27 | 0:00 | 6297 | 28.772 | 139.119 | 54.885 | 17.901 | 0 | 14.168 | 3.525 |  | 17.693 | 17.693 | 0.80077 | 0 | 12.88 | 12.9671 | 8.0235 | 71.0775 | 0.18244 | 7.029 | 5.711 | 33.0175 | 310.608 | 299.6107 | 1420.5564 | 1371.1264 | 3.4796 | 88.9799 | 835.3686 | 96.0476 | 139.119 | 117.337 | 17.901 | 8.592 | 9.747 | 18.339 | 18.339 | 0.37462 | 0.46851 | 13.0511 | 13.1394 | 4.0739 | 106.2531 | 0.12366 | 5.711 | 5.711 | 16.848 | 299.6107 | 555.3 | 548.8666 | 1.1585 | 94.3767 | 424.2387 | 96.0287 | 117.337 | 101.437 | 17.901 | 4.28 | 5.467 | 9.747 | 9.747 | 0.40585 | 0.43911 | 13.0025 | 13.0905 | 7.681 | 83.805 | 0.1562 | 5.711 | 5.711 | 3.2835 | 555.3 | 989.625 | 987.4622 | 0.21855 | 98.9041 | 771.3811 | 99.5743 | 101.437 | 54.885 | 17.901 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5979 | 10.7503 | 49.5097 | 0.23426 | 5.711 | 6.291 | 81.5315 | 989.625 | 1420.5564 | 1323.4943 | 6.8327 | 72.7875 | 1156.5596 | 92.9505
[11 empty] | 1999-02-27 | 8:00 | 6305 | 28.862 | 138.295 | 54.607 | 17.797 | 0 | 14.115 | 3.525 |  | 17.64 | 17.64 | 0.80017 | 0 | 12.8318 | 12.8843 | 7.9819 | 70.6721 | 0.18231 | 7.013 | 5.708 | 33.417 | 306.24 | 299.2925 | 1420.5564 | 1363.9258 | 3.9865 | 88.8347 | 831.6091 | 95.9816 | 138.295 | 116.52 | 17.797 | 8.534 | 9.803 | 18.337 | 18.337 | 0.37534 | 0.4654 | 12.963 | 13.016 | 4.0547 | 105.5558 | 0.12331 | 5.708 | 5.708 | 16.7895 | 299.2925 | 554.85 | 545.2254 | 1.7346 | 94.3903 | 422.2589 | 96.0239 | 116.52 | 100.935 | 17.797 | 4.28 | 5.523 | 9.803 | 9.803 | 0.40884 | 0.4366 | 13.0025 | 13.0557 | 7.6528 | 83.2777 | 0.15677 | 5.708 | 5.708 | 3.2831 | 554.85 | 985.3025 | 982.2819 | 0.30657 | 98.903 | 768.5659 | 99.5728 | 100.935 | 54.607 | 17.797 | 1.301 | 3.525 | 4.826 | 4.826 | 0.16708 | 0.26958 | 11.5644 | 11.6117 | 10.705 | 49.269 | 0.23568 | 5.708 | 6.245 | 81.5786 | 985.3025 | 1420.5564 | 1318.8471 | 7.1598 | 72.7429 | 1152.0748 | 92.919
[11 empty] | 1999-02-27 | 16:00 | 6313 | 28.836 | 138.221 | 54.592 | 17.851 | 0 | 14.11 | 3.464 |  | 17.574 | 17.574 | 0.80289 | 0 | 12.8273 | 12.8896 | 8.0778 | 70.4777 | 0.18289 | 7.063 | 5.723 | 33.276 | 307.584 | 299.2843 | 1427.2648 | 1382.8228 | 3.1138 | 88.8815 | 841.0536 | 96.0435 | 138.221 | 116.662 | 17.851 | 8.534 | 9.688 | 18.222 | 18.222 | 0.37227 | 0.46833 | 12.963 | 13.026 | 4.0692 | 105.5213 | 0.12344 | 5.723 | 5.723 | 16.7895 | 299.2843 | 553.5 | 548.1294 | 0.9703 | 94.3901 | 423.7068 | 96.0375 | 116.662 | 100.89 | 17.851 | 4.28 | 5.408 | 9.688 | 9.688 | 0.40271 | 0.44178 | 13.0025 | 13.0657 | 7.6795 | 83.2455 | 0.15695 | 5.723 | 5.723 | 3.281 | 553.5 | 979.8425 | 988.9544 | -0.92993 | 98.9037 | 771.2272 | 99.5746 | 100.89 | 54.592 | 17.851 | 1.296 | 3.464 | 4.76 | 4.76 | 0.16454 | 0.27227 | 11.52 | 11.576 | 10.6642 | 49.2258 | 0.23516 | 5.723 | 6.413 | 81.4755 | 979.8425 | 1427.2648 | 1315.9521 | 7.799 | 72.7765 | 1147.8973 | 92.9022
[11 empty] | 1999-02-28 | 0:00 | 6321 | 28.794 | 138.509 | 54.63 | 17.866 | 0 | 14.165 | 3.525 |  | 17.69 | 17.69 | 0.80073 | 0 | 12.8773 | 12.9559 | 8.0154 | 70.6881 | 0.18328 | 7.031 | 5.707 | 33.1585 | 309.168 | 299.521 | 1423.6058 | 1369.8824 | 3.7738 | 88.9295 | 834.7017 | 96.0275 | 138.509 | 116.842 | 17.866 | 8.594 | 9.568 | 18.162 | 18.162 | 0.36987 | 0.47319 | 13.0542 | 13.1339 | 4.0937 | 105.7158 | 0.12424 | 5.707 | 5.707 | 17.0235 | 299.521 | 556.65 | 553.2608 | 0.60885 | 94.3164 | 426.3909 | 96.0075 | 116.842 | 101.055 | 17.866 | 4.28 | 5.288 | 9.568 | 9.568 | 0.3963 | 0.44732 | 13.0025 | 13.0819 | 7.7731 | 83.3094 | 0.15703 | 5.707 | 5.707 | 3.2823 | 556.65 | 987.1225 | 1004.5346 | -1.7639 | 98.9042 | 780.5923 | 99.5795 | 101.055 | 54.63 | 17.866 | 1.291 | 3.525 | 4.816 | 4.816 | 0.16688 | 0.26806 | 11.4756 | 11.5456 | 10.7141 | 49.2624 | 0.23437 | 5.707 | 6.322 | 81.545 | 987.1225 | 1423.6058 | 1318.7822 | 7.3632 | 72.7749 | 1152.9524 | 92.9273
[11 empty] | 1999-02-28 | 8:00 | 6329 | 28.896 | 138.147 | 54.51 | 17.803 | 0 | 14.17 | 3.525 |  | 17.695 | 17.695 | 0.80079 | 0 | 12.8818 | 12.9215 | 7.9918 | 70.5337 | 0.1832 | 7.017 | 5.731 | 33.558 | 305.712 | 299.0722 | 1424.2154 | 1366.4014 | 4.0594 | 88.7793 | 832.7368 | 95.9702 | 138.147 | 116.67 | 17.803 | 8.594 | 9.629 | 18.223 | 18.223 | 0.37149 | 0.4716 | 13.0542 | 13.0944 | 4.08 | 105.5255 | 0.12409 | 5.731 | 5.731 | 16.965 | 299.0722 | 552.15 | 550.8562 | 0.23431 | 94.3275 | 424.9642 | 96.0079 | 116.67 | 100.837 | 17.803 | 4.28 | 5.349 | 9.629 | 9.629 | 0.39956 | 0.44449 | 13.0025 | 13.0426 | 7.6846 | 83.2659 | 0.15664 | 5.731 | 5.731 | 3.2824 | 552.15 | 982.8 | 991.3262 | -0.86754 | 98.9025 | 771.7381 | 99.5747 | 100.837 | 54.51 | 17.803 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5555 | 10.6692 | 49.2013 | 0.23486 | 5.731 | 6.326 | 81.5517 | 982.8 | 1424.2154 | 1314.1526 | 7.728 | 72.7318 | 1148.4763 | 92.8991
[11 empty] | 1999-02-28 | 16:00 | 6337 | 28.883 | 138 | 54.525 | 17.826 | 0 | 14.093 | 3.464 |  | 17.557 | 17.557 | 0.8027 | 0 | 12.8118 | 12.8562 | 8.0603 | 70.3762 | 0.18268 | 7.006 | 5.754 | 33.417 | 307.008 | 299.064 | 1430.3137 | 1379.827 | 3.5298 | 88.8261 | 839.4455 | 96.0192 | 138 | 116.317 | 17.826 | 8.535 | 9.622 | 18.157 | 18.157 | 0.37052 | 0.47007 | 12.9646 | 13.0095 | 4.0719 | 105.2606 | 0.12359 | 5.754 | 5.754 | 16.9845 | 299.064 | 551.25 | 549.2769 | 0.35793 | 94.3208 | 424.1705 | 95.9958 | 116.317 | 100.672 | 17.826 | 4.266 | 5.356 | 9.622 | 9.622 | 0.39956 | 0.44336 | 12.96 | 13.0049 | 7.662 | 83.0065 | 0.15667 | 5.754 | 5.754 | 3.2798 | 551.25 | 977.5675 | 987.7027 | -1.0368 | 98.9033 | 769.4764 | 99.5738 | 100.672 | 54.525 | 17.826 | 1.292 | 3.464 | 4.756 | 4.756 | 0.16446 | 0.27166 | 11.4844 | 11.5242 | 10.6319 | 49.1406 | 0.23452 | 5.754 | 6.495 | 81.489 | 977.5675 | 1430.3137 | 1311.7862 | 8.2868 | 72.752 | 1144.6768 | 92.8811
[11 empty] | 1999-03-01 | 0:00 | 6345 | 28.772 | 138.281 | 54.697 | 17.802 | 0 | 14.173 | 3.464 |  | 17.637 | 17.637 | 0.80359 | 0 | 12.8845 | 12.9717 | 8.1146 | 70.5724 | 0.18381 | 6.952 | 5.746 | 33.041 | 309.792 | 299.4638 | 1410.7986 | 1389.5363 | 1.5071 | 88.9666 | 844.5001 | 96.0875 | 138.281 | 116.707 | 17.802 | 8.592 | 9.447 | 18.039 | 18.039 | 0.036661 | 0.4763 | 13.0511 | 13.1394 | 4.1113 | 105.5807 | 0.12445 | 5.746 | 5.746 | 16.848 | 299.4638 | 555.75 | 556.5016 | -0.13523 | 94.3739 | 427.9827 | 96.0634 | 116.707 | 101.1 | 17.802 | 4.28 | 5.167 | 9.447 | 9.447 | 0.038985 | 0.45305 | 13.0025 | 13.0905 | 7.8128 | 83.2887 | 0.15717 | 5.746 | 5.746 | 3.2819 | 555.75 | 985.985 | 1013.3779 | -2.7782 | 98.9041 | 784.564 | 99.5817 | 101.1 | 54.697 | 17.802 | 1.301 | 3.464 | 4.765 | 4.765 | 0.16464 | 0.27303 | 11.5644 | 11.6426 | 10.742 | 49.3545 | 0.2359 | 5.746 | 6.404 | 81.6122 | 985.985 | 1410.7986 | 1325.647 | 6.0357 | 72.7472 | 1155.816 | 92.939
[11 empty] | 1999-03-01 | 9:47 | 6354.7783 | 28.828 | 138.241 | 54.547 | 17.854 | 0 | 14.112 | 3.524 |  | 17.636 | 17.636 | 0.80018 | 0 | 12.8291 | 12.8945 | 7.9872 | 70.5528 | 0.18276 | 6.996 | 5.74 | 33.229 | 308.448 | 299.268 | 1426.045 | 1364.6319 | 4.3065 | 88.8966 | 831.9499 | 96.0059 | 138.241 | 116.7 | 17.854 | 8.536 | 9.561 | 18.097 | 18.097 | 0.036891 | 0.47168 | 12.9661 | 13.0322 | 4.0869 | 105.5296 | 0.12349 | 5.74 | 5.74 | 16.7115 | 299.268 | 553.5 | 551.5326 | 0.35544 | 94.4159 | 425.4003 | 96.0716 | 116.7 | 101.04 | 17.854 | 4.28 | 5.281 | 9.561 | 9.561 | 0.039593 | 0.44765 | 13.0025 | 13.0688 | 7.7318 | 83.2842 | 0.15692 | 5.74 | 5.74 | 3.2809 | 553.5 | 980.07 | 999.4265 | -1.975 | 98.9037 | 776.4632 | 99.5775 | 101.04 | 54.547 | 17.854 | 1.296 | 3.524 | 4.82 | 4.82 | 0.16694 | 0.26888 | 11.52 | 11.5787 | 10.6378 | 49.3017 | 0.23485 | 5.74 | 6.415 | 81.5203 | 980.07 | 1426.045 | 1310.5241 | 8.1008 | 72.7601 | 1145.2971 | 92.8822
[11 empty] | 1999-03-01 | 16:00 | 6361.0003 | 28.857 | 138.12 | 54.54 | 17.83 | 0 | 14.172 | 3.525 |  | 17.697 | 17.697 | 0.80081 | 0 | 12.8836 | 12.9382 | 8.003 | 70.497 | 0.18353 | 6.765 | 5.745 | 33.276 | 307.584 | 299.1374 | 1426.045 | 1368.0136 | 4.0694 | 88.876 | 833.5755 | 96.008 | 138.12 | 116.647 | 17.83 | 8.596 | 9.501 | 18.097 | 18.097 | 0.036811 | 0.475 | 13.0572 | 13.1125 | 4.101 | 105.4525 | 0.12435 | 5.745 | 5.745 | 16.77 | 299.1374 | 553.95 | 554.6085 | -0.11887 | 94.3939 | 426.873 | 96.0714 | 116.647 | 101.01 | 17.83 | 4.28 | 5.221 | 9.501 | 9.501 | 0.039273 | 0.45048 | 13.0025 | 13.0576 | 7.7638 | 83.2347 | 0.15688 | 5.745 | 5.745 | 3.281 | 553.95 | 980.07 | 1005.3699 | -2.5814 | 98.9032 | 779.66 | 99.5792 | 101.01 | 54.54 | 17.83 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5688 | 10.6374 | 49.3076 | 0.23462 | 5.745 | 6.439 | 81.5158 | 980.07 | 1426.045 | 1310.432 | 8.1072 | 72.7497 | 1145.251 | 92.8823
[11 empty] | 1999-03-02 | 0:00 | 6369 | 28.764 | 138.744 | 54.847 | 17.805 | 0 | 14.171 | 3.526 |  | 17.697 | 17.697 | 0.80076 | 0 | 12.8827 | 12.9729 | 8.0243 | 70.9662 | 0.1828 | 6.923 | 5.718 | 32.947 | 310.752 | 299.5781 | 1408.9691 | 1371.1688 | 2.6828 | 89.0022 | 835.3735 | 96.056 | 138.744 | 117.465 | 17.805 | 8.594 | 9.572 | 18.166 | 18.166 | 0.036997 | 0.47308 | 13.0542 | 13.1456 | 4.0976 | 106.2019 | 0.12378 | 5.718 | 5.718 | 16.77 | 299.5781 | 554.4 | 553.4908 | 0.164 | 94.4021 | 426.5344 | 96.0683 | 117.465 | 101.587 | 17.805 | 4.281 | 5.291 | 9.572 | 9.572 | 0.039649 | 0.44724 | 13.0056 | 13.0966 | 7.7407 | 83.9803 | 0.15595 | 5.718 | 5.718 | 3.2848 | 554.4 | 990.99 | 1000.3127 | -0.94075 | 98.9035 | 777.3564 | 99.5774 | 101.587 | 54.847 | 17.805 | 1.296 | 3.526 | 4.822 | 4.822 | 0.16702 | 0.26877 | 11.52 | 11.6006 | 10.7651 | 49.6469 | 0.23366 | 5.718 | 6.287 | 81.6032 | 990.99 | 1408.9691 | 1325.2399 | 5.9426 | 72.7606 | 1158.115 | 92.9538
[11 empty] | 1999-03-02 | 8:00 | 6377.0003 | 28.798 | 138.127 | 54.337 | 17.82 | 0 | 14.176 | 3.526 |  | 17.702 | 17.702 | 0.80081 | 0 | 12.8873 | 12.9645 | 8.0237 | 70.3883 | 0.18418 | 6.938 | 5.687 | 32.1715 | 302.016 | 298.7213 | 1387.624 | 1370.3633 | 1.2439 | 89.2303 | 834.5423 | 96.145 | 138.127 | 116.707 | 17.82 | 8.595 | 9.685 | 18.28 | 18.28 | 0.0373 | 0.47019 | 13.0557 | 13.1339 | 4.0805 | 105.5165 | 0.12447 | 5.687 | 5.687 | 16.0875 | 298.7213 | 546.75 | 549.546 | -0.51138 | 94.6145 | 424.1336 | 96.207 | 116.707 | 100.822 | 17.82 | 4.28 | 5.405 | 9.685 | 9.685 | 0.040255 | 0.44192 | 13.0025 | 13.0804 | 7.5865 | 83.358 | 0.15692 | 5.687 | 5.687 | 3.277 | 546.75 | 969.3775 | 977.1042 | -0.79708 | 98.903 | 761.9271 | 99.5699 | 100.822 | 54.337 | 17.82 | 1.301 | 3.526 | 4.827 | 4.827 | 0.16712 | 0.26953 | 11.5644 | 11.6337 | 10.5243 | 49.2352 | 0.23629 | 5.687 | 5.856 | 80.8685 | 969.3775 | 1387.624 | 1297.2136 | 6.5155 | 72.9285 | 1133.2956 | 92.8643
[11 empty] | 1999-03-02 | 16:00 | 6385 | 28.768 | 138.811 | 54.952 | 18.22 | 0 | 14.521 | 3.525 |  | 18.046 | 18.046 | 0.80467 | 0 | 13.2009 | 13.2917 | 8.1513 | 70.5102 | 0.18851 | 6.401 | 5.731 | 31.114 | 297.312 | 297.5218 | 1371.1583 | 1394.9706 | -1.7367 | 89.5423 | 846.2462 | 96.3233 | 138.811 | 117.397 | 18.22 | 8.954 | 9.146 | 18.1 | 18.1 | 0.036341 | 0.4947 | 13.601 | 13.6946 | 4.1926 | 105.6914 | 0.12957 | 5.731 | 5.731 | 16.0485 | 297.5218 | 533.25 | 573.0861 | -7.4704 | 94.6059 | 435.3039 | 96.3133 | 117.397 | 101.632 | 18.22 | 4.28 | 4.866 | 9.146 | 9.146 | 0.037379 | 0.46796 | 13.0025 | 13.092 | 7.6307 | 83.6638 | 0.15648 | 5.731 | 5.731 | 3.2595 | 533.25 | 943.4425 | 999.4151 | -5.9328 | 98.9045 | 766.3326 | 99.5747 | 101.632 | 54.952 | 18.22 | 1.287 | 3.525 | 4.812 | 4.812 | 0.1668 | 0.26746 | 11.44 | 11.5187 | 10.2055 | 49.8665 | 0.23099 | 5.731 | 6.397 | 80.4406 | 943.4425 | 1371.1583 | 1258.53 | 8.2141 | 72.9631 | 1100.9862 | 92.6938
[11 empty] | 1999-03-03 | 0:00 | 6393 | 28.713 | 138.831 | 55.027 | 18.196 | 0 | 14.532 | 3.525 |  | 18.057 | 18.057 | 0.80478 | 0 | 13.2109 | 13.3235 | 8.1619 | 70.5711 | 0.18879 | 6.327 | 5.712 | 31.02 | 298.08 | 297.636 | 1369.9384 | 1396.7746 | -1.9589 | 89.5779 | 847.2053 | 96.3385 | 138.831 | 117.6 | 18.196 | 8.951 | 9.278 | 18.229 | 18.229 | 0.036689 | 0.49103 | 13.5965 | 13.7123 | 4.1751 | 105.8444 | 0.12955 | 5.712 | 5.712 | 15.99 | 297.636 | 532.35 | 569.3555 | -6.9513 | 94.6277 | 433.4957 | 96.3114 | 117.6 | 101.722 | 18.196 | 4.28 | 4.998 | 9.278 | 9.278 | 0.038083 | 0.46131 | 13.0025 | 13.1133 | 7.5563 | 83.9087 | 0.15628 | 5.712 | 5.712 | 3.2609 | 532.35 | 946.855 | 985.4315 | -4.0742 | 98.9044 | 758.8907 | 99.5703 | 101.722 | 55.027 | 18.196 | 1.301 | 3.525 | 4.826 | 4.826 | 0.16708 | 0.26958 | 11.5644 | 11.663 | 10.2635 | 49.915 | 0.23366 | 5.712 | 6.281 | 80.4003 | 946.855 | 1369.9384 | 1266.6444 | 7.5401 | 72.987 | 1106.7497 | 92.7355
[11 empty] | 1999-03-03 | 8:00 | 6401 | 28.768 | 138.583 | 54.735 | 18.189 | 0 | 14.52 | 3.525 |  | 18.045 | 18.045 | 0.80466 | 0 | 13.2 | 13.2908 | 8.1511 | 70.3189 | 0.18901 | 6.101 | 5.707 | 31.0435 | 296.352 | 297.4565 | 1369.9384 | 1394.8512 | -1.8185 | 89.5637 | 846.1539 | 96.3312 | 138.583 | 117.315 | 18.189 | 8.953 | 9.209 | 18.162 | 18.162 | 0.036508 | 0.49295 | 13.5995 | 13.6931 | 4.1837 | 105.5763 | 0.1297 | 5.707 | 5.707 | 15.9315 | 297.4565 | 532.35 | 571.1554 | -7.2894 | 94.6441 | 434.3059 | 96.3317 | 117.315 | 101.527 | 18.189 | 4.28 | 4.929 | 9.209 | 9.209 | 0.037715 | 0.46476 | 13.0025 | 13.092 | 7.588 | 83.644 | 0.15652 | 5.707 | 5.707 | 3.2594 | 532.35 | 942.9875 | 991.7754 | -5.1738 | 98.9043 | 762.0627 | 99.5723 | 101.527 | 54.735 | 18.189 | 1.287 | 3.525 | 4.812 | 4.812 | 0.1668 | 0.26746 | 11.44 | 11.5187 | 10.2006 | 49.7414 | 0.23157 | 5.707 | 6.295 | 80.3958 | 942.9875 | 1369.9384 | 1257.9252 | 8.1765 | 72.9722 | 1100.4564 | 92.6943
[11 empty] | 1999-03-03 | 16:00 | 6409 | 28.747 | 138.703 | 55.02 | 18.211 | 0 | 14.515 | 3.525 |  | 18.04 | 18.04 | 0.8046 | 0 | 13.1955 | 13.2945 | 8.15 | 70.5005 | 0.18857 | 6.075 | 5.72 | 31.0435 | 298.032 | 297.481 | 1369.3282 | 1394.5986 | -1.8455 | 89.5645 | 846.0398 | 96.3307 | 138.703 | 117.322 | 18.211 | 8.95 | 9.029 | 17.979 | 17.979 | 0.036024 | 0.4978 | 13.5949 | 13.697 | 4.2109 | 105.5906 | 0.12972 | 5.72 | 5.72 | 15.9315 | 297.481 | 532.35 | 576.567 | -8.306 | 94.6445 | 437.024 | 96.3545 | 117.322 | 101.527 | 18.211 | 4.293 | 4.736 | 9.029 | 9.029 | 0.03672 | 0.47547 | 13.042 | 13.1399 | 7.6889 | 83.5246 | 0.15732 | 5.72 | 5.72 | 3.2593 | 532.35 | 942.9875 | 1011.9502 | -7.3132 | 98.9044 | 772.1501 | 99.5779 | 101.527 | 55.02 | 18.211 | 1.272 | 3.525 | 4.797 | 4.797 | 0.1665 | 0.26517 | 11.3067 | 11.3915 | 10.1822 | 49.8803 | 0.22838 | 5.72 | 6.308 | 80.3981 | 942.9875 | 1369.3282 | 1254.2538 | 8.4037 | 72.9737 | 1098.6207 | 92.6819
[11 empty] | 1999-03-04 | 0:00 | 6417 | 28.687 | 138.489 | 55.035 | 18.133 | 0 | 14.513 | 3.585 |  | 18.098 | 18.098 | 0.80191 | 0 | 13.1936 | 13.3163 | 8.0728 | 70.5562 | 0.18873 | 5.975 | 5.679 | 30.926 | 299.52 | 297.8726 | 1355.9119 | 1378.5411 | -1.6689 | 89.6177 | 838.2069 | 96.3105 | 138.489 | 117.217 | 18.133 | 8.95 | 9.329 | 18.279 | 18.279 | 0.036824 | 0.48963 | 13.5949 | 13.7213 | 4.1681 | 105.5519 | 0.13 | 5.679 | 5.679 | 16.185 | 297.8726 | 535.5 | 568.1164 | -6.0908 | 94.5665 | 432.9945 | 96.2621 | 117.217 | 101.437 | 18.133 | 4.267 | 5.062 | 9.329 | 9.329 | 0.03839 | 0.45739 | 12.963 | 13.0835 | 7.5656 | 83.6284 | 0.15645 | 5.679 | 5.679 | 3.2606 | 535.5 | 949.585 | 984.1499 | -3.64 | 98.9054 | 759.8249 | 99.5709 | 101.437 | 55.035 | 18.133 | 1.296 | 3.585 | 4.881 | 4.881 | 0.16938 | 0.26552 | 11.52 | 11.6271 | 10.2622 | 49.8408 | 0.23328 | 5.679 | 6.315 | 80.4653 | 949.585 | 1355.9119 | 1263.7772 | 6.795 | 72.9867 | 1106.6811 | 92.7291
[11 empty] | 1999-03-04 | 8:00 | 6425 | 28.658 | 139.025 | 55.147 | 18.238 | 0 | 14.522 | 3.586 |  | 18.108 | 18.108 | 0.80197 | 0 | 13.2018 | 13.336 | 8.0709 | 70.7771 | 0.18842 | 6.293 | 5.674 | 31.302 | 298.56 | 298.1256 | 1365.0595 | 1378.6645 | -0.99665 | 89.5004 | 838.395 | 96.2664 | 139.025 | 117.832 | 18.238 | 8.951 | 9.275 | 18.226 | 18.226 | 0.036681 | 0.49111 | 13.5965 | 13.7346 | 4.1865 | 106.004 | 0.12957 | 5.674 | 5.674 | 15.7365 | 298.1256 | 538.2 | 570.6501 | -6.0294 | 94.7215 | 434.3879 | 96.3773 | 117.832 | 102 | 18.238 | 4.28 | 4.995 | 9.275 | 9.275 | 0.038067 | 0.46146 | 13.0025 | 13.1346 | 7.6411 | 84.0369 | 0.1563 | 5.674 | 5.674 | 3.2687 | 538.2 | 961.415 | 996.5596 | -3.6555 | 98.9036 | 767.3798 | 99.574 | 102 | 55.147 | 18.238 | 1.291 | 3.586 | 4.877 | 4.877 | 0.16932 | 0.26471 | 11.4756 | 11.5922 | 10.3929 | 49.9426 | 0.23211 | 5.674 | 5.879 | 80.6691 | 961.415 | 1365.0595 | 1278.4933 | 6.3416 | 72.9412 | 1119.9542 | 92.7971
[11 empty] | 1999-03-04 | 16:00 | 6433.0003 | 28.607 | 138.971 | 55.2 | 18.258 | 0 | 14.527 | 3.585 |  | 18.112 | 18.112 | 0.80206 | 0 | 13.2064 | 13.3607 | 8.0764 | 70.7511 | 0.18884 | 6.337 | 5.682 | 31.4195 | 301.296 | 298.3133 | 1368.1089 | 1379.8101 | -0.85528 | 89.4676 | 839.0617 | 96.2554 | 138.971 | 117.72 | 18.258 | 8.951 | 9.151 | 18.102 | 18.102 | 0.036351 | 0.49448 | 13.5965 | 13.7553 | 4.2052 | 105.8823 | 0.12991 | 5.682 | 5.682 | 15.912 | 298.3133 | 540 | 574.5425 | -6.3968 | 94.666 | 436.4279 | 96.354 | 117.72 | 102.007 | 18.258 | 4.28 | 4.871 | 9.151 | 9.151 | 0.037406 | 0.46771 | 13.0025 | 13.1545 | 7.7254 | 83.8801 | 0.15682 | 5.682 | 5.682 | 3.2659 | 540 | 958.0025 | 1011.612 | -5.596 | 98.9052 | 775.806 | 99.579 | 102.007 | 55.2 | 18.258 | 1.296 | 3.585 | 4.881 | 4.881 | 0.16938 | 0.26552 | 11.52 | 11.6546 | 10.3601 | 49.9854 | 0.23316 | 5.682 | 6.086 | 80.5907 | 958.0025 | 1368.1089 | 1275.1924 | 6.7916 | 72.9845 | 1116.5974 | 92.7825
[11 empty] | 1999-03-05 | 0:00 | 6441 | 28.7 | 139.521 | 55.275 | 18.294 | 0 | 14.511 | 3.526 |  | 18.037 | 18.037 | 0.80451 | 0 | 13.1918 | 13.3093 | 8.1582 | 70.9458 | 0.1876 | 6.44 | 5.683 | 32.9 | 311.232 | 299.7086 | 1407.7492 | 1397.7405 | 0.71098 | 89.0227 | 848.7245 | 96.1236 | 139.521 | 118.08 | 18.294 | 8.948 | 9.16 | 18.108 | 18.108 | 0.036371 | 0.49415 | 13.5919 | 13.713 | 4.2116 | 106.2949 | 0.12901 | 5.683 | 5.683 | 16.7505 | 299.7086 | 554.4 | 576.118 | -3.9174 | 94.4111 | 437.9133 | 96.1749 | 118.08 | 102.36 | 18.294 | 4.267 | 4.893 | 9.16 | 9.16 | 0.037488 | 0.46583 | 12.963 | 13.0785 | 7.9142 | 84.0118 | 0.15567 | 5.683 | 5.683 | 3.2815 | 554.4 | 988.4875 | 1035.0096 | -4.7064 | 98.9051 | 794.7048 | 99.5871 | 102.36 | 55.275 | 18.294 | 1.296 | 3.526 | 4.822 | 4.822 | 0.16702 | 0.26877 | 11.52 | 11.6226 | 10.7364 | 49.7871 | 0.23345 | 5.683 | 6.16 | 81.5226 | 988.4875 | 1407.7492 | 1321.8473 | 6.1021 | 72.7994 | 1155.1674 | 92.9428
[11 empty] | 1999-03-05 | 8:00 | 6449.0003 | 28.709 | 139.112 | 55.012 | 18.315 | 0 | 14.512 | 3.526 |  | 18.038 | 18.038 | 0.80452 | 0 | 13.1927 | 13.3067 | 8.1642 | 70.5828 | 0.18853 | 6.355 | 5.647 | 30.832 | 296.832 | 297.8237 | 1354.0824 | 1396.6845 | -3.1462 | 89.6476 | 847.2541 | 96.361 | 139.112 | 117.577 | 18.315 | 8.949 | 9.157 | 18.106 | 18.106 | 0.036364 | 0.49426 | 13.5934 | 13.7108 | 4.1999 | 105.8296 | 0.12956 | 5.647 | 5.647 | 15.6975 | 297.8237 | 534.15 | 573.5414 | -7.3746 | 94.7293 | 435.6825 | 96.397 | 117.577 | 101.887 | 18.315 | 4.281 | 4.876 | 9.157 | 9.157 | 0.037435 | 0.46751 | 13.0056 | 13.1179 | 7.6395 | 83.7775 | 0.15658 | 5.647 | 5.647 | 3.2587 | 534.15 | 945.035 | 1000.2586 | -5.8436 | 98.9058 | 767.2043 | 99.5752 | 101.887 | 55.012 | 18.315 | 1.282 | 3.526 | 4.808 | 4.808 | 0.16674 | 0.26664 | 11.3956 | 11.494 | 10.2217 | 49.9128 | 0.23028 | 5.647 | 5.836 | 80.1024 | 945.035 | 1354.0824 | 1259.5113 | 6.9841 | 73.1041 | 1102.2732 | 92.733
[11 empty] | 1999-03-05 | 16:00 | 6457 | 28.785 | 138.824 | 55.117 | 18.234 | 0 | 14.526 | 3.525 |  | 18.051 | 18.051 | 0.80472 | 0 | 13.2055 | 13.2896 | 8.1505 | 70.586 | 0.18828 | 6.423 | 5.694 | 31.913 | 301.488 | 298.2317 | 1381.5257 | 1395.6913 | -1.0254 | 89.2993 | 846.9615 | 96.2321 | 138.824 | 117.532 | 18.234 | 8.95 | 9.09 | 18.04 | 18.04 | 0.036186 | 0.49612 | 13.5949 | 13.6816 | 4.2064 | 105.7376 | 0.12939 | 5.694 | 5.694 | 16.3605 | 298.2317 | 540.9 | 575.7616 | -6.4451 | 94.5142 | 436.9966 | 96.2561 | 117.532 | 101.932 | 18.234 | 4.28 | 4.81 | 9.09 | 9.09 | 0.03708 | 0.47085 | 13.0025 | 13.0854 | 7.7683 | 83.7297 | 0.15628 | 5.694 | 5.694 | 3.2678 | 540.9 | 963.235 | 1019.292 | -5.8197 | 98.9043 | 780.096 | 99.5811 | 101.932 | 55.117 | 18.234 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5934 | 10.4461 | 49.8444 | 0.23259 | 5.694 | 6.259 | 80.8349 | 963.235 | 1381.5257 | 1287.6579 | 6.7945 | 72.8953 | 1125.4464 | 92.8175
[11 empty] | 1999-03-06 | 0:00 | 6465 | 28.768 | 138.717 | 55.155 | 18.327 | 0 | 14.519 | 3.525 |  | 18.044 | 18.044 | 0.80464 | 0 | 13.1991 | 13.2899 | 8.1448 | 70.4642 | 0.18861 | 6.322 | 5.656 | 32.2655 | 302.256 | 298.4846 | 1379.6962 | 1395.0054 | -1.1096 | 89.1902 | 846.745 | 96.1895 | 138.717 | 117.57 | 18.327 | 8.948 | 9.091 | 18.039 | 18.039 | 0.036186 | 0.49604 | 13.5919 | 13.6854 | 4.2111 | 105.6054 | 0.12959 | 5.656 | 5.656 | 16.263 | 298.4846 | 544.5 | 576.267 | -5.8342 | 94.5515 | 437.3758 | 96.2817 | 117.57 | 101.775 | 18.327 | 4.28 | 4.811 | 9.091 | 9.091 | 0.037085 | 0.4708 | 13.0025 | 13.092 | 7.8198 | 83.5257 | 0.15674 | 5.656 | 5.656 | 3.269 | 544.5 | 962.5525 | 1025.9942 | -6.591 | 98.9048 | 785.2471 | 99.5837 | 101.775 | 55.155 | 18.327 | 1.291 | 3.525 | 4.816 | 4.816 | 0.16688 | 0.26806 | 11.4756 | 11.5545 | 10.4319 | 49.7061 | 0.23246 | 5.656 | 6.092 | 80.8259 | 962.5525 | 1379.6962 | 1285.477 | 6.829 | 72.9212 | 1124.0148 | 92.8092
[11 empty] | 1999-03-06 | 8:00 | 6473.0003 | 28.891 | 138.174 | 54.757 | 18.22 | 0 | 14.532 | 3.525 |  | 18.057 | 18.057 | 0.80478 | 0 | 13.2109 | 13.2535 | 8.1344 | 70.1111 | 0.18904 | 6.163 | 5.675 | 32.383 | 299.952 | 298.1011 | 1393.1131 | 1393.5382 | -0.030518 | 89.1369 | 845.8197 | 96.1714 | 138.174 | 117.03 | 18.22 | 8.951 | 9.211 | 18.162 | 18.162 | 0.036511 | 0.49284 | 13.5965 | 13.6403 | 4.1858 | 105.1962 | 0.12967 | 5.675 | 5.675 | 16.3995 | 298.1011 | 541.35 | 571.8511 | -5.6343 | 94.4987 | 434.9761 | 96.2298 | 117.03 | 101.43 | 18.22 | 4.28 | 4.931 | 9.211 | 9.211 | 0.037726 | 0.46466 | 13.0025 | 13.0445 | 7.716 | 83.294 | 0.15661 | 5.675 | 5.675 | 3.2695 | 541.35 | 955.7275 | 1008.3921 | -5.5104 | 98.9032 | 774.871 | 99.5781 | 101.43 | 54.757 | 18.22 | 1.301 | 3.525 | 4.826 | 4.826 | 0.16708 | 0.26958 | 11.5644 | 11.6018 | 10.3634 | 49.5101 | 0.23433 | 5.675 | 6.083 | 80.8394 | 955.7275 | 1393.1131 | 1278.6295 | 8.2178 | 72.8819 | 1117.1785 | 92.764
[11 empty] | 36225 | 0.66667 | 6481 | 28.853 | 137.517 | 54.442 | 17.934 | 0 | 14.274 | 3.524 |  | 17.798 | 17.798 | 0.802 | 0 | 12.9764 | 13.0329 | 8.0178 | 70.0277 | 0.18611 | 6.18 | 5.741 | 33.2525 | 300.864 | 298.2806 | 1416.2872 | 1371.78 | 3.1425 | 88.8519 | 835.0303 | 96.0178 | 137.517 | 116.49 | 17.934 | 8.712 | 9.513 | 18.225 | 18.225 | 0.036997 | 0.47802 | 13.2334 | 13.291 | 4.103 | 104.9665 | 0.12662 | 5.741 | 5.741 | 16.848 | 298.2806 | 543.6 | 556.0165 | -2.2841 | 94.3516 | 427.1486 | 96.0557 | 116.49 | 100.845 | 17.934 | 4.266 | 5.247 | 9.513 | 9.513 | 0.039374 | 0.44844 | 12.96 | 13.0164 | 7.5998 | 83.1337 | 0.15657 | 5.741 | 5.741 | 3.2696 | 543.6 | 956.6375 | 982.9081 | -2.7461 | 98.9039 | 763.254 | 99.5716 | 100.845 | 54.442 | 17.934 | 1.296 | 3.524 | 4.82 | 4.82 | 0.16694 | 0.26888 | 11.52 | 11.5702 | 10.3595 | 49.35 | 0.23445 | 5.741 | 6.224 | 81.5942 | 956.6375 | 1416.2872 | 1278.4468 | 9.7325 | 72.6451 | 1117.5422 | 92.6988
[11 empty] | 36226 | 0 | 6489 | 28.798 | 138.053 | 54.757 | 17.992 | 0 | 14.286 | 3.525 |  | 17.811 | 17.811 | 0.80209 | 0 | 12.9873 | 13.0651 | 8.0445 | 70.3685 | 0.18567 | 6.028 | 5.72 | 32.6885 | 303.216 | 298.501 | 1412.6281 | 1375.7766 | 2.6087 | 89.0491 | 837.1388 | 96.0952 | 138.053 | 116.925 | 17.992 | 8.71 | 9.392 | 18.102 | 18.102 | 0.036672 | 0.48116 | 13.2304 | 13.3096 | 4.1254 | 105.3716 | 0.12631 | 5.72 | 5.72 | 16.653 | 298.501 | 544.5 | 559.8825 | -2.8251 | 94.4211 | 429.1917 | 96.1199 | 116.925 | 101.16 | 17.992 | 4.28 | 5.112 | 9.392 | 9.392 | 0.038691 | 0.45571 | 13.0025 | 13.0804 | 7.678 | 83.3725 | 0.15689 | 5.72 | 5.72 | 3.2707 | 544.5 | 963.0075 | 997.6419 | -3.5965 | 98.9043 | 771.071 | 99.5758 | 101.16 | 54.757 | 17.992 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.589 | 10.4364 | 49.5301 | 0.23398 | 5.72 | 6.132 | 81.424 | 963.0075 | 1412.6281 | 1287.1301 | 8.884 | 72.7224 | 1125.0688 | 92.7628
[11 empty] | 36226 | 0.33333 | 6497 | 28.874 | 138.355 | 54.682 | 17.914 | 0 | 14.292 | 3.586 |  | 17.878 | 17.878 | 0.79942 | 0 | 12.9927 | 13.0412 | 7.9465 | 70.658 | 0.18457 | 5.987 | 5.717 | 32.6415 | 301.296 | 298.1664 | 1399.8209 | 1356.4157 | 3.1008 | 89.0526 | 827.291 | 96.0544 | 138.355 | 117.12 | 17.914 | 8.711 | 9.451 | 18.162 | 18.162 | 0.036831 | 0.47963 | 13.2319 | 13.2813 | 4.1145 | 105.709 | 0.12564 | 5.717 | 5.717 | 16.5165 | 298.1664 | 543.6 | 557.7635 | -2.6055 | 94.4606 | 427.965 | 96.1407 | 117.12 | 101.017 | 17.914 | 4.28 | 5.171 | 9.451 | 9.451 | 0.039006 | 0.45286 | 13.0025 | 13.051 | 7.6394 | 83.5151 | 0.15627 | 5.717 | 5.717 | 3.2705 | 543.6 | 958.23 | 990.8269 | -3.4018 | 98.9031 | 767.2134 | 99.5737 | 101.017 | 54.682 | 17.914 | 1.301 | 3.586 | 4.887 | 4.887 | 0.16952 | 0.26622 | 11.5644 | 11.6076 | 10.3591 | 49.5764 | 0.23414 | 5.717 | 6.119 | 81.3837 | 958.23 | 1399.8209 | 1276.3496 | 8.8205 | 72.7053 | 1117.2898 | 92.716
[11 empty] | 36226 | 0.66667 | 6505 | 28.857 | 137.846 | 54.802 | 18.106 | 0 | 14.291 | 3.524 |  | 17.815 | 17.815 | 0.80219 | 0 | 12.9918 | 13.0468 | 8.0311 | 70.1869 | 0.18589 | 6.173 | 5.734 | 32.9 | 300.96 | 298.1582 | 1405.9197 | 1373.8692 | 2.2797 | 88.9656 | 836.0137 | 96.0647 | 137.846 | 116.715 | 18.106 | 8.715 | 9.442 | 18.157 | 18.157 | 0.036812 | 0.47998 | 13.238 | 13.294 | 4.1156 | 105.0589 | 0.12654 | 5.734 | 5.734 | 16.5555 | 298.1582 | 542.25 | 558.0786 | -2.9191 | 94.4474 | 428.1184 | 96.133 | 116.715 | 101.167 | 18.106 | 4.28 | 5.162 | 9.442 | 9.442 | 0.038958 | 0.45329 | 13.0025 | 13.0576 | 7.6242 | 83.2108 | 0.15692 | 5.734 | 5.734 | 3.2697 | 542.25 | 956.6375 | 989.138 | -3.3974 | 98.9034 | 765.694 | 99.573 | 101.167 | 54.802 | 18.106 | 1.296 | 3.524 | 4.82 | 4.82 | 0.16694 | 0.26888 | 11.52 | 11.5688 | 10.3636 | 49.5149 | 0.23364 | 5.734 | 6.274 | 81.2448 | 956.6375 | 1405.9197 | 1278.5753 | 9.0577 | 72.7511 | 1117.6064 | 92.7305
[11 empty] | 36227 | 0 | 6513 | 28.823 | 138.174 | 54.772 | 17.889 | 0 | 14.277 | 3.585 |  | 17.862 | 17.862 | 0.79929 | 0 | 12.9791 | 13.0472 | 7.9459 | 70.6381 | 0.1847 | 6.226 | 5.701 | 32.712 | 302.304 | 298.3541 | 1402.2607 | 1356.2542 | 3.2809 | 89.0358 | 827.3041 | 96.046 | 138.174 | 117.157 | 17.889 | 8.71 | 9.567 | 18.277 | 18.277 | 0.037139 | 0.47656 | 13.2304 | 13.2998 | 4.1047 | 105.6718 | 0.12586 | 5.701 | 5.701 | 16.2825 | 298.3541 | 544.5 | 555.158 | -1.9574 | 94.5426 | 426.7561 | 96.1846 | 117.157 | 101.4 | 17.889 | 4.28 | 5.287 | 9.567 | 9.567 | 0.039625 | 0.44737 | 13.0025 | 13.0707 | 7.603 | 83.7865 | 0.156 | 5.701 | 5.701 | 3.2708 | 544.5 | 958.9125 | 982.6428 | -2.4747 | 98.9037 | 763.5714 | 99.5716 | 101.4 | 54.772 | 17.889 | 1.287 | 3.585 | 4.872 | 4.872 | 0.1692 | 0.26416 | 11.44 | 11.5 | 10.3523 | 49.8447 | 0.23072 | 5.701 | 6.157 | 81.2269 | 958.9125 | 1402.2607 | 1273.998 | 9.1469 | 72.775 | 1116.4552 | 92.7246
[11 empty] | 36227 | 0.33333 | 6521 | 28.849 | 138.342 | 54.885 | 17.973 | 0 | 14.286 | 3.585 |  | 17.871 | 17.871 | 0.7994 | 0 | 12.9873 | 13.0454 | 7.9575 | 70.683 | 0.18456 | 6.352 | 5.701 | 32.2655 | 301.392 | 298.1827 | 1400.4311 | 1357.8462 | 3.0408 | 89.1793 | 828.0144 | 96.1033 | 138.342 | 117.127 | 17.973 | 8.715 | 9.561 | 18.276 | 18.276 | 0.037129 | 0.47685 | 13.238 | 13.2972 | 4.1046 | 105.6569 | 0.12585 | 5.701 | 5.701 | 16.224 | 298.1827 | 543.6 | 555.1925 | -2.1325 | 94.559 | 426.6876 | 96.1977 | 117.127 | 101.437 | 17.973 | 4.28 | 5.281 | 9.561 | 9.561 | 0.039593 | 0.44765 | 13.0025 | 13.0607 | 7.5928 | 83.7162 | 0.15601 | 5.701 | 5.701 | 3.2707 | 543.6 | 962.325 | 981.5113 | -1.9937 | 98.9031 | 762.5556 | 99.5711 | 101.437 | 54.885 | 17.973 | 1.291 | 3.585 | 4.876 | 4.876 | 0.16928 | 0.26477 | 11.4756 | 11.5269 | 10.3975 | 49.7905 | 0.23151 | 5.701 | 6.206 | 81.2224 | 962.325 | 1400.4311 | 1279.6202 | 8.6267 | 72.7609 | 1120.9726 | 92.7543
[11 empty] | 36227 | 0.66667 | 6529 | 28.819 | 138.047 | 54.922 | 17.947 | 0 | 14.284 | 3.465 |  | 17.749 | 17.749 | 0.80478 | 0 | 12.9855 | 13.0551 | 8.144 | 70.3935 | 0.18546 | 6.42 | 5.685 | 32.3125 | 302.304 | 298.3541 | 1401.651 | 1395.075 | 0.46916 | 89.1697 | 846.7145 | 96.1838 | 138.047 | 117.127 | 17.947 | 8.708 | 9.395 | 18.103 | 18.103 | 0.036677 | 0.48103 | 13.2273 | 13.2983 | 4.1271 | 105.5129 | 0.12603 | 5.685 | 5.685 | 16.341 | 298.3541 | 544.5 | 559.7452 | -2.7999 | 94.523 | 429.0497 | 96.1913 | 117.127 | 101.535 | 17.947 | 4.28 | 5.115 | 9.395 | 9.395 | 0.038707 | 0.45556 | 13.0025 | 13.0723 | 7.6767 | 83.7073 | 0.15617 | 5.685 | 5.685 | 3.2707 | 544.5 | 963.0075 | 997.3761 | -3.5689 | 98.9038 | 770.9381 | 99.5758 | 101.535 | 54.922 | 17.947 | 1.296 | 3.465 | 4.761 | 4.761 | 0.16458 | 0.27221 | 11.52 | 11.5818 | 10.4673 | 49.8142 | 0.2325 | 5.685 | 6.22 | 81.1888 | 963.0075 | 1401.651 | 1292.8306 | 7.7637 | 72.7878 | 1127.919 | 92.8019
[11 empty] | 36228 | 0 | 6537 | 28.798 | 139.186 | 55.057 | 17.967 | 0 | 14.27 | 3.585 |  | 17.855 | 17.855 | 0.79922 | 0 | 12.9727 | 13.0504 | 7.9659 | 71.1886 | 0.18332 | 6.446 | 5.663 | 32.2185 | 303.024 | 298.6152 | 1399.8209 | 1359.0004 | 2.9161 | 89.2107 | 828.8078 | 96.1127 | 139.186 | 117.915 | 17.967 | 8.708 | 9.632 | 18.34 | 18.34 | 0.03731 | 0.47481 | 13.2273 | 13.3066 | 4.1001 | 106.4834 | 0.12496 | 5.663 | 5.663 | 16.2435 | 298.6152 | 543.6 | 553.8989 | -1.8946 | 94.5604 | 426.2571 | 96.1893 | 117.915 | 101.94 | 17.967 | 4.28 | 5.352 | 9.632 | 9.632 | 0.039972 | 0.44435 | 13.0025 | 13.0804 | 7.5638 | 84.3967 | 0.15499 | 5.663 | 5.663 | 3.2721 | 543.6 | 965.965 | 975.7008 | -1.0079 | 98.9043 | 759.6504 | 99.5693 | 101.94 | 55.057 | 17.967 | 1.282 | 3.585 | 4.867 | 4.867 | 0.1691 | 0.26341 | 11.3956 | 11.4638 | 10.4299 | 50.1016 | 0.22881 | 5.663 | 6.09 | 81.1776 | 965.965 | 1399.8209 | 1282.366 | 8.3907 | 72.8153 | 1124.1655 | 92.7789
[11 empty] | 36228 | 0.33333 | 6545 | 28.879 | 137.966 | 54.817 | 17.938 | 0 | 14.288 | 3.585 |  | 17.873 | 17.873 | 0.79942 | 0 | 12.9891 | 13.0356 | 7.9534 | 70.5001 | 0.1849 | 6.425 | 5.703 | 32.3125 | 301.488 | 298.0685 | 1402.2607 | 1357.2376 | 3.2107 | 89.1594 | 827.6531 | 96.0959 | 137.966 | 117.135 | 17.938 | 8.712 | 9.453 | 18.165 | 18.165 | 0.036837 | 0.4796 | 13.2334 | 13.2808 | 4.1161 | 105.4964 | 0.12589 | 5.703 | 5.703 | 16.302 | 298.0685 | 540.45 | 557.7479 | -3.2006 | 94.5308 | 427.9082 | 96.1903 | 117.135 | 101.415 | 17.938 | 4.28 | 5.173 | 9.453 | 9.453 | 0.039017 | 0.45277 | 13.0025 | 13.0491 | 7.594 | 83.743 | 0.15582 | 5.703 | 5.703 | 3.2708 | 540.45 | 959.14 | 984.8975 | -2.6855 | 98.9027 | 762.6738 | 99.5711 | 101.415 | 54.817 | 17.938 | 1.296 | 3.585 | 4.881 | 4.881 | 0.16938 | 0.26552 | 11.52 | 11.5613 | 10.3669 | 49.8111 | 0.2321 | 5.703 | 6.096 | 81.1507 | 959.14 | 1402.2607 | 1276.5386 | 8.9657 | 72.7745 | 1117.8393 | 92.7404
[11 empty] | 36228 | 0.51631 | 6549.3914 | 28.862 | 138.328 | 54.84 | 18.052 | 0 | 14.293 | 3.585 |  | 17.878 | 17.878 | 0.79947 | 0 | 12.9936 | 13.0467 | 7.9588 | 70.5732 | 0.18487 | 6.496 | 5.7 | 32.43 | 301.872 | 298.3051 | 1405.9197 | 1358.3199 | 3.3857 | 89.1286 | 828.3125 | 96.0848 | 138.328 | 117.24 | 18.052 | 8.712 | 9.39 | 18.102 | 18.102 | 0.036669 | 0.48127 | 13.2334 | 13.2875 | 4.1248 | 105.6072 | 0.12582 | 5.7 | 5.7 | 16.536 | 298.3051 | 542.25 | 559.7292 | -3.2235 | 94.4567 | 429.0172 | 96.1456 | 117.24 | 101.64 | 18.052 | 4.28 | 5.11 | 9.39 | 9.39 | 0.038681 | 0.4558 | 13.0025 | 13.0557 | 7.647 | 83.741 | 0.15591 | 5.7 | 5.7 | 3.2712 | 542.25 | 956.1825 | 993.6843 | -3.922 | 98.9034 | 767.9671 | 99.574 | 101.64 | 54.84 | 18.052 | 1.301 | 3.585 | 4.886 | 4.886 | 0.16948 | 0.26627 | 11.5644 | 11.6117 | 10.3382 | 49.8498 | 0.23293 | 5.7 | 6.189 | 81.1373 | 956.1825 | 1405.9197 | 1273.7373 | 9.4018 | 72.8006 | 1114.9599 | 92.7229
[11 empty] | 36228 | 0.83334 | 6557.0003 | 28.819 | 138.462 | 54.967 | 17.989 | 0 | 14.286 | 3.525 |  | 17.811 | 17.811 | 0.80209 | 0 | 12.9873 | 13.0569 | 8.0573 | 70.6682 | 0.18476 | 6.463 | 5.667 | 32.289 | 302.352 | 298.5254 | 1402.8703 | 1377.5194 | 1.8071 | 89.1838 | 838.0224 | 96.147 | 138.462 | 117.202 | 17.989 | 8.71 | 9.515 | 18.225 | 18.225 | 0.037 | 0.47791 | 13.2304 | 13.3014 | 4.1128 | 105.7302 | 0.1258 | 5.667 | 5.667 | 16.38 | 298.5254 | 544.95 | 556.8005 | -2.1746 | 94.513 | 427.6629 | 96.1699 | 117.202 | 101.512 | 17.989 | 4.28 | 5.235 | 9.515 | 9.515 | 0.039348 | 0.44982 | 13.0025 | 13.0723 | 7.6311 | 83.7369 | 0.15611 | 5.667 | 5.667 | 3.2724 | 544.95 | 959.14 | 987.8115 | -2.9893 | 98.9038 | 766.3808 | 99.573 | 101.512 | 54.967 | 17.989 | 1.296 | 3.525 | 4.821 | 4.821 | 0.16698 | 0.26882 | 11.52 | 11.5818 | 10.3939 | 49.8566 | 0.2323 | 5.667 | 6.056 | 81.1485 | 959.14 | 1402.8703 | 1281.942 | 8.6201 | 72.8169 | 1120.541 | 92.7581
[11 empty] | 36229 | 0.16667 | 6565 | 28.798 | 138.409 | 54.982 | 17.986 | 0 | 14.292 | 3.525 |  | 17.817 | 17.817 | 0.80216 | 0 | 12.9927 | 13.0705 | 8.0645 | 70.645 | 0.18502 | 6.385 | 5.658 | 32.2185 | 303.072 | 298.6152 | 1401.0408 | 1378.7121 | 1.5937 | 89.2107 | 838.6637 | 96.1584 | 138.409 | 117.637 | 17.986 | 8.711 | 9.568 | 18.279 | 18.279 | 0.037143 | 0.47656 | 13.2319 | 13.3111 | 4.104 | 105.933 | 0.12566 | 5.658 | 5.658 | 16.5945 | 298.6152 | 544.05 | 555.3755 | -2.0817 | 94.4428 | 426.9953 | 96.1137 | 117.637 | 101.565 | 17.986 | 4.28 | 5.288 | 9.568 | 9.568 | 0.03963 | 0.44732 | 13.0025 | 13.0804 | 7.5963 | 84.0187 | 0.15568 | 5.658 | 5.658 | 3.2723 | 544.05 | 966.42 | 981.7445 | -1.5857 | 98.9042 | 762.8973 | 99.5711 | 101.565 | 54.982 | 17.986 | 1.301 | 3.525 | 4.826 | 4.826 | 0.16708 | 0.26958 | 11.5644 | 11.6337 | 10.4865 | 49.801 | 0.2336 | 5.658 | 5.978 | 81.1395 | 966.42 | 1401.0408 | 1293.1576 | 7.7002 | 72.8281 | 1129.7888 | 92.8182
[11 empty] | 36229 | 0.5 | 6573 | 28.947 | 138.033 | 54.637 | 18.142 | 0 | 14.299 | 3.524 |  | 17.823 | 17.823 | 0.80228 | 0 | 12.9991 | 13.0195 | 8.0361 | 70.1569 | 0.18558 | 6.434 | 5.721 | 32.665 | 299.76 | 297.9869 | 1412.0185 | 1374.5583 | 2.653 | 89.0381 | 836.2726 | 96.094 | 138.033 | 116.91 | 18.142 | 8.718 | 9.502 | 18.22 | 18.22 | 0.036976 | 0.47849 | 13.2425 | 13.2633 | 4.1008 | 105.2287 | 0.12604 | 5.721 | 5.721 | 16.8675 | 297.9869 | 541.35 | 555.9114 | -2.6898 | 94.3395 | 426.9491 | 96.0493 | 116.91 | 101.077 | 18.142 | 4.28 | 5.222 | 9.502 | 9.502 | 0.039278 | 0.45043 | 13.0025 | 13.0229 | 7.5859 | 83.2656 | 0.1564 | 5.721 | 5.721 | 3.2687 | 541.35 | 950.95 | 982.3665 | -3.3037 | 98.9031 | 761.8582 | 99.571 | 101.077 | 54.637 | 18.142 | 1.301 | 3.524 | 4.825 | 4.825 | 0.16704 | 0.26964 | 11.5644 | 11.5826 | 10.305 | 49.41 | 0.23442 | 5.721 | 6.291 | 81.0275 | 950.95 | 1412.0185 | 1272.1104 | 9.9084 | 72.8084 | 1111.5302 | 92.7103
[11 empty] | 36229 | 0.83334 | 6581.0003 | 28.891 | 138.489 | 54.937 | 18.109 | 0 | 14.293 | 3.524 |  | 17.817 | 17.817 | 0.80221 | 0 | 12.9936 | 13.0356 | 8.0433 | 70.5607 | 0.18474 | 6.546 | 5.693 | 32.5475 | 301.872 | 298.1827 | 1406.5299 | 1375.5732 | 2.2009 | 89.0847 | 836.878 | 96.1108 | 138.489 | 117.3 | 18.109 | 8.712 | 9.687 | 18.399 | 18.399 | 0.037462 | 0.4735 | 13.2334 | 13.2761 | 4.0815 | 105.704 | 0.1256 | 5.693 | 5.693 | 16.6335 | 298.1827 | 543.15 | 551.3939 | -1.5178 | 94.4217 | 424.7883 | 96.0843 | 117.3 | 101.61 | 18.109 | 4.28 | 5.407 | 9.687 | 9.687 | 0.040265 | 0.44183 | 13.0025 | 13.0445 | 7.5355 | 83.8105 | 0.15564 | 5.693 | 5.693 | 3.2714 | 543.15 | 957.5475 | 970.4998 | -1.3527 | 98.9029 | 756.8249 | 99.5677 | 101.61 | 54.937 | 18.109 | 1.301 | 3.524 | 4.825 | 4.825 | 0.16704 | 0.26964 | 11.5644 | 11.6018 | 10.3824 | 49.7821 | 0.23305 | 5.693 | 6.231 | 81.0902 | 957.5475 | 1406.5299 | 1281.1204 | 8.9162 | 72.8052 | 1119.3339 | 92.7555
[11 empty] | 36230 | 0.16668 | 6589.0003 | 28.772 | 138.703 | 55.207 | 17.937 | 0 | 14.278 | 3.586 |  | 17.864 | 17.864 | 0.79926 | 0 | 12.98 | 13.0678 | 7.9743 | 71.0437 | 0.18394 | 6.513 | 5.654 | 32.054 | 305.28 | 298.6805 | 1385.7944 | 1360.2792 | 1.8412 | 89.2681 | 829.4798 | 96.1357 | 138.703 | 117.915 | 17.937 | 8.71 | 9.635 | 18.345 | 18.345 | 0.03732 | 0.47479 | 13.2304 | 13.3198 | 4.099 | 106.273 | 0.12534 | 5.654 | 5.654 | 16.38 | 298.6805 | 546.3 | 553.8789 | -1.3873 | 94.5159 | 426.2797 | 96.1575 | 117.915 | 102.105 | 17.937 | 4.281 | 5.354 | 9.635 | 9.635 | 0.039985 | 0.44432 | 13.0056 | 13.0935 | 7.6013 | 84.4717 | 0.155 | 5.654 | 5.654 | 3.2733 | 546.3 | 968.4675 | 980.4983 | -1.2422 | 98.9041 | 763.3991 | 99.5712 | 102.105 | 55.207 | 17.937 | 1.287 | 3.586 | 4.873 | 4.873 | 0.16924 | 0.26411 | 11.44 | 11.5174 | 10.4648 | 50.2542 | 0.22918 | 5.654 | 6.096 | 81.2045 | 968.4675 | 1385.7944 | 1286.9024 | 7.1361 | 72.8123 | 1127.6849 | 92.799
[11 empty] | 36230 | 0.5 | 6597 | 28.917 | 138.208 | 54.78 | 18.031 | 0 | 14.305 | 3.583 |  | 17.888 | 17.888 | 0.7997 | 0 | 13.0045 | 13.0365 | 7.9519 | 70.5111 | 0.18489 | 6.669 | 5.718 | 32.7355 | 301.344 | 298.1338 | 1399.8209 | 1357.7269 | 3.0071 | 89.0199 | 827.9303 | 96.0461 | 138.208 | 117.262 | 18.031 | 8.716 | 9.558 | 18.274 | 18.274 | 0.037123 | 0.47696 | 13.2395 | 13.272 | 4.0954 | 105.6086 | 0.12567 | 5.718 | 5.718 | 16.848 | 298.1338 | 540.9 | 554.64 | -2.5402 | 94.3488 | 426.3869 | 96.0487 | 117.262 | 101.362 | 18.031 | 4.293 | 5.265 | 9.558 | 9.558 | 0.039542 | 0.44915 | 13.042 | 13.0741 | 7.5682 | 83.7128 | 0.15618 | 5.718 | 5.718 | 3.2689 | 540.9 | 951.6325 | 979.2762 | -2.9049 | 98.9036 | 760.0881 | 99.5699 | 101.362 | 54.78 | 18.031 | 1.296 | 3.583 | 4.879 | 4.879 | 0.1693 | 0.26563 | 11.52 | 11.5483 | 10.2809 | 49.7591 | 0.23208 | 5.718 | 6.265 | 80.9962 | 951.6325 | 1399.8209 | 1266.5487 | 9.5207 | 72.8323 | 1109.0906 | 92.6971
[11 empty] | 36230 | 0.83334 | 6605.0003 | 28.917 | 138.174 | 54.697 | 17.997 | 0 | 14.276 | 3.525 |  | 17.801 | 17.801 | 0.80198 | 0 | 12.9782 | 13.0101 | 8.0556 | 70.3829 | 0.18485 | 6.489 | 5.667 | 31.9365 | 301.584 | 298.2398 | 1391.8932 | 1376.7495 | 1.088 | 89.2917 | 837.4947 | 96.1867 | 138.174 | 116.992 | 17.997 | 8.713 | 9.567 | 18.28 | 18.28 | 0.037143 | 0.47664 | 13.2349 | 13.2674 | 4.1018 | 105.4842 | 0.12578 | 5.667 | 5.667 | 16.3995 | 298.2398 | 540.9 | 554.9217 | -2.5923 | 94.5012 | 426.5807 | 96.1556 | 116.992 | 101.145 | 17.997 | 4.281 | 5.286 | 9.567 | 9.567 | 0.039622 | 0.44748 | 13.0056 | 13.0375 | 7.5534 | 83.5181 | 0.1561 | 5.667 | 5.667 | 3.2677 | 540.9 | 955.7275 | 976.315 | -2.1541 | 98.9043 | 758.6075 | 99.5692 | 101.145 | 54.697 | 17.997 | 1.282 | 3.525 | 4.807 | 4.807 | 0.1667 | 0.26669 | 11.3956 | 11.4235 | 10.3403 | 49.5837 | 0.23039 | 5.667 | 6.071 | 80.7968 | 955.7275 | 1391.8932 | 1273.9292 | 8.4751 | 72.9088 | 1114.8284 | 92.7525
[11 empty] | 36231 | 0.16667 | 6613 | 28.891 | 137.745 | 54.547 | 17.872 | 0 | 14.275 | 3.525 |  | 17.8 | 17.8 | 0.80197 | 0 | 12.9773 | 13.0192 | 8.0626 | 70.2114 | 0.18543 | 6.407 | 5.658 | 31.725 | 302.016 | 298.2725 | 1376.0372 | 1377.6953 | -0.1205 | 89.3638 | 837.9839 | 96.2141 | 137.745 | 117.022 | 17.872 | 8.708 | 9.521 | 18.229 | 18.229 | 0.037013 | 0.4777 | 13.2273 | 13.27 | 4.112 | 105.3995 | 0.1259 | 5.658 | 5.658 | 16.107 | 298.2725 | 538.65 | 556.3438 | -3.2848 | 94.5999 | 427.3081 | 96.2306 | 117.022 | 101.07 | 17.872 | 4.28 | 5.241 | 9.521 | 9.521 | 0.03938 | 0.44953 | 13.0025 | 13.0445 | 7.5399 | 83.6341 | 0.15597 | 5.658 | 5.658 | 3.2669 | 538.65 | 953.225 | 975.8642 | -2.375 | 98.9047 | 757.2571 | 99.5686 | 101.07 | 54.547 | 17.872 | 1.287 | 3.525 | 4.812 | 4.812 | 0.1668 | 0.26746 | 11.44 | 11.4769 | 10.3167 | 49.6198 | 0.2313 | 5.658 | 5.986 | 80.8147 | 953.225 | 1376.0372 | 1271.7476 | 7.579 | 72.9057 | 1112.4863 | 92.7357
[11 empty] | 36231 | 0.5 | 6621 | 29.04 | 137.692 | 53.73 | 17.968 | 0 | 14.273 | 3.524 |  | 17.797 | 17.797 | 0.80199 | 0 | 12.9755 | 12.9601 | 8.0166 | 69.7264 | 0.18587 | 6.664 | 5.714 | 32.6415 | 297.744 | 297.6442 | 1408.9691 | 1370.9651 | 2.6973 | 89.0334 | 834.3046 | 96.0876 | 137.692 | 116.385 | 17.968 | 8.711 | 9.325 | 18.036 | 18.036 | 0.036495 | 0.48298 | 13.2319 | 13.2163 | 4.1209 | 104.9496 | 0.12593 | 5.714 | 5.714 | 16.7505 | 297.6442 | 535.95 | 560.0425 | -4.4953 | 94.3723 | 428.8433 | 96.094 | 116.385 | 100.23 | 17.968 | 4.28 | 5.045 | 9.325 | 9.325 | 0.038334 | 0.45898 | 13.0025 | 12.9872 | 7.5864 | 82.7531 | 0.15694 | 5.714 | 5.714 | 3.262 | 535.95 | 942.305 | 987.8637 | -4.8348 | 98.904 | 761.9068 | 99.5719 | 100.23 | 53.73 | 17.968 | 1.282 | 3.524 | 4.806 | 4.806 | 0.16666 | 0.26675 | 11.3956 | 11.3821 | 10.1795 | 48.8325 | 0.23308 | 5.714 | 6.3 | 81.023 | 942.305 | 1408.9691 | 1255.6318 | 10.8829 | 72.7786 | 1098.9684 | 92.6274
[11 empty] | 36231 | 0.83334 | 6629.0003 | 28.985 | 138.033 | 53.572 | 17.865 | 0 | 14.261 | 3.525 |  | 17.786 | 17.786 | 0.80181 | 0 | 12.9645 | 12.9703 | 7.9999 | 69.9376 | 0.18546 | 7.353 | 5.675 | 33.1585 | 298.992 | 297.8074 | 1414.4576 | 1368.4903 | 3.2498 | 88.8658 | 833.1488 | 96.0201 | 138.033 | 116.97 | 17.865 | 8.712 | 9.45 | 18.162 | 18.162 | 0.036829 | 0.47968 | 13.2334 | 13.2393 | 4.1058 | 105.5307 | 0.12545 | 5.675 | 5.675 | 16.77 | 297.8074 | 541.35 | 556.897 | -2.8719 | 94.3688 | 427.3522 | 96.0758 | 116.97 | 100.305 | 17.865 | 4.267 | 5.183 | 9.45 | 9.45 | 0.039036 | 0.45153 | 12.963 | 12.9688 | 7.5958 | 83.1767 | 0.15592 | 5.675 | 5.675 | 3.2644 | 541.35 | 951.6325 | 984.3388 | -3.4369 | 98.9038 | 762.8444 | 99.5721 | 100.305 | 53.572 | 17.865 | 1.282 | 3.525 | 4.807 | 4.807 | 0.1667 | 0.26669 | 11.3956 | 11.4006 | 10.2836 | 48.7899 | 0.23367 | 5.675 | 6.285 | 81.5046 | 951.6325 | 1414.4576 | 1268.0875 | 10.3481 | 72.6318 | 1109.86 | 92.6563
Note on A1: Catherine Hughes was not part of the EPA reviewing team. All comments from Catherine Hughes are lab verifications.
Note on Q171: Pilot unit was down between 6364 and 6482 hours.
Note on Q172: Assume pilot resumed operation at 8 am of 2/18. Cumulative down time for this shutdown period is estimated at 104 hours.
Note on V125: Operational data reported value as 20.1. No reason for low value. Changed to NR
Note on V126: Operational data reported value as 20.1. No reason for low value. Changed to NR
Note on V160: Operational data reported value as 37.1. No reason for low value. Changed to NR
Note on Z177: Originally reported as -0.01. Sensor error suspected. Changed to NR
Note on AA8: No cleaning events took place during this time
Note on AJ126: Due to lower PC value which has been changed to NR, these values are no longer computational.
Note on AK172: Value reported as 9.95. Most likely a transcription error. Changed value to 7.95
Note on DV22: TOC Concnetration lab verified. This feed TOC value is within the expected range.
Note on DV33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on EO16: Questioanable data
Note on EO22: Possible mislabeling of lab sampling vials has resulted in the laboratory analysis of this sample to show a TOC concentration of 4.82. Because we cannot be sure of this error, it is being reported as NR
Note on EO39: Lab verified that concenteration was 61.7. This value is quite high. Chnaged to NR
Note on EO40: Lab verified that concenteration was 36.9. This value is quite high. Chnaged to NR
Note on EP16: Questionable Data
Note on EP22: TOC concentration was 39.4. This is well above the expected range. Therefore, feed TOC is being reported as NR.
Note on EP33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on FI22: TOC concentration was reported to be 11.4 This is out of the expected range and is therefore being reported as NR due to the questionable value.
Note on FJ22: TOC concentration was reported to be 58.7. This is out of the expected range and is therefore being reported as NR due to the questionable value.
Note on FJ33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GC22: This value falls within the expected effluent TOC concentrations.
Note on GD22: This value falls within the expected values of TOC. The calue has also been lab verified.
Note on GD25: Bromide concentration reported as 400 ug/L. This value is questionable due to the low bromide levels previously measured. Reported as NR
Note on GD33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GD40: Lab verified
Note on GW48: Lab verified
Note on GX17: Lab verified: TSC-ADM: changed TDS to NR, from reported value of 94 mg/L (operational data does not reflect sharp drop in TDS concentrations, as reported here).
Note on GX23: Lab verified TSC-ADM: reviewer changed reported value of 0.057 cm-1 to NR - there was no explanation for this reported drop in UV, and the reported UV values for the staged influent do not reflect this trend.
Note on GX25: Bromide level reported as 100 ug/L. This is questionable die to low overall bromide concntrations. Being reported as NR
Note on GX33: The chlorine dose recorded was not sufficient to meet ammonia and TOC demand. The feed SDS DBPs are therefore being reported as NR
Note on GX39: Lab verified
Note on GX48: Lab verified
Note on HI17: Lab verified: TSC-ADM: changed TDS to NR, from reported value of 94 mg/L (operational data does not reflect sharp drop in TDS concentrations, as reported here).
Note on HI22: Lab verified TSC-ADM: reviewer changed reported value of 0.057 cm-1 to NR - there was no explanation for this reported drop in UV, and the reported UV values for the staged influent do not reflect this trend.
Note on HO3: No Duplicate data available