## 7450. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Hydranautics Corp. | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.16873 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.54 | [7 empty] | Recovery during sample collection (decimal) | 0.28 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-23 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.7 | [7 empty] | Feed flow rate during sample collection (mL/min) | 8.7 | [7 empty] | Feed flow rate during sample collection (mL/min) | 16.1 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 1000 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:00 | 7:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 109.6 | 109.6 | 109.6 | 109.6 | SDS-THM4F, ug/L | 109.6 | 109.6 | 109.6 | 109.6 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 25 | 153 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 40.9 | 53.1 | 38.8 | 38.8 | SDS-THM4p, ug/L | 40.9 | 53.1 | 38.8 | 38.8 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.2 | 7.9 | 8.05 | 3.7267 | 1998-04-13 | 8:00 | 0 | 23 | 80 | 79 | 263 | 4.1 | 2.3 | 6.4 | 0.20103 | 0.64062 | 40.0938 | 9.358 | 9.8112 | 0 | 0 | 0 | 0 | 79.5 | 0.12341 | 1998-04-14 | 7:30 | 0 | 23 | 81 | 79 | 263 | 5.1 | 2.57 |  | 7.67 | 0.20103 | 0.66493 | 33.2894 | 11.6405 | 12.2042 | 291.7704 | 241.7343 | 290.8001 | 0.49551 | 79.5045 | 0.1535 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 75.5 | 75.5 | 75.5 | 75.5 | SDS-HAA5F, ug/L | 75.5 | 75.5 | 75.5 | 75.5 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 23 | 23.5 | 4.2553 | 1998-04-13 | 9:00 | 1 | 23 | 80 | 79 | 263 | 4.08 | 2 | 6.08 | 0.20103 | 0.67105 | 42.2566 | 9.3124 | 9.7634 | 0 | 0 | 0 | 0 | 79.5 | 0.12281 | 1998-04-14 | 8:15 | 0.75 | 23 | 81 | 79 | 263 | 5.13 | 2.6 |  | 7.73 | 0.20103 | 0.66365 | 33.0233 | 11.709 | 12.276 | 291.7017 | 241.6726 | 290.7259 | 0.49541 | 79.5046 | 0.15441 | 7.4 | 7.5 | 7.4 | 120 | 260 | 121 | 531.7712 | -339.4803 | 53.5783 | 527.7552 | 77.2622 | 0.02 | 0.155 | 0.165 | 0.4288 | -159.8776 | 87.3016 | 0.42481 | 95.292 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 15.75 | 29.1 | 13.4 | 17.3 | SDS-HAA5p, ug/L | 15.75 | 29.1 | 13.4 | 17.3 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 140 | NA | 140 | #VALUE! | 1998-04-13 | 9:30 | 1.5 | 23 | 80 | 79 | 263 | 4.13 | 1.95 | 6.08 | 0.20103 | 0.67928 | 42.2566 | 9.4265 | 9.883 | 0 | 0 | 0 | 0 | 79.5 | 0.12431 | 1998-04-14 | 9:15 | 1.75 | 23 | 81 | 79 | 263 | 5 | 2.6 |  | 7.6 | 0.20103 | 0.65789 | 33.6053 | 11.4122 | 11.9649 | 291.3618 | 241.4119 | 290.4122 | 0.49475 | 79.5052 | 0.15049 |  |  |  | 226 |  | 251 | 321 | -27.8884 | 12.5725 | 320.097 | 29.3964 | 0.027 |  | 0.189 | 0.40846 | -116.1172 | 82.8571 | 0.40484 | 93.3306 | [8 empty] | Sampling date | MM/DD/YY | 1998-04-15 | 1998-04-16 | --- | --- | 1998-04-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-20 | 1998-04-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-21 | 1998-04-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-22 | 1998-04-22 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 275 | 275 | 275 | 275 | SDS-TOXF, ug Cl- /L | 275 | 275 | 275 | 275 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 260 | 257 | 258.5 | 1.1605 | 1998-04-13 | 10:30 | 2.5 | 23 | 80 | 79 | 263 | 4.23 | 1.77 | 6 | 0.20103 | 0.705 | 42.8333 | 9.6547 | 10.1223 | 0 | 0 | 0 | 0 | 79.5 | 0.12732 | 1998-04-14 | 10:15 | 2.75 | 23 | 81 | 79 | 263 | 5 | 2.5 |  | 7.5 | 0.20103 | 0.66667 | 34.0667 | 11.4122 | 11.9649 | 291.8565 | 241.8218 | 290.9053 | 0.49559 | 79.5044 | 0.15049 | 7.5 |  | 7.6 | 245 |  | 275 | 285.5 | -3.8182 | 5.2224 | 285.115 | 14.0698 | 0.036 |  | 0.252 | 0.4005 | -58.9286 | 77.1429 | 0.39704 | 90.9328 | [8 empty] | Sampling time | hh:mm | 7:30 | 9:45 | --- | --- | 7:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:40 | 13:40 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 102.5 | 160 | 95 | 82 | SDS-TOXp, ug Cl- /L | 102.5 | 160 | 95 | 82 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 188 | NA | 188 | #VALUE! | 1998-04-13 | 11:30 | 3.5 | 23 | 80 | 78 | 263 | 4.17 | 1.77 | 5.94 | 0.20103 | 0.70202 | 43.2761 | 9.5178 | 9.9788 | 0 | 0 | 0 | 0 | 79 | 0.12631 | 1998-04-14 | 11:15 | 3.75 | 23 | 81 | 79 | 263 | 5 | 2.46 |  | 7.46 | 0.20103 | 0.67024 | 34.2547 | 11.4122 | 11.9649 | 292.0586 | 241.9892 | 291.1067 | 0.49593 | 79.5041 | 0.15049 | 7.5 |  | 7.6 | 250 |  | 278 | 275.7764 | 0.79985 | 3.2882 | 275.5314 | 9.2662 | 0.038 | 0.156 | 0.285 | 0.40039 | -40.4864 | 75.873 | 0.39694 | 90.4268 | [8 empty] | Operation time | hh.hh | 24 | 50.25 | --- | --- | 24 | --- | --- | --- | --- | --- | Operation time | hh.hh | 86 | 86 | --- | --- | --- | --- | --- | Operation time | hh.hh | 111 | 111 | --- | --- | --- | --- | --- | Cumulative time | hr | 136 | 136 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 6.21 | 6.21 | 6.21 | 6.21 | SDS-CDF, mg/L | 6.21 | 6.21 | 6.21 | 6.21 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 158 | NA | 158 | #VALUE! | 1998-04-13 | 12:30 | 4.5 | 23 | 80 | 78 | 263 | 4.3 | 1.73 | 6.03 | 0.20103 | 0.7131 | 42.6153 | 9.8145 | 10.2898 | 0 | 0 | 0 | 0 | 79 | 0.13025 | 1998-04-14 | 12:15 | 4.75 | 23 | 80 | 79 | 263 | 5 | 2.33 |  | 7.33 | 0.20103 | 0.68213 | 34.8799 | 11.4122 | 11.9649 | 292.7325 | 242.5476 | 291.7785 | 0.49708 | 79.0029 | 0.15145 |  | 7.6 |  | 249 | 262 | 279 | 278.8863 | 0.040765 | 3.675 | 278.6022 | 10.6252 | 0.04 | 0.156 | 0.303 | 0.40965 | -35.1967 | 74.6032 | 0.40613 | 90.151 | [8 empty] | pH | --- | 8 | 8.1 | 8.05 | 1.2422 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.4 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.2 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.3 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.585 | 1.83 | 1.76 | 0.94 | SDS-CDp, mg/L | 2.585 | 1.83 | 1.76 | 0.94 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 53.9325 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.33 | NA | 0.33 | #VALUE! | 1998-04-13 | 13:30 | 5.5 | 23 | 80 | 78 | 263 | 4.31 | 2.3 | 6.61 | 0.20103 | 0.65204 | 38.7882 | 9.8373 | 10.3138 | 0 | 0 | 0 | 0 | 79 | 0.13055 | 1998-04-14 | 13:15 | 5.75 | 23 | 80 | 78 | 263 | 5 | 2.45 |  | 7.45 | 0.20103 | 0.67114 | 34.302 | 11.4122 | 11.9649 | 292.1095 | 242.0314 | 291.1574 | 0.49602 | 78.504 | 0.15241 |  |  |  | 248 |  | 277 | 279.9286 | -1.0572 | 4.0619 | 279.6251 | 11.3098 | 0.04 |  | 0.313 | 0.3973 | -26.9316 | 74.6032 | 0.3939 | 89.8451 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.85 | 3.85 | 3.85 | 3.85 | TOCF, mg/L | 3.85 | 3.85 | 3.85 | 3.85 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 63.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | NA | #DIV/0! | #VALUE! | 1998-04-13 | 14:00 | 6 | 23 | 70 | 68 | 263 | 3.8 | 1.86 | 5.66 | 0.20103 | 0.67138 | 45.4664 | 8.6733 | 9.0933 | 0 | 0 | 0 | 0 | 69 | 0.13179 | 1998-04-14 | 14:15 | 6.75 | 23 | 79 | 78 | 263 | 4.9 | 2.31 |  | 7.21 | 0.20103 | 0.67961 | 35.4771 | 11.184 | 11.7256 | 292.5772 | 242.435 | 291.643 | 0.49675 | 78.0032 | 0.15032 | 7.5 |  |  | 250 |  | 279 | 276.5303 | 0.8852 | 3.2882 | 276.2832 | 9.5131 | 0.039 |  | 0.321 | 0.40886 | -27.3718 | 75.2381 | 0.40542 | 90.3803 | [8 empty] | Alkalinity | mg/L as CaCO3 | 184 | 184 | 184 | 0 | 214 | 37.3333 | 82.5545 | -31.4286 | 38.7191 | -375.2172 | Alkalinity | mg/L as CaCO3 | 192 | 212 | -280.7273 | 232.4185 | -37.1429 | -276.1681 | 169.5229 | Alkalinity | mg/L as CaCO3 | 184 | 204 | 88.3478 | 56.6922 | -31.4286 | 89.2021 | -106.2731 | Alkalinity | mg/L as CaCO3 | 180 | 200 | 124.4444 | 37.7778 | -28.5714 | 124.9206 | -44.0916 | TOCp, mg/L | 1.3 | 2 | 1.2 | 0.9 | TOCp, mg/L | 1.3 | 2 | 1.2 | 0.9 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 51.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 3.9 | 3.8 | 3.85 | 2.5974 | 1998-04-13 | 14:15 | 6.25 | 23 | 60 | 58 | 263 | 3.23 | 1.6 | 4.83 | 0.20103 | 0.66874 | 53.4513 | 7.3723 | 7.7293 | 0 | 0 | 0 | 0 | 59 | 0.13101 | 1998-04-14 | 16:00 | 8.5 | 23 | 79 | 78 | 263 | 4.9 | 2.48 |  | 7.38 | 0.20103 | 0.66396 | 34.6369 | 11.184 | 11.7256 | 291.6914 | 241.7011 | 290.7601 | 0.49525 | 78.0048 | 0.15032 | [27 empty] | Total dissolved solids | mg/L | 238 | 240 | 239 | 0.83682 | 277 | 304 | -9.7473 | 7.5435 | 303.3858 | 21.2224 | Total dissolved solids | mg/L | 245 | 278 | 367.7273 | -32.276 | 5.2224 | 366.5436 | 33.1594 | Total dissolved solids | mg/L | 239 | 269 | 281.3913 | -4.6064 | 7.5435 | 281.0127 | 14.9505 | Total dissolved solids | mg/L | 233 | 261 | 268.4167 | -2.8416 | 9.8646 | 268.1131 | 13.0964 | UV254 F, cm-1 | 0.1575 | 0.1575 | 0.1575 | 0.1575 | UV254 F, cm-1 | 0.1575 | 0.1575 | 0.1575 | 0.1575 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 51.0754 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.161 | 0.154 | 0.1575 | 4.4444 | 1998-04-13 | 14:45 | 6.75 | 23 | 92 | 91 | 263 | 5.6 | 3.2 | 8.8 | 0.20103 | 0.63636 | 28.8864 | 12.7817 | 13.4007 | 0 | 0 | 0 | 0 | 91.5 | 0.14646 | 1998-04-15 | 7:30 | 24 | 23 | 80 | 78 | 263 | 4.76 | 2.44 |  | 7.2 | 0.20103 | 0.66111 | 35.5278 | 10.8644 | 11.3906 | 291.5143 | 241.5767 | 290.6105 | 0.49486 | 78.5051 | 0.14509 | 7.5 | 7.5 | 7.5 | 256 | 261 | 282 | 263.377 | 6.6039 | 0.96712 | 263.3103 | 2.7763 | 0.038 | 0.156 | 0.417 | 0.39062 | 6.3254 | 75.873 | 0.38743 | 90.1918 | [8 empty] | Total hardness | mg/L as CaCO3 | 218 | 216 | 217 | 0.92166 | 259 | 120.3333 | 53.5393 | -15.4255 | 121.2467 | -78.9739 | Total hardness | mg/L as CaCO3 | 218 | 236 | -54.7273 | 123.1895 | -15.9574 | -52.097 | 518.4505 | Total hardness | mg/L as CaCO3 | 206 | 238 | 166.8696 | 29.8867 | -9.5745 | 167.2191 | -23.1917 | Total hardness | mg/L as CaCO3 | 206 | 234 | 181 | 22.6496 | -9.5745 | 181.2143 | -13.6776 | UV254 p, cm-1 | 0.0325 | 0.051 | 0.025 | 0.021 | UV254 p, cm-1 | 0.0325 | 0.051 | 0.025 | 0.021 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.1282 | 4.0526 | 4.0904 | 1.8476 | 1998-04-13 | 15:15 | 7.25 | 23 | 81 | 79 | 263 | 5 | 2.55 | 7.55 | 0.20103 | 0.66225 | 33.8344 | 11.4122 | 11.9649 | 0 | 0 | 0 | 0 | 80 | 0.14956 | 1998-04-15 | 9:00 | 25.5 | 23 | 80 | 78 | 263 | 4.9 | 1.8 |  | 6.7 | 0.20103 | 0.73134 | 38.2537 | 11.184 | 11.7256 | 295.5429 | 244.8924 | 294.5992 | 0.50179 | 78.4982 | 0.14937 | [11 empty] | 0.037 |  | 0.419 | 0.48553 | -15.8778 | 76.5079 | 0.48135 | 92.3133 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 206 | 206 | 206 | 0 | 252 | 46 | 81.746 | -30.3797 | 47.5118 | -333.5766 | Calcium hardness | mg/L as CaCO3 | 190 | 226 | -100.9091 | 144.65 | -20.2532 | -98.1034 | 293.6732 | Calcium hardness | mg/L as CaCO3 | 190 | 232 | 120.4348 | 48.0885 | -20.2532 | 121.0561 | -56.952 | Calcium hardness | mg/L as CaCO3 | 190 | 214 | 145.5556 | 31.9834 | -20.2532 | 145.9365 | -30.1936 | BromideF, ug/L | 82 | 82 | 82 | 82 | BromideF, ug/L | 82 | 82 | 82 | 82 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 82 | NA | 82 | #VALUE! | 1998-04-13 | 16:15 | 8.25 | 23 | 81 | 79 | 263 | 5 | 2.56 | 7.56 | 0.20103 | 0.66138 | 33.7884 | 11.4122 | 11.9649 | 0 | 0 | 0 | 0 | 80 | 0.14956 | 1998-04-15 | 10:00 | 26.5 | 23 | 81 | 79 | 263 | 4.81 | 2.13 |  | 6.94 | 0.20103 | 0.69308 | 36.8963 | 10.9786 | 11.5103 | 293.3324 | 243.0753 | 292.4132 | 0.49798 | 79.502 | 0.14478 |  |  |  | 247 |  |  | 284.4695 |  | 4.4487 | 284.1268 | 13.067 | 0.038 |  |  | 0.42736 |  | 75.873 | 0.4238 | 91.0334 | [8 empty] | Turbidity | ntu | 0.08 | 0.09 | 0.085 | 11.7647 | 0.32 | 0.90167 | -181.7708 | 74.2424 | 0.89395 | 90.4916 | Turbidity | ntu | 0.08 | 0.55 | 2.3527 | -327.7686 | 75.7576 | 2.3308 | 96.5677 | Turbidity | ntu | 0.08 | 0.4 | 0.62348 | -55.8696 | 75.7576 | 0.61862 | 87.0681 | Turbidity | ntu | 0.09 | 0.67 | 0.42333 | 36.8159 | 72.7273 | 0.42048 | 78.5957 | Bromidep, ug/L | 74.5 | 71 | 68 | 68 | Bromidep, ug/L | 74.5 | 71 | 68 | 68 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 7 | NA | 7 | #VALUE! | 1998-04-13 | 18:00 | 10 | 23 | 81 | 79 | 263 | 5 | 2.45 | 7.45 | 0.20103 | 0.67114 | 34.302 | 11.4122 | 11.9649 | 0 | 0 | 0 | 0 | 80 | 0.14956 | 1998-04-15 | 11:30 | 28 | 23 | 81 | 79 | 263 | 4.9 | 2.5 |  | 7.4 | 0.20103 | 0.66216 | 34.5405 | 11.184 | 11.7256 | 291.5903 | 241.6172 | 290.6592 | 0.49508 | 79.5049 | 0.14748 | 7.5 |  |  | 249 |  |  | 277.12 |  | 3.675 | 276.858 | 10.0622 | 0.036 |  |  | 0.39564 |  | 77.1429 | 0.39229 | 90.8231 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 140 | 140 | 140 | 140 | AlkF, mg/L CaCO3 | 140 | 140 | 140 | 140
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.79 | NA | 0.79 | #VALUE! | 1998-04-14 | 7:00 | 23 | 23 | 81 | 80 | 263 | 5.08 | 1.69 | 6.77 | 0.20103 | 0.75037 | 37.8479 | 11.5948 | 12.1564 | 0 | 0 | 0 | 0 | 80.5 | 0.15101 | 1998-04-15 | 13:00 | 29.5 | 23 | 81 | 79 | 263 | 4.9 | 2.56 |  | 7.46 | 0.20103 | 0.65684 | 34.2547 | 11.184 | 11.7256 | 291.2904 | 241.3687 | 290.3603 | 0.49457 | 79.5054 | 0.14748 |  |  |  | 250 |  |  | 274.7695 |  | 3.2882 | 274.5388 | 8.9382 | 0.035 |  | 0.355 | 0.39197 | -10.4148 | 77.7778 | 0.38865 | 90.9944 | [8 empty] | Total organic carbon | mg/L | 1.3 | 1.3 | 1.3 | 0 | 9.9 | 9.8 | 1.0101 | 66.2338 | 9.7197 | 86.6251 | Total organic carbon | mg/L | 2 | 19.1 | 18.8182 | 1.4755 | 48.0519 | 18.656 | 89.2796 | Total organic carbon | mg/L | 1.2 | 7.3 | 6.9609 | 4.6456 | 68.8312 | 6.9094 | 82.6324 | Total organic carbon | mg/L | 0.9 | 5.8 | 4.9972 | 13.841 | 76.6234 | 4.9621 | 81.8625 | Alkp, mg/L CaCO3 | 184 | 192 | 184 | 180 | Alkp, mg/L CaCO3 | 184 | 192 | 184 | 180
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 6.21 | NA | 6.21 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 14:45 | 31.25 | 23 | 80 | 78 | 263 | 4.7 | 2.4 |  | 7.1 | 0.20103 | 0.66197 | 36.0423 | 10.7275 | 11.247 | 291.5556 | 241.6206 | 290.6632 | 0.49489 | 78.5051 | 0.14326 | [27 empty] | UV254 | cm-1 | 0.033 | 0.032 | 0.0325 | 3.0769 | 0.37 | 0.44917 | -21.3964 | 79.3651 | 0.44523 | 92.7004 | UV254 | cm-1 | 0.051 | 0.762 | 1.0192 | -33.7509 | 67.619 | 1.0098 | 94.9497 | UV254 | cm-1 | 0.025 | 0.276 | 0.31304 | -13.4216 | 84.127 | 0.31047 | 91.9477 | UV254 | cm-1 | 0.021 | 0.215 | 0.21058 | 2.0543 | 86.6667 | 0.20896 | 89.9502 | T-HdF, mg/L CaCO3 | 188 | 188 | 188 | 188 | T-HdF, mg/L CaCO3 | 188 | 188 | 188 | 188
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 26 | NA | 26 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 16:30 | 33 | 23 | 80 | 78 | 263 | 4.7 | 2.4 |  | 7.1 | 0.20103 | 0.66197 | 36.0423 | 10.7275 | 11.247 | 291.5556 | 241.6206 | 290.6632 | 0.49489 | 78.5051 | 0.14326 | [27 empty] | SUVA | L/(mg*m) | 2.5385 | 2.4615 | 2.5 | 3.0769 | 3.7374 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.55 | 3.9895 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.0833 | 3.7808 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.3333 | 3.7069 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 217 | 218 | 206 | 206 | T-Hdp, mg/L CaCO3 | 217 | 218 | 206 | 206
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.2 | NA | 8.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-16 | 7:45 | 48.25 | 23 | 80 | 78 | 263 | 4.7692 | 2 |  | 6.7692 | 0.20103 | 0.70455 | 37.8523 | 10.8855 | 11.4127 | 293.9822 | 243.6204 | 293.0689 | 0.49905 | 78.5009 | 0.14538 | 7.5 | 7.2 | 7.4 | 251 | 259 | 274 | 276.3846 | -0.8703 | 2.9014 | 276.1545 | 9.1088 | 0.034 | 0.157 | 0.387 | 0.452 | -16.7959 | 78.4127 | 0.44821 | 92.4143 | [8 empty] | Bromide | mg/L | 73 | 76 | 74.5 | 4.0268 | --- | 99.5 | --- | 9.1463 | 99.2638 | 24.9475 | Bromide | mg/L | 71 | --- | 171 | --- | 13.4146 | 170.0356 | 58.244 | Bromide | mg/L | 68 | --- | 98.4348 | --- | 17.0732 | 98.163 | 30.7274 | Bromide | mg/L | 68 | --- | 87.4444 | --- | 17.0732 | 87.2778 | 22.0879 | Ca-HdF, mg/L CaCO3 | 158 | 158 | 158 | 158 | Ca-HdF, mg/L CaCO3 | 158 | 158 | 158 | 158
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | NA | 24 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-16 | 9:45 | 50.25 | 23 | 80 | 78 | 263 | 4.76 | 2.0923 |  | 6.8523 | 0.20103 | 0.69466 | 37.3812 | 10.8644 | 11.3906 | 293.4157 | 243.1524 | 292.506 | 0.49808 | 78.5019 | 0.1451 |  |  |  | 248 |  |  | 282.3875 |  | 4.0619 | 282.0763 | 12.0805 | 0.034 |  | 0.386 | 0.43846 | -13.5913 | 78.4127 | 0.4348 | 92.1804 | [8 empty] | SDS-Cl2 dose | mg/L | 4 | 3 | 3.5 | 28.5714 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 206 | 190 | 190 | 190 | Ca-Hdp, mg/L CaCO3 | 206 | 190 | 190 | 190
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 275 | NA | 275 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-16 | 11:15 | 51.75 | 23 | 80 | 78 | 263 | 4.7 | 2.09 |  | 6.79 | 0.20103 | 0.69219 | 37.7334 | 10.7275 | 11.247 | 293.2677 | 243.0395 | 292.3701 | 0.49779 | 78.5022 | 0.14327 |  |  |  | 247 |  |  | 284.3612 |  | 4.4487 | 284.0274 | 13.0366 | 0.034 |  | 0.388 | 0.43523 | -12.172 | 78.4127 | 0.43164 | 92.1231 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.02 | 0.81 | 0.915 | 22.9508 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.17 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.24 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.06 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 80 | NA | 80 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-16 | 12:45 | 53.25 | 23 | 80 | 78 | 263 | 4.7273 | 2.0632 |  | 6.7904 | 0.20103 | 0.69617 | 37.731 | 10.7897 | 11.3123 | 293.4977 | 243.2257 | 292.5941 | 0.4982 | 78.5018 | 0.1441 | 7.4 |  |  | 250 |  | 278 | 277.9759 | 0.0086758 | 3.2882 | 277.7245 | 9.9827 | 0.034 | 0.155 | 0.391 | 0.44047 | -12.653 | 78.4127 | 0.43682 | 92.2165 | [8 empty] | SDS-Cl2 demand | mg/L | 2.98 | 2.19 | 2.585 | 30.5609 | --- | 14.6683 | --- | 58.3736 | 14.5542 | 82.2388 | SDS-Cl2 demand | mg/L | 1.83 | --- | 41.6482 | --- | 70.5314 | 41.2642 | 95.5652 | SDS-Cl2 demand | mg/L | 1.76 | --- | 11.4339 | --- | 71.6586 | 11.3475 | 84.49 | SDS-Cl2 demand | mg/L | 0.94 | --- | 8.2594 | --- | 84.8631 | 8.1967 | 88.532 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 24 | NA | 24 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-16 | 14:30 | 55 | 23 | 80 | 78 | 263 | 4.73 | 2 |  | 6.73 | 0.20103 | 0.70282 | 38.0788 | 10.796 | 11.3188 | 293.8785 | 243.5408 | 292.9732 | 0.49885 | 78.5011 | 0.14419 |  |  |  | 248 |  |  | 283.3325 |  | 4.0619 | 283.0148 | 12.3721 | [16 empty] | SDS-Chlorination temp. | oC | 26 | 26 | 26 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 54.7307 | 66.5487 | 53.1073 | 53.1073 | Qp/QT (THM4), % | 107.1325 | 130.2655 | 103.9548 | 103.9548
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 5.6 | NA | 5.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-16 | 16:00 | 56.5 | 23 | 80 | 78 | 263 | 4.8 | 2 |  | 6.8 | 0.20103 | 0.70588 | 37.6765 | 10.9557 | 11.4863 | 294.0628 | 243.6822 | 293.1433 | 0.49921 | 78.5008 | 0.14632 |  |  |  | 250 |  |  | 278.9 |  | 3.2882 | 278.6363 | 10.2773 | [16 empty] | SDS-Chlorination pH | --- | 8.2 | 8.2 | 8.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 8:00 | 72.5 | 23 | 80 | 78 | 263 | 4.8182 | 1.7852 |  | 6.6034 | 0.20103 | 0.72965 | 38.8279 | 10.9972 | 11.5298 | 295.4337 | 244.8153 | 294.5064 | 0.50155 | 78.4985 | 0.14688 | 7.5 | 7.5 | 7.5 | 247 | 259 | 280 | 289.5374 | -3.4062 | 4.4487 | 289.1478 | 14.5766 | 0.034 | 0.155 | 0.45 | 0.49081 | -9.07 | 78.4127 | 0.48663 | 93.0132 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 42.7984 | 44.6214 | 42.5203 | 44.5915 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 109.6 | NA | 109.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 9:15 | 73.75 | 23 | 80 | 78 | 263 | 4.8571 | 1.6857 |  | 6.5429 | 0.20103 | 0.74236 | 39.1965 | 11.0862 | 11.6231 | 296.1761 | 245.4242 | 295.2388 | 0.50283 | 78.4972 | 0.14807 | 7.5 |  |  | 248 |  | 280 | 288.7542 | -3.1265 | 4.0619 | 288.3779 | 14.0017 | 0.034 |  | 0.447 | 0.51335 | -14.8428 | 78.4127 | 0.50892 | 93.3192 | [8 empty] | SDS-TOX | mg Cl- /L | 100 | 105 | 102.5 | 4.878 | --- | 677.5 | --- | 62.7273 | 672.067 | 84.7485 | SDS-TOX | mg Cl- /L | 160 | --- | 1205.4545 | --- | 41.8182 | 1195.3717 | 86.615 | SDS-TOX | mg Cl- /L | 95 | --- | 486.3043 | --- | 65.4545 | 482.8094 | 80.3235 | SDS-TOX | mg Cl- /L | 82 | --- | 350.0556 | --- | 70.1818 | 347.7582 | 76.4204 | SDS-TOXb, ug Cl- /L | 180.5895 | 198.469 | 179.4068 | 172.5028 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 2.9 | NA | 2.9 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 10:15 | 74.75 | 23 | 80 | 78 | 263 | 4.86 | 1.6714 |  | 6.5314 | 0.20103 | 0.74409 | 39.2668 | 11.0927 | 11.6299 | 296.2776 | 245.5077 | 295.3394 | 0.50301 | 78.497 | 0.14816 |  |  |  | 248 |  | 281 | 289.0308 | -2.8579 | 4.0619 | 288.6517 | 14.0833 | 0.034 |  | 0.437 | 0.5166 | -18.2151 | 78.4127 | 0.51214 | 93.3612 | [8 empty] | SDS-CHCl3 | mg/L | 14 | 13 | 13.5 | 7.4074 | --- | 235.1667 | --- | 83.125 | 233.0722 | 94.2078 | SDS-CHCl3 | mg/L | 23 | --- | 541.1818 | --- | 71.25 | 536.1842 | 95.7104 | SDS-CHCl3 | mg/L | 12 | --- | 159.8261 | --- | 85 | 158.5058 | 92.4293 | SDS-CHCl3 | mg/L | 12 | --- | 106.4444 | --- | 85 | 105.635 | 88.6401 | SDS-CDb, mg/L | 4.226 | 3.2952 | 3.8467 | 3.4112 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | 29 | NA | 29 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 12:00 | 76.5 | 23 | 80 | 78 | 263 | 4.65 | 1.6462 |  | 6.2962 | 0.20103 | 0.73855 | 40.7715 | 10.6134 | 11.1274 | 295.9262 | 245.2507 | 295.0302 | 0.50227 | 78.4977 | 0.14175 | 7.6 |  |  | 248 |  | 281 | 288.16 | -2.5481 | 4.0619 | 287.805 | 13.8306 | [16 empty] | SDS-BDCM | mg/L | 14 | 13 | 13.5 | 7.4074 | --- | 48.5 | --- | 43.75 | 48.1693 | 71.9738 | SDS-BDCM | mg/L | 18 | --- | 72.5455 | --- | 25 | 72.0194 | 75.0067 | SDS-BDCM | mg/L | 12 | --- | 38.087 | --- | 50 | 37.854 | 68.2992 | SDS-BDCM | mg/L | 12 | --- | 28.6667 | --- | 50 | 28.5238 | 57.9299 | TOCb, mg/L | 2.4544 | 2.6188 | 2.4427 | 2.2833 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 41 | NA | 41 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 13:30 | 78 | 23 | 80 | 78 | 263 | 4.6429 | 1.7054 |  | 6.3483 | 0.20103 | 0.73136 | 40.4285 | 10.5971 | 11.1103 | 295.5087 | 244.9059 | 294.6154 | 0.50156 | 78.4984 | 0.14154 |  |  |  | 248 |  |  | 287.0852 |  | 4.0619 | 286.7402 | 13.5106 | [16 empty] | SDS-DBCM | mg/L | 12 | 11 | 11.5 | 8.6957 | --- | -8.1667 | --- | -105.3571 | -7.9808 | 244.0951 | SDS-DBCM | mg/L | 11 | --- | -38.0909 | --- | -96.4286 | -37.6175 | 129.2417 | SDS-DBCM | mg/L | 12 | --- | -1.913 | --- | -114.2857 | -1.7888 | 770.8489 | SDS-DBCM | mg/L | 12 | --- | 3.1111 | --- | -114.2857 | 3.1873 | -276.4952 | UV254 b, cm-1 | 0.089087 | 0.086626 | 0.087133 | 0.085008 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | 1 | NA | 1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 15:00 | 79.5 | 23 | 80 | 78 | 263 | 4.6667 | 1.6 |  | 6.2667 | 0.20103 | 0.74468 | 40.9681 | 10.6514 | 11.1673 | 296.2848 | 245.5452 | 295.3845 | 0.50289 | 78.4971 | 0.14226 |  |  |  | 250 |  | 280 | 283.2917 | -1.1756 | 3.2882 | 282.9963 | 11.6596 | [16 empty] | SDS-CHBr3 | mg/L | 2.4 | 2.4 | 2.4 | 0 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 77.8952 | 74.6796 | 74.565 | 74.565 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 1.6 | NA | 1.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-17 | 16:30 | 81 | 23 | 80 | 78 | 263 | 4.6875 | 1.6333 |  | 6.3208 | 0.20103 | 0.7416 | 40.6084 | 10.699 | 11.2171 | 296.1083 | 245.3956 | 295.2045 | 0.50261 | 78.4974 | 0.1429 | [27 empty] | SDS-THM4 | mg/L | 42.4 | 39.4 | 40.9 | 7.335 | --- | 269.9 | --- | 62.6825 | 267.7363 | 84.7238 | SDS-THM4 | mg/L | 53.1 | --- | 566.7364 | --- | 51.5511 | 561.7826 | 90.5479 | SDS-THM4 | mg/L | 38.8 | --- | 192.713 | --- | 64.5985 | 191.3384 | 79.7218 | SDS-THM4 | mg/L | 38.8 | --- | 137.1333 | --- | 64.5985 | 136.2906 | 71.5314 | Alkb, mg/L CaCO3 | 164.0815 | 174.6053 | 163.3672 | 161.2429 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 8.5 | NA | 8.5 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 7:30 | 81.5 | 23 | 80 | 79 | 263 | 4.53 | 0.94 |  | 5.47 | 0.20103 | 0.82815 | 47.0804 | 10.3395 | 10.8402 | 301.1983 | 249.6399 | 300.3102 | 0.51114 | 78.9889 | 0.13724 |  |  |  | 253 |  |  | 285.0053 |  | 2.1277 | 284.7297 | 11.1438 | 0.04 |  | 0.804 | 0.72375 | 9.9813 | 74.6032 | 0.71786 | 94.4279 | [8 empty] | SDS-MCAA* | mg/L | BMRL | 2.4 | 2.4 | #VALUE! | --- | 4.0667 | --- | 17.2414 | 4.0509 | 40.7542 | SDS-MCAA* | mg/L | 3.4 | --- | -1.1455 | --- | -17.2414 | -1.1016 | 408.6375 | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | 4.4 | --- | 2.3167 | --- | -51.7241 | 2.3345 | -88.4755 | T-Hdb, mg/L CaCO3 | 203.8719 | 207.9646 | 197.5593 | 197.5593 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | NR | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 8:00 | 82 | 23 | 80 | 79 | 263 | 4.5 | 0.58947 |  | 5.0895 | 0.20103 | 0.88418 | 50.6753 | 10.271 | 10.7684 | 304.5967 | 252.4616 | 303.7047 | 0.51689 | 78.9831 | 0.13634 |  |  |  | 243 |  |  | 376.8259 |  | 5.9961 | 375.681 | 35.3175 | 0.041 |  | 1.132 | 1.0469 | 7.5218 | 73.9683 | 1.0382 | 96.051 | [8 empty] | SDS-DCAA* | mg/L | 6.1 | 6.2 | 6.15 | 1.626 | --- | 82.3167 | --- | 78.7931 | 81.597 | 92.463 | SDS-DCAA* | mg/L | 11 | --- | 174.6364 | --- | 62.069 | 173.0582 | 93.6438 | SDS-DCAA* | mg/L | 5.8 | --- | 56.2348 | --- | 80 | 55.7843 | 89.6028 | SDS-DCAA* | mg/L | 5.7 | --- | 38.0611 | --- | 80.3448 | 37.7838 | 84.9142 | Ca-Hdb, mg/L CaCO3 | 184.2707 | 179.2956 | 174.9944 | 174.9944 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 2.5 | NA | 2.5 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 8:30 | 82.5 | 23 | 80 | 79 | 263 | 4.44 | 0.34276 |  | 4.7828 | 0.20103 | 0.92833 | 53.9892 | 10.1341 | 10.6249 | 307.3226 | 254.731 | 306.4347 | 0.52148 | 78.9785 | 0.13453 |  |  |  | 245 |  |  | 433.375 |  | 5.2224 | 431.7849 | 43.2588 | 0.043 |  |  | 1.6407 |  | 72.6984 | 1.6272 | 97.3574 | [8 empty] | SDS-TCAA* | mg/L | 5.3 | 5.2 | 5.25 | 1.9048 | --- | 124.4167 | --- | 87.1951 | 123.2907 | 95.7418 | SDS-TCAA* | mg/L | 12 | --- | 275.6364 | --- | 70.7317 | 273.0937 | 95.6059 | SDS-TCAA* | mg/L | 4.4 | --- | 83.9652 | --- | 89.2683 | 83.2546 | 94.715 | SDS-TCAA* | mg/L | 4.3 | --- | 55.2722 | --- | 89.5122 | 54.8354 | 92.1583
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 15 | NA | 15 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 9:00 | 83 | 23 | 80 | 79 | 263 | 4.67 | 0.34483 |  | 5.0148 | 0.20103 | 0.93124 | 51.4445 | 10.659 | 11.1752 | 307.5473 | 254.8784 | 306.6121 | 0.52201 | 78.978 | 0.1415 |  |  |  | 251 |  | 280 | 360.0725 | -28.5973 | 2.9014 | 359.1041 | 30.1038 | 0.047 |  |  | 1.654 |  | 70.1587 | 1.6397 | 97.1337 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 75.5 | NA | 75.5 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 9:30 | 83.5 | 23 | 80 | 79 | 263 | 4.57 | 0.32 |  | 4.89 | 0.20103 | 0.93456 | 52.7832 | 10.4308 | 10.9359 | 307.7368 | 255.0523 | 306.8213 | 0.52227 | 78.9777 | 0.13847 | 7.6 |  | 7.6 | 244 | 259 |  | 465.5781 |  | 5.6093 | 463.653 | 47.3744 | 0.05 | 0.155 | 0.764 | 1.6927 | -121.5621 | 68.254 | 1.6785 | 97.0211 | [8 empty] | SDS-DBAA* | mg/L | 3.1 | 3.2 | 3.15 | 3.1746 | --- | -2.0167 | --- | -96.875 | -1.9678 | 260.0733 | SDS-DBAA* | mg/L | 2.7 | --- | -7.3 | --- | -68.75 | -7.2036 | 137.4815 | SDS-DBAA* | mg/L | 3.2 | --- | -0.27826 | --- | -100 | -0.24719 | 1394.5268 | SDS-DBAA* | mg/L | 2.9 | --- | 1.0944 | --- | -81.25 | 1.1099 | -161.2804 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 84 | NA | 84 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 10:15 | 84.25 | 23 | 80 | 79 | 263 | 4.67 | 0.8 |  | 5.47 | 0.20103 | 0.85375 | 47.0804 | 10.659 | 11.1752 | 302.767 | 250.9168 | 301.8463 | 0.5139 | 78.9861 | 0.14148 |  |  |  | 250 |  | 280 | 308.1187 | -10.0424 | 3.2882 | 307.6028 | 18.7263 | 0.044 |  |  | 0.82006 |  | 72.0635 | 0.81317 | 94.5891 | [8 empty] | SDS-BCAA* | mg/L | 5.5 | 5.3 | 5.4 | 3.7037 | --- | 15.7333 | --- | 36.4706 | 15.6357 | 65.4636 | SDS-BCAA* | mg/L | 6.6 | --- | 23.8727 | --- | 22.3529 | 23.7061 | 72.1591 | SDS-BCAA* | mg/L | 5.2 | --- | 12.3739 | --- | 38.8235 | 12.3098 | 57.7574 | SDS-BCAA* | mg/L | 4.6 | --- | 10.0167 | --- | 45.8824 | 9.9702 | 53.8627 | Qp/QT (HAA5), % | 35.9833 | 46.3362 | 34.6216 | 36.9416 | Qp/QT (HAA5), % | 81.1715 | 104.5259 | 78.0998 | 83.3333
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 11:00 | 85 | 23 | 80 | 79 | 263 | 4.71 | 0.72 |  | 5.43 | 0.20103 | 0.8674 | 47.4346 | 10.7503 | 11.271 | 303.6054 | 251.6049 | 302.6741 | 0.51535 | 78.9847 | 0.1427 | 7.7 |  |  | 250 |  |  | 314.1042 |  | 3.2882 | 313.5302 | 20.2629 | 0.045 |  |  | 0.89344 |  | 71.4286 | 0.88584 | 94.9201 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 84.8795 | 83.42 | 85.0879 | 83.4454 | SDS-THM4b, ug/L | 53.8351 | NA | 54.3053 | 50.6
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 12:00 | 86 | 23 | 80 | 79 | 263 | 4.64 | 0.61176 |  | 5.2518 | 0.20103 | 0.88351 | 49.0784 | 10.5906 | 11.1035 | 304.5803 | 252.4245 | 303.6601 | 0.51696 | 78.983 | 0.14058 | 7.6 |  |  | 252 |  |  | 307.8 |  | 2.5145 | 307.3078 | 17.9975 | 0.047 |  | 0.62 | 0.9956 | -60.5806 | 70.1587 | 0.98723 | 95.2392 | [8 empty] | SDS-CDBAA | mg/L | 3.6 | 3.4 | 3.5 | 5.7143 | --- | 0.16667 | --- | -40 | 0.19816 | -1666.2296 | SDS-CDBAA | mg/L | 3.7 | --- | -7.2091 | --- | -48 | -7.1039 | 152.0842 | SDS-CDBAA | mg/L | 4 | --- | 0.73913 | --- | -60 | 0.76826 | -420.6604 | SDS-CDBAA | mg/L | 3.8 | --- | 1.9944 | --- | -52 | 2.0099 | -89.0624 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | NA | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-20 | 13:00 | 87 | 23 | 80 | 79 | 263 | 4.61 | 0.64 |  | 5.25 | 0.20103 | 0.8781 | 49.0952 | 10.5221 | 11.0317 | 304.2425 | 252.1496 | 303.3294 | 0.51636 | 78.9836 | 0.13967 |  | 7.6 |  | 252 | 260 |  | 305.3203 |  | 2.5145 | 304.853 | 17.3372 | 0.05 | 0.153 |  | 0.93184 |  | 68.254 | 0.92411 | 94.5894 | [8 empty] | SDS-DCBAA | mg/L | 6.5 | 5.7 | 6.1 | 13.1148 | --- | 35.7667 | --- | 59.3333 | 35.4864 | 82.8103 | SDS-DCBAA | mg/L | 10 | --- | 55.4545 | --- | 33.3333 | 55.0162 | 81.8235 | SDS-DCBAA | mg/L | 6 | --- | 25.5652 | --- | 60 | 25.3905 | 76.3691 | SDS-DCBAA | mg/L | 5.5 | --- | 18.6944 | --- | 63.3333 | 18.5814 | 70.4004 | SDS-TOXb, ug Cl- /L | 212.9289 | 221.7134 | 212.6812 | 203.7027 | SDS-TOXb, ug Cl- /L | 134.9791 | NA | 134.4203 | 114.1667
[44 empty] | 1998-04-20 | 15:00 | 89 | 23 | 79 | 78 | 263 | 4.5556 | 0.58333 |  | 5.1389 | 0.20103 | 0.88649 | 50.1784 | 10.3978 | 10.9014 | 304.7483 | 252.578 | 303.8447 | 0.51719 | 77.9828 | 0.13979 |  |  |  | 251 |  |  | 317.0714 |  | 2.9014 | 316.4992 | 20.6949 | [16 empty] | SDS-HAA5 | mg/L | 14.5 | 17 | 15.75 | 15.873 | --- | 214.9167 | --- | 79.1391 | 213.0348 | 92.6068 | SDS-HAA5 | mg/L | 29.1 | --- | 450.9182 | --- | 61.457 | 446.85 | 93.4877 | SDS-HAA5 | mg/L | 13.4 | --- | 148.4 | --- | 82.2517 | 147.1942 | 90.8964 | SDS-HAA5 | mg/L | 17.3 | --- | 98.1333 | --- | 77.0861 | 97.4406 | 82.2456 | SDS-CDb, mg/L | 4.9056 | 4.1805 | 4.6693 | 4.2632 | SDS-CDb, mg/L | 3.2675 | NA | 2.7346 | 1.8183
[44 empty] | 1998-04-20 | 16:30 | 90.5 | 23 | 80 | 78 | 263 | 4.58 | 0.48 |  | 5.06 | 0.20103 | 0.90514 | 50.9763 | 10.4536 | 10.9599 | 305.9042 | 253.5319 | 304.9922 | 0.51916 | 78.4808 | 0.13965 | [27 empty] | SDS-HAA6 | mg/L | 20 | 22.3 | 21.15 | 10.8747 | --- | 230.65 | --- | 74.8214 | 228.6705 | 90.7509 | SDS-HAA6 | mg/L | 35.7 | --- | 474.7909 | --- | 57.5 | 470.5561 | 92.4132 | SDS-HAA6 | mg/L | 18.6 | --- | 160.7739 | --- | 77.8571 | 159.5041 | 88.3389 | SDS-HAA6 | mg/L | 21.9 | --- | 108.15 | --- | 73.9286 | 107.4108 | 79.611 | TOCb, mg/L | 2.9324 | 2.9928 | 2.9325 | 2.7602 | TOCb, mg/L | 1.7801 | NA | 1.7804 | 1.3917
[44 empty] | 1998-04-21 | 7:30 | 105.5 | 23 | 80 | 78 | 263 | 4.39 | 0.4 |  | 4.79 | 0.20103 | 0.91649 | 53.9061 | 10.0199 | 10.5052 | 306.5748 | 254.1196 | 305.6992 | 0.52017 | 78.4798 | 0.13386 |  |  |  | 252 |  |  | 329.8375 |  | 2.5145 | 329.1879 | 23.448 | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.11252 | 0.10815 | 0.11163 | 0.10707 | UV254 b, cm-1 | 0.056036 | NA | 0.054018 | 0.04375
[44 empty] | 1998-04-21 | 7:45 | 105.75 | 23 | 81 | 80 | 263 | 4.67 | 4.64 |  | 9.31 | 0.20103 | 0.50161 | 27.2492 | 10.659 | 11.1752 | 282.7928 | 234.3632 | 281.9329 | 0.48 | 80.02 | 0.13966 | 7.6 | 7.6 |  | 249 | 257 |  | 268.0614 |  | 3.675 | 267.8922 | 7.0522 | 0.055 | 0.154 |  | 0.26066 |  | 65.0794 | 0.25884 | 78.7511 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 79.3013 | 76.903 | 77.153 | 76.8282 | Bromideb, ug/L | 75.9121 | NA | 71.066 | 70.3333
[44 empty] | 1998-04-21 | 8:15 | 106.25 | 23 | 82 | 80 | 263 | 4.71 | 3.89 |  | 8.6 | 0.20103 | 0.54767 | 29.5814 | 10.7503 | 11.271 | 285.2583 | 236.4003 | 284.3833 | 0.48421 | 80.5158 | 0.13998 | 7.6 |  | 7.7 | 242 |  | 279 | 278.4781 | 0.18704 | 6.383 | 278.1515 | 12.9971 | 0.036 |  | 0.645 | 0.30461 | 52.7734 | 77.1429 | 0.30221 | 88.0876 | [47 empty] | Alkb, mg/L CaCO3 | 155.8326 | 164.0948 | 155.2335 | 154.7766 | Alkb, mg/L CaCO3 | 175.7155 | NA | 174.3639 | 173.3333
[44 empty] | 1998-04-21 | 9:00 | 107 | 23 | 82 | 81 | 263 | 4.67 | 4.3 |  | 8.97 | 0.20103 | 0.52062 | 28.32 | 10.659 | 11.1752 | 283.8037 | 235.2011 | 282.9407 | 0.48171 | 81.0183 | 0.13793 |  |  |  | 238 |  | 275 | 280.764 | -2.096 | 7.9304 | 280.3843 | 15.1165 | 0.029 |  | 0.443 | 0.29706 | 32.9442 | 81.5873 | 0.29468 | 90.1587 | [47 empty] | T-Hdb, mg/L CaCO3 | 198.4351 | 201.9009 | 194.2319 | 194.6495 | T-Hdb, mg/L CaCO3 | 211.5397 | NA | 202.058 | 203
[44 empty] | 1998-04-21 | 10:00 | 108 | 23 | 83 | 82 | 263 | 4.73 | 5.04 |  | 9.77 | 0.20103 | 0.48414 | 25.9191 | 10.796 | 11.3188 | 281.8748 | 233.5932 | 281.0065 | 0.47847 | 82.0215 | 0.138 |  |  |  | 239 |  | 274 | 276.8006 | -1.0221 | 7.5435 | 276.4607 | 13.5501 | 0.024 |  | 0.349 | 0.28279 | 18.9717 | 84.7619 | 0.28046 | 91.4427 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 175.272 | 172.8276 | 169.0789 | 169.8213 | Ca-Hdb, mg/L CaCO3 | 196.9623 | NA | 182.9919 | 184.6667
[44 empty] | 1998-04-21 | 13:00 | 111 | 23 | 80 | 78 | 263 | 4.6 | 4.8 |  | 9.4 | 0.20103 | 0.48936 | 26.9787 | 10.4993 | 11.0077 | 282.1395 | 233.8327 | 281.2946 | 0.47884 | 78.5212 | 0.14019 |  |  |  | 235 | 257 |  | 281.0208 |  | 9.0909 | 280.6184 | 16.2564 | 0.024 | 0.153 |  | 0.28544 |  | 84.7619 | 0.28315 | 91.524 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-04-21 | 14:30 | 112.5 | 23 | 80 | 78 | 263 | 4.6 | 4.8 |  | 9.4 | 0.20103 | 0.48936 | 26.9787 | 10.4993 | 11.0077 | 282.1395 | 233.8327 | 281.2946 | 0.47884 | 78.5212 | 0.14019 | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-04-21 | 16:30 | 114.5 | 23 | 80 | 78 | 263 | 4.6 | 4.8 |  | 9.4 | 0.20103 | 0.48936 | 26.9787 | 10.4993 | 11.0077 | 282.1395 | 233.8327 | 281.2946 | 0.47884 | 78.5212 | 0.14019 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-04-22 | 7:30 | 129.5 | 23 | 80 | 78 | 263 | 4.57 | 2.1943 |  | 6.7643 | 0.20103 | 0.67561 | 37.8807 | 10.4308 | 10.9359 | 292.3096 | 242.2663 | 291.44 | 0.49609 | 78.5039 | 0.1393 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-04-22 | 7:45 | 129.75 | 23 | 81 | 79 | 263 | 4.69 | 16.1 |  | 20.79 | 0.20103 | 0.22559 | 11.6503 | 10.7047 | 11.2231 | 268.8887 | 222.8373 | 268.0675 | 0.45641 | 79.5436 | 0.14109 | 7.6 | 7.7 | 7.6 | 244 |  |  | 262.7239 |  | 5.6093 | 262.557 | 7.0678 | 0.027 |  |  | 0.19552 |  | 82.8571 | 0.19401 | 86.0834 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-04-22 | 8:30 | 130.5 | 23 | 83 | 82 | 263 | 4.75 | 11.7 |  | 16.45 | 0.20103 | 0.28875 | 14.9878 | 10.8416 | 11.3667 | 271.9516 | 225.3667 | 271.1102 | 0.46164 | 82.0384 | 0.13855 |  |  |  | 239 | 259 | 267 | 266.4167 | 0.21848 | 7.5435 | 266.1691 | 10.2075 | 0.02 | 0.153 | 0.214 | 0.21332 | 0.31652 | 87.3016 | 0.21158 | 90.5472 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-04-22 | 9:15 | 131.25 | 23 | 84 | 82 | 263 | 4.75 | 10.67 |  | 15.42 | 0.20103 | 0.30804 | 16.0558 | 10.8416 | 11.3667 | 272.9001 | 226.1527 | 272.0558 | 0.46325 | 82.5367 | 0.13772 |  |  |  | 236 |  | 262 | 268.5164 | -2.4872 | 8.7041 | 268.2228 | 12.0134 | 0.02 |  | 0.209 | 0.21871 | -4.6466 | 87.3016 | 0.21692 | 90.7799 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-04-22 | 10:30 | 132.5 | 23 | 84 | 83 | 263 | 4.96 | 8.7 |  | 13.66 | 0.20103 | 0.3631 | 18.2533 | 11.3209 | 11.8692 | 275.6572 | 228.4057 | 274.7661 | 0.46806 | 83.0319 | 0.14295 | 7.6 |  |  | 233 | 257 | 266 | 273.0379 | -2.6458 | 9.8646 | 272.6604 | 14.5457 | 0.02 | 0.15 | 0.214 | 0.23589 | -10.2293 | 87.3016 | 0.23386 | 91.4477 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-04-22 | 11:20 | 133.3333 | 23 | 80 | 80 | 263 | 4.57 | 9.57 |  | 14.14 | 0.20103 | 0.3232 | 17.5997 | 10.4308 | 10.9359 | 273.6409 | 226.7936 | 272.8268 | 0.4644 | 79.5356 | 0.1375 | 7.7 |  |  | 234 |  | 266 | 270.1996 | -1.5788 | 9.4778 | 269.8851 | 13.2964 | 0.019 |  | 0.219 | 0.22364 | -2.118 | 87.9365 | 0.22186 | 91.4361 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-04-22 | 13:40 | 135.6667 | 23 | 80 | 79 | 263 | 4.55 | 10.67 |  | 15.22 | 0.20103 | 0.29895 | 16.2799 | 10.3851 | 10.8881 | 272.4427 | 225.8036 | 271.6358 | 0.46236 | 79.0376 | 0.13776 | 7.8 | 7.7 |  | 235 |  | 263 | 268.5211 | -2.0993 | 9.0909 | 268.2311 | 12.389 | 0.02 |  | 0.214 | 0.21613 | -0.99721 | 87.3016 | 0.21444 | 90.6733 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-04-22 | 14:45 | 136.75 | 23 | 80 | 80 | 263 | 4.39 | 9.17 |  | 13.56 | 0.20103 | 0.32375 | 18.3953 | 10.0199 | 10.5052 | 273.6589 | 226.8356 | 272.8773 | 0.46432 | 79.5357 | 0.13208 | 7.6 |  | 7.7 | 233 |  | 265 | 270.7077 | -2.1539 | 9.8646 | 270.393 | 13.8291 | 0.019 |  | 0.215 | 0.2238 | -4.0953 | 87.9365 | 0.2221 | 91.4451 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-04-22 | 16:15 | 138.25 | 23 | 80 | 78 | 263 | 4.6667 | 13.33 |  | 17.9967 | 0.20103 | 0.25931 | 13.6138 | 10.6514 | 11.1673 | 270.5127 | 224.1866 | 269.6907 | 0.45915 | 78.5408 | 0.14218 |  |  |  | 230 |  | 264 | 268.4775 | -1.696 | 11.0251 | 268.1361 | 14.2227 | [55 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-04-23 | 7:30 | 153.5 | 23 | 80 | 78 | 263 | 4.5 | 12.4 |  | 16.9 | 0.20103 | 0.26627 | 14.5621 | 10.271 | 10.7684 | 270.8438 | 224.4859 | 270.0506 | 0.45961 | 78.5404 | 0.13711
[44 empty] | 1998-04-23 | 8:00 | 154 | 23 | 80 | 78 | 263 | 4.6 | 12.3 | X | 16.9 | 0.20103 | 0.27219 | 14.5621 | 10.4993 | 11.0077 | 271.1358 | 224.713 | 270.3238 | 0.46017 | 78.5398 | 0.14015
[44 empty] | 1998-04-23 | 11:40 |  | 23 | 42 | 42 | 263 | 2.4 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 5.4779 | 5.7432 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-23 | 12:00 |  | 23 | 64 | 62 | 263 | 3.5 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 7.9886 | 8.3755 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-23 | 12:15 |  | 23 | 81 | 80 | 263 | 4.5 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 10.271 | 10.7684 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-23 | 12:30 |  | 23 | 92 | 91 | 263 | 5.4 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 12.3252 | 12.9221 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on BV7: Alison Gusses: Consultant verified MTCw values. However, no explanation was given as to why the MTCw was lower during the 1st quarter relative to the other 3 quarters
Note on DG10: Alison Gusses: Consultant verified all water quality parameters due to high mass balance closure errors
Note on DQ10: Alison Gusses: Consultant verified all water quality parameters due to high mass balance closure errors
Note on EA10: Alison Gusses: Consultant verified all water quality parameters due to high mass balance closure errors
Note on EK10: Alison Gusses: Consultant verified all water quality parameters due to high mass balance closure errors

## 7450. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Hydranautics Corp. | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.17931 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.54 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-06-17 | 1998-06-27 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.36 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.46 | [7 empty] | Feed flow rate during sample collection (mL/min) | 8.83 | [7 empty] | Feed flow rate during sample collection (mL/min) | 15 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 1000 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 302 | [10 empty] | Influent flow rate during sample collection (mL/min) | 302 | [7 empty] | Influent flow rate during sample collection (mL/min) | 302 | [7 empty] | Influent flow rate during sample collection (mL/min) | 302 | [6 empty] | SDS-THM4F, ug/L | 154.1 | 154.1 | 154.1 | 154.1 | SDS-THM4F, ug/L | 154.1 | 154.1 | 154.1 | 154.1 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | -240 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 47.35 | 58.5 | 40.1 | 32.9 | SDS-THM4p, ug/L | 47.35 | 58.5 | 40.1 | 32.9 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.78 | 8.02 | 7.9 | 3.038 | 1998-06-26 | 9:30 | 0 | 24.5 | [17 empty] | 1998-06-27 | 9:00 | 0 | 23 | 55 | 53 | 302 | 7.42 | 3.05 |  | 10.47 | 0.23084 | 0.70869 | 27.8443 | 16.9358 | 17.756 | 325.1715 | 265.6653 | 323.7095 | 0.58775 | 53.4122 | 0.33243 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 61 | 61 | 61 | 61 | SDS-HAA5F, ug/L | 61 | 61 | 61 | 61 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-06-26 | 10:00 | 0.5 | 24.5 | 64 | 62 | 302 | 7.7 | 3.13 | 10.83 | 0.23084 | 0.71099 | 26.8855 | 17.5748 | 17.6269 | 0 | 0 | 0 | 0 | 63 | 0.27979 | 1998-06-27 | 9:30 | 0.5 | 23 | 55 | 53 | 302 | 7.42 | 3.05 |  | 10.47 | 0.23084 | 0.70869 | 27.8443 | 16.9358 | 17.756 | 325.1715 | 265.6653 | 323.7095 | 0.58775 | 53.4122 | 0.33243 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 10.35 | 14 | 7.1 | 5.8 | SDS-HAA5p, ug/L | 10.35 | 14 | 7.1 | 5.8 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 212 | 312 | 262 | 38.1679 | 1998-06-26 | 10:30 | 1 | 24.5 | 60 | 58 | 302 | 7.2 | 2.46 | 9.66 | 0.23084 | 0.74534 | 30.2629 | 16.4336 | 16.4823 | 0 | 0 | 0 | 0 | 59 | 0.27936 | 1998-06-27 | 10:00 | 1 | 23 | 55 | 53 | 302 | 7.13 | 2.93 |  | 10.06 | 0.23084 | 0.70875 | 29.0199 | 16.2738 | 17.062 | 325.1364 | 265.6845 | 323.7328 | 0.5875 | 53.4125 | 0.31944 | [27 empty] | Sampling date | MM/DD/YY | 1998-06-28 | 1998-06-29 | --- | --- | 1998-06-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-30 | 1998-06-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-01 | 1998-07-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-02 | 1998-07-02 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 387.5 | 387.5 | 387.5 | 387.5 | SDS-TOXF, ug Cl- /L | 387.5 | 387.5 | 387.5 | 387.5 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 276 | 290 | 283 | 4.947 | 1998-06-26 | 11:15 | 1.75 | 24.5 | 60 | 58 | 302 | 7.52 | 2.36 | 9.88 | 0.23084 | 0.76113 | 29.5668 | 17.164 | 17.2148 | 0 | 0 | 0 | 0 | 59 | 0.29178 | 1998-06-27 | 11:00 | 2 | 23 | 55 | 53 | 302 | 7.07 | 3.02 |  | 10.09 | 0.23084 | 0.70069 | 28.9306 | 16.1369 | 16.9184 | 324.5793 | 265.2391 | 323.1901 | 0.58646 | 53.4135 | 0.31674 | [27 empty] | Sampling time | hh:mm | 10:00 | 8:30 | --- | --- | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:30 | 11:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:10 | 11:10 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 90.5 | 125 | 68 | 59 | SDS-TOXp, ug Cl- /L | 90.5 | 125 | 68 | 59 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 242 | 306 | 274 | 23.3577 | 1998-06-26 | 11:30 | 2 | 24.5 | 56 | 54 | 302 | 7.4 | 7.6 | 15 | 0.23084 | 0.49333 | 19.1333 | 16.8901 | 16.9401 | 0 | 0 | 0 | 0 | 55 | 0.308 | 1998-06-27 | 12:00 | 3 | 23 | 55 | 53 | 302 | 6.89 | 2.62 |  | 9.51 | 0.23084 | 0.7245 | 30.756 | 15.7261 | 16.4877 | 326.1829 | 266.5792 | 324.8231 | 0.58924 | 53.4108 | 0.3087 | 8.14 | 7.98 | 8.17 | 278 | 288 | 301 | 296.1489 | 1.6117 | 1.7668 | 295.9418 | 6.0626 | 0.034 | 0.141 | 0.294 | 0.39516 | -34.4089 | 74.5318 | 0.39104 | 91.3053 | [8 empty] | Operation time | hh.hh | 25 | 47.5 | --- | --- | 25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 79.5 | 79.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101 | 101 | --- | --- | --- | --- | --- | Cumulative time | hr | 122.17 | 122.17 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 3.58 | 3.58 | 3.58 | 3.58 | SDS-CDF, mg/L | 3.58 | 3.58 | 3.58 | 3.58 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 236 | 286 | 261 | 19.1571 | 1998-06-26 | 11:45 | 2.25 | 24.5 | 55 | 54 | 302 | 7.1 | 5.5 | 12.6 | 0.23084 | 0.56349 | 22.9683 | 16.2054 | 16.2533 | 0 | 0 | 0 | 0 | 54.5 | 0.29823 | 1998-06-27 | 13:00 | 4 | 23 | 55 | 53 | 302 | 6.69 | 2.68 |  | 9.37 | 0.23084 | 0.71398 | 31.2305 | 15.2696 | 16.0091 | 325.4348 | 266.0007 | 324.1182 | 0.58776 | 53.4122 | 0.29973 | 8.12 | 7.96 | 8.12 | 272 | 290 | 300 | 310.459 | -3.4863 | 3.8869 | 310.033 | 12.2674 | 0.034 | 0.136 | 0.318 | 0.38188 | -20.0877 | 74.5318 | 0.37803 | 91.0059 | [8 empty] | pH | --- | 8.44 | 8.5 | 8.47 | 0.70838 | 8.24 | --- | --- | --- | --- | --- | pH | --- | 8.47 | 8.18 | --- | --- | --- | --- | --- | pH | --- | 8.36 | 8.3 | --- | --- | --- | --- | --- | pH | --- | 7.87 | 8.19 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.105 | 1.19 | 0.84 | 0.74 | SDS-CDp, mg/L | 1.105 | 1.19 | 0.84 | 0.74 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 53.9325 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.15 | 0.147 | 0.1485 | 2.0202 | 1998-06-26 | 13:15 | 3.75 | 24.5 | 56 | 54 | 302 | 7.6 | 2.37 | 9.97 | 0.23084 | 0.76229 | 29.2909 | 17.3466 | 17.3979 | 0 | 0 | 0 | 0 | 55 | 0.31633 | 1998-06-27 | 14:00 | 5 | 23 | 55 | 53 | 302 | 6.59 | 2.58 |  | 9.17 | 0.23084 | 0.71865 | 31.9335 | 15.0413 | 15.7698 | 325.7404 | 266.267 | 324.4427 | 0.58825 | 53.4118 | 0.29525 | 8.16 | 8.03 | 8.16 | 273 | 290 | 300 | 308.5426 | -2.8475 | 3.5336 | 308.1548 | 11.4082 | 0.035 | 0.138 | 0.328 | 0.38509 | -17.407 | 73.7828 | 0.38128 | 90.8203 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 4 | 4 | 4 | 4 | TOCF, mg/L | 4 | 4 | 4 | 4 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 63.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.13 | BMRL | 0.13 | #VALUE! | 1998-06-26 | 14:15 | 4.75 | 24.5 | 55 | 55 | 302 | 7.25 | 4.56 | 11.81 | 0.23084 | 0.61389 | 24.5715 | 16.5477 | 16.5967 | 0 | 0 | 0 | 0 | 55 | 0.30176 | 1998-06-27 | 15:00 | 6 | 23 | 55 | 53 | 302 | 6.55 | 2.55 |  | 9.1 | 0.23084 | 0.71978 | 32.1868 | 14.95 | 15.6741 | 325.8125 | 266.3325 | 324.5225 | 0.58835 | 53.4117 | 0.29346 | 8.12 | 8 | 8.12 | 268 | 289 | 301 | 321.5294 | -6.8204 | 5.3004 | 320.9489 | 16.4976 | 0.035 | 0.139 | 0.343 | 0.38651 | -12.6851 | 73.7828 | 0.3827 | 90.8544 | [8 empty] | Alkalinity | mg/L as CaCO3 | 210 | 254 | 232 | 18.9655 | 342 | 328.7742 | 3.8672 | 11.4504 | 327.85 | 29.2359 | Alkalinity | mg/L as CaCO3 | 224 | 362 | 604 | -66.8508 | 14.5038 | 600.9084 | 62.7231 | Alkalinity | mg/L as CaCO3 | 206 | 308 | 327.7391 | -6.4088 | 21.374 | 326.7781 | 36.9603 | Alkalinity | mg/L as CaCO3 | 210 | 284 | 284.2857 | -0.1006 | 19.8473 | 283.7323 | 25.9866 | TOCp, mg/L | 1.25 | 1.6 | 0.9 | 0.8 | TOCp, mg/L | 1.25 | 1.6 | 0.9 | 0.8 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 51.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 3.9 | 4.1 | 4 | 5 | 1998-06-26 | 15:00 | 5.5 | 24.5 | 55 | 54 | 302 | 7.3 | 4 | 11.3 | 0.23084 | 0.64602 | 25.7257 | 16.6619 | 16.7112 | 0 | 0 | 0 | 0 | 54.5 | 0.30663 | 1998-06-27 | 16:00 | 7 | 23 | 55 | 53 | 302 | 6.46 | 2.46 |  | 8.92 | 0.23084 | 0.72422 | 32.8565 | 14.7446 | 15.4587 | 326.1041 | 266.5857 | 324.831 | 0.58882 | 53.4112 | 0.28943 | 8.03 | 8.01 | 8.17 | 268 | 287 | 302 | 322.3902 | -6.7517 | 5.3004 | 321.8085 | 16.7207 | 0.034 | 0.137 | 0.353 | 0.39479 | -11.8381 | 74.5318 | 0.39093 | 91.3028 | [8 empty] | Total dissolved solids | mg/L | 252 | 263 | 257.5 | 4.2718 | 304 | 339.7581 | -11.7625 | 9.0106 | 338.9725 | 24.0351 | Total dissolved solids | mg/L | 268 | 314 | 418 | -33.121 | 5.3004 | 416.7796 | 35.6974 | Total dissolved solids | mg/L | 261 | 275 | 308.8261 | -12.3004 | 7.7739 | 308.4485 | 15.383 | Total dissolved solids | mg/L | 226 | 280 | 307.4286 | -9.7959 | 20.1413 | 306.8219 | 26.3416 | UV254 F, cm-1 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | UV254 F, cm-1 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 51.0754 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.136 | 0.131 | 0.1335 | 3.7453 | 1998-06-26 | 15:15 | 5.75 | 24.5 | 56 | 54 | 302 | 7.13 | 2.93 | 10.06 | 0.23084 | 0.70875 | 29.0199 | 16.2738 | 16.322 | 0 | 0 | 0 | 0 | 55 | 0.29676 | 1998-06-27 | 17:00 | 8 | 23 | 55 | 53 | 302 | 6.35 | 2.41 |  | 8.76 | 0.23084 | 0.72489 | 33.4749 | 14.4935 | 15.1955 | 326.135 | 266.6291 | 324.8838 | 0.5888 | 53.4112 | 0.2845 | 8.09 | 7.97 | 8.16 | 273 | 288 | 307 | 309.3485 | -0.765 | 3.5336 | 308.9664 | 11.6409 | 0.034 | 0.138 | 0.362 | 0.39567 | -9.3006 | 74.5318 | 0.39187 | 91.3236 | [8 empty] | Total hardness | mg/L as CaCO3 | 246 | 254 | 250 | 3.2 | 314 | 327.4194 | -4.2737 | 8.7591 | 326.68 | 23.4725 | Total hardness | mg/L as CaCO3 | 310 | 386 | -50 | 112.9534 | -13.1387 | -47.0711 | 758.5778 | Total hardness | mg/L as CaCO3 | 252 | 310 | 299.8261 | 3.2819 | 8.0292 | 299.4485 | 15.8453 | Total hardness | mg/L as CaCO3 | 246 | 308 | 286 | 7.1429 | 10.219 | 285.702 | 13.8963 | UV254 p, cm-1 | 0.026 | 0.034 | 0.015 | 0.011 | UV254 p, cm-1 | 0.026 | 0.034 | 0.015 | 0.011 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.4872 | 3.1951 | 3.3412 | 8.7412 | 1998-06-26 | 15:30 | 6 | 24.5 | 56 | 54 | 302 | 7.29 | 3.64 | 10.93 | 0.23084 | 0.66697 | 26.6304 | 16.639 | 16.6883 | 0 | 0 | 0 | 0 | 55 | 0.30342 | 1998-06-27 | 18:00 | 9 | 23 | 55 | 53 | 302 | 6.43 | 2.44 |  | 8.87 | 0.23084 | 0.72492 | 33.0474 | 14.6761 | 15.3869 | 326.148 | 266.6266 | 324.8807 | 0.58888 | 53.4111 | 0.28808 | 8.19 | 8.01 | 8.25 | 280 | 288 | 307 | 290.9057 | 5.2424 | 1.0601 | 290.7896 | 3.7105 | 0.036 | 0.135 | 0.366 | 0.39044 | -6.6766 | 73.0337 | 0.38666 | 90.6896 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 218 | 232 | 225 | 6.2222 | 296 | 341.129 | -15.2463 | 13.7931 | 340.02 | 33.8274 | Calcium hardness | mg/L as CaCO3 | 244 | 354 | 414 | -16.9492 | 6.5134 | 412.6169 | 40.8652 | Calcium hardness | mg/L as CaCO3 | 228 | 292 | 299.7391 | -2.6504 | 12.6437 | 299.1728 | 23.7899 | Calcium hardness | mg/L as CaCO3 | 232 | 264 | 273.4286 | -3.5714 | 11.1111 | 273.1199 | 15.0556 | BromideF, ug/L | 62 | 62 | 62 | 62 | BromideF, ug/L | 62 | 62 | 62 | 62 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 62 | 62 | 62 | 0 | 1998-06-26 | 15:45 | 6.25 | 24.5 | 56 | 54 | 302 | 7.3 | 3.7 | 11 | 0.23084 | 0.66364 | 26.4545 | 16.6619 | 16.7112 | 0 | 0 | 0 | 0 | 55 | 0.30384 | 1998-06-27 | 19:00 | 10 | 23 | 55 | 53 | 302 | 6.5 | 2.15 |  | 8.65 | 0.23084 | 0.75145 | 33.9133 | 14.8359 | 15.5544 | 327.9882 | 268.1193 | 326.6996 | 0.59225 | 53.4078 | 0.29124 | 8.1 | 7.95 | 8.13 | 272 | 282 | 303 | 316.2558 | -4.3749 | 3.8869 | 315.7796 | 13.864 | 0.043 | 0.139 | 0.379 | 0.4071 | -7.4155 | 67.7903 | 0.40319 | 89.335 | [8 empty] | Turbidity | ntu | 0.067 | 0.051 | 0.059 | 27.1186 | 0.152 | 0.34771 | -128.7564 | 60.2694 | 0.34495 | 82.8962 | Turbidity | ntu | 0.049 | 0.245 | 1.044 | -326.1224 | 67.0034 | 1.0359 | 95.2698 | Turbidity | ntu | 0.042 | 0.21 | 0.27352 | -30.2484 | 71.7172 | 0.27169 | 84.5414 | Turbidity | ntu | 0.052 | 0.145 | 0.18986 | -30.936 | 64.9832 | 0.18883 | 72.462 | Bromidep, ug/L | 60 | 63 | 61 | 58 | Bromidep, ug/L | 60 | 63 | 61 | 58 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | 1998-06-26 | 16:00 | 6.5 | 24.5 | 56 | 54 | 302 | 7.07 | 3.6 | 10.67 | 0.23084 | 0.66261 | 27.3037 | 16.1369 | 16.1847 | 0 | 0 | 0 | 0 | 55 | 0.29427 | 1998-06-27 | 19:30 | 10.5 | 23 | 55 | 53 | 302 | 6.44 | 3.48 |  | 9.92 | 0.23084 | 0.64919 | 29.4435 | 14.699 | 15.4108 | 321.0364 | 262.4462 | 319.787 | 0.57966 | 53.4203 | 0.28848 | [27 empty] | Ammonia | mg NH3-N / L | 0.5 | BMRL | 0.5 | #VALUE! | NA | -0.69355 | #VALUE! | -284.6154 | -0.68215 | 173.2977 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.08 | NA | 0.15143 | #VALUE! | 38.4615 | 0.1509 | 46.9835 | AlkF, mg/L CaCO3 | 262 | 262 | 262 | 262 | AlkF, mg/L CaCO3 | 262 | 262 | 262 | 262
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.49 | 1.35 | 1.42 | 9.8592 | 1998-06-26 | 16:20 | 6.8333 | 24.5 | 40 | 38 | 302 | 5.28 | 1.92 | 7.2 | 0.23084 | 0.73333 | 40.9444 | 12.0513 | 12.087 | 0 | 0 | 0 | 0 | 39 | 0.30992 | 1998-06-28 | 10:00 | 25 | 23 | 55 | 54 | 302 | 6.11 | 2.32 |  | 8.43 | 0.23084 | 0.72479 | 34.8244 | 13.9457 | 14.6211 | 326.0956 | 266.6364 | 324.8927 | 0.58858 | 53.9114 | 0.27121 | 8.16 | 7.4 | 8.24 | 275 | 288 | 307 | 304.069 | 0.95473 | 2.8269 | 303.7749 | 9.4724 | 0.04 | 0.139 | 0.392 | 0.37974 | 3.1266 | 70.0375 | 0.37631 | 89.3704 | [8 empty] | Total organic carbon | mg/L | 1.3 | 1.2 | 1.25 | 8 | 10.4 | 10.121 | 2.683 | 68.75 | 10.0362 | 87.5451 | Total organic carbon | mg/L | 1.6 | 23.4 | 25.6 | -9.4017 | 60 | 25.4047 | 93.702 | Total organic carbon | mg/L | 0.9 | 7.6 | 7.6391 | -0.51487 | 77.5 | 7.5859 | 88.1359 | Total organic carbon | mg/L | 0.8 | 5.7 | 5.3714 | 5.7644 | 80 | 5.3374 | 85.0113 | Alkp, mg/L CaCO3 | 232 | 224 | 206 | 210 | Alkp, mg/L CaCO3 | 232 | 224 | 206 | 210
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.51 | 3.65 | 3.58 | 3.9106 | 1998-06-26 | 16:45 | 7.25 | 24.5 | 70 | 68 | 302 | 9.76 | 5.44 | 15.2 | 0.23084 | 0.64211 | 18.8684 | 22.2767 | 22.3426 | 0 | 0 | 0 | 0 | 69 | 0.32381 | 1998-06-28 | 11:00 | 26 | 23 | 55 | 53 | 302 | 6.2 | 2.88 |  | 9.08 | 0.23084 | 0.68282 | 32.2599 | 14.1512 | 14.8365 | 323.2565 | 264.3002 | 322.0461 | 0.58351 | 53.4165 | 0.27775 | 7.97 | 7.93 | 8.1 | 283 | 288 | 308 | 283 | 8.1169 | 0 | 283 | 0 | 0.025 | 0.134 | 0.368 | 0.36708 | 0.25098 | 81.2734 | 0.36357 | 93.1237 | [8 empty] | UV254 | cm-1 | 0.027 | 0.025 | 0.026 | 7.6923 | 0.365 | 0.37277 | -2.1299 | 80.5243 | 0.36946 | 92.9627 | UV254 | cm-1 | 0.034 | 0.884 | 1.029 | -16.4027 | 74.5318 | 1.0209 | 96.6696 | UV254 | cm-1 | 0.015 | 0.247 | 0.27261 | -10.3679 | 88.764 | 0.27058 | 94.4563 | UV254 | cm-1 | 0.011 | 0.179 | 0.186 | -3.9106 | 91.7603 | 0.1847 | 94.0443 | T-HdF, mg/L CaCO3 | 274 | 274 | 274 | 274 | T-HdF, mg/L CaCO3 | 274 | 274 | 274 | 274
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | 1998-06-26 | 17:00 | 7.5 | 24.5 | 55 | 53 | 302 | 7.25 | 3.55 | 10.8 | 0.23084 | 0.6713 | 26.963 | 16.5477 | 16.5967 | 0 | 0 | 0 | 0 | 54 | 0.30735 | 1998-06-28 | 16:00 | 31 | 23 | 55 | 53 | 302 | 5.5 | 3.18 |  | 8.68 | 0.23084 | 0.63364 | 33.7926 | 12.5535 | 13.1614 | 319.8975 | 261.6665 | 318.837 | 0.57701 | 53.423 | 0.24636 | 8.14 | 8.15 | 8.25 | 280 | 288 | 311 | 288.1887 | 7.3348 | 1.0601 | 288.1141 | 2.8163 | 0.025 | 0.132 | 0.358 | 0.32116 | 10.2913 | 81.2734 | 0.31846 | 92.1497 | [8 empty] | SUVA | L/(mg*m) | 2.0769 | 2.0833 | 2.0801 | 0.30817 | 3.5096 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.125 | 3.7778 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.6667 | 3.25 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.375 | 3.1404 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 250 | 310 | 252 | 246 | T-Hdp, mg/L CaCO3 | 250 | 310 | 252 | 246
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.07 | 8.26 | 8.165 | 2.327 | 1998-06-27 | 9:00 | 23.5 | 24.5 | 55 | 53 | 302 | 7.3 | 3 | 10.3 | 0.23084 | 0.70874 | 28.3204 | 16.6619 | 16.7112 | 0 | 0 | 0 | 0 | 54 | 0.30947 | 1998-06-28 | 18:00 | 33 | 23 | 55 | 53 | 302 | 5.6 | 2 |  | 7.6 | 0.23084 | 0.73684 | 38.7368 | 12.7817 | 13.4007 | 326.8519 | 267.3386 | 325.7484 | 0.58962 | 53.4104 | 0.2509 | 8.15 | 8.13 | 8.18 | 267 | 288 | 308 | 327.8 | -6.4286 | 5.6537 | 327.2363 | 18.4076 | 0.024 | 0.136 | 0.329 | 0.4401 | -33.769 | 82.0225 | 0.43624 | 94.4985 | [8 empty] | Bromide | mg/L | 60 | 60 | 60 | 0 | --- | 66.4516 | --- | 3.2258 | 66.39 | 9.6249 | Bromide | mg/L | 63 | --- | 53 | --- | -1.6129 | 53.0814 | -18.6857 | Bromide | mg/L | 61 | --- | 63.1739 | --- | 1.6129 | 63.1568 | 3.4149 | Bromide | mg/L | 58 | --- | 63.7143 | --- | 6.4516 | 63.6717 | 8.9077 | Ca-HdF, mg/L CaCO3 | 261 | 261 | 261 | 261 | Ca-HdF, mg/L CaCO3 | 261 | 261 | 261 | 261
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-28 | 20:00 | 35 | 23 | 55 | 53 | 302 | 5.61 | 2.05 |  | 7.66 | 0.23084 | 0.73238 | 38.4256 | 12.8045 | 13.4247 | 326.5466 | 267.0872 | 325.4421 | 0.58907 | 53.4109 | 0.25135 | [27 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 225 | 244 | 228 | 232 | Ca-Hdp, mg/L CaCO3 | 225 | 244 | 228 | 232
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 385 | 390 | 387.5 | 1.2903 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-28 | 0:00 | 39 | 23 | 55 | 53 | 302 | 5.63 | 3.06 |  | 8.69 | 0.23084 | 0.64787 | 33.7526 | 12.8502 | 13.4725 | 320.8524 | 262.4266 | 319.7632 | 0.57881 | 53.4212 | 0.25219 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.23 | 1.56 | 1.395 | 23.6559 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.31 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.66 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.76 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 120 | 120 | 120 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 8:30 | 47.5 | 23 | 55 | 54 | 302 | 5.31 | 2 |  | 7.31 | 0.23084 | 0.7264 | 40.3133 | 12.1198 | 12.7068 | 326.0962 | 266.7679 | 325.053 | 0.58807 | 53.9119 | 0.23569 | [27 empty] | SDS-Cl2 demand | mg/L | 1.27 | 0.94 | 1.105 | 29.8643 | --- | 9.0889 | --- | 69.1341 | 9.0126 | 87.7394 | SDS-Cl2 demand | mg/L | 1.19 | --- | 25.09 | --- | 66.7598 | 24.8956 | 95.22 | SDS-Cl2 demand | mg/L | 0.84 | --- | 6.7965 | --- | 76.5363 | 6.7495 | 87.5546 | SDS-Cl2 demand | mg/L | 0.74 | --- | 4.7971 | --- | 79.3296 | 4.7669 | 84.4763 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 27 | 28 | 27.5 | 3.6364 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 10:30 | 49.5 | 23 | 55 | 54 | 302 | 5.38 | 3.83 |  | 9.21 | 0.23084 | 0.58415 | 31.7904 | 12.2796 | 12.8743 | 316.6601 | 259.0375 | 315.6336 | 0.57109 | 53.9289 | 0.23873 | [27 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 76.9087 | 85.8787 | 72.0175 | 67.7393 | Qp/QT (THM4), % | 110.6323 | 123.5356 | 103.5965 | 97.4422
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 6.5 | 6.7 | 6.6 | 3.0303 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 11:30 | 50.5 | 23 | 56 | 54 | 302 | 5.25 | 2.08 |  | 7.33 | 0.23084 | 0.71623 | 40.2005 | 11.9828 | 12.5632 | 325.3945 | 266.2037 | 324.3655 | 0.58676 | 54.4132 | 0.23088 | 8.11 | 8.13 | 8.19 |  | 289 | 358 |  | #VALUE! |  |  |  | 0.02 | 0.133 | 0.323 | 0.41998 | -30.0243 | 85.0187 | 0.4165 | 95.1981 | [8 empty] | SDS-Chlorination pH | --- | 8.3 | 8.29 | 8.295 | 0.12055 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.12 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.16 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | 36
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 12:30 | 51.5 | 23 | 56 | 54 | 302 | 5.26 | 2.25 |  | 7.51 | 0.23084 | 0.7004 | 39.213 | 12.0057 | 12.5871 | 324.3216 | 265.3244 | 323.2941 | 0.58483 | 54.4152 | 0.23132 | 8.09 | 8.13 | 8.19 | 281 | 296 | 315 | 287.6756 | 8.6744 | 0.70671 | 287.6174 | 2.3008 | 0.021 | 0.137 | 0.343 | 0.3965 | -15.5977 | 84.2697 | 0.39323 | 94.6596 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 22.0458 | 20.637 | 22.1825 | 23.6079 | SDS-HAA5b, ug/L | NA | NA | NA | 7.2119
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 153.5 | 154.7 | 154.1 | 0.77872 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 13:30 | 52.5 | 23 | 56 | 54 | 302 | 5.25 | 2.14 |  | 7.39 | 0.23084 | 0.71042 | 39.866 | 11.9828 | 12.5632 | 324.9992 | 265.8803 | 323.9715 | 0.58605 | 54.4139 | 0.23088 | 8.12 | 8.16 | 8.21 | 272 | 288 | 316 | 309.986 | 1.9032 | 3.8869 | 309.6558 | 12.1605 | 0.021 | 0.136 | 0.359 | 0.40949 | -14.0649 | 84.2697 | 0.40612 | 94.8291 | [8 empty] | SDS-TOX | mg Cl- /L | 90 | 91 | 90.5 | 1.105 | --- | 1048.5645 | --- | 76.6452 | 1039.4147 | 91.2932 | SDS-TOX | mg Cl- /L | 125 | --- | 2750 | --- | 67.7419 | 2728.6436 | 95.419 | SDS-TOX | mg Cl- /L | 68 | --- | 762.5652 | --- | 82.4516 | 757.0821 | 91.0181 | SDS-TOX | mg Cl- /L | 59 | --- | 528.2857 | --- | 84.7742 | 524.7894 | 88.7574 | SDS-TOXb, ug Cl- /L | 159.0813 | 162.0685 | 157.4039 | 164.9765 | SDS-TOXb, ug Cl- /L | NA | NA | NA | 67.4022
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 3.6 | 2.7 | 3.15 | 28.5714 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 14:30 | 53.5 | 23 | 56 | 54 | 302 | 5.11 | 2.85 |  | 7.96 | 0.23084 | 0.64196 | 36.9397 | 11.6633 | 12.2282 | 320.4005 | 262.1406 | 319.4147 | 0.57767 | 54.4223 | 0.22469 | 8.15 | 8.2 | 8.22 | 279 | 290 | 309 | 290.1719 | 6.0932 | 1.4134 | 290.0774 | 3.8188 | 0.021 | 0.136 | 0.349 | 0.33521 | 3.9511 | 84.2697 | 0.33255 | 93.6852 | [8 empty] | SDS-CHCl3 | mg/L | 16 | 15 | 15.5 | 6.4516 | --- | 352.5968 | --- | 87.0833 | 349.3774 | 95.5635 | SDS-CHCl3 | mg/L | 25 | --- | 975 | --- | 79.1667 | 967.271 | 97.4154 | SDS-CHCl3 | mg/L | 11 | --- | 247.9565 | --- | 90.8333 | 246.0859 | 95.53 | SDS-CHCl3 | mg/L | 8.5 | --- | 167.7857 | --- | 92.9167 | 166.599 | 94.8979 | SDS-CDb, mg/L | 1.6765 | 1.5275 | 1.6067 | 1.6562 | SDS-CDb, mg/L | NA | NA | NA | 0.81264
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | 30 | 33 | 31.5 | 9.5238 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 15:45 | 54.75 | 23 | 55 | 54 | 302 | 5.15 | 2.26 |  | 7.41 | 0.23084 | 0.69501 | 39.7557 | 11.7546 | 12.3239 | 323.9432 | 265.0327 | 322.9386 | 0.58408 | 53.9159 | 0.22858 | 8.15 | 8.18 | 8.2 | 272 | 292 | 310 | 308.0664 | 0.62375 | 3.8869 | 307.7589 | 11.6191 | 0.023 | 0.138 | 0.359 | 0.3853 | -7.3268 | 82.7715 | 0.38221 | 93.9824 | [8 empty] | SDS-BDCM | mg/L | 16 | 14 | 15 | 13.3333 | --- | 55.3226 | --- | 45.4545 | 54.9375 | 72.6962 | SDS-BDCM | mg/L | 18 | --- | 113 | --- | 34.5455 | 112.2271 | 83.9611 | SDS-BDCM | mg/L | 12 | --- | 45.6957 | --- | 56.3636 | 45.4296 | 73.5855 | SDS-BDCM | mg/L | 9.3 | --- | 35.3 | --- | 66.1818 | 35.1063 | 73.509 | TOCb, mg/L | 1.885 | 1.9389 | 1.7675 | 1.8323 | TOCb, mg/L | NA | NA | NA | 0.88185
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-29 | 17:00 | 56 | 23 | 55 | 54 | 302 | 5.11 | 2.06 |  | 7.17 | 0.23084 | 0.71269 | 41.1199 | 11.6633 | 12.2282 | 325.1349 | 266.0141 | 324.1345 | 0.58621 | 53.9138 | 0.22681 | 8.16 | 8.21 | 8.25 | 277 | 295 | 315 | 297.8835 | 5.4338 | 2.1201 | 297.7068 | 6.9554 | 0.021 | 0.133 | 0.371 | 0.41257 | -11.2036 | 84.2697 | 0.40925 | 94.8687 | [8 empty] | SDS-DBCM | mg/L | 14 | 13 | 13.5 | 7.4074 | --- | -8.7581 | --- | -104.5455 | -8.5455 | 257.978 | SDS-DBCM | mg/L | 13 | --- | -51 | --- | -96.9697 | -50.4793 | 125.7531 | SDS-DBCM | mg/L | 13 | --- | -0.91304 | --- | -96.9697 | -0.80321 | 1718.5083 | SDS-DBCM | mg/L | 11 | --- | 4.7143 | --- | -66.6667 | 4.7611 | -131.0383 | UV254 b, cm-1 | 0.050823 | 0.048051 | 0.048159 | 0.050519 | UV254 b, cm-1 | NA | NA | NA | 0.014133
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 8:00 | 71 | 23 | 55 | 54 | 302 | 5.12 | 1.29 |  | 6.41 | 0.23084 | 0.79875 | 46.1139 | 11.6861 | 12.2521 | 331.0889 | 270.8839 | 330.0682 | 0.59695 | 53.9031 | 0.2273 | [27 empty] | SDS-CHBr3 | mg/L | 3.2 | 3.5 | 3.35 | 8.9552 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 60.4618 | 62.8588 | 61.2798 | 59.2904 | Bromideb, ug/L | NA | NA | NA | 58.1023
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 1.3 | 1.4 | 1.35 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 8:30 | 71.5 | 23 | 55 | 54 | 302 | 5.13 | 3.17 |  | 8.3 | 0.23084 | 0.61807 | 35.3855 | 11.709 | 12.276 | 318.8348 | 260.8565 | 317.85 | 0.57486 | 53.9251 | 0.22765 | 8.24 | 8.11 | 8.21 | 268 | 290 | 308 | 307.2744 | 0.23557 | 5.3004 | 306.9409 | 12.6868 | 0.027 | 0.136 | 0.566 | 0.30585 | 45.9631 | 79.7753 | 0.30348 | 91.1032 | [8 empty] | SDS-THM4 | mg/L | 49.2 | 45.5 | 47.35 | 7.8141 | --- | 391.7048 | --- | 69.2732 | 388.4161 | 87.8095 | SDS-THM4 | mg/L | 58.5 | --- | 1014.5 | --- | 62.0376 | 1006.7222 | 94.1891 | SDS-THM4 | mg/L | 40.1 | --- | 287.9261 | --- | 73.9779 | 285.9697 | 85.9775 | SDS-THM4 | mg/L | 32.9 | --- | 206.0429 | --- | 78.6502 | 204.7529 | 83.9319 | Alkb, mg/L CaCO3 | 238.9274 | 229.3661 | 221.6702 | 226.7756 | Alkb, mg/L CaCO3 | NA | NA | NA | 211.33
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 8 | 7.9 | 7.95 | 1.2579 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 10:00 | 73 | 23 | 55 | 54 | 302 | 5.07 | 1.55 |  | 6.62 | 0.23084 | 0.76586 | 44.6193 | 11.572 | 12.1324 | 328.781 | 269.0038 | 327.7774 | 0.59275 | 53.9072 | 0.22506 | 8.35 | 8.23 | 8.38 | 265 | 290 | 306 | 341.8774 | -11.7246 | 6.3604 | 341.2321 | 22.3403 | 0.023 | 0.136 | 0.493 | 0.49494 | -0.3939 | 82.7715 | 0.49098 | 95.3155 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 255.5419 | 304.9163 | 258.1561 | 255.033 | T-Hdb, mg/L CaCO3 | NA | NA | NA | 246.7162
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 11:00 | 74 | 23 | 55 | 54 | 302 | 5.14 | 2.21 |  | 7.35 | 0.23084 | 0.69932 | 40.0884 | 11.7318 | 12.2999 | 324.233 | 265.2714 | 323.2295 | 0.5846 | 53.9154 | 0.22813 | 8.44 | 8.32 | 8.42 | 262 | 278 | 304 | 331.8416 | -9.1584 | 7.4205 | 331.2473 | 20.905 | 0.022 | 0.133 | 0.441 | 0.39283 | 10.9239 | 83.5206 | 0.38967 | 94.3542 | [8 empty] | SDS-DCAA* | mg/L | 4.6 | 4.5 | 4.55 | 2.1978 | --- | 91.4855 | --- | 85.5556 | 90.6552 | 94.981 | SDS-DCAA* | mg/L | 7.2 | --- | 250.2 | --- | 77.1429 | 248.223 | 97.0994 | SDS-DCAA* | mg/L | 2.6 | --- | 65.4261 | --- | 91.746 | 64.9301 | 95.9957 | SDS-DCAA* | mg/L | 2 | --- | 44.1429 | --- | 93.6508 | 43.8289 | 95.4368 | Ca-Hdb, mg/L CaCO3 | 233.3129 | 246.4006 | 237.2342 | 241.3556 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | 232.7417
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 12:00 | 75 | 23 | 55 | 54 | 302 | 5.09 | 1.95 |  | 7.04 | 0.23084 | 0.72301 | 41.8977 | 11.6177 | 12.1803 | 325.8346 | 266.5899 | 324.8361 | 0.58745 | 53.9125 | 0.22593 | 8.27 | 8.23 |  | 262 | 278 | 306 | 337.8154 | -10.3972 | 7.4205 | 337.1765 | 22.2959 | 0.014 | 0.129 | 0.418 | 0.44543 | -6.5612 | 89.5131 | 0.44179 | 96.8311 | [8 empty] | SDS-TCAA* | mg/L | 2.6 | 2.4 | 2.5 | 8 | --- | 75.0806 | --- | 90 | 74.3875 | 96.6392 | SDS-TCAA* | mg/L | 3.7 | --- | 216.7 | --- | 85.2 | 214.9671 | 98.2788 | SDS-TCAA* | mg/L | 1.3 | --- | 52.8217 | --- | 94.8 | 52.415 | 97.5198 | SDS-TCAA* | mg/L | 1 | --- | 35.2857 | --- | 96 | 35.0303 | 97.1453
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 7.5 | 6.1 | 6.8 | 20.5882 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 13:30 | 76.5 | 23 | 55 | 54 | 302 | 4.97 | 2.22 |  | 7.19 | 0.23084 | 0.69124 | 41.0028 | 11.3438 | 11.8931 | 323.6662 | 264.8352 | 322.698 | 0.58347 | 53.9165 | 0.22058 | 8.28 | 8.27 | 8.3 | 264 | 279 | 306 | 325.536 | -6.3843 | 6.7138 | 325.0297 | 18.7767 | 0.023 | 0.134 | 0.439 | 0.38088 | 13.239 | 82.7715 | 0.37794 | 93.9143 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 59.9 | 62.1 | 61 | 3.6066 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 14:30 | 77.5 | 23 | 55 | 54 | 302 | 5.03 | 2.09 |  | 7.12 | 0.23084 | 0.70646 | 41.4157 | 11.4807 | 12.0367 | 324.7016 | 265.6727 | 323.7185 | 0.58537 | 53.9146 | 0.22326 | 8.32 | 8.3 | 8.24 | 265 | 280 | 305 | 326.3206 | -6.9904 | 6.3604 | 325.8099 | 18.6642 | 0.021 | 0.133 | 0.436 | 0.40425 | 7.2813 | 84.2697 | 0.40106 | 94.7639 | [8 empty] | SDS-DBAA* | mg/L | 3.3 | 3.3 | 3.3 | 0 | --- | -2.9903 | --- | -144.4444 | -2.9302 | 212.6185 | SDS-DBAA* | mg/L | 3.1 | --- | -14.4 | --- | -129.6296 | -14.2576 | 121.7428 | SDS-DBAA* | mg/L | 3.2 | --- | -0.82174 | --- | -137.037 | -0.78999 | 505.0684 | SDS-DBAA* | mg/L | 2.8 | --- | 0.72857 | --- | -107.4074 | 0.744 | -276.3419 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 67.9 | 70 | 68.95 | 3.0457 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 14:45 | 77.75 | 23 | 55 | 54 | 302 | 4.96 | 0.51 |  | 5.47 | 0.23084 | 0.90676 | 54.2102 | 11.3209 | 11.8692 | 338.8462 | 277.2577 | 337.8347 | 0.61083 | 53.8892 | 0.22025 | 8.27 | 8.27 |  | 269 | 290 |  | 419.1569 |  | 4.947 | 417.9238 | 35.6342 | 0.021 | 0.134 | 0.421 | 1.2276 | -191.5956 | 84.2697 | 1.2177 | 98.2755 | [8 empty] | SDS-BCAA* | mg/L | 4.5 | 4.4 | 4.45 | 2.2472 | --- | 15.7403 | --- | 44.0252 | 15.6325 | 71.5337 | SDS-BCAA* | mg/L | 5.4 | --- | 30.9 | --- | 32.0755 | 30.6925 | 82.4061 | SDS-BCAA* | mg/L | 3.4 | --- | 13.2913 | --- | 57.2327 | 13.2132 | 74.2682 | SDS-BCAA* | mg/L | 2.8 | --- | 10.1571 | --- | 64.7799 | 10.1023 | 72.2836 | Qp/QT (HAA5), % | 13.8203 | 14.8936 | 12.987 | 12.6812 | Qp/QT (HAA5), % | 67.1273 | 72.3404 | 63.0798 | 61.5942
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 15:00 | 78 | 23 | 55 | 54 | 302 | 5.01 | 0.86 |  | 5.87 | 0.23084 | 0.85349 | 50.448 | 11.4351 | 11.9889 | 334.9713 | 274.0788 | 333.9612 | 0.60387 | 53.8961 | 0.22244 | 8.34 | 8.27 |  | 265 | 288 |  | 387.8605 |  | 6.3604 | 386.8414 | 31.4965 | 0.028 | 0.132 | 0.43 | 0.7481 | -73.9765 | 79.0262 | 0.74213 | 96.2271 | [8 empty] | SDS-TBAA | mg/L | NR | NR | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 139.3468 | 139.8617 | 139.2948 | 138.7304 | SDS-THM4b, ug/L | 82.4416 | 84.9426 | 82.1891 | 79.4478
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 15:30 | 78.5 | 23 | 55 | 54 | 302 | 5.11 | 0.78 |  | 5.89 | 0.23084 | 0.86757 | 50.2733 | 11.6633 | 12.2282 | 336.0066 | 274.909 | 334.9728 | 0.60581 | 53.8942 | 0.22689 | 8.37 | 8.25 |  | 268 | 288 |  | 381.2692 |  | 5.3004 | 380.3109 | 29.5313 | 0.022 | 0.133 | 0.455 | 0.86397 | -89.8831 | 83.5206 | 0.85684 | 97.4324 | [8 empty] | SDS-CDBAA | mg/L | 2.7 | 2.6 | 2.65 | 3.7736 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-30 | 15:45 | 78.75 | 23 | 55 | 54 | 302 | 5 | 0.66 |  | 5.66 | 0.23084 | 0.88339 | 52.3569 | 11.4122 | 11.9649 | 337.1385 | 275.8537 | 336.1239 | 0.60778 | 53.8922 | 0.22202 | 8.32 | 8.28 |  | 268 | 290 |  | 396.6364 |  | 5.3004 | 395.5715 | 32.2499 | 0.023 | 0.133 |  | 0.97062 |  | 82.7715 | 0.96278 | 97.6111 | [8 empty] | SDS-DCBAA | mg/L | 3.1 | 3.3 | 3.2 | 6.25 | --- | 14.8129 | --- | 52.9412 | 14.702 | 78.2342 | SDS-DCBAA | mg/L | 3.5 | --- | 36.5 | --- | 48.5294 | 36.2315 | 90.3399 | SDS-DCBAA | mg/L | 2.3 | --- | 12.0826 | --- | 66.1765 | 12.0054 | 80.8419 | SDS-DCBAA | mg/L | 1.8 | --- | 8.9429 | --- | 73.5294 | 8.8896 | 79.7517 | SDS-TOXb, ug Cl- /L | 346.4536 | 348.4043 | 346.0065 | 345.8424 | SDS-TOXb, ug Cl- /L | 188.1318 | 197.6064 | 185.9601 | 185.163
[44 empty] | 1998-06-30 | 16:00 | 79 | 23 | 55 | 54 | 302 | 4.91 | 0.59 |  | 5.5 | 0.23084 | 0.89273 | 53.9091 | 11.2068 | 11.7496 | 337.8052 | 276.4144 | 336.8071 | 0.60892 | 53.8911 | 0.21802 | 8.32 | 8.2 | 8.34 | 273 | 280 | 312 | 366.2203 | -17.3783 | 3.5336 | 365.4625 | 25.3001 | 0.025 | 0.137 | 0.474 | 1.0364 | -118.6584 | 81.2734 | 1.0282 | 97.5686 | [8 empty] | SDS-HAA5 | mg/L | 10.5 | 10.2 | 10.35 | 2.8986 | --- | 173.7371 | --- | 83.0328 | 172.1767 | 93.9887 | SDS-HAA5 | mg/L | 14 | --- | 484 | --- | 77.0492 | 480.1762 | 97.0844 | SDS-HAA5 | mg/L | 7.1 | --- | 124.2739 | --- | 88.3607 | 123.3489 | 94.244 | SDS-HAA5 | mg/L | 5.8 | --- | 84.6571 | --- | 90.4918 | 84.0696 | 93.101 | SDS-CDb, mg/L | 3.2379 | 3.224 | 3.2242 | 3.2199 | SDS-CDb, mg/L | 1.9186 | 1.8511 | 1.8516 | 1.8307
[44 empty] | 1998-06-30 | 16:30 | 79.5 | 23 | 55 | 54 | 302 | 4.89 | 0.5 |  | 5.39 | 0.23084 | 0.90724 | 55.0297 | 11.1612 | 11.7017 | 338.8681 | 277.2875 | 337.871 | 0.61082 | 53.8892 | 0.21714 | 8.35 | 8.21 | 8.36 | 273 | 292 | 311 | 380.8 | -22.4437 | 3.5336 | 379.9272 | 28.1441 | 0.024 | 0.135 | 0.508 | 1.2044 | -137.0886 | 82.0225 | 1.1949 | 97.9914 | [8 empty] | SDS-HAA6 | mg/L | 15 | 14.6 | 14.8 | 2.7027 | --- | 189.4774 | --- | 78.5352 | 187.8092 | 92.1197 | SDS-HAA6 | mg/L | 19.4 | --- | 514.9 | --- | 71.8637 | 510.8687 | 96.2025 | SDS-HAA6 | mg/L | 10.5 | --- | 137.5652 | --- | 84.7716 | 136.5621 | 92.3112 | SDS-HAA6 | mg/L | 8.6 | --- | 94.8143 | --- | 87.5272 | 94.172 | 90.8678 | TOCb, mg/L | 3.6199 | 3.6426 | 3.5974 | 3.5942 | TOCb, mg/L | 2.154 | 2.2638 | 2.0445 | 2.029
[44 empty] | 1998-06-30 | 17:00 | 80 | 23 | 55 | 54 | 302 | 5 | 0.63 |  | 5.63 | 0.23084 | 0.8881 | 52.6412 | 11.4122 | 11.9649 | 337.4826 | 276.1352 | 336.4669 | 0.6084 | 53.8916 | 0.22202 | 8.38 | 8.31 | 8.37 | 275 | 290 | 315 | 346.4921 | -9.9975 | 2.8269 | 345.9002 | 20.4973 | 0.025 | 0.136 | 0.557 | 0.99461 | -78.5657 | 81.2734 | 0.98658 | 97.466 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.11864 | 0.11868 | 0.11811 | 0.11797 | UV254 b, cm-1 | 0.061338 | 0.061521 | 0.05875 | 0.058047
[44 empty] | 1998-06-30 | 17:30 | 80.5 | 23 | 55 | 54 | 302 | 4.93 | 0.51 |  | 5.44 | 0.23084 | 0.90625 | 54.5147 | 11.2525 | 11.7974 | 338.8028 | 277.2273 | 337.7976 | 0.61073 | 53.8893 | 0.21892 | 8.4 | 8.27 | 8.41 | 273 | 288 | 314 | 379.6667 | -20.913 | 3.5336 | 378.796 | 27.9296 | 0.026 | 0.136 | 0.577 | 1.1727 | -103.2351 | 80.5243 | 1.1633 | 97.765 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 61.7236 | 62.1489 | 61.8701 | 61.4928 | Bromideb, ug/L | 60.6575 | 62.7234 | 61.3692 | 59.5362
[44 empty] | 1998-06-30 | 18:00 | 81 | 23 | 55 | 54 | 302 | 5.08 | 0.49 |  | 5.57 | 0.23084 | 0.91203 | 53.219 | 11.5948 | 12.1564 | 339.2572 | 277.5736 | 338.2196 | 0.61165 | 53.8884 | 0.22558 | 8.38 | 8.38 | 8.31 | 272 | 288 | 316 | 397.0408 | -25.6458 | 3.8869 | 395.9891 | 31.3112 | 0.029 | 0.134 | 0.608 | 1.2169 | -100.146 | 78.2772 | 1.2069 | 97.5971 | [47 empty] | Alkb, mg/L CaCO3 | 257.8539 | 256.3404 | 254.7273 | 255.4058 | Alkb, mg/L CaCO3 | 241.8618 | 234.5106 | 226.6753 | 229.971
[44 empty] | 1998-07-01 | 8:00 | 95 | 23 | 55 | 54 | 302 | 4.78 | 0.51 |  | 5.29 | 0.23084 | 0.90359 | 56.0888 | 10.9101 | 11.4385 | 338.5795 | 277.07 | 337.6059 | 0.61023 | 53.8898 | 0.21226 | [66 empty] | T-Hdb, mg/L CaCO3 | 270.6831 | 279.3617 | 271.1429 | 270.4493 | T-Hdb, mg/L CaCO3 | 257.8894 | 300.0426 | 260.1224 | 256.7536
[44 empty] | 1998-07-01 | 9:00 | 96 | 23 | 55 | 54 | 302 | 4.85 | 0.53 |  | 5.38 | 0.23084 | 0.90149 | 55.1338 | 11.0699 | 11.606 | 338.4374 | 276.9419 | 337.4498 | 0.61002 | 53.89 | 0.21536 | 8.29 | 8.38 |  | 266 | 288 |  | 438.566 |  | 6.0071 | 437.1804 | 39.1555 | 0.035 | 0.136 | 1.164 | 1.0349 | 11.0938 | 73.7828 | 1.0268 | 96.5915 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 256.0247 | 258.4681 | 256.7143 | 257.3225 | Ca-Hdb, mg/L CaCO3 | 236.8342 | 248.7021 | 240.1837 | 243.1377
[44 empty] | 1998-07-01 | 10:00 | 97 | 23 | 55 | 54 | 302 | 4.85 | 0.67 |  | 5.52 | 0.23084 | 0.87862 | 53.7101 | 11.0699 | 11.606 | 336.7643 | 275.5728 | 335.7816 | 0.607 | 53.893 | 0.21535 | 8.36 | 8.35 | 8.32 | 267 | 281 | 316 | 398.8209 | -26.2091 | 5.6537 | 397.7624 | 32.8745 | 0.031 | 0.134 | 1.125 | 0.87548 | 22.1798 | 76.779 | 0.8687 | 96.4314 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-07-01 | 11:00 | 98 | 23 | 54 | 52 | 302 | 4.71 | 7.63 |  | 12.34 | 0.23084 | 0.38169 | 23.4733 | 10.7503 | 11.271 | 304.0811 | 248.8495 | 303.2197 | 0.54801 | 52.452 | 0.21488 | 8.35 | 8.38 | 8.37 | 261 | 280 | 305 | 296.5806 | 2.7605 | 7.7739 | 296.3031 | 11.9145 | 0.026 | 0.134 | 0.783 | 0.19986 | 74.4751 | 80.5243 | 0.1985 | 86.902 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-07-01 | 11:15 | 98.25 | 23 | 54 | 53 | 302 | 4.8 | 5.9 |  | 10.7 | 0.23084 | 0.4486 | 27.2243 | 10.9557 | 11.4863 | 308.1114 | 252.1339 | 307.2217 | 0.55533 | 52.9447 | 0.21695 | 8.4 | 8.36 | 8.35 | 253 | 279 | 293 | 307.4068 | -4.917 | 10.6007 | 306.9744 | 17.5827 | 0.016 | 0.127 | 0.537 | 0.22909 | 57.3383 | 88.015 | 0.2274 | 92.9639 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-07-01 | 11:30 | 98.5 | 23 | 54 | 53 | 302 | 4.65 | 5.63 |  | 10.28 | 0.23084 | 0.45233 | 28.3774 | 10.6134 | 11.1274 | 308.3279 | 252.3342 | 307.4657 | 0.55563 | 52.9444 | 0.21017 | 8.15 | 8.21 | 8.25 | 246 | 282 | 298 | 313.5595 | -5.2213 | 13.0742 | 313.0394 | 21.4156 | 0.019 | 0.132 | 0.457 | 0.22807 | 50.0943 | 85.7678 | 0.22646 | 91.61 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-07-01 | 12:00 | 99 | 23 | 54 | 53 | 302 | 4.71 | 5.47 |  | 10.18 | 0.23084 | 0.46267 | 28.666 | 10.7503 | 11.271 | 308.9645 | 252.8459 | 308.0892 | 0.55681 | 52.9432 | 0.21289 | 8.3 | 8.29 | 8.17 | 267 | 284 | 321 | 296.777 | 7.5461 | 5.6537 | 296.5448 | 9.963 | 0.016 | 0.133 | 0.36 | 0.23467 | 34.8126 | 88.015 | 0.23297 | 93.1321 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-07-01 | 12:30 | 99.5 | 23 | 54 | 53 | 302 | 4.82 | 5.31 |  | 10.13 | 0.23084 | 0.47581 | 28.8124 | 11.0014 | 11.5342 | 309.7807 | 253.4968 | 308.8823 | 0.55835 | 52.9417 | 0.21787 | 8.18 | 8.27 | 8.19 | 255 | 280 | 298 | 308.4162 | -3.4954 | 9.894 | 307.9899 | 17.2051 | 0.013 | 0.133 | 0.298 | 0.24288 | 18.4965 | 90.2622 | 0.24105 | 94.6068 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-07-01 | 13:30 | 100.5 | 23 | 54 | 53 | 302 | 4.7 | 4.84 |  | 9.54 | 0.23084 | 0.49266 | 30.6562 | 10.7275 | 11.247 | 310.8121 | 254.3595 | 309.9335 | 0.56013 | 52.9399 | 0.21245 | 8.35 | 8.13 | 8.33 | 245 | 280 | 293 | 319.9008 | -9.1812 | 13.4276 | 319.318 | 23.274 | 0.014 | 0.133 | 0.263 | 0.24954 | 5.1166 | 89.5131 | 0.24771 | 94.3482 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-07-01 | 14:00 | 101 | 23.2 | 55 | 54 | 302 | 4.76 | 4.69 |  | 9.45 | 0.23084 | 0.5037 | 30.9577 | 10.8644 | 11.3235 | 311.5033 | 254.9159 | 310.6114 | 0.56142 | 53.9386 | 0.20993 | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-07-01 | 15:00 | 102 | 23 | 55 | 54 | 302 | 4.62 | 4.44 |  | 9.06 | 0.23084 | 0.50993 | 32.3333 | 10.5449 | 11.0556 | 311.8796 | 255.2456 | 311.0132 | 0.56201 | 53.938 | 0.20497 | 8.2 | 8.22 | 8.27 | 248 | 275 | 308 | 319.4189 | -3.7074 | 12.3675 | 318.8726 | 22.226 | 0.014 | 0.133 | 0.26 | 0.25784 | 0.829 | 89.5131 | 0.25598 | 94.5308 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-07-01 | 16:00 | 103 | 23 | 55 | 54 | 302 | 4.71 | 3.87 |  | 8.58 | 0.23084 | 0.54895 | 34.1981 | 10.7503 | 11.271 | 314.3426 | 257.2472 | 313.4521 | 0.5665 | 53.9335 | 0.20898 | 8.36 | 8.26 | 8.31 | 262 | 276 | 301 | 308.5581 | -2.511 | 7.4205 | 308.1951 | 14.9889 | 0.015 | 0.136 | 0.273 | 0.27772 | -1.7293 | 88.764 | 0.27567 | 94.5588 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-07-01 | 16:30 | 103.5 | 23.5 | 55 | 54 | 302 | 4.6 | 4.78 |  | 9.38 | 0.23084 | 0.49041 | 31.1962 | 10.4993 | 10.8462 | 310.6638 | 254.2537 | 309.8046 | 0.5598 | 53.9402 | 0.20108 | 8.26 | 8.27 | 8.3 | 252 | 275 | 293 | 312.8326 | -6.7688 | 10.9541 | 312.3693 | 19.3263 | 0.014 | 0.133 | 0.255 | 0.2485 | 2.549 | 89.5131 | 0.24671 | 94.3254 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-07-01 | 17:00 | 104 | 23 | 55 | 54 | 302 | 4.76 | 4.8 |  | 9.56 | 0.23084 | 0.49791 | 30.59 | 10.8644 | 11.3906 | 311.1427 | 254.6208 | 310.2519 | 0.56077 | 53.9392 | 0.21117 | 8.26 | 8.29 |  | 265 | 280 | 305 | 300.85 | 1.3607 | 6.3604 | 300.5675 | 11.8334 | 0.014 | 0.134 | 0.258 | 0.252 | 2.324 | 89.5131 | 0.25013 | 94.4029 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-07-02 | 8:00 | 119 | 23 | 55 | 54 | 302 | 4.6 | 2.33 |  | 6.93 | 0.23084 | 0.66378 | 42.5786 | 10.4993 | 11.0077 | 321.7843 | 263.3549 | 320.8943 | 0.57984 | 53.9202 | 0.20415
[44 empty] | 1998-07-02 | 8:30 | 119.5 | 23 | 54 | 52 | 302 | 4.48 | 12.29 |  | 16.77 | 0.23084 | 0.26714 | 17.0083 | 10.2254 | 10.7206 | 297.4225 | 243.4346 | 296.6217 | 0.53588 | 52.4641 | 0.20434
[44 empty] | 1998-07-02 | 8:45 | 119.75 | 23 | 54 | 52 | 302 | 4.47 | 11.9 |  | 16.37 | 0.23084 | 0.27306 | 17.4484 | 10.2025 | 10.6966 | 297.7582 | 243.7108 | 296.9582 | 0.53647 | 52.4635 | 0.20389
[44 empty] | 1998-07-02 | 9:00 | 120 | 23 | 54 | 52 | 302 | 4.45 | 11.75 |  | 16.2 | 0.23084 | 0.27469 | 17.642 | 10.1569 | 10.6488 | 297.8501 | 243.789 | 297.0535 | 0.53663 | 52.4634 | 0.20298
[44 empty] | 1998-07-02 | 9:15 | 120.25 | 23 | 53 | 52 | 302 | 4.43 | 11.87 |  | 16.3 | 0.23084 | 0.27178 | 17.5276 | 10.1112 | 10.6009 | 297.6837 | 243.6558 | 296.8911 | 0.53632 | 51.9637 | 0.20401
[44 empty] | 1998-07-02 | 10:00 | 121 | 23 | 53 | 52 | 302 | 4.4 | 11.42 |  | 15.82 | 0.23084 | 0.27813 | 18.0898 | 10.0428 | 10.5291 | 298.0437 | 243.9549 | 297.2556 | 0.53695 | 51.9631 | 0.20263
[44 empty] | 1998-07-02 | 10:30 | 121.5 | 23 | 53 | 52 | 302 | 4.44 | 11.4 |  | 15.84 | 0.23084 | 0.2803 | 18.0657 | 10.1341 | 10.6249 | 298.1693 | 244.0518 | 297.3737 | 0.5372 | 51.9628 | 0.20447 | 8.23 | 8.27 | 8.34 | 248 | 276 | 297 | 296.6316 | 0.12405 | 12.3675 | 296.2741 | 16.2937 | 0.01 | 0.132 | 0.181 | 0.1816 | -0.33149 | 92.5094 | 0.18034 | 94.4549
[44 empty] | 1998-07-02 | 10:50 | 121.8333 | 23 | 54 | 52 | 302 | 4.46 | 10.58 |  | 15.04 | 0.23084 | 0.29654 | 19.0798 | 10.1797 | 10.6727 | 299.0991 | 244.8098 | 298.2973 | 0.53888 | 52.4611 | 0.20344 |  | 8.22 | 8.31 | 250 | 285 | 297 | 296.9112 | 0.029915 | 11.6608 | 296.5648 | 15.7014 | 0.01 | 0.132 | 0.189 | 0.18556 | 1.8193 | 92.5094 | 0.18427 | 94.573
[44 empty] | 1998-07-02 | 11:10 | 122.1667 | 23 | 54 | 52 | 302 | 4.46 | 10.43 |  | 14.89 | 0.23084 | 0.29953 | 19.2821 | 10.1797 | 10.6727 | 299.2706 | 244.9502 | 298.4684 | 0.53919 | 52.4608 | 0.20344 | 8.35 | 8.35 | 8.37 | 229 | 293 | 298 | 306.0911 | -2.7151 | 19.0813 | 305.5218 | 25.0463 | 0.01 | 0.132 | 0.183 | 0.18631 | -1.8088 | 92.5094 | 0.18501 | 94.5948
[44 empty] | 1998-07-02 | 11:45 | 122.75 | 23 | 54 | 52 | 302 | 4.44 | 9.88 |  | 14.32 | 0.23084 | 0.31006 | 20.0894 | 10.1341 | 10.6249 | 299.8755 | 245.4483 | 299.0753 | 0.54027 | 52.4597 | 0.20253 | 8.25 | 8.25 | 8.31 | 238 | 277 | 291 | 303.2227 | -4.2002 | 15.9011 | 302.7432 | 21.3855 | 0.01 | 0.132 | 0.188 | 0.189 | -0.53191 | 92.5094 | 0.18768 | 94.6719
[44 empty] | 1998-07-02 | 13:15 | 124.25 | 23 | 54 | 52 | 302 | 4.48 | 10 |  | 14.48 | 0.23084 | 0.30939 | 19.8564 | 10.2254 | 10.7206 | 299.8392 | 245.4126 | 299.0318 | 0.54023 | 52.4598 | 0.20436 | 8.35 | 8.35 | 8.39 | 245 | 277 | 283 | 300.024 | -6.0155 | 13.4276 | 299.6159 | 18.2286 | 0.009 | 0.132 | 0.189 | 0.18928 | -0.14603 | 93.2584 | 0.18794 | 95.2112
[44 empty] | 1998-07-02 | 14:00 | 125 | 23 | 54 | 52 | 302 | 4.49 | 11 |  | 15.49 | 0.23084 | 0.28986 | 18.4964 | 10.2482 | 10.7445 | 298.7178 | 244.4932 | 297.9116 | 0.53821 | 52.4618 | 0.20481 | 8.33 | 8.24 | 8.35 | 242 | 275 | 288 | 299.7355 | -4.0748 | 14.4876 | 299.3063 | 19.1464 | 0.009 | 0.133 | 0.186 | 0.18432 | 0.90396 | 93.2584 | 0.18302 | 95.0824
[44 empty] | 1998-07-02 | 15:00 | 126 | 23 | 54 | 52 | 302 | 4.51 | 10.75 |  | 15.26 | 0.23084 | 0.29554 | 18.7903 | 10.2938 | 10.7924 | 299.0441 | 244.7574 | 298.2334 | 0.53881 | 52.4612 | 0.20572 | 8.51 | 8.41 | 8.51 | 242 | 271 | 283 | 300.2009 | -6.0781 | 14.4876 | 299.7664 | 19.2705 | BMRL | 0.166 | 0.185 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-02 | 16:00 | 127 | 23 | 54 | 52 | 302 | 4.46 | 10.15 |  | 14.61 | 0.23084 | 0.30527 | 19.6708 | 10.1797 | 10.6727 | 299.6007 | 245.2204 | 298.7976 | 0.53979 | 52.4602 | 0.20344 | 8.54 | 8.45 | 8.5 | 245 | 275 | 289 | 299.6975 | -3.7016 | 13.4276 | 299.2936 | 18.1406 | 0.011 | 0.136 | 0.19 | 0.18733 | 1.4065 | 91.7603 | 0.18603 | 94.0868
[44 empty] | 1998-07-02 | 17:00 | 128 | 23 | 54 | 52 | 302 | 4.49 | 10.96 |  | 15.45 | 0.23084 | 0.29061 | 18.5469 | 10.2482 | 10.7445 | 298.7607 | 244.5284 | 297.9544 | 0.53829 | 52.4617 | 0.20481 | 8.55 | 8.48 | 8.5 | 244 | 275 | 284 | 298.9772 | -5.2737 | 13.7809 | 298.5685 | 18.2767 | 0.011 | 0.136 | 0.184 | 0.18368 | 0.17132 | 91.7603 | 0.1824 | 93.9693
[44 empty] | 1998-07-02 | 18:00 | 129 | 23 | 54 | 52 | 302 | 4.48 | 10.85 |  | 15.33 | 0.23084 | 0.29224 | 18.6999 | 10.2254 | 10.7206 | 298.8532 | 244.6056 | 298.0485 | 0.53845 | 52.4615 | 0.20435 | 8.6 | 8.51 | 8.54 | 245 | 274 | 285 | 298.6903 | -4.8036 | 13.4276 | 298.2921 | 17.8657 | 0.011 | 0.134 | 0.187 | 0.18408 | 1.5612 | 91.7603 | 0.1828 | 93.9824
[44 empty] | 1998-07-02 | 19:00 | 130 | 23 | 54 | 52 | 302 | 4.56 | 10.58 | X | 15.14 | 0.23084 | 0.30119 | 18.9472 | 10.408 | 10.912 | 299.3707 | 245.0172 | 298.55 | 0.53943 | 52.4606 | 0.208 | 8.35 | 8.48 | 8.35 | 246 | 276 | 289 | 298.9471 | -3.4419 | 13.0742 | 298.5473 | 17.601 | 0.011 | 0.133 | 0.179 | 0.1863 | -4.0769 | 91.7603 | 0.18497 | 94.0532
[44 empty] | 1998-07-03 | 14:00 |  | 23 | 40 | 38 | 302 | 3.7 | 2.37 |  | 6.07 | 0.23084 | 0.60956 | 48.7529 | 8.4451 | 8.854 | 318.1238 | 260.5018 | 317.4178 | 0.57269 | 38.4273 | 0.23041
[44 empty] | 1998-07-03 | 14:20 |  | 23 | 70 | 68 | 302 | 6.67 | 3.56 |  | 10.23 | 0.23084 | 0.652 | 28.521 | 15.2239 | 15.9612 | 321.2509 | 262.5842 | 319.9552 | 0.58019 | 68.4198 | 0.23328
[44 empty] | 1998-07-03 | 15:00 |  | 23 | 55 | 53 | 302 | 4.88 | 2.52 |  | 7.4 | 0.23084 | 0.65946 | 39.8108 | 11.1383 | 11.6778 | 321.5312 | 263.1028 | 320.587 | 0.57956 | 53.4204 | 0.2186
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on AA13: C. Rice 7/8/99: Consultant verified that the alkalinity and hardness values were checked and found to be correct.
Note on AA14: C. Rice 7/8/99: Consultant verified that the alkalinity and hardness values were checked and found to be correct.
Note on DQ10: Alison Gusses: Mass balance closure errors were high for the 90% recovery run indicating that the system may not have been at steady-state - all water quality parameters for this run were verified by the consultant.

## 7450. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Hydranautics Corp. | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.20341 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.92 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.30175 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-10-13 | 1998-11-01 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.16 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.29 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.79 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.149 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 1000 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 142.1 | 142.1 | 142.1 | 142.1 | SDS-THM4F, ug/L | 142.1 | 142.1 | 142.1 | 142.1 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | -432 | 120 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 48.55 | 56.7 | 35.5 | 30.2 | SDS-THM4p, ug/L | 48.55 | 56.7 | 35.5 | 30.2 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.07 | 8.19 | 7.63 | 14.6789 | 1998-10-26 | 8:45 | 0 | [18 empty] | 1998-10-27 | 9:00 | 0 | 23 | 57 | 58.5 | 263 | 6.43 | 2.48 |  | 8.91 | 0.20103 | 0.72166 | 28.5174 | 14.6761 | 15.3869 | 294.0178 | 233.0227 | 292.5266 | 0.6025 | 57.1475 | 0.26925 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 22 | 23 | 8.6957 | 1998-10-26 | 9:00 | 0.25 | 23.5 | 59 | 60.5 | 263 | 5.5 | NA |  | 0.20103 |  |  | 12.5535 | 12.9683 |  |  |  | 0 | 59.75 | 0.21704 | 1998-10-27 | 9:30 | 0.5 | 23 | 57 | 58.5 | 263 | 6.43 | 2.48 |  | 8.91 | 0.20103 | 0.72166 | 28.5174 | 14.6761 | 15.3869 | 294.0178 | 233.0227 | 292.5266 | 0.6025 | 57.1475 | 0.26925 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 10.4 | 13.7 | 6 | 4.1 | SDS-HAA5p, ug/L | 10.4 | 13.7 | 6 | 4.1 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 376 | 380 | 378 | 1.0582 | 1998-10-26 | 10:00 | 1.25 | 23.5 | 59 | 60.5 | 263 | 5.85 | NA |  | 0.20103 |  |  | 13.3523 | 13.7936 |  |  |  | 0 | 59.75 | 0.23086 | 1998-10-27 | 10:00 | 1 | 23 | 57 | 58.5 | 263 | 6.37 | 2.36 |  | 8.73 | 0.20103 | 0.72967 | 29.126 | 14.5392 | 15.2433 | 294.5836 | 233.4824 | 293.1037 | 0.60361 | 57.1464 | 0.26674 | 6.38 | 5.98 | 6.43 | 199 | 243 | 246 | 387.6568 | -57.5841 | 20.4 | 385.3721 | 48.3616 | 0.031 | 0.144 | 0.225 | 0.44715 | -98.7354 | 78.3972 | 0.44211 | 92.9882 | [8 empty] | Sampling date | MM/DD/YY | 1998-10-28 | 1998-10-29 | --- | --- | 1998-10-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-31 | 1998-10-31 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-01 | 1998-11-01 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-02 | 1998-11-02 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 352.5 | 352.5 | 352.5 | 352.5 | SDS-TOXF, ug Cl- /L | 352.5 | 352.5 | 352.5 | 352.5 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 248 | 252 | 250 | 1.6 | 1998-10-26 | 11:00 | 2.25 | 23.5 | 59 | 60.5 | 263 | 6.1 | 4.35 | 10.45 | 0.20103 | 0.58373 | 24.1675 | 13.9229 | 14.3831 | 0 | 0 | 0 | 0 | 59.75 | 0.24072 | 1998-10-27 | 11:00 | 2 | 23 | 57 | 58.5 | 263 | 6.29 | 3.05 |  | 9.34 | 0.20103 | 0.67345 | 27.1585 | 14.3566 | 15.0519 | 290.5791 | 230.3233 | 289.138 | 0.59535 | 57.1546 | 0.26335 |  |  |  | 204 | 247 | 248 | 344.8656 | -39.0587 | 18.4 | 343.1811 | 40.5562 | 0.037 |  | 0.275 | 0.36313 | -32.0489 | 74.216 | 0.35923 | 89.7003 | [8 empty] | Sampling time | hh:mm | 8:00 | 10:45 | --- | --- | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:30 | 13:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:20 | 12:20 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 95.5 | 120 | 58 | 50 | SDS-TOXp, ug Cl- /L | 95.5 | 120 | 58 | 50 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 234 | 222 | 228 | 5.2632 | 1998-10-26 | 12:00 | 3.25 | 23.5 | 59.5 | 60.5 | 263 | 6.16 | 2.27 | 8.43 | 0.20103 | 0.73072 | 30.1981 | 14.0599 | 14.5245 | 0 | 0 | 0 | 0 | 60 | 0.24208 | 1998-10-27 | 13:00 | 4 | 23 | 57 | 58.5 | 263 | 6.27 | 3 |  | 9.27 | 0.20103 | 0.67638 | 27.3711 | 14.3109 | 15.004 | 290.7813 | 230.4874 | 289.3439 | 0.59575 | 57.1542 | 0.26252 | 7.65 | 7.6 | 7.68 | 200 | 242 | 245 | 354.5 | -44.6939 | 20 | 352.6583 | 43.2879 | 0.04 | 0.143 | 0.324 | 0.35981 | -11.054 | 72.1254 | 0.356 | 88.7641 | [8 empty] | Operation time | hh.hh | 23 | 49.75 | --- | --- | 23 | --- | --- | --- | --- | --- | Operation time | hh.hh | 100 | 100 | --- | --- | --- | --- | --- | Operation time | hh.hh | 124.5 | 124.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 147.33 | 147.33 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 4.225 | 4.225 | 4.225 | 4.225 | SDS-CDF, mg/L | 4.225 | 4.225 | 4.225 | 4.225 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 230 | 218 | 224 | 5.3571 | 1998-10-26 | 13:15 | 4.5 | 23.5 | 59 | 60.5 | 263 | 6.1 | 2.51 | 8.61 | 0.20103 | 0.70848 | 29.5459 | 13.9229 | 14.3831 | 0 | 0 | 0 | 0 | 59.75 | 0.24072 | 1998-10-27 | 14:00 | 5 | 23 | 57 | 58.5 | 263 | 6.23 | 2.5 |  | 8.73 | 0.20103 | 0.71363 | 29.126 | 14.2196 | 14.9083 | 293.4115 | 232.5797 | 291.9705 | 0.60111 | 57.1489 | 0.26087 |  |  |  | 200 |  | 240 | 374.6 | -56.0833 | 20 | 372.532 | 46.3133 | 0.042 |  | 0.331 | 0.39644 | -19.7698 | 70.7317 | 0.39224 | 89.2923 | [8 empty] | pH | --- | 7.81 | 7.78 | 7.795 | 0.38486 | 8.05 | --- | --- | --- | --- | --- | pH | --- | 7.81 | 8.25 | --- | --- | --- | --- | --- | pH | --- | 7.99 | 8.22 | --- | --- | --- | --- | --- | pH | --- | 7.98 | 8.23 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.28 | 1.05 | 0.6 | 0.5 | SDS-CDp, mg/L | 1.28 | 1.05 | 0.6 | 0.5 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 53.9325 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.43 | 0.278 | 0.354 | 42.9379 | 1998-10-26 | 14:00 | 5.25 | 23.5 | 59 | 60.5 | 263 | 6.17 | 2.73 | 8.9 | 0.20103 | 0.69326 | 28.5506 | 14.0827 | 14.5481 | 0 | 0 | 0 | 0 | 59.75 | 0.24348 | 1998-10-27 | 17:50 | 8.8333 | 23 | 63.5 | 64.5 | 263 | 6.53 | 2.29 |  | 8.82 | 0.20103 | 0.74036 | 28.8186 | 14.9044 | 15.6262 | 295.3821 | 234.085 | 293.8602 | 0.60536 | 63.3946 | 0.24649 |  |  |  | 210 |  | 232 | 364.0611 | -56.9229 | 16 | 362.1486 | 42.0127 | 0.027 |  | 0.227 | 0.4757 | -109.5608 | 81.1847 | 0.47013 | 94.2569 | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.55 | 3.55 | 3.55 | 3.55 | TOCF, mg/L | 3.55 | 3.55 | 3.55 | 3.55 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 63.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-10-26 | 15:00 | 6.25 | 23.5 | 59 | 60.5 | 263 | 6.31 | 2.71 | 9.02 | 0.20103 | 0.69956 | 28.1574 | 14.4022 | 14.8782 | 0 | 0 | 0 | 0 | 59.75 | 0.24901 | 1998-10-27 | 18:00 | 9 | 23 | 62.5 | 64 | 263 | 6.4 | 3.23 |  | 9.63 | 0.20103 | 0.66459 | 26.3105 | 14.6077 | 15.3151 | 289.9758 | 229.8247 | 288.512 | 0.59419 | 62.6558 | 0.24443 | 7.13 | 6.79 | 7.16 | 215 | 244 | 238 | 319.3498 | -34.1806 | 14 | 318.0802 | 32.407 | 0.031 | 0.137 | 0.251 | 0.36641 | -45.9802 | 78.3972 | 0.36233 | 91.4442 | [8 empty] | Alkalinity | mg/L as CaCO3 | 336 | 346 | 341 | 2.9326 | 412 | 468.5862 | -13.7345 | 9.7884 | 467.0087 | 26.9821 | Alkalinity | mg/L as CaCO3 | 368 | 424 | 493 | -16.2736 | 2.6455 | 491.6248 | 25.1462 | Alkalinity | mg/L as CaCO3 | 332 | 402 | 425.8776 | -5.9397 | 12.1693 | 424.8954 | 21.8631 | Alkalinity | mg/L as CaCO3 | 340 | 382 | 394.4215 | -3.2517 | 10.0529 | 394.011 | 13.708 | TOCp, mg/L | 1.3 | 1.5 | 0.9 | 0.7 | TOCp, mg/L | 1.3 | 1.5 | 0.9 | 0.7 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 51.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 3.6 | 3.5 | 3.55 | 2.8169 | 1998-10-26 | 16:00 | 7.25 | 23.5 | 59 | 60.5 | 263 | 6.29 | 2.43 | 8.72 | 0.20103 | 0.72133 | 29.1606 | 14.3566 | 14.8311 | 0 | 0 | 0 | 0 | 59.75 | 0.24822 | 1998-10-28 | 5:30 | 20.5 | 23 | 62.5 | 64 | 263 | 6.57 | 2.24 |  | 8.81 | 0.20103 | 0.74574 | 28.8524 | 14.9957 | 15.7219 | 295.779 | 234.3919 | 294.2455 | 0.6062 | 62.6438 | 0.25097 | [12 empty] | 0.142 | [14 empty] | Total dissolved solids | mg/L | 237 | 236 | 236.5 | 0.42283 | 270 | 283.0517 | -4.834 | 5.4 | 282.4761 | 16.2761 | Total dissolved solids | mg/L | 244 | 278 | 319 | -14.7482 | 2.4 | 318.1749 | 23.3126 | Total dissolved solids | mg/L | 231 | 266 | 269.7755 | -1.4194 | 7.6 | 269.3698 | 14.2443 | Total dissolved solids | mg/L | 224 | 255 | 261.2358 | -2.4454 | 10.4 | 260.9549 | 14.1614 | UV254 F, cm-1 | 0.1435 | 0.1435 | 0.1435 | 0.1435 | UV254 F, cm-1 | 0.1435 | 0.1435 | 0.1435 | 0.1435 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 51.0754 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.146 | 0.141 | 0.1435 | 3.4843 | 1998-10-26 | 17:00 | 8.25 | 23.5 | 59 | 60.5 | 263 | 6.33 | 2.34 | 8.67 | 0.20103 | 0.7301 | 29.3345 | 14.4479 | 14.9254 | 0 | 0 | 0 | 0 | 59.75 | 0.2498 | 1998-10-28 | 8:00 | 23 | 23 | 62 | 64 | 263 | 6.53 | 3.5 |  | 10.03 | 0.20103 | 0.65105 | 25.2213 | 14.9044 | 15.6262 | 289.0521 | 229.0686 | 287.5628 | 0.59239 | 62.4076 | 0.25039 | [12 empty] | 0.139 | [14 empty] | Total hardness | mg/L as CaCO3 | 202 | 184 | 193 | 9.3264 | 250 | 313.6897 | -25.4759 | 15.3509 | 312.1974 | 38.1801 | Total hardness | mg/L as CaCO3 | 200 | 210 | 550 | -161.9048 | 12.2807 | 546.1495 | 63.38 | Total hardness | mg/L as CaCO3 | 194 | 228 | 263.3878 | -15.5209 | 14.9123 | 262.6618 | 26.1408 | Total hardness | mg/L as CaCO3 | 192 | 210 | 243.5573 | -15.9796 | 15.7895 | 243.1684 | 21.0424 | UV254 p, cm-1 | 0.0335 | 0.041 | 0.02 | 0.014 | UV254 p, cm-1 | 0.0335 | 0.041 | 0.02 | 0.014 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.0556 | 4.0286 | 4.0421 | 0.66758 | 1998-10-27 | 7:30 | 22.75 | 23.5 | 60 | 61.5 | 263 | 7 | 2.22 | 9.22 | 0.20103 | 0.75922 | 27.5249 | 15.9771 | 16.5052 | 0 | 0 | 0 | 0 | 60.75 | 0.27169 | 1998-10-28 | 9:00 | 24 | 23 | 62 | 64 | 263 | 6.57 | 3.6 |  | 10.17 | 0.20103 | 0.64602 | 24.8604 | 14.9957 | 15.7219 | 288.7092 | 228.7895 | 287.2124 | 0.59171 | 62.4083 | 0.25192 | [12 empty] | 0.137 | [14 empty] | Calcium hardness | mg/L as CaCO3 | 184 | 170 | 177 | 7.9096 | 240 | 339.069 | -41.2787 | 20.9821 | 337.0651 | 47.4879 | Calcium hardness | mg/L as CaCO3 | 178 | 204 | 753 | -269.1176 | 20.5357 | 746.6741 | 76.161 | Calcium hardness | mg/L as CaCO3 | 174 | 226 | 276.0408 | -22.142 | 22.3214 | 274.9733 | 36.7211 | Calcium hardness | mg/L as CaCO3 | 184 | 178 | 241.2858 | -35.5538 | 17.8571 | 240.8537 | 23.6051 | BromideF, ug/L | 69.5 | 69.5 | 69.5 | 69.5 | BromideF, ug/L | 69.5 | 69.5 | 69.5 | 69.5 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 69 | 70 | 69.5 | 1.4388 | 1998-10-27 | 8:00 | 23.25 | 23.5 | 70 | 72.5 | 263 | 8.27 | NA |  | 0.20103 |  |  | 18.8758 | 19.4997 |  |  |  | 0 | 71.25 | 0.27368 | 1998-10-28 | 11:00 | 26 | 23 | 62.5 | 64 | 263 | 6.53 | 2.9 |  | 9.43 | 0.20103 | 0.69247 | 26.8897 | 14.9044 | 15.6262 | 291.9538 | 231.3681 | 290.4495 | 0.59834 | 62.6517 | 0.24941 | [12 empty] | 0.141 | [14 empty] | Turbidity | ntu | 0.404 | 0.17 | 0.287 | 81.5331 | 0.71 | 0.51803 | 27.0374 | 18.9266 | 0.51518 | 44.2911 | Turbidity | ntu | 0.153 | 0.427 | 2.6655 | -524.2389 | 56.7797 | 2.6379 | 94.1998 | Turbidity | ntu | 0.175 | 0.238 | 0.54031 | -127.0194 | 50.565 | 0.53648 | 67.3802 | Turbidity | ntu | 0.107 | 0.188 | 0.46074 | -145.0745 | 69.774 | 0.45807 | 76.6412 | Bromidep, ug/L | 68 | 68 | 67 | 64 | Bromidep, ug/L | 68 | 68 | 67 | 64 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 6 | 5 | 5.5 | 18.1818 | 1998-10-27 | 8:15 | 23.5 | 23.5 | 40 | 41.5 | 263 | 4.54 | NA |  | 0.20103 |  |  | 10.3623 | 10.7048 |  |  |  | 0 | 40.75 | 0.26269 | 1998-10-28 | 12:00 | 27 | 23 | 62.5 | 64 | 263 | 6.57 | 2.9 |  | 9.47 | 0.20103 | 0.69377 | 26.7719 | 14.9957 | 15.7219 | 292.0518 | 231.4383 | 290.5376 | 0.59856 | 62.6514 | 0.25094 | [27 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 378 | 378 | 378 | 378 | AlkF, mg/L CaCO3 | 378 | 378 | 378 | 378
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.11 | 1.44 | 1.275 | 25.8824 | 1998-10-27 | 8:40 | 23.9167 | 23.5 | 50 | 52 | 263 | 5.8 | NA |  | 0.20103 |  |  | 13.2382 | 13.6757 |  |  |  | 0 | 51 | 0.26815 | 1998-10-28 | 13:15 | 28.25 | 23 | 62.5 | 64 | 263 | 6.52 | 2.8 |  | 9.32 | 0.20103 | 0.69957 | 27.2189 | 14.8816 | 15.6023 | 292.4555 | 231.7676 | 290.951 | 0.59936 | 62.6506 | 0.24904 | [12 empty] | 0.139 | [14 empty] | Total organic carbon | mg/L | 1.3 | 1.3 | 1.3 | 0 | 9 | 9.0586 | -0.65134 | 63.3803 | 8.9627 | 85.4954 | Total organic carbon | mg/L | 1.5 | 23.5 | 27.125 | -15.4255 | 57.7465 | 26.8431 | 94.412 | Total organic carbon | mg/L | 0.9 | 7.4 | 6.3082 | 14.7546 | 74.6479 | 6.2516 | 85.6036 | Total organic carbon | mg/L | 0.7 | 5.2 | 4.7816 | 8.0459 | 80.2817 | 4.7508 | 85.2657 | Alkp, mg/L CaCO3 | 341 | 368 | 332 | 340 | Alkp, mg/L CaCO3 | 341 | 368 | 332 | 340
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 4.89 | 3.56 | 4.225 | 31.4793 | 1998-10-27 | 9:00 | 24.25 | 23.5 | 60 | 61.5 | 263 | 6.93 | NA |  | 0.20103 |  |  | 15.8174 | 16.3401 |  |  |  | 0 | 60.75 | 0.26897 | 1998-10-28 | 14:00 | 29 | 23 | 63 | 64.5 | 263 | 6.47 | 2.71 |  | 9.18 | 0.20103 | 0.70479 | 27.6492 | 14.7674 | 15.4826 | 292.819 | 232.065 | 291.3244 | 0.60007 | 63.1499 | 0.24517 | 7.02 | 6.84 | 7.1 | 195 | 250 | 260 | 381.31 | -46.6577 | 22 | 379.0183 | 48.5513 | 0.032 |  | 0.365 | 0.4097 | -12.2469 | 77.7003 | 0.40506 | 92.0998 | [8 empty] | UV254 | cm-1 | 0.033 | 0.034 | 0.0335 | 2.9851 | 0.345 | 0.41281 | -19.6552 | 76.6551 | 0.40812 | 91.7916 | UV254 | cm-1 | 0.041 | 0.951 | 1.3222 | -39.0379 | 71.4286 | 1.3082 | 96.8658 | UV254 | cm-1 | 0.02 | 0.263 | 0.27204 | -3.4376 | 86.0627 | 0.2694 | 92.5762 | UV254 | cm-1 | 0.014 | 0.184 | 0.19946 | -8.4037 | 90.2439 | 0.19806 | 92.9316 | T-HdF, mg/L CaCO3 | 228 | 228 | 228 | 228 | T-HdF, mg/L CaCO3 | 228 | 228 | 228 | 228
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 26 | 26 | 26 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-28 | 15:00 | 30 | 24 | 63 | 64.5 | 263 | 6.46 | 2.66 |  | 9.12 | 0.20103 | 0.70833 | 27.8377 | 14.7446 | 15.0084 | 293.0696 | 232.2655 | 291.576 | 0.60057 | 63.1494 | 0.23767 | 6.99 | 6.98 | 7.05 | 240 | 250 | 260 | 274.2857 | -5.4945 | 4 | 273.8646 | 12.3655 | 0.032 |  | 0.366 | 0.41429 | -13.1928 | 77.7003 | 0.40959 | 92.1873 | [8 empty] | SUVA | L/(mg*m) | 2.5385 | 2.6154 | 2.5769 | 2.9851 | 3.8333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.7333 | 4.0468 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.2222 | 3.5541 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 3.5385 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 193 | 200 | 194 | 192 | T-Hdp, mg/L CaCO3 | 193 | 200 | 194 | 192
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 7.82 | 7.94 | 7.88 | 1.5228 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-28 | 16:00 | 31 | 24 | 63 | 64 | 263 | 6.43 | 2.56 |  | 8.99 | 0.20103 | 0.71524 | 28.2547 | 14.6761 | 14.9387 | 293.5579 | 232.6581 | 292.069 | 0.60155 | 62.8984 | 0.23751 | 7.38 | 7.33 | 7.39 | 220 | 250 | 250 | 325.3516 | -30.1406 | 12 | 324.0637 | 32.1121 | 0.032 | 0.139 | 0.362 | 0.42356 | -17.0046 | 77.7003 | 0.41877 | 92.3586 | [8 empty] | Bromide | mg/L | 68 | 68 | 68 | 0 | --- | 73.1724 | --- | 2.1583 | 73.1085 | 6.9875 | Bromide | mg/L | 68 | --- | 86.75 | --- | 2.1583 | 86.5437 | 21.427 | Bromide | mg/L | 67 | --- | 72.102 | --- | 3.5971 | 72.0487 | 7.0073 | Bromide | mg/L | 64 | --- | 71.8768 | --- | 7.9137 | 71.8174 | 10.8851 | Ca-HdF, mg/L CaCO3 | 224 | 224 | 224 | 224 | Ca-HdF, mg/L CaCO3 | 224 | 224 | 224 | 224
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 8:45 | 47.75 | 24 | 63 | 64.5 | 263 | 6.47 | 2.25 |  | 8.72 | 0.20103 | 0.74197 | 29.1606 | 14.7674 | 15.0317 | 295.4888 | 234.1809 | 293.9805 | 0.60554 | 63.1445 | 0.23805 | 7.26 | 7.6 | 7.63 | 220 | 250 | 260 | 336.2667 | -29.3333 | 12 | 334.8365 | 34.2963 | 0.033 |  | 0.409 | 0.46125 | -12.7748 | 77.0035 | 0.45598 | 92.7629 | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 177 | 178 | 174 | 184 | Ca-Hdp, mg/L CaCO3 | 177 | 178 | 174 | 184
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 355 | 350 | 352.5 | 1.4184 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 10:45 | 49.75 | 24 | 63 | 65 | 263 | 6.43 | 3.22 |  | 9.65 | 0.20103 | 0.66632 | 26.2539 | 14.6761 | 14.9387 | 290.1009 | 229.9183 | 288.6296 | 0.59447 | 63.4055 | 0.23561 |  |  |  | 228 | 250 | 261 | 293.9317 | -12.6175 | 8.8 | 293.1257 | 22.2177 | 0.03 | 0.143 | 0.339 | 0.37015 | -9.1881 | 79.0941 | 0.36599 | 91.803 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1 | 1.44 | 1.22 | 36.0656 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.45 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.4 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.5 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 96 | 130 | 113 | 30.0885 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 11:45 | 50.75 | 24 | 63 | 65 | 263 | 6.46 | 3 |  | 9.46 | 0.20103 | 0.68288 | 26.8013 | 14.7446 | 15.0084 | 291.2661 | 230.8362 | 289.7818 | 0.59688 | 63.4031 | 0.23671 | 7.4 | 7.29 | 7.63 | 220 | 250 | 258 | 314.6 | -21.938 | 12 | 313.4382 | 29.8107 | 0.03 |  | 0.342 | 0.3879 | -13.422 | 79.0941 | 0.38351 | 92.1775 | [8 empty] | SDS-Cl2 demand | mg/L | 1.5 | 1.06 | 1.28 | 34.375 | --- | 11.4352 | --- | 69.7041 | 11.3096 | 88.6822 | SDS-Cl2 demand | mg/L | 1.05 | --- | 40.7375 | --- | 75.1479 | 40.3009 | 97.3946 | SDS-Cl2 demand | mg/L | 0.6 | --- | 7.998 | --- | 85.7988 | 7.9206 | 92.4248 | SDS-Cl2 demand | mg/L | 0.5 | --- | 5.8347 | --- | 88.1657 | 5.7945 | 91.3711 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 21 | 27 | 24 | 25 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 12:45 | 51.75 | 24 | 63.5 | 65.5 | 263 | 6.43 | 2.91 |  | 9.34 | 0.20103 | 0.68844 | 27.1585 | 14.6761 | 14.9387 | 291.6537 | 231.149 | 290.1744 | 0.59765 | 63.9023 | 0.23377 | 7.4 |  | 7.37 | 238 | 255 | 263 | 276.5155 | -5.139 | 4.8 | 276.0446 | 13.7821 | 0.029 |  | 0.343 | 0.3965 | -15.5982 | 79.7909 | 0.39201 | 92.6022 | [8 empty] | SDS-Chlorination temp. | oC | 26 | 26 | 26 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 74.9332 | 82.0843 | 65.7598 | 62.6452 | Qp/QT (THM4), % | 113.4153 | 124.2389 | 99.531 | 94.8168
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 4.1 | 6.1 | 5.1 | 39.2157 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 14:45 | 53.75 | 24 | 63.5 | 65 | 263 | 6.4 | 2.49 |  | 8.89 | 0.20103 | 0.71991 | 28.5838 | 14.6077 | 14.869 | 293.8875 | 232.925 | 292.404 | 0.60221 | 63.6478 | 0.23361 |  |  |  | 238 | 251 | 269 | 280.8434 | -4.4027 | 4.8 | 280.3221 | 15.0977 | 0.03 | 0.138 | 0.371 | 0.43523 | -17.3118 | 79.0941 | 0.4303 | 93.0281 | [8 empty] | SDS-Chlorination pH | --- | 7.8 | 7.86 | 7.83 | 0.76628 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.91 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.96 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.99 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | 36 | 36
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 15:45 | 54.75 | 24 | 63.5 | 65 | 263 | 6.4 | 2.42 |  | 8.82 | 0.20103 | 0.72562 | 28.8186 | 14.6077 | 14.869 | 294.2975 | 233.25 | 292.812 | 0.60305 | 63.647 | 0.23362 | 7.72 | 7.41 | 7.69 | 238 | 250 | 268 | 281.7355 | -5.1252 | 4.8 | 281.2034 | 15.3638 | 0.031 | 0.139 | 0.379 | 0.44102 | -16.3643 | 78.3972 | 0.43603 | 92.8904 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 22.3443 | 21.6456 | 23.822 | 24.2529 | SDS-HAA5b, ug/L | NA | NA | 6.2441 | 6.8963
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 121.1 | 163.1 | 142.1 | 29.5567 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-29 | 16:45 | 55.75 | 24 | 63.5 | 65 | 263 | 6.37 | 2.39 |  | 8.76 | 0.20103 | 0.72717 | 29.0228 | 14.5392 | 14.7993 | 294.4038 | 233.3399 | 292.9248 | 0.60324 | 63.6468 | 0.23252 |  |  |  | 238 | 253 | 268 | 281.9833 | -5.2176 | 4.8 | 281.4506 | 15.4381 | 0.031 |  | 0.382 | 0.44334 | -16.0584 | 78.3972 | 0.43835 | 92.928 | [8 empty] | SDS-TOX | mg Cl- /L | 91 | 100 | 95.5 | 9.4241 | --- | 981.7069 | --- | 72.9078 | 970.7496 | 90.1622 | SDS-TOX | mg Cl- /L | 120 | --- | 3026.25 | --- | 65.9574 | 2994.2768 | 95.9924 | SDS-TOX | mg Cl- /L | 58 | --- | 659.0204 | --- | 83.5461 | 652.7327 | 91.1143 | SDS-TOX | mg Cl- /L | 50 | --- | 483.2241 | --- | 85.8156 | 479.9563 | 89.5824 | SDS-TOXb, ug Cl- /L | 159.9217 | 161.654 | 158.8372 | 162.9982 | SDS-TOXb, ug Cl- /L | NA | NA | 59.3813 | 65.6792
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 3 | 2.8 | 2.9 | 6.8966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 8:45 | 71.75 | 24 | 63.5 | 65 | 263 | 6.31 | 1.77 |  | 8.08 | 0.20103 | 0.78094 | 31.5495 | 14.4022 | 14.6599 | 298.3113 | 236.4483 | 296.827 | 0.61121 | 63.6388 | 0.23036 | 7.32 | 7.64 | 7.61 | 238 | 248 | 269 | 292.7797 | -8.84 | 4.8 | 292.1225 | 18.5273 | 0.032 |  | 0.445 | 0.54099 | -21.5718 | 77.7003 | 0.53489 | 94.0174 | [8 empty] | SDS-CHCl3 | mg/L | 19 | 20 | 19.5 | 5.1282 | --- | 341.9138 | --- | 82.7434 | 337.9274 | 94.2295 | SDS-CHCl3 | mg/L | 25 | --- | 1125 | --- | 77.8761 | 1112.8983 | 97.7536 | SDS-CHCl3 | mg/L | 8.6 | --- | 221.6612 | --- | 92.3894 | 219.4322 | 96.0808 | SDS-CHCl3 | mg/L | 6.6 | --- | 158.9803 | --- | 94.1593 | 157.8309 | 95.8183 | SDS-CDb, mg/L | 2.0182 | 1.6188 | 1.8412 | 1.8915 | SDS-CDb, mg/L | NA | NA | 0.617 | 0.69307
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | 30 | 27 | 28.5 | 10.5263 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 9:45 | 72.75 | 23 | 63.5 | 65 | 263 | 6.29 | 2.61 |  | 8.9 | 0.20103 | 0.70674 | 28.5506 | 14.3566 | 15.0519 | 292.9297 | 232.1866 | 291.477 | 0.60017 | 63.6498 | 0.23648 |  |  |  | 238 |  | 266 | 278.9195 | -4.857 | 4.8 | 278.4302 | 14.5208 | 0.035 | 0.139 | 0.403 | 0.40498 | -0.49152 | 75.6098 | 0.40056 | 91.2622 | [8 empty] | SDS-BDCM | mg/L | 15 | 16 | 15.5 | 6.4516 | --- | 44.8103 | --- | 35.4167 | 44.4479 | 65.1277 | SDS-BDCM | mg/L | 18 | --- | 93 | --- | 25 | 92.1749 | 80.4719 | SDS-BDCM | mg/L | 11 | --- | 37.5306 | --- | 54.1667 | 37.2531 | 70.4722 | SDS-BDCM | mg/L | 8.7 | --- | 30.6118 | --- | 63.75 | 30.4465 | 71.4253 | TOCb, mg/L | 1.864 | 1.8673 | 1.8074 | 1.7646 | TOCb, mg/L | NA | NA | 0.91243 | 0.84772
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 23 | 28 | 25.5 | 19.6078 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 10:30 | 73.5 | 23 | 63.5 | 65 | 263 | 6.29 | 2.51 |  | 8.8 | 0.20103 | 0.71477 | 28.8864 | 14.3566 | 15.0519 | 293.5024 | 232.6405 | 292.0468 | 0.60134 | 63.6487 | 0.23648 |  |  |  | 239 | 253 | 266 | 277.5657 | -4.348 | 4.4 | 277.1046 | 13.751 | 0.03 | 0.137 | 0.396 | 0.42793 | -8.0627 | 79.0941 | 0.42317 | 92.9106 | [8 empty] | SDS-DBCM | mg/L | 11 | 12 | 11.5 | 8.6957 | --- | -10.569 | --- | -125.4902 | -10.2961 | 211.6928 | SDS-DBCM | mg/L | 12 | --- | -74.25 | --- | -135.2941 | -73.3011 | 116.3708 | SDS-DBCM | mg/L | 12 | --- | -2.0816 | --- | -135.2941 | -1.9343 | 720.3751 | SDS-DBCM | mg/L | 11 | --- | 2.5503 | --- | -115.6863 | 2.6141 | -320.7988 | UV254 b, cm-1 | 0.061073 | 0.059364 | 0.062287 | 0.062374 | UV254 b, cm-1 | NA | NA | 0.020579 | 0.020712
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 13:00 | 76 | 23 | 63 | 64.5 | 263 | 6.16 | 2.14 |  | 8.3 | 0.20103 | 0.74217 | 30.6867 | 14.0599 | 14.7408 | 295.4515 | 234.21 | 294.0171 | 0.60524 | 63.1448 | 0.23344 | 7.6 | 7.57 | 7.69 | 242 | 254 | 270 | 273.028 | -1.1215 | 3.2 | 272.6647 | 11.2463 | 0.031 |  | 0.417 | 0.46733 | -12.07 | 78.3972 | 0.46222 | 93.2933 | [8 empty] | SDS-CHBr3 | mg/L | 1.9 | 2.2 | 2.05 | 14.6341 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.9 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.9 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 68.376 | 68.2687 | 67.856 | 66.0545 | Bromideb, ug/L | NA | NA | 67.0117 | 64.2851
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 1.2 | 1.1 | 1.15 | 8.6957 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 14:00 | 77 | 23 | 63 | 64.5 | 263 | 6.16 | 2.13 |  | 8.29 | 0.20103 | 0.74306 | 30.725 | 14.0599 | 14.7408 | 295.5163 | 234.2614 | 294.0816 | 0.60538 | 63.1446 | 0.23344 | 7.87 | 7.51 | 7.89 | 239 | 255 | 270 | 281.8122 | -4.3749 | 4.4 | 281.3108 | 15.0406 | 0.03 |  | 0.411 | 0.47174 | -14.7796 | 79.0941 | 0.46657 | 93.5701 | [8 empty] | SDS-THM4 | mg/L | 46.9 | 50.2 | 48.55 | 6.7971 | --- | 371.1362 | --- | 65.8339 | 367.1477 | 86.7764 | SDS-THM4 | mg/L | 56.7 | --- | 1124.2 | --- | 60.0985 | 1112.4559 | 94.9032 | SDS-THM4 | mg/L | 35.5 | --- | 253.051 | --- | 75.0176 | 250.775 | 85.8439 | SDS-THM4 | mg/L | 30.2 | --- | 190.4571 | --- | 78.7474 | 189.2483 | 84.0421 | Alkb, mg/L CaCO3 | 350.2747 | 369.7916 | 347.7505 | 354.1948 | Alkb, mg/L CaCO3 | NA | NA | 332.2158 | 341.9696
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 6.5 | 7.1 | 6.8 | 8.8235 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 15:00 | 78 | 23 | 63 | 64.5 | 263 | 6.17 | 1.88 |  | 8.05 | 0.20103 | 0.76646 | 31.6708 | 14.0827 | 14.7647 | 297.2219 | 235.6115 | 295.7765 | 0.60888 | 63.1411 | 0.23384 |  |  |  | 242 | 255 | 265 | 276.2553 | -4.2473 | 3.2 | 275.8535 | 12.2723 | 0.032 |  | 0.427 | 0.50943 | -19.3053 | 77.7003 | 0.50383 | 93.6487 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 201.7734 | 205.0164 | 205.6417 | 205.4477 | T-Hdb, mg/L CaCO3 | NA | NA | 194.1595 | 193.866
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | NR | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 16:00 | 79 | 23 | 63 | 64.5 | 263 | 6.09 | 2.81 |  | 8.9 | 0.20103 | 0.68427 | 28.5506 | 13.9001 | 14.5733 | 291.3093 | 230.9394 | 289.9113 | 0.59671 | 63.1533 | 0.23076 |  |  |  | 239 | 253 | 269 | 273.8399 | -1.7992 | 4.4 | 273.4365 | 12.594 | 0.029 |  | 0.397 | 0.39165 | 1.3473 | 79.7909 | 0.38745 | 92.5152 | [8 empty] | SDS-DCAA* | mg/L | 4.8 | 4.9 | 4.85 | 2.0619 | --- | 86.4017 | --- | 82.9825 | 85.3934 | 94.3204 | SDS-DCAA* | mg/L | 6.5 | --- | 281.5 | --- | 77.193 | 278.4746 | 97.6659 | SDS-DCAA* | mg/L | 2.2 | --- | 55.8735 | --- | 92.2807 | 55.3119 | 96.0226 | SDS-DCAA* | mg/L | 1.6 | --- | 40.1247 | --- | 94.386 | 39.8341 | 95.9833 | Ca-Hdb, mg/L CaCO3 | 188.7814 | 186.2412 | 191.1201 | 198.9419 | Ca-Hdb, mg/L CaCO3 | NA | NA | 174.2345 | 186.0733
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 2.1 | 2.8 | 2.45 | 28.5714 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-30 | 17:00 | 80 | 23 | 63 | 64.5 | 263 | 6.09 | 2.71 |  | 8.8 | 0.20103 | 0.69205 | 28.8864 | 13.9001 | 14.5733 | 291.8573 | 231.3739 | 290.4567 | 0.59783 | 63.1522 | 0.23076 | 7.42 | 7.45 | 7.65 | 237 | 254 | 270 | 279.214 | -3.4126 | 5.2 | 278.7253 | 14.97 | 0.029 |  | 0.373 | 0.40081 | -7.4553 | 79.7909 | 0.3965 | 92.6861 | [8 empty] | SDS-TCAA* | mg/L | 3.1 | 3.1 | 3.1 | 0 | --- | 80.3414 | --- | 87.8431 | 79.3863 | 96.095 | SDS-TCAA* | mg/L | 4.9 | --- | 262.4 | --- | 80.7843 | 259.5671 | 98.1122 | SDS-TCAA* | mg/L | 1.2 | --- | 50.7918 | --- | 95.2941 | 50.273 | 97.613 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 5.1 | 7.9 | 6.5 | 43.0769 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-31 | 9:00 | 96 | 23 | 63 | 64.5 | 263 | 5.89 | 1.82 |  | 7.71 | 0.20103 | 0.76394 | 33.1115 | 13.4436 | 14.0947 | 296.9894 | 235.4804 | 295.6119 | 0.6082 | 63.1418 | 0.22322 | 7.29 | 7.46 | 7.68 | 245 | 255 | 267 | 266.1813 | 0.30662 | 2 | 265.9441 | 7.8754 | 0.028 |  | 0.458 | 0.51729 | -12.9451 | 80.4878 | 0.51181 | 94.5292 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 57.2 | 58.9 | 58.05 | 2.9285 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-31 | 10:00 | 97 | 23 | 63.5 | 64.5 | 263 | 5.88 | 0.75 |  | 6.63 | 0.20103 | 0.88688 | 38.6682 | 13.4208 | 14.0708 | 306.2503 | 242.8252 | 304.8323 | 0.62716 | 63.3728 | 0.22203 |  |  |  | 243 |  |  | 304.88 |  | 2.8 | 304.1883 | 20.1153 | 0.037 |  | 0.507 | 0.97846 | -92.9901 | 74.216 | 0.96794 | 96.1774 | [8 empty] | SDS-DBAA* | mg/L | 2.4 | 2.5 | 2.45 | 4.0816 | --- | -2.0328 | --- | -113.0435 | -1.9773 | 223.9043 | SDS-DBAA* | mg/L | 2.3 | --- | -12.075 | --- | -100 | -11.9169 | 119.3004 | SDS-DBAA* | mg/L | 2.6 | --- | -0.35918 | --- | -126.087 | -0.32823 | 892.1388 | SDS-DBAA* | mg/L | 2.5 | --- | 0.5666 | --- | -117.3913 | 0.58119 | -330.1543 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 63.7 | 66 | 64.85 | 3.5466 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-31 | 10:20 | 97.3333 | 23 | 63.5 | 65 | 263 | 5.89 | 0.72 |  | 6.61 | 0.20103 | 0.89107 | 38.7882 | 13.4436 | 14.0947 | 306.5788 | 243.0837 | 305.1568 | 0.62784 | 63.6222 | 0.22154 |  |  |  | 241 | 255 |  | 323.625 |  | 3.6 | 322.6998 | 25.3176 | 0.031 |  | 0.53 | 1.0638 | -100.7193 | 78.3972 | 1.0522 | 97.0539 | [8 empty] | SDS-BCAA* | mg/L | 4.3 | 4.3 | 4.3 | 0 | --- | 12.9207 | --- | 36.7647 | 12.8141 | 66.4432 | SDS-BCAA* | mg/L | 4.9 | --- | 28.65 | --- | 27.9412 | 28.3887 | 82.7396 | SDS-BCAA* | mg/L | 2.9 | --- | 10.8592 | --- | 57.3529 | 10.7759 | 73.0881 | SDS-BCAA* | mg/L | 2.6 | --- | 8.615 | --- | 61.7647 | 8.5696 | 69.6603 | Qp/QT (HAA5), % | 8.4995 | 9.1319 | 7.781 | 7.507 | Qp/QT (HAA5), % | 65.1626 | 70.0113 | 59.6542 | 57.5533
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-31 | 10:40 | 97.6667 | 23 | 63.5 | 65 | 263 | 5.92 | 0.71 |  | 6.63 | 0.20103 | 0.89291 | 38.6682 | 13.5121 | 14.1665 | 306.7284 | 243.1964 | 305.2983 | 0.62817 | 63.6218 | 0.22267 |  |  |  | 242 | 255 |  | 316.7042 |  | 3.2 | 315.8634 | 23.3846 | 0.032 |  | 0.552 | 1.0732 | -94.4185 | 77.7003 | 1.0615 | 96.9853 | [8 empty] | SDS-TBAA | mg/L | NR | NR | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 134.1487 | 134.3014 | 133.8055 | 133.6997 | SDS-THM4b, ug/L | 81.1403 | 82.3104 | 78.5086 | 77.6979
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-31 | 11:40 | 98.6667 | 22 | 63.5 | 65 | 263 | 5.83 | 0.67 |  | 6.5 | 0.20103 | 0.89692 | 39.4615 | 13.3067 | 14.3696 | 307.022 | 243.4469 | 305.6127 | 0.6287 | 63.6213 | 0.22586 |  |  |  | 242 | 255 |  | 319.6119 |  | 3.2 | 318.7517 | 24.0788 | 0.032 |  | 0.629 | 1.1137 | -77.0614 | 77.7003 | 1.1017 | 97.0955 | [8 empty] | SDS-CDBAA | mg/L | 3.1 | 3.1 | 3.1 | 0 | --- | 0.85862 | --- | -26.5306 | 0.88633 | -249.7554 | SDS-CDBAA | mg/L | 3.3 | --- | -7.325 | --- | -34.6939 | -7.2081 | 145.7818 | SDS-CDBAA | mg/L | 3.2 | --- | 1.6694 | --- | -30.6122 | 1.6854 | -89.8658 | SDS-CDBAA | mg/L | 3.2 | --- | 2.1259 | --- | -30.6122 | 2.134 | -49.9537 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-31 | 12:00 | 99 | 22 | 63.5 | 65 | 263 | 5.86 | 0.66 |  | 6.52 | 0.20103 | 0.89877 | 39.3374 | 13.3751 | 14.4436 | 307.173 | 243.5607 | 305.7556 | 0.62904 | 63.621 | 0.22703 |  |  |  | 242 | 255 |  | 321.0303 |  | 3.2 | 320.1499 | 24.4104 | 0.033 | 0.135 | 0.647 | 1.1246 | -73.8186 | 77.0035 | 1.1124 | 97.0336 | [8 empty] | SDS-DCBAA | mg/L | 3.5 | 3.1 | 3.3 | 12.1212 | --- | 14.3345 | --- | 49.2308 | 14.198 | 76.7574 | SDS-DCBAA | mg/L | 4.7 | --- | 27.2 | --- | 27.6923 | 26.9525 | 82.5619 | SDS-DCBAA | mg/L | 2.5 | --- | 10.6633 | --- | 61.5385 | 10.5779 | 76.3657 | SDS-DCBAA | mg/L | 2.3 | --- | 8.315 | --- | 64.6154 | 8.2696 | 72.1874 | SDS-TOXb, ug Cl- /L | 330.6563 | 331.2683 | 329.585 | 329.7915 | SDS-TOXb, ug Cl- /L | 185.032 | 189.7238 | 176.8184 | 178.4013
[44 empty] | 1998-10-31 | 12:20 | 99.3333 | 22 | 63.5 | 65 | 263 | 5.89 | 0.66 |  | 6.55 | 0.20103 | 0.89924 | 39.1527 | 13.4436 | 14.5175 | 307.2157 | 243.5887 | 305.7908 | 0.62915 | 63.6209 | 0.22819 |  |  |  | 248 | 255 |  | 267.8485 |  | 0.8 | 267.6262 | 7.3334 | 0.033 |  | 0.668 | 1.1296 | -69.1061 | 77.0035 | 1.1173 | 97.0466 | [8 empty] | SDS-HAA5 | mg/L | 10.3 | 10.5 | 10.4 | 1.9231 | --- | 174.7103 | --- | 82.0844 | 172.6788 | 93.9773 | SDS-HAA5 | mg/L | 13.7 | --- | 568.075 | --- | 76.3997 | 561.976 | 97.5622 | SDS-HAA5 | mg/L | 6 | --- | 112.2245 | --- | 89.6641 | 111.1132 | 94.6001 | SDS-HAA5 | mg/L | 4.1 | --- | 81.3643 | --- | 92.9371 | 80.7815 | 94.9246 | SDS-CDb, mg/L | 3.9747 | 3.9351 | 3.9429 | 3.9454 | SDS-CDb, mg/L | 2.306 | 2.0021 | 2.0625 | 2.0811
[44 empty] | 1998-10-31 | 12:40 | 99.6667 | 22 | 63.5 | 65 | 263 | 5.86 | 0.64 |  | 6.5 | 0.20103 | 0.90154 | 39.4615 | 13.3751 | 14.4436 | 307.3893 | 243.7322 | 305.9709 | 0.62948 | 63.6205 | 0.22703 |  |  |  | 242 | 255 |  | 323.25 |  | 3.2 | 322.3448 | 24.9251 | 0.033 |  | 0.679 | 1.1553 | -70.1422 | 77.0035 | 1.1428 | 97.1123 | [8 empty] | SDS-HAA6 | mg/L | 14.6 | 14.8 | 14.7 | 1.3605 | --- | 187.631 | --- | 77.3323 | 185.4929 | 92.0752 | SDS-HAA6 | mg/L | 18.6 | --- | 596.725 | --- | 71.3184 | 590.3647 | 96.8494 | SDS-HAA6 | mg/L | 8.9 | --- | 123.0837 | --- | 86.276 | 121.8891 | 92.6983 | SDS-HAA6 | mg/L | 6.7 | --- | 89.9793 | --- | 89.6685 | 89.3511 | 92.5015 | TOCb, mg/L | 3.3588 | 3.3628 | 3.3438 | 3.3361 | TOCb, mg/L | 2.0838 | 2.1148 | 1.9692 | 1.9097
[44 empty] | 1998-10-31 | 13:00 | 100 | 22 | 63.5 | 65 | 263 | 5.89 | 0.61 |  | 6.5 | 0.20103 | 0.90615 | 39.4615 | 13.4436 | 14.5175 | 307.7575 | 244.0183 | 306.33 | 0.63025 | 63.6197 | 0.22819 | 7.79 | 7.86 | 7.76 | 247 | 255 |  | 278.9672 |  | 1.2 | 278.6093 | 11.3454 | 0.033 | 0.136 | 0.719 | 1.2105 | -68.3531 | 77.0035 | 1.1973 | 97.2437 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.13415 | 0.13414 | 0.13389 | 0.13378 | UV254 b, cm-1 | 0.071821 | 0.071738 | 0.069827 | 0.068968
[44 empty] | 1998-11-01 | 9:30 | 120.5 | 22 | 62.5 | 63.5 | 263 | 5.68 | 0.4 |  | 6.08 | 0.20103 | 0.93421 | 42.2566 | 12.9643 | 13.9999 | 309.9267 | 245.7798 | 308.5413 | 0.63454 | 62.3655 | 0.22448 | 7.45 | 7.63 |  | 249 | 254 | 276 | 264.2 | 4.2754 | 0.4 | 264.0359 | 5.6946 | 0.042 | 0.136 | 1.204 | 1.5848 | -31.6279 | 70.7317 | 1.5681 | 97.3217 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 69.3725 | 69.363 | 69.3055 | 69.0871 | Bromideb, ug/L | 68.5226 | 68.4498 | 68.0086 | 66.3346
[44 empty] | 1998-11-01 | 10:40 | 121.6667 | 22 | 64 | 65.5 | 263 | 5.89 | 5.94 |  | 11.83 | 0.20103 | 0.49789 | 21.2316 | 13.4436 | 14.5175 | 278.743 | 221.013 | 277.4501 | 0.57084 | 64.1792 | 0.2262 | 7.7 |  | 7.75 | 228 | 255 | 263 | 271.8148 | -3.3516 | 8.8 | 271.3242 | 15.9677 | 0.023 |  | 0.403 | 0.26299 | 34.743 | 83.9721 | 0.2603 | 91.164 | [47 empty] | Alkb, mg/L CaCO3 | 374.8552 | 377.0868 | 374.4207 | 375.1474 | Alkb, mg/L CaCO3 | 353.8898 | 370.9989 | 350.5591 | 356.1297
[44 empty] | 1998-11-01 | 11:00 | 122 | 22 | 64 | 65.5 | 263 | 5.89 | 5.83 |  | 11.72 | 0.20103 | 0.50256 | 21.4403 | 13.4436 | 14.5175 | 279.0441 | 221.2517 | 277.7499 | 0.57145 | 64.1785 | 0.22621 | 7.69 |  | 7.88 | 228 | 254 |  | 272.2264 |  | 8.8 | 271.7312 | 16.0935 | 0.022 |  | 0.347 | 0.26625 | 23.2708 | 84.669 | 0.26352 | 91.6513 | [47 empty] | T-Hdb, mg/L CaCO3 | 225.0252 | 225.4431 | 225.3545 | 225.2975 | T-Hdb, mg/L CaCO3 | 205.1931 | 208.3968 | 207.7176 | 207.2808
[44 empty] | 1998-11-01 | 11:20 | 122.3333 | 22 | 64 | 65.5 | 263 | 5.9 | 5.73 |  | 11.63 | 0.20103 | 0.50731 | 21.6139 | 13.4664 | 14.5422 | 279.3518 | 221.4939 | 278.0539 | 0.57209 | 64.1779 | 0.22659 |  |  |  | 231 | 254 | 264 | 269.5637 | -2.1075 | 7.6 | 269.1311 | 14.1682 | 0.021 |  | 0.307 | 0.26963 | 12.1712 | 85.3659 | 0.26685 | 92.1303 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 220.0052 | 219.7993 | 220.1095 | 220.9972 | Ca-Hdb, mg/L CaCO3 | 193.3736 | 191.7948 | 194.1729 | 200.9787
[44 empty] | 1998-11-01 | 13:05 | 124.0833 | 22 | 64 | 65.5 | 263 | 5.92 | 5.27 |  | 11.19 | 0.20103 | 0.52904 | 22.5031 | 13.5121 | 14.5915 | 280.7663 | 222.6118 | 279.4572 | 0.575 | 64.175 | 0.22737 |  |  |  | 228 | 254 | 264 | 274.7135 | -4.0581 | 8.8 | 274.1877 | 16.8453 | 0.017 |  | 0.261 | 0.2856 | -9.4262 | 88.1533 | 0.28258 | 93.984 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-11-01 | 13:30 | 124.5 | 22 | 64 | 65.5 | 263 | 5.91 | 6.29 |  | 12.2 | 0.20103 | 0.48443 | 20.5574 | 13.4893 | 14.5668 | 277.8812 | 220.3261 | 276.5879 | 0.56908 | 64.1809 | 0.22697 | 7.85 |  |  | 228 |  | 264 | 270.6709 | -2.5269 | 8.8 | 270.1915 | 15.6154 | 0.019 |  | 0.251 | 0.26048 | -3.7763 | 86.7596 | 0.25777 | 92.629 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-11-02 | 8:30 | 143.5 | 22 | 64.5 | 65.5 | 263 | 5.71 | 3.67 |  | 9.38 | 0.20103 | 0.60874 | 27.0384 | 13.0328 | 14.0739 | 286.0431 | 226.834 | 284.7576 | 0.58566 | 64.4143 | 0.21849 | 8.01 | 7.94 | 7.87 | 232 | 253 | 267 | 278.0054 | -4.1219 | 7.2 | 277.506 | 16.3982 | 0.018 | 0.139 | 0.308 | 0.33876 | -9.9871 | 87.4564 | 0.33528 | 94.6313 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-11-02 | 8:50 | 143.8333 | 22 | 64 | 65 | 263 | 5.68 | 13.49 |  | 19.17 | 0.20103 | 0.2963 | 12.7194 | 12.9643 | 13.9999 | 266.3331 | 211.2089 | 265.1426 | 0.54529 | 63.9547 | 0.2189 |  |  |  | 226 | 253 | 258 | 260.1053 | -0.81599 | 9.6 | 259.737 | 12.9889 | 0.02 |  | 0.25 | 0.1955 | 21.8 | 86.0627 | 0.1936 | 89.6697 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-11-02 | 10:20 | 145.3333 | 22 | 64.5 | 66 | 263 | 5.77 | 12.06 |  | 17.83 | 0.20103 | 0.32361 | 13.7504 | 13.1697 | 14.2218 | 267.9523 | 212.4776 | 266.7352 | 0.54866 | 64.7013 | 0.21981 |  |  |  | 218 | 253 | 256 | 265.3101 | -3.6368 | 12.8 | 264.7911 | 17.671 | 0.018 |  | 0.191 | 0.20354 | -6.5677 | 87.4564 | 0.20151 | 91.0674 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-11-02 | 10:40 | 145.6667 | 22 | 64.5 | 65.5 | 263 | 5.71 | 13.6 |  | 19.31 | 0.20103 | 0.2957 | 12.6199 | 13.0328 | 14.0739 | 266.2998 | 211.1774 | 265.103 | 0.54524 | 64.4548 | 0.21835 |  |  |  | 221 |  | 256 | 262.1757 | -2.4124 | 11.6 | 261.7288 | 15.5614 | 0.018 |  | 0.186 | 0.19619 | -5.4793 | 87.4564 | 0.19426 | 90.7339 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-11-02 | 11:20 | 146.3333 | 22 | 64.5 | 66 | 263 | 5.77 | 12.87 |  | 18.64 | 0.20103 | 0.30955 | 13.1094 | 13.1697 | 14.2218 | 267.1187 | 211.8166 | 265.9054 | 0.54695 | 64.703 | 0.2198 |  |  |  | 221 |  | 255 | 263.0016 | -3.1379 | 11.6 | 262.5408 | 15.8226 | 0.016 |  | 0.188 | 0.20066 | -6.7351 | 88.8502 | 0.19864 | 91.9451 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-11-02 | 11:40 | 146.6667 | 22 | 64 | 65.5 | 263 | 5.71 | 14.06 |  | 19.77 | 0.20103 | 0.28882 | 12.303 | 13.0328 | 14.0739 | 265.8964 | 210.8576 | 264.7015 | 0.54441 | 64.2056 | 0.2192 |  |  |  | 219 |  | 254 | 262.5896 | -3.3817 | 12.4 | 262.1164 | 16.4493 | 0.013 |  | 0.186 | 0.1965 | -5.6442 | 90.9408 | 0.19451 | 93.3164 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-11-02 | 12:00 | 147 | 22 | 64 | 65 | 263 | 5.65 | 14.43 |  | 20.08 | 0.20103 | 0.28137 | 12.0976 | 12.8958 | 13.926 | 265.4581 | 210.5202 | 264.2779 | 0.54348 | 63.9565 | 0.21774 |  |  |  | 222 | 253 | 254 | 260.9633 | -2.7414 | 11.2 | 260.5447 | 14.7939 | 0.013 |  | 0.177 | 0.1946 | -9.9416 | 90.9408 | 0.19265 | 93.2519 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-11-02 | 12:20 | 147.3333 | 22 | 64 | 65 | 263 | 5.84 | 14 |  | 19.84 | 0.20103 | 0.29435 | 12.256 | 13.3295 | 14.3943 | 266.2276 | 211.0981 | 265.0035 | 0.54517 | 63.9548 | 0.22507 |  |  |  | 220 | 253 | 254 | 262.5143 | -3.3521 | 12 | 262.0423 | 16.0441 | 0.013 |  | 0.18 | 0.19794 | -9.9651 | 90.9408 | 0.19588 | 93.3634 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-11-02 | 13:00 | 148 | 22 | 64 | 65 | 263 | 5.75 | 13.47 |  | 19.22 | 0.20103 | 0.29917 | 12.6837 | 13.1241 | 14.1725 | 266.5056 | 211.3338 | 265.2994 | 0.54569 | 63.9543 | 0.2216 | 7.42 | 8.03 | 8.11 | 224 | 253 | 255 | 261.0987 | -2.3917 | 10.4 | 260.6932 | 14.0752 | 0.013 | 0.139 | 0.183 | 0.19921 | -8.8564 | 90.9408 | 0.19717 | 93.4068 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-11-02 | 14:00 | 149 | 22 | 64 | 65.5 | 263 | 5.8 | 12.87 |  | 18.67 | 0.20103 | 0.31066 | 13.0868 | 13.2382 | 14.2957 | 267.186 | 211.8649 | 265.966 | 0.54711 | 64.2029 | 0.22266 |  |  |  | 223 |  | 254 | 262.1678 | -3.2157 | 10.8 | 261.7359 | 14.7996 | 0.013 |  | 0.184 | 0.20231 | -9.9517 | 90.9408 | 0.20022 | 93.5073 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-11-02 | 15:00 | 150 | 22 | 64 | 66 | 263 | 5.77 | 12.1 |  | 17.87 | 0.20103 | 0.32289 | 13.7174 | 13.1697 | 14.2218 | 267.9092 | 212.4435 | 266.6923 | 0.54857 | 64.4514 | 0.22066 |  |  |  | 222 | 253 | 257 | 263.3521 | -2.4716 | 11.2 | 262.8985 | 15.5567 | 0.014 |  | 0.183 | 0.20525 | -12.1603 | 90.2439 | 0.20316 | 93.1087
[44 empty] | 1998-11-02 | 16:00 | 151 | 22 | 64 | 65 | 263 | 5.74 | 13.6 |  | 19.34 | 0.20103 | 0.29679 | 12.5988 | 13.1012 | 14.1478 | 266.3655 | 211.2245 | 265.1621 | 0.54539 | 63.9546 | 0.22122 | 7.85 | 8.3 |  | 221 | 253 | 264 | 262.2397 | 0.66678 | 11.6 | 261.7897 | 15.5811 | 0.013 | 0.14 | 0.181 | 0.19858 | -9.712 | 90.9408 | 0.19655 | 93.386
[44 empty] | 1998-11-03 | 8:30 | 167.5 | 22 | 64.5 | 66 | 263 | 5.86 | 7.45 | X | 13.31 | 0.20103 | 0.44027 | 18.7596 | 13.3751 | 14.4436 | 275.0806 | 218.1143 | 273.8113 | 0.56332 | 64.6867 | 0.22329 |  |  |  | 229 |  | 258 | 266.5181 | -3.3016 | 8.4 | 266.1001 | 13.9422 | 0.015 |  | 0.219 | 0.24458 | -11.6782 | 89.547 | 0.24202 | 93.8021
[44 empty] | 1998-11-03 | 15:45 |  | 22 | 62.5 | 64 | 263 | 5.52 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 12.5991 | 13.6056 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-11-03 | 16:05 |  | 22 | 70.5 | 72 | 263 | 6.16 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 14.0599 | 15.183 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-11-03 | 16:25 |  | 22 | 39.5 | 40.5 | 263 | 3.42 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 7.806 | 8.4295 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-11-03 | 16:45 |  | 22 | 50.5 | 52 | 263 | 4.4 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 10.0428 | 10.845 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-11-03 | 17:05 |  | 22 | 61 | 62.5 | 263 | 5.29 | NA |  | #VALUE! | 0.20103 | #VALUE! | #VALUE! | 12.0741 | 13.0387 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on DQ10: Alison Gusses: Mass balance closure errors were high for the 90% recovery run indicating that the system may not have been at steady-state - all water quality parameters for this run were verified by the consultant.

## 7450. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Hydranautics Corp. | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.16692 | [45 empty] | Recovery during sample collection (decimal) | 0.70168 | [10 empty] | Recovery during sample collection (decimal) | 0.8799 | [7 empty] | Recovery during sample collection (decimal) | 0.52147 | [7 empty] | Recovery during sample collection (decimal) | 0.29962 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1999-02-18 | 1999-03-01 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 6.6837 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.04 | [7 empty] | Feed flow rate during sample collection (mL/min) | 8.64 | [7 empty] | Feed flow rate during sample collection (mL/min) | 15.1583 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 1000 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 11:00 | 10:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [6 empty] | SDS-THM4F, ug/L | 134.3 | 134.3 | 134.3 | 134.3 | SDS-THM4F, ug/L | 134.3 | 134.3 | 134.3 | 134.3 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | -48 | 168 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 41.05 | 56.1 | 39.1 | 34.1 | SDS-THM4p, ug/L | 41.05 | 56.1 | 39.1 | 34.1 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.75 | 7.74 | 7.745 | 0.12912 | 1999-02-18 | 8:30 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-20 | 11:00 | 0 | 24 | 50 | 51 | 263 | 5.52 | 1.94 |  | 7.46 | 0.20103 | 0.73995 | 34.2547 | 12.5991 | 12.8245 | 307.6779 | 255.4067 | 306.5808 | 0.51723 | 49.9828 | 0.25658 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 65.4 | 65.4 | 65.4 | 65.4 | SDS-HAA5F, ug/L | 65.4 | 65.4 | 65.4 | 65.4 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 23 | 23 | 0 | 1999-02-18 | 10:30 | 2 | 22.8 | 47 | 48 | 272 | 5.42 | 4.38 | 9.8 | 0.20791 | 0.55306 | 26.7551 | 12.3709 | 13.0469 | 0 | 0 | 0 | 0 | 47.5 | 0.27467 | 1999-02-20 | 12:00 | 1 | 24 | 50 | 50 | 272 | 5.5 | 6.2 |  | 11.7 | 0.20791 | 0.47009 | 22.2479 | 12.5535 | 12.7781 | 292.3311 | 242.6995 | 291.3275 | 0.4913 | 49.5087 | 0.2581 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 9.65 | 15.2 | 9 | 7.2 | SDS-HAA5p, ug/L | 9.65 | 15.2 | 9 | 7.2 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 264 | 316 | 290 | 17.931 | 1999-02-18 | 11:00 | 2.5 | 23 | 47 | 48 | 272 | 5.55 | 3.03 | 8.58 | 0.20791 | 0.64685 | 30.7016 | 12.6676 | 13.2811 | 0 | 0 | 0 | 0 | 47.5 | 0.2796 | 1999-02-20 | 12:30 | 1.5 | 24 | 50 | 50 | 272 | 5.55 | 1.83 |  | 7.38 | 0.20791 | 0.75203 | 35.8564 | 12.6676 | 12.8942 | 308.3799 | 256.0153 | 307.3114 | 0.5183 | 49.4817 | 0.26059 | [27 empty] | Sampling date | MM/DD/YY | 1999-02-21 | 1999-02-22 | --- | --- | 1999-02-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-23 | 1999-02-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-24 | 1999-02-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-25 | 1999-02-25 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 390 | 390 | 390 | 390 | SDS-TOXF, ug Cl- /L | 390 | 390 | 390 | 390 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 269 | 269 | 269 | 0 | 1999-02-18 | 11:45 | 3.25 | 23.1 | 49 | 50 | 272 | 6.07 | 2.21 | 8.28 | 0.20791 | 0.73309 | 31.8502 | 13.8545 | 14.4826 | 0 | 0 | 0 | 0 | 49.5 | 0.29258 | 1999-02-20 | 13:00 | 2 | 24 | 50 | 50 | 272 | 5.6 | 1.32 |  | 6.92 | 0.20791 | 0.80925 | 38.3064 | 12.7817 | 13.0104 | 311.861 | 258.8971 | 310.7705 | 0.52419 | 49.4758 | 0.26297 | 8.04 | 7.83 | 7.8 | 249 | 265 | 281 | 353.8485 | -25.9247 | 7.4349 | 352.7692 | 29.4156 | 0.028 | 0.152 | 0.292 | 0.74097 | -153.7567 | 82.9268 | 0.73363 | 96.1834 | [8 empty] | Sampling time | hh:mm | 13:30 | 10:30 | --- | --- | 13:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:00 | 20:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:30 | 14:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 84 | 125 | 76 | 66 | SDS-TOXp, ug Cl- /L | 84 | 125 | 76 | 66 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 288 | 332 | 310 | 14.1935 | 1999-02-18 | 12:15 | 3.75 | 23.1 | 49 | 50 | 272 | 6.2 | 2 | 8.2 | 0.20791 | 0.7561 | 32.1707 | 14.1512 | 14.7927 | 0 | 0 | 0 | 0 | 49.5 | 0.29884 | 1999-02-20 | 14:00 | 3 | 24 | 50 | 50 | 272 | 5.47 | 2.53 |  | 8 | 0.20791 | 0.68375 | 33 | 12.485 | 12.7084 | 304.3246 | 252.6615 | 303.2857 | 0.51144 | 49.4886 | 0.25679 | 7.79 | 7.86 | 7.85 | 248 | 265 | 281 | 314.4032 | -11.8872 | 7.8067 | 313.7355 | 20.9525 | 0.031 | 0.154 | 0.345 | 0.45155 | -30.885 | 81.0976 | 0.44732 | 93.0699 | [8 empty] | Operation time | hh.hh | 26.5 | 47.5 | --- | --- | 26.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 81 | 81 | --- | --- | --- | --- | --- | Operation time | hh.hh | 99.5 | 99.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 123 | 123 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 7.39 | 7.39 | 7.39 | 7.39 | SDS-CDF, mg/L | 7.39 | 7.39 | 7.39 | 7.39 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 250 | 276 | 263 | 9.8859 | 1999-02-18 | 13:15 | 4.75 | 23.1 | 50 | 51 | 272 | 6.33 | 2.68 | 9.01 | 0.20791 | 0.70255 | 29.1887 | 14.4479 | 15.1029 | 0 | 0 | 0 | 0 | 50.5 | 0.29907 | 1999-02-20 | 15:00 | 4 | 24 | 50 | 50 | 272 | 5.49 | 2.4 |  | 7.89 | 0.20791 | 0.69582 | 33.474 | 12.5306 | 12.7548 | 305.0341 | 253.2474 | 303.9889 | 0.51264 | 49.4874 | 0.25774 | 8.08 | 7.97 | 7.94 | 253 | 266 | 298 | 305.6 | -2.5503 | 5.948 | 305.0692 | 17.068 | 0.0314 | 0.158 | 0.361 | 0.46732 | -29.4522 | 80.8537 | 0.46292 | 93.217 | [8 empty] | pH | --- | 7.78 | 7.74 | 7.76 | 0.51546 | 7.85 | --- | --- | --- | --- | --- | pH | --- | 7.82 | 7.93 | --- | --- | --- | --- | --- | pH | --- | 7.88 | 8.11 | --- | --- | --- | --- | --- | pH | --- | 7.72 | 8.08 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.47 | 4.5 | 3.88 | 3.78 | SDS-CDp, mg/L | 4.47 | 4.5 | 3.88 | 3.78 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 53.9325 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.502 | 0.138 | 0.32 | 113.75 | 1999-02-18 | 14:00 | 5.5 | 23.2 | 49 | 50 | 272 | 6.27 | 2.08 | 8.35 | 0.20791 | 0.7509 | 31.5749 | 14.3109 | 14.9156 | 0 | 0 | 0 | 0 | 49.5 | 0.30132 | 1999-02-20 | 16:30 | 5.5 | 24 | 50 | 50 | 272 | 5.51 | 2.36 |  | 7.87 | 0.20791 | 0.70013 | 33.5616 | 12.5763 | 12.8013 | 305.29 | 253.4566 | 304.24 | 0.51308 | 49.4869 | 0.25868 | 8.2 | 8.03 | 8 | 250 | 265 | 286 | 313.3602 | -9.5665 | 7.0632 | 312.7184 | 20.0559 | 0.032 | 0.159 | 0.378 | 0.47219 | -24.917 | 80.4878 | 0.46773 | 93.1584 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 4.65 | 4.65 | 4.65 | 4.65 | TOCF, mg/L | 4.65 | 4.65 | 4.65 | 4.65 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 63.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.45 | 0.26 | 0.355 | 53.5211 | 1999-02-18 | 15:00 | 6.5 | 23.2 | 49 | 50 | 272 | 6.29 | 4.25 | 10.54 | 0.20791 | 0.59677 | 24.8065 | 14.3566 | 14.9632 | 0 | 0 | 0 | 0 | 49.5 | 0.30229 | 1999-02-20 | 17:30 | 6.5 | 24 | 49 | 50 | 272 | 5.47 | 2.32 |  | 7.79 | 0.20791 | 0.70218 | 33.9166 | 12.485 | 12.7084 | 305.4058 | 253.5592 | 304.3631 | 0.51325 | 48.9867 | 0.25942 | 7.91 | 7.85 | 7.83 | 250 | 264 | 299 | 313.7974 | -4.949 | 7.0632 | 313.1559 | 20.1676 | 0.032 | 0.158 | 0.386 | 0.47522 | -23.1151 | 80.4878 | 0.47077 | 93.2026 | [8 empty] | Alkalinity | mg/L as CaCO3 | 170 | 242 | 206 | 34.9515 | 325 | 487.577 | -50.0237 | 28.9655 | 485.1495 | 57.5389 | Alkalinity | mg/L as CaCO3 | 276 | 344 | 392.5655 | -14.1179 | 4.8276 | 391.6153 | 29.5227 | Alkalinity | mg/L as CaCO3 | 164 | 226 | 427.3059 | -89.0734 | 43.4483 | 425.1252 | 61.4231 | Alkalinity | mg/L as CaCO3 | 152 | 222 | 349.035 | -57.223 | 47.5862 | 347.39 | 56.2451 | TOCp, mg/L | 1.6 | 2.3 | 1 | 0.9 | TOCp, mg/L | 1.6 | 2.3 | 1 | 0.9 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 51.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 4.2 | 5.1 | 4.65 | 19.3548 | 1999-02-18 | 15:15 | 6.75 | 23.3 | 49 | 50 | 272 | 6.29 | 3.07 | 9.36 | 0.20791 | 0.67201 | 28.0598 | 14.3566 | 14.919 | 0 | 0 | 0 | 0 | 49.5 | 0.30139 | 1999-02-20 | 18:30 | 7.5 | 24 | 49 | 50 | 272 | 5.56 | 2.3 |  | 7.86 | 0.20791 | 0.70738 | 33.6056 | 12.6904 | 12.9175 | 305.7237 | 253.8085 | 304.6625 | 0.51385 | 48.9862 | 0.2637 | 7.97 | 7.87 | 7.87 | 250 | 265 | 284 | 314.9304 | -10.891 | 7.0632 | 314.2668 | 20.4498 | 0.032 | 0.158 | 0.391 | 0.4831 | -23.5539 | 80.4878 | 0.47849 | 93.3122 | [8 empty] | Total dissolved solids | mg/L | 248 | 252 | 250 | 1.6 | 272 | 313.69 | -15.3272 | 7.0632 | 313.141 | 20.1638 | Total dissolved solids | mg/L | 261 | 301 | 327.6089 | -8.8402 | 2.974 | 327.0659 | 20.1996 | Total dissolved solids | mg/L | 239 | 276 | 301.6919 | -9.3087 | 11.1524 | 301.1727 | 20.6435 | Total dissolved solids | mg/L | 230 | 268 | 285.6838 | -6.5984 | 14.4981 | 285.2189 | 19.3602 | UV254 F, cm-1 | 0.164 | 0.164 | 0.164 | 0.164 | UV254 F, cm-1 | 0.164 | 0.164 | 0.164 | 0.164 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 51.0754 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.17 | 0.158 | 0.164 | 7.3171 | 1999-02-18 | 15:45 | 7.25 | 23.3 | 49 | 50 | 272 | 6.25 | 2.28 | 8.53 | 0.20791 | 0.73271 | 30.8875 | 14.2653 | 14.8241 | 0 | 0 | 0 | 0 | 49.5 | 0.29948 | 1999-02-21 | 13:30 | 26.5 | 24 | 49 | 50 | 272 | 4.73 | 2.05 |  | 6.78 | 0.20791 | 0.69764 | 39.118 | 10.796 | 10.9891 | 305.0444 | 253.3782 | 304.1459 | 0.51217 | 48.9878 | 0.22432 | 7.873 | 7.89 | 7.9 | 254 | 264 | 290 | 303.6098 | -4.693 | 5.5762 | 303.1784 | 16.2209 | 0.032 | 0.159 | 0.394 | 0.46857 | -18.9253 | 80.4878 | 0.46477 | 93.1149 | [8 empty] | Total hardness | mg/L as CaCO3 | 226 | 262 | 244 | 14.7541 | 346 | 465.2391 | -34.4622 | 21.2903 | 463.3318 | 47.338 | Total hardness | mg/L as CaCO3 | 314 | 366 | 280.6956 | 23.3072 | -1.2903 | 280.9671 | -11.7569 | Total hardness | mg/L as CaCO3 | 212 | 290 | 416.7935 | -43.7219 | 31.6129 | 415.0973 | 48.9276 | Total hardness | mg/L as CaCO3 | 216 | 286 | 350.2123 | -22.4518 | 30.3226 | 349.0918 | 38.1252 | UV254 p, cm-1 | 0.0275 | 0.038 | 0.024 | 0.016 | UV254 p, cm-1 | 0.0275 | 0.038 | 0.024 | 0.016 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.0476 | 3.098 | 3.5728 | 26.5778 | 1999-02-18 | 16:30 | 8 | 23 | 49 | 50 | 272 | 6.28 | 3.35 | 9.63 | 0.20791 | 0.65213 | 27.2451 | 14.3338 | 15.028 | 0 | 0 | 0 | 0 | 49.5 | 0.3036 | 1999-02-21 | 14:30 | 27.5 | 23.7 | 49 | 50 | 272 | 4.73 | 2.11 |  | 6.84 | 0.20791 | 0.69152 | 38.7661 | 10.796 | 11.087 | 304.6863 | 253.0808 | 303.7889 | 0.51157 | 48.9884 | 0.22632 | 7.82 | 7.9 | 7.78 | 253 | 265 | 283 | 304.8673 | -7.727 | 5.948 | 304.4163 | 16.8901 | 0.028 | 0.159 | 0.406 | 0.46887 | -15.4857 | 82.9268 | 0.46504 | 93.979 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 180 | 216 | 198 | 18.1818 | 283 | 415.887 | -46.9565 | 24.7148 | 414.0086 | 52.1749 | Calcium hardness | mg/L as CaCO3 | 248 | 316 | 372.8916 | -18.0037 | 5.7034 | 371.8735 | 33.3107 | Calcium hardness | mg/L as CaCO3 | 158 | 272 | 377.4216 | -38.7579 | 39.924 | 375.6043 | 57.9345 | Calcium hardness | mg/L as CaCO3 | 152 | 258 | 310.4847 | -20.3429 | 42.2053 | 309.1615 | 50.8348 | BromideF, ug/L | 85 | 85 | 85 | 85 | BromideF, ug/L | 85 | 85 | 85 | 85 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 85 | 85 | 85 | 0 | 1999-02-19 | 9:15 | 24.75 | 23 | 49 | 50 | 272 | 6.11 | 2.48 | 8.59 | 0.20791 | 0.71129 | 30.6647 | 13.9457 | 14.6211 | 0 | 0 | 0 | 0 | 49.5 | 0.29538 | 1999-02-21 | 15:30 | 28.5 | 23.7 | 49 | 50 | 272 | 4.71 | 2.11 |  | 6.82 | 0.20791 | 0.69062 | 38.8827 | 10.7503 | 11.0402 | 304.6309 | 253.038 | 303.7375 | 0.51146 | 48.9885 | 0.22536 | 7.92 | 7.87 | 8.01 | 255 | 265 | 285 | 300.2512 | -5.3513 | 5.2045 | 299.8594 | 14.9601 | 0.025 | 0.159 | 0.407 | 0.47428 | -16.5306 | 84.7561 | 0.47039 | 94.6853 | [8 empty] | Turbidity | ntu | 0.077 | 0.075 | 0.076 | 2.6316 | 0.26 | 0.89391 | -243.8132 | 76.25 | 0.88686 | 91.4305 | Turbidity | ntu | 0.117 | 0.344 | 1.8072 | -425.3488 | 63.4375 | 1.7934 | 93.4762 | Turbidity | ntu | 0.069 | 0.188 | 0.59352 | -215.7032 | 78.4375 | 0.58918 | 88.2888 | Turbidity | ntu | 0.063 | 0.153 | 0.42994 | -181.0079 | 80.3125 | 0.42688 | 85.2417 | Bromidep, ug/L | 82.5 | 84 | 81 | 77 | Bromidep, ug/L | 82.5 | 84 | 81 | 77 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 9 | 8 | 8.5 | 11.7647 | 1999-02-19 | 10:30 | 26 | 23.1 | 49 | 50 | 263 | 5.85 | 1.3 | 7.15 | 0.20103 | 0.81818 | 35.7832 | 13.3523 | 13.9577 | 0 | 0 | 0 | 0 | 49.5 | 0.28197 | 1999-02-21 | 16:30 | 29.5 | 23.6 | 49 | 50 | 272 | 4.73 | 2.08 |  | 6.81 | 0.20791 | 0.69457 | 38.9413 | 10.796 | 11.1199 | 304.8644 | 253.2287 | 303.9665 | 0.51187 | 48.9881 | 0.22699 | 7.94 | 7.89 | 8.01 | 256 | 264 | 288 | 298.5625 | -3.6675 | 4.8327 | 298.1924 | 14.1494 | 0.031 | 0.158 | 0.41 | 0.46645 | -13.7676 | 81.0976 | 0.46266 | 93.2996 | [8 empty] | Ammonia | mg NH3-N / L | 0.44 | 0.42 | 0.43 | 4.6512 | NA | 0.17859 | #VALUE! | -21.1268 | 0.18076 | -137.8854 | Ammonia | mg NH3-N / L | 0.36 | NA | 0.31837 | #VALUE! | -1.4085 | 0.31871 | -12.9558 | Ammonia | mg NH3-N / L | 0.2 | NA | 0.52391 | #VALUE! | 43.662 | 0.52123 | 61.6289 | Ammonia | mg NH3-N / L | 0.11 | NA | 0.45981 | #VALUE! | 69.0141 | 0.45689 | 75.9241 | AlkF, mg/L CaCO3 | 290 | 290 | 290 | 290 | AlkF, mg/L CaCO3 | 290 | 290 | 290 | 290
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1 | 1.22 | 1.11 | 19.8198 | 1999-02-19 | 11:00 | 26.5 | 23.1 | 49 | 50 | 272 | 6.27 | 4.87 | 11.14 | 0.20791 | 0.56284 | 23.4165 | 14.3109 | 14.9597 | 0 | 0 | 0 | 0 | 49.5 | 0.30222 | 1999-02-21 | 18:00 | 31 | 23.6 | 49 | 50 | 272 | 4.8 | 2.28 |  | 7.08 | 0.20791 | 0.67797 | 37.4181 | 10.9557 | 11.2844 | 303.9046 | 252.4203 | 302.9961 | 0.5103 | 48.9897 | 0.23034 | 7.88 | 7.89 | 8 | 255 | 266 | 283 | 298.4737 | -5.4677 | 5.2045 | 298.0901 | 14.4554 | 0.028 | 0.159 | 0.401 | 0.45032 | -12.2982 | 82.9268 | 0.44659 | 93.7303 | [8 empty] | Total organic carbon | mg/L | 1.2 | 2 | 1.6 | 50 | 10.2 | 11.8239 | -15.9209 | 65.5914 | 11.7358 | 86.3665 | Total organic carbon | mg/L | 2.3 | 21.2 | 21.8664 | -3.1432 | 50.5376 | 21.7068 | 89.4043 | Total organic carbon | mg/L | 1 | 7.8 | 8.6275 | -10.6091 | 78.4946 | 8.5643 | 88.3237 | Total organic carbon | mg/L | 0.9 | 5.7 | 6.2542 | -9.723 | 80.6452 | 6.2095 | 85.5061 | Alkp, mg/L CaCO3 | 206 | 276 | 164 | 152 | Alkp, mg/L CaCO3 | 206 | 276 | 164 | 152
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 8 | 6.78 | 7.39 | 16.5088 | 1999-02-19 | 11:30 | 27 | 23.1 | 49 | 50 | 272 | 6.2 | 3.86 | 10.06 | 0.20791 | 0.6163 | 26.0378 | 14.1512 | 14.7927 | 0 | 0 | 0 | 0 | 49.5 | 0.29884 | 1999-02-21 | 19:00 | 32 | 23.5 | 49 | 50 | 272 | 4.8 | 2.08 |  | 6.88 | 0.20791 | 0.69767 | 38.5349 | 10.9557 | 11.3178 | 305.0553 | 253.376 | 304.1433 | 0.51223 | 48.9878 | 0.23103 | 7.89 | 7.87 | 8.03 | 254 | 265 | 281 | 303.6154 | -8.0482 | 5.5762 | 303.1776 | 16.2207 | 0.026 | 0.159 | 0.398 | 0.48246 | -21.2215 | 84.1463 | 0.47843 | 94.5656 | [8 empty] | UV254 | cm-1 | 0.029 | 0.026 | 0.0275 | 10.9091 | 0.4 | 0.48506 | -21.2657 | 83.2317 | 0.48112 | 94.2841 | UV254 | cm-1 | 0.038 | 0.8 | 1.0871 | -35.8862 | 76.8293 | 1.0785 | 96.4767 | UV254 | cm-1 | 0.024 | 0.274 | 0.31656 | -15.5336 | 85.3659 | 0.31414 | 92.3601 | UV254 | cm-1 | 0.016 | 0.208 | 0.22731 | -9.2851 | 90.2439 | 0.22555 | 92.9062 | T-HdF, mg/L CaCO3 | 310 | 310 | 310 | 310 | T-HdF, mg/L CaCO3 | 310 | 310 | 310 | 310
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | 1999-02-19 | 13:00 | 28.5 | 23.2 | 49 | 50 | 272 | 6.2 | 3 | 9.2 | 0.20791 | 0.67391 | 28.5652 | 14.1512 | 14.7491 | 0 | 0 | 0 | 0 | 49.5 | 0.29796 | 1999-02-21 | 20:00 | 33 | 23.5 | 49 | 50 | 272 | 4.73 | 2.08 |  | 6.81 | 0.20791 | 0.69457 | 38.9413 | 10.796 | 11.1528 | 304.8644 | 253.2287 | 303.9665 | 0.51187 | 48.9881 | 0.22766 | 7.83 | 7.89 | 7.94 | 254 | 266 | 280 | 303.1106 | -8.2538 | 5.5762 | 302.6836 | 16.084 | 0.026 | 0.159 | 0.391 | 0.47782 | -22.2039 | 84.1463 | 0.47389 | 94.5135 | [8 empty] | SUVA | L/(mg*m) | 2.4167 | 1.3 | 1.8583 | 60.0897 | 3.9216 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.6522 | 3.7736 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.4 | 3.5128 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.7778 | 3.6491 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 244 | 314 | 212 | 216 | T-Hdp, mg/L CaCO3 | 244 | 314 | 212 | 216
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.02 | 8 | 8.01 | 0.24969 | 1999-02-19 | 14:00 | 29.5 | 23.2 | 49 | 51 | 272 | 6.2 | 2.58 | 8.78 | 0.20791 | 0.70615 | 29.9795 | 14.1512 | 14.7491 | 0 | 0 | 0 | 0 | 50 | 0.29498 | 1999-02-21 | 21:00 | 34 | 23.5 | 49 | 50 | 272 | 4.85 | 2.05 |  | 6.9 | 0.20791 | 0.7029 | 38.4203 | 11.0699 | 11.4357 | 305.3682 | 253.6279 | 304.4456 | 0.51279 | 48.9872 | 0.23344 | 7.85 | 7.91 | 7.97 | 255 | 265 | 281 | 302.122 | -7.5167 | 5.2045 | 301.7018 | 15.4795 | 0.025 | 0.158 | 0.387 | 0.49285 | -27.3524 | 84.7561 | 0.48868 | 94.8842 | [8 empty] | Bromide | mg/L | 83 | 82 | 82.5 | 1.2121 | --- | 90.8803 | --- | 2.9412 | 90.808 | 9.149 | Bromide | mg/L | 84 | --- | 92.3261 | --- | 1.1765 | 92.2582 | 8.9512 | Bromide | mg/L | 81 | --- | 89.3589 | --- | 4.7059 | 89.2897 | 9.284 | Bromide | mg/L | 77 | --- | 88.4223 | --- | 9.4118 | 88.327 | 12.8239 | Ca-HdF, mg/L CaCO3 | 263 | 263 | 263 | 263 | Ca-HdF, mg/L CaCO3 | 263 | 263 | 263 | 263
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | 1999-02-19 | 15:00 | 30.5 | 23.2 | 49 | 50 | 272 | 6.05 | 2.47 | 8.52 | 0.20791 | 0.71009 | 30.9249 | 13.8088 | 14.3922 | 0 | 0 | 0 | 0 | 49.5 | 0.29075 | 1999-02-22 | 9:00 | 46 | 23.5 | 49 | 50 | 272 | 4.7 | 1.95 |  | 6.65 | 0.20791 | 0.70677 | 39.9023 | 10.7275 | 11.082 | 305.5762 | 253.8248 | 304.682 | 0.51304 | 48.987 | 0.22622 | 7.87 | 7.9 | 7.95 | 252 | 266 | 288 | 309.9744 | -7.63 | 6.3197 | 309.4735 | 18.5714 | 0.025 | 0.158 | 0.408 | 0.49903 | -22.3102 | 84.7561 | 0.49493 | 94.9488 | [8 empty] | SDS-Cl2 dose | mg/L | 5.5 | 5.5 | 5.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 198 | 248 | 158 | 152 | Ca-Hdp, mg/L CaCO3 | 198 | 248 | 158 | 152
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 380 | 400 | 390 | 5.1282 | 1999-02-19 | 16:00 | 31.5 | 23.2 | 49 | 50 | 272 | 6.27 | 3.4 | 9.67 | 0.20791 | 0.6484 | 27.1282 | 14.3109 | 14.9156 | 0 | 0 | 0 | 0 | 49.5 | 0.30132 | 1999-02-22 | 10:30 | 47.5 | 23.5 | 49 | 50 | 272 | 4.7 | 1.96 |  | 6.66 | 0.20791 | 0.70571 | 39.8408 | 10.7275 | 11.082 | 305.5138 | 253.773 | 304.6198 | 0.51294 | 48.9871 | 0.22622 | 7.89 | 7.91 | 7.96 | 254 | 266 | 280 | 304.9694 | -8.9176 | 5.5762 | 304.529 | 16.5925 | 0.026 | 0.158 | 0.424 | 0.49492 | -16.726 | 84.1463 | 0.49087 | 94.7033 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.01 | 1.05 | 1.03 | 3.8835 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.12 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.22 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 95 | 100 | 97.5 | 5.1282 | 1999-02-19 | 16:15 | 31.75 | 23.1 | 60 | 61 | 272 | 7.4 | 3.6 | 11 | 0.20791 | 0.67273 | 23.7273 | 16.8901 | 17.6558 | 0 | 0 | 0 | 0 | 60.5 | 0.29183 | 1999-02-22 | 12:00 | 49 | 23.6 | 49 | 50 | 272 | 4.47 | 1.88 |  | 6.35 | 0.20791 | 0.70394 | 41.8346 | 10.2025 | 10.5086 | 305.3804 | 253.6991 | 304.5311 | 0.51257 | 48.9874 | 0.21452 | 8.08 | 8.1 | 8.03 | 243 | 266 | 285 | 330.8191 | -16.0769 | 9.6654 | 330.0975 | 26.3854 | 0.025 | 0.159 | 0.42 | 0.49449 | -17.7368 | 84.7561 | 0.49064 | 94.9046 | [8 empty] | SDS-Cl2 demand | mg/L | 4.49 | 4.45 | 4.47 | 0.89485 | --- | 14.2582 | --- | 39.5129 | 14.1738 | 68.4629 | SDS-Cl2 demand | mg/L | 4.5 | --- | 28.5625 | --- | 39.1069 | 28.3663 | 84.1361 | SDS-Cl2 demand | mg/L | 3.88 | --- | 11.215 | --- | 47.4966 | 11.1542 | 65.2149 | SDS-Cl2 demand | mg/L | 3.78 | --- | 8.9343 | --- | 48.8498 | 8.8913 | 57.4865 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 30 | 29 | 29.5 | 3.3898 | 1999-02-19 | 16:30 | 32 | 23.1 | 40 | 41 | 272 | 5.2 | 2.43 | 7.63 | 0.20791 | 0.68152 | 34.6488 | 11.8687 | 12.4068 | 0 | 0 | 0 | 0 | 40.5 | 0.30634 | 1999-02-22 | 13:30 | 50.5 | 23.6 | 49 | 50 | 272 | 4.67 | 1.93 |  | 6.6 | 0.20791 | 0.70758 | 40.2121 | 10.659 | 10.9788 | 305.6199 | 253.8659 | 304.7313 | 0.5131 | 48.9869 | 0.22412 | 7.7 | 7.79 | 7.81 | 256 | 265 | 285 | 300.456 | -5.4231 | 4.8327 | 300.0743 | 14.6878 | 0.026 | 0.159 | 0.422 | 0.49792 | -17.9898 | 84.1463 | 0.49387 | 94.7354 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 66.8097 | 79.6675 | 65.4412 | 62.1756 | Qp/QT (THM4), % | 105.4155 | 125.7033 | 103.2563 | 98.1038
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 8 | 6.6 | 7.3 | 19.1781 | 1999-02-19 | 17:00 | 32.5 | 23.1 | 50 | 51 | 272 | 6.4 | 2.87 | 9.27 | 0.20791 | 0.6904 | 28.342 | 14.6077 | 15.2699 | 0 | 0 | 0 | 0 | 50.5 | 0.30237 | 1999-02-22 | 14:30 | 51.5 | 23.6 | 49 | 50 | 272 | 4.6 | 1.88 |  | 6.48 | 0.20791 | 0.70988 | 40.9753 | 10.4993 | 10.8142 | 305.7461 | 253.982 | 304.8707 | 0.51326 | 48.9867 | 0.22076 | 7.7 | 7.89 | 7.87 | 260 | 266 | 289 | 291.0213 | -0.6994 | 3.3457 | 290.759 | 10.5789 | 0.028 | 0.159 | 0.429 | 0.49677 | -15.7963 | 82.9268 | 0.4928 | 94.3182 | [8 empty] | SDS-Chlorination pH | --- | 8.2 | 8.2 | 8.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | 36
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-02-20 | 11:00 | 50.5 | 23.1 | 50 | 51 | 263 | 5.52 | 1.94 | 7.46 | 0.20103 | 0.73995 | 34.2547 | 12.5991 | 13.1703 | 0 | 0 | 0 | 0 | 50.5 | 0.2608 | 1999-02-22 | 16:00 | 53 | 23.9 | 49 | 50 | 272 | 4.67 | 1.81 |  | 6.48 | 0.20791 | 0.72068 | 40.9753 | 10.659 | 10.8819 | 306.3923 | 254.5075 | 305.5015 | 0.51439 | 48.9856 | 0.22214 | 7.75 | 7.91 | 7.96 | 261 | 265 | 295 | 289.6409 | 1.8166 | 2.974 | 289.395 | 9.8119 | 0.026 | 0.159 | 0.43 | 0.52006 | -20.9431 | 84.1463 | 0.51581 | 94.9594 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 28.1536 | 25.4069 | 28.4912 | 29.2138 | SDS-HAA5b, ug/L | NA | NA | NA | 8.3036
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 133 | 135.6 | 134.3 | 1.936 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-22 | 17:00 | 54 | 23.9 | 49 | 50 | 272 | 4.72 | 1.89 |  | 6.61 | 0.20791 | 0.71407 | 40.1498 | 10.7731 | 10.9984 | 306.0087 | 254.1808 | 305.1094 | 0.51378 | 48.9862 | 0.22452 | 7.81 | 7.92 | 7.98 | 260 | 266 | 292 | 291.4762 | 0.17939 | 3.3457 | 291.2031 | 10.7152 | 0.026 | 0.159 | 0.419 | 0.50863 | -21.3926 | 84.1463 | 0.50445 | 94.8458 | [8 empty] | SDS-TOX | mg Cl- /L | 82 | 86 | 84 | 4.7619 | --- | 1109.7449 | --- | 78.4615 | 1100.9019 | 92.3699 | SDS-TOX | mg Cl- /L | 125 | --- | 2331.4184 | --- | 67.9487 | 2313.4318 | 94.5968 | SDS-TOX | mg Cl- /L | 76 | --- | 732.175 | --- | 80.5128 | 726.7405 | 89.5423 | SDS-TOX | mg Cl- /L | 66 | --- | 528.604 | --- | 83.0769 | 524.7418 | 87.4224 | SDS-TOXb, ug Cl- /L | 185.5625 | 178.8811 | 184.5147 | 188.5509 | SDS-TOXb, ug Cl- /L | NA | NA | NA | 72.1437
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 2 | BMRL | 2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 9:00 | 70 | 23.4 | 49 | 50 | 272 | 4.4 | 1.79 |  | 6.19 | 0.20791 | 0.71082 | 42.9418 | 10.0428 | 10.4054 | 305.7759 | 254.0389 | 304.939 | 0.51319 | 48.9868 | 0.21241 | 7.45 | 7.85 | 7.91 | 248 | 266 | 290 | 320.6201 | -10.5587 | 7.8067 | 320.0327 | 22.5079 | 0.028 | 0.159 | 0.419 | 0.4983 | -18.9264 | 82.9268 | 0.4945 | 94.3377 | [8 empty] | SDS-CHCl3 | mg/L | 10 | 11 | 10.5 | 9.5238 | --- | 302.1334 | --- | 89.2308 | 299.6192 | 96.4956 | SDS-CHCl3 | mg/L | 20 | --- | 665.2733 | --- | 79.4872 | 660.0131 | 96.9698 | SDS-CHCl3 | mg/L | 9.1 | --- | 193.8321 | --- | 90.6667 | 192.3021 | 95.2679 | SDS-CHCl3 | mg/L | 7.2 | --- | 136.1294 | --- | 92.6154 | 135.053 | 94.6688 | SDS-CDb, mg/L | 5.4392 | 5.0876 | 5.093 | 5.1455 | SDS-CDb, mg/L | NA | NA | NA | 3.8485
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | 28 | 28 | 28 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 10:00 | 71 | 23.4 | 49 | 50 | 272 | 4.4 | 1.78 |  | 6.18 | 0.20791 | 0.71197 | 43.0129 | 10.0428 | 10.4054 | 305.8436 | 254.0951 | 305.0065 | 0.5133 | 48.9867 | 0.21241 | 7.91 | 7.85 | 7.91 | 247 | 264 | 288 | 323.382 | -12.2854 | 8.1784 | 322.7642 | 23.4736 | 0.028 | 0.158 | 0.425 | 0.50018 | -17.6894 | 82.9268 | 0.49636 | 94.3589 | [8 empty] | SDS-BDCM | mg/L | 13 | 14 | 13.5 | 7.4074 | --- | 67.1337 | --- | 54.2373 | 66.6713 | 79.7514 | SDS-BDCM | mg/L | 19 | --- | 106.4241 | --- | 35.5932 | 105.7114 | 82.0265 | SDS-BDCM | mg/L | 13 | --- | 47.4805 | --- | 55.9322 | 47.195 | 72.4547 | SDS-BDCM | mg/L | 11 | --- | 37.4141 | --- | 62.7119 | 37.1936 | 70.425 | TOCb, mg/L | 2.6123 | 2.7778 | 2.2614 | 2.3184 | TOCb, mg/L | NA | NA | NA | 0.97111
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 34 | 36 | 35 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 11:00 | 72 | 23.4 | 49 | 50 | 272 | 4.4 | 1.76 |  | 6.16 | 0.20791 | 0.71429 | 43.1558 | 10.0428 | 10.4054 | 305.9796 | 254.2081 | 305.1422 | 0.51353 | 48.9865 | 0.21241 | 8.01 | 7.91 | 8.04 | 254 | 265 | 287 | 306.5 | -6.7944 | 5.5762 | 306.0754 | 17.0139 | 0.029 | 0.159 | 0.427 | 0.5015 | -17.4473 | 82.3171 | 0.49768 | 94.1729 | [8 empty] | SDS-DBCM | mg/L | 14 | 14 | 14 | 0 | --- | -8.4591 | --- | -91.7808 | -8.2655 | 269.3787 | SDS-DBCM | mg/L | 15 | --- | -49.111 | --- | -105.4795 | -48.5884 | 130.8716 | SDS-DBCM | mg/L | 14 | --- | -0.0011868 | --- | -91.7808 | 0.11477 | -12097.9626 | SDS-DBCM | mg/L | 13 | --- | 4.8616 | --- | -78.0822 | 4.9295 | -163.7162 | UV254 b, cm-1 | 0.072805 | 0.063619 | 0.072382 | 0.07198 | UV254 b, cm-1 | NA | NA | NA | 0.018806
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 12:00 | 73 | 22.6 | 49 | 50 | 272 | 4.44 | 1.77 |  | 6.21 | 0.20791 | 0.71498 | 42.8003 | 10.1341 | 10.7512 | 306.0255 | 254.2398 | 305.1802 | 0.51363 | 48.9864 | 0.21947 | 8.02 | 7.99 | 8.06 | 255 | 266 | 288 | 304.1186 | -5.5968 | 5.2045 | 303.7177 | 16.0405 | 0.028 | 0.159 | 0.425 | 0.50515 | -18.8594 | 82.9268 | 0.50126 | 94.4141 | [8 empty] | SDS-CHBr3 | mg/L | 3.3 | 2.8 | 3.05 | 16.3934 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.9 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 83.3298 | 84.2033 | 82.3824 | 80.0259 | Bromideb, ug/L | NA | NA | NA | 77.1517
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 1.5 | 1.3 | 1.4 | 14.2857 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 13:30 | 74.5 | 22.6 | 49 | 50 | 272 | 4.5 | 1.73 |  | 6.23 | 0.20791 | 0.72231 | 42.6597 | 10.271 | 10.8965 | 306.4662 | 254.5963 | 305.6081 | 0.51441 | 48.9856 | 0.22244 | 7.85 | 7.89 | 8.14 | 253 | 265 | 290 | 310.6185 | -7.1098 | 5.948 | 310.1419 | 18.4244 | 0.028 | 0.158 | 0.432 | 0.51776 | -19.8512 | 82.9268 | 0.51371 | 94.5494 | [8 empty] | SDS-THM4 | mg/L | 40.3 | 41.8 | 41.05 | 3.6541 | --- | 353.634 | --- | 69.4341 | 350.9392 | 88.3028 | SDS-THM4 | mg/L | 56.1 | --- | 707.2016 | --- | 58.2278 | 701.8938 | 92.0073 | SDS-THM4 | mg/L | 39.1 | --- | 238.0422 | --- | 70.8861 | 236.3946 | 83.4599 | SDS-THM4 | mg/L | 34.1 | --- | 177.1646 | --- | 74.6091 | 175.9702 | 80.6217 | Alkb, mg/L CaCO3 | 233.8799 | 278.8465 | 207.5441 | 204.1976 | Alkb, mg/L CaCO3 | NA | NA | NA | 154.6168
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 8.9 | 8.3 | 8.6 | 6.9767 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 15:00 | 76 | 23.4 | 49 | 50 | 272 | 4.62 | 1.75 |  | 6.37 | 0.20791 | 0.72527 | 41.7002 | 10.5449 | 10.9256 | 306.6575 | 254.7358 | 305.7755 | 0.51481 | 48.9852 | 0.22304 | 8.07 | 8.03 | 8.11 | 256 | 266 | 288 | 303.32 | -5.3194 | 4.8327 | 302.9181 | 15.4887 | 0.029 | 0.159 | 0.432 | 0.5204 | -20.463 | 82.3171 | 0.51623 | 94.3823 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 265.9056 | 313.1867 | 245.8676 | 251.5549 | T-Hdb, mg/L CaCO3 | NA | NA | NA | 217.7824
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 16:45 | 77.75 | 23.8 | 49 | 50 | 272 | 4.58 | 1.71 |  | 6.29 | 0.20791 | 0.72814 | 42.2432 | 10.4536 | 10.7037 | 306.8218 | 254.8788 | 305.9471 | 0.51506 | 48.9849 | 0.21851 | 8.04 | 8.01 | 8.13 | 254 | 264 | 287 | 309.1754 | -7.7266 | 5.5762 | 308.7109 | 17.7224 | 0.03 | 0.158 | 0.436 | 0.5229 | -19.9313 | 81.7073 | 0.51875 | 94.2169 | [8 empty] | SDS-DCAA* | mg/L | 3.5 | 3.4 | 3.45 | 2.8986 | --- | 85.7442 | --- | 87.6786 | 85.0348 | 95.9428 | SDS-DCAA* | mg/L | 6.7 | --- | 184.0461 | --- | 76.0714 | 182.6004 | 96.3308 | SDS-DCAA* | mg/L | 3.2 | --- | 55.0253 | --- | 88.5714 | 54.5961 | 94.1388 | SDS-DCAA* | mg/L | 2.5 | --- | 38.9086 | --- | 91.0714 | 38.6047 | 93.5241 | Ca-Hdb, mg/L CaCO3 | 219.5737 | 251.0499 | 194.2868 | 193.985 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | 154.1048
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 2.2 | BMRL | 2.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 18:00 | 79 | 23.8 | 49 | 50 | 272 | 4.48 | 0.91 |  | 5.39 | 0.20791 | 0.83117 | 49.4638 | 10.2254 | 10.47 | 313.0338 | 260.0556 | 312.1613 | 0.52542 | 48.9746 | 0.21379 | 7.93 | 7.85 | 7.87 | 259 | 266 | 292 | 318.2308 | -8.9831 | 3.7175 | 317.743 | 18.4876 | 0.032 | 0.159 | 0.493 | 0.81385 | -65.0804 | 80.4878 | 0.80741 | 96.0367 | [8 empty] | SDS-TCAA* | mg/L | 2.6 | 3.5 | 3.05 | 29.5082 | --- | 110.1498 | --- | 91.2857 | 109.2265 | 97.2076 | SDS-TCAA* | mg/L | 5.2 | --- | 253.318 | --- | 85.1429 | 251.2953 | 97.9307 | SDS-TCAA* | mg/L | 2.4 | --- | 70.5252 | --- | 93.1429 | 69.961 | 96.5695 | SDS-TCAA* | mg/L | 1.6 | --- | 49.2882 | --- | 95.4286 | 48.8901 | 96.7274
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 11 | 9.8 | 10.4 | 11.5385 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 18:30 | 79.5 | 23.8 | 49 | 50 | 272 | 4.43 | 0.71 |  | 5.14 | 0.20791 | 0.86187 | 51.9183 | 10.1112 | 10.3532 | 314.9296 | 261.6388 | 314.0617 | 0.52857 | 48.9714 | 0.21141 | 8.02 | 8.01 | 8.11 | 263 | 265 | 297 | 306.4366 | -3.1773 | 2.2305 | 306.0829 | 14.0756 | 0.033 | 0.159 | 0.535 | 0.98137 | -83.4329 | 79.878 | 0.97364 | 96.6107 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 65.5 | 65.3 | 65.4 | 0.30581 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 19:00 | 80 | 23.8 | 49 | 50 | 272 | 4.4 | 0.65 |  | 5.05 | 0.20791 | 0.87129 | 52.8614 | 10.0428 | 10.2831 | 315.5133 | 262.1287 | 314.6497 | 0.52953 | 48.9705 | 0.20999 | 8.17 | 8.06 | 8.1 | 264 | 266 | 300 | 302.8462 | -0.94872 | 1.8587 | 302.532 | 12.7365 | 0.035 | 0.16 | 0.573 | 1.0372 | -81.0176 | 78.6585 | 1.0291 | 96.5991 | [8 empty] | SDS-DBAA* | mg/L | 3.3 | 3 | 3.15 | 9.5238 | --- | -2.7162 | --- | -125 | -2.6656 | 218.1716 | SDS-DBAA* | mg/L | 3.3 | --- | -12.5196 | --- | -135.7143 | -12.3906 | 126.633 | SDS-DBAA* | mg/L | 3.4 | --- | -0.77946 | --- | -142.8571 | -0.74484 | 556.4715 | SDS-DBAA* | mg/L | 3.1 | --- | 0.67276 | --- | -121.4286 | 0.69302 | -347.3167 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 74.4 | 73.6 | 74 | 1.0811 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 20:00 | 81 | 23.8 | 49 | 50 | 272 | 4.53 | 0.53 |  | 5.06 | 0.20791 | 0.89526 | 52.7549 | 10.3395 | 10.5869 | 317.0442 | 263.3789 | 316.1504 | 0.53218 | 48.9678 | 0.2162 | 8.2 | 8.02 | 8.07 | 264 | 266 | 301 | 311.7358 | -3.5667 | 1.8587 | 311.3383 | 15.2048 | 0.037 | 0.16 | 0.619 | 1.2495 | -101.8563 | 77.439 | 1.2394 | 97.0147 | [8 empty] | SDS-BCAA* | mg/L | 4.3 | 4.2 | 4.25 | 2.3529 | --- | 18.8317 | --- | 50.5814 | 18.706 | 77.28 | SDS-BCAA* | mg/L | 5.9 | --- | 28.3805 | --- | 31.3953 | 28.1972 | 79.076 | SDS-BCAA* | mg/L | 4.3 | --- | 13.2858 | --- | 50 | 13.2114 | 67.4524 | SDS-BCAA* | mg/L | 3.6 | --- | 10.7389 | --- | 58.1395 | 10.6793 | 66.2901 | Qp/QT (HAA5), % | 20.4484 | 22.7092 | 20.2128 | 19.5876 | Qp/QT (HAA5), % | 68.8789 | 76.494 | 68.0851 | 65.9794
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 21:00 | 82 | 23.8 | 49 | 50 | 272 | 4.5 | 0.57 |  | 5.07 | 0.20791 | 0.88757 | 52.6489 | 10.271 | 10.5168 | 316.5538 | 262.9765 | 315.6674 | 0.53134 | 48.9687 | 0.21477 | 8.2 | 8.1 | 8.13 | 263 | 265 | 303 | 316.3684 | -4.412 | 2.2305 | 315.927 | 16.7529 | 0.039 | 0.158 | 0.655 | 1.1508 | -75.7011 | 76.2195 | 1.1416 | 96.5839 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 115.2318 | 116.5414 | 115.0574 | 114.6732 | SDS-THM4b, ug/L | 70.0704 | 74.4817 | 69.483 | 68.1887
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-23 | 22:30 | 83.5 | 23.8 | 49 | 50 | 272 | 4.44 | 0.48 |  | 4.92 | 0.20791 | 0.90244 | 54.2846 | 10.1341 | 10.3766 | 317.4831 | 263.7586 | 316.6061 | 0.53286 | 48.9671 | 0.21191 | 8.17 | 8.1 | 8.09 | 264 | 266 | 300 | 315.25 | -5.0833 | 1.8587 | 314.8317 | 16.1457 | 0.041 | 0.159 | 0.713 | 1.3017 | -82.5736 | 75 | 1.2915 | 96.8253 | [8 empty] | SDS-CDBAA | mg/L | 2.7 | 3 | 2.85 | 10.5263 | --- | 0.67113 | --- | -29.5455 | 0.68991 | -313.0948 | SDS-CDBAA | mg/L | 3.1 | --- | -4.3935 | --- | -40.9091 | -4.3324 | 171.5537 | SDS-CDBAA | mg/L | 3.1 | --- | 1.2192 | --- | -40.9091 | 1.2348 | -151.0487 | SDS-CDBAA | mg/L | 2.8 | --- | 1.9433 | --- | -27.2727 | 1.9505 | -43.5545 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-24 | 10:00 | 95 | 23.8 | 49 | 50 | 272 | 4.23 | 0.42 |  | 4.65 | 0.20791 | 0.90968 | 57.4946 | 9.6547 | 9.8858 | 317.9051 | 264.1442 | 317.069 | 0.53343 | 48.9666 | 0.20189 | 8.01 | 7.89 | 7.97 | 267 | 266 | 310 | 289.1429 | 6.7281 | 0.74349 | 288.9707 | 7.6031 | 0.042 | 0.159 | 0.796 | 1.3927 | -74.9641 | 74.3902 | 1.3822 | 96.9614 | [8 empty] | SDS-DCBAA | mg/L | 3.1 | 4.6 | 3.85 | 38.961 | --- | 25.8063 | --- | 62.9808 | 25.617 | 84.9709 | SDS-DCBAA | mg/L | 4.4 | --- | 54.3566 | --- | 57.6923 | 53.9494 | 91.8442 | SDS-DCBAA | mg/L | 3.7 | --- | 17.7012 | --- | 64.4231 | 17.5852 | 78.9596 | SDS-DCBAA | mg/L | 3.1 | --- | 13.5229 | --- | 70.1923 | 13.4358 | 76.9274 | SDS-TOXb, ug Cl- /L | 327.4278 | 329.8207 | 326.5319 | 326.5361 | SDS-TOXb, ug Cl- /L | 179.2305 | 187.2908 | 176.2128 | 176.2268
[44 empty] | 1999-02-24 | 11:15 | 96.25 | 23.8 | 49 | 50 | 272 | 4.42 | 4.15 |  | 8.57 | 0.20791 | 0.51575 | 30.7386 | 10.0884 | 10.3298 | 294.7203 | 244.8508 | 293.91 | 0.49464 | 49.0054 | 0.21079 | 8.09 | 8.24 | 8.03 | 253 | 266 | 289 | 286.041 | 1.0239 | 5.948 | 285.7725 | 11.468 | 0.04 | 0.161 | 0.761 | 0.29607 | 61.0949 | 75.6098 | 0.29399 | 86.394 | [8 empty] | SDS-HAA5 | mg/L | 9.4 | 9.9 | 9.65 | 5.1813 | --- | 196.53 | --- | 85.2446 | 194.9189 | 95.0492 | SDS-HAA5 | mg/L | 15.2 | --- | 433.1706 | --- | 76.7584 | 429.7633 | 96.4632 | SDS-HAA5 | mg/L | 9 | --- | 126.8607 | --- | 86.2385 | 125.8846 | 92.8506 | SDS-HAA5 | mg/L | 7.2 | --- | 90.2974 | --- | 88.9908 | 89.6036 | 91.9646 | SDS-CDb, mg/L | 6.7929 | 6.7337 | 6.6805 | 6.6829 | SDS-CDb, mg/L | 5.3787 | 5.1793 | 5.0002 | 5.0081
[44 empty] | 1999-02-24 | 11:45 | 96.75 | 23.3 | 49 | 50 | 272 | 4.58 | 4.67 |  | 9.25 | 0.20791 | 0.49514 | 28.4054 | 10.4536 | 10.8631 | 293.6115 | 243.9049 | 292.7745 | 0.49288 | 49.0071 | 0.22166 | 8.1 | 8.26 | 8.12 | 252 | 264 | 281 | 285.6724 | -1.6628 | 6.3197 | 285.3889 | 11.6994 | 0.03 | 0.158 | 0.479 | 0.29542 | 38.3262 | 81.7073 | 0.29318 | 89.7675 | [8 empty] | SDS-HAA6 | mg/L | 13.7 | 14.1 | 13.9 | 2.8777 | --- | 215.3617 | --- | 81.2162 | 213.6249 | 93.4933 | SDS-HAA6 | mg/L | 21.1 | --- | 461.5511 | --- | 71.4865 | 457.9605 | 95.3926 | SDS-HAA6 | mg/L | 13.3 | --- | 140.1466 | --- | 82.027 | 139.096 | 90.4383 | SDS-HAA6 | mg/L | 10.8 | --- | 101.0363 | --- | 85.4054 | 100.283 | 89.2305 | TOCb, mg/L | 4.0263 | 4.1163 | 3.9122 | 3.9155 | TOCb, mg/L | 2.5492 | 2.8524 | 2.1649 | 2.1758
[44 empty] | 1999-02-24 | 13:30 | 98.5 | 23.3 | 49 | 50 | 272 | 4.44 | 3.96 |  | 8.4 | 0.20791 | 0.52857 | 31.381 | 10.1341 | 10.5311 | 295.4242 | 245.4325 | 294.6082 | 0.49584 | 49.0042 | 0.2149 | 8.11 | 8.31 | 8.13 | 250 | 266 | 278 | 290.303 | -4.4256 | 7.0632 | 289.9741 | 13.7854 | 0.023 | 0.16 | 0.305 | 0.32209 | -5.6036 | 85.9756 | 0.31965 | 92.8046 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.13609 | 0.13539 | 0.1357 | 0.13501 | UV254 b, cm-1 | 0.06998 | 0.067618 | 0.068681 | 0.066351
[44 empty] | 1999-02-24 | 14:30 | 99.5 | 23.3 | 49 | 50 | 272 | 4.58 | 4.48 |  | 9.06 | 0.20791 | 0.50552 | 29.0221 | 10.4536 | 10.8631 | 294.1759 | 244.3738 | 293.3373 | 0.49383 | 49.0062 | 0.22167 | 8.34 | 8.35 | 8.15 | 247 | 265 | 276 | 291.4911 | -5.6127 | 8.1784 | 291.1165 | 15.1542 | 0.02 | 0.16 | 0.287 | 0.31121 | -8.437 | 87.8049 | 0.30876 | 93.5225 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 84.4888 | 84.7729 | 84.1915 | 83.433 | Bromideb, ug/L | 83.278 | 84.2351 | 82.2766 | 79.7216
[44 empty] | 1999-02-24 | 15:30 | 100.5 | 23.6 | 49 | 50 | 272 | 4.56 | 3.56 |  | 8.12 | 0.20791 | 0.56158 | 32.4975 | 10.408 | 10.7202 | 297.2591 | 246.9381 | 296.4155 | 0.49899 | 49.001 | 0.21877 | 8.18 | 8.5 | 8.14 | 246 | 265 | 276 | 298.4607 | -8.1379 | 8.5502 | 298.0209 | 17.4555 | 0.022 | 0.16 | 0.285 | 0.34589 | -21.3641 | 86.5854 | 0.34317 | 93.5892 | [47 empty] | Alkb, mg/L CaCO3 | 272.8233 | 286.8207 | 264.5319 | 262.9691 | Alkb, mg/L CaCO3 | 232.1417 | 279.2908 | 204.2128 | 198.9485
[44 empty] | 1999-02-24 | 16:30 | 101.5 | 23.6 | 49 | 50 | 272 | 4.4 | 4.22 |  | 8.62 | 0.20791 | 0.51044 | 30.5545 | 10.0428 | 10.344 | 294.4287 | 244.6116 | 293.6228 | 0.49414 | 49.0059 | 0.21108 | 7.56 | 7.82 | 7.8 | 242 | 266 | 280 | 297.1517 | -6.1256 | 10.0372 | 296.7056 | 18.4377 | 0.022 | 0.16 | 0.28 | 0.31206 | -11.4489 | 86.5854 | 0.30971 | 92.8966 | [47 empty] | T-Hdb, mg/L CaCO3 | 296.504 | 310.9084 | 290.1915 | 291.5876 | T-Hdb, mg/L CaCO3 | 264.5399 | 313.0598 | 243.2766 | 247.9794
[44 empty] | 1999-02-24 | 17:30 | 102.5 | 23.6 | 49 | 50 | 272 | 4.4 | 4.2 |  | 8.6 | 0.20791 | 0.51163 | 30.6279 | 10.0428 | 10.344 | 294.4934 | 244.6654 | 293.6874 | 0.49425 | 49.0057 | 0.21108 | 8.04 | 8.02 | 7.398 | 240 | 265 | 278 | 299.381 | -7.691 | 10.7807 | 298.9007 | 19.7058 | 0.023 | 0.16 | 0.278 | 0.31171 | -12.1274 | 85.9756 | 0.30938 | 92.5658 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 249.7085 | 259.5936 | 241.7766 | 241.2577 | Ca-Hdb, mg/L CaCO3 | 218.2287 | 251.5259 | 191.5106 | 189.7629
[44 empty] | 1999-02-25 | 9:00 | 118 | 23 | 49 | 50 | 272 | 4.56 | 4.24 |  | 8.8 | 0.20791 | 0.51818 | 29.9091 | 10.408 | 10.912 | 294.8654 | 244.9497 | 294.0286 | 0.49497 | 49.005 | 0.22267 | 7.91 | 7.85 | 7.84 | 238 | 265 | 279 | 302.3396 | -8.3655 | 11.5242 | 301.8003 | 21.1399 | 0.022 | 0.16 | 0.279 | 0.31672 | -13.5186 | 86.5854 | 0.31425 | 92.9991 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-02-25 | 9:30 | 118.5 | 23.1 | 49 | 50 | 272 | 4.48 | 14.06 |  | 18.54 | 0.20791 | 0.24164 | 13.671 | 10.2254 | 10.6889 | 280.4699 | 233.0029 | 279.6881 | 0.47076 | 49.0292 | 0.21801 | 7.99 | 7.96 | 7.97 | 241 | 266 | 269 | 277.9218 | -3.3166 | 10.4089 | 277.6177 | 13.19 | 0.022 | 0.161 | 0.229 | 0.20925 | 8.6262 | 86.5854 | 0.2077 | 89.408 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-02-25 | 10:30 | 119.5 | 23.1 | 49 | 50 | 272 | 4.51 | 11.55 |  | 16.06 | 0.20791 | 0.28082 | 15.9365 | 10.2938 | 10.7605 | 282.4239 | 234.6217 | 281.6313 | 0.47406 | 49.0259 | 0.21949 | 8.18 | 8.19 | 8.13 | 235 | 266 | 270 | 282.2762 | -4.5467 | 12.6394 | 281.8843 | 16.6324 | 0.02 | 0.16 | 0.207 | 0.22023 | -6.3906 | 87.8049 | 0.21857 | 90.8496 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-02-25 | 11:00 | 120 | 23.1 | 49 | 50 | 272 | 4.48 | 11.04 |  | 15.52 | 0.20791 | 0.28866 | 16.5258 | 10.2254 | 10.6889 | 282.8165 | 234.9523 | 282.0281 | 0.4747 | 49.0253 | 0.21803 | 8.15 | 8.1 | 8.16 | 237 | 266 | 261 | 281.9855 | -8.0404 | 11.8959 | 281.615 | 15.8426 | 0.017 | 0.16 | 0.209 | 0.22365 | -7.0106 | 89.6341 | 0.22195 | 92.3406 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-02-25 | 11:30 | 120.5 | 23.1 | 49 | 50 | 272 | 4.44 | 10.3 |  | 14.74 | 0.20791 | 0.30122 | 17.4532 | 10.1341 | 10.4381 | 283.4481 | 235.483 | 282.6652 | 0.47574 | 49.0243 | 0.21292 | 8.11 | 8.12 | 8.09 | 238 | 265 | 269 | 282.3631 | -4.9677 | 11.5242 | 282.001 | 15.6031 | 0.018 | 0.159 | 0.209 | 0.22694 | -8.5818 | 89.0244 | 0.22523 | 92.0082 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-02-25 | 12:00 | 121 | 23.6 | 49 | 50 | 272 | 4.47 | 9.73 |  | 14.2 | 0.20791 | 0.31479 | 18.1549 | 10.2025 | 10.5086 | 284.137 | 236.0508 | 283.3467 | 0.47691 | 49.0231 | 0.21436 | 8.13 | 8.17 | 8.1 | 233 | 265 | 266 | 285.5385 | -7.3453 | 13.3829 | 285.1068 | 18.2762 | 0.016 | 0.16 | 0.201 | 0.23199 | -15.4188 | 90.2439 | 0.23022 | 93.05 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-02-25 | 14:00 | 123 | 23.6 | 49 | 50 | 272 | 4.56 | 11.9 |  | 16.46 | 0.20791 | 0.27704 | 15.5249 | 10.408 | 10.7202 | 282.2361 | 234.4583 | 281.4352 | 0.47377 | 49.0262 | 0.21866 | 8.15 | 8.19 | 8.14 | 233 | 265 | 269 | 282.795 | -5.1282 | 13.3829 | 282.3776 | 17.4864 | 0.017 | 0.161 | 0.202 | 0.22033 | -9.074 | 89.6341 | 0.21863 | 92.2241 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-02-25 | 14:30 | 123.5 | 23.6 | 49 | 50 | 272 | 4.48 | 11.3 |  | 15.78 | 0.20791 | 0.2839 | 16.237 | 10.2254 | 10.7523 | 282.5773 | 234.7536 | 281.7896 | 0.4743 | 49.0257 | 0.21932 | 8.13 | 8.2 | 8.11 | 237 | 265 | 270 | 281.6867 | -4.3284 | 11.8959 | 281.3187 | 15.7539 | 0.014 | 0.16 | 0.196 | 0.22347 | -14.0148 | 91.4634 | 0.22174 | 93.6864 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-02-25 | 15:30 | 124.5 | 22.9 | 49 | 50 | 272 | 4.44 | 10.96 |  | 15.4 | 0.20791 | 0.28831 | 16.6623 | 10.1341 | 10.6563 | 282.7971 | 234.9422 | 282.016 | 0.47464 | 49.0254 | 0.21736 | 8.16 | 8.17 | 8.1 | 234 | 266 | 268 | 283.1788 | -5.6637 | 13.0112 | 282.7774 | 17.2494 | 0.014 | 0.161 | 0.191 | 0.22477 | -17.6788 | 91.4634 | 0.22305 | 93.7233 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-02-25 | 16:30 | 125.5 | 22.9 | 49 | 50 | 272 | 4.52 | 11 |  | 15.52 | 0.20791 | 0.29124 | 16.5258 | 10.3167 | 10.8483 | 282.948 | 235.0556 | 282.1522 | 0.47494 | 49.0251 | 0.22128 | 8.11 | 8.18 | 8.08 | 236 | 266 | 270 | 282.56 | -4.6519 | 12.2677 | 282.1731 | 16.3634 | 0.016 | 0.16 | 0.204 | 0.22481 | -10.2032 | 90.2439 | 0.22308 | 92.8277 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-02-26 | 17:30 | 126.5 | 22.9 | 49 | 50 | 272 | 4.48 | 10.75 |  | 15.23 | 0.20791 | 0.29416 | 16.8595 | 10.2254 | 10.7523 | 283.0933 | 235.1823 | 282.3042 | 0.47516 | 49.0248 | 0.21932 | 8.1 | 8.16 | 8.05 | 233 | 265 | 269 | 284.0028 | -5.5772 | 13.3829 | 283.5828 | 17.837 | 0.015 | 0.159 | 0.201 | 0.22609 | -12.485 | 90.8537 | 0.22436 | 93.3142 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-02-26 | 9:30 | 142.5 | 22.9 | 49 | 50 | 272 | 4.56 | 8 | X | 12.56 | 0.20791 | 0.36306 | 20.6561 | 10.408 | 10.9443 | 286.6152 | 238.0961 | 285.8018 | 0.48112 | 49.0189 | 0.22327 | 8.01 | 8.09 | 8.03 | 231 | 266 | 268 | 290.66 | -8.4552 | 14.1264 |  |  | 0.015 | 0.16 | 0.211 | 0.24893 | -17.9763 | 90.8537 | 0.24697 | 93.9264 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-02-26 | 11:00 |  | 22.9 | 49 | 50 | 272 | 4.68 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 10.6818 | 11.2323 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 14:00 |  | 22.9 | 60 | 61 | 272 | 5.75 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 13.1241 | 13.8004 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 14:30 |  | 22.9 | 40 | 41 | 272 | 3.73 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 8.5135 | 8.9523 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 14:45 |  | 22.9 | 50 | 51 | 272 | 4.64 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 10.5906 | 11.1363 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 15:00 |  | 22.9 | 49 | 50 | 272 | 4.45 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 10.1569 | 10.6803 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 16:00 |  | 22.9 | 59 | 60 | 272 | 5.05 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 11.5264 | 12.1204 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 16:15 |  | 22.9 | 39 | 40 | 272 | 3.45 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 7.8744 | 8.2802 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-26 | 16:30 |  | 22.9 | 50 | 51 | 272 | 4.73 | NA |  | #VALUE! | 0 | #VALUE! | #VALUE! | 10.796 | 22.3387 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | #VALUE! | #DIV/0! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on X14: Alison Gusses: Verified by consultant
Note on X16: Alison Gusses: Verified by consultant
Note on X18: Alison Gusses: Verified by consultant
Note on CY21: C. Rice 7/8/99: Consultant verified that ammonia concentrations were checked and found to be correct.
Note on DG10: Alison Gusses: Consultant verified calcium hardness, UV and ammonia concentrations due to high mass balance closure errors.
Note on DQ10: Alison Gusses: Consultant verified calcium hardness, UV and ammonia concentrations due to high mass balance closure errors.
Note on EA10: Alison Gusses: Consultant verified calcium hardness, UV and ammonia concentrations due to high mass balance closure errors.
Note on EK10: Alison Gusses: Consultant verified calcium hardness, UV and ammonia concentrations due to high mass balance closure errors.

## SR40. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.57981 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.93 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.33 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-23 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.55 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.55 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.3 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.95 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:00 | 7:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 109.6 | 109.6 | 109.6 | 109.6 | SDS-THM4F, ug/L | 109.6 | 109.6 | 109.6 | 109.6 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 25 | 153 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 7.05 | 10.3 | 7 | 4.6 | SDS-THM4p, ug/L | 7.05 | 10.3 | 7 | 4.6 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.2 | 7.9 | 8.05 | 3.7267 | 1998-04-06 | 8:30 | 0 | 23 | 50 | 48.5 | 263 | 6.36 | 2.67 | 9.03 | 0.18158 | 0.70432 | 28.1251 | 14.5164 | 15.2194 | 0 | 0 | 0 | 0 | 49.25 | 0.30902 | 1998-04-07 | 7:30 | 0 | 23 | 50 | 48 | 263 | 7.1 | 3 |  | 10.1 | 0.18158 | 0.70297 | 25.0396 | 16.2054 | 16.9902 | 439.8249 | 181.8839 | 432.8615 | 2.5446 | 46.4554 | 0.36573 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 75.5 | 75.5 | 75.5 | 75.5 | SDS-HAA5F, ug/L | 75.5 | 75.5 | 75.5 | 75.5 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 23 | 23.5 | 4.2553 | 1998-04-06 | 10:30 | 2 | 23 | 50 | 48.5 | 263 | 6.54 | 2.31 | 8.85 | 0.18158 | 0.73898 | 28.7175 | 14.9272 | 15.6501 | 0 | 0 | 0 | 0 | 49.25 | 0.31777 | 1998-04-07 | 8:30 | 1 | 23 | 50 | 48 | 263 | 6.88 | 2.92 |  | 9.8 | 0.18158 | 0.70204 | 25.8367 | 15.7032 | 16.4637 | 439.3081 | 181.7617 | 432.5707 | 2.5418 | 46.4582 | 0.35438 |  |  |  |  | 265 | [7 empty] | 0.16 | [14 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.6 | 3.7 | 2.2 | 2.3 | SDS-HAA5p, ug/L | 2.6 | 3.7 | 2.2 | 2.3 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 140 | NA | 140 | #VALUE! | 1998-04-06 | 11:30 | 3 | 23 | 50 | 48 | 263 | 6.62 | 3.97 | 10.59 | 0.18158 | 0.62512 | 23.8347 | 15.1098 | 15.8416 | 0 | 0 | 0 | 0 | 49 | 0.3233 | 1998-04-07 | 9:30 | 2 | 23 | 50 | 49 | 263 | 6.45 | 2.86 |  | 9.31 | 0.18158 | 0.6928 | 27.2492 | 14.7218 | 15.4348 | 435.0953 | 180.1957 | 428.8439 | 2.5177 | 46.9823 | 0.32852 | [27 empty] | Sampling date | MM/DD/YY | 1998-04-08 | 1998-04-09 | --- | --- | 1998-04-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-10 | 1998-04-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-11 | 1998-04-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-11 | 1998-04-11 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 275 | 275 | 275 | 275 | SDS-TOXF, ug Cl- /L | 275 | 275 | 275 | 275 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 260 | 257 | 258.5 | 1.1605 | 1998-04-06 | 12:30 | 4 | 23 | 50 | 48 | 263 | 6.67 | 2.18 | 8.85 | 0.18158 | 0.75367 | 28.7175 | 15.2239 | 15.9612 | 0 | 0 | 0 | 0 | 49 | 0.32574 | 1998-04-07 | 10:30 | 3 | 23 | 50.5 | 49 | 263 | 6.25 | 2.71 |  | 8.96 | 0.18158 | 0.69754 | 28.3527 | 14.2653 | 14.9562 | 437.0415 | 181.0844 | 430.9589 | 2.5292 | 47.2208 | 0.31673 |  |  |  | 155 |  | 383 | 497.1993 | -29.817 | 40.0387 | 493.1332 | 68.5683 | BMRL |  | 0.263 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 8:15 | 9:00 | --- | --- | 8:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 4:30 | 4:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 22:00 | 22:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 188 | NA | 188 | #VALUE! | 1998-04-06 | 13:00 | 4.5 | 23 | 49 | 47.5 | 263 | 6.75 | 4.45 | 11.2 | 0.18158 | 0.60268 | 22.4821 | 15.4065 | 16.1527 | 0 | 0 | 0 | 0 | 48.25 | 0.33477 | 1998-04-07 | 11:30 | 4 | 23 | 50.5 | 49 | 263 | 6.1 | 2.65 |  | 8.75 | 0.18158 | 0.69714 | 29.0571 | 13.9229 | 14.5972 | 436.7948 | 181.0441 | 430.8629 | 2.5278 | 47.2222 | 0.30912 |  |  |  | 167 |  | 425 | 469.1226 | -10.3818 | 35.3965 | 465.6189 | 64.1338 | BMRL |  | 0.364 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 25 | 50 | --- | --- | 25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 81 | 81 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101 | 101 | --- | --- | --- | --- | --- | Cumulative time | hr | 111 | 111 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 6.21 | 6.21 | 6.21 | 6.21 | SDS-CDF, mg/L | 6.21 | 6.21 | 6.21 | 6.21 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 158 | NA | 158 | #VALUE! | 1998-04-06 | 13:30 | 5 | 23 | 49 | 48 | 263 | 6.63 | 2.64 | 9.27 | 0.18158 | 0.71521 | 27.3711 | 15.1326 | 15.8655 | 0 | 0 | 0 | 0 | 48.5 | 0.32712 | 1998-04-07 | 13:00 | 5.5 | 23 | 50.5 | 49 | 263 | 6.3 | 2.61 |  | 8.91 | 0.18158 | 0.70707 | 28.5174 | 14.3794 | 15.0758 | 441.2282 | 182.7983 | 435.0377 | 2.5533 | 47.1967 | 0.31943 | 7.26 | 7.53 | 7.6 | 173 | 264 | 445 | 464.8793 | -4.4673 | 33.0754 | 461.3834 | 62.5041 | BMRL | 0.159 | 0.424 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 8.2 | 8.3 | 8.25 | 1.2121 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.2 | --- | --- | --- | --- | --- | pH | --- | 8.3 | 8.1 | --- | --- | --- | --- | --- | pH | --- | 8.3 | 8.3 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.855 | 2.06 | 1.55 | 1.65 | SDS-CDp, mg/L | 1.855 | 2.06 | 1.55 | 1.65 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.33 | NA | 0.33 | #VALUE! | 1998-04-06 | 15:00 | 6.5 | 23 | 49 | 48 | 263 | 6.7 | 3.89 | 10.59 | 0.18158 | 0.63267 | 23.8347 | 15.2924 | 16.033 | 0 | 0 | 0 | 0 | 48.5 | 0.33058 | 1998-04-07 | 15:30 | 8 | 23 | 51 | 50 | 263 | 6.44 | 3.67 |  | 10.11 | 0.18158 | 0.63699 | 25.0138 | 14.699 | 15.4108 | 412.3957 | 170.7986 | 406.4798 | 2.3864 | 48.1136 | 0.3203 | 7.34 |  |  | 169 |  | 402 | 415.5518 | -3.3711 | 34.6228 | 412.5332 | 59.0336 | BMRL | 0.159 | 0.399 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.85 | 3.85 | 3.85 | 3.85 | TOCF, mg/L | 3.85 | 3.85 | 3.85 | 3.85 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | NA | #DIV/0! | #VALUE! | 1998-04-06 | 16:15 | 7.75 | 23 | 49 | 48 | 263 | 6.8 | 2.96 | 9.76 | 0.18158 | 0.69672 | 25.9467 | 15.5206 | 16.2723 | 0 | 0 | 0 | 0 | 48.5 | 0.33551 | 1998-04-07 | 17:30 | 10 | 23 | 51 | 50 | 263 | 6.42 | 3.8 |  | 10.22 | 0.18158 | 0.62818 | 24.7339 | 14.6533 | 15.363 | 409.019 | 169.4078 | 403.1699 | 2.3669 | 48.1331 | 0.31918 | 7.29 | [26 empty] | Alkalinity | mg/L as CaCO3 | 124 | 140 | 132 | 12.1212 | 226 | 157.8065 | 30.1741 | 5.7143 | 157.4832 | 16.1815 | Alkalinity | mg/L as CaCO3 | 136 | 124 | 193.1429 | -55.7604 | 2.8571 | 192.4811 | 29.3437 | Alkalinity | mg/L as CaCO3 | 114 | 228 | 167.0612 | 26.7275 | 18.5714 | 166.377 | 31.4809 | Alkalinity | mg/L as CaCO3 | 112 | 130 | 153.791 | -18.3008 | 20 | 153.2155 | 26.9004 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 3.9 | 3.8 | 3.85 | 2.5974 | 1998-04-07 | 7:00 | 22.5 | 23 | 50 | 48 | 263 | 7.1 | 3.04 | 10.14 | 0.18158 | 0.7002 | 24.9369 | 16.2054 | 16.9902 | 0 | 0 | 0 | 0 | 49 | 0.34674 | 1998-04-08 | 7:30 | 24 | 23 | 52 | 51 | 263 | 6.4 | 3.25 |  | 9.65 | 0.18158 | 0.66321 | 26.2539 | 14.6077 | 15.3151 | 422.738 | 175.0979 | 416.7117 | 2.4463 | 49.0537 | 0.31221 | [27 empty] | Total dissolved solids | mg/L | 163 | 178 | 170.5 | 8.7977 | 373 | 454.371 | -21.8153 | 34.0426 | 450.8148 | 62.1796 | Total dissolved solids | mg/L | 187 | 595 | 1208.4286 | -103.0972 | 27.6596 | 1196.5996 | 84.3724 | Total dissolved solids | mg/L | 151 | 333 | 370.3878 | -11.2276 | 41.5861 | 367.5587 | 58.9181 | Total dissolved solids | mg/L | 146 | 232 | 313.9104 | -35.3062 | 43.5203 | 311.5982 | 53.1448 | UV254 F, cm-1 | 0.1575 | 0.1575 | 0.1575 | 0.1575 | UV254 F, cm-1 | 0.1575 | 0.1575 | 0.1575 | 0.1575 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.161 | 0.154 | 0.1575 | 4.4444 | 1998-04-07 | 7:15 | 22.75 | 23 | 40 | 38 | 263 | 5.35 | 2.4 | 7.75 | 0.18158 | 0.69032 | 32.9355 | 12.2111 | 12.8025 | 0 | 0 | 0 | 0 | 39 | 0.32827 | 1998-04-08 | 8:15 | 24.75 | 23 | 52 | 51 | 263 | 6.4 | 3.25 |  | 9.65 | 0.18158 | 0.66321 | 26.2539 | 14.6077 | 15.3151 | 422.738 | 175.0979 | 416.7117 | 2.4463 | 49.0537 | 0.31221 | 7.45 | 7.54 | 7.66 | 172 | 261 | 425 | 428.8385 | -0.90317 | 33.4623 | 425.7134 | 59.5972 | BMRL | 0.158 | 0.416 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 128 | 146 | 137 | 13.1387 | 386 | 301.5161 | 21.887 | 27.1277 | 299.4551 | 54.2502 | Total hardness | mg/L as CaCO3 | 154 | 442 | 639.7143 | -44.7317 | 18.0851 | 634.0893 | 75.7132 | Total hardness | mg/L as CaCO3 | 114 | 310 | 265.0204 | 14.5095 | 39.3617 | 263.0729 | 56.666 | Total hardness | mg/L as CaCO3 | 112 | 202 | 225.4328 | -11.6004 | 40.4255 | 223.8708 | 49.9711 | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.1282 | 4.0526 | 4.0904 | 1.8476 | 1998-04-07 | 7:30 | 23 | 23 | 60 | 59 | 263 | 8.5 | 4 | 12.5 | 0.18158 | 0.68 | 20.04 | 19.4008 | 20.3404 | 0 | 0 | 0 | 0 | 59.5 | 0.34186 | 1998-04-08 | 9:30 | 26 | 23 | 53 | 52 | 263 | 6.5 | 3.2333 |  | 9.7333 | 0.18158 | 0.66781 | 26.0205 | 14.8359 | 15.5544 | 424.6514 | 175.8503 | 418.5024 | 2.4573 | 50.0427 | 0.31082 | 7.43 |  | 7.66 | 169 |  | 425 | 438.4227 | -3.1583 | 34.6228 | 435.0933 | 61.1578 | BMRL |  | 0.419 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 124 | 142 | 133 | 13.5338 | 362 | 213.6452 | 40.982 | 15.8228 | 212.6349 | 37.4515 | Calcium hardness | mg/L as CaCO3 | 118 | 426 | 689.4286 | -61.8377 | 25.3165 | 682.811 | 82.7185 | Calcium hardness | mg/L as CaCO3 | 106 | 302 | 212.1224 | 29.7608 | 32.9114 | 210.754 | 49.7044 | Calcium hardness | mg/L as CaCO3 | 112 | 174 | 180.6567 | -3.8257 | 29.1139 | 179.7113 | 37.6778 | BromideF, ug/L | 82 | 82 | 82 | 82 | BromideF, ug/L | 82 | 82 | 82 | 82 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 82 | NA | 82 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-08 | 10:30 | 27 | 23 | 53 | 52 | 263 | 6.75 | 5.6 |  | 12.35 | 0.18158 | 0.54656 | 20.2955 | 15.4065 | 16.1527 | 380.3458 | 157.4131 | 374.6241 | 2.2007 | 50.2993 | 0.32113 | 7.38 |  | 7.64 | 176 | 262 |  | 357.942 |  | 31.9149 | 355.6072 | 50.5072 | BMRL |  | 0.419 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.25 | 0.35 | 0.3 | 33.3333 | 0.19 | 0.39677 | -108.8285 | 9.0909 | 0.39556 | 24.1585 | Turbidity | ntu | 0.07 | 0.25 | 3.7843 | -1413.7143 | 78.7879 | 3.7413 | 98.129 | Turbidity | ntu | 0.11 | 0.14 | 0.55898 | -299.2711 | 66.6667 | 0.55319 | 80.1153 | Turbidity | ntu | 0.06 | 0.14 | 0.46299 | -230.7036 | 81.8182 | 0.45744 | 86.8834 | Bromidep, ug/L | 66.5 | 77 | 62 | 54 | Bromidep, ug/L | 66.5 | 77 | 62 | 54 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 7 | NA | 7 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-08 | 11:30 | 28 | 23 | 53 | 52 | 263 | 6.5714 | 2.9846 |  | 9.556 | 0.18158 | 0.68767 | 26.5218 | 14.9989 | 15.7253 | 432.9623 | 179.2626 | 426.6232 | 2.5053 | 49.9947 | 0.31454 |  | 7.53 |  | 171 |  |  | 451.1546 |  | 33.8491 | 447.6546 | 61.8009 | BMRL | 0.159 |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 140 | 140 | 140 | 140 | AlkF, mg/L CaCO3 | 140 | 140 | 140 | 140
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.79 | NA | 0.79 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-08 | 13:00 | 29.5 | 23 | 53 | 52 | 263 | 6.5714 | 2.9846 |  | 9.556 | 0.18158 | 0.68767 | 26.5218 | 14.9989 | 15.7253 | 432.9623 | 179.2626 | 426.6232 | 2.5053 | 49.9947 | 0.31454 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 12.15 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 34 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 8.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 132 | 136 | 114 | 112 | Alkp, mg/L CaCO3 | 132 | 136 | 114 | 112
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 6.21 | NA | 6.21 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-08 | 14:00 | 30.5 | 23 | 53 | 52 | 263 | 6.3237 | 3.1928 |  | 9.5165 | 0.18158 | 0.6645 | 26.6363 | 14.4335 | 15.1325 | 423.2266 | 175.3309 | 417.2661 | 2.4492 | 50.0508 | 0.30234 |  |  |  | 168 |  |  | 437.7463 |  | 35.0097 | 434.5034 | 61.3352 | [16 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.4085 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | BMRL | 1.092 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.267 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 188 | 188 | 188 | 188 | T-HdF, mg/L CaCO3 | 188 | 188 | 188 | 188
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 26 | NA | 26 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-08 | 16:00 | 32.5 | 23 | 52 | 51 | 263 | 6.5 | 3 |  | 9.5 | 0.18158 | 0.68421 | 26.6842 | 14.8359 | 15.5544 | 431.4629 | 178.671 | 425.2152 | 2.4967 | 49.0033 | 0.31742 | [27 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.3621 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.2118 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.2963 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 2.9508 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 137 | 154 | 114 | 112 | T-Hdp, mg/L CaCO3 | 137 | 154 | 114 | 112
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.2 | NA | 8.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-08 | 17:00 | 33.5 | 23 | 52 | 51 | 263 | 6.5 | 3 |  | 9.5 | 0.18158 | 0.68421 | 26.6842 | 14.8359 | 15.5544 | 431.4629 | 178.671 | 425.2152 | 2.4967 | 49.0033 | 0.31742 | [27 empty] | Bromide | mg/L | 66 | 67 | 66.5 | 1.5038 | --- | 116.5 | --- | 18.9024 | 115.8736 | 42.6099 | Bromide | mg/L | 77 | --- | 148.4286 | --- | 6.0976 | 147.6014 | 47.8325 | Bromide | mg/L | 62 | --- | 102.8163 | --- | 24.3902 | 102.29 | 39.388 | Bromide | mg/L | 54 | --- | 95.791 | --- | 34.1463 | 95.2155 | 43.2866 | Ca-HdF, mg/L CaCO3 | 158 | 158 | 158 | 158 | Ca-HdF, mg/L CaCO3 | 158 | 158 | 158 | 158
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | NA | 24 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 8:30 | 49 | 23 | 52 | 51 | 263 | 6.5 | 2.63 |  | 9.13 | 0.18158 | 0.71194 | 27.8061 | 14.8359 | 15.5544 | 443.4885 | 183.6508 | 437.0666 | 2.5663 | 48.9337 | 0.31787 | 7.5 | 7.56 |  | 182 | 264 | 436 | 447.5684 | -2.6533 | 29.5938 | 444.2867 | 59.0355 | BMRL | 0.161 | 0.484 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 133 | 118 | 106 | 112 | Ca-Hdp, mg/L CaCO3 | 133 | 118 | 106 | 112
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 275 | NA | 275 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 9:00 | 49.5 | 23 | 53 | 52 | 263 | 6.46 | 2.8 |  | 9.26 | 0.18158 | 0.69762 | 27.4017 | 14.7446 | 15.4587 | 437.1783 | 181.0543 | 430.8872 | 2.5298 | 49.9702 | 0.30936 |  |  |  | 180 |  | 423 | 439.6107 | -3.9269 | 30.3675 | 436.4223 | 58.7555 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.51 | 0.78 | 0.645 | 41.8605 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.94 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.95 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.85 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 80 | NA | 80 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 10:30 | 51 | 23 | 53 | 52 | 263 | 6.57 | 2.65 |  | 9.22 | 0.18158 | 0.71258 | 27.5249 | 14.9957 | 15.7219 | 443.8111 | 183.755 | 437.3146 | 2.5681 | 49.9319 | 0.31487 | 7.47 | 7.57 | 7.7 | [8 empty] | BMRL |  | 0.486 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 1.99 | 1.72 | 1.855 | 14.5553 | --- | 15.9034 | --- | 70.1288 | 15.7274 | 88.2053 | SDS-Cl2 demand | mg/L | 2.06 | --- | 61.3457 | --- | 66.8277 | 60.6591 | 96.604 | SDS-Cl2 demand | mg/L | 1.55 | --- | 11.0602 | --- | 75.0403 | 10.9376 | 85.8287 | SDS-Cl2 demand | mg/L | 1.65 | --- | 8.456 | --- | 73.43 | 8.3622 | 80.2685 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 24 | NA | 24 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 11:30 | 52 | 23 | 53 | 52 | 263 | 6.56 | 2.63 |  | 9.19 | 0.18158 | 0.71382 | 27.6181 | 14.9728 | 15.698 | 444.3594 | 183.9863 | 437.8649 | 2.5713 | 49.9287 | 0.31441 |  |  |  | 180 |  | 435 | 454.3023 | -4.4373 | 30.3675 | 450.8813 | 60.0782 | BMRL | 0.16 | 0.48 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 26 | 26 | 26 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 36.665 | 37.8651 | 36.6472 | 35.8095 | Qp/QT (THM4), % | 71.7699 | 74.1188 | 71.7349 | 70.0952
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 5.6 | NA | 5.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 13:00 | 53.5 | 23 | 53 | 52 | 263 | 6.55 | 2.55 |  | 9.1 | 0.18158 | 0.71978 | 27.9011 | 14.95 | 15.6741 | 447.0382 | 185.0996 | 440.5146 | 2.5868 | 49.9132 | 0.31403 | 7.6 |  |  | 182 |  | 435 | 455 | -4.5977 | 29.5938 | 451.6005 | 59.6989 | [16 empty] | SDS-Chlorination pH | --- | 8.2 | 8.2 | 8.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.2 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 15:00 | 55.5 | 23 | 53 | 52 | 263 | 6.6 | 2.63 |  | 9.23 | 0.18158 | 0.71506 | 27.494 | 15.0641 | 15.7937 | 444.9359 | 184.2081 | 438.3929 | 2.5746 | 49.9254 | 0.31635 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 48.7712 | 48.3129 | 48.6376 | 49.2874 | SDS-HAA5b, ug/L | 23.1798 | 22.2827 | 22.9183 | 24.1903
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 109.6 | NA | 109.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 16:00 | 56.5 | 23 | 53 | 52 | 263 | 6.6 | 2.65 |  | 9.25 | 0.18158 | 0.71351 | 27.4324 | 15.0641 | 15.7937 | 444.2431 | 183.9213 | 437.7104 | 2.5706 | 49.9294 | 0.31632 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 2.9 | NA | 2.9 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-09 | 18:00 | 58.5 | 23 | 53 | 52 | 263 | 6.6 | 2.65 |  | 9.25 | 0.18158 | 0.71351 | 27.4324 | 15.0641 | 15.7937 | 444.2431 | 183.9213 | 437.7104 | 2.5706 | 49.9294 | 0.31632 | [27 empty] | SDS-CHCl3 | mg/L | 1.1 | 1.5 | 1.3 | 30.7692 | --- | 255.171 | --- | 98.375 | 251.9906 | 99.4841 | SDS-CHCl3 | mg/L | 1.9 | --- | 1117.6143 | --- | 97.625 | 1104.6934 | 99.828 | SDS-CHCl3 | mg/L | 1.4 | --- | 161.8082 | --- | 98.25 | 159.7396 | 99.1236 | SDS-CHCl3 | mg/L | 1.4 | --- | 118.7134 | --- | 98.25 | 117.0979 | 98.8044 | SDS-CDb, mg/L | 4.6132 | 4.6386 | 4.5022 | 4.5771 | SDS-CDb, mg/L | 3.0844 | 3.1341 | 2.8672 | 3.0137
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 29 | NA | 29 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 7:30 | 72 | 23 | 52 | 51 | 263 | 6.36 | 2.32 |  | 8.68 | 0.18158 | 0.73272 | 29.2995 | 14.5164 | 15.2194 | 452.8726 | 187.5968 | 446.4575 | 2.6207 | 48.8793 | 0.31137 | 7.7 | 7.51 | 7.81 | 186 | 262 | 450 | 457.25 | -1.6111 | 28.0464 | 453.9702 | 59.0282 | [16 empty] | SDS-BDCM | mg/L | 1.3 | 1.3 | 1.3 | 0 | --- | 74.5258 | --- | 94.5833 | 73.6085 | 98.2339 | SDS-BDCM | mg/L | 2 | --- | 316.2857 | --- | 91.6667 | 312.646 | 99.3603 | SDS-BDCM | mg/L | 1.6 | --- | 47.3143 | --- | 93.3333 | 46.7248 | 96.5757 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 41 | NA | 41 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 8:30 | 73 | 23 | 52 | 51 | 263 | 6.31 | 2.3 |  | 8.61 | 0.18158 | 0.73287 | 29.5459 | 14.4022 | 15.0997 | 452.9148 | 187.6357 | 446.5501 | 2.621 | 48.879 | 0.30892 |  |  |  | 183 |  | 444 | 465.6326 | -4.8722 | 29.207 | 462.2421 | 60.4104 | [16 empty] | SDS-DBCM | mg/L | 2.3 | 2.5 | 2.4 | 8.3333 | --- | 12.7226 | --- | 57.1429 | 12.5933 | 80.9422 | SDS-DBCM | mg/L | 3.9 | --- | 28.1857 | --- | 30.3571 | 27.9045 | 86.0237 | SDS-DBCM | mg/L | 2.5 | --- | 8.8265 | --- | 55.3571 | 8.7449 | 71.4121 | SDS-DBCM | mg/L | 1.5 | --- | 7.6194 | --- | 73.2143 | 7.5351 | 80.0933 | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | 1 | NA | 1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 10:00 | 74.5 | 23 | 54 | 52 | 263 | 6.56 | 2.4 |  | 8.96 | 0.18158 | 0.73214 | 28.3527 | 14.9728 | 15.698 | 452.7148 | 187.4458 | 446.0982 | 2.6196 | 50.3804 | 0.31159 |  |  |  | 186 |  |  | 456.6667 |  | 28.0464 | 453.2911 | 58.9668 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 1.9 | 2.2 | 2.05 | 14.6341 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 76.3169 | 80.1067 | 74.6706 | 71.9733 | Bromideb, ug/L | 70.8757 | 78.2941 | 67.653 | 62.3733
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.6 | NA | 1.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 11:15 | 75.75 | 23 | 53 | 52 | 263 | 6.57 | 2.3 |  | 8.87 | 0.18158 | 0.7407 | 28.6505 | 14.9957 | 15.7219 | 456.7306 | 189.1042 | 450.045 | 2.6428 | 49.8572 | 0.31534 | 7.65 |  | 7.8 | 189 |  | 450 | 457.0283 | -1.5618 | 26.8859 | 453.6805 | 58.3407 | BMRL | 0.16 | 0.525 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 6.6 | 7.5 | 7.05 | 12.766 | --- | 337.8565 | --- | 93.5675 | 333.7123 | 97.8874 | SDS-THM4 | mg/L | 10.3 | --- | 1428.8714 | --- | 90.6022 | 1412.4432 | 99.2708 | SDS-THM4 | mg/L | 7 | --- | 216.3878 | --- | 93.6131 | 213.6876 | 96.7242 | SDS-THM4 | mg/L | 4.6 | --- | 161.3164 | --- | 95.8029 | 159.1583 | 97.1098 | Alkb, mg/L CaCO3 | 137.0668 | 138.4854 | 130.4717 | 129.9733 | Alkb, mg/L CaCO3 | 134.2584 | 137.0352 | 121.3489 | 120.3733
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 8.5 | NA | 8.5 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 12:15 | 76.75 | 23 | 54 | 52 | 263 | 6.66 | 2.3 |  | 8.96 | 0.18158 | 0.7433 | 28.3527 | 15.2011 | 15.9373 | 458.0169 | 189.5978 | 451.2196 | 2.6502 | 50.3498 | 0.31653 |  |  |  | 185 | 259 | 453 | 471.3304 | -4.0465 | 28.4333 | 467.705 | 60.4452 | BMRL |  | 0.53 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 169.3008 | 175.1259 | 160.8811 | 160.7848 | T-Hdb, mg/L CaCO3 | 151.3974 | 162.7996 | 134.9162 | 134.7276
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | NR | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 13:30 | 78 | 23 | 53 | 52 | 263 | 6.7 | 2.3 |  | 9 | 0.18158 | 0.74444 | 28.2222 | 15.2924 | 16.033 | 458.583 | 189.8148 | 451.7361 | 2.6534 | 49.8466 | 0.32165 | [27 empty] | SDS-DCAA* | mg/L | 1 | 1.2 | 1.1 | 18.1818 | --- | 91.1 | --- | 96.2069 | 89.9725 | 98.7774 | SDS-DCAA* | mg/L | 1.2 | --- | 398.3429 | --- | 95.8621 | 393.7436 | 99.6952 | SDS-DCAA* | mg/L | 1.2 | --- | 57.9347 | --- | 95.8621 | 57.2031 | 97.9022 | SDS-DCAA* | mg/L | 1.2 | --- | 42.6925 | --- | 95.8621 | 42.1211 | 97.1511 | Ca-Hdb, mg/L CaCO3 | 148.8337 | 142.854 | 138.9435 | 141.5276 | Ca-Hdb, mg/L CaCO3 | 140.0575 | 128.3525 | 120.6979 | 125.7562
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 2.5 | NA | 2.5 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 13:35 | 78.0833 | 23 | 54 | 52 | 263 | 6.5 | 1 |  | 7.5 | 0.18158 | 0.86667 | 34.0667 | 14.8359 | 15.5544 | 525.167 | 217.4743 | 517.5624 | 3.0389 | 49.9611 | 0.31133 |  |  |  | 192 |  |  | 690.75 |  | 25.7253 | 684.5867 | 71.9539 | BMRL |  | 0.537 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | 1 | 1 | 1 | 0 | --- | 130.0323 | --- | 97.561 | 128.4158 | 99.2213 | SDS-TCAA* | mg/L | 1.1 | --- | 571.1 | --- | 97.3171 | 564.4989 | 99.8051 | SDS-TCAA* | mg/L | 1 | --- | 82.6327 | --- | 97.561 | 81.58 | 98.7742 | SDS-TCAA* | mg/L | 1.1 | --- | 60.6522 | --- | 97.3171 | 59.8322 | 98.1615
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 15 | NA | 15 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 14:00 | 78.5 | 23 | 54 | 52 | 263 | 6.42 | 0.95 |  | 7.37 | 0.18158 | 0.8711 | 34.6852 | 14.6533 | 15.363 | 527.8813 | 218.6383 | 520.3325 | 3.0547 | 49.9453 | 0.3076 | 7.7 |  |  | 199 |  |  | 660.5947 |  | 23.0174 | 654.9608 | 69.6165 | BMRL |  | 0.578 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 75.5 | NA | 75.5 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 14:30 | 79 | 23 | 54 | 52 | 263 | 6.41 | 0.92 |  | 7.33 | 0.18158 | 0.87449 | 34.8799 | 14.6305 | 15.339 | 530.0214 | 219.5297 | 522.4539 | 3.0671 | 49.9329 | 0.30719 |  |  |  | 203 |  | 485 | 645.1902 | -33.0289 | 21.47 | 639.8015 | 68.2714 | BMRL |  | 0.63 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | BMRL | 1 | 1 | #VALUE! | --- | 2.9355 | --- | 37.5 | 2.9112 | 65.6503 | SDS-DBAA* | mg/L | 1.4 | --- | 4.2571 | --- | 12.5 | 4.2241 | 66.8565 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 84 | NA | 84 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 15:00 | 79.5 | 23 | 54 | 52 | 263 | 6.4 | 0.85 |  | 7.25 | 0.18158 | 0.88276 | 35.2759 | 14.6077 | 15.3151 | 535.33 | 221.7335 | 527.6988 | 3.0978 | 49.9022 | 0.3069 | 7.65 |  |  | 204 |  |  | 668.8529 |  | 21.0832 | 663.1969 | 69.2399 | BMRL |  | 0.682 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.1 | --- | 106.8143 | --- | 87.0588 | 105.59 | 98.9582 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 29.4925 | 29.9443 | 29.3315 | 29.3716 | Qp/QT (HAA5), % | 66.5295 | 67.5487 | 66.1664 | 66.2568
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 15:30 | 80 | 23 | 54 | 52 | 263 | 6.4 | 0.86 |  | 7.26 | 0.18158 | 0.88154 | 35.2259 | 14.6077 | 15.3151 | 534.5415 | 221.4069 | 526.9215 | 3.0932 | 49.9068 | 0.30687 | 7.69 |  |  | 210 |  |  | 619.4302 |  | 18.7621 | 614.4486 | 65.823 | BMRL |  | 0.715 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 79.3555 | 79.8653 | 79.5059 | 78.7598 | SDS-THM4b, ug/L | 41.374 | 42.5241 | 41.7132 | 40.0303
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 16:00 | 80.5 | 23 | 54 | 52 | 263 | 6.4 | 0.8 |  | 7.2 | 0.18158 | 0.88889 | 35.5278 | 14.6077 | 15.3151 | 539.341 | 223.3949 | 531.6526 | 3.121 | 49.879 | 0.30705 |  |  |  | 212 |  |  | 630.5 |  | 17.9884 | 625.408 | 66.1021 | BMRL |  | 0.756 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 16:30 | 81 | 23 | 54 | 52 | 263 | 6.4 | 0.67 |  | 7.07 | 0.18158 | 0.90523 | 36.1994 | 14.6077 | 15.3151 | 550.3349 | 227.9485 | 542.4898 | 3.1846 | 49.8154 | 0.30744 |  |  |  | 214 |  | 530 | 683.5746 | -28.9763 | 17.2147 | 677.8612 | 68.4301 | BMRL | 0.161 | 0.779 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | 1 | --- | 201 | --- | 93.3333 | 198.6838 | 99.4967 | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-11 | 8:00 | 96.5 | 23 | 54 | 52 | 263 | 5.92 | 0.33 |  | 6.25 | 0.18158 | 0.9472 | 41.08 | 13.5121 | 14.1665 | 580.1694 | 240.5691 | 572.5252 | 3.3578 | 49.6422 | 0.28537 |  |  |  | 224 |  |  | 877.4091 |  | 13.3462 | 870.0551 | 74.2545 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 2 | 3.2 | 2.6 | 46.1538 | --- | 237.7613 | --- | 96.5563 | 234.8153 | 98.8927 | SDS-HAA5 | mg/L | 3.7 | --- | 1029.4143 | --- | 95.0993 | 1017.5357 | 99.6364 | SDS-HAA5 | mg/L | 2.2 | --- | 151.7918 | --- | 97.0861 | 149.8628 | 98.532 | SDS-HAA5 | mg/L | 2.3 | --- | 111.5537 | --- | 96.9536 | 110.0492 | 97.91 | SDS-CDb, mg/L | 4.9256 | 4.9673 | 4.8432 | 4.8707 | SDS-CDb, mg/L | 3.3126 | 3.4067 | 3.1266 | 3.1887
[44 empty] | 1998-04-11 | 8:30 | 97 | 23 | 54 | 52 | 263 | 6 | 0.33 |  | 6.33 | 0.18158 | 0.94787 | 40.5482 | 13.6947 | 14.3579 | 580.7719 | 240.775 | 573.0153 | 3.3612 | 49.6388 | 0.28925 | 7.64 | 7.55 |  | 227 | 262 |  | 831.2273 |  | 12.1857 | 824.3349 | 72.4626 | BMRL | 0.16 | 1.678 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 2 | 3.2 | 2.6 | 46.1538 | --- | 265.1806 | --- | 96.9048 | 261.8911 | 99.0072 | SDS-HAA6 | mg/L | 4.8 | --- | 1136.2286 | --- | 94.2857 | 1123.1257 | 99.5726 | SDS-HAA6 | mg/L | 2.2 | --- | 169.1388 | --- | 97.381 | 166.986 | 98.6825 | SDS-HAA6 | mg/L | 2.3 | --- | 124.2403 | --- | 97.2619 | 122.5611 | 98.1234 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-11 | 9:00 | 97.5 | 23 | 52 | 50 | 263 | 5.82 | 5.55 |  | 11.37 | 0.18158 | 0.51187 | 22.131 | 13.2838 | 13.9272 | 369.0617 | 153.0674 | 364.2819 | 2.136 | 48.864 | 0.28502 | 7.6 | 7.51 | 7.64 | 227 | 261 | 652 | 291.5324 | 55.2864 | 12.1857 | 290.8184 | 21.9444 | BMRL | 0.161 | 1.698 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-11 | 9:30 | 98 | 23 | 52 | 50 | 263 | 6 | 5.56 |  | 11.56 | 0.18158 | 0.51903 | 21.7509 | 13.6947 | 14.3579 | 371.3293 | 153.9448 | 366.37 | 2.149 | 48.851 | 0.29391 |  |  |  | 201 |  | 603 | 320.5504 | 46.8407 | 22.2437 | 319.1867 | 37.0274 | BMRL |  | 1.429 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 77.4287 | 80.5028 | 76.1337 | 73.776 | Bromideb, ug/L | 71.6879 | 78.6226 | 68.7667 | 63.4481
[44 empty] | 1998-04-11 | 10:00 | 98.5 | 23 | 52 | 50 | 263 | 6.35 | 5.6 |  | 11.95 | 0.18158 | 0.53138 | 21.0084 | 14.4935 | 15.1955 | 375.3219 | 155.4759 | 370.0138 | 2.1719 | 48.8281 | 0.3112 |  |  |  | 183 |  | 474 | 344.1116 | 27.4026 | 29.207 | 342.1666 | 46.5173 | BMRL |  | 0.852 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 137.6406 | 138.8022 | 132.3738 | 131.776 | Alkb, mg/L CaCO3 | 134.6776 | 137.2981 | 122.7967 | 121.4481
[44 empty] | 1998-04-11 | 10:30 | 99 | 23 | 52 | 50 | 263 | 6.34 | 5.75 |  | 12.09 | 0.18158 | 0.5244 | 20.7535 | 14.4707 | 15.1715 | 373.1042 | 154.5608 | 367.8359 | 2.1591 | 48.8409 | 0.31063 | 7.7 |  |  | 169 |  | 414 | 357.1835 | 13.7238 | 34.6228 | 354.9153 | 52.383 | BMRL |  | 0.58 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 172.9588 | 177.8189 | 166.2947 | 165.6776 | T-Hdb, mg/L CaCO3 | 154.07 | 165.0334 | 139.0368 | 137.6448
[44 empty] | 1998-04-11 | 11:00 | 99.5 | 23 | 52 | 50 | 263 | 6.33 | 7.7 |  | 14.03 | 0.18158 | 0.45118 | 17.7455 | 14.4479 | 15.1476 | 351.3514 | 145.5529 | 346.3981 | 2.0332 | 48.9668 | 0.30934 | 7.6 |  |  | 161 |  | 369 | 338.6526 | 8.2242 | 37.7176 | 336.5147 | 52.1566 | BMRL |  | 0.415 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 150.6269 | 146.0223 | 142.7476 | 144.4891 | Ca-Hdb, mg/L CaCO3 | 141.3676 | 130.9805 | 123.5935 | 127.5219
[44 empty] | 1998-04-11 | 11:30 | 100 | 23 | 52 | 50 | 263 | 6.43 | 7 |  | 13.43 | 0.18158 | 0.47878 | 18.583 | 14.6761 | 15.3869 | 359.2685 | 148.7987 | 354.1228 | 2.079 | 48.921 | 0.31453 | 7.62 |  |  | 160 |  | 353 | 348.9793 | 1.139 | 38.1044 | 346.6691 | 53.8465 | BMRL |  | 0.347 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-04-11 | 12:00 | 100.5 | 23 | 52 | 50 | 263 | 6.4 | 6.9 |  | 13.3 | 0.18158 | 0.4812 | 18.7744 | 14.6077 | 15.3151 | 359.9722 | 149.1003 | 354.8407 | 2.0831 | 48.9169 | 0.31308 |  |  |  | 160 |  | 349 | 349.8623 | -0.24708 | 38.1044 | 347.5522 | 53.9638 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-04-11 | 20:00 | 108.5 | 23 | 52 | 50 | 263 | 7 | 6.3 |  | 13.3 | 0.18158 | 0.52632 | 18.7744 | 15.9771 | 16.7509 | 373.8871 | 154.6516 | 368.052 | 2.1632 | 48.8368 | 0.343 | 7.58 |  |  | 165 |  | 360 | 362.3889 | -0.66358 | 36.1702 | 359.762 | 54.1364 | BMRL |  | 0.319 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-04-11 | 20:30 | 109 | 23 | 52 | 50 | 263 | 7 | 6.3 |  | 13.3 | 0.18158 | 0.52632 | 18.7744 | 15.9771 | 16.7509 | 373.8871 | 154.6516 | 368.052 | 2.1632 | 48.8368 | 0.343 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-04-11 | 20:35 | 109.0833 | 23 | 54 | 54 | 263 | 7.4 | 18 |  | 25.4 | 0.18158 | 0.29134 | 9.3543 | 16.8901 | 17.7081 | 311.7997 | 128.852 | 306.6521 | 1.8037 | 52.1963 | 0.33926 |  |  |  | 164 |  | 336 | 297.35 | 11.503 | 36.5571 | 295.474 | 44.496 | BMRL |  | 0.277 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-04-11 | 20:45 | 109.25 | 23 | 54 | 53 | 263 | 7.43 | 17.3 |  | 24.73 | 0.18158 | 0.30044 | 9.6349 | 16.9586 | 17.7799 | 313.8255 | 129.6802 | 308.6232 | 1.8154 | 51.6846 | 0.34401 | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-04-11 | 21:00 | 109.5 | 23 | 54 | 53 | 263 | 7.3 | 16.8 |  | 24.1 | 0.18158 | 0.3029 | 9.9129 | 16.6619 | 17.4688 | 314.3621 | 129.9407 | 309.2431 | 1.8186 | 51.6814 | 0.33801 |  |  |  | 147 | 260 | 311 | 306.9494 | 1.3024 | 43.1335 | 304.7296 | 51.7605 | BMRL |  | 0.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-04-11 | 21:30 | 110 | 23 | 54 | 53 | 263 | 7.29 | 16.64 |  | 23.93 | 0.18158 | 0.30464 | 9.9904 | 16.639 | 17.4449 | 314.7503 | 130.1042 | 309.6322 | 1.8209 | 51.6791 | 0.33756 | 7.7 |  |  | 150 |  | 311 | 306.034 | 1.5968 | 41.9729 | 303.8714 | 50.637 | BMRL |  | 0.224 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-04-11 | 22:00 | 110.5 | 23 | 54 | 53 | 263 | 7.3 | 16.6 |  | 23.9 | 0.18158 | 0.30544 | 10.0042 | 16.6619 | 17.4688 | 314.9316 | 130.1761 | 309.8034 | 1.8219 | 51.6781 | 0.33803 |  |  |  | 149 |  |  | 306.6536 |  | 42.3598 | 304.4656 | 51.0618 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-04-12 | 9:30 | 122 | 23 | 55 | 54 | 263 | 7.24 | 13.5 |  | 20.74 | 0.18158 | 0.34908 | 11.6808 | 16.5249 | 17.3252 | 325.0636 | 134.3827 | 319.8145 | 1.8806 | 52.6194 | 0.32926 |  |  |  | 150 |  | 310 | 316.6881 | -2.1575 | 41.9729 | 314.3938 | 52.2891 | [55 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-04-12 | 10:00 | 122.5 | 23 | 55 | 54 | 263 | 7.27 | 13.47 |  | 20.74 | 0.18158 | 0.35053 | 11.6808 | 16.5934 | 17.397 | 325.4149 | 134.5187 | 320.1381 | 1.8826 | 52.6174 | 0.33063 |  |  |  | 152 | 260 | 314 | 315.98 | -0.63056 | 41.1992 | 313.7135 | 51.5482 | [55 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-04-12 | 10:30 | 123 | 23 | 55 | 54 | 263 | 7.1 | 15.3 | X | 22.4 | 0.18158 | 0.31696 | 10.7411 | 16.2054 | 16.9902 | 317.5238 | 131.3078 | 312.4967 | 1.837 | 52.663 | 0.32262 |  |  |  | 148 |  | 313 | 309.7778 | 1.0295 | 42.7466 | 307.5941 | 51.8846 | [55 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-04-12 | 11:45 |  | 23 | 60 | 58 | 263 | 9 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 20.542 | 21.5369 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-12 | 12:00 |  | 23 | 70 | 69 | 263 | 10.5 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 23.9657 | 25.1264 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-04-12 | 12:15 |  | 23 | 51 | 50 | 263 | 7.4 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 16.8901 | 17.7081 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on DO16: C. Hill (7/8/99): This value was verified by the consultant.
Note on DQ10: S Allgeier 7/9/99: Consultant verified data responsible for high mass balance closure errors.

## SR40. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.53027 | [45 empty] | Recovery during sample collection (decimal) | 0.68 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.31 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-06-17 | 1998-06-27 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.81 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.23 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.89 | [7 empty] | Feed flow rate during sample collection (mL/min) | 17.52 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 302 | [10 empty] | Influent flow rate during sample collection (mL/min) | 302 | [7 empty] | Influent flow rate during sample collection (mL/min) | 302 | [7 empty] | Influent flow rate during sample collection (mL/min) | 302 | [6 empty] | SDS-THM4F, ug/L | 154.1 | 154.1 | 154.1 | 154.1 | SDS-THM4F, ug/L | 154.1 | 154.1 | 154.1 | 154.1 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 240 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 19.15 | 28.1 | 16.6 | 13 | SDS-THM4p, ug/L | 19.15 | 28.1 | 16.6 | 13 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.78 | 8.02 | 7.9 | 3.038 | 1998-06-15 | 15:30 | 0 | 24 | 65 | 65 | 263 | 7.47 | 0.65 | 8.12 | 0.18158 | 0.91995 | 31.3892 | 17.0499 | 17.355 | 0 | 0 | 0 | 0 | 65 | 0.267 | 1998-06-17 | 9:00 | 0 | 24 | 57 | 56 | 302 | 6.74 | 2.98 |  | 9.72 | 0.2085 | 0.69342 | 30.07 | 15.3837 | 15.659 | 450.3466 | 209.01 | 444.9605 | 2.3864 | 54.1136 | 0.28937 | 7.75 | 7.57 | 7.81 | 53 | 271 | 51 | 803.2013 | -1474.9046 | 81.2721 | 794.8299 | 93.3319 | BMRL | 0.152 | 0.013 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 61 | 61 | 61 | 61 | SDS-HAA5F, ug/L | 61 | 61 | 61 | 61 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-06-15 | 15:45 | 0.25 | 24 | 65 | 65 | 263 | 7.4 | 1.22 | 8.62 | 0.18158 | 0.85847 | 29.5104 | 16.8901 | 17.1923 | 0 | 0 | 0 | 0 | 65 | 0.2645 | 1998-06-17 | 10:00 | 1 | 24 | 57 | 56 | 302 | 6.23 | 3.11 |  | 9.34 | 0.2085 | 0.66702 | 31.334 | 14.2196 | 14.4741 | 440.2377 | 204.5073 | 435.3748 | 2.333 | 54.167 | 0.26721 | 7.64 | 7.6 | 7.81 | 180 | 269 | 356 | 489.3312 | -37.4526 | 36.3958 | 486.1406 | 62.9737 | BMRL | 0.151 | 0.207 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.1 | 3.9 | 1.5 | 1 | SDS-HAA5p, ug/L | 2.1 | 3.9 | 1.5 | 1 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 212 | 312 | 262 | 38.1679 | 1998-06-15 | 16:15 | 0.75 | 24 | 65 | 61 | 263 | 7.6 | 1.9 | 9.5 | 0.18158 | 0.8 | 26.6842 | 17.3466 | 17.657 | 0 | 0 | 0 | 0 | 63 | 0.28027 | 1998-06-17 | 11:00 | 2 | 24 | 57 | 56 | 302 | 5.75 | 3.73 |  | 9.48 | 0.2085 | 0.60654 | 30.8565 | 13.1241 | 13.3589 | 418.9702 | 194.7967 | 414.702 | 2.2204 | 54.2796 | 0.24611 | 7.64 | 7.62 | 7.81 | 201 | 269 | 385 | 409.4075 | -6.3396 | 28.9753 | 407.4235 | 50.6656 | BMRL | 0.15 | 0.267 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-06-18 | 1998-06-19 | --- | --- | 1998-06-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-20 | 1998-06-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-23 | 1998-06-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-24 | 1998-06-24 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 387.5 | 387.5 | 387.5 | 387.5 | SDS-TOXF, ug Cl- /L | 387.5 | 387.5 | 387.5 | 387.5 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 276 | 290 | 283 | 4.947 | 1998-06-15 | 16:45 | 1.25 | 24 | 60 | 62 | 263 | 7.27 | 4.16 | 11.43 | 0.18158 | 0.63605 | 22.0096 | 16.5934 | 16.8903 | 0 | 0 | 0 | 0 | 61 | 0.27689 | 1998-06-17 | 12:00 | 3 | 24 | 55 | 54 | 302 | 6.1 | 2.37 |  | 8.47 | 0.2085 | 0.72019 | 34.6553 | 13.9229 | 14.1721 | 460.5781 | 214.0066 | 455.5977 | 2.4408 | 52.0592 | 0.27223 | 7.65 | 7.61 | 7.84 | 215 | 269 | 406 | 458.0211 | -12.8131 | 24.0283 | 455.5667 | 52.806 | BMRL | 0.148 | 0.323 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 9:30 | 10:00 | --- | --- | 9:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:00 | 20:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:15 | 8:15 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 28 | 38 | BMRL | BMRL | SDS-TOXp, ug Cl- /L | 28 | 38 | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 242 | 306 | 274 | 23.3577 | 1998-06-16 | 10:45 | 19.25 | 24 | 60 | 58 | 263 | 6.97 | 2.88 | 9.85 | 0.18158 | 0.70761 | 25.7005 | 15.9087 | 16.1933 | 0 | 0 | 0 | 0 | 59 | 0.27446 | 1998-06-17 | 13:45 | 4.75 | 24.1 | 55 | 56 | 302 | 6 | 2.76 |  | 8.76 | 0.2085 | 0.68493 | 33.4749 | 13.6947 | 13.8986 | 446.8106 | 207.6471 | 442.059 | 2.3679 | 53.1321 | 0.26159 | 7.64 | 7.62 | 7.85 | 204 | 269 | 405 | 454.7391 | -12.2813 | 27.9152 | 452.2483 | 54.892 | BMRL | 0.15 | 0.369 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 24.5 | 49 | --- | --- | 24.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 83 | 83 | --- | --- | --- | --- | --- | Operation time | hh.hh | 148 | 148 | --- | --- | --- | --- | --- | Cumulative time | hr | 167.25 | 167.25 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 3.58 | 3.58 | 3.58 | 3.58 | SDS-CDF, mg/L | 3.58 | 3.58 | 3.58 | 3.58 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 236 | 286 | 261 | 19.1571 | 1998-06-16 | 11:30 | 20 | 24 | 56 | 54 | 263 | 6.67 | 4.27 | 10.94 | 0.18158 | 0.60969 | 23.0402 | 15.2239 | 15.4963 | 0 | 0 | 0 | 0 | 55 | 0.28175 | 1998-06-17 | 15:00 | 6 | 24.1 | 55 | 53 | 302 | 6.13 | 2.73 |  | 8.86 | 0.2085 | 0.69187 | 33.0858 | 13.9914 | 14.1997 | 449.5014 | 208.8485 | 444.6166 | 2.3821 | 51.6179 | 0.27509 | 7.65 | 7.65 | 7.86 | 194 | 269 | 402 | 482.8425 | -20.1101 | 31.4488 | 479.911 | 59.5758 | BMRL | 0.151 | 0.38 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.82 | 8.06 | 7.94 | 3.0227 | 8.09 | --- | --- | --- | --- | --- | pH | --- | 8.13 | 8.45 | --- | --- | --- | --- | --- | pH | --- | 8.17 | 8.47 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.35 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.67 | 1.46 | 1 | 0.85 | SDS-CDp, mg/L | 1.67 | 1.46 | 1 | 0.85 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.15 | 0.147 | 0.1485 | 2.0202 | 1998-06-16 | 12:15 | 20.75 | 24 | 58 | 56 | 263 | 6.69 | 2.42 | 9.11 | 0.18158 | 0.73436 | 27.8694 | 15.2696 | 15.5428 | 0 | 0 | 0 | 0 | 57 | 0.27268 | 1998-06-17 | 16:00 | 7 | 24.1 | 55 | 53 | 302 | 5.98 | 2.78 |  | 8.76 | 0.2085 | 0.68265 | 33.4749 | 13.649 | 13.8523 | 445.9421 | 207.251 | 441.2157 | 2.3633 | 51.6367 | 0.26826 | 7.59 | 7.58 | 7.82 | 203 | 269 | 410 | 455.0863 | -10.9967 | 28.2686 | 452.5905 | 55.1471 | BMRL | 0.151 | 0.388 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 4 | 4 | 4 | 4 | TOCF, mg/L | 4 | 4 | 4 | 4 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.13 | BMRL | 0.13 | #VALUE! | 1998-06-16 | 13:15 | 21.75 | 24 | 55 | 54 | 263 | 6.71 | 3.01 | 9.72 | 0.18158 | 0.69033 | 26.0576 | 15.3152 | 15.5893 | 0 | 0 | 0 | 0 | 54.5 | 0.28604 | 1998-06-17 | 17:00 | 8 | 24 | 54 | 53 | 302 | 6.09 | 2.76 |  | 8.85 | 0.2085 | 0.68814 | 33.1243 | 13.9001 | 14.1488 | 448.0607 | 208.1942 | 443.2237 | 2.3745 | 51.1255 | 0.27675 | [27 empty] | Alkalinity | mg/L as CaCO3 | 168 | 172 | 170 | 2.3529 | 304 | 457.5 | -50.4934 | 35.1145 | 454.6484 | 62.6085 | Alkalinity | mg/L as CaCO3 | 210 | 430 | 730 | -69.7674 | 19.8473 | 725.1728 | 71.0414 | Alkalinity | mg/L as CaCO3 | 162 | 382 | 366.0816 | 4.1671 | 38.1679 | 364.2051 | 55.5196 | Alkalinity | mg/L as CaCO3 | 226 | 250 | 278.1739 | -11.2696 | 13.7405 | 277.7048 | 18.6186 | TOCp, mg/L | #DIV/0! | 0.6 | BMRL | BMRL | TOCp, mg/L | #DIV/0! | 0.6 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 3.9 | 4.1 | 4 | 5 | 1998-06-16 | 14:15 | 22.75 | 24 | 55 | 54 | 263 | 6.69 | 2.72 | 9.41 | 0.18158 | 0.71095 | 26.949 | 15.2696 | 15.5428 | 0 | 0 | 0 | 0 | 54.5 | 0.28519 | 1998-06-18 | 8:30 | 23.5 | 24 | 55 | 54 | 302 | 6.17 | 2.8 |  | 8.97 | 0.2085 | 0.68785 | 32.6678 | 14.0827 | 14.3347 | 447.9845 | 208.1286 | 443.0841 | 2.3741 | 52.1259 | 0.275 | [27 empty] | Total dissolved solids | mg/L | 196 | 247 | 221.5 | 23.0248 | 412 | 413.6875 | -0.40959 | 21.7314 | 411.7813 | 46.2093 | Total dissolved solids | mg/L | 238 | 530 | 688 | -29.8113 | 15.9011 | 683.8226 | 65.1957 | Total dissolved solids | mg/L | 211 | 340 | 357.9388 | -5.2761 | 25.4417 | 356.5876 | 40.828 | Total dissolved solids | mg/L | 189 | 314 | 325.2319 | -3.577 | 33.2155 | 324.0069 | 41.6679 | UV254 F, cm-1 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | UV254 F, cm-1 | 0.1335 | 0.1335 | 0.1335 | 0.1335 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.136 | 0.131 | 0.1335 | 3.7453 | 1998-06-16 | 16:30 | 25 | 24 | 55 | 56 | 263 | 6.92 | 2.54 | 9.46 | 0.18158 | 0.7315 | 26.8013 | 15.7945 | 16.0771 | 0 | 0 | 0 | 0 | 55.5 | 0.28968 | 1998-06-18 | 9:30 | 24.5 | 24.5 | 55 | 54 | 302 | 6.18 | 2.75 |  | 8.93 | 0.2085 | 0.69205 | 32.8186 | 14.1055 | 14.1473 | 449.5894 | 208.8704 | 444.6634 | 2.3826 | 52.1174 | 0.27145 | 7.58 | 7.56 | 7.78 | 211 | 269 | 404 | 444.8036 | -10.0999 | 25.4417 | 442.4114 | 52.3068 | BMRL | 0.149 | 0.416 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 164 | 162 | 163 | 1.227 | 422 | 509.875 | -20.8235 | 40.5109 | 506.4345 | 67.8142 | Total hardness | mg/L as CaCO3 | 202 | 584 | 922 | -57.8767 | 26.2774 | 915.3162 | 77.9311 | Total hardness | mg/L as CaCO3 | 158 | 350 | 394.7347 | -12.7813 | 42.3358 | 392.5579 | 59.7512 | Total hardness | mg/L as CaCO3 | 156 | 316 | 327.0145 | -3.4856 | 43.0657 | 325.4767 | 52.0703 | UV254 p, cm-1 | #DIV/0! | 0.013 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.013 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.4872 | 3.1951 | 3.3412 | 8.7412 | 1998-06-16 | 18:00 | 26.5 | 24 | 56 | 54 | 263 | 6.83 | 3.9 | 10.73 | 0.18158 | 0.63653 | 23.5107 | 15.5891 | 15.8681 | 0 | 0 | 0 | 0 | 55 | 0.28851 | 1998-06-18 | 10:30 | 25.5 | 24.4 | 55 | 54 | 302 | 6.1 | 2.8 |  | 8.9 | 0.2085 | 0.68539 | 32.9326 | 13.9229 | 14.0055 | 447.0257 | 207.7095 | 442.1919 | 2.369 | 52.131 | 0.26866 | 7.58 | 7.56 | 7.75 | 209 | 269 | 403 | 444.2143 | -10.2269 | 26.1484 | 441.8388 | 52.6977 | BMRL | 0.15 | 0.411 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 158 | 156 | 157 | 1.2739 | 406 | 482 | -18.7192 | 39.8467 | 478.7765 | 67.2081 | Calcium hardness | mg/L as CaCO3 | 186 | 572 | 936 | -63.6364 | 28.7356 | 929.0377 | 79.9793 | Calcium hardness | mg/L as CaCO3 | 132 | 334 | 395.2653 | -18.3429 | 49.4253 | 392.8445 | 66.3989 | Calcium hardness | mg/L as CaCO3 | 124 | 294 | 322.5507 | -9.7111 | 52.4904 | 320.7653 | 61.3425 | BromideF, ug/L | 62 | 62 | 62 | 62 | BromideF, ug/L | 62 | 62 | 62 | 62 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 62 | 62 | 62 | 0 | 1998-06-17 | 8:00 | 40.5 | 24 | 56 | 54 | 263 | 6.87 | 2.97 | 9.84 | 0.18158 | 0.69817 | 25.7276 | 15.6804 | 15.961 | 0 | 0 | 0 | 0 | 55 | 0.2902 | 1998-06-18 | 11:30 | 26.5 | 24.5 | 55 | 54 | 302 | 6 | 2.76 |  | 8.76 | 0.2085 | 0.68493 | 33.4749 | 13.6947 | 13.7352 | 446.8106 | 207.6471 | 442.059 | 2.3679 | 52.1321 | 0.26347 | 7.57 | 7.57 | 7.78 | 218 | 269 | 397 | 424.3043 | -6.8777 | 22.9682 | 422.255 | 48.3724 | BMRL | 0.145 | 0.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.044 | 0.045 | 0.0445 | 2.2472 | 0.237 | 0.3695 | -55.9072 | 70.0337 | 0.36628 | 87.8507 | Turbidity | ntu | 0.052 | 0.796 | 1.017 | -27.7638 | 64.9832 | 1.008 | 94.8415 | Turbidity | ntu | 0.053 | 0.663 | 0.2479 | 62.6097 | 64.3098 | 0.24611 | 78.4645 | Turbidity | ntu | 0.044 | 0.753 | 0.19545 | 74.0439 | 70.3704 | 0.19409 | 77.3298 | Bromidep, ug/L | 57.5 | 64 | 58 | 57 | Bromidep, ug/L | 57.5 | 64 | 58 | 57 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-18 | 13:30 | 28.5 | 24.6 | 55 | 54 | 302 | 5.88 | 2.78 |  | 8.66 | 0.2085 | 0.67898 | 33.873 | 13.4208 | 13.4208 | 444.5282 | 206.6312 | 439.8963 | 2.3558 | 52.1442 | 0.25738 | 7.61 | 7.58 | 7.77 | 220 | 269 | 404 | 416.2518 | -3.0326 | 22.2615 | 414.3413 | 46.9037 | BMRL | 0.149 | 0.402 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.2 | 0.21 | 0.205 | 4.878 | NA | -0.029375 | #VALUE! | -57.6923 | -0.02705 | 857.8463 | Ammonia | mg NH3-N / L | 0.11 | NA | 0.31 | #VALUE! | 15.3846 | 0.30814 | 64.3023 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 262 | 262 | 262 | 262 | AlkF, mg/L CaCO3 | 262 | 262 | 262 | 262
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.49 | 1.35 | 1.42 | 9.8592 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-18 | 14:00 | 29 | 24.5 | 55 | 54 | 302 | 5.88 | 2.8 |  | 8.68 | 0.2085 | 0.67742 | 33.7926 | 13.4208 | 13.4605 | 443.9444 | 206.3598 | 439.3186 | 2.3527 | 52.1473 | 0.25812 | 7.61 | 7.6 | 7.82 | 217 | 269 | 399 | 421.6 | -5.6642 | 23.3216 | 419.6082 | 48.2851 | BMRL | 0.149 | 0.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 11.7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 0.6 | 32.4 | 34.6 | -6.7901 | 85 | 34.2844 | 98.2499 | Total organic carbon | mg/L | BMRL | 7.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 170 | 210 | 162 | 226 | Alkp, mg/L CaCO3 | 170 | 210 | 162 | 226
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.51 | 3.65 | 3.58 | 3.9106 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-18 | 15:00 | 30 | 24 | 55 | 53 | 302 | 6.03 | 2.76 |  | 8.79 | 0.2085 | 0.68601 | 33.3572 | 13.7632 | 14.0094 | 447.2293 | 207.8304 | 442.4492 | 2.3701 | 51.6299 | 0.27134 | 7.6 | 7.52 | 7.87 | 215 | 269 | 394 | 431.5652 | -9.5343 | 24.0283 | 429.4032 | 49.9305 | BMRL | 0.148 | 0.402 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.39 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.013 | 1.102 | 1.218 | -10.5263 | 90.2622 | 1.2068 | 98.9228 | UV254 | cm-1 | BMRL | 0.262 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.195 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 274 | 274 | 274 | 274 | T-HdF, mg/L CaCO3 | 274 | 274 | 274 | 274
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-18 | 16:30 | 31.5 | 24.9 | 55 | 53 | 302 | 5.98 | 2.76 |  | 8.74 | 0.2085 | 0.68421 | 33.5538 | 13.649 | 13.5285 | 446.5305 | 207.5244 | 441.7978 | 2.3664 | 51.6336 | 0.26201 | 7.65 | 7.61 | 7.82 | 223 | 269 | 392 | 413 | -5.3571 | 21.2014 | 411.1189 | 45.7578 | BMRL | 0.146 | 0.401 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.3333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.1667 | 3.4012 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.3165 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.3051 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 163 | 202 | 158 | 156 | T-Hdp, mg/L CaCO3 | 163 | 202 | 158 | 156
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.07 | 8.26 | 8.165 | 2.327 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-19 | 9:00 | 48 | 24 | 56 | 55 | 302 | 6.13 | 2.87 |  | 9 | 0.2085 | 0.68111 | 32.5556 | 13.9914 | 14.2418 | 445.4249 | 206.9544 | 440.5844 | 2.3605 | 53.1395 | 0.26801 | [27 empty] | Bromide | mg/L | 58 | 57 | 57.5 | 1.7391 | --- | 71.5625 | --- | 7.2581 | 71.423 | 19.4937 | Bromide | mg/L | 64 | --- | 44 | --- | -3.2258 | 44.1857 | -44.8434 | Bromide | mg/L | 58 | --- | 66.1633 | --- | 6.4516 | 66.0882 | 12.2385 | Bromide | mg/L | 57 | --- | 64.2464 | --- | 8.0645 | 64.1812 | 11.189 | Ca-HdF, mg/L CaCO3 | 261 | 261 | 261 | 261 | Ca-HdF, mg/L CaCO3 | 261 | 261 | 261 | 261
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-19 | 10:00 | 49 | 24 | 57 | 56 | 302 | 6.2 | 2.82 |  | 9.02 | 0.2085 | 0.68736 | 32.4812 | 14.1512 | 14.4044 | 447.8119 | 208.0371 | 442.8894 | 2.3731 | 54.1269 | 0.26612 | 7.64 | 7.63 | 7.85 | 210 | 269 | 394 | 443.4965 | -12.5626 | 25.7951 | 441.0996 | 52.3917 | BMRL | 0.152 | 0.412 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 3 | 2.75 | 18.1818 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 157 | 186 | 132 | 124 | Ca-Hdp, mg/L CaCO3 | 157 | 186 | 132 | 124
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 385 | 390 | 387.5 | 1.2903 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-19 | 11:00 | 50 | 24.3 | 57 | 56 | 302 | 6.19 | 2.8 |  | 8.99 | 0.2085 | 0.68854 | 32.5929 | 14.1283 | 14.2542 | 448.2565 | 208.2475 | 443.3371 | 2.3755 | 54.1245 | 0.26336 | 7.7 | 7.65 | 7.83 | 199 | 269 | 397 | 468.7 | -18.0605 | 29.682 | 465.936 | 57.2903 | BMRL | 0.147 | 0.408 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.31 | 0.85 | 1.08 | 42.5926 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.04 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.65 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 120 | 120 | 120 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-19 | 12:00 | 51 | 24 | 57 | 56 | 302 | 6.13 | 2.82 |  | 8.95 | 0.2085 | 0.68492 | 32.743 | 13.9914 | 14.2418 | 446.8577 | 207.6201 | 442.0016 | 2.3681 | 54.1319 | 0.26309 | 7.71 | 7.63 | 7.88 | 194 | 269 | 393 | 476.4645 | -21.2378 | 31.4488 | 473.5978 | 59.037 | BMRL | 0.151 | 0.407 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 1.19 | 2.15 | 1.67 | 57.485 | --- | 7.6387 | --- | 53.352 | 7.5795 | 77.967 | SDS-Cl2 demand | mg/L | 1.46 | --- | 22.66 | --- | 59.2179 | 22.4632 | 93.5005 | SDS-Cl2 demand | mg/L | 1 | --- | 6.2653 | --- | 72.067 | 6.2169 | 83.9148 | SDS-Cl2 demand | mg/L | 0.85 | --- | 4.8065 | --- | 76.257 | 4.7709 | 82.1838 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 27 | 28 | 27.5 | 3.6364 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-19 | 15:15 | 54.25 | 24 | 57 | 55 | 302 | 5.95 | 2.85 |  | 8.8 | 0.2085 | 0.67614 | 33.3182 | 13.5806 | 13.8236 | 443.4944 | 206.1246 | 438.8177 | 2.3503 | 53.6497 | 0.25766 | 7.7 | 7.63 | 7.83 | 204 | 269 | 396 | 447.9298 | -13.1136 | 27.9152 | 445.5269 | 54.2115 | BMRL | 0.146 | 0.398 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 60.8373 | 65.1587 | 59.7091 | 58.1857 | Qp/QT (THM4), % | 87.5139 | 93.7302 | 85.8909 | 83.6995
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 6.5 | 6.7 | 6.6 | 3.0303 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-19 | 16:15 | 55.25 | 24 | 57 | 56 | 302 | 6.03 | 2.66 |  | 8.69 | 0.2085 | 0.6939 | 33.7526 | 13.7632 | 14.0094 | 450.2359 | 209.2276 | 445.4238 | 2.386 | 54.114 | 0.25889 | 7.7 | 7.66 | 7.89 | 200 | 269 | 401 | 471.1541 | -17.4948 | 29.3286 | 468.4471 | 57.3057 | BMRL | 0.149 | 0.404 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 7.82 | 8.26 | 8.04 | 5.4726 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.16 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.27 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.21 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 11:00 | 74 | 24 | 56 | 55 | 302 | 6.09 | 2.2 |  | 8.29 | 0.2085 | 0.73462 | 35.4294 | 13.9001 | 14.1488 | 466.4381 | 216.7333 | 461.4027 | 2.4719 | 53.0281 | 0.26682 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 25.1668 | 23.7944 | 25.4731 | 26.0886 | SDS-HAA5b, ug/L | 9.4543 | 7.4801 | 9.8949 | 10.7803
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 153.5 | 154.7 | 154.1 | 0.77872 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 12:00 | 75 | 24 | 56 | 55 | 302 | 6.23 | 3.2 |  | 9.43 | 0.2085 | 0.66066 | 31.0255 | 14.2196 | 14.4741 | 437.9156 | 203.4286 | 433.0783 | 2.3207 | 53.1793 | 0.27218 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | 28 | 28 | #VALUE! | --- | 1151.4375 | --- | 92.7742 | 1140.2946 | 97.5445 | SDS-TOX | mg Cl- /L | 38 | --- | 3533 | --- | 90.1935 | 3500.5555 | 98.9145 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 168.7897 | 159.7702 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 72.8876 | 59.9131 | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 3.6 | 2.7 | 3.15 | 28.5714 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 12:30 | 75.5 | 26.7 | 56 | 55 | 302 | 6.25 | 2.6 |  | 8.85 | 0.2085 | 0.70621 | 33.1243 | 14.2653 | 13.4067 | 455.103 | 211.4052 | 450.0596 | 2.4118 | 53.0882 | 0.25254 | 7.81 | 7.78 | 7.95 | 248 | 269 | 397 | 367.1346 | 7.5228 | 12.3675 | 365.9018 | 32.2223 | BMRL | 0.138 | 0.437 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 6 | 7.1 | 6.55 | 16.7939 | --- | 361.0813 | --- | 94.5417 | 357.5648 | 98.1682 | SDS-CHCl3 | mg/L | 8.3 | --- | 1125.3 | --- | 93.0833 | 1114.9308 | 99.2556 | SDS-CHCl3 | mg/L | 4.7 | --- | 240.0061 | --- | 96.0833 | 237.8424 | 98.0239 | SDS-CHCl3 | mg/L | 4.4 | --- | 171.9362 | --- | 96.3333 | 170.4297 | 97.4183 | SDS-CDb, mg/L | 2.418 | 2.1986 | 2.0395 | 1.9915 | SDS-CDb, mg/L | 1.9085 | 1.5929 | 1.364 | 1.295
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 30 | 33 | 31.5 | 9.5238 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 13:30 | 76.5 | 24 | 56 | 55 | 302 | 6.28 | 2.37 |  | 8.65 | 0.2085 | 0.72601 | 33.9133 | 14.3338 | 14.5902 | 463.0098 | 215.0664 | 457.8539 | 2.4537 | 53.0463 | 0.27505 | 7.75 | 7.74 | 7.93 | 206 | 269 | 400 | 487.0338 | -21.7584 | 27.2085 | 484.1117 | 57.4478 | BMRL | 0.138 | 0.433 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 3.3 | 3.4 | 3.35 | 2.9851 | --- | 78.8187 | --- | 87.8182 | 78.0702 | 95.709 | SDS-BDCM | mg/L | 5.9 | --- | 221.9 | --- | 78.5455 | 219.8948 | 97.3169 | SDS-BDCM | mg/L | 3.1 | --- | 52.8959 | --- | 88.7273 | 52.438 | 94.0883 | SDS-BDCM | mg/L | 2.3 | --- | 38.8217 | --- | 91.6364 | 38.4933 | 94.0249 | TOCb, mg/L | #DIV/0! | 1.7846 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 0.81317 | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 14:00 | 77 | 24 | 56 | 55 | 302 | 6.29 | 2.33 |  | 8.62 | 0.2085 | 0.7297 | 34.0348 | 14.3566 | 14.6135 | 464.5149 | 215.7616 | 459.3339 | 2.4616 | 53.0384 | 0.27553 | 7.71 | 7.69 | 7.92 | 202 | 269 | 398 | 501.6652 | -26.0465 | 28.6219 | 498.5446 | 59.4821 | BMRL | 0.143 | 0.421 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 6.2 | 5.3 | 5.75 | 15.6522 | --- | 8.4062 | --- | 12.8788 | 8.3799 | 31.3835 | SDS-DBCM | mg/L | 9.3 | --- | -17.7 | --- | -40.9091 | -17.4494 | 153.2971 | SDS-DBCM | mg/L | 5.7 | --- | 7.5367 | --- | 13.6364 | 7.5198 | 24.2006 | SDS-DBCM | mg/L | 4.1 | --- | 7.7232 | --- | 37.8788 | 7.6906 | 46.6882 | UV254 b, cm-1 | #DIV/0! | 0.054984 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.020555 | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 15:00 | 78 | 24 | 57 | 55 | 302 | 6.28 | 0.18 |  | 6.46 | 0.2085 | 0.97214 | 45.7492 | 14.3338 | 14.5902 | 590.2997 | 274.192 | 583.7263 | 3.1282 | 52.8718 | 0.27596 | 7.93 | 7.83 | 7.99 | 223 | 269 | 429 | 2376.3333 | -453.9239 | 21.2014 | 2353.9444 | 90.5265 | BMRL | 0.138 | 0.49 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 4.1 | 2.9 | 3.5 | 34.2857 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 59.2623 | 63.3032 | 59.6116 | 59.0907 | Bromideb, ug/L | 58.0619 | 63.8746 | 58.5644 | 57.815
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.3 | 1.4 | 1.35 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 15:30 | 78.5 | 24 | 57 | 55 | 302 | 6.27 | 0.18 |  | 6.45 | 0.2085 | 0.97209 | 45.8217 | 14.3109 | 14.567 | 590.2611 | 274.1791 | 583.6987 | 3.128 | 52.872 | 0.27551 | 7.87 | 7.76 | 8 | 213 | 269 | 457 | 2721.3333 | -495.4778 | 24.735 | 2695.2948 | 92.0973 | BMRL | 0.143 | 0.597 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 19.6 | 18.7 | 19.15 | 4.6997 | --- | 440.8687 | --- | 87.573 | 436.6859 | 95.6147 | SDS-THM4 | mg/L | 28.1 | --- | 1288.1 | --- | 81.7651 | 1276.4033 | 97.7985 | SDS-THM4 | mg/L | 16.6 | --- | 297.2122 | --- | 89.2278 | 294.632 | 94.3659 | SDS-THM4 | mg/L | 13 | --- | 217.4928 | --- | 91.5639 | 215.6539 | 93.9718 | Alkb, mg/L CaCO3 | 206.0296 | 228.1175 | 202.2909 | 241.0532 | Alkb, mg/L CaCO3 | 181.4872 | 213.2603 | 176.1091 | 231.8682
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 8 | 7.9 | 7.95 | 1.2579 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 16:30 | 79.5 | 24 | 56 | 55 | 302 | 6.18 | 0.71 |  | 6.89 | 0.2085 | 0.89695 | 42.8316 | 14.1055 | 14.3579 | 544.488 | 252.9585 | 538.5223 | 2.8855 | 52.6145 | 0.27289 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 206.4705 | 227.0857 | 204.7375 | 205.3409 | T-Hdb, mg/L CaCO3 | 176.8596 | 206.5143 | 174.3665 | 175.2346
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 17:30 | 80.5 | 24 | 56 | 54 | 302 | 6.05 | 0.53 |  | 6.58 | 0.2085 | 0.91945 | 44.8967 | 13.8088 | 14.0559 | 557.2978 | 258.9706 | 551.3214 | 2.9534 | 52.0466 | 0.27006 | [27 empty] | SDS-DCAA* | mg/L | BMRL | 1.2 | 1.2 | #VALUE! | --- | 95.8875 | --- | 96.1905 | 94.9483 | 98.7362 | SDS-DCAA* | mg/L | 1.4 | --- | 302.4 | --- | 95.5556 | 299.6058 | 99.5327 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 197.7292 | 212.131 | 183.9753 | 181.2856 | Ca-Hdb, mg/L CaCO3 | 169.9856 | 190.7024 | 150.2007 | 146.3317
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 18:30 | 81.5 | 24 | 56 | 54 | 302 | 6.03 | 1.68 |  | 7.71 | 0.2085 | 0.7821 | 38.1699 | 13.7632 | 14.0094 | 486.801 | 226.2196 | 481.598 | 2.5798 | 52.4202 | 0.26725 | [27 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 7.5 | 6.1 | 6.8 | 20.5882 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 19:00 | 82 | 24 | 56 | 54 | 302 | 6.14 | 0.7 |  | 6.84 | 0.2085 | 0.89766 | 43.152 | 14.0142 | 14.265 | 544.8542 | 253.1469 | 538.9234 | 2.8874 | 52.1126 | 0.27373 | 7.89 | 7.76 | 8 | 221 | 269 | 473 | 826.8286 | -74.8052 | 21.9081 | 820.67 | 73.0708 | BMRL | 0.144 | 0.697 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 59.9 | 62.1 | 61 | 3.6066 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 20:00 | 83 | 24 | 56 | 54 | 302 | 6.16 | 0.54 |  | 6.7 | 0.2085 | 0.9194 | 44.0746 | 14.0599 | 14.3115 | 557.3618 | 258.9488 | 551.275 | 2.9537 | 52.0463 | 0.27498 | 7.78 | 7.73 | 7.94 | 224 | 269 | 484 | 956.037 | -97.5283 | 20.8481 | 948.5712 | 76.3855 | [16 empty] | SDS-DBAA* | mg/L | 1.7 | 1.3 | 1.5 | 26.6667 | --- | 1.0312 | --- | -11.1111 | 1.0359 | -44.8017 | SDS-DBAA* | mg/L | 2.5 | --- | -9 | --- | -85.1852 | -8.8932 | 128.1112 | SDS-DBAA* | mg/L | 1.5 | --- | 1.1939 | --- | -11.1111 | 1.1967 | -25.3455 | SDS-DBAA* | mg/L | 1 | --- | 1.5072 | --- | 25.9259 | 1.5027 | 33.4525 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 67.9 | 70 | 68.95 | 3.0457 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-20 | 21:00 | 84 | 24 | 56 | 54 | 302 | 6.15 | 0.5 |  | 6.65 | 0.2085 | 0.92481 | 44.4135 | 14.037 | 14.2882 | 560.5504 | 260.4349 | 554.4388 | 2.9706 | 52.0294 | 0.27462 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.6 | --- | 65.1 | --- | 79.8742 | 64.5105 | 97.5198 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 11.8846 | 12.2592 | 11.7647 | 11.6667 | Qp/QT (HAA5), % | 57.725 | 59.5447 | 57.1429 | 56.6667
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-21 | 11:00 | 98 | 24 | 55 | 54 | 302 | 5.63 | 0.63 |  | 6.26 | 0.2085 | 0.89936 | 47.2428 | 12.8502 | 13.0801 | 545.4054 | 253.6367 | 539.9661 | 2.8905 | 51.6095 | 0.25344 | [27 empty] | SDS-TBAA | mg/L | NR | NR | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 138.0618 | 138.6534 | 137.9235 | 137.6383 | SDS-THM4b, ug/L | 76.2002 | 79.0737 | 75.5286 | 74.1433
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-21 | 12:00 | 99 | 24 | 55 | 54 | 302 | 5.63 | 0.42 |  | 6.05 | 0.2085 | 0.93058 | 48.9174 | 12.8502 | 13.0801 | 563.5429 | 262.0714 | 557.9227 | 2.9866 | 51.5134 | 0.25392 | [27 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-21 | 13:00 | 100 | 24 | 55 | 51 | 302 | 5.6 | 0.77 |  | 6.37 | 0.2085 | 0.87912 | 46.4097 | 12.7817 | 13.0104 | 534.2346 | 248.4552 | 528.9353 | 2.8313 | 50.1687 | 0.25933 | [27 empty] | SDS-DCBAA | mg/L | 1 | 1 | 1 | 0 | --- | 19.125 | --- | 85.2941 | 18.9452 | 94.7216 | SDS-DCBAA | mg/L | 1.5 | --- | 54.5 | --- | 77.9412 | 54.008 | 97.2226 | SDS-DCBAA | mg/L | 1 | --- | 12.8367 | --- | 85.2941 | 12.7279 | 92.1432 | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 344.775 | 344.6541 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 179.9788 | 179.3914 | #VALUE! | #VALUE!
[44 empty] | 1998-06-22 | 8:00 | 119 | 24 | 54 | 53 | 302 | 5.63 | 1.61 |  | 7.24 | 0.2085 | 0.77762 | 40.7127 | 12.8502 | 13.0801 | 484.5857 | 225.3529 | 479.7529 | 2.5682 | 50.9318 | 0.25682 | [27 empty] | SDS-HAA5 | mg/L | 1.7 | 2.5 | 2.1 | 38.0952 | --- | 186.1625 | --- | 96.5574 | 184.3369 | 98.8608 | SDS-HAA5 | mg/L | 3.9 | --- | 574.9 | --- | 93.6066 | 569.5993 | 99.3153 | SDS-HAA5 | mg/L | 1.5 | --- | 122.9286 | --- | 97.541 | 121.812 | 98.7686 | SDS-HAA5 | mg/L | 1 | --- | 87.9565 | --- | 98.3607 | 87.1746 | 98.8529 | SDS-CDb, mg/L | 3.353 | 3.3201 | 3.2765 | 3.2615 | SDS-CDb, mg/L | 2.4775 | 2.3177 | 2.1057 | 2.033
[44 empty] | 1998-06-22 | 8:30 | 119.5 | 24 | 55 | 53 | 302 | 5.7 | 0.61 |  | 6.31 | 0.2085 | 0.90333 | 46.8605 | 13.0099 | 13.2427 | 547.7015 | 254.6723 | 542.1708 | 2.9026 | 51.0974 | 0.25917 | [27 empty] | SDS-HAA6 | mg/L | 1.7 | 2.5 | 2.1 | 38.0952 | --- | 211.0062 | --- | 96.9543 | 208.9342 | 98.9949 | SDS-HAA6 | mg/L | 5.5 | --- | 640 | --- | 92.0232 | 634.1099 | 99.1326 | SDS-HAA6 | mg/L | 1.5 | --- | 139.1531 | --- | 97.8245 | 137.8873 | 98.9122 | SDS-HAA6 | mg/L | 1 | --- | 99.4783 | --- | 98.5497 | 98.5927 | 98.9857 | TOCb, mg/L | #DIV/0! | 3.5832 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 1.9755 | #VALUE! | #VALUE!
[44 empty] | 1998-06-22 | 9:00 | 120 | 24 | 55 | 53 | 302 | 5.75 | 0.47 |  | 6.22 | 0.2085 | 0.92444 | 47.5531 | 13.1241 | 13.3589 | 559.9833 | 260.3596 | 554.2785 | 2.9677 | 51.0323 | 0.26177 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.11873 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.061749 | #VALUE! | #VALUE!
[44 empty] | 1998-06-22 | 10:00 | 121 | 24 | 55 | 53 | 302 | 5.68 | 0.59 |  | 6.27 | 0.2085 | 0.9059 | 47.1659 | 12.9643 | 13.1963 | 549.1484 | 255.3543 | 543.6227 | 2.9103 | 51.0897 | 0.2583 | 8.01 | 7.62 | 7.9 | 223 | 269 | 494 | 860.6271 | -74.216 | 21.2014 | 854.6309 | 73.9069 | 0.011 | 0.139 | 0.884 | 1.3128 | -48.5093 | 91.7603 | 1.3006 | 99.1542 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 61.4652 | 62.2452 | 61.5294 | 61.4167 | Bromideb, ug/L | 59.4024 | 63.1909 | 59.7143 | 59.1667
[44 empty] | 1998-06-22 | 11:00 | 122 | 24 | 54 | 53 | 302 | 5.55 | 0.48 |  | 6.03 | 0.2085 | 0.9204 | 49.0829 | 12.6676 | 12.8942 | 557.4289 | 259.2656 | 551.9495 | 2.9542 | 50.5458 | 0.2551 | 7.77 | 7.73 | 7.89 | 247 | 269 | 496 | 699.25 | -40.9778 | 12.7208 | 695.0944 | 64.4653 | 0.013 | 0.14 | 0.933 | 1.5268 | -63.6421 | 90.2622 | 1.5129 | 99.1407 | [47 empty] | Alkb, mg/L CaCO3 | 251.0662 | 255.6252 | 250.2353 | 257.8 | Alkb, mg/L CaCO3 | 208.893 | 231.0368 | 204.8571 | 241.6
[44 empty] | 1998-06-22 | 12:00 | 123 | 24 | 54 | 53 | 302 | 5.56 | 0.7 |  | 6.26 | 0.2085 | 0.88818 | 47.2428 | 12.6904 | 12.9175 | 539.1357 | 250.7527 | 533.8264 | 2.8573 | 50.6427 | 0.25507 | 7.74 | 7.75 | 7.89 | 248 | 269 | 517 | 561 | -8.5106 | 12.3675 | 558.1187 | 55.565 | 0.011 | 0.139 | 0.968 | 1.1065 | -14.3079 | 91.7603 | 1.0964 | 98.9967 | [47 empty] | T-Hdb, mg/L CaCO3 | 260.8081 | 265.1734 | 260.3529 | 260.2333 | T-Hdb, mg/L CaCO3 | 209.9253 | 231.1278 | 207.7143 | 207.1333
[44 empty] | 1998-06-22 | 14:00 | 125 | 24 | 54 | 53 | 302 | 5.43 | 0.62 |  | 6.05 | 0.2085 | 0.89752 | 48.9174 | 12.3937 | 12.6155 | 544.2148 | 253.1744 | 538.9819 | 2.8842 | 50.6158 | 0.24924 | 7.77 | 7.72 | 7.87 | 254 | 269 | 518 | 536.9839 | -3.6648 | 10.2473 | 534.4398 | 52.4736 | 0.011 | 0.139 | 1.025 | 1.2064 | -17.6939 | 91.7603 | 1.1956 | 99.08 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 248.6401 | 251.8056 | 245.8235 | 245.0167 | Ca-Hdb, mg/L CaCO3 | 200.966 | 216.3415 | 187.2857 | 183.3667
[44 empty] | 1998-06-22 | 15:00 | 126 | 24 | 54 | 53 | 302 | 5.4 | 0.58 |  | 5.98 | 0.2085 | 0.90301 | 49.5017 | 12.3252 | 12.5458 | 547.2805 | 254.6143 | 542.0474 | 2.9005 | 50.5995 | 0.24794 | 7.74 | 7.76 | 7.87 | 261 | 269 | 528 | 487.8276 | 7.6084 | 7.7739 | 485.7997 | 46.2741 | 0.009 | 0.137 | 1.057 | 1.2926 | -22.2931 | 93.2584 | 1.2812 | 99.2975 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-06-22 | 16:00 | 127 | 24 | 54 | 52 | 302 | 5.33 | 0.44 |  | 5.77 | 0.2085 | 0.92374 | 51.3397 | 12.1654 | 12.3831 | 559.2122 | 260.1982 | 553.9349 | 2.9638 | 50.0362 | 0.24748 | 7.88 | 7.67 | 7.95 | 263 | 269 | 526 | 525.2727 | 0.13826 | 7.0671 | 522.9583 | 49.7092 | 0.009 | 0.138 | 1.072 | 1.6416 | -53.1388 | 93.2584 | 1.6272 | 99.4469 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-06-22 | 17:00 | 128 | 24 | 54 | 52 | 302 | 5.35 | 0.57 |  | 5.92 | 0.2085 | 0.90372 | 50.0135 | 12.2111 | 12.4296 | 547.6403 | 254.8047 | 542.4526 | 2.9024 | 50.0976 | 0.24811 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-06-22 | 18:00 | 129 | 24 | 54 | 53 | 302 | 5.35 | 0.52 |  | 5.87 | 0.2085 | 0.91141 | 50.448 | 12.2111 | 12.4296 | 552.0374 | 256.8506 | 546.8081 | 2.9257 | 50.5743 | 0.24577 | 7 |  | 7.86 | 229 | 269 | 600 | 838.5769 | -39.7628 | 19.0813 | 833.1775 | 72.5149 | 0.01 | 0.14 | 1.082 | 1.4041 | -29.7713 | 92.5094 | 1.3918 | 99.2815 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-06-22 | 21:00 | 132 | 24 | 54 | 53 | 302 | 5.48 | 0.49 |  | 5.97 | 0.2085 | 0.91792 | 49.5863 | 12.5078 | 12.7316 | 555.9202 | 258.5965 | 550.5251 | 2.9463 | 50.5537 | 0.25184 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-06-22 | 22:00 | 133 | 24 | 54 | 52 | 302 | 5.62 | 0.64 |  | 6.26 | 0.2085 | 0.89776 | 47.2428 | 12.8273 | 13.0569 | 544.5007 | 253.2206 | 539.0802 | 2.8857 | 50.1143 | 0.26054 | 7.79 | 7.78 | 7.88 | 261 | 269 | 529 | 476.1875 | 9.9835 | 7.7739 | 474.1853 | 44.9582 | 0.013 | 0.138 | 1.15 | 1.1916 | -3.6209 | 90.2622 | 1.1807 | 98.8989 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-06-22 | 24:00 | 135 | 24 | 54 | 52 | 302 | 5.55 | 1.075 |  | 6.625 | 0.2085 | 0.83774 | 44.5849 | 12.6676 | 12.8942 | 512.7711 | 238.4948 | 507.7306 | 2.7176 | 50.2824 | 0.25644 | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-06-23 | 10:00 | 145 | 24 | 54 | 53 | 302 | 5.27 | 0.46 |  | 5.73 | 0.2085 | 0.91972 | 51.7051 | 12.0285 | 12.2437 | 556.7947 | 259.1014 | 551.5999 | 2.951 | 50.549 | 0.24221 | 7.78 | 7.79 | 8.02 | 231 | 269 | 538 | 878.7391 | -63.3344 | 18.3746 | 873.0875 | 73.5422 | 0.018 | 0.138 | 1.309 | 1.4567 | -11.2856 | 86.5169 | 1.4442 | 98.7536 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-06-23 | 10:15 | 145.25 | 24 | 54 | 53 | 302 | 5.27 | 0.46 |  | 5.73 | 0.2085 | 0.91972 | 51.7051 | 12.0285 | 12.2437 | 556.7947 | 259.1014 | 551.5999 | 2.951 | 50.549 | 0.24221 | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-06-23 | 10:45 | 145.75 | 24 | 54 | 52 | 302 | 5.19 | 4.34 |  | 9.53 | 0.2085 | 0.5446 | 30.6894 | 11.8459 | 12.0579 | 399.2296 | 185.8061 | 395.5618 | 2.1159 | 50.8841 | 0.23697 | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-06-23 | 11:15 | 146.25 | 24 | 53 | 52 | 302 | 5.26 | 6.86 |  | 12.12 | 0.2085 | 0.43399 | 23.9175 | 12.0057 | 12.2205 | 368.5056 | 171.4851 | 365.074 | 1.953 | 50.547 | 0.24177 | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-06-23 | 12:00 | 147 | 24 | 53 | 52 | 302 | 5.38 | 5.4 |  | 10.78 | 0.2085 | 0.49907 | 27.0148 | 12.2796 | 12.4993 | 386.0202 | 179.5968 | 382.3429 | 2.0458 | 50.4542 | 0.24774 | 7.7 | 7.66 | 7.84 | 218 | 286 | 373 | 347.7593 | 6.767 | 22.9682 | 346.6035 | 37.1039 | 0.013 | 0.136 | 0.419 | 0.25355 | 39.486 | 90.2622 | 0.25141 | 94.8292 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-06-23 | 12:30 | 147.5 | 24 | 53 | 52 | 302 | 5.29 | 5.1 |  | 10.39 | 0.2085 | 0.50914 | 28.0664 | 12.0741 | 12.2902 | 388.8564 | 180.9457 | 385.2145 | 2.0609 | 50.4391 | 0.24366 | 7.83 | 7.76 | 7.89 | 208 | 276 | 353 | 360.7941 | -2.208 | 26.5018 | 359.4559 | 42.1348 | 0.012 | 0.136 | 0.346 | 0.25953 | 24.9923 | 91.0112 | 0.25736 | 95.3372
[44 empty] | 1998-06-23 | 13:00 | 148 | 24 | 53 | 52 | 302 | 5.4 | 5.07 |  | 10.47 | 0.2085 | 0.51576 | 27.8443 | 12.3252 | 12.5458 | 390.7813 | 181.8053 | 387.0446 | 2.0711 | 50.4289 | 0.24878 | 7.85 | 7.7 | 7.92 | 219 | 277 | 351 | 351.1657 | -0.047202 | 22.6148 | 349.9841 | 37.4257 | 0.01 | 0.136 | 0.319 | 0.26504 | 16.9158 | 92.5094 | 0.26276 | 96.1942
[44 empty] | 1998-06-23 | 13:45 | 148.75 | 24 | 53 | 51 | 302 | 5.4 | 5.2 |  | 10.6 | 0.2085 | 0.50943 | 27.4906 | 12.3252 | 12.5458 | 388.9645 | 180.9601 | 385.2452 | 2.0614 | 49.9386 | 0.25122 | 7.77 | 7.76 | 7.86 | 205 | 277 | 349 | 364 | -4.298 | 27.5618 | 362.5785 | 43.4605 | 0.009 | 0.138 | 0.289 | 0.26279 | 9.0697 | 93.2584 | 0.26052 | 96.5454
[44 empty] | 1998-06-23 | 15:15 | 150.25 | 24 | 52 | 51 | 302 | 5.44 | 6.11 |  | 11.55 | 0.2085 | 0.471 | 25.1472 | 12.4165 | 12.6387 | 378.2854 | 175.9791 | 374.6412 | 2.0048 | 49.4952 | 0.25535 | 7.74 |  | 7.96 | 205 | 288 | 330 | 352.4468 | -6.8021 | 27.5618 | 351.1188 | 41.6152 | 0.009 | 0.135 | 0.255 | 0.24435 | 4.1773 | 93.2584 | 0.24223 | 96.2845
[44 empty] | 1998-06-23 | 16:30 | 151.5 | 24 | 52 | 51 | 302 | 5.5 | 6.44 |  | 11.94 | 0.2085 | 0.46064 | 24.2931 | 12.5535 | 12.7781 | 375.5162 | 174.672 | 371.8584 | 1.9902 | 49.5098 | 0.25809 |  |  | 7.96 | 205 | 276 | 341 | 349.6149 | -2.5264 | 27.5618 | 348.298 | 41.1424 | BMRL | 0.137 | 0.263 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 0:30 | 159.5 | 24 | 53 | 52 | 302 | 5.83 | 4.93 |  | 10.76 | 0.2085 | 0.54182 | 27.0669 | 13.3067 | 13.5448 | 398.5593 | 185.2801 | 394.442 | 2.1122 | 50.3878 | 0.26881
[44 empty] | 1998-06-24 | 8:00 | 167 | 24 | 53 | 52 | 302 | 5.6 | 4.4 |  | 10 | 0.2085 | 0.56 | 29.2 | 12.7817 | 13.0104 | 404.0329 | 187.9027 | 400.0252 | 2.1413 | 50.3587 | 0.25835
[44 empty] | 1998-06-24 | 8:15 | 167.25 | 24 | 51 | 50 | 302 | 5.4 | 12.3 |  | 17.7 | 0.2085 | 0.30508 | 16.0621 | 12.3252 | 12.5458 | 338.1723 | 157.3298 | 334.9387 | 1.7923 | 48.7077 | 0.25757
[44 empty] | 1998-06-24 | 9:00 | 168 | 24 | 51 | 50 | 302 | 5.38 | 12.4 |  | 17.78 | 0.2085 | 0.30259 | 15.9854 | 12.2796 | 12.4993 | 337.6314 | 157.0838 | 334.415 | 1.7894 | 48.7106 | 0.2566 | 7.74 | 7.71 | 7.88 | 198 | 276 | 327 | 319.879 | 2.1777 | 30.0353 | 318.7934 | 37.8908 | BMRL | 0.137 | 0.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 9:30 | 168.5 | 24 | 52 | 50 | 302 | 5.46 | 11.8 |  | 17.26 | 0.2085 | 0.31634 | 16.4971 | 12.4622 | 12.6851 | 340.6283 | 158.4553 | 337.3347 | 1.8053 | 49.1947 | 0.25786 | 7.79 | 7.74 | 7.89 | 200 | 286 | 321 | 321.4051 | -0.12619 | 29.3286 | 320.3076 | 37.56 | BMRL | 0.137 | 0.202 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 10:00 | 169 | 24 | 52 | 50 | 302 | 5.44 | 11.1 |  | 16.54 | 0.2085 | 0.3289 | 17.2588 | 12.4165 | 12.6387 | 343.4028 | 159.7517 | 340.0946 | 1.82 | 49.18 | 0.25699 | 7.79 | 7.77 | 7.89 | 197 | 281 | 320 | 325.1477 | -1.6087 | 30.3887 | 323.9936 | 39.1963 | BMRL | 0.138 | 0.202 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 11:00 | 170 | 24 | 52 | 50 | 302 | 5.58 | 12.3 |  | 17.88 | 0.2085 | 0.31208 | 15.8904 | 12.7361 | 12.9639 | 339.7101 | 157.9939 | 336.3525 | 1.8004 | 49.1996 | 0.2635 | 7.89 | 7.83 | 7.92 | 201 | 285 | 320 | 320.2 | -0.0625 | 28.9753 | 319.0988 | 37.0101 | 0.009 | 0.142 | 0.198 | 0.18998 | 4.0503 | 93.2584 | 0.18831 | 95.2206
[44 empty] | 1998-06-24 | 12:00 | 171 | 24 | 52 | 50 | 302 | 5.4 | 11.63 |  | 17.03 | 0.2085 | 0.31709 | 16.7334 | 12.3252 | 12.5458 | 340.7861 | 158.5458 | 337.5275 | 1.8061 | 49.1939 | 0.25503 | 7.94 | 7.9 | 7.97 | 186 | 286 | 316 | 328.0387 | -3.8097 | 34.2756 | 326.7688 | 43.079 | BMRL | 0.136 | 0.197 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 13:00 | 172 | 24 | 51 | 50 | 302 | 5.51 | 12.4 |  | 17.91 | 0.2085 | 0.30765 | 15.8621 | 12.5763 | 12.8013 | 338.7389 | 157.5621 | 335.4333 | 1.7952 | 48.7048 | 0.26283 | 7.88 | 7.79 | 8.01 | 192 | 286 | 315 | 323.4363 | -2.6782 | 32.1555 | 322.2373 | 40.4166 | BMRL | 0.141 | 0.197 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 13:45 | 172.75 | 24 | 51 | 50 | 302 | 5.46 | 12.89 |  | 18.35 | 0.2085 | 0.29755 | 15.4578 | 12.4622 | 12.6851 | 336.5573 | 156.5615 | 333.3031 | 1.7837 | 48.7163 | 0.26039 | 7.98 | 7.96 | 8.12 | 199 | 270 | 311 | 318.5811 | -2.4376 | 29.682 | 317.5001 | 37.3229 | BMRL | 0.138 | 0.189 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 15:00 | 174 | 24 | 52 | 50 | 302 | 5.51 | 12 |  | 17.51 | 0.2085 | 0.31468 | 16.2473 | 12.5763 | 12.8013 | 340.2699 | 158.2743 | 336.9494 | 1.8034 | 49.1966 | 0.26021 | 7.94 | 7.9 | 7.97 | 191 | 281 | 303 | 325.2433 | -7.341 | 32.5088 | 324.0187 | 41.0528 | BMRL | 0.14 | 0.197 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 16:00 | 175 | 24 | 52 | 50 | 302 | 5.6 | 12 |  | 17.6 | 0.2085 | 0.31818 | 16.1591 | 12.7817 | 13.0104 | 341.0484 | 158.6106 | 337.6654 | 1.8075 | 49.1925 | 0.26448 | 7.78 | 7.72 | 7.9 | 192 | 280 | 315 | 325.4667 | -3.3228 | 32.1555 | 324.2292 | 40.7826 | BMRL | 0.138 | 0.198 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-24 | 17:00 | 176 | 24 | 52 | 50 | 302 | 5.6 | 11.6 | X | 17.2 | 0.2085 | 0.32558 | 16.5581 | 12.7817 | 13.0104 | 342.683 | 159.3708 | 339.2839 | 1.8161 | 49.1839 | 0.26453 | 7.92 | 7.85 | 8.01 | 198 | 281 | 321 | 324.0345 | -0.94532 | 30.0353 | 322.866 | 38.6742 | BMRL | 0.134 | 0.201 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-25 | 15:00 |  | 24 | 68 | 68 | 302 | 8.98 | 4.53 |  | 13.51 | 0.2085 | 0.66469 | 21.3538 | 20.4964 | 20.8631 | 440.4405 | 203.5785 | 433.3974 | 2.3334 | 65.6666 | 0.31771
[44 empty] | 1998-06-25 | 16:00 |  | 24 | 60 | 58 | 302 | 7.7 | 3.25 |  | 10.95 | 0.2085 | 0.7032 | 26.5799 | 17.5748 | 17.8893 | 454.5498 | 210.5926 | 448.3297 | 2.4085 | 56.5915 | 0.31611
[44 empty] | 1998-06-25 | 16:30 |  | 24 | 55 | 53 | 302 | 7.07 | 2.83 |  | 9.9 | 0.2085 | 0.71414 | 29.5051 | 16.1369 | 16.4256 | 458.597 | 212.7115 | 452.8407 | 2.4301 | 51.5699 | 0.31851
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on CE8: Alison Gusses: Consultant verified reported TDS values. However, no explanation was given as to why the TDS rejections for the 2nd and 4th quarters appear lower than those during the 1st and 3rd quarters
Note on DG10: S Allgeier (7/9/99): Data responsible for high mass balance closure errors verified by consultant.
Note on DQ10: S Allgeier (7/9/99): Data responsible for high mass balance closure errors verified by consultant.
Note on EH16: C. Hill (7/8/99): Consultant verifed this reported value.

## SR40. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.67462 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.91 | [7 empty] | Recovery during sample collection (decimal) | 0.53 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-10-13 | 1998-11-01 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.34 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.08 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.43 | [7 empty] | Feed flow rate during sample collection (mL/min) | 20.4 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 142.1 | 142.1 | 142.1 | 142.1 | SDS-THM4F, ug/L | 142.1 | 142.1 | 142.1 | 142.1 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 432 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 7.25 | 14 | 8.9 | 8.1 | SDS-THM4p, ug/L | 7.25 | 14 | 8.9 | 8.1 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.07 | 8.19 | 7.63 | 14.6789 | 1998-10-12 | 9:00 | 0 | 24 | 41 | 42 | 152 | 4.4 | 5.7 | 10.1 | 0.10494 | 0.43564 | 14.0495 | 10.0428 | 10.2225 | 0 | 0 | 0 | 0 | 41.5 | 0.24632 | 1998-10-13 | 9:00 | 0 | 23 | 51 | 52.5 | 263 | 6.4 | 3.4 |  | 9.8 | 0.18158 | 0.65306 | 25.8367 | 14.6077 | 15.3151 | 449.7104 | 143.9038 | 442.2688 | 3.0209 | 48.7291 | 0.31429 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 22 | 23 | 8.6957 | 1998-10-12 | 9:30 | 0.5 | 24 | 41 | 42 | 152 | 4.4 | 5.7 | 10.1 | 0.10494 | 0.43564 | 14.0495 | 10.0428 | 10.2225 | 0 | 0 | 0 | 0 | 41.5 | 0.24632 | 1998-10-13 | 10:00 | 1 | 23 | 51 | 52 | 263 | 6.07 | 3.2 |  | 9.27 | 0.18158 | 0.6548 | 27.3711 | 13.8545 | 14.5254 | 450.5205 | 144.289 | 443.4527 | 3.027 | 48.473 | 0.29966 | 6.02 | 5.8 | 6.56 | 124 | 248 | 366 | 489.0063 | -33.6083 | 50.4 | 484.7941 | 74.4221 | BMRL | 0.148 | 0.272 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0.5 | 1.8 | 1.1 | 0 | SDS-HAA5p, ug/L | 0.5 | 1.8 | 1.1 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 376 | 380 | 378 | 1.0582 | 1998-10-12 | 10:00 | 1 | 24 | 50.5 | 51.5 | 263 | 5.97 | 3.57 | 9.54 | 0.18158 | 0.62579 | 26.5681 | 13.6262 | 13.87 | 0 | 0 | 0 | 0 | 51 | 0.27196 | 1998-10-13 | 11:00 | 2 | 23 | 51 | 52 | 263 | 5.96 | 3.1 |  | 9.06 | 0.18158 | 0.65784 | 28.0287 | 13.6034 | 14.2622 | 452.1521 | 144.8538 | 445.1883 | 3.0382 | 48.4618 | 0.2943 |  |  |  | 133 | 255 | 386 | 474.9419 | -23.042 | 46.8 | 471.0675 | 71.7663 | BMRL |  | 0.336 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-10-14 | 1998-10-15 | --- | --- | 1998-10-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-16 | 1998-10-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-17 | 1998-10-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-18 | 1998-10-18 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 352.5 | 352.5 | 352.5 | 352.5 | SDS-TOXF, ug Cl- /L | 352.5 | 352.5 | 352.5 | 352.5 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 248 | 252 | 250 | 1.6 | 1998-10-12 | 11:00 | 2 | 24 | 50.5 | 51 | 263 | 6.35 | 2.27 | 8.62 | 0.18158 | 0.73666 | 29.5104 | 14.4935 | 14.7529 | 0 | 0 | 0 | 0 | 50.75 | 0.2907 | 1998-10-13 | 12:00 | 3 | 23 | 50.5 | 52 | 263 | 5.87 | 3.02 |  | 8.89 | 0.18158 | 0.66029 | 28.5838 | 13.398 | 14.0468 | 453.4798 | 145.3137 | 446.6017 | 3.0473 | 48.2027 | 0.29141 |  |  |  | 133 | 254 | 393 | 477.4139 | -21.4794 | 46.8 | 473.5704 | 71.9155 | BMRL |  | 0.358 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 8:15 | 9:30 | --- | --- | 8:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:40 | 17:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:20 | 12:20 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 234 | 222 | 228 | 5.2632 | 1998-10-12 | 12:00 | 3 | 24 | 50 | 51 | 263 | 6.4 | 1.68 | 8.08 | 0.18158 | 0.79208 | 31.5495 | 14.6077 | 14.869 | 0 | 0 | 0 | 0 | 50.5 | 0.29444 | 1998-10-13 | 13:30 | 4.5 | 23 | 50.5 | 52 | 263 | 5.9 | 2.91 |  | 8.81 | 0.18158 | 0.66969 | 28.8524 | 13.4664 | 14.1186 | 458.8108 | 147.0103 | 451.816 | 3.083 | 48.167 | 0.29312 |  | 7.25 |  | 135 | 252 | 403 | 483.1615 | -19.8912 | 46 | 479.2563 | 71.8314 | BMRL | 0.149 | 0.382 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 23.25 | 48.5 | --- | --- | 23.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80.67 | 80.67 | --- | --- | --- | --- | --- | Operation time | hh.hh | 100 | 100 | --- | --- | --- | --- | --- | Cumulative time | hr | 123.33 | 123.33 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 4.225 | 4.225 | 4.225 | 4.225 | SDS-CDF, mg/L | 4.225 | 4.225 | 4.225 | 4.225 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 230 | 218 | 224 | 5.3571 | 1998-10-12 | 13:00 | 4 | 24 | 50 | 51 | 263 | 6.3 | 2.96 | 9.26 | 0.18158 | 0.68035 | 27.4017 | 14.3794 | 14.6367 | 0 | 0 | 0 | 0 | 50.5 | 0.28984 | 1998-10-13 | 14:30 | 5.5 | 23 | 50.5 | 52 | 263 | 5.85 | 2.88 |  | 8.73 | 0.18158 | 0.6701 | 29.126 | 13.3523 | 13.999 | 459.0213 | 147.0972 | 452.0831 | 3.0846 | 48.1654 | 0.29064 |  |  |  | 143 | 250 | 409 | 467.3438 | -14.265 | 42.8 | 463.7365 | 69.1635 | BMRL |  | 0.388 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.75 | 7.69 | 7.72 | 0.7772 | 6.61 | --- | --- | --- | --- | --- | pH | --- | 7.71 | 6.78 | --- | --- | --- | --- | --- | pH | --- | 8.08 | 6.92 | --- | --- | --- | --- | --- | pH | --- | 7.39 | 6.97 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.185 | 0.39 | 0.3 | 0.33 | SDS-CDp, mg/L | 1.185 | 0.39 | 0.3 | 0.33 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.43 | 0.278 | 0.354 | 42.9379 | 1998-10-12 | 14:00 | 5 | 24 | 50 | 51 | 263 | 6.6 | 2.6 | 9.2 | 0.18158 | 0.71739 | 27.587 | 15.0641 | 15.3337 | 0 | 0 | 0 | 0 | 50.5 | 0.30364 | 1998-10-13 | 15:30 | 6.5 | 23 | 50.5 | 52 | 263 | 5.89 | 2.8 |  | 8.69 | 0.18158 | 0.67779 | 29.2647 | 13.4436 | 14.0947 | 463.4865 | 148.5124 | 456.4325 | 3.1145 | 48.1355 | 0.29281 |  |  |  | 137 | 249 | 399 | 487.7036 | -22.2315 | 45.2 | 483.7765 | 71.6811 | BMRL |  | 0.396 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.55 | 3.55 | 3.55 | 3.55 | TOCF, mg/L | 3.55 | 3.55 | 3.55 | 3.55 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-10-12 | 15:00 | 6 | 24 | 50 | 51 | 263 | 6.44 | 2.17 | 8.61 | 0.18158 | 0.74797 | 29.5459 | 14.699 | 14.962 | 0 | 0 | 0 | 0 | 50.5 | 0.29628 | 1998-10-13 | 16:30 | 7.5 | 23 | 50.5 | 52 | 263 | 5.86 | 2.76 |  | 8.62 | 0.18158 | 0.67981 | 29.5104 | 13.3751 | 14.0229 | 464.6564 | 148.899 | 457.6209 | 3.1224 | 48.1276 | 0.29137 | 5.51 | 6.06 | 6.78 | 138 | 251 | 400 | 487.7971 | -21.9493 | 44.8 | 483.9001 | 71.4817 | BMRL | 0.149 | 0.391 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 266 | 278 | 272 | 4.4118 | 605 | 637.5172 | -5.3748 | 28.0423 | 633.4025 | 57.0573 | Alkalinity | mg/L as CaCO3 | 348 | 594 | 681.3333 | -14.7026 | 7.9365 | 677.8271 | 48.6595 | Alkalinity | mg/L as CaCO3 | 266 | 526 | 504.2979 | 4.1259 | 29.6296 | 501.5534 | 46.9648 | Alkalinity | mg/L as CaCO3 | 234 | 464 | 439.7143 | 5.234 | 38.0952 | 437.3208 | 46.4924 | TOCp, mg/L | #DIV/0! | 0.7 | BMRL | BMRL | TOCp, mg/L | #DIV/0! | 0.7 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 3.6 | 3.5 | 3.55 | 2.8169 | 1998-10-12 | 15:30 | 6.5 | 24 | 60 | 61 | 263 | 7.8 | 2.8 | 10.6 | 0.18158 | 0.73585 | 23.8113 | 17.8031 | 18.1216 | 0 | 0 | 0 | 0 | 60.5 | 0.29953 | 1998-10-14 | 8:15 | 23.25 | 23 | 50 | 52 | 263 | 6.07 | 2.5 |  | 8.57 | 0.18158 | 0.70828 | 29.6884 | 13.8545 | 14.5254 | 482.1052 | 154.4048 | 474.542 | 3.2392 | 47.7608 | 0.30413 |  |  |  | 150 | 250 | 405 | 492.8 | -21.679 | 40 | 488.8441 | 69.3154 | BMRL |  | 0.445 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 162 | 164 | 163 | 1.227 | 409 | 463 | -13.2029 | 34.8 | 459.6228 | 64.5361 | Total dissolved solids | mg/L | 198 | 486 | 775.7778 | -59.6251 | 20.8 | 769.7003 | 74.2757 | Total dissolved solids | mg/L | 150 | 332 | 362.766 | -9.2669 | 40 | 360.3155 | 58.3698 | Total dissolved solids | mg/L | 139 | 288 | 297.5714 | -3.3234 | 44.4 | 295.7265 | 52.9971 | UV254 F, cm-1 | 0.1435 | 0.1435 | 0.1435 | 0.1435 | UV254 F, cm-1 | 0.1435 | 0.1435 | 0.1435 | 0.1435 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.146 | 0.141 | 0.1435 | 3.4843 | 1998-10-12 | 16:00 | 7 | 24 | 30 | 31 | 263 | 3.95 | 0.89 | 4.84 | 0.18158 | 0.81612 | 53.3388 | 9.0157 | 9.177 | 0 | 0 | 0 | 0 | 30.5 | 0.30088 | 1998-10-14 | 9:00 | 24 | 24 | 50 | 52 | 263 | 6 | 2.47 |  | 8.47 | 0.18158 | 0.70838 | 30.0508 | 13.6947 | 13.9397 | 482.128 | 154.4406 | 474.6522 | 3.2395 | 47.7605 | 0.29187 | 6.38 | 6.29 | 6.18 | 147 | 250 | 404 | 500.2024 | -23.8125 | 41.2 | 496.1735 | 70.3733 | BMRL | 0.148 | 0.447 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 136 | 136 | 136 | 0 | 330 | 453.2414 | -37.3459 | 40.3509 | 449.6701 | 69.7556 | Total hardness | mg/L as CaCO3 | 182 | 544 | 693.1111 | -27.4101 | 20.1754 | 687.7349 | 73.5363 | Total hardness | mg/L as CaCO3 | 122 | 244 | 347.5319 | -42.4311 | 46.4912 | 344.9345 | 64.631 | Total hardness | mg/L as CaCO3 | 108 | 240 | 279.4286 | -16.4286 | 52.6316 | 277.434 | 61.0718 | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.0556 | 4.0286 | 4.0421 | 0.66758 | 1998-10-12 | 16:30 | 7.5 | 24 | 40 | 40.5 | 263 | 5.07 | 1.15 | 6.22 | 0.18158 | 0.81511 | 41.283 | 11.572 | 11.7791 | 0 | 0 | 0 | 0 | 40.25 | 0.29265 | 1998-10-14 | 10:00 | 25 | 24 | 50 | 52 | 263 | 5.97 | 2.42 |  | 8.39 | 0.18158 | 0.71156 | 30.3468 | 13.6262 | 13.87 | 484.1283 | 155.0937 | 476.6594 | 3.253 | 47.747 | 0.29049 |  |  |  | 147 | 251 | 407 | 504.095 | -23.8563 | 41.2 | 500.0421 | 70.6025 | BMRL |  | 0.438 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 116 | 120 | 118 | 3.3898 | 442 | 483.5172 | -9.393 | 47.3214 | 479.4025 | 75.386 | Calcium hardness | mg/L as CaCO3 | 158 | 560 | 891.3333 | -59.1667 | 29.4643 | 883.6197 | 82.119 | Calcium hardness | mg/L as CaCO3 | 118 | 322 | 343.5319 | -6.6869 | 47.3214 | 340.9345 | 65.3892 | Calcium hardness | mg/L as CaCO3 | 104 | 236 | 275.4286 | -16.707 | 53.5714 | 273.434 | 61.9652 | BromideF, ug/L | 69.5 | 69.5 | 69.5 | 69.5 | BromideF, ug/L | 69.5 | 69.5 | 69.5 | 69.5 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 69 | 70 | 69.5 | 1.4388 | 1998-10-12 | 17:00 | 8 | 24 | 50 | 51 | 263 | 6.6 | 1.53 | 8.13 | 0.18158 | 0.81181 | 31.3493 | 15.0641 | 15.3337 | 0 | 0 | 0 | 0 | 50.5 | 0.30364 | 1998-10-14 | 11:00 | 26 | 24 | 50 | 52 | 263 | 5.92 | 2.42 |  | 8.34 | 0.18158 | 0.70983 | 30.5348 | 13.5121 | 13.7539 | 483.0009 | 154.753 | 475.6122 | 3.2455 | 47.7545 | 0.28801 |  |  |  | 149 | 245 | 407 | 497.0744 | -22.1313 | 40.4 | 493.1569 | 69.7865 | BMRL |  | 0.445 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.149 | 0.15 | 0.1495 | 0.6689 | 0.43 | 0.85467 | -98.761 | 57.7684 | 0.84673 | 82.3439 | Turbidity | ntu | 0.104 | 0.806 | 2.8818 | -257.5407 | 70.6215 | 2.8526 | 96.3542 | Turbidity | ntu | 0.079 | 0.398 | 0.66411 | -66.8609 | 77.6836 | 0.65737 | 87.9824 | Turbidity | ntu | 0.09 | 0.54 | 0.46714 | 13.4921 | 74.5763 | 0.46275 | 80.5513 | Bromidep, ug/L | 54 | 65 | 51 | 49 | Bromidep, ug/L | 54 | 65 | 51 | 49 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 6 | 5 | 5.5 | 18.1818 | 1998-10-12 | 17:30 | 8.5 | 24 | 50 | 51 | 263 | 6.48 | 2.88 | 9.36 | 0.18158 | 0.69231 | 27.0983 | 14.7903 | 15.0549 | 0 | 0 | 0 | 0 | 50.5 | 0.29812 | 1998-10-14 | 12:00 | 27 | 24 | 50 | 52 | 263 | 5.94 | 2.42 |  | 8.36 | 0.18158 | 0.71053 | 30.4593 | 13.5577 | 13.8003 | 483.4528 | 154.8896 | 476.032 | 3.2485 | 47.7515 | 0.289 |  |  |  | 150 | 244 | 408 | 495.4545 | -21.4349 | 40 | 491.5534 | 69.4845 | BMRL |  | 0.444 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.2 | 0.13 | 0.165 | 42.4242 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 378 | 378 | 378 | 378 | AlkF, mg/L CaCO3 | 378 | 378 | 378 | 378
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.11 | 1.44 | 1.275 | 25.8824 | 1998-10-13 | 8:30 | 23.5 | 24 | 50 | 51.5 | 263 | 6.6 | 1.6 | 8.2 | 0.18158 | 0.80488 | 31.0732 | 15.0641 | 15.3337 | 0 | 0 | 0 | 0 | 50.75 | 0.30214 | 1998-10-14 | 14:00 | 29 | 24 | 50 | 52 | 263 | 5.94 | 2.4 |  | 8.34 | 0.18158 | 0.71223 | 30.5348 | 13.5577 | 13.8003 | 484.5379 | 155.2372 | 477.1004 | 3.2558 | 47.7442 | 0.28905 | 7.56 | 7.39 | 7.22 | 153 | 248 | 420 | 490.075 | -16.6845 | 38.8 | 486.2685 | 68.5359 | BMRL | 0.151 | 0.456 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 11.6 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 0.7 | 29.2 | 32.3667 | -10.8447 | 80.2817 | 32.0336 | 97.8148 | Total organic carbon | mg/L | BMRL | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 272 | 348 | 266 | 234 | Alkp, mg/L CaCO3 | 272 | 348 | 266 | 234
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 4.89 | 3.56 | 4.225 | 31.4793 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-14 | 15:00 | 30 | 24 | 50 | 52 | 263 | 5.97 | 2.38 |  | 8.35 | 0.18158 | 0.71497 | 30.497 | 13.6262 | 13.87 | 486.31 | 155.7926 | 478.8074 | 3.2677 | 47.7323 | 0.29058 |  |  |  | 156 | 249 | 419 | 485.7899 | -15.9403 | 37.6 | 482.0469 | 67.638 | BMRL |  | 0.448 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.449 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | BMRL | 1.048 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.287 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.204 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 228 | 228 | 228 | 228 | T-HdF, mg/L CaCO3 | 228 | 228 | 228 | 228
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 26 | 26 | 26 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-14 | 16:00 | 31 | 24 | 50 | 52 | 263 | 5.95 | 2.38 |  | 8.33 | 0.18158 | 0.71429 | 30.5726 | 13.5806 | 13.8236 | 485.859 | 155.6564 | 478.3887 | 3.2647 | 47.7353 | 0.28959 | 7.64 | 7.46 | 7.31 | 150 | 248 | 399 | 500 | -25.3133 | 40 | 496.0409 | 69.7606 | BMRL | 0.148 | 0.452 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.8707 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.589 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.5875 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.7778 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 136 | 182 | 122 | 108 | T-Hdp, mg/L CaCO3 | 136 | 182 | 122 | 108
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 7.82 | 7.94 | 7.88 | 1.5228 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-14 | 17:00 | 32 | 24 | 50 | 52 | 263 | 5.94 | 2.36 |  | 8.3 | 0.18158 | 0.71566 | 30.6867 | 13.5577 | 13.8003 | 486.7385 | 155.9423 | 479.2673 | 3.2706 | 47.7294 | 0.28914 |  |  |  | 149 | 246 | 414 | 504.2119 | -21.7903 | 40.4 | 500.2005 | 70.2119 | BMRL |  | 0.45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 52 | 56 | 54 | 7.4074 | --- | 107.4483 | --- | 22.3022 | 106.8466 | 49.4602 | Bromide | mg/L | 65 | --- | 115 | --- | 6.4748 | 114.4741 | 43.2186 | Bromide | mg/L | 51 | --- | 90.3617 | --- | 26.6187 | 89.9084 | 43.2756 | Bromide | mg/L | 49 | --- | 78.2857 | --- | 29.4964 | 77.945 | 37.1351 | Ca-HdF, mg/L CaCO3 | 224 | 224 | 224 | 224 | Ca-HdF, mg/L CaCO3 | 224 | 224 | 224 | 224
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 8:30 | 47.5 | 24 | 50 | 52 | 263 | 5.83 | 2.08 |  | 7.91 | 0.18158 | 0.73704 | 32.2491 | 13.3067 | 13.5448 | 500.8395 | 160.5067 | 493.2953 | 3.3656 | 47.6344 | 0.28435 | 6.48 | 6.37 | 6.28 | 160 | 248 | 419 | 502.2596 | -19.871 | 36 | 498.4661 | 67.9015 | BMRL | 0.148 | 0.482 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 1.5 | 2 | 50 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 118 | 158 | 118 | 104 | Ca-Hdp, mg/L CaCO3 | 118 | 158 | 118 | 104
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 355 | 350 | 352.5 | 1.4184 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 9:30 | 48.5 | 24 | 50 | 52 | 263 | 5.83 | 2.37 |  | 8.2 | 0.18158 | 0.71098 | 31.0732 | 13.3067 | 13.5448 | 483.6765 | 155.0063 | 476.3907 | 3.2503 | 47.7497 | 0.28366 |  |  |  | 163 | 248 | 400 | 464.0127 | -16.0032 | 34.8 | 460.6763 | 64.6172 | BMRL |  | 0.464 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.01 | 0.62 | 0.815 | 47.8528 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.11 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.17 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 96 | 130 | 113 | 30.0885 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 10:30 | 49.5 | 24 | 50 | 52 | 263 | 5.83 | 2.31 |  | 8.14 | 0.18158 | 0.71622 | 31.3096 | 13.3067 | 13.5448 | 487.032 | 156.0817 | 479.6957 | 3.2728 | 47.7272 | 0.2838 |  |  |  | 161 |  | 405 | 474.619 | -17.1899 | 35.6 | 471.143 | 65.8278 | BMRL |  | 0.457 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 1.49 | 0.88 | 1.185 | 51.4768 | --- | 11.6678 | --- | 71.9527 | 11.5497 | 89.74 | SDS-Cl2 demand | mg/L | 0.39 | --- | 43.0011 | --- | 90.7692 | 42.5529 | 99.0835 | SDS-Cl2 demand | mg/L | 0.3 | --- | 8.6511 | --- | 92.8994 | 8.5549 | 96.4932 | SDS-Cl2 demand | mg/L | 0.33 | --- | 5.8943 | --- | 92.1893 | 5.8295 | 94.3392 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 21 | 27 | 24 | 25 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 11:30 | 50.5 | 24 | 50 | 52 | 263 | 5.86 | 2.26 |  | 8.12 | 0.18158 | 0.72167 | 31.3892 | 13.3751 | 13.6145 | 490.5946 | 157.2109 | 483.1664 | 3.2967 | 47.7033 | 0.2854 |  |  |  | 162 |  | 406 | 478.177 | -17.7776 | 35.2 | 474.6546 | 65.8699 | BMRL |  | 0.462 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 26 | 26 | 26 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 26 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 51.9837 | 54.7229 | 52.6276 | 52.3134 | Qp/QT (THM4), % | 78.68 | 82.8259 | 79.6547 | 79.1791
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 4.1 | 6.1 | 5.1 | 39.2157 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 13:00 | 52 | 24 | 50 | 52 | 263 | 5.89 | 2.23 |  | 8.12 | 0.18158 | 0.72537 | 31.3892 | 13.4436 | 13.6842 | 493.0416 | 157.9826 | 485.5378 | 3.3131 | 47.6869 | 0.28696 | 7.49 | 7.34 | 7.18 | 152 | 241 | 407 | 508.843 | -25.0229 | 39.2 | 504.8472 | 69.8919 | BMRL | 0.148 | 0.464 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 6.83 | 7.97 | 7.4 | 15.4054 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.04 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.11 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 14:00 | 53 | 24 | 50 | 52 | 263 | 5.91 | 2.46 |  | 8.37 | 0.18158 | 0.70609 | 30.4217 | 13.4893 | 13.7306 | 480.6358 | 153.9993 | 473.2958 | 3.2297 | 47.7703 | 0.28743 |  |  |  | 153 |  | 403 | 483.0366 | -19.8602 | 38.8 | 479.3284 | 68.0803 | BMRL |  | 0.452 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 28.1334 | 27.2684 | 28.0786 | 27.6821 | SDS-HAA5b, ug/L | 12.7697 | 11.4604 | 12.6867 | 12.0865
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 121.1 | 163.1 | 142.1 | 29.5567 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 15:00 | 54 | 24 | 50 | 52 | 263 | 5.89 | 2.42 |  | 8.31 | 0.18158 | 0.70878 | 30.6486 | 13.4436 | 13.6842 | 482.3207 | 154.5473 | 474.9801 | 3.241 | 47.759 | 0.28653 |  |  |  | 162 |  | 413 | 464.1818 | -12.3927 | 35.2 | 460.7981 | 64.8436 | BMRL |  | 0.45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 3 | 2.8 | 2.9 | 6.8966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 16:00 | 55 | 24 | 50.5 | 52 | 263 | 5.91 | 2.38 |  | 8.29 | 0.18158 | 0.71291 | 30.725 | 13.4893 | 13.7306 | 484.9532 | 155.3826 | 477.5473 | 3.2587 | 47.9913 | 0.28611 | 7.43 | 7.53 | 7.25 | 157 | 248 | 399 | 480.937 | -20.5356 | 37.2 | 477.2973 | 67.1065 | BMRL | 0.148 | 0.449 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 1.6 | BMRL | 1.6 | #VALUE! | --- | 385.7379 | --- | 98.5841 | 381.4135 | 99.5805 | SDS-CHCl3 | mg/L | 1.4 | --- | 1241.4 | --- | 98.7611 | 1228.3569 | 99.886 | SDS-CHCl3 | mg/L | 1 | --- | 239.2979 | --- | 99.115 | 236.5534 | 99.5773 | SDS-CHCl3 | mg/L | 1 | --- | 161 | --- | 99.115 | 159.1384 | 99.3716 | SDS-CDb, mg/L | 2.6447 | 2.1264 | 2.1594 | 2.1874 | SDS-CDb, mg/L | 1.8331 | 1.0486 | 1.0986 | 1.141
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 30 | 27 | 28.5 | 10.5263 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-15 | 17:00 | 56 | 24 | 50.5 | 52 | 263 | 5.94 | 2.38 |  | 8.32 | 0.18158 | 0.71394 | 30.6106 | 13.5577 | 13.8003 | 485.633 | 155.5881 | 478.1788 | 3.2632 | 47.9868 | 0.28759 |  |  |  | 156 |  | 402 | 484.605 | -20.5485 | 37.6 | 480.8942 | 67.5604 | BMRL |  | 0.452 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 2.2 | 1.4 | 1.8 | 44.4444 | --- | 78.3517 | --- | 92.5 | 77.4899 | 97.6771 | SDS-BDCM | mg/L | 2.7 | --- | 239.3667 | --- | 88.75 | 236.8773 | 98.8602 | SDS-BDCM | mg/L | 1.7 | --- | 49.1468 | --- | 92.9167 | 48.6004 | 96.5021 | SDS-BDCM | mg/L | 1.6 | --- | 33.6 | --- | 93.3333 | 33.2277 | 95.1847 | TOCb, mg/L | #DIV/0! | 1.9904 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 1.1895 | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 23 | 28 | 25.5 | 19.6078 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 9:00 | 72 | 24 | 50.5 | 52 | 263 | 5.83 | 1.64 |  | 7.47 | 0.18158 | 0.78046 | 34.2075 | 13.3067 | 13.5448 | 532.2984 | 170.5884 | 524.2803 | 3.577 | 47.673 | 0.28412 | 7.44 | 7.35 | 7.17 | 172 | 247 | 428 | 527.2805 | -23.1964 | 31.2 | 523.3427 | 67.1343 | BMRL | 0.151 | 0.552 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 3.1 | 2.7 | 2.9 | 13.7931 | --- | 10.4862 | --- | 43.1373 | 10.4008 | 72.1175 | SDS-DBCM | mg/L | 5.8 | --- | -1.9778 | --- | -13.7255 | -1.896 | 405.9126 | SDS-DBCM | mg/L | 3.4 | --- | 7.017 | --- | 33.3333 | 6.9754 | 51.257 | SDS-DBCM | mg/L | 3.2 | --- | 5.9143 | --- | 37.2549 | 5.8827 | 45.6033 | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 10:00 | 73 | 24 | 50.5 | 52 | 263 | 5.89 | 2.47 |  | 8.36 | 0.18158 | 0.70455 | 30.4593 | 13.4436 | 13.6842 | 479.6549 | 153.6931 | 472.3548 | 3.2231 | 48.0269 | 0.28493 |  |  |  | 160 | 251 | 406 | 464.6154 | -14.4373 | 36 | 461.2044 | 65.3082 | BMRL |  | 0.484 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 1.3 | 2.2 | 1.75 | 51.4286 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 61.4425 | 67.0375 | 59.7639 | 58.7757 | Bromideb, ug/L | 57.3046 | 65.7728 | 54.7639 | 53.2683
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.2 | 1.1 | 1.15 | 8.6957 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 11:00 | 74 | 24 | 50.5 | 52 | 263 | 5.92 | 2.4 |  | 8.32 | 0.18158 | 0.71154 | 30.6106 | 13.5121 | 13.7539 | 484.0855 | 155.1005 | 476.6802 | 3.2528 | 47.9972 | 0.28656 |  |  |  | 165 | 254 | 404 | 459.6667 | -13.7789 | 34 | 456.3503 | 63.8436 | BMRL |  | 0.464 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 8.2 | 6.3 | 7.25 | 26.2069 | --- | 472.25 | --- | 94.898 | 467.0153 | 98.4476 | SDS-THM4 | mg/L | 14 | --- | 1437.3333 | --- | 90.1478 | 1422.3618 | 99.0157 | SDS-THM4 | mg/L | 8.9 | --- | 292.3043 | --- | 93.7368 | 289.0403 | 96.9208 | SDS-THM4 | mg/L | 8.1 | --- | 199.5286 | --- | 94.2998 | 197.3013 | 95.8946 | Alkb, mg/L CaCO3 | 322.8973 | 361.5831 | 319.0571 | 302.6687 | Alkb, mg/L CaCO3 | 294.5992 | 353.1522 | 288.7868 | 263.9821
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 6.5 | 7.1 | 6.8 | 8.8235 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 12:00 | 75 | 24 | 50.5 | 52 | 263 | 5.94 | 2.33 |  | 8.27 | 0.18158 | 0.71826 | 30.8017 | 13.5577 | 13.8003 | 488.4163 | 156.4798 | 480.9193 | 3.2819 | 47.9681 | 0.2877 | 7.65 | 7.51 | 7.32 | 153 | 243 |  | 497.2876 |  | 38.8 | 493.3996 | 68.9907 | BMRL | 0.147 | 0.467 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 180.175 | 202.8275 | 172.2147 | 165.2239 | T-Hdb, mg/L CaCO3 | 155.6144 | 189.9001 | 143.5661 | 132.9851
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | NR | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 13:30 | 76.5 | 24 | 50.5 | 52 | 263 | 5.94 | 2.24 |  | 8.18 | 0.18158 | 0.72616 | 31.1516 | 13.5577 | 13.8003 | 493.5954 | 158.1391 | 486.0189 | 3.3167 | 47.9333 | 0.28791 |  |  |  | 153 | 242 | 397 | 507.2232 | -27.764 | 38.8 | 503.2231 | 69.596 | BMRL |  | 0.466 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 168.8973 | 187.8829 | 168.2147 | 161.2239 | Ca-Hdb, mg/L CaCO3 | 140.5992 | 169.3349 | 139.5661 | 128.9851
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 2.1 | 2.8 | 2.45 | 28.5714 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 14:30 | 77.5 | 24 | 50.5 | 52 | 263 | 5.91 | 2.19 |  | 8.1 | 0.18158 | 0.72963 | 31.4691 | 13.4893 | 13.7306 | 495.885 | 158.8853 | 488.3121 | 3.3321 | 47.9179 | 0.28655 |  |  |  | 158 | 243 | 397 | 498.274 | -25.5098 | 36.8 | 494.4507 | 68.0454 | BMRL |  | 0.476 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 5.1 | 7.9 | 6.5 | 43.0769 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 15:40 | 78.6667 | 24 | 50.5 | 52 | 263 | 5.8 | 0.68 |  | 6.48 | 0.18158 | 0.89506 | 39.5864 | 13.2382 | 13.4751 | 638.0707 | 204.5021 | 628.5091 | 4.2879 | 46.9621 | 0.28693 |  |  |  | 172 | 251 | 406 | 915.2941 | -125.4419 | 31.2 | 907.0981 | 81.0384 | BMRL |  | 0.522 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 57.2 | 58.9 | 58.05 | 2.9285 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 16:00 | 79 | 24 | 50.5 | 52 | 263 | 5.71 | 0.64 |  | 6.35 | 0.18158 | 0.89921 | 40.4173 | 13.0328 | 13.266 | 642.5842 | 205.9976 | 633.1054 | 4.3185 | 46.9315 | 0.28267 |  |  |  | 174 | 254 | 410 | 928.0625 | -126.3567 | 30.4 | 919.8768 | 81.0844 | BMRL |  | 0.547 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | BMRL | 1 | 1 | #VALUE! | --- | 1.5172 | --- | 13.0435 | 1.5114 | 33.837 | SDS-DBAA* | mg/L | 1.8 | --- | -5.4222 | --- | -56.5217 | -5.3463 | 133.6684 | SDS-DBAA* | mg/L | 1.1 | --- | 1.2064 | --- | 4.3478 | 1.2052 | 8.7256 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 63.7 | 66 | 64.85 | 3.5466 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 16:20 | 79.3333 | 24 | 50.5 | 52 | 263 | 5.7 | 0.64 |  | 6.34 | 0.18158 | 0.89905 | 40.4826 | 13.0099 | 13.2427 | 642.3932 | 205.9418 | 632.934 | 4.3172 | 46.9328 | 0.28216 |  |  |  | 174 | 245 | 417 | 926.875 | -122.2722 | 30.4 | 918.7165 | 81.0605 | BMRL |  | 0.594 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1 | --- | 65.4444 | --- | 85.2941 | 64.7666 | 98.456 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 7.0374 | 7.2 | 7.1115 | 6.9767 | Qp/QT (HAA5), % | 53.9531 | 55.2 | 54.5215 | 53.4884
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 16:40 | 79.6667 | 24 | 50.5 | 52 | 263 | 5.69 | 0.62 |  | 6.31 | 0.18158 | 0.90174 | 40.6799 | 12.9871 | 13.2195 | 645.4112 | 206.9148 | 635.9243 | 4.3375 | 46.9125 | 0.28179 |  |  |  | 176 | 246 | 426 | 929.129 | -118.1054 | 29.6 | 920.9821 | 80.89 | BMRL |  | 0.634 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 132.6101 | 132.8768 | 132.6275 | 132.7512 | SDS-THM4b, ug/L | 69.3443 | 71.3888 | 69.4773 | 70.4256
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 17:00 | 80 | 24 | 50.5 | 52 | 263 | 5.69 | 0.61 |  | 6.3 | 0.18158 | 0.90317 | 40.746 | 12.9871 | 13.2195 | 647.0356 | 207.4356 | 637.5248 | 4.3484 | 46.9016 | 0.28186 |  |  |  | 177 | 246 | 435 | 930.9344 | -114.0079 | 29.2 | 922.7787 | 80.8188 | BMRL |  | 0.672 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.2 | --- | 4.9778 | --- | 10.2041 | 4.9486 | 55.5426 | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-16 | 17:20 | 80.3333 | 24 | 50.5 | 52 | 263 | 5.63 | 0.6 |  | 6.23 | 0.18158 | 0.90369 | 41.2151 | 12.8502 | 13.0801 | 647.5476 | 207.6326 | 638.1304 | 4.3521 | 46.8979 | 0.27891 |  |  |  | 178 | 246 | 437 | 925.6 | -111.8078 | 28.8 | 917.5981 | 80.6015 | BMRL |  | 0.705 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1 | BMRL | 1 | #VALUE! | --- | 19.9655 | --- | 84.6154 | 19.752 | 94.9372 | SDS-DCBAA | mg/L | 1.1 | --- | 61.1 | --- | 83.0769 | 60.4689 | 98.1809 | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-16 | 17:40 | 80.6667 | 24 | 50.5 | 52 | 263 | 5.69 | 0.59 |  | 6.28 | 0.18158 | 0.90605 | 40.879 | 12.9871 | 13.2195 | 650.3248 | 208.49 | 640.7657 | 4.3706 | 46.8794 | 0.28199 |  |  |  | 180 | 245 | 447 | 925.0847 | -106.9541 | 28 | 917.0248 | 80.3713 | BMRL |  | 0.732 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | 1 | 0.5 | 200 | --- | 198.9483 | --- | 99.1387 | 196.7143 | 99.7458 | SDS-HAA5 | mg/L | 1.8 | --- | 626.8 | --- | 96.8992 | 620.2259 | 99.7098 | SDS-HAA5 | mg/L | 1.1 | --- | 122.2702 | --- | 98.1051 | 120.8747 | 99.09 | SDS-HAA5 | mg/L | 0 | --- | 82.9286 | --- | 100 | 81.9637 | 100 | SDS-CDb, mg/L | 4.0111 | 3.9489 | 3.9459 | 3.9533 | SDS-CDb, mg/L | 2.5848 | 2.1081 | 2.085 | 2.1416
[44 empty] | 1998-10-17 | 9:30 | 96.5 | 23 | 50.5 | 52 | 263 | 5.43 | 0.45 |  | 5.88 | 0.18158 | 0.92347 | 43.7279 | 12.3937 | 12.9939 | 670.6147 | 215.1424 | 661.2109 | 4.5077 | 46.7423 | 0.27799 | 7.51 | 7.45 | 7.26 | 190 | 256 | 604 | 974 | -61.2583 | 24 | 965.9066 | 80.3294 | BMRL | 0.148 | 1.34 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | 1 | 0.5 | 200 | --- | 222.3966 | --- | 99.229 | 219.8986 | 99.7726 | SDS-HAA6 | mg/L | 2.8 | --- | 692.2444 | --- | 95.6823 | 684.9924 | 99.5912 | SDS-HAA6 | mg/L | 1.1 | --- | 136.7383 | --- | 98.3038 | 135.1762 | 99.1862 | SDS-HAA6 | mg/L | 0 | --- | 92.6429 | --- | 100 | 91.565 | 100 | TOCb, mg/L | #DIV/0! | 3.3448 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 1.9768 | #VALUE! | #VALUE!
[44 empty] | 1998-10-17 | 10:40 | 97.6667 | 23 | 50 | 52 | 263 | 5.86 | 5.91 |  | 11.77 | 0.18158 | 0.49788 | 21.3449 | 13.3751 | 14.0229 | 377.8328 | 121.0765 | 372.1119 | 2.539 | 48.461 | 0.28936 |  |  |  | 154 |  | 375 | 345.1878 | 7.9499 | 38.4 | 343.0579 | 55.1096 | BMRL |  | 0.531 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-17 | 11:00 | 98 | 23 | 50 | 52 | 263 | 5.94 | 5.89 |  | 11.83 | 0.18158 | 0.50211 | 21.2316 | 13.5577 | 14.2143 | 379.5039 | 121.5862 | 373.6787 | 2.5501 | 48.4499 | 0.29338 |  |  |  | 146 |  | 341 | 354.8829 | -4.0712 | 41.6 | 352.524 | 58.5844 | BMRL |  | 0.418 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 68.4092 | 69.176 | 68.1844 | 68.0698 | Bromideb, ug/L | 61.1373 | 67.016 | 59.4135 | 58.5349
[44 empty] | 1998-10-17 | 11:20 | 98.3333 | 23 | 50 | 52 | 263 | 5.94 | 5.86 |  | 11.8 | 0.18158 | 0.50339 | 21.2881 | 13.5577 | 14.2143 | 380.0043 | 121.7466 | 374.1714 | 2.5534 | 48.4466 | 0.2934 |  |  |  | 137 |  | 324 | 364.5427 | -12.5132 | 45.2 | 361.9731 | 62.1519 | BMRL |  | 0.365 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 370.5404 | 375.84 | 370.0351 | 367.9535 | Alkb, mg/L CaCO3 | 320.8097 | 361.44 | 316.9359 | 300.9767
[44 empty] | 1998-10-17 | 11:40 | 98.6667 | 23 | 50 | 52 | 263 | 6 | 5.77 |  | 11.77 | 0.18158 | 0.50977 | 21.3449 | 13.6947 | 14.3579 | 382.5409 | 122.5398 | 376.6093 | 2.5704 | 48.4296 | 0.29647 |  |  |  | 138 |  | 319 | 366.4645 | -14.8791 | 44.8 | 363.8584 | 62.0732 | BMRL |  | 0.32 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 221.5256 | 224.688 | 220.4618 | 219.6279 | T-Hdb, mg/L CaCO3 | 178.3632 | 202.608 | 170.2072 | 163.814
[44 empty] | 1998-10-17 | 12:00 | 99 | 23 | 50 | 52 | 263 | 5.94 | 5.71 |  | 11.65 | 0.18158 | 0.50987 | 21.5751 | 13.5577 | 14.2143 | 382.5658 | 122.5672 | 376.6936 | 2.5706 | 48.4294 | 0.29351 |  |  |  | 139 | 241 | 320 | 365.4711 | -14.2097 | 44.4 | 362.9136 | 61.6989 | BMRL |  | 0.302 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 216.5404 | 219.248 | 216.4618 | 215.6279 | Ca-Hdb, mg/L CaCO3 | 166.8097 | 187.568 | 166.2072 | 159.814
[44 empty] | 1998-10-17 | 12:20 | 99.3333 | 23 | 50 | 52 | 263 | 5.94 | 6.11 |  | 12.05 | 0.18158 | 0.49295 | 20.8257 | 13.5577 | 14.2143 | 375.9483 | 120.4471 | 370.1777 | 2.5262 | 48.4738 | 0.29324 |  |  |  | 138 |  | 308 | 358.8838 | -16.5207 | 44.8 | 356.3894 | 61.2783 | BMRL |  | 0.29 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-10-17 | 12:40 | 99.6667 | 23 | 50 | 52 | 263 | 6 | 6.11 |  | 12.11 | 0.18158 | 0.49546 | 20.7176 | 13.6947 | 14.3579 | 376.9304 | 120.7426 | 371.0858 | 2.5327 | 48.4673 | 0.29624 |  |  |  | 139 |  | 318 | 359.0016 | -12.8936 | 44.4 | 356.4921 | 61.009 | BMRL |  | 0.28 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-10-17 | 13:00 | 100 | 23 | 50 | 52 | 263 | 6 | 6.09 |  | 12.09 | 0.18158 | 0.49628 | 20.7535 | 13.6947 | 14.3579 | 377.2472 | 120.8441 | 371.3977 | 2.5348 | 48.4652 | 0.29625 | 8.06 | 7.9 | 7.82 | 136 | 246 | 306 | 362.3153 | -18.4037 | 45.6 | 359.7337 | 62.1943 | BMRL | 0.146 | 0.282 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-10-18 | 9:30 | 120.5 | 23 | 50 | 52 | 263 | 5.97 | 4.8 |  | 10.77 | 0.18158 | 0.55432 | 23.4197 | 13.6262 | 14.2861 | 401.1156 | 128.5 | 394.9273 | 2.6952 | 48.3048 | 0.29575 | 7.68 | 7.5 | 7.48 | 151 | 247 | 332 | 373.1313 | -12.3889 | 39.6 | 370.6101 | 59.2564 | BMRL | 0.147 | 0.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-10-18 | 10:20 | 121.3333 | 23 | 49.5 | 51 | 263 | 6 | 15 |  | 21 | 0.18158 | 0.28571 | 11.5238 | 13.6947 | 14.3579 | 310.2472 | 99.3819 | 305.4366 | 2.0846 | 48.1654 | 0.2981 |  |  |  | 135 |  | 267 | 296 | -10.8614 | 46 | 294.1635 | 54.1072 | BMRL |  | 0.201 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-10-18 | 10:40 | 121.6667 | 23 | 49.5 | 51 | 263 | 6 | 15.1 |  | 21.1 | 0.18158 | 0.28436 | 11.4645 | 13.6947 | 14.3579 | 309.8933 | 99.2685 | 305.0882 | 2.0822 | 48.1678 | 0.29808 |  |  |  | 125 |  | 168 | 299.6689 | -78.3743 | 50 | 297.6765 | 58.0081 | BMRL |  | 0.203 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-10-18 | 11:00 | 122 | 23 | 49.5 | 51 | 263 | 6.03 | 15 |  | 21.03 | 0.18158 | 0.28673 | 11.5059 | 13.7632 | 14.4297 | 310.5169 | 99.4604 | 305.6779 | 2.0864 | 48.1636 | 0.2996 |  |  |  | 127 |  | 168 | 299.446 | -78.2417 | 49.2 | 297.4691 | 57.3065 | BMRL |  | 0.199 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-10-18 | 11:20 | 122.3333 | 23 | 49.5 | 51 | 263 | 6 | 15 |  | 21 | 0.18158 | 0.28571 | 11.5238 | 13.6947 | 14.3579 | 310.2472 | 99.3819 | 305.4366 | 2.0846 | 48.1654 | 0.2981 |  |  |  | 122 |  | 265 | 301.2 | -13.6604 | 51.2 | 299.1559 | 59.2186 | BMRL |  | 0.199 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-10-18 | 11:40 | 122.6667 | 23 | 49.5 | 51 | 263 | 6 | 15 |  | 21 | 0.18158 | 0.28571 | 11.5238 | 13.6947 | 14.3579 | 310.2472 | 99.3819 | 305.4366 | 2.0846 | 48.1654 | 0.2981 |  |  |  | 126 |  | 264 | 299.6 | -13.4848 | 49.6 | 297.6198 | 57.6641 | BMRL |  | 0.199 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-10-18 | 12:00 | 123 | 23 | 49.5 | 51 | 263 | 6 | 14.8 |  | 20.8 | 0.18158 | 0.28846 | 11.6442 | 13.6947 | 14.3579 | 310.9678 | 99.6127 | 306.146 | 2.0894 | 48.1606 | 0.29813 |  |  |  | 127 |  | 265 | 299.8649 | -13.1566 | 49.2 | 297.893 | 57.3672 | BMRL |  | 0.202 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-10-18 | 12:20 | 123.3333 | 23 | 49.5 | 51 | 263 | 6.03 | 14.93 |  | 20.96 | 0.18158 | 0.28769 | 11.5477 | 13.7632 | 14.4297 | 310.7682 | 99.5408 | 305.9252 | 2.0881 | 48.1619 | 0.29961 | 7.89 | 7.7 | 7.59 | 126 | 247 | 264 | 300.0817 | -13.6673 | 49.6 | 298.0861 | 57.7303 | BMRL |  | 0.202 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-10-19 | 8:45 | 143.75 | 23 | 50 | 51.5 | 263 | 6.03 | 13.8 | X | 19.83 | 0.18158 | 0.30408 | 12.2627 | 13.7632 | 14.4297 | 315.1332 | 100.939 | 310.2222 | 2.1174 | 48.6326 | 0.29671 | 7.75 | 7.6 | 7.52 | 136 | 247 | 279 | 299.813 | -7.4599 | 45.6 | 297.9351 | 54.3525 | BMRL |  | 0.202 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-10-19 | 14:30 |  | 23 | 45 | 46.5 | 263 | 6 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 13.6947 | 14.3579 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-19 | 14:45 |  | 23 | 55 | 56.5 | 263 | 7.42 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 16.9358 | 17.756 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-19 | 15:00 |  | 23 | 65.5 | 66.5 | 263 | 9 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 20.542 | 21.5369 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-19 | 15:20 |  | 23 | 34.5 | 35.5 | 263 | 4.67 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 10.659 | 11.1752 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-19 | 15:40 |  | 23 | 45 | 46.5 | 263 | 6.13 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 13.9914 | 14.669 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on X12: Alison Gusses: Verified by consultant
Note on X13: Alison Gusses: Verified by consultant
Note on CY18: Alison Gusses: Verified by consultant
Note on DQ10: S Allgeier (7/9/99): Data responsible for high mass balance closure errors verified by the consultant.
Note on DV18: Alison Gusses: Verified by consultant

## SR40. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Hollywood | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.43088 | [45 empty] | Recovery during sample collection (decimal) | 0.69935 | [10 empty] | Recovery during sample collection (decimal) | 0.90404 | [7 empty] | Recovery during sample collection (decimal) | 0.54302 | [7 empty] | Recovery during sample collection (decimal) | 0.28484 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL4060642 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1999-02-18 | 1999-03-01 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.8471 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.4238 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.0614 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.85 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 11:00 | 10:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 265.5714 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 261.7143 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [6 empty] | SDS-THM4F, ug/L | 134.3 | 134.3 | 134.3 | 134.3 | SDS-THM4F, ug/L | 134.3 | 134.3 | 134.3 | 134.3 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 169 | 385 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 18.8 | 23.3 | 21.6 | 19.5 | SDS-THM4p, ug/L | 18.8 | 23.3 | 21.6 | 19.5 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.75 | 7.74 | 7.745 | 0.12912 | 1999-02-10 | 8:45 | 0 | [18 empty] | 1999-02-11 | 10:00 | 0 | 23 | 52 | 53 | 272 | 6.2 | 3.45 |  | 9.65 | 0.18779 | 0.64249 | 27.1865 | 14.1512 | 14.8365 | 373.8582 | 210.6515 | 370.138 | 1.6135 | 50.8865 | 0.29156 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 65.4 | 65.4 | 65.4 | 65.4 | SDS-HAA5F, ug/L | 65.4 | 65.4 | 65.4 | 65.4 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 23 | 23 | 0 | 1999-02-10 | 9:00 | 0.25 | 23 | 48 | 48 | 272 | 5.3 | 2.2 | 7.5 | 0.18779 | 0.70667 | 35.2667 | 12.097 | 12.6828 | 0 | 0 | 0 | 0 | 48 | 0.26423 | 1999-02-11 | 10:30 | 0.5 | 23 | 51 | 52 | 272 | 5.87 | 1.48 |  | 7.35 | 0.18779 | 0.79864 | 36.0068 | 13.398 | 14.0468 | 412.83 | 232.7362 | 408.9434 | 1.7815 | 49.7185 | 0.28253 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.85 | 4.9 | 4.4 | 4 | SDS-HAA5p, ug/L | 2.85 | 4.9 | 4.4 | 4 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 264 | 316 | 290 | 17.931 | 1999-02-10 | 9:45 | 1 | 23 | 50 | 50 | 263 | 5.6 | 1.23 | 6.83 | 0.18158 | 0.81991 | 37.5066 | 12.7817 | 13.4007 | 0 | 0 | 0 | 0 | 50 | 0.26801 | 1999-02-11 | 10:45 | 0.75 | 23 | 50 | 51 | 272 | 5.55 | 2.73 |  | 8.28 | 0.18779 | 0.67029 | 31.8502 | 12.6676 | 13.2811 | 380.0565 | 214.3722 | 376.6758 | 1.6399 | 48.8601 | 0.27182 | [27 empty] | Sampling date | MM/DD/YY | 1999-02-12 | 1999-02-13 | --- | --- | 1999-02-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-14 | 1999-02-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-15 | 1999-02-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-16 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 390 | 390 | 390 | 390 | SDS-TOXF, ug Cl- /L | 390 | 390 | 390 | 390 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 269 | 269 | 269 | 0 | 1999-02-10 | 10:15 | 1.5 | 23.2 | 50 | 50 | 263 | 6 | 2.8 | 8.8 | 0.18158 | 0.68182 | 28.8864 | 13.6947 | 14.2733 | 0 | 0 | 0 | 0 | 50 | 0.28547 | 1999-02-11 | 11:00 | 1 | 23 | 50 | 51 | 272 | 5.5 | 2.02 |  | 7.52 | 0.18779 | 0.73138 | 35.1702 | 12.5535 | 13.1614 | 394.8972 | 222.7614 | 391.4165 | 1.704 | 48.796 | 0.26972 | 7.74 | 7.39 | 7.55 | 160 | 268 | 254 | 565.7822 | -122.7489 | 40.5204 | 561.6796 | 71.514 | BMRL | 0.167 | 0.172 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 12:00 | 11:00 | --- | --- | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:00 | 20:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:30 | 19:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 32 | 36 | 33 | 32 | SDS-TOXp, ug Cl- /L | 32 | 36 | 33 | 32 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 288 | 332 | 310 | 14.1935 | 1999-02-10 | 10:45 | 2 | 23.2 | 50 | 50 | 263 | 5.9 | 1.7 | 7.6 | 0.18158 | 0.77632 | 33.6053 | 13.4664 | 14.0354 | 0 | 0 | 0 | 0 | 50 | 0.28071 | 1999-02-11 | 11:45 | 1.75 | 23.2 | 50 | 51 | 272 | 5.5 | 2.26 |  | 7.76 | 0.18779 | 0.70876 | 34.0515 | 12.5535 | 13.0838 | 389.2627 | 219.583 | 385.8316 | 1.6796 | 48.8204 | 0.268 | 7.67 | 7.51 | 7.42 | 212 | 290 | 371 | 407.7168 | -9.8967 | 21.1896 | 405.7381 | 47.7495 | BMRL | 0.166 | 0.292 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 26 | 49 | --- | --- | 26 | --- | --- | --- | --- | --- | Operation time | hh.hh | 82 | 82 | --- | --- | --- | --- | --- | Operation time | hh.hh | 81.5 | 81.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 101 | 101 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 7.39 | 7.39 | 7.39 | 7.39 | SDS-CDF, mg/L | 7.39 | 7.39 | 7.39 | 7.39 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 250 | 276 | 263 | 9.8859 | 1999-02-10 | 11:15 | 2.5 | 23.2 | 50 | 50 | 263 | 5.6 | 0.69 | 6.29 | 0.18158 | 0.8903 | 40.8124 | 12.7817 | 13.3217 | 0 | 0 | 0 | 0 | 50 | 0.26643 | 1999-02-11 | 12:45 | 2.75 | 23.2 | 50 | 51 | 272 | 5.46 | 2.58 |  | 8.04 | 0.18779 | 0.6791 | 32.8308 | 12.4622 | 12.9887 | 382.1005 | 215.5569 | 378.7574 | 1.6487 | 48.8513 | 0.26588 | 7.37 | 7.25 | 7.38 | 208 | 268 | 369 | 398.093 | -7.8843 | 22.6766 | 396.1851 | 47.4993 | BMRL | 0.167 | 0.382 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.76 | 7.9 | 7.83 | 1.788 | 7.92 | --- | --- | --- | --- | --- | pH | --- | 7.76 | 7.95 | --- | --- | --- | --- | --- | pH | --- | 8.01 | 7.75 | --- | --- | --- | --- | --- | pH | --- | 7.95 | 7.93 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.195 | 4.2 | 4.34 | 4.48 | SDS-CDp, mg/L | 4.195 | 4.2 | 4.34 | 4.48 | Labor Rate + Fringe ($/work-hour) | 27.95
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 6.5 | 69.7434 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.502 | 0.138 | 0.32 | 113.75 | 1999-02-10 | 11:30 | 2.75 | 23.2 | 50 | 50 | 263 | 5.97 | 4.47 | 10.44 | 0.18158 | 0.57184 | 24.1916 | 13.6262 | 14.2019 | 0 | 0 | 0 | 0 | 50 | 0.28404 | 1999-02-11 | 14:30 | 4.5 | 23.6 | 50 | 51 | 272 | 5.48 | 3.56 |  | 9.04 | 0.18779 | 0.60619 | 29.0885 | 12.5078 | 12.883 | 365.603 | 206.2433 | 362.3924 | 1.5775 | 48.9225 | 0.26334 | 7.72 | 7.48 | 7.42 | 242 | 270 | 397 | 310.5618 | 21.7728 | 10.0372 | 309.8711 | 21.903 | BMRL | 0.171 | 0.406 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 4.65 | 4.65 | 4.65 | 4.65 | TOCF, mg/L | 4.65 | 4.65 | 4.65 | 4.65 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 16.5 | 79.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.45 | 0.26 | 0.355 | 53.5211 | 1999-02-10 | 13:00 | 4.25 | 23 | 50 | 50 | 263 | 5.95 | 1.3 | 7.25 | 0.18158 | 0.82069 | 35.2759 | 13.5806 | 14.2383 | 0 | 0 | 0 | 0 | 50 | 0.28477 | 1999-02-11 | 15:30 | 5.5 | 23.6 | 50 | 51 | 263 | 5.53 | 1.89 |  | 7.42 | 0.18158 | 0.74528 | 34.4447 | 12.6219 | 13.0006 | 398.5303 | 224.7302 | 394.8758 | 1.7197 | 48.7803 | 0.26651 | 7.59 | 7.52 | 7.56 | 236 | 269 | 389 | 365.5556 | 6.0268 | 12.2677 | 364.1935 | 35.1993 | BMRL | 0.169 | 0.457 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 172 | 210 | 191 | 19.8953 | 355 | 520.2862 | -46.5595 | 34.1379 | 516.8839 | 63.0478 | Alkalinity | mg/L as CaCO3 | 324 | 410 | -30.3272 | 107.3969 | -11.7241 | -27.0242 | 1298.9256 | Alkalinity | mg/L as CaCO3 | 148 | 312 | 458.7352 | -47.0305 | 48.9655 | 455.4918 | 67.5076 | Alkalinity | mg/L as CaCO3 | 142 | 286 | 348.947 | -22.0094 | 51.0345 | 346.796 | 59.0537 | TOCp, mg/L | 0.7 | 0.8 | 0.6 | 0.5 | TOCp, mg/L | 0.7 | 0.8 | 0.6 | 0.5 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 67.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 4.2 | 5.1 | 4.65 | 19.3548 | 1999-02-10 | 13:45 | 5 | 23 | 50 | 50 | 263 | 5.79 | 1.18 | 6.97 | 0.18158 | 0.8307 | 36.7331 | 13.2154 | 13.8554 | 0 | 0 | 0 | 0 | 50 | 0.27711 | 1999-02-11 | 16:00 | 6 | 23.6 | 50 | 51 | 263 | 5.5 | 2.06 |  | 7.56 | 0.18158 | 0.72751 | 33.7884 | 12.5535 | 12.9301 | 393.9946 | 222.1838 | 390.4016 | 1.7001 | 48.7999 | 0.26496 | 7.6 | 7.54 | 7.7 | 243 | 270 | 416 | 338.4175 | 18.6496 | 9.6654 | 337.4198 | 27.9829 | BMRL | 0.167 | 0.453 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 215 | 221 | 218 | 2.7523 | 391 | 387.6323 | 0.86131 | 18.9591 | 385.8796 | 43.5057 | Total dissolved solids | mg/L | 226.625 | 612 | 668.2313 | -9.1881 | 15.7528 | 664.1147 | 65.8756 | Total dissolved solids | mg/L | 205 | 356 | 345.0497 | 3.0759 | 23.7918 | 343.5879 | 40.3355 | Total dissolved solids | mg/L | 201 | 331 | 296.0837 | 10.5487 | 25.2788 | 295.0955 | 31.8865 | UV254 F, cm-1 | 0.164 | 0.164 | 0.164 | 0.164 | UV254 F, cm-1 | 0.164 | 0.164 | 0.164 | 0.164 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 3.6429 | 66.8862 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.17 | 0.158 | 0.164 | 7.3171 | 1999-02-10 | 14:00 | 5.25 | 23 | 52 | 52 | 263 | 5.97 | 3.7 | 9.67 | 0.18158 | 0.61737 | 26.1975 | 13.6262 | 14.2861 | 0 | 0 | 0 | 0 | 52 | 0.27473 | 1999-02-11 | 16:30 | 6.5 | 23.6 | 49 | 50 | 263 | 5.51 | 2.19 |  | 7.7 | 0.18158 | 0.71558 | 33.1558 | 12.5763 | 12.9536 | 391.0194 | 220.5023 | 387.447 | 1.6873 | 47.8127 | 0.27092 | 7.57 | 7.62 | 7.67 | 221 | 268 | 416 | 389.7671 | 6.306 | 17.8439 | 387.9992 | 43.0411 | BMRL | 0.167 | 0.451 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 204 | 198 | 201 | 2.9851 | 465 | 563.5474 | -21.193 | 35.1613 | 559.8015 | 64.0944 | Total hardness | mg/L as CaCO3 | 256 | 786 | 818.7549 | -4.1673 | 17.4194 | 813.509 | 68.5314 | Total hardness | mg/L as CaCO3 | 202 | 412 | 438.3339 | -6.3917 | 34.8387 | 435.867 | 53.6556 | Total hardness | mg/L as CaCO3 | 164 | 322 | 368.1504 | -14.3324 | 47.0968 | 366.0285 | 55.1947 | UV254 p, cm-1 | #DIV/0! | 0.012 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.012 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 4.0476 | 3.098 | 3.5728 | 26.5778 | 1999-02-10 | 14:30 | 5.75 | 23 | 51 | 51 | 263 | 6.1 | 2.97 | 9.07 | 0.18158 | 0.67255 | 27.9967 | 13.9229 | 14.5972 | 0 | 0 | 0 | 0 | 51 | 0.28622 | 1999-02-12 | 9:00 | 23 | 23.4 | 49 | 50 | 263 | 4.84 | 0.22 |  | 5.06 | 0.18158 | 0.95652 | 50.9763 | 11.047 | 11.4459 | 461.0208 | 260.2718 | 457.3264 | 1.989 | 47.511 | 0.24091 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 163 | 164 | 163.5 | 0.61162 | 417 | 494.4492 | -18.573 | 37.8327 | 491.0298 | 66.7026 | Calcium hardness | mg/L as CaCO3 | 208 | 750 | 781.1763 | -4.1568 | 20.9125 | 775.8333 | 73.1901 | Calcium hardness | mg/L as CaCO3 | 156 | 366 | 390.1456 | -6.5972 | 40.6844 | 387.7016 | 59.7629 | Calcium hardness | mg/L as CaCO3 | 142 | 274 | 311.1931 | -13.5741 | 46.0076 | 309.4346 | 54.1099 | BromideF, ug/L | 85 | 85 | 85 | 85 | BromideF, ug/L | 85 | 85 | 85 | 85 | Current Process Water Rate ($/1000 gal) | 0.47
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 85 | 85 | 85 | 0 | 1999-02-10 | 15:00 | 6.25 | 23 | 51 | 51 | 263 | 6.17 | 2.3 | 8.47 | 0.18158 | 0.72845 | 30.0508 | 14.0827 | 14.7647 | 0 | 0 | 0 | 0 | 51 | 0.2895 | 1999-02-12 | 9:30 | 23.5 | 23.4 | 49 | 50 | 263 | 5.24 | 3.31 |  | 8.55 | 0.18158 | 0.61287 | 29.7602 | 11.96 | 12.3919 | 367.0364 | 207.0724 | 363.8493 | 1.5837 | 47.9163 | 0.25861 | 7.58 | 7.54 | 7.69 | 230 | 269 | 530 | 330.7402 | 37.5962 | 14.4981 | 329.7366 | 30.2474 | 0.017 | 0.169 | 1.21 | 0.39671 | 67.2138 | 89.6341 | 0.39293 | 95.6735 | [8 empty] | Turbidity | ntu | 0.073 | 0.076 | 0.0745 | 4.0268 | 0.348 | 0.89106 | -156.0526 | 76.7188 | 0.88263 | 91.5593 | Turbidity | ntu | 0.099 | 0.85 | 2.4021 | -182.6031 | 69.0625 | 2.3807 | 95.8415 | Turbidity | ntu | 0.087 | 0.511 | 0.59687 | -16.804 | 72.8125 | 0.59155 | 85.2928 | Turbidity | ntu | 0.056 | 0.495 | 0.42515 | 14.1114 | 82.5 | 0.42131 | 86.7082 | Bromidep, ug/L | 76.5 | 85 | 75 | 67 | Bromidep, ug/L | 76.5 | 85 | 75 | 67 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 9 | 8 | 8.5 | 11.7647 | 1999-02-10 | 15:30 | 6.75 | 23 | 51 | 51 | 263 | 6.11 | 1.71 | 7.82 | 0.18158 | 0.78133 | 32.6317 | 13.9457 | 14.6211 | 0 | 0 | 0 | 0 | 51 | 0.28669 | 1999-02-12 | 10:00 | 24 | 23.2 | 50 | 50 | 263 | 5.32 | 2.26 |  | 7.58 | 0.18158 | 0.70185 | 33.6966 | 12.1426 | 12.6556 | 387.5727 | 218.6289 | 384.1552 | 1.6724 | 48.3276 | 0.26187 | 7.56 | 7.24 | 7.78 | 233 | 273 | 479 | 353.7434 | 26.1496 | 13.3829 | 352.5222 | 33.9049 | 0.015 | 0.169 | 1.149 | 0.51474 | 55.2008 | 90.8537 | 0.50969 | 97.057 | [8 empty] | Ammonia | mg NH3-N / L | 0.48 | 0.46 | 0.47 | 4.2553 | NA | 0.087496 | #VALUE! | -32.3944 | 0.091448 | -413.9534 | Ammonia | mg NH3-N / L | 0.44 | NA | -0.44582 | #VALUE! | -23.9437 | -0.43756 | 200.5575 | Ammonia | mg NH3-N / L | 0.49 | NA | 0.19458 | #VALUE! | -38.0282 | 0.19767 | -147.8926 | Ammonia | mg NH3-N / L | 0.5 | NA | 0.29725 | #VALUE! | -40.8451 | 0.29936 | -67.0256 | AlkF, mg/L CaCO3 | 290 | 290 | 290 | 290 | AlkF, mg/L CaCO3 | 290 | 290 | 290 | 290
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1 | 1.22 | 1.11 | 19.8198 | 1999-02-10 | 16:00 | 7.25 | 23 | 52 | 52 | 263 | 6.17 | 2.33 | 8.5 | 0.18158 | 0.72588 | 29.9412 | 14.0827 | 14.7647 | 0 | 0 | 0 | 0 | 52 | 0.28394 | 1999-02-12 | 11:15 | 25.25 | 23.2 | 49 | 50 | 263 | 5.41 | 2.24 |  | 7.65 | 0.18158 | 0.70719 | 33.3791 | 12.348 | 12.8697 | 388.9116 | 219.3508 | 385.4237 | 1.6782 | 47.8218 | 0.26912 | 7.79 | 7.69 | 7.64 | 221 | 269 | 428 | 384.9286 | 10.0634 | 17.8439 | 383.2425 | 42.3342 | BMRL | 0.169 | 0.709 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | 0.6 | 0.8 | 0.7 | 28.5714 | 14 | 13.8382 | 1.1558 | 84.9462 | 13.7024 | 94.8914 | Total organic carbon | mg/L | 0.8 | 47.8 | 40.9223 | 14.3884 | 82.7957 | 40.5483 | 98.027 | Total organic carbon | mg/L | 0.6 | 8.8 | 9.4625 | -7.5286 | 87.0968 | 9.37 | 93.5966 | Total organic carbon | mg/L | 0.5 | 6.3 | 6.3029 | -0.046104 | 89.2473 | 6.2426 | 91.9905 | Alkp, mg/L CaCO3 | 191 | 324 | 148 | 142 | Alkp, mg/L CaCO3 | 191 | 324 | 148 | 142
Plant Name | Hollywood Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 8 | 6.78 | 7.39 | 16.5088 | 1999-02-10 | 16:30 | 7.75 | 23 | 52 | 52 | 263 | 6.3 | 2.47 | 8.77 | 0.18158 | 0.71836 | 28.9886 | 14.3794 | 15.0758 | 0 | 0 | 0 | 0 | 52 | 0.28992 | 1999-02-12 | 11:45 | 25.75 | 23 | 49 | 50 | 263 | 5.5 | 2.32 |  | 7.82 | 0.18158 | 0.70332 | 32.6317 | 12.5535 | 13.1614 | 388.0003 | 218.8035 | 384.462 | 1.6743 | 47.8257 | 0.2752 | 7.75 | 7.73 | 7.68 | 214 | 270 | 402 | 399.3879 | 0.64977 | 20.4461 | 397.4495 | 46.1567 | BMRL | 0.169 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.52 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.012 | 1.672 | 1.5961 | 4.5424 | 92.6829 | 1.5813 | 99.2411 | UV254 | cm-1 | BMRL | 0.344 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 310 | 310 | 310 | 310 | T-HdF, mg/L CaCO3 | 310 | 310 | 310 | 310
Treatment Plant Category | Other/GW | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | 1999-02-10 | 17:00 | 8.25 | 23 | 52 | 52 | 263 | 6.2 | 2.05 | 8.25 | 0.18158 | 0.75152 | 30.8788 | 14.1512 | 14.8365 | 0 | 0 | 0 | 0 | 52 | 0.28532 | 1999-02-12 | 13:00 | 27 | 23 | 49 | 50 | 263 | 5.6 | 2.59 |  | 8.19 | 0.18158 | 0.68376 | 31.1123 | 12.7817 | 13.4007 | 383.3195 | 216.1272 | 379.7595 | 1.6541 | 47.8459 | 0.28008 | 7.75 | 7.79 | 7.74 | 214 | 268 | 406 | 387.9189 | 4.4535 | 20.4461 | 386.0673 | 44.5693 | BMRL | 0.167 | 0.541 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | NR | NR | #DIV/0! | #VALUE! | 3.7143 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.5 | 3.4979 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.9091 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | NR | 3.4921 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 201 | 256 | 202 | 164 | T-Hdp, mg/L CaCO3 | 201 | 256 | 202 | 164
Process Train Name | Blend from nanofiltration and lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.02 | 8 | 8.01 | 0.24969 | 1999-02-10 | 17:15 | 8.5 | 23 | 52 | 52 | 263 | 6.22 | 2.71 | 8.93 | 0.18158 | 0.69653 | 28.4513 | 14.1968 | 14.8844 | 0 | 0 | 0 | 0 | 52 | 0.28624 | 1999-02-12 | 14:00 | 28 | 23.1 | 49 | 50 | 263 | 5.6 | 2.28 |  | 7.88 | 0.18158 | 0.71066 | 32.3756 | 12.7817 | 13.3612 | 389.8371 | 219.802 | 386.2166 | 1.6822 | 47.8178 | 0.27942 | 7.66 | 7.73 | 7.72 | 213 | 271 | 400 | 406.5439 | -1.636 | 20.8178 | 404.4833 | 47.3402 | BMRL | 0.169 | 0.529 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 76 | 77 | 76.5 | 1.3072 | --- | 104.772 | --- | 10 | 104.4799 | 26.7802 | Bromide | mg/L | 85 | --- | 85 | --- | 0 | 85 | 0 | Bromide | mg/L | 75 | --- | 96.8828 | --- | 11.7647 | 96.6544 | 22.4039 | Bromide | mg/L | 67 | --- | 92.1692 | --- | 21.1765 | 91.9076 | 27.1007 | Ca-HdF, mg/L CaCO3 | 263 | 263 | 263 | 263 | Ca-HdF, mg/L CaCO3 | 263 | 263 | 263 | 263
ICR Treatment Plant Identification Number | 298 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | 1999-02-10 | 17:30 | 8.75 | 23 | 52 | 52 | 263 | 6.27 | 2.6 | 8.87 | 0.18158 | 0.70688 | 28.6505 | 14.3109 | 15.004 | 0 | 0 | 0 | 0 | 52 | 0.28854 | 1999-02-12 | 15:00 | 29 | 23.1 | 49 | 50 | 263 | 5.5 | 2.43 |  | 7.93 | 0.18158 | 0.69357 | 32.1652 | 12.5535 | 13.1226 | 385.6339 | 217.469 | 382.1172 | 1.6641 | 47.8359 | 0.27432 | 7.61 | 7.7 | 7.75 | 222 | 270 | 399 | 375.3786 | 5.9202 | 17.4721 | 373.7748 | 40.606 | BMRL | 0.168 | 0.52 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 163.5 | 208 | 156 | 142 | Ca-Hdp, mg/L CaCO3 | 163.5 | 208 | 156 | 142
PWSID Number of Plant (if assigned) | FL4060642 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 380 | 400 | 390 | 5.1282 | 1999-02-11 | 8:30 | 23.75 | 22.9 | 52 | 52 | 263 | 6.07 | 2.27 | 8.34 | 0.18158 | 0.72782 | 30.5348 | 13.8545 | 14.5684 | 0 | 0 | 0 | 0 | 52 | 0.28016 | 1999-02-12 | 16:00 | 30 | 23.1 | 49 | 50 | 272 | 5.6 | 2.56 |  | 8.16 | 0.18779 | 0.68627 | 32.3333 | 12.7817 | 13.3612 | 383.8528 | 216.4959 | 380.4072 | 1.6563 | 47.8437 | 0.27927 | 7.6 | 7.7 | 7.61 | 223 | 270 | 396 | 369.625 | 6.6604 | 17.1004 | 368.1156 | 39.4212 | BMRL | 0.169 | 0.476 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.88 | 0.73 | 0.805 | 18.6335 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.16 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.02 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 95 | 100 | 97.5 | 5.1282 | 1999-02-11 | 8:45 | 24 | 22.9 | 52 | 52 | 263 | 6.13 | 3.2 | 9.33 | 0.18158 | 0.65702 | 27.1886 | 13.9914 | 14.7124 | 0 | 0 | 0 | 0 | 52 | 0.28293 | 1999-02-12 | 17:00 | 31 | 23.1 | 49 | 50 | 272 | 5.54 | 2.41 |  | 7.95 | 0.18779 | 0.69686 | 33.2138 | 12.6448 | 13.218 | 386.375 | 217.9398 | 382.9443 | 1.6672 | 47.8328 | 0.27634 | 7.75 | 7.89 | 7.67 | 211 | 269 | 391 | 402.3278 | -2.8971 | 21.5613 | 400.3794 | 47.3 | BMRL | 0.169 | 0.431 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 4.12 | 4.27 | 4.195 | 3.5757 | --- | 14.822 | --- | 43.2341 | 14.7122 | 71.4862 | SDS-Cl2 demand | mg/L | 4.2 | --- | 37.4442 | --- | 43.1664 | 37.1343 | 88.6897 | SDS-Cl2 demand | mg/L | 4.34 | --- | 11.0142 | --- | 41.272 | 10.9446 | 60.3457 | SDS-Cl2 demand | mg/L | 4.48 | --- | 8.549 | --- | 39.3775 | 8.5067 | 47.3358 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 30 | 29 | 29.5 | 3.3898 | 1999-02-11 | 9:00 | 24.25 | 23 | 52 | 52 | 263 | 6.2 | 3.13 | 9.33 | 0.18158 | 0.66452 | 27.1886 | 14.1512 | 14.8365 | 0 | 0 | 0 | 0 | 52 | 0.28532 | 1999-02-12 | 18:00 | 32 | 23.1 | 49 | 50 | 272 | 5.6 | 2.6 |  | 8.2 | 0.18779 | 0.68293 | 32.1707 | 12.7817 | 13.3612 | 383.055 | 216.0459 | 379.6166 | 1.6529 | 47.8471 | 0.27925 | 7.77 | 7.92 | 7.68 | 224 | 268 | 395 | 365.9231 | 7.3612 | 16.7286 | 364.4621 | 38.5396 | BMRL | 0.167 | 0.466 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 53.9394 | 56.1261 | 55.2795 | 54.2683 | Qp/QT (THM4), % | 85.1082 | 88.5586 | 87.2227 | 85.6272
State Approved Plant Capacity (MGD) | 57.5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 8 | 6.6 | 7.3 | 19.1781 | 1999-02-11 | 9:15 | 24.5 | 23 | 61 | 62 | 263 | 7.23 | 4.83 | 12.06 | 0.18158 | 0.5995 | 20.8076 | 16.5021 | 17.3013 | 0 | 0 | 0 | 0 | 61.5 | 0.28132 | 1999-02-13 | 10:00 | 48 | 23.1 | 49 | 50 | 263 | 5.16 | 2.38 |  | 7.54 | 0.18158 | 0.68435 | 33.8806 | 11.7774 | 12.3114 | 383.3029 | 216.2789 | 380.026 | 1.6539 | 47.8461 | 0.25731 | 7.75 | 7.84 | 7.62 | 223 | 271 | 412 | 368.7311 | 10.5022 | 17.1004 | 367.3015 | 39.2869 | BMRL | 0.169 | 0.612 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 8.22 | 8.19 | 8.205 | 0.36563 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.05 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.1 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.19 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-02-11 | 9:30 | 24.75 | 23 | 40 | 41 | 263 | 4.66 | 2.44 | 7.1 | 0.18158 | 0.65634 | 36.0423 | 10.6362 | 11.1513 | 0 | 0 | 0 | 0 | 40.5 | 0.27534 | 1999-02-13 | 11:00 | 49 | 23.2 | 49 | 50 | 263 | 5.45 | 2.41 |  | 7.86 | 0.18158 | 0.69338 | 32.4606 | 12.4393 | 12.9649 | 385.5712 | 217.452 | 382.0873 | 1.6638 | 47.8362 | 0.27103 | 7.83 | 7.93 | 7.62 | 221 | 270 | 415 | 377.5477 | 9.0246 | 17.8439 | 375.9257 | 41.2118 | BMRL | 0.168 | 0.622 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 31.6609 | 31.4437 | 31.6795 | 32.0793 | SDS-HAA5b, ug/L | 12.1648 | 11.8221 | 12.1941 | 12.8249
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 133 | 135.6 | 134.3 | 1.936 | 1999-02-11 | 10:00 | 25.25 | 23 | 52 | 53 | 272 | 6.2 | 3.45 | 9.65 | 0.18779 | 0.64249 | 27.1865 | 14.1512 | 14.8365 | 0 | 0 | 0 | 0 | 52.5 | 0.2826 | 1999-02-13 | 12:00 | 50 | 23.2 | 49 | 50 | 263 | 5.46 | 2.37 |  | 7.83 | 0.18158 | 0.69732 | 32.5888 | 12.4622 | 12.9887 | 386.5251 | 217.9863 | 383.0262 | 1.6679 | 47.8321 | 0.27155 | 7.78 | 7.72 | 7.71 | 228 | 271 | 395 | 363.4557 | 7.9859 | 15.2416 | 362.0496 | 37.0252 | 0.009 | 0.17 | 0.61 | 0.52109 | 14.5756 | 94.5122 | 0.51577 | 98.255 | [8 empty] | SDS-TOX | mg Cl- /L | 29 | 35 | 32 | 18.75 | --- | 1222.7521 | --- | 91.7949 | 1210.4489 | 97.3564 | SDS-TOX | mg Cl- /L | 36 | --- | 3725.1713 | --- | 90.7692 | 3690.7813 | 99.0246 | SDS-TOX | mg Cl- /L | 33 | --- | 814.2147 | --- | 91.5385 | 806.0604 | 95.906 | SDS-TOX | mg Cl- /L | 32 | --- | 532.5879 | --- | 91.7949 | 527.385 | 93.9323 | SDS-TOXb, ug Cl- /L | 196.897 | 191.3135 | 192.6522 | 195.7195 | SDS-TOXb, ug Cl- /L | 85.3126 | 76.5027 | 78.6149 | 83.4547
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 2 | BMRL | 2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-13 | 13:00 | 51 | 23.4 | 49 | 50 | 263 | 5.4 | 2.09 |  | 7.49 | 0.18158 | 0.72096 | 34.1135 | 12.3252 | 12.7702 | 392.3134 | 221.2732 | 388.8015 | 1.6928 | 47.8072 | 0.26712 | 7.69 | 7.63 | 7.64 | 223 | 270 | 395 | 387.8517 | 1.8097 | 17.1004 | 386.1593 | 42.2518 | BMRL | 0.169 | 0.585 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 2.9 | 2.8 | 2.85 | 3.5088 | --- | 317.6675 | --- | 97.0769 | 314.4148 | 99.0936 | SDS-CHCl3 | mg/L | 4.1 | --- | 977.4576 | --- | 95.7949 | 968.3841 | 99.5766 | SDS-CHCl3 | mg/L | 3.6 | --- | 209.0792 | --- | 96.3077 | 206.9344 | 98.2603 | SDS-CHCl3 | mg/L | 3.3 | --- | 135.0189 | --- | 96.6154 | 133.6499 | 97.5309 | SDS-CDb, mg/L | 5.6666 | 5.5996 | 5.704 | 5.8108 | SDS-CDb, mg/L | 4.6708 | 4.565 | 4.7297 | 4.8982
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 28 | 28 | 28 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-13 | 14:30 | 52.5 | 23.4 | 49 | 50 | 263 | 5.48 | 2.4 |  | 7.88 | 0.18158 | 0.69543 | 32.3756 | 12.5078 | 12.9594 | 386.0762 | 217.7258 | 382.5683 | 1.666 | 47.834 | 0.27092 | 7.75 | 7.8 | 7.58 | 224 | 268 | 407 | 371.75 | 8.6609 | 16.7286 | 370.2107 | 39.4939 | BMRL | 0.17 | 0.61 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 4.7 | 4.7 | 4.7 | 0 | --- | 87.1879 | --- | 84.0678 | 86.3356 | 94.5561 | SDS-BDCM | mg/L | 6.5 | --- | 246.1919 | --- | 77.9661 | 243.9575 | 97.3356 | SDS-BDCM | mg/L | 5.7 | --- | 57.781 | --- | 80.678 | 57.2374 | 90.0415 | SDS-BDCM | mg/L | 5.2 | --- | 39.1785 | --- | 82.3729 | 38.8253 | 86.6067 | TOCb, mg/L | 2.5194 | 2.4891 | 2.4112 | 2.3979 | TOCb, mg/L | 1.2882 | 1.2405 | 1.1175 | 1.0965
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 34 | 36 | 35 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-13 | 15:30 | 53.5 | 23.4 | 49 | 50 | 272 | 5.45 | 1.91 |  | 7.36 | 0.18779 | 0.74049 | 35.9565 | 12.4393 | 12.8885 | 397.1917 | 224.0741 | 393.723 | 1.7138 | 47.7862 | 0.26971 | 7.75 | 7.69 | 7.68 | 230 | 270 | 424 | 380.2827 | 10.3107 | 14.4981 | 378.7771 | 39.2783 | BMRL | 0.169 | 0.593 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 6.8 | 7.3 | 7.05 | 7.0922 | --- | 7.8815 | --- | 3.4247 | 7.8729 | 10.4528 | SDS-DBCM | mg/L | 8.7 | --- | -5.8899 | --- | -19.1781 | -5.7539 | 251.2008 | SDS-DBCM | mg/L | 8.1 | --- | 6.3494 | --- | -10.9589 | 6.3677 | -27.2054 | SDS-DBCM | mg/L | 7.2 | --- | 7.3398 | --- | 1.3699 | 7.3384 | 1.8856 | UV254 b, cm-1 | #DIV/0! | 0.078688 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.029391 | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-13 | 16:30 | 54.5 | 23.2 | 49 | 50 | 263 | 5.45 | 2.24 |  | 7.69 | 0.18158 | 0.70871 | 33.2003 | 12.4393 | 12.9649 | 389.3006 | 219.5553 | 385.7831 | 1.6799 | 47.8201 | 0.27112 | 7.68 | 7.54 | 7.63 | 231 | 269 | 420 | 361.4554 | 13.9392 | 14.1264 | 360.1037 | 35.8518 | BMRL | 0.168 | 0.589 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 3.9 | 4.5 | 4.2 | 14.2857 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 80.4152 | 85 | 79.472 | 75.2317 | Bromideb, ug/L | 77.7658 | 85 | 76.2777 | 69.5871
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1.5 | 1.3 | 1.4 | 14.2857 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-13 | 17:30 | 55.5 | 23.2 | 49 | 50 | 263 | 5.5 | 2.4 |  | 7.9 | 0.18158 | 0.6962 | 32.2911 | 12.5535 | 13.0838 | 386.2699 | 217.8277 | 382.7474 | 1.6668 | 47.8332 | 0.27353 | 7.69 | 7.63 | 7.71 | 224 | 270 | 412 | 372.125 | 9.6784 | 16.7286 | 370.5762 | 39.5536 | BMRL | 0.169 | 0.59 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 18.3 | 19.3 | 18.8 | 5.3191 | --- | 402.9672 | --- | 86.0015 | 398.9979 | 95.2882 | SDS-THM4 | mg/L | 23.3 | --- | 1180.0741 | --- | 82.6508 | 1169.2908 | 98.0073 | SDS-THM4 | mg/L | 21.6 | --- | 268.2188 | --- | 83.9166 | 265.6445 | 91.8688 | SDS-THM4 | mg/L | 19.5 | --- | 180.0237 | --- | 85.4803 | 178.3553 | 89.0668 | Alkb, mg/L CaCO3 | 236.6 | 309.0829 | 211.5031 | 209.6829 | Alkb, mg/L CaCO3 | 205.7429 | 320.1099 | 166.1437 | 163.2718
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 8.9 | 8.3 | 8.6 | 6.9767 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 15:00 | 77 | 23.3 | 50 | 50 | 263 | 5.03 | 1.05 |  | 6.08 | 0.18158 | 0.8273 | 42.2566 | 11.4807 | 11.9305 | 420.5715 | 237.3598 | 417.0675 | 1.8146 | 48.1854 | 0.24759 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 251.2061 | 279.6919 | 250.2981 | 230.7683 | T-Hdb, mg/L CaCO3 | 217.232 | 262.1784 | 215.7995 | 184.9843
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 16:00 | 78 | 23.3 | 50 | 51 | 272 | 5.3 | 4.85 |  | 10.15 | 0.18779 | 0.52217 | 25.798 | 12.097 | 12.5709 | 348.2276 | 196.4993 | 345.2711 | 1.5025 | 48.9975 | 0.25656 | [27 empty] | SDS-DCAA* | mg/L | 1 | BMRL | 1 | #VALUE! | --- | 90.8053 | --- | 96.4286 | 89.8774 | 98.8874 | SDS-DCAA* | mg/L | 1.4 | --- | 278.6089 | --- | 95 | 276.0248 | 99.4928 | SDS-DCAA* | mg/L | 1.2 | --- | 59.8458 | --- | 95.7143 | 59.2337 | 97.9741 | SDS-DCAA* | mg/L | 1.1 | --- | 38.714 | --- | 96.0714 | 38.3231 | 97.1297 | Ca-Hdb, mg/L CaCO3 | 209.3303 | 232.1306 | 203.8509 | 197.3354 | Ca-Hdb, mg/L CaCO3 | 178.3173 | 214.2928 | 169.6717 | 159.3911
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 2.2 | BMRL | 2.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 16:30 | 78.5 | 23.3 | 50 | 50 | 272 | 5.12 | 0.26 |  | 5.38 | 0.18779 | 0.95167 | 49.5576 | 11.6861 | 12.1439 | 459.4372 | 259.3294 | 455.6705 | 1.9822 | 48.0178 | 0.2529 | [27 empty] | SDS-TCAA* | mg/L | 1 | BMRL | 1 | #VALUE! | --- | 114.0882 | --- | 97.1429 | 112.9197 | 99.1144 | SDS-TCAA* | mg/L | 1.2 | --- | 353.4429 | --- | 96.5714 | 350.1593 | 99.6573 | SDS-TCAA* | mg/L | 1.1 | --- | 75.2826 | --- | 96.8571 | 74.5083 | 98.5237 | SDS-TCAA* | mg/L | 1 | --- | 48.5419 | --- | 97.1429 | 48.0477 | 97.9187
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 11 | 9.8 | 10.4 | 11.5385 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 17:00 | 79 | 23.2 | 50 | 50 | 263 | 5.18 |  |  | 5.18 | 0.18158 | 1 | 49.7722 | 11.8231 | 12.3226 | 476.7547 | 269 | 472.6628 | 2.0571 | 47.9429 | 0.25703 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 65.5 | 65.3 | 65.4 | 0.30581 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 18:00 | 80 | 23.2 | 50 | 50 | 263 | 5.02 | 0.43 |  | 5.45 | 0.18158 | 0.9211 | 47.2569 | 11.4579 | 11.942 | 449.2666 | 253.5588 | 445.531 | 1.9384 | 48.0616 | 0.24847 | 7.31 | 7.64 |  | 215 | 267 |  | 899.4186 |  | 20.0743 | 892.8867 | 75.9208 | 0.01 | 0.168 |  | 1.9619 |  | 93.9024 | 1.9432 | 99.4854 | [8 empty] | SDS-DBAA* | mg/L | 1.9 | 1.8 | 1.85 | 5.4054 | --- | 0.35324 | --- | -32.1429 | 0.36871 | -401.7501 | SDS-DBAA* | mg/L | 2.3 | --- | -7.0792 | --- | -64.2857 | -6.9918 | 132.8956 | SDS-DBAA* | mg/L | 2.1 | --- | 0.56821 | --- | -50 | 0.5842 | -259.4688 | SDS-DBAA* | mg/L | 1.9 | --- | 1.2009 | --- | -35.7143 | 1.2081 | -57.269 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 74.4 | 73.6 | 74 | 1.0811 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 18:30 | 80.5 | 23.2 | 50 | 50 | 263 | 5.02 | 0.48 |  | 5.5 | 0.18158 | 0.91273 | 46.8182 | 11.4579 | 11.942 | 446.5461 | 252.0235 | 442.8332 | 1.9267 | 48.0733 | 0.24841 | 7.55 | 7.68 |  | 220 | 265 |  | 781.4583 |  | 18.2156 | 776.0999 | 71.6531 | 0.01 | 0.165 |  | 1.7746 |  | 93.9024 | 1.7577 | 99.4311 | [8 empty] | SDS-BCAA* | mg/L | 1.5 | 1.4 | 1.45 | 6.8966 | --- | 25.2318 | --- | 83.1395 | 24.9861 | 94.1968 | SDS-BCAA* | mg/L | 2.2 | --- | 68.8969 | --- | 74.4186 | 68.2751 | 96.7777 | SDS-BCAA* | mg/L | 1.7 | --- | 16.7991 | --- | 80.2326 | 16.6415 | 89.7846 | SDS-BCAA* | mg/L | 1.6 | --- | 11.388 | --- | 81.3953 | 11.2863 | 85.8235 | Qp/QT (HAA5), % | 18.2254 | 18.843 | 18.6885 | 18.5668 | Qp/QT (HAA5), % | 61.3909 | 63.4711 | 62.9508 | 62.5407
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 19:00 | 81 | 23.2 | 50 | 50 | 263 | 5.02 | 0.32 |  | 5.34 | 0.18158 | 0.94007 | 48.2509 | 11.4579 | 11.942 | 455.5552 | 257.108 | 451.7673 | 1.9655 | 48.0345 | 0.24861 |  |  |  | 221 | 266 |  | 1022 |  | 17.8439 | 1014.3555 | 78.2128 | 0.01 | 0.166 |  | 2.5799 |  | 93.9024 | 2.5553 | 99.6087 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 113.2496 | 113.3843 | 113.238 | 112.9853 | SDS-THM4b, ug/L | 63.3935 | 63.8471 | 63.3544 | 62.5033
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 19:30 | 81.5 | 23.4 | 50 | 50 | 263 | 5.04 | 2.44 |  | 7.48 | 0.18158 | 0.6738 | 34.1604 | 11.5035 | 11.9189 | 380.7661 | 214.891 | 377.5874 | 1.6429 | 48.3571 | 0.24648 | [27 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-02-14 | 20:00 | 82 | 23.4 | 50 | 50 | 263 | 5.04 | 1.04 |  | 6.08 | 0.18158 | 0.82895 | 42.2566 | 11.5035 | 11.9189 | 421.0484 | 237.6249 | 417.5334 | 1.8167 | 48.1833 | 0.24737 | 7.65 | 7.69 |  | 210 | 266 |  | 554.9231 |  | 21.9331 | 551.6181 | 61.9302 | 0.01 | 0.167 |  | 0.91031 |  | 93.9024 | 0.90168 | 98.891 | [8 empty] | SDS-DCBAA | mg/L | 1.3 | 1.2 | 1.25 | 8 | --- | 31.684 | --- | 87.9808 | 31.3696 | 96.0152 | SDS-DCBAA | mg/L | 1.9 | --- | 90.4818 | --- | 81.7308 | 89.656 | 97.8808 | SDS-DCBAA | mg/L | 1.6 | --- | 20.8568 | --- | 84.6154 | 20.6558 | 92.254 | SDS-DCBAA | mg/L | 1.4 | --- | 13.9846 | --- | 86.5385 | 13.8538 | 89.8945 | SDS-TOXb, ug Cl- /L | 324.753 | 323.2959 | 323.282 | 323.5309 | SDS-TOXb, ug Cl- /L | 170.2206 | 165.3124 | 165.2656 | 166.1042
[44 empty] | 1999-02-14 | 20:30 | 82.5 | 23.2 | 50 | 50 | 263 | 4.96 | 0.6 |  | 5.56 | 0.18158 | 0.89209 | 46.3022 | 11.3209 | 11.7993 | 439.9423 | 248.3215 | 436.3284 | 1.8981 | 48.1019 | 0.2453 |  |  |  | 218 | 265 |  | 690.6 |  | 18.9591 | 686.1435 | 68.2282 | 0.01 | 0.167 |  | 1.4371 |  | 93.9024 | 1.4236 | 99.2976 | [8 empty] | SDS-HAA5 | mg/L | 3.9 | 1.8 | 2.85 | 73.6842 | --- | 210.899 | --- | 95.6422 | 208.7494 | 98.6347 | SDS-HAA5 | mg/L | 4.9 | --- | 635.394 | --- | 92.5076 | 629.5166 | 99.2216 | SDS-HAA5 | mg/L | 4.4 | --- | 137.8849 | --- | 93.2722 | 136.4915 | 96.7764 | SDS-HAA5 | mg/L | 4 | --- | 89.855 | --- | 93.8838 | 88.9627 | 95.5037 | SDS-CDb, mg/L | 6.8077 | 6.7889 | 6.82 | 6.8497 | SDS-CDb, mg/L | 5.4286 | 5.3653 | 5.47 | 5.5701
[44 empty] | 1999-02-14 | 21:00 | 83 | 23.2 | 50 | 50 | 263 | 4.9 | 0.46 |  | 5.36 | 0.18158 | 0.91418 | 48.0672 | 11.184 | 11.6565 | 446.9378 | 252.2956 | 443.3114 | 1.9283 | 48.0717 | 0.24248 | 7.67 |  |  | 222 | 265 |  | 769.6522 |  | 17.4721 | 764.5505 | 70.9633 | 0.01 | 0.166 |  | 1.8044 |  | 93.9024 | 1.7877 | 99.4406 | [8 empty] | SDS-HAA6 | mg/L | 5.4 | 3.2 | 4.3 | 51.1628 | --- | 236.1308 | --- | 94.1892 | 233.7354 | 98.1603 | SDS-HAA6 | mg/L | 7.1 | --- | 704.2909 | --- | 90.4054 | 697.7917 | 98.9825 | SDS-HAA6 | mg/L | 6.1 | --- | 154.684 | --- | 91.7568 | 153.133 | 96.0165 | SDS-HAA6 | mg/L | 5.6 | --- | 101.2431 | --- | 92.4324 | 100.249 | 94.4139 | TOCb, mg/L | 3.9301 | 3.9245 | 3.8931 | 3.8795 | TOCb, mg/L | 2.2251 | 2.2064 | 2.1005 | 2.0546
[44 empty] | 1999-02-15 | 8:45 | 94.75 | 23.2 | 50 | 50 | 263 | 4.53 | 0.17 |  | 4.7 | 0.18158 | 0.96383 | 54.9574 | 10.3395 | 10.7763 | 463.3219 | 261.7076 | 459.8492 | 1.9988 | 48.0012 | 0.2245 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.13536 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.067524 | #VALUE! | #VALUE!
[44 empty] | 1999-02-15 | 11:45 | 97.75 | 23.1 | 49 | 50 | 263 | 4.91 | 0.53 |  | 5.44 | 0.18158 | 0.90257 | 47.3456 | 11.2068 | 11.7149 | 443.2222 | 250.1939 | 439.6185 | 1.9123 | 47.5877 | 0.24617 | 7.69 | 7.7 | 7.75 |  | 268 | 602 |  | #VALUE! |  |  |  | 0.016 | 0.167 | 1.814 | 1.5351 | 15.3752 | 90.2439 | 1.5209 | 98.948 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 83.4508 | 85 | 83.1311 | 81.658 | Bromideb, ug/L | 79.7818 | 85 | 78.7049 | 73.7427
[44 empty] | 1999-02-15 | 14:00 | 100 | 23.1 | 49 | 50 | 263 | 4.93 | 0.41 |  | 5.34 | 0.18158 | 0.92322 | 48.2509 | 11.2525 | 11.7626 | 449.901 | 253.9555 | 446.228 | 1.9411 | 47.5589 | 0.24733 | 7.75 | 7.71 | 7.72 |  | 269 | 604 |  | #VALUE! |  |  |  | 0.014 | 0.167 | 1.789 | 1.9677 | -9.9865 | 91.4634 | 1.9493 | 99.2818 | [47 empty] | Alkb, mg/L CaCO3 | 271.9568 | 296.4066 | 263.4623 | 262.5212 | Alkb, mg/L CaCO3 | 229.223 | 311.5802 | 200.6098 | 197.4397
[44 empty] | 1999-02-15 | 15:00 | 101 | 23.1 | 49 | 50 | 263 | 4.95 | 0.51 |  | 5.46 | 0.18158 | 0.90659 | 47.1685 | 11.2981 | 11.8103 | 444.5298 | 250.9151 | 440.8857 | 1.9179 | 47.5821 | 0.24821 | 7.69 | 7.72 | 7.71 | 256 | 271 |  | 395.1765 |  | 4.8327 | 393.8667 | 35.0034 | 0.012 | 0.167 | 1.781 | 1.6393 | 7.9565 | 92.6829 | 1.624 | 99.2611 | [47 empty] | T-Hdb, mg/L CaCO3 | 290.1343 | 299.8248 | 289.8164 | 282.8925 | T-Hdb, mg/L CaCO3 | 243.0839 | 275.7256 | 242.0131 | 218.6906
[44 empty] | 1999-02-15 | 16:00 | 102 | 23.1 | 49 | 50 | 263 | 4.91 | 0.54 |  | 5.45 | 0.18158 | 0.90092 | 47.2569 | 11.2068 | 11.7149 | 442.6961 | 249.897 | 439.0967 | 1.91 | 47.59 | 0.24616 | 7.71 | 7.71 | 7.71 | 251 | 268 |  | 432.6667 |  | 6.6914 | 430.9709 | 41.7594 | 0.012 | 0.166 | 1.782 | 1.5461 | 13.2394 | 92.6829 | 1.5318 | 99.2166 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 244.8657 | 252.6364 | 243.0033 | 240.5342 | Ca-Hdb, mg/L CaCO3 | 201.9161 | 228.0909 | 195.6426 | 187.3257
[44 empty] | 1999-02-15 | 17:20 | 103.3333 | 22.9 | 50 | 50 | 263 | 5.15 | 2.95 |  | 8.1 | 0.18158 | 0.6358 | 31.4691 | 11.7546 | 12.3604 | 372.0838 | 209.952 | 368.909 | 1.6054 | 48.3946 | 0.25541 | [66 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-02-15 | 18:00 | 104 | 22.9 | 50 | 50 | 263 | 5.47 | 6.13 |  | 11.6 | 0.18158 | 0.47155 | 21.6724 | 12.485 | 13.1284 | 338.628 | 190.9708 | 335.5569 | 1.4612 | 48.5388 | 0.27047 | 7.58 | 7.46 | 7.56 | 187 | 265 | 360 | 342.1713 | 4.9524 | 30.4833 | 340.5576 | 45.0901 | 0.012 | 0.163 | 0.492 | 0.29963 | 39.0987 | 92.6829 | 0.29664 | 95.9547 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-02-15 | 18:30 | 104.5 | 23.1 | 50 | 50 | 263 | 5.28 | 4.95 |  | 10.23 | 0.18158 | 0.51613 | 24.7087 | 12.0513 | 12.5977 | 347.0798 | 195.8002 | 344.0427 | 1.4976 | 48.5024 | 0.25973 | 7.46 | 7.43 | 7.56 | 183 | 265 | 351 | 360.7333 | -2.773 | 31.9703 | 358.9492 | 49.0179 | 0.011 | 0.166 | 0.421 | 0.3272 | 22.2803 | 93.2927 | 0.32403 | 96.6052 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-02-15 | 19:00 | 105 | 23.1 | 50 | 50 | 263 | 5.39 | 5.41 |  | 10.8 | 0.18158 | 0.49907 | 23.3519 | 12.3024 | 12.8601 | 343.8055 | 193.917 | 340.7336 | 1.4835 | 48.5165 | 0.26507 | 7.58 | 7.51 | 7.81 | 180 | 266 | 349 | 357.671 | -2.4845 | 33.0855 | 355.8504 | 49.4169 | 0.011 | 0.162 | 0.352 | 0.31643 | 10.1039 | 93.2927 | 0.3133 | 96.489 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-02-15 | 19:30 | 105.5 | 23 | 50 | 50 | 263 | 5.55 | 4.33 |  | 9.88 | 0.18158 | 0.56174 | 25.6194 | 12.6676 | 13.2811 | 356.2854 | 200.9016 | 353.0064 | 1.5374 | 48.4626 | 0.27405 | 7.83 | 7.7 | 7.84 | 195 | 265 | 346 | 363.8499 | -5.1589 | 27.5093 | 362.0683 | 46.1428 | BMRL | 0.165 | 0.342 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-02-15 | 20:00 | 106 | 23 | 49 | 50 | 263 | 5.55 | 5.55 |  | 11.1 | 0.18158 | 0.5 | 22.6937 | 12.6676 | 13.2811 | 344.0165 | 193.9835 | 340.8504 | 1.4845 | 48.0155 | 0.2766 | 7.89 | 7.95 | 7.71 | 201 | 267 | 359 | 337 | 6.1281 | 25.2788 | 335.565 | 40.101 | 0.011 | 0.167 | 0.354 | 0.317 | 10.452 | 93.2927 | 0.31377 | 96.4943 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-02-15 | 20:30 | 106.5 | 23 | 50 | 50 | 254 | 5.38 | 3.73 |  | 9.11 | 0.17537 | 0.59056 | 26.8814 | 12.2796 | 12.8743 | 362.3226 | 204.2987 | 358.9754 | 1.5635 | 48.4365 | 0.2658 | 7.85 | 7.88 | 7.68 | 200 | 266 | 352 | 368.5228 | -4.694 | 25.6506 | 366.738 | 45.4652 | 0.01 | 0.166 | 0.356 | 0.38612 | -8.4616 | 93.9024 | 0.38214 | 97.3832 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-02-16 | 9:00 | 119 | 23 | 49 | 50 | 263 | 5.13 | 3.7 |  | 8.83 | 0.18158 | 0.58097 | 28.7848 | 11.709 | 12.276 | 360.1758 | 203.2397 | 357.1147 | 1.5541 | 47.9459 | 0.25604 | 7.53 | 7.32 | 7.58 | 217 | 266 | 424 | 341.0973 | 19.5525 | 19.3309 | 339.887 | 36.1553 | 0.012 | 0.166 | 0.66 | 0.37475 | 43.2203 | 92.6829 | 0.37121 | 96.7673 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-02-16 | 10:00 | 120 | 23 | 49 | 50 | 263 | 5.36 | 4.92 |  | 10.28 | 0.18158 | 0.5214 | 24.5837 | 12.2339 | 12.8264 | 348.1298 | 196.366 | 345.0368 | 1.5022 | 47.9978 | 0.26723 | 7.6 | 7.52 | 7.63 | 210 | 269 | 360 | 333.2764 | 7.4232 | 21.9331 | 332.0202 | 36.7508 | 0.012 | 0.167 | 0.422 | 0.32959 | 21.8973 | 92.6829 | 0.32636 | 96.323 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-02-16 | 11:00 | 121 | 23 | 49 | 50 | 263 | 5.37 | 3.6 |  | 8.97 | 0.18158 | 0.59866 | 28.32 | 12.2567 | 12.8503 | 363.9989 | 205.3136 | 360.7588 | 1.5707 | 47.9293 | 0.26811 | 7.75 | 7.62 | 7.65 | 207 | 267 | 357 | 361.4833 | -1.2558 | 23.0483 | 359.9062 | 42.485 | 0.009 | 0.166 | 0.4 | 0.39521 | 1.1979 | 94.5122 | 0.39127 | 97.6998 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-02-16 | 12:00 | 122 | 23 | 49 | 50 | 263 | 5.49 | 6.77 |  | 12.26 | 0.18158 | 0.4478 | 20.4519 | 12.5306 | 13.1375 | 334.273 | 188.5085 | 331.2303 | 1.4424 | 48.0576 | 0.27337 | 7.7 | 7.65 | 7.66 | 206 | 269 | 330 | 320.0886 | 3.0034 | 23.4201 | 318.8979 | 35.4025 | BMRL | 0.166 | 0.325 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-02-16 | 13:00 | 123 | 23 | 49 | 50 | 272 | 5.6 | 18.4 |  | 24 | 0.18779 | 0.23333 | 10.3333 | 12.7817 | 13.4007 | 299.4651 | 168.9005 | 296.777 | 1.2922 | 48.2078 | 0.27798 |  | 7.69 | 7.98 | 207 | 271 | 293 | 287.8696 | 1.751 | 23.0483 | 287.0371 | 27.8839 | BMRL | 0.166 | 0.213 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-02-16 | 14:00 | 124 | 23 | 49 | 50 | 272 | 5.53 | 15.73 |  | 21.26 | 0.18779 | 0.26011 | 11.794 | 12.6219 | 13.2332 | 303.403 | 171.1412 | 300.714 | 1.3092 | 48.1908 | 0.2746 |  |  |  | 210 | 273 | 301 | 289.7419 | 3.7402 | 21.9331 | 288.9313 | 27.3184 | BMRL | 0.166 | 0.218 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-16 | 14:30 | 124.5 | 23.3 | 49 | 50 | 272 | 5.55 | 15.2 |  | 20.75 | 0.18779 | 0.26747 | 12.1084 | 12.6676 | 13.1638 | 304.5062 | 171.7578 | 301.7975 | 1.3139 | 48.1861 | 0.27319 | 7.94 | 7.79 | 7.76 | 254 | 271 | 301 | 274.477 | 8.8116 | 5.5762 | 274.2681 | 7.3899 | BMRL | 0.166 | 0.222 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-16 | 15:00 | 125 | 23.3 | 49 | 50 | 272 | 5.54 | 14.93 |  | 20.47 | 0.18779 | 0.27064 | 12.2877 | 12.6448 | 13.1401 | 304.9824 | 172.0293 | 302.2745 | 1.316 | 48.184 | 0.27271 | 7.68 | 7.47 | 7.58 | 199 | 271 | 295 | 294.9745 | 0.0086278 | 26.0223 | 293.9972 | 32.3123 | BMRL | 0.167 | 0.221 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-16 | 16:00 | 126 | 23.3 | 49 | 50 | 272 | 5.6 | 15.2 |  | 20.8 | 0.18779 | 0.26923 | 12.0769 | 12.7817 | 13.2824 | 304.7753 | 171.8956 | 302.0396 | 1.3151 | 48.1849 | 0.27566 | 7.63 | 7.38 | 7.57 | 192 | 272 | 295 | 297.3684 | -0.80285 | 28.6245 | 296.2837 | 35.1973 | BMRL | 0.166 | 0.225 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-16 | 17:00 | 127 | 23.3 | 49 | 50 | 272 | 5.75 | 14.53 |  | 20.28 | 0.18779 | 0.28353 | 12.4122 | 13.1241 | 13.6382 | 306.9573 | 173.0837 | 304.1272 | 1.3246 | 48.1754 | 0.28309 | 7.9 | 7.76 | 7.76 | 200 | 269 | 298 | 296.3056 | 0.5686 | 25.6506 | 295.2876 | 32.2694 | BMRL | 0.166 | 0.222 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-17 | 8:30 | 142.5 | 23.3 | 49 | 50 | 272 | 5.65 | 11.3 | X | 16.95 | 0.18779 | 0.33333 | 15.0472 | 12.8958 | 13.401 | 314.7473 | 177.5053 | 311.8965 | 1.3582 | 48.1418 | 0.27837
[44 empty] | 1999-02-17 | 13:00 |  | 23.3 | 50 | 51 | 272 | 6.23 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 14.2196 | 14.7767 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-17 | 13:15 |  | 23.3 | 60 | 61 | 272 | 7.42 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 16.9358 | 17.5992 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-17 | 13:30 |  | 23.3 | 40 | 41 | 272 | 5.01 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 11.4351 | 11.883 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-02-17 | 14:00 |  | 23.3 | 50 | 51 | 272 | 6.17 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 14.0827 | 14.6344 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/8/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on T6: Alison Gusses: Consultant verified that cartridge filtration was the only pretreatment used during this study
Note on X11: Alison Gusses: Verified by consultant
Note on DG16: S Allgeier (7/9/99): Data responsible for high mass balance closure errors verified by consultant.
Note on DQ16: S Allgeier (7/9/99): Data responsible for high mass balance closure errors verified by consultant.
Note on EA16: Alison Gusses: Data responsible for high mass balance closure errors verified by consultant.
Note on EK16: Alison Gusses: Data responsible for high mass balance closure errors verified by consultant.