## XLE. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 1.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 2000 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.96904 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.88 | [7 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 19.3 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1998-04-09 | 1998-04-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.9 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.57 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 14.6 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -4.96 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 6:30 | 14:15 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 330 | [6 empty] | SDS-THM4F, ug/L | 71.08 | 71.08 | 71.08 | 71.08 | SDS-THM4F, ug/L | 71.08 | 71.08 | 71.08 | 71.08 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 112 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 0 | 174.75 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 0 | 0 | 0 | 0 | SDS-THM4p, ug/L | 0 | 0 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.97 | 6.29 | 6.13 | 5.2202 | 1998-04-07 | 14:00 | 0 | 24.5 | 76 | 76 | 350 | 6.6 | 38 | 44.6 | 0.23793 | 0.14798 | 6.8475 | 15.0341 | 14.0875 | 2339.3923 | 45.9229 | 2296.1441 | 22.7185 | 53.2815 | 0.2644 | 1998-04-09 | 7:00 | 0 | 24.5 | 75 | 73 | 350 | 6.3 | 3.2 |  | 9.5 | 0.23793 | 0.66316 | 35.8421 | 14.3507 | 13.4472 | 313.0125 | 9.5214 | 307.5497 | 3.0076 | 70.9924 | 0.18942 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 41.17 | 41.17 | 41.17 | 41.17 | SDS-HAA5F, ug/L | 41.17 | 41.17 | 41.17 | 41.17 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21328 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | 20 | 21 | 20.5 | 4.878 | 1998-04-07 | 16:00 | 2 | 24.5 | 76 | 76 | 350 | 6.6 | 37.5 | 44.1 | 0.23793 | 0.14966 | 6.9365 | 15.0341 | 14.0875 | 2343.902 | 46.0114 | 2300.5703 | 22.7622 | 53.2378 | 0.26462 | 1998-04-09 | 9:00 | 2 | 23.6 | 60 | 60 | 350 | 8.2 | 2.9 |  | 11.1 | 0.23793 | 0.73874 | 30.5315 | 18.6787 | 17.9746 | 394.0239 | 11.9214 | 385.0718 | 3.7763 | 56.2237 | 0.3197 | 6.32 | 6.07 | 6.52 | 38.3 | 108.4 | 506 | 319.4362 | 36.8703 | 65.7271 | 316.1429 | 87.8852 | 0 | 0.065 | 0.213 |  | #VALUE! | [11 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 2 | 2.5 | 2.25 | 22.2222 | 1998-04-08 | 7:00 | 18 | 24.9 | 78 | 78 | 350 | 6.7 | 38.5 | 45.2 | 0.23793 | 0.14823 | 6.7434 | 15.2619 | 14.1329 | 2340.0602 | 45.9229 | 2296.1438 | 22.7218 | 55.2782 | 0.25567 | 1998-04-09 | 11:00 | 5 | 24.9 | 56 | 57 | 350 | 6.8 | 2.8 |  | 9.6 | 0.23793 | 0.70833 | 35.4583 | 15.4897 | 14.3438 | 356.8203 | 10.8387 | 350.0984 | 3.4262 | 53.0738 | 0.27026 | [27 empty] | Sampling date | MM/DD/YY | 1998-04-12 | 1998-04-12 | --- | --- | 1998-04-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-13 | 1998-04-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-14 | 1998-04-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-15 | 1998-04-15 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 417.5 | 417.5 | 417.5 | 417.5 | SDS-TOXF, ug Cl- /L | 417.5 | 417.5 | 417.5 | 417.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 112.4 | 111.1 | 111.75 | 1.1633 | 1998-04-08 | 10:00 | 21 | 24.9 | 78 | 79 | 360 | 6.7 | 38.5 | 45.2 | 0.24473 | 0.14823 | 6.9646 | 15.2619 | 14.1329 | 2340.0559 | 45.9472 | 2297.36 | 22.7276 | 55.7724 | 0.2534 | 1998-04-09 | 13:00 | 7 | 24.4 | 56 | 57 | 350 | 6.9 | 2.8 |  | 9.7 | 0.23793 | 0.71134 | 35.0825 | 15.7174 | 14.7715 | 360.1804 | 10.9377 | 353.2953 | 3.458 | 53.042 | 0.27849 | 6.44 | [10 empty] | 0 | [15 empty] | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 27.2 | 23.6 | 25.4 | 14.1732 | 1998-04-08 | 12:00 | 23 | 24.5 | 79 | 80 | 360 | 6.8 | 38.6 | 45.4 | 0.24473 | 0.14978 | 6.9295 | 15.4897 | 14.5144 | 2344.2251 | 46.0163 | 2300.8145 | 22.765 | 56.735 | 0.25583 | 1998-04-09 | 15:00 | 9 | 24.9 | 57 | 57 | 350 | 6.9 | 2.8 |  | 9.7 | 0.23793 | 0.71134 | 35.0825 | 15.7174 | 14.5548 | 360.1804 | 10.9377 | 353.2953 | 3.458 | 53.542 | 0.27184 | 6.23 | [10 empty] | 0 | [15 empty] | Operation time | hh.hh | 82 | 82 | --- | --- | 82 | --- | --- | --- | --- | --- | Operation time | hh.hh | 106.5 | 106.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 131 | 131 | --- | --- | --- | --- | --- | Cumulative time | hr | 153 | 153 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 1.589 | 1.589 | 1.589 | 1.589 | SDS-CDF, mg/L | 1.589 | 1.589 | 1.589 | 1.589 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 14.5 | 11 | 12.75 | 27.451 | 1998-04-08 | 15:00 | 26 | 24.8 | 81 | 81 | 370 | 6.9 | 38.6 | 45.5 | 0.25153 | 0.15165 | 7.1319 | 15.7174 | 14.5979 | 2349.2676 | 46.1263 | 2306.3171 | 22.8167 | 58.1833 | 0.25089 | 1998-04-09 | 17:00 | 11 | 24.4 | 58 | 59 | 350 | 7.1 | 2.9 |  | 10 | 0.23793 | 0.71 | 34 | 16.173 | 15.1996 | 358.6921 | 10.8863 | 351.6366 | 3.4428 | 55.0572 | 0.27607 | [27 empty] | pH | --- | 5.97 | 5.87 | 5.92 | 1.6892 | 6.69 | --- | --- | --- | --- | --- | pH | --- | 6.15 | 7.11 | --- | --- | --- | --- | --- | pH | --- | 5.86 | 6.49 | --- | --- | --- | --- | --- | pH | --- | 5.61 | 6.02 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.036 | 0.678 | -0.043 | 0.06 | SDS-CDp, mg/L | 0.036 | 0.678 | -0.043 | 0.06 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 3.6811 | 74.0109 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 5.6 |  |  |  | Turbidity | ntu | 0.23 | 0.45 | 0.34 | 64.7059 | 1998-04-08 | 17:00 | 28 | 24.9 | 80 | 80 | 370 | 6.8 | 38.5 | 45.3 | 0.25153 | 0.15011 | 7.1678 | 15.4897 | 14.3438 | 2345.112 | 46.0572 | 2302.8591 | 22.7793 | 57.2207 | 0.25068 | 1998-04-10 | 7:00 | 24 | 23.5 | 59 | 60 | 350 | 6.7 | 2.9 |  | 9.6 | 0.23793 | 0.69792 | 35.4583 | 15.2619 | 14.73 | 345.6659 | 10.5028 | 339.2499 | 3.3196 | 56.1804 | 0.26219 | 6.06 | 6.47 | 6.51 | 7.7 | 109.1 | 338 | 352.1414 | -4.1838 | 93.1096 | 348.8446 | 97.7927 | 0 | 0.066 | 0.222 |  | #VALUE! | [11 empty] | Temperature | oC | 24.2 | 24.2 | 24.2 | 0 | 22.3 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 22 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.75 | 3.75 | 3.75 | 3.75 | TOCF, mg/L | 3.75 | 3.75 | 3.75 | 3.75 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 10.9984 | 81.3283 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-04-09 | 6:00 | 41 | 24.9 | 82 | 82 | 370 | 7 | 39 | 46 | 0.25153 | 0.15217 | 7.0435 | 15.9452 | 14.7657 | 2350.6925 | 46.1419 | 2307.0929 | 22.8275 | 59.1725 | 0.24954 | 1998-04-10 | 9:00 | 26 | 23.5 | 59 | 60 | 350 | 6.6 | 2.8 |  | 9.4 | 0.23793 | 0.70213 | 36.234 | 15.0341 | 14.5102 | 350.0807 | 10.64 | 343.6799 | 3.3624 | 56.1376 | 0.25847 | [27 empty] | Alkalinity | mg/L as CaCO3 | 0.5 | 1 | 0.75 | 66.6667 | 6 | 5.5887 | 6.8548 | 66.6667 | 5.5463 | 86.4774 | Alkalinity | mg/L as CaCO3 | 1 | 11.5 | 11.4167 | 0.72464 | 55.5556 | 11.3437 | 91.1846 | Alkalinity | mg/L as CaCO3 | 1 | 4.5 | 3.451 | 23.3115 | 55.5556 | 3.4355 | 70.8925 | Alkalinity | mg/L as CaCO3 | 0.5 | 3 | 3 | 0 | 77.7778 | 2.9834 | 83.2406 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 2.2176 | 72.5475 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.7 | 3.8 | 3.75 | 2.6667 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 11:00 | 28 | 23.5 | 59 | 60 | 350 | 6.6 | 2.8 |  | 9.4 | 0.23793 | 0.70213 | 36.234 | 15.0341 | 14.5102 | 350.0807 | 10.64 | 343.6799 | 3.3624 | 56.1376 | 0.25847 | 5.72 |  |  | 11.5 |  |  | 348.0536 |  | 89.7092 | 344.8804 | 96.6655 | 0 | [15 empty] | Total dissolved solids | mg/L | 6.8 | 7 | 6.9 | 2.8986 | 302 | 345.1258 | -14.2801 | 93.8255 | 342.1586 | 97.9834 | Total dissolved solids | mg/L | 12 | 671 | 843.25 | -25.6706 | 89.2617 | 837.4293 | 98.567 | Total dissolved solids | mg/L | 6.2 | 176.1 | 213.1608 | -21.0453 | 94.4519 | 211.8569 | 97.0735 | Total dissolved solids | mg/L | 7.1 | 144.4 | 156.6 | -8.4488 | 93.6465 | 155.6079 | 95.4372 | UV254 F, cm-1 | 0.06 | 0.06 | 0.06 | 0.06 | UV254 F, cm-1 | 0.06 | 0.06 | 0.06 | 0.06 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 1.5904 | 71.9203 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.073 | 0.047 | 0.06 | 43.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 13:00 | 30 | 24 | 59 | 60 | 350 | 6.5 | 2.8 |  | 9.3 | 0.23793 | 0.69892 | 36.6344 | 14.8063 | 14.0807 | 346.7012 | 10.5402 | 340.4582 | 3.3304 | 56.1696 | 0.25068 | [27 empty] | Total hardness | mg/L as CaCO3 | BMRL | BMRL | #DIV/0! | #VALUE! | 94.1 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total hardness | mg/L as CaCO3 | 0.3 | 252.5 | 209.4667 | 17.0429 | 98.8189 | 208.002 | 99.8558 | Total hardness | mg/L as CaCO3 | BMRL | 54 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | BMRL | 35.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 p, cm-1 | 0.007 | 0.014 | 0 | 0.002 | UV254 p, cm-1 | 0.007 | 0.014 | 0 | 0.002 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.12 |  |  |  | SUVA | L/(mg*m) | 1.973 | 1.2368 | 1.6049 | 45.8675 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 15:00 | 32 | 24.4 | 59 | 60 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.7011 | 343.3151 | 10.4403 | 337.2283 | 3.2983 | 56.2017 | 0.24378 | [27 empty] | Calcium hardness | mg/L as CaCO3 | BMRL | BMRL | #DIV/0! | #VALUE! | 52.4 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | BMRL | 144.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 30.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 17.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | BromideF, ug/L | 60 | 60 | 60 | 60 | BromideF, ug/L | 60 | 60 | 60 | 60 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 62 | 58 | 60 | 6.6667 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 17:00 | 34 | 24.5 | 59 | 60 | 350 | 6.2 | 2.8 |  | 9 | 0.23793 | 0.68889 | 37.8889 | 14.1229 | 13.2337 | 336.5233 | 10.2395 | 330.7434 | 3.2339 | 56.2661 | 0.2352 | 5.76 |  |  | 10.5 |  |  | 335.9464 |  | 90.604 | 333.0639 | 96.8475 | 0 | [15 empty] | Turbidity | ntu | 0.12 | 0.11 | 0.115 | 8.6957 | 0.21 | 0.84081 | -300.384 | 66.1765 | 0.83444 | 86.2183 | Turbidity | ntu | 0.11 | 0.33 | 2.0267 | -514.1414 | 67.6471 | 2.0132 | 94.5362 | Turbidity | ntu | 0.12 | 0.22 | 0.55137 | -150.6239 | 64.7059 | 0.54865 | 78.1283 | Turbidity | ntu | 0.13 | 0.22 | 0.43 | -95.4545 | 61.7647 | 0.42801 | 69.6268 | Bromidep, ug/L | #DIV/0! | BMRL | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | BMRL | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4 | 2.5 | 3.25 | 46.1538 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 7:00 | 48 | 23.9 | 59 | 60 | 340 | 5.8 | 2.8 |  | 8.6 | 0.23113 | 0.67442 | 38.5349 | 13.2118 | 12.6015 | 322.8692 | 9.8304 | 317.5291 | 3.1037 | 56.3963 | 0.22344 | 6.13 | 6.15 | 6.48 | 7.9 | 112.3 | 194 | 326.8679 | -68.4886 | 92.9306 | 324.1472 | 97.5628 | 0.001 | 0.07 | 0.21 | 0.18221 | 13.2313 | 98.3333 | 0.18067 | 99.4465 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25 | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | Total Hardness (mg/L as CaCO3) | 31.8 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 2.5 | 0.822 | 1.661 | 101.0235 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 9:00 | 50 | 23.6 | 70 | 70 | 350 | 6.8 | 3.2 |  | 10 | 0.23793 | 0.68 | 34 | 15.4897 | 14.9057 | 328.044 | 9.9646 | 321.8642 | 3.1499 | 66.8501 | 0.22297 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 30 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 0.75 | 1 | 1 | 0.5 | Alkp, mg/L CaCO3 | 0.75 | 1 | 1 | 0.5
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | pH | 5.47 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 1.5 | 1.678 | 1.589 | 11.202 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 11:00 | 52 | 23.8 | 70 | 70 | 350 | 6.8 | 2.8 |  | 9.6 | 0.23793 | 0.70833 | 35.4583 | 15.4897 | 14.8179 | 356.8203 | 10.8387 | 350.0984 | 3.4262 | 66.5738 | 0.22258 | 6.22 |  |  | 6.9 |  |  | 366.3857 |  | 93.8255 | 362.8936 | 98.0986 | 0 | [15 empty] | UV254 | cm-1 | 0.007 | 0.007 | 0.007 | 0 | 0.213 | 0.17797 | 16.4471 | 88.3333 | 0.17647 | 96.0333 | UV254 | cm-1 | 0.014 | 0.555 | 0.39733 | 28.4084 | 76.6667 | 0.39465 | 96.4525 | UV254 | cm-1 | 0 | 0.129 | 0.11765 | 8.8007 | 100 | 0.11691 | 100 | UV254 | cm-1 | 0.002 | 0.098 | 0.084857 | 13.4111 | 96.6667 | 0.084307 | 97.6277 | T-HdF, mg/L CaCO3 | 25.4 | 25.4 | 25.4 | 25.4 | T-HdF, mg/L CaCO3 | 25.4 | 25.4 | 25.4 | 25.4
Treatment Plant Category | CONV | [11 empty] | Ammonia (mg/L) | BMRL | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20.9 | 20.9 | 20.9 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 13:00 | 54 | 24.4 | 70 | 70 | 350 | 6.7 | 2.9 |  | 9.6 | 0.23793 | 0.69792 | 35.4583 | 15.2619 | 14.3433 | 345.6659 | 10.5028 | 339.2499 | 3.3196 | 66.6804 | 0.21511 | [27 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.775 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.85 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.7671 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.8846 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | #DIV/0! | 0.3 | BMRL | BMRL | T-Hdp, mg/L CaCO3 | #DIV/0! | 0.3 | BMRL | BMRL
Process Train Name | Conventional Train | Additional Information | [10 empty] | TOC (mg/L) | 3.8 |  |  |  | SDS-Chlorination pH | --- | 7.7 | 7.7 | 7.7 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 15:00 | 56 | 24.5 | 70 | 60 | 350 | 6.6 | 2.9 |  | 9.5 | 0.23793 | 0.69474 | 35.8421 | 15.0341 | 14.0875 | 342.3941 | 10.4064 | 336.1338 | 3.2886 | 61.7114 | 0.22828 | [27 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 12.75 | 12.75 | 12.75 | 12.75 | Ca-HdF, mg/L CaCO3 | 12.75 | 12.75 | 12.75 | 12.75
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | UV254 (cm-1) | 0.075 |  |  |  | SDS-Incubation time | hours | 6.75 | 6.8 | 6.775 | 0.73801 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 17:00 | 58 | 24.5 | 70 | 70 | 350 | 6.6 | 2.8 |  | 9.4 | 0.23793 | 0.70213 | 36.234 | 15.0341 | 14.0875 | 350.0807 | 10.64 | 343.6799 | 3.3624 | 66.6376 | 0.21141 | 6.25 |  |  | 5.9 |  |  | 361.2536 |  | 94.7204 | 357.9031 | 98.3515 | 0 | [15 empty] | SDS-Cl2 dose | mg/L | 1 | 1 | 1 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | #DIV/0! | BMRL | BMRL | BMRL | Ca-Hdp, mg/L CaCO3 | #DIV/0! | BMRL | BMRL | BMRL
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | Bromide (ug/L) | 55 |  |  |  | SDS-TOX | mg Cl- /L | 610 | 225 | 417.5 | 92.2156 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-12 | 8:00 | 73 | 24.1 | 71 | 72 | 350 | 6.2 | 2.7 |  | 8.9 | 0.23793 | 0.69663 | 38.3258 | 14.1229 | 13.3911 | 344.3045 | 10.4762 | 338.391 | 3.3087 | 68.1913 | 0.19638 | 5.96 | 5.92 | 6.22 | 9.1 | 110.4 | 311 | 347.4648 | -11.725 | 91.8568 | 344.4679 | 97.3582 | 0 | 0.064 | 0.204 |  | #VALUE! | [11 empty] | SDS-Free Cl2 residual | mg/L | 1 | 0.928 | 0.964 | 7.4689 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.822 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.043 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.94 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 50.6 | 41.4 | 46 | 20 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-12 | 17:00 | 82 | 24.2 | 74 | 74 | 350 | 6.1 | 2.8 |  | 8.9 | 0.23793 | 0.68539 | 38.3258 | 13.8951 | 13.1363 | 333.1174 | 10.1387 | 327.4884 | 3.2016 | 70.7984 | 0.18554 | 6.16 |  |  | 6.7 |  |  | 340.6089 |  | 94.0045 | 337.6992 | 98.016 | 0 | [15 empty] | SDS-Cl2 demand | mg/L | 0 | 0.072 | 0.036 | 200 | --- | 5.0457 | --- | 97.7344 | 5.0017 | 99.2802 | SDS-Cl2 demand | mg/L | 0.678 | --- | 8.2697 | --- | 57.3317 | 8.2165 | 91.7483 | SDS-Cl2 demand | mg/L | -0.043 | --- | 3.157 | --- | 102.7061 | 3.1368 | 101.3708 | SDS-Cl2 demand | mg/L | 0.06 | --- | 2.2443 | --- | 96.224 | 2.2298 | 97.3092 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 21.4 | 18.76 | 20.08 | 13.1474 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 7:30 | 97.5 | 23.8 | 74 | 74 | 350 | 5.6 | 2.8 |  | 8.4 | 0.23793 | 0.66667 | 40.6667 | 12.7562 | 12.203 | 315.9881 | 9.6309 | 311.0864 | 3.0391 | 70.9609 | 0.17197 | [27 empty] | SDS-Chlorination temp. | oC | 20.9 | 20.9 | 20.9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20.9 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | -1.2943 | -1.2943 | -1.2943 | -1.2943 | Qp/QT (THM4), % | 49.3528 | 49.3528 | 49.3528 | 49.3528
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 5.3 | 4.7 | 5 | 12 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 9:30 | 99.5 | 23.8 | 84 | 84 | 350 | 5.7 | 0.67 |  | 6.37 | 0.23793 | 0.89482 | 53.9451 | 12.984 | 12.4209 | 843.7411 | 25.7089 | 830.4189 | 8.1137 | 75.8863 | 0.16368 | [27 empty] | SDS-Chlorination pH | --- | 7.74 | 7.74 | 7.74 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.63 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.74 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.65 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 10:00 | 100 | 23.1 | 84 | 84 | 340 | 5.5 | 0.67 |  | 6.17 | 0.23113 | 0.89141 | 54.1053 | 12.5284 | 12.2356 | 823.1784 | 25.0851 | 810.268 | 7.9164 | 76.0836 | 0.16082 | 6.31 |  |  | 9.1 |  |  | 954.3993 |  | 91.8568 | 946.7535 | 99.0388 | 0 | [15 empty] | SDS-Incubation time | hours | 6.75 | 6.75 | 6.75 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.75 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.75 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.75 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 20.8514 | 20.8514 | 20.8514 | 20.8514
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 77.3 | 64.86 | 71.08 | 17.5014 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 12:30 | 102.5 | 23 | 86 | 85 | 350 | 5.4 | 0.7 |  | 6.1 | 0.23793 | 0.88525 | 56.377 | 12.3006 | 12.0487 | 788.3571 | 24.0417 | 776.5648 | 7.5842 | 77.9158 | 0.15464 | 6.35 |  |  | 12 |  |  | 881.25 |  | 89.2617 | 874.5444 | 98.6279 | [16 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | 2.04 | 2.04 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 16:30 | 106.5 | 23.1 | 86 | 86 | 350 | 4.9 | 0.67 |  | 5.57 | 0.23793 | 0.87971 | 61.8366 | 11.1617 | 10.9008 | 759.4155 | 23.1917 | 749.1084 | 7.3107 | 78.6893 | 0.13853 | [27 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 0.82255 | 1.1394 | 0.78356 | 0.8344
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 20.38 | 19.87 | 20.125 | 2.5342 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 9:00 | 123 | 23.2 | 92 | 91 | 350 | 4.4 | 4.1 |  | 8.5 | 0.23793 | 0.51765 | 40.1765 | 10.0227 | 9.7596 | 224.3149 | 6.8599 | 221.5812 | 2.1609 | 89.3391 | 0.10924 | 5.82 | 5.8 | 6.1 | 7.7 | 112.4 | 182.9 | 223.4134 | -22.1506 | 93.1096 | 222.0575 | 96.5324 | 0.001 | 0.071 | 0.139 | 0.12332 | 11.2827 | 98.3333 | 0.12255 | 99.184 | [8 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 22.75 | 16.26 | 19.505 | 33.2735 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 11:00 | 125 | 23.1 | 92 | 91 | 350 | 4.6 | 4.3 |  | 8.9 | 0.23793 | 0.51685 | 38.3258 | 10.4783 | 10.2334 | 223.9733 | 6.8456 | 221.1196 | 2.157 | 89.343 | 0.11454 | 5.86 |  |  | 7.7 |  |  | 223.0593 |  | 93.1096 | 221.6441 | 96.526 | 0.002 |  |  | 0.12205 |  | 96.6667 | 0.12126 | 98.3506 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.033843 | 0.037298 | 0.030388 | 0.031375
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 13:00 | 127 | 23.1 | 92 | 92 | 350 | 4.6 | 4.8 |  | 9.4 | 0.23793 | 0.48936 | 36.234 | 10.4783 | 10.2334 | 212.616 | 6.4985 | 209.907 | 2.0476 | 89.9524 | 0.11376 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 1.04 | BMRL | 1.04 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 15:00 | 129 | 23.1 | 92 | 92 | 350 | 4.6 | 4.5 |  | 9.1 | 0.23793 | 0.50549 | 37.4615 | 10.4783 | 10.2334 | 219.1367 | 6.6978 | 216.3446 | 2.1104 | 89.8896 | 0.11384 | 5.84 |  |  | 7.4 |  |  | 218.4189 |  | 93.3781 | 217.0322 | 96.5904 | 0.002 |  |  | 0.11929 |  | 96.6667 | 0.11852 | 98.3125 | [8 empty] | SDS-THM4 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 229.2903 | --- | 100 | 227.2788 | 100 | SDS-THM4 | mg/L | 0 | --- | 592.3333 | --- | 100 | 588.1856 | 100 | SDS-THM4 | mg/L | 0 | --- | 139.3725 | --- | 100 | 138.4945 | 100 | SDS-THM4 | mg/L | 0 | --- | 101.5429 | --- | 100 | 100.869 | 100 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 1.5097 | 1.6331 | 1.6331 | 1.3863
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 5.44 | 6.32 | 5.88 | 14.966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 17:00 | 131 | 23.5 | 92 | 92 | 350 | 4.4 | 4.6 |  | 9 | 0.23793 | 0.48889 | 37.8889 | 10.0227 | 9.6734 | 212.4274 | 6.4964 | 209.8385 | 2.0464 | 89.9536 | 0.10754 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | #DIV/0! | 13.0124 | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 8:00 | 144 | 23.5 | 90 | 90 | 330 | 4.2 | 9.7 |  | 13.9 | 0.22434 | 0.30216 | 22.741 | 9.5671 | 9.2337 | 158.0442 | 4.8325 | 156.0942 | 1.5224 | 88.4776 | 0.10436 | [27 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 9:00 | 145 | 23.5 | 91 | 90 | 330 | 4.4 | 9.7 |  | 14.1 | 0.22434 | 0.31206 | 22.4043 | 10.0227 | 9.6734 | 160.2198 | 4.8961 | 158.1488 | 1.5429 | 88.9571 | 0.10874 | 6.11 | 6.26 | 6.39 | 4 | 107.8 | 134.6 | 160.6263 | -19.336 | 96.4206 | 159.5821 | 97.4935 | 0.001 | 0.07 | 0.093 | 0.086763 | 6.7066 | 98.3333 | 0.086191 | 98.8398 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 11:00 | 147 | 23.4 | 91 | 90 | 330 | 4.4 | 10.4 |  | 14.8 | 0.22434 | 0.2973 | 21.2973 | 10.0227 | 9.7021 | 156.999 | 4.7977 | 154.9697 | 1.5119 | 88.9881 | 0.10903 | 6.03 |  |  | 4 |  |  | 157.3365 |  | 96.4206 | 156.3143 | 97.4411 | 0.003 |  |  | 0.084115 |  | 95 | 0.083575 | 96.4104 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 44.17 | 38.17 | 41.17 | 14.5737 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 13:00 | 149 | 23.5 | 90 | 90 | 330 | 4.4 | 10.4 |  | 14.8 | 0.22434 | 0.2973 | 21.2973 | 10.0227 | 9.6734 | 156.999 | 4.7977 | 154.9697 | 1.5119 | 88.4881 | 0.10932 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 49.61 | 44.49 | 47.05 | 10.882 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 15:00 | 151 | 24 | 90 | 89 | 330 | 4.4 | 10.2 |  | 14.6 | 0.22434 | 0.30137 | 21.6027 | 10.0227 | 9.5315 | 157.8747 | 4.8245 | 155.8341 | 1.5203 | 87.9797 | 0.10834 | 6.03 |  |  | 4 |  |  | 158.2304 |  | 96.4206 | 157.2022 | 97.4555 | 0.001 |  |  | 0.085451 |  | 98.3333 | 0.084888 | 98.822 | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -31.1635 | -31.1635 | -31.1635 | -31.1635 | Qp/QT (HAA5), % | 34.4183 | 34.4183 | 34.4183 | 34.4183
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 17:00 | 153 | 23.5 | 90 | 90 | 330 | 4.4 | 10.2 |  | 14.6 | 0.22434 | 0.30137 | 21.6027 | 10.0227 | 9.6734 | 157.8747 | 4.8245 | 155.8341 | 1.5203 | 88.4797 | 0.10933 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 46.6155 | 46.6155 | 46.6155 | 46.6155
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-18 | 10:30 | 171.5 | 23.5 | 49 | 50 | 350 | 5.4 | 10.5 | X | 15.9 | 0.23793 | 0.33962 | 21.0126 | 12.3006 | 11.8719 | 166.6084 | 5.0809 | 164.1163 | 1.6028 | 47.8972 | 0.24786 | 6.05 | 6.39 | 6.43 | 6.6 | 115.8 | 152.3 | 165.8271 | -8.8819 | 94.094 | 164.5988 | 95.9903 | [16 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-18 | 12:00 | 173 | 23 | 49 | 50 | 350 | 5.4 | 11.6 |  | 17 | 0.23793 | 0.31765 | 19.5882 | 12.3006 | 12.0487 | 161.4791 | 4.9245 | 159.0637 | 1.5535 | 47.9465 | 0.25129 | [11 empty] | 0 | 0.069 | 0.097 |  | #VALUE! | [11 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-04-18 | 14:00 | 175 | 23.2 | 48 | 49 | 350 | 5.3 | 11.4 |  | 16.7 | 0.23793 | 0.31737 | 19.9581 | 12.0728 | 11.7559 | 161.4148 | 4.9239 | 159.0451 | 1.5531 | 46.9469 | 0.25041 | [27 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 132.8065 | --- | 100 | 131.6414 | 100 | SDS-HAA5 | mg/L | 0 | --- | 343.0833 | --- | 100 | 340.681 | 100 | SDS-HAA5 | mg/L | 0 | --- | 80.7255 | --- | 100 | 80.2169 | 100 | SDS-HAA5 | mg/L | 0 | --- | 58.8143 | --- | 100 | 58.424 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.0545 | 1.2754 | 1.0273 | 1.0627
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 151.7742 | --- | 100 | 150.4427 | 100 | SDS-HAA6 | mg/L | 0 | --- | 392.0833 | --- | 100 | 389.3379 | 100 | SDS-HAA6 | mg/L | 0 | --- | 92.2549 | --- | 100 | 91.6737 | 100 | SDS-HAA6 | mg/L | 0 | --- | 67.2143 | --- | 100 | 66.7682 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.041758 | 0.044168 | 0.039349 | 0.040037
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 1.7337 | 1.8198 | 1.8198 | 1.6477
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | #DIV/0! | 16.761 | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on R8: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R9: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R10: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R11: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R12: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R13: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R14: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R15: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R16: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R17: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R18: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on U6: C. Hill (8/30/99): Reviewer added chemical formula and dose. This information was copied from the pretreatment data for the NF200 membrane used during this study. All other pre-treatment information for these two membranes was identical, so it was assumed the alum formula and dose were also identical.
Note on X27: C. Hill (8/30/99): The primary and feed TOX concentrations were verified by the consultant. The high TOX concentration in the primary feed sample may be due to contamination, though there is no evidence to support this in any of the QC samples during the run, i.e. method blanks. The QC samples for both TOX runs met the ICR QC criteria.
Note on DQ17: C. Hill (8/30/99): Permeate and concentrate TDS and UV data during Run 2 (90%) and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study,or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.
Note on DQ23: C. Hill (8/30/99): Permeate and concentrate TDS and UV data during Run 2 (90%) and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study,or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.
Note on EA17: C. Hill (8/30/99): Permeate and concentrate TDS and UV data during Run 2 (90%) and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study,or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.

## XLE. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 5.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.97262 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 16.4 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-15 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.2 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.3 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.4 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.6 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -4.2 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 12:00 | 10:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [6 empty] | SDS-THM4F, ug/L | 89.285 | 89.285 | 89.285 | 89.285 | SDS-THM4F, ug/L | 89.285 | 89.285 | 89.285 | 89.285 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 112 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 0 | 159 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 0 | 1.095 | 0 | 0 | SDS-THM4p, ug/L | 0 | 1.095 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.87 | 6.31 | 6.09 | 7.225 | 1998-07-06 | 10:00 | 0 | 22.7 | 50 | 50 | 360 | 8.5 | 3.8 | 12.3 | 0.24473 | 0.69106 | 28.2683 | 19.3621 | 19.1345 | 2.481 | 0.048472 | 2.4236 | 0.024039 | 49.976 | 0.38287 | 1998-07-08 | 12:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 41.04 | 41.04 | 41.04 | 41.04 | SDS-HAA5F, ug/L | 41.04 | 41.04 | 41.04 | 41.04 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21328 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | 20 | 23 | 21.5 | 13.9535 | 1998-07-06 | 12:00 | 2 | 23.8 | 50 | 51 | 350 | 8.7 | 3.8 | 12.5 | 0.23793 | 0.696 | 27 | 19.8176 | 18.9582 | 2.519 | 0.049153 | 2.4577 | 0.024392 | 50.4756 | 0.37559 | 1998-07-08 | 13:00 | 1 | 24.6 | 50 | 50 | 350 | 7.9 | 3.5 |  | 11.4 | 0.23793 | 0.69298 | 29.7018 | 17.9953 | 16.8126 | 344.1629 | 9.2152 | 336.6027 | 3.3117 | 46.6883 | 0.3601 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 5.3 | 6.5 | 5.9 | 20.339 | 1998-07-06 | 14:00 | 4 | 23.7 | 50 | 50 | 350 | 9 | 3.8 | 12.8 | 0.23793 | 0.70312 | 26.3438 | 20.501 | 19.67 | 2.5758 | 0.050217 | 2.5109 | 0.024931 | 49.9751 | 0.3936 | 1998-07-08 | 15:00 | 3 | 25.4 | 50 | 51 | 350 | 7.8 | 3.6 |  | 11.4 | 0.23793 | 0.68421 | 29.7018 | 17.7675 | 16.2118 | 335.3638 | 8.9821 | 328.0901 | 3.2274 | 47.2726 | 0.34294 | 5.68 | 5.87 | 6.58 | 14.1 | 110 | 287 | 324.275 | -12.9878 | 87.4163 | 320.8188 | 95.605 | 0 | 0.066 | 0.2 |  | #VALUE! | [11 empty] | Sampling date | MM/DD/YY | 1998-07-11 | 1998-07-11 | --- | --- | 1998-07-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-12 | 1998-07-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-14 | 1998-07-14 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 272.5 | 272.5 | 272.5 | 272.5 | SDS-TOXF, ug Cl- /L | 272.5 | 272.5 | 272.5 | 272.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 110 | 114.1 | 112.05 | 3.6591 | 1998-07-06 | 16:00 | 6 | 25.2 | 50 | 50 | 350 | 9.1 | 3.8 | 12.9 | 0.23793 | 0.70543 | 26.1318 | 20.7288 | 19.0259 | 2.5947 | 0.050571 | 2.5285 | 0.02511 | 49.9749 | 0.38071 | 1998-07-08 | 17:00 | 5 | 24.8 | 50 | 51 | 350 | 7.5 | 3.4 |  | 10.9 | 0.23793 | 0.68807 | 31.1101 | 17.0842 | 15.8672 | 339.164 | 9.0916 | 332.0911 | 3.2654 | 47.2346 | 0.33592 | [27 empty] | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | 15:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 28.8 | 31.3 | 30.05 | 8.3195 | 1998-07-06 | 17:30 | 7.5 | 24.8 | 50 | 50 | 350 | 9 | 3.9 | 12.9 | 0.23793 | 0.69767 | 26.1318 | 20.501 | 19.0407 | 2.5322 | 0.049368 | 2.4684 | 0.024509 | 49.9755 | 0.381 | 1998-07-09 | 7:00 | 19 | 22.3 | 50 | 51 | 350 | 6.8 | 3.2 |  | 10 | 0.23793 | 0.68 | 34 | 15.4897 | 15.4897 | 331.2498 | 8.8971 | 324.987 | 3.1922 | 47.3078 | 0.32742 | 6.1 |  |  | 9.9 |  |  | 329.1187 |  | 91.1647 | 326.0178 | 96.9634 | 0.001 |  |  | 0.22912 |  | 98.6486 | 0.22691 | 99.5593 | [8 empty] | Operation time | hh.hh | 75 | 75 | --- | --- | 75 | --- | --- | --- | --- | --- | Operation time | hh.hh | 96 | 96 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122 | 122 | --- | --- | --- | --- | --- | Cumulative time | hr | 146 | 146 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.41 | 2.41 | 2.41 | 2.41 | SDS-CDF, mg/L | 2.41 | 2.41 | 2.41 | 2.41 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 19.5 | 20 | 19.75 | 2.5316 | 1998-07-07 | 8:00 | 22 | 23 | 50 | 51 | 350 | 8.6 | 3.6 | 12.2 | 0.23793 | 0.70492 | 27.6885 | 19.5899 | 19.1887 | 2.5903 | 0.050559 | 2.5279 | 0.025086 | 50.4749 | 0.38016 | 1998-07-09 | 9:00 | 21 | 22 | 51 | 51 | 350 | 6.7 | 3 |  | 9.7 | 0.23793 | 0.69072 | 35.0825 | 15.2619 | 15.3978 | 341.7868 | 9.1828 | 335.4198 | 3.2942 | 47.7058 | 0.32277 | [27 empty] | pH | --- | 6.48 | 6.32 | 6.4 | 2.5 | 7.03 | --- | --- | --- | --- | --- | pH | --- | 6.75 | 7.67 | --- | --- | --- | --- | --- | pH | --- | 6.83 | 6.76 | --- | --- | --- | --- | --- | pH | --- | 6.13 | 7 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.1335 | 0.165 | 0.307 | 0.22 | SDS-CDp, mg/L | 0.1335 | 0.165 | 0.307 | 0.22 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 3.6811 | 74.0109 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 6.57 |  |  |  | Turbidity | ntu | 0.17 | 0.16 | 0.165 | 6.0606 | 1998-07-07 | 10:00 | 24 | 23.6 | 50 | 51 | 350 | 8.6 | 3.6 | 12.2 | 0.23793 | 0.70492 | 27.6885 | 19.5899 | 18.8514 | 2.5903 | 0.050559 | 2.5279 | 0.025086 | 50.4749 | 0.37348 | 1998-07-09 | 11:00 | 23 | 23 | 52 | 52 | 350 | 6.8 | 3 |  | 9.8 | 0.23793 | 0.69388 | 34.7143 | 15.4897 | 15.1725 | 345.0245 | 9.2671 | 338.5012 | 3.325 | 48.675 | 0.31171 | 6.11 | 6.43 | 7.19 | 9.5 | 109.7 | 329 | 344.4967 | -4.7102 | 91.5216 | 341.2424 | 97.2161 | 0 | 0.067 | 0.227 |  | #VALUE! | [11 empty] | Temperature | oC | 23.2 | 23.2 | 23.2 | 0 | 23.2 | --- | --- | --- | --- | --- | Temperature | oC | 23.2 | 23.2 | --- | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.65 | 3.65 | 3.65 | 3.65 | TOCF, mg/L | 3.65 | 3.65 | 3.65 | 3.65 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 10.9984 | 81.3283 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-07-07 | 12:00 | 26 | 23.8 | 52 | 52 | 350 | 8.7 | 3.5 | 12.2 | 0.23793 | 0.71311 | 27.6885 | 19.8176 | 18.9582 | 2.6596 | 0.051895 | 2.5948 | 0.025753 | 51.9742 | 0.36476 | 1998-07-09 | 13:00 | 25 | 22.9 | 52 | 52 | 350 | 6.5 | 3 |  | 9.5 | 0.23793 | 0.68421 | 35.8421 | 14.8063 | 14.546 | 335.2958 | 9.0135 | 329.2363 | 3.2325 | 48.7675 | 0.29827 | [27 empty] | Alkalinity | mg/L as CaCO3 | 1.6 | 0.9 | 1.25 | 56 | 18.2 | 16.75 | 7.967 | 78.8136 | 16.6074 | 92.4732 | Alkalinity | mg/L as CaCO3 | 1 | 41 | 45.5455 | -11.0865 | 83.0508 | 45.1886 | 97.7871 | Alkalinity | mg/L as CaCO3 | 0.2 | 11.4 | 11.8327 | -3.7952 | 96.6102 | 11.736 | 98.2958 | Alkalinity | mg/L as CaCO3 | 0.3 | 8.6 | 8.1873 | 4.7986 | 94.9153 | 8.1233 | 96.3069 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 2.2176 | 72.5475 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.6 | 3.7 | 3.65 | 2.7397 | 1998-07-07 | 14:00 | 28 | 23.6 | 50 | 50 | 350 | 8.6 | 3.5 | 12.1 | 0.23793 | 0.71074 | 27.9256 | 19.5899 | 18.8514 | 2.6391 | 0.051511 | 2.5756 | 0.025558 | 49.9744 | 0.37722 | 1998-07-09 | 15:00 | 27 | 23.1 | 52 | 52 | 350 | 6.6 | 2.8 |  | 9.4 | 0.23793 | 0.70213 | 36.234 | 15.0341 | 14.6827 | 353.7583 | 9.5071 | 347.2667 | 3.4101 | 48.5899 | 0.30218 | [27 empty] | Total dissolved solids | mg/L | 10.4 | 10 | 10.2 | 3.9216 | 331 | 349.7 | -5.6495 | 90.8969 | 346.5766 | 97.0569 | Total dissolved solids | mg/L | 16.8 | 714 | 882.7091 | -23.6287 | 85.0067 | 875.7732 | 98.0817 | Total dissolved solids | mg/L | 5.1 | 179.2 | 223.3653 | -24.6458 | 95.4485 | 221.5525 | 97.6981 | Total dissolved solids | mg/L | 6.1 | 148.9 | 155.3254 | -4.3152 | 94.556 | 154.1136 | 96.0419 | UV254 F, cm-1 | 0.074 | 0.074 | 0.074 | 0.074 | UV254 F, cm-1 | 0.074 | 0.074 | 0.074 | 0.074 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 1.5904 | 71.9203 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.072 | 0.076 | 0.074 | 5.4054 | 1998-07-07 | 17:00 | 31 | 25.5 | 50 | 50 | 350 | 9 | 3.8 | 12.8 | 0.23793 | 0.70312 | 26.3438 | 20.501 | 18.6507 | 2.5758 | 0.050217 | 2.5109 | 0.024931 | 49.9751 | 0.3732 | 1998-07-09 | 17:00 | 29 | 24.1 | 50 | 51 | 350 | 7 | 3 |  | 10 | 0.23793 | 0.7 | 34 | 15.9452 | 15.119 | 351.4843 | 9.4353 | 344.6434 | 3.3863 | 47.1137 | 0.32091 | 5.59 |  |  | 11.4 |  |  | 346.9 |  | 89.826 | 343.545 | 96.6817 | 0 | [15 empty] | Total hardness | mg/L as CaCO3 | 0.4 | 0.6 | 0.5 | 40 | 89.4 | 99 | -10.7383 | 98.3361 | 98.0938 | 99.4903 | Total hardness | mg/L as CaCO3 | 3.3 | 205 | 246.4818 | -20.235 | 89.0183 | 244.5339 | 98.6505 | Total hardness | mg/L as CaCO3 | 0.2 | 58.6 | 61.1184 | -4.2976 | 99.3344 | 60.6124 | 99.67 | Total hardness | mg/L as CaCO3 | 3 | 46.1 | 41.0986 | 10.849 | 90.0166 | 40.7892 | 92.6451 | UV254 p, cm-1 | 0.003 | 0.003 | 0.004 | 0.002 | UV254 p, cm-1 | 0.003 | 0.003 | 0.004 | 0.002 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.16 |  |  |  | SUVA | L/(mg*m) | 2 | 2.0541 | 2.027 | 2.6667 | 1998-07-08 | 7:00 | 45 | 23.2 | 50 | 50 | 350 | 8.5 | 3.6 | 12.1 | 0.23793 | 0.70248 | 27.9256 | 19.3621 | 18.8538 | 2.5704 | 0.050184 | 2.5092 | 0.024896 | 49.9751 | 0.37726 | 1998-07-10 | 7:00 | 43 | 22.6 | 50 | 50 | 350 | 6.2 | 2.8 |  | 9 | 0.23793 | 0.68889 | 37.8889 | 14.1229 | 13.9982 | 339.9104 | 9.1453 | 334.0511 | 3.2784 | 46.7216 | 0.29961 | 6.13 |  |  | 9.3 |  |  | 339.5679 |  | 91.7001 | 336.6426 | 97.2374 | 0.001 |  |  | 0.23564 |  | 98.6486 | 0.23356 | 99.5719 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 0.4 | 0.4 | 0.4 | 0 | 53 | 64.9 | -22.4528 | 97.9747 | 64.3066 | 99.378 | Calcium hardness | mg/L as CaCO3 | 2.5 | 115.4 | 159.3182 | -38.0573 | 87.3418 | 158.0621 | 98.4183 | Calcium hardness | mg/L as CaCO3 | 0.2 | 36.7 | 40.098 | -9.2587 | 98.9873 | 39.7666 | 99.4971 | Calcium hardness | mg/L as CaCO3 | 3 | 29.5 | 26.5915 | 9.8592 | 84.8101 | 26.4 | 88.6364 | BromideF, ug/L | 60.5 | 60.5 | 60.5 | 60.5 | BromideF, ug/L | 60.5 | 60.5 | 60.5 | 60.5 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 63 | 58 | 60.5 | 8.2645 | 1998-07-08 | 10:00 | 48 | 23.4 | 50 | 51 | 350 | 8.3 | 3.5 | 11.8 | 0.23793 | 0.70339 | 28.661 | 18.9065 | 18.3016 | 2.5777 | 0.050356 | 2.5178 | 0.024974 | 50.475 | 0.36259 | 1998-07-10 | 9:00 | 45 | 22.2 | 51 | 51 | 350 | 6.4 | 2.9 |  | 9.3 | 0.23793 | 0.68817 | 36.6344 | 14.5785 | 14.6217 | 339.2034 | 9.1211 | 333.1676 | 3.2706 | 47.7294 | 0.30635 | [27 empty] | Turbidity | ntu | 0.13 | 0.1 | 0.115 | 26.087 | 0.2 | 0.28167 | -40.8333 | 30.303 | 0.28013 | 58.9481 | Turbidity | ntu | 0.08 | 0.23 | 0.85273 | -270.751 | 51.5152 | 0.84654 | 90.5497 | Turbidity | ntu | 0.13 | 0.21 | 0.20143 | 4.0816 | 21.2121 | 0.20084 | 35.2703 | Turbidity | ntu | 0.08 | 0.12 | 0.19972 | -66.4319 | 51.5152 | 0.19875 | 59.7477 | Bromidep, ug/L | #DIV/0! | 25 | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | 25 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 3.64 | 3.7 | 3.67 | 1.6349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 11:00 | 47 | 22.7 | 52 | 52 | 350 | 6.2 | 2.6 |  | 8.8 | 0.23793 | 0.70455 | 38.7727 | 14.1229 | 13.9569 | 356.3814 | 9.5885 | 350.2382 | 3.4372 | 48.5628 | 0.2874 | 6.11 | 6.38 | 7.06 | 8.6 | 111.9 | 327 | 358.7385 | -9.706 | 92.3249 | 355.6372 | 97.5818 | 0.001 | 0.071 | 0.233 | 0.24808 | -6.4708 | 98.6486 | 0.24589 | 99.5933 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 5.9 | 5.9 | 5.9 | 5.9 | AlkF, mg/L CaCO3 | 5.9 | 5.9 | 5.9 | 5.9
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | Total Hardness (mg/L as CaCO3) | 26.6 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.66 | 0.86 | 1.26 | 63.4921 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 13:00 | 49 | 23.5 | 52 | 52 | 350 | 6.3 | 2.8 |  | 9.1 | 0.23793 | 0.69231 | 37.4615 | 14.3507 | 13.8506 | 343.3813 | 9.2361 | 337.3667 | 3.3114 | 48.6886 | 0.28447 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 29.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 1.25 | 1 | 0.2 | 0.3 | Alkp, mg/L CaCO3 | 1.25 | 1 | 0.2 | 0.3
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | pH | 5.72 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 1.98 | 2.84 | 2.41 | 35.6846 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 15:00 | 51 | 23.9 | 51 | 51 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.9051 | 346.8463 | 9.3266 | 340.6745 | 3.3443 | 47.6557 | 0.29178 | [27 empty] | UV254 | cm-1 | 0.005 | 0.001 | 0.003 | 133.3333 | 0.232 | 0.23967 | -3.3046 | 95.9459 | 0.23749 | 98.7368 | UV254 | cm-1 | 0.003 | 0.567 | 0.64845 | -14.3659 | 95.9459 | 0.64328 | 99.5336 | UV254 | cm-1 | 0.004 | 0.145 | 0.14686 | -1.2808 | 94.5946 | 0.14567 | 97.2541 | UV254 | cm-1 | 0.002 | 0.1045 | 0.10341 | 1.0445 | 97.2973 | 0.10259 | 98.0504 | T-HdF, mg/L CaCO3 | 30.05 | 30.05 | 30.05 | 30.05 | T-HdF, mg/L CaCO3 | 30.05 | 30.05 | 30.05 | 30.05
Treatment Plant Category | CONV | [11 empty] | Ammonia (mg/L) | BMRL | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 30 | 30.3 | 30.15 | 0.99502 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 17:00 | 53 | 24.5 | 51 | 51 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.6606 | 346.8463 | 9.3266 | 340.6745 | 3.3443 | 47.6557 | 0.28665 | 6.06 |  |  | 8.7 |  |  | 348.2786 |  | 92.2356 | 345.1739 | 97.4795 | 0 | [15 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.922 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.9863 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.0096 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 0.5 | 3.3 | 0.2 | 3 | T-Hdp, mg/L CaCO3 | 0.5 | 3.3 | 0.2 | 3
Process Train Name | Conventional Train | Additional Information | [10 empty] | TOC (mg/L) | 3.55 |  |  |  | SDS-Chlorination pH | --- | 8 | 8.12 | 8.06 | 1.4888 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 7:00 | 67 | 22.1 | 50 | 51 | 350 | 5.8 | 2.8 |  | 8.6 | 0.23793 | 0.67442 | 39.6977 | 13.2118 | 13.2901 | 325.9663 | 8.7801 | 320.7101 | 3.1456 | 47.3544 | 0.28065 | 6.81 |  |  | 8.2 |  |  | 327.1679 |  | 92.6818 | 324.525 | 97.4732 | 0.003 |  |  | 0.22107 |  | 95.9459 | 0.21926 | 98.6318 | [8 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | 25 | --- | 347.7273 | --- | 58.6777 | 345.1422 | 92.7566 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 19.75 | 19.75 | 19.75 | 19.75 | Ca-HdF, mg/L CaCO3 | 19.75 | 19.75 | 19.75 | 19.75
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | UV254 (cm-1) | 0.068 |  |  |  | SDS-Incubation time | hours | 6.4 | 6.4 | 6.4 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 9:00 | 69 | 22 | 56 | 57 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 14.7084 | 346.8463 | 9.3266 | 340.6745 | 3.3443 | 53.1557 | 0.2767 | [27 empty] | SDS-Cl2 dose | mg/L | 1.2 | 1.2 | 1.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 0.4 | 2.5 | 0.2 | 3 | Ca-Hdp, mg/L CaCO3 | 0.4 | 2.5 | 0.2 | 3
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | Bromide (ug/L) | 57 |  |  |  | SDS-TOX | mg Cl- /L | 275 | 270 | 272.5 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 11:00 | 71 | 21.9 | 56 | 57 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 14.7519 | 346.8463 | 9.3266 | 340.6745 | 3.3443 | 53.1557 | 0.27752 | 6.59 | 6.72 | 7.18 | 7.9 | 110.9 | 338 | 350.1071 | -3.582 | 92.9496 | 346.9784 | 97.7232 | 0.002 | 0.069 | 0.238 | 0.23857 | -0.2401 | 97.2973 | 0.23641 | 99.154 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.023 | 1.11 | 1.0665 | 8.1575 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.035 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.893 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.98 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 53.46 | 72.22 | 62.84 | 29.8536 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 13:00 | 73 | 22.8 | 56 | 57 | 350 | 6.4 | 2.4 |  | 8.8 | 0.23793 | 0.72727 | 38.7727 | 14.5785 | 14.3646 | 383.3607 | 10.3085 | 376.5392 | 3.6964 | 52.8036 | 0.27204 | [27 empty] | SDS-Cl2 demand | mg/L | 0.177 | 0.09 | 0.1335 | 65.1685 | --- | 7.7218 | --- | 94.4606 | 7.652 | 98.2554 | SDS-Cl2 demand | mg/L | 0.165 | --- | 20.5741 | --- | 93.1535 | 20.4106 | 99.1916 | SDS-Cl2 demand | mg/L | 0.307 | --- | 4.5988 | --- | 87.2614 | 4.5632 | 93.2723 | SDS-Cl2 demand | mg/L | 0.22 | --- | 3.3045 | --- | 90.8714 | 3.2795 | 93.2916 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 19.09 | 23.12 | 21.105 | 19.095 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 15:00 | 75 | 22.4 | 56 | 57 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 14.5355 | 346.8463 | 9.3266 | 340.6745 | 3.3443 | 53.1557 | 0.27345 | [27 empty] | SDS-Chlorination temp. | oC | 30.3 | 30.3 | 30.3 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 19.3594 | 19.5997 | 19.3594 | 19.3594 | Qp/QT (THM4), % | 59.6797 | 60.4207 | 59.6797 | 59.6797
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 4.92 | 5.76 | 5.34 | 15.7303 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 17:00 | 77 | 22.2 | 58 | 59 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 14.6217 | 346.8463 | 9.3266 | 340.6745 | 3.3443 | 55.1557 | 0.2651 | 5.9 |  |  | 10.2 |  |  | 344.85 |  | 90.8969 | 341.7903 | 97.0157 | 0.002 |  |  | 0.23857 |  | 97.2973 | 0.23641 | 99.154 | [8 empty] | SDS-Chlorination pH | --- | 8.13 | 8.09 | 8.11 | 0.49322 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.11 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.09 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.05 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 7:00 | 91 | 22.4 | 59 | 60 | 350 | 6.3 | 2.8 |  | 9.1 | 0.23793 | 0.69231 | 37.4615 | 14.3507 | 14.3084 | 343.3813 | 9.2361 | 337.3667 | 3.3114 | 56.1886 | 0.25465 | [27 empty] | SDS-Incubation time | hours | 6.34 | 6.34 | 6.34 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.34 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.34 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.34 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 33.0949 | 32.9963 | 33.0949 | 33.0949 | SDS-HAA5b, ug/L | 16.5475 | 16.2434 | 16.5475 | 16.5475
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 77.47 | 101.1 | 89.285 | 26.4658 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 8:00 | 92 | 21.9 | 59 | 60 | 350 | 6 | 0.67 |  | 6.67 | 0.23793 | 0.89955 | 51.4738 | 13.6673 | 13.8299 | 898.8023 | 24.196 | 883.8091 | 8.6711 | 50.8289 | 0.27209 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | 2.55 | 1.75 | 2.15 | 37.2093 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 9:00 | 93 | 22 | 59 | 60 | 360 | 5.8 | 0.7 |  | 6.5 | 0.24473 | 0.89231 | 54.3846 | 13.2118 | 13.3294 | 850.5519 | 22.9205 | 837.2178 | 8.2096 | 51.2904 | 0.25988 | 6.25 |  |  | 13.1 |  |  | 931.9214 |  | 88.3088 | 924.5198 | 98.583 | 0.001 |  |  | 0.67886 |  | 98.6486 | 0.6734 | 99.8515 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 1.9693 | 1.97 | 2.0029 | 1.986 | SDS-CDb, mg/L | 1.0514 | 1.0536 | 1.1549 | 1.103
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 18.99 | 21.73 | 20.36 | 13.4578 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 10:00 | 94 | 21.7 | 59 | 60 | 350 | 5.7 | 0.67 |  | 6.37 | 0.23793 | 0.89482 | 53.9451 | 12.984 | 13.2163 | 866.6581 | 23.3505 | 852.9242 | 8.3644 | 51.1356 | 0.25846 | 6.09 |  |  | 14.8 |  |  | 939.4007 |  | 86.7916 | 931.8719 | 98.4118 | 0.001 |  |  | 0.69504 |  | 98.6486 | 0.68939 | 99.8549 | [8 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 18.5 | 16.14 | 17.32 | 13.6259 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 11:00 | 95 | 22 | 59 | 60 | 350 | 5.6 | 0.7 |  | 6.3 | 0.23793 | 0.88889 | 54.5556 | 12.7562 | 12.8698 | 829.5864 | 22.3579 | 816.6708 | 8.0077 | 51.4923 | 0.24994 | 6.15 | 6.09 | 7.31 | 15.8 | 109.8 | 643 | 882.05 | -37.1773 | 85.8992 | 875.12 | 98.1945 | 0.001 | 0.075 | 0.523 | 0.658 | -25.8126 | 98.6486 | 0.65274 | 99.8468 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 1.095 | --- | 39.6859 | --- | 79.4944 | 39.3768 | 97.2192 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.060255 | 0.060084 | 0.060448 | 0.060061 | UV254 b, cm-1 | 0.031627 | 0.031101 | 0.032224 | 0.031031
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 12:00 | 96 | 22 | 59 | 60 | 350 | 5.6 | 0.7 |  | 6.3 | 0.23793 | 0.88889 | 54.5556 | 12.7562 | 12.8698 | 829.5864 | 22.3579 | 816.6708 | 8.0077 | 51.4923 | 0.24994 |  |  |  | 15.9 |  |  | 881.25 |  | 85.8099 | 874.3272 | 98.1815 | 0 | [15 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | #DIV/0! | 53.5421 | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 39.0507 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 1.11 | 1.31 | 1.21 | 16.5289 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 15:00 | 99 | 21.5 | 66 | 66 | 350 | 5.7 | 0.76 |  | 6.46 | 0.23793 | 0.88235 | 53.1796 | 12.984 | 13.2947 | 792.3186 | 21.3475 | 779.7628 | 7.6469 | 58.3531 | 0.22783 | [27 empty] | SDS-THM4 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 297.6167 | --- | 100 | 294.8786 | 100 | SDS-THM4 | mg/L | 1.095 | --- | 802.8223 | --- | 98.7736 | 796.4004 | 99.8625 | SDS-THM4 | mg/L | 0 | --- | 182.2143 | --- | 100 | 180.7009 | 100 | SDS-THM4 | mg/L | 0 | --- | 125.7535 | --- | 100 | 124.7324 | 100 | Alkb, mg/L CaCO3 | 4.9998 | 4.9396 | 4.7965 | 4.8159 | Alkb, mg/L CaCO3 | 3.1249 | 2.9394 | 2.4983 | 2.5579
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 5.36 | 6.2 | 5.78 | 14.5329 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 8:00 | 116 | 22.4 | 64 | 65 | 360 | 5.9 | 5.6 |  | 11.5 | 0.24473 | 0.51304 | 30.3043 | 13.4396 | 13.3999 | 223.7518 | 6.028 | 220.1835 | 2.1594 | 62.3406 | 0.21495 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 24.3293 | 24.8071 | 24.2712 | 24.8133 | T-Hdb, mg/L CaCO3 | 12.4147 | 13.8875 | 12.2356 | 13.9066
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 9:00 | 117 | 22.5 | 64 | 65 | 350 | 6.2 | 6.4 |  | 12.6 | 0.23793 | 0.49206 | 26.7778 | 14.1229 | 14.0397 | 214.9948 | 5.7844 | 211.2887 | 2.0736 | 62.4264 | 0.2249 | [27 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 16.004 | 16.369 | 15.9652 | 16.5073 | Ca-Hdb, mg/L CaCO3 | 8.202 | 9.3274 | 8.0826 | 9.7537
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 10:00 | 118 | 22.7 | 64 | 65 | 350 | 6.2 | 6.2 |  | 12.4 | 0.23793 | 0.5 | 27.2258 | 14.1229 | 13.9569 | 218.2286 | 5.8714 | 214.4668 | 2.1048 | 62.3952 | 0.22369 | 6.38 |  |  | 5.1 |  |  | 219 |  | 95.4485 | 217.1055 | 97.6509 | 0.001 |  |  | 0.147 |  | 98.6486 | 0.14571 | 99.3137 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 12:00 | 120 | 22.5 | 64 | 65 | 350 | 6.1 | 6 |  | 12.1 | 0.23793 | 0.50413 | 27.9256 | 13.8951 | 13.8132 | 219.9494 | 5.9194 | 216.2192 | 2.1216 | 62.3784 | 0.22144 | 6.37 |  |  | 5.2 |  |  | 220.6808 |  | 95.3592 | 218.8031 | 97.6234 | 0.001 |  |  | 0.14822 |  | 98.6486 | 0.14693 | 99.3194 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 41.15 | 40.93 | 41.04 | 0.53606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 14:00 | 122 | 23.9 | 58 | 60 | 350 | 5.8 | 5.6 |  | 11.4 | 0.23793 | 0.50877 | 29.7018 | 13.2118 | 12.6015 | 221.911 | 5.9773 | 218.3327 | 2.1414 | 56.8586 | 0.22163 | 5.7 | 6.56 | 7.1 | 5 | 113 | 183.5 | 222.9232 | -21.484 | 95.5377 | 221.1176 | 97.7388 | 0.001 | 0.07 | 0.145 | 0.14961 | -3.1773 | 98.6486 | 0.14838 | 99.326 | [8 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 46.51 | 47.13 | 46.82 | 1.3242 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 16:00 | 124 | 24.3 | 60 | 61 | 350 | 6 | 6 |  | 12 | 0.23793 | 0.5 | 28.1667 | 13.6673 | 12.8828 | 218.2253 | 5.8747 | 214.585 | 2.1053 | 58.3947 | 0.22062 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -31.5789 | -31.5789 | -31.5789 | -31.5789 | Qp/QT (HAA5), % | 34.2105 | 34.2105 | 34.2105 | 34.2105
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 8:00 | 140 | 23 | 60 | 61 | 350 | 5.8 | 14 |  | 19.8 | 0.23793 | 0.29293 | 16.6768 | 13.2118 | 12.9412 | 156.7219 | 4.2214 | 154.1947 | 1.5124 | 58.9876 | 0.21939 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 58.7401 | 59.1147 | 58.7401 | 58.7401
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 9:00 | 141 | 23.3 | 60 | 61 | 350 | 5.7 | 13.9 |  | 19.6 | 0.23793 | 0.29082 | 16.8571 | 12.984 | 12.6058 | 156.272 | 4.2105 | 153.7955 | 1.5082 | 58.9918 | 0.21369 | [27 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 10:00 | 142 | 23.4 | 60 | 60 | 350 | 5.8 | 14 |  | 19.8 | 0.23793 | 0.29293 | 16.6768 | 13.2118 | 12.7891 | 156.7219 | 4.2214 | 154.1947 | 1.5124 | 58.4876 | 0.21866 | 6.73 |  |  | 6.4 |  |  | 155.8193 |  | 94.2883 | 154.5812 | 95.8598 | 0.001 |  |  | 0.10424 |  | 98.6486 | 0.10339 | 99.0328 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-07-14 | 12:00 | 144 | 23.6 | 60 | 60 | 350 | 5.8 | 13.9 |  | 19.7 | 0.23793 | 0.29442 | 16.7665 | 13.2118 | 12.7137 | 157.0397 | 4.2299 | 154.5074 | 1.5154 | 58.4846 | 0.21739 | 6.83 | 5.7 | 7.09 | 5.6 | 113 | 149.1 | 156.468 | -4.9416 | 95.0022 | 155.2179 | 96.3922 | 0.002 | 0.079 | 0.108 | 0.10404 | 3.6637 | 97.2973 | 0.1032 | 98.062 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 136.8 | --- | 100 | 135.5414 | 100 | SDS-HAA5 | mg/L | 0 | --- | 373.0909 | --- | 100 | 370.1025 | 100 | SDS-HAA5 | mg/L | 0 | --- | 83.7551 | --- | 100 | 83.0595 | 100 | SDS-HAA5 | mg/L | 0 | --- | 57.8028 | --- | 100 | 57.3335 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.6312 | 1.642 | 1.6906 | 1.6608
[45 empty] | 1998-07-14 | 14:00 | 146 | 24 | 59 | 60 | 350 | 5.8 | 13.8 |  | 19.6 | 0.23793 | 0.29592 | 16.8571 | 13.2118 | 12.5643 | 157.362 | 4.2386 | 154.8246 | 1.5185 | 57.9815 | 0.21669 | 6.15 |  |  | 5.5 |  |  | 156.8319 |  | 95.0915 | 155.578 | 96.4648 | 0.001 |  |  | 0.10468 |  | 98.6486 | 0.10382 | 99.0368 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 156.0667 | --- | 100 | 154.6309 | 100 | SDS-HAA6 | mg/L | 0 | --- | 425.6364 | --- | 100 | 422.227 | 100 | SDS-HAA6 | mg/L | 0 | --- | 95.551 | --- | 100 | 94.7574 | 100 | SDS-HAA6 | mg/L | 0 | --- | 65.9437 | --- | 100 | 65.4082 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-07-14 | 16:00 | 148 | 23.4 | 60 | 60 | 350 | 6 | 14 |  | 20 | 0.23793 | 0.3 | 16.5 | 13.6673 | 13.2301 | 158.2457 | 4.26 | 155.606 | 1.5267 | 58.4733 | 0.22626 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.049711 | 0.049711 | 0.050053 | 0.049368
[45 empty] | 1998-07-15 | 17:00 | 166 | 24.2 | 58 | 59 | 350 | 7.5 | 17.8 | X | 25.3 | 0.23793 | 0.29644 | 12.834 | 17.0842 | 16.1511 | 157.4834 | 4.2215 | 154.1992 | 1.5162 | 56.9838 | 0.28343 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | #DIV/0! | 48.3553 | #VALUE! | #VALUE!
[45 empty] | 1998-07-16 | 8:00 | 181 | 23.4 | 57 | 58 | 350 | 7.2 | 17.6 |  | 24.8 | 0.23793 | 0.29032 | 13.1129 | 16.4008 | 15.8761 | 156.1746 | 4.19 | 153.048 | 1.5042 | 55.9958 | 0.28352 | 6.86 | 6.96 | 6.29 | 5.5 | 109.7 | 148.7 | 155.6386 | -4.6662 | 95.0915 | 154.0944 | 96.4308 | 0.001 | 0.071 | 0.103 | 0.10386 | -0.83848 | 98.6486 | 0.10281 | 99.0273 | [47 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 4.3092 | 4.2237 | 3.95 | 3.9842
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 19.9408 | 20.8987 | 19.8382 | 20.7961
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 13.1303 | 13.8487 | 13.0618 | 14.0197
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on R8: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R9: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R10: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R11: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R12: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R13: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R14: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R16: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R17: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R18: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on U6: C. Hill (8/30/99): Reviewer added chemical formula and dose. This information was copied from the pretreatment data for the NF200 membrane used during this study. All other pre-treatment information for these two membranes was identical, so it was assumed the alum formula and dose were also identical.
Note on DG19: C. Hill (8/30/99): Calcium hardness permeate and concentrate during Run 1 (70%), permeate and concentrate TDS, total and calcium hardness data during Run 2 (90%), and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ17: C. Hill (8/30/99): Calcium hardness permeate and concentrate during Run 1 (70%), permeate and concentrate TDS, total and calcium hardness data during Run 2 (90%), and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ18: C. Hill (8/30/99): Calcium hardness permeate and concentrate during Run 1 (70%), permeate and concentrate TDS, total and calcium hardness data during Run 2 (90%), and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ19: C. Hill (8/30/99): Calcium hardness permeate and concentrate during Run 1 (70%), permeate and concentrate TDS, total and calcium hardness data during Run 2 (90%), and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on EA17: C. Hill (8/30/99): Calcium hardness permeate and concentrate during Run 1 (70%), permeate and concentrate TDS, total and calcium hardness data during Run 2 (90%), and permeate and concentrate TDS data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."

## XLE. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 1.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.96908 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 14.1 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1998-10-07 | 1998-10-14 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.3 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.53 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 14 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -5.08 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 12:00 | 8:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [6 empty] | SDS-THM4F, ug/L | 79.515 | 79.515 | 79.515 | 79.515 | SDS-THM4F, ug/L | 79.515 | 79.515 | 79.515 | 79.515 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 112 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 1 | 161 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 0 | 0 | 0 | 0 | SDS-THM4p, ug/L | 0 | 0 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.35 | 5.98 | 5.665 | 11.1209 | 1998-10-05 | 10:00 | 0 | 21.9 | 56 | 57 | 350 | 9.8 | 3.8 | 13.6 | 0.23793 | 0.72059 | 24.7353 | 22.3233 | 22.5888 | 2.7264 | 0.053031 | 2.6515 | 0.026359 | 56.4736 | 0.39999 | 1998-10-07 | 11:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 56.855 | 56.855 | 56.855 | 56.855 | SDS-HAA5F, ug/L | 56.855 | 56.855 | 56.855 | 56.855 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21328 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | NA | 22.5 | 22.5 | #VALUE! | 1998-10-05 | 12:00 | 2 | 21.7 | 56 | 57 | 350 | 10.2 | 4.1 | 14.3 | 0.23793 | 0.71329 | 23.4755 | 23.2345 | 23.6502 | 2.6616 | 0.051711 | 2.5855 | 0.025719 | 56.4743 | 0.41878 | 1998-10-07 | 12:00 | 1 | 21.8 | 59 | 60 | 350 | 9.2 | 3.9 |  | 13.1 | 0.23793 | 0.70229 | 25.7176 | 20.9566 | 21.2686 | 328.8135 | 9.9089 | 320.4309 | 3.1471 | 56.3529 | 0.37742 |  | 5.35 |  |  | 104.6 | [7 empty] | 0.073 | [14 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 2.4 | 2.6 | 2.5 | 8 | 1998-10-05 | 14:00 | 4 | 22.3 | 56 | 57 | 350 | 10.4 | 4.3 | 14.7 | 0.23793 | 0.70748 | 22.8095 | 23.6901 | 23.6901 | 2.6122 | 0.050722 | 2.5361 | 0.025234 | 56.4748 | 0.41948 | 1998-10-07 | 14:00 | 3 | 22.1 | 60 | 60 | 350 | 9 | 3.9 |  | 12.9 | 0.23793 | 0.69767 | 26.1318 | 20.501 | 20.6226 | 324.2494 | 9.7769 | 316.1629 | 3.1043 | 56.8957 | 0.36246 | 5.05 |  | 5.95 | 18 |  | 280 | 305.2731 | -9.0261 | 82.8326 | 301.5796 | 94.0314 | 0.001 |  | 0.242 | 0.24081 | 0.49269 | 98.6395 | 0.23772 | 99.5793 | [8 empty] | Sampling date | MM/DD/YY | 1998-10-10 | 1998-10-10 | --- | --- | 1998-10-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-11 | 1998-10-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-12 | 1998-10-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-13 | 1998-10-13 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 267.5 | 267.5 | 267.5 | 267.5 | SDS-TOXF, ug Cl- /L | 267.5 | 267.5 | 267.5 | 267.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 104.6 | 105.1 | 104.85 | 0.47687 | 1998-10-05 | 16:00 | 6 | 21.8 | 56 | 57 | 350 | 10.3 | 4.5 | 14.8 | 0.23793 | 0.69595 | 22.6486 | 23.4623 | 23.8116 | 2.5191 | 0.048929 | 2.4464 | 0.024338 | 56.4757 | 0.42163 | 1998-10-07 | 17:00 | 6 | 21.7 | 60 | 60 | 350 | 8.9 | 3.9 |  | 12.8 | 0.23793 | 0.69531 | 26.3438 | 20.2732 | 20.636 | 321.9626 | 9.7108 | 314.0225 | 3.0828 | 56.9172 | 0.36256 | [27 empty] | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 63 | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | 63 | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 30 | 27.2 | 28.6 | 9.7902 | 1998-10-06 | 7:30 | 21.5 | 21.6 | 56 | 57 | 350 | 10.1 | 4.4 | 14.5 | 0.23793 | 0.69655 | 23.1379 | 23.0067 | 23.4877 | 2.5238 | 0.049047 | 2.4524 | 0.02439 | 56.4756 | 0.41589 | 1998-10-08 | 7:00 | 20 | 21.3 | 62 | 62 | 340 | 8.4 | 4 |  | 12.4 | 0.23113 | 0.67742 | 26.4194 | 19.1343 | 19.7083 | 305.661 | 9.2257 | 298.3373 | 2.9277 | 59.0723 | 0.33363 | 6.19 |  |  | 9 |  |  | 306.135 |  | 91.4163 | 302.4645 | 97.0244 | 0 | [15 empty] | Operation time | hh.hh | 73 | 73 | --- | --- | 73 | --- | --- | --- | --- | --- | Operation time | hh.hh | 97 | 97 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122 | 122 | --- | --- | --- | --- | --- | Cumulative time | hr | 145.5 | 145.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.805 | 2.805 | 2.805 | 2.805 | SDS-CDF, mg/L | 2.805 | 2.805 | 2.805 | 2.805 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 17 | 15.2 | 16.1 | 11.1801 | 1998-10-06 | 12:00 | 26 | 22.7 | 56 | 57 | 340 | 10.2 | 4.4 | 14.6 | 0.23113 | 0.69863 | 22.2877 | 23.2345 | 22.9614 | 2.5402 | 0.04931 | 2.4655 | 0.024536 | 56.4755 | 0.40657 | 1998-10-08 | 9:00 | 22 | 21.7 | 62 | 63 | 340 | 8.4 | 3.6 |  | 12 | 0.23113 | 0.7 | 27.3333 | 19.1343 | 19.4767 | 326.5053 | 9.8549 | 318.6822 | 3.1274 | 59.3726 | 0.32804 | [27 empty] | pH | --- | 5.7 | 5.71 | 5.705 | 0.17528 | 6.33 | --- | --- | --- | --- | --- | pH | --- | 5.71 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 6.09 | 6.75 | --- | --- | --- | --- | --- | pH | --- | 6.24 | 6.48 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.235 | 0.36 | 0.17 | 0.16 | SDS-CDp, mg/L | 0.235 | 0.36 | 0.17 | 0.16 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 3.6811 | 74.0109 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 5.6 |  |  |  | Turbidity | ntu | 0.16 | 0.16 | 0.16 | 0 | 1998-10-06 | 14:00 | 28 | 22.9 | 56 | 57 | 340 | 10.3 | 4.4 | 14.7 | 0.23113 | 0.70068 | 22.1293 | 23.4623 | 23.0498 | 2.5566 | 0.049613 | 2.4806 | 0.02469 | 56.4753 | 0.40814 | 1998-10-08 | 11:00 | 24 | 21.6 | 63 | 63 | 340 | 8.4 | 3.6 |  | 12 | 0.23113 | 0.7 | 27.3333 | 19.1343 | 19.5343 | 326.5053 | 9.8549 | 318.6822 | 3.1274 | 59.8726 | 0.32626 | 5.86 | 5.8 | 6.35 | 10.9 | 104.9 | 306 | 324.0667 | -5.9041 | 89.6042 | 320.1981 | 96.5959 | 0 | 0.072 | 0.23 |  | #VALUE! | [11 empty] | Temperature | oC | 21.1 | 21.1 | 21.1 | 0 | 21.1 | --- | --- | --- | --- | --- | Temperature | oC | 21.2 | 21.2 | --- | --- | --- | --- | --- | Temperature | oC | 22.8 | 22.8 | --- | --- | --- | --- | --- | Temperature | oC | 22.5 | 22.5 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.525 | 3.525 | 3.525 | 3.525 | TOCF, mg/L | 3.525 | 3.525 | 3.525 | 3.525 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 10.9984 | 81.3283 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-10-06 | 18:00 | 32 | 22.4 | 58 | 58 | 350 | 10.4 | 4.4 | 14.8 | 0.23793 | 0.7027 | 22.6486 | 23.6901 | 23.6201 | 2.5728 | 0.049957 | 2.4979 | 0.024854 | 57.9751 | 0.40742 | 1998-10-08 | 13:00 | 26 | 21.6 | 63 | 63 | 340 | 8.2 | 3.5 |  | 11.7 | 0.23113 | 0.70085 | 28.0598 | 18.6787 | 19.0692 | 327.3377 | 9.8858 | 319.6815 | 3.1362 | 59.8638 | 0.31854 | [27 empty] | Alkalinity | mg/L as CaCO3 | 0.4 | 0.7 | 0.55 | 54.5455 | 4.8 | 7.05 | -46.875 | 78 | 6.9961 | 92.1384 | Alkalinity | mg/L as CaCO3 | 0.8 | 10.2 | 16.2545 | -59.3583 | 68 | 16.1459 | 95.0452 | Alkalinity | mg/L as CaCO3 | BMRL | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 0.8 | 2.6 | 3.2286 | -24.1758 | 68 | 3.214 | 75.1089 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 2.2176 | 72.5475 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.45 | 3.6 | 3.525 | 4.2553 | 1998-10-07 | 7:30 | 45.5 | 21.8 | 58 | 58 | 340 | 10.2 | 4.4 | 14.6 | 0.23113 | 0.69863 | 22.2877 | 23.2345 | 23.5804 | 2.5402 | 0.04931 | 2.4655 | 0.024536 | 57.9755 | 0.40673 | 1998-10-08 | 15:00 | 28 | 21.8 | 62 | 62 | 340 | 8.2 | 3.6 |  | 11.8 | 0.23113 | 0.69492 | 27.8136 | 18.6787 | 18.9568 | 321.5552 | 9.7111 | 314.0343 | 3.0808 | 58.9192 | 0.32174 | [27 empty] | Total dissolved solids | mg/L | 10.1 | 10.1 | 10.1 | 0 | 216 | 325.9333 | -50.8951 | 90.3672 | 323.3119 | 96.8761 | Total dissolved solids | mg/L | 18.3 | 599 | 805.1182 | -34.4104 | 82.5465 | 799.5861 | 97.7113 | Total dissolved solids | mg/L | 8.5 | 174 | 205.1327 | -17.8923 | 91.8932 | 203.8433 | 95.8301 | Total dissolved solids | mg/L | 9.4 | 142.3 | 145.7571 | -2.4295 | 91.0348 | 144.939 | 93.5145 | UV254 F, cm-1 | 0.0735 | 0.0735 | 0.0735 | 0.0735 | UV254 F, cm-1 | 0.0735 | 0.0735 | 0.0735 | 0.0735 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 1.5904 | 71.9203 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.073 | 0.074 | 0.0735 | 1.3605 | 1998-10-07 | 10:30 | 48.5 | 21.8 | 58 | 59 | 350 | 10.3 | 4.5 | 14.8 | 0.23793 | 0.69595 | 22.6486 | 23.4623 | 23.8116 | 2.5191 | 0.048929 | 2.4464 | 0.024338 | 58.4757 | 0.40721 | 1998-10-08 | 17:00 | 30 | 21.7 | 63 | 64 | 340 | 8.2 | 3.5 |  | 11.7 | 0.23113 | 0.70085 | 28.0598 | 18.6787 | 19.0129 | 327.3377 | 9.8858 | 319.6815 | 3.1362 | 60.3638 | 0.31497 | 5.96 |  |  | 8.7 |  |  | 330.1157 |  | 91.7024 | 326.2398 | 97.3333 | 0 | [15 empty] | Total hardness | mg/L as CaCO3 | 0.8 | 1.1 | 0.95 | 31.5789 | 84.5 | 93.1167 | -10.1972 | 96.6783 | 92.3517 | 98.9713 | Total hardness | mg/L as CaCO3 | 1 | 216 | 251.9091 | -16.6246 | 96.5035 | 250.1449 | 99.6002 | Total hardness | mg/L as CaCO3 | 7.4 | 62.6 | 50.6653 | 19.065 | 74.1259 | 50.3816 | 85.3121 | Total hardness | mg/L as CaCO3 | 0.7 | 38.9 | 40.5571 | -4.26 | 97.5524 | 40.318 | 98.2638 | UV254 p, cm-1 | 0 | 0 | 0.002 | 0.001 | UV254 p, cm-1 | 0 | 0 | 0.002 | 0.001 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.19 |  |  |  | SUVA | L/(mg*m) | 2.1159 | 2.0556 | 2.0857 | 2.8952 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 7:00 | 44 | 20.8 | 62 | 63 | 350 | 7 | 3.5 |  | 10.5 | 0.23793 | 0.66667 | 32.3333 | 15.9452 | 16.6681 | 296.564 | 8.993 | 290.8125 | 2.847 | 59.653 | 0.27942 | 5.46 |  |  | 10.4 |  |  | 293.75 |  | 90.0811 | 290.9165 | 96.4251 | 0.004 |  |  | 0.2125 |  | 94.5578 | 0.21041 | 98.099 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 0.6 | 0.9 | 0.75 | 40 | 47.9 | 51.9167 | -8.3855 | 95.3416 | 51.492 | 98.5435 | Calcium hardness | mg/L as CaCO3 | 0.8 | 130.8 | 139.8909 | -6.9502 | 95.0311 | 138.913 | 99.4241 | Calcium hardness | mg/L as CaCO3 | 7.2 | 35.7 | 25.3633 | 28.9544 | 55.2795 | 25.2442 | 71.4786 | Calcium hardness | mg/L as CaCO3 | 0.4 | 22.2 | 22.8286 | -2.8314 | 97.5155 | 22.694 | 98.2374 | BromideF, ug/L | 56.2 | 56.2 | 56.2 | 56.2 | BromideF, ug/L | 56.2 | 56.2 | 56.2 | 56.2 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 53.4 | 59 | 56.2 | 9.9644 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 9:00 | 46 | 20.7 | 62 | 63 | 340 | 6.9 | 3 |  | 9.9 | 0.23113 | 0.69697 | 33.3434 | 15.7174 | 16.4786 | 323.4523 | 9.8055 | 317.0871 | 3.1046 | 59.3954 | 0.27744 | [27 empty] | Turbidity | ntu | 0.14 | 0.12 | 0.13 | 15.3846 | 0.17 | 0.23 | -35.2941 | 18.75 | 0.22917 | 43.2736 | Turbidity | ntu | 0.1 | 0.19 | 0.64545 | -239.7129 | 37.5 | 0.64162 | 84.4144 | Turbidity | ntu | 0.15 | 0.17 | 0.17041 | -0.2401 | 6.25 | 0.17027 | 11.9069 | Turbidity | ntu | 0.45 | 0.6 | 0.035714 | 94.0476 | -181.25 | 0.0382 | -1078.0105 | Bromidep, ug/L | #DIV/0! | 27 | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | 27 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 11:00 | 48 | 21.1 | 62 | 62 | 340 | 6.6 | 3 |  | 9.6 | 0.23113 | 0.6875 | 34.4167 | 15.0341 | 15.5769 | 314.5249 | 9.5432 | 308.6047 | 3.0202 | 58.9798 | 0.26411 | 5.45 | 5.84 | 6.14 | 10.1 | 103.8 | 294 | 313.3 | -6.5646 | 90.3672 | 310.3572 | 96.7457 | 0.004 | 0.074 | 0.228 | 0.2264 | 0.70175 | 94.5578 | 0.22424 | 98.2162 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 2.5 | 2.5 | 2.5 | 2.5 | AlkF, mg/L CaCO3 | 2.5 | 2.5 | 2.5 | 2.5
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 2.16 | 2.23 | 2.195 | 3.1891 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 13:00 | 50 | 21.4 | 62 | 62 | 350 | 6.7 | 3 |  | 9.7 | 0.23793 | 0.69072 | 35.0825 | 15.2619 | 15.6733 | 317.4948 | 9.6359 | 311.6015 | 3.0491 | 58.9509 | 0.26587 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 29 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.96 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 0.55 | 0.8 | BMRL | 0.8 | Alkp, mg/L CaCO3 | 0.55 | 0.8 | BMRL | 0.8
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | pH | 5.45 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 2.84 | 2.77 | 2.805 | 2.4955 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 15:00 | 52 | 21.4 | 62 | 62 | 350 | 6.7 | 3 |  | 9.7 | 0.23793 | 0.69072 | 35.0825 | 15.2619 | 15.6733 | 317.4948 | 9.6359 | 311.6015 | 3.0491 | 58.9509 | 0.26587 | [27 empty] | UV254 | cm-1 | 0 | 0 | 0 | #DIV/0! | 0.231 | 0.245 | -6.0606 | 100 | 0.24297 | 100 | UV254 | cm-1 | 0 | 0.452 | 0.66818 | -47.8278 | 100 | 0.66348 | 100 | UV254 | cm-1 | 0.002 | 0.148 | 0.14792 | 0.055157 | 97.2789 | 0.14696 | 98.6391 | UV254 | cm-1 | 0.001 | 0.099 | 0.10457 | -5.6277 | 98.6395 | 0.10395 | 99.038 | T-HdF, mg/L CaCO3 | 28.6 | 28.6 | 28.6 | 28.6 | T-HdF, mg/L CaCO3 | 28.6 | 28.6 | 28.6 | 28.6
Treatment Plant Category | CONV | [11 empty] | UV254 | 0.0625 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 30.4 | 30.3 | 30.35 | 0.32949 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 17:00 | 54 | 21.4 | 62 | 62 | 350 | 6.7 | 3 |  | 9.7 | 0.23793 | 0.69072 | 35.0825 | 15.2619 | 15.6733 | 317.4948 | 9.6359 | 311.6015 | 3.0491 | 58.9509 | 0.26587 | 5.35 |  |  | 7.9 |  |  | 321.3717 |  | 92.4654 | 318.3713 | 97.5186 | 0.003 |  |  | 0.23095 |  | 95.9184 | 0.22877 | 98.6886 | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.5586 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.0845 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.996 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 0.95 | 1 | 7.4 | 0.7 | T-Hdp, mg/L CaCO3 | 0.95 | 1 | 7.4 | 0.7
Process Train Name | Conventional Train | Additional Information | [10 empty] | Ammonia (mg/L) | BMRL |  |  |  | SDS-Chlorination pH | --- | 7.79 | 7.8 | 7.795 | 0.12829 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 7:00 | 68 | 20.3 | 62 | 63 | 350 | 6 | 2.9 |  | 8.9 | 0.23793 | 0.67416 | 38.3258 | 13.6673 | 14.4997 | 302.734 | 9.2061 | 297.7021 | 2.9101 | 59.5899 | 0.24332 | 5.7 |  |  | 10.1 |  |  | 300.8845 |  | 90.3672 | 298.392 | 96.6152 | 0.001 |  |  | 0.2235 |  | 98.6395 | 0.22159 | 99.5487 | [8 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | 27 | --- | 292.4545 | --- | 51.9573 | 290.5881 | 90.7085 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 16.1 | 16.1 | 16.1 | 16.1 | Ca-HdF, mg/L CaCO3 | 16.1 | 16.1 | 16.1 | 16.1
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | TDS (mg/L) | 107 |  |  |  | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 9:00 | 70 | 20.9 | 62 | 63 | 350 | 5.8 | 2.5 |  | 8.3 | 0.23793 | 0.6988 | 41.1687 | 13.2118 | 13.77 | 325.1496 | 9.8933 | 319.9253 | 3.1264 | 59.3736 | 0.23192 | [27 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 0.75 | 0.8 | 7.2 | 0.4 | Ca-Hdp, mg/L CaCO3 | 0.75 | 0.8 | 7.2 | 0.4
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | TOC (mg/L) | 3.4 |  |  |  | SDS-TOX | mg Cl- /L | 270 | 265 | 267.5 | 1.8692 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 11:00 | 72 | 21.1 | 62 | 63 | 350 | 5.8 | 2.5 |  | 8.3 | 0.23793 | 0.6988 | 41.1687 | 13.2118 | 13.6888 | 325.1496 | 9.8933 | 319.9253 | 3.1264 | 59.3736 | 0.23055 | 5.62 | 5.94 | 6.48 | 9.5 | 102.8 | 297 | 326.062 | -9.7852 | 90.9394 | 323.4391 | 97.0628 | 0 | 0.073 | 0.232 |  | #VALUE! | [11 empty] | SDS-Free Cl2 residual | mg/L | 2.33 | 2.2 | 2.265 | 5.7395 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.14 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.33 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.34 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 50.43 | 63.19 | 56.81 | 22.4608 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 13:00 | 74 | 20.8 | 62 | 63 | 350 | 5.8 | 2.6 |  | 8.4 | 0.23793 | 0.69048 | 40.6667 | 13.2118 | 13.8107 | 317.2151 | 9.6519 | 312.1183 | 3.0501 | 59.4499 | 0.23231 | [27 empty] | SDS-Cl2 demand | mg/L | 0.17 | 0.3 | 0.235 | 55.3191 | --- | 8.8017 | --- | 91.6221 | 8.7306 | 97.3083 | SDS-Cl2 demand | mg/L | 0.36 | --- | 22.5873 | --- | 87.1658 | 22.431 | 98.3951 | SDS-Cl2 demand | mg/L | 0.17 | --- | 5.5476 | --- | 93.9394 | 5.5123 | 96.916 | SDS-Cl2 demand | mg/L | 0.16 | --- | 3.9386 | --- | 94.2959 | 3.9159 | 95.9141 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 16.8 | 20.92 | 18.86 | 21.8452 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 15:00 | 76 | 21.1 | 62 | 63 | 350 | 5.8 | 2.6 |  | 8.4 | 0.23793 | 0.69048 | 40.6667 | 13.2118 | 13.6888 | 317.2151 | 9.6519 | 312.1183 | 3.0501 | 59.4499 | 0.23026 | [27 empty] | SDS-Chlorination temp. | oC | 30.3 | 30.3 | 30.3 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 9.451 | 9.451 | 9.451 | 9.451 | Qp/QT (THM4), % | 54.7255 | 54.7255 | 54.7255 | 54.7255
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 3.49 | 4.2 | 3.845 | 18.4655 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 17:00 | 78 | 21.1 | 62 | 63 | 350 | 5.8 | 2.6 |  | 8.4 | 0.23793 | 0.69048 | 40.6667 | 13.2118 | 13.6888 | 317.2151 | 9.6519 | 312.1183 | 3.0501 | 59.4499 | 0.23026 | 5.72 |  |  | 8.4 |  |  | 320.0077 |  | 91.9886 | 317.4258 | 97.3537 | 0.002 |  |  | 0.233 |  | 97.2789 | 0.23109 | 99.1345 | [8 empty] | SDS-Chlorination pH | --- | 7.83 | 7.8 | 7.815 | 0.38388 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.79 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.83 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.84 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 8:00 | 93 | 20.3 | 63 | 63 | 340 | 5 | 0.63 |  | 5.63 | 0.23113 | 0.8881 | 59.3908 | 11.3895 | 12.0831 | 754.4666 | 22.9983 | 743.7097 | 7.2609 | 55.7391 | 0.21678 | [27 empty] | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 51.4816 | 51.4816 | 51.4816 | 51.4816 | SDS-HAA5b, ug/L | 25.7408 | 25.7408 | 25.7408 | 25.7408
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 70.72 | 88.31 | 79.515 | 22.1216 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 9:00 | 94 | 20.9 | 63 | 63 | 350 | 5 | 0.6 |  | 5.6 | 0.23793 | 0.89286 | 61.5 | 11.3895 | 11.8707 | 780.3026 | 23.7957 | 769.4953 | 7.511 | 55.489 | 0.21393 | 5.6 |  |  | 16.9 |  |  | 837.7667 |  | 83.8817 | 831.9033 | 97.9685 | 0 | [15 empty] | SDS-TOX | mg Cl- /L | BMRL | 63 | 63 | #VALUE! | --- | 744.6667 | --- | 76.4486 | 739.0088 | 91.4751 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 248.1726 | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 155.5863 | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 10:00 | 95 | 20.9 | 63 | 63 | 350 | 4.8 | 0.63 |  | 5.43 | 0.23793 | 0.88398 | 63.4567 | 10.9339 | 11.3958 | 733.2446 | 22.3732 | 723.4955 | 7.06 | 55.94 | 0.20372 | 5.63 |  |  | 18 |  |  | 766.5643 |  | 82.8326 | 761.4313 | 97.636 | 0 | [15 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 2.5621 | 2.5739 | 2.556 | 2.555 | SDS-CDb, mg/L | 1.3986 | 1.467 | 1.363 | 1.3575
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 30.38 | 25.1 | 27.74 | 19.0339 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 11:00 | 96 | 21.2 | 63 | 63 | 350 | 4.9 | 0.63 |  | 5.53 | 0.23793 | 0.88608 | 62.2911 | 11.1617 | 11.5305 | 743.8653 | 22.6909 | 733.7688 | 7.1613 | 55.8387 | 0.2065 | 5.61 |  |  | 18.1 |  |  | 779.5722 |  | 82.7372 | 774.2419 | 97.6622 | 0 | [15 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 31.73 | 25.47 | 28.6 | 21.8881 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 12:00 | 97 | 21.2 | 63 | 63 | 350 | 4.9 | 0.63 |  | 5.53 | 0.23793 | 0.88608 | 62.2911 | 11.1617 | 11.5305 | 743.8653 | 22.6909 | 733.7688 | 7.1613 | 55.8387 | 0.2065 | 5.66 | 5.9 | 6.58 | 17.9 | 102.2 | 522 | 781.1278 | -49.6413 | 82.928 | 775.7852 | 97.6927 | 0 | 0.068 | 0.449 |  | #VALUE! | [11 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.066553 | 0.066553 | 0.066743 | 0.066648 | UV254 b, cm-1 | 0.033277 | 0.033277 | 0.034371 | 0.033824
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 13:00 | 98 | 21.2 | 63 | 63 | 350 | 4.9 | 0.63 |  | 5.53 | 0.23793 | 0.88608 | 62.2911 | 11.1617 | 11.5305 | 743.8653 | 22.6909 | 733.7688 | 7.1613 | 55.8387 | 0.2065 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | #DIV/0! | 53.4403 | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 40.2201 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 1.03 | BMRL | 1.03 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 15:00 | 100 | 21.1 | 63 | 63 | 350 | 4.9 | 0.63 |  | 5.53 | 0.23793 | 0.88608 | 62.2911 | 11.1617 | 11.5647 | 743.8653 | 22.6909 | 733.7688 | 7.1613 | 55.8387 | 0.20711 | [27 empty] | SDS-THM4 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 265.05 | --- | 100 | 262.8501 | 100 | SDS-THM4 | mg/L | 0 | --- | 722.8636 | --- | 100 | 717.7812 | 100 | SDS-THM4 | mg/L | 0 | --- | 162.2755 | --- | 100 | 161.2114 | 100 | SDS-THM4 | mg/L | 0 | --- | 113.5929 | --- | 100 | 112.9113 | 100 | Alkb, mg/L CaCO3 | 2.3157 | 2.3393 | #VALUE! | 2.3393 | Alkb, mg/L CaCO3 | 1.4329 | 1.5697 | #VALUE! | 1.5697
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.53 | 5.77 | 7.15 | 38.6014 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 8:00 | 117 | 20.6 | 63 | 63 | 350 | 4.2 | 4.2 |  | 8.4 | 0.23793 | 0.5 | 40.6667 | 9.5671 | 10.0602 | 203.4808 | 6.2192 | 201.1137 | 1.9608 | 61.0392 | 0.16481 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 25.9868 | 25.9915 | 26.5964 | 25.9632 | T-Hdb, mg/L CaCO3 | 13.4684 | 13.4958 | 16.9982 | 13.3316
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 9:00 | 118 | 21.1 | 62 | 63 | 350 | 4.3 | 4.3 |  | 8.6 | 0.23793 | 0.5 | 39.6977 | 9.7949 | 10.1486 | 203.4825 | 6.2175 | 201.059 | 1.9605 | 60.5395 | 0.16764 | [27 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 14.6493 | 14.654 | 15.2589 | 14.6162 | Ca-Hdb, mg/L CaCO3 | 7.6996 | 7.727 | 11.2294 | 7.5081
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 10:00 | 119 | 20.6 | 62 | 63 | 350 | 4.6 | 4.3 |  | 8.9 | 0.23793 | 0.51685 | 38.3258 | 10.4783 | 11.0183 | 210.1516 | 6.4159 | 207.474 | 2.024 | 60.476 | 0.18219 | 6.02 |  |  | 6.1 |  |  | 210.4895 |  | 94.1822 | 209.1464 | 97.0834 | 0.001 |  |  | 0.15106 |  | 98.6395 | 0.15007 | 99.3337 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 11:00 | 120 | 21.3 | 62 | 63 | 350 | 4.5 | 4.5 |  | 9 | 0.23793 | 0.5 | 37.8889 | 10.2505 | 10.558 | 203.4859 | 6.2141 | 200.9495 | 1.96 | 60.54 | 0.1744 | 5.97 |  |  | 5.7 |  |  | 204 |  | 94.5637 | 202.7252 | 97.1883 | 0.001 |  |  | 0.146 |  | 98.6395 | 0.14507 | 99.3107 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 63.14 | 50.57 | 56.855 | 22.1089 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 12:00 | 121 | 21.8 | 62 | 63 | 350 | 4.6 | 4.4 |  | 9 | 0.23793 | 0.51111 | 37.8889 | 10.4783 | 10.6343 | 207.8324 | 6.3451 | 205.1843 | 2.0016 | 60.4984 | 0.17578 | 6.08 | 6.01 | 6.41 | 5.5 | 103.5 | 174.3 | 208.7159 | -19.7452 | 94.7544 | 207.3805 | 97.3479 | 0.001 | 0.071 | 0.144 | 0.1493 | -3.6774 | 98.6395 | 0.14832 | 99.3258 | [8 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 71.67 | 56.34 | 64.005 | 23.9513 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 15:00 | 124 | 22.1 | 62 | 62 | 350 | 4.5 | 4.5 |  | 9 | 0.23793 | 0.5 | 37.8889 | 10.2505 | 10.3113 | 203.4859 | 6.2141 | 200.9495 | 1.96 | 60.04 | 0.17174 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 5.0215 | 5.0215 | 5.0215 | 5.0215 | Qp/QT (HAA5), % | 52.5108 | 52.5108 | 52.5108 | 52.5108
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-13 | 8:00 | 141 | 21.4 | 59 | 60 | 350 | 4.2 | 9.9 |  | 14.1 | 0.23793 | 0.29787 | 23.8227 | 9.5671 | 9.8251 | 147.4203 | 4.5058 | 145.7053 | 1.4206 | 58.0794 | 0.16917 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 75.5221 | 75.5221 | 75.5221 | 75.5221 | SDS-THM4b, ug/L | 37.7611 | 37.7611 | 37.7611 | 37.7611
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-13 | 9:00 | 142 | 21.1 | 59 | 60 | 350 | 4.2 | 10.6 |  | 14.8 | 0.23793 | 0.28378 | 22.6486 | 9.5671 | 9.9126 | 144.6427 | 4.4209 | 142.96 | 1.3938 | 58.1062 | 0.17059 | [27 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-13 | 10:00 | 143 | 20.9 | 59 | 60 | 350 | 4.2 | 9.8 |  | 14 | 0.23793 | 0.3 | 24 | 9.5671 | 9.9714 | 147.8491 | 4.5189 | 146.1291 | 1.4247 | 58.0753 | 0.1717 | 6.6 |  |  | 5.3 |  |  | 147.5143 |  | 94.9452 | 146.661 | 96.3862 | 0.003 |  |  | 0.10371 |  | 95.9184 | 0.10311 | 97.0905 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | 257.2309 | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 160.1155 | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-10-13 | 11:00 | 144 | 20.9 | 59 | 60 | 350 | 4.2 | 9.8 |  | 14 | 0.23793 | 0.3 | 24 | 9.5671 | 9.9714 | 147.8491 | 4.5189 | 146.1291 | 1.4247 | 58.0753 | 0.1717 | 6.54 |  |  | 5 |  |  | 147.6429 |  | 95.2313 | 146.787 | 96.5937 | 0.003 |  |  | 0.10371 |  | 95.9184 | 0.10311 | 97.0905 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 189.5167 | --- | 100 | 187.9437 | 100 | SDS-HAA5 | mg/L | 0 | --- | 516.8636 | --- | 100 | 513.2296 | 100 | SDS-HAA5 | mg/L | 0 | --- | 116.0306 | --- | 100 | 115.2698 | 100 | SDS-HAA5 | mg/L | 0 | --- | 81.2214 | --- | 100 | 80.7341 | 100 | SDS-CDb, mg/L | 2.6759 | 2.6822 | 2.6727 | 2.6722 | SDS-CDb, mg/L | 1.4555 | 1.5211 | 1.4213 | 1.4161
[45 empty] | 1998-10-13 | 12:00 | 145 | 21.3 | 59 | 60 | 350 | 4.2 | 9.8 |  | 14 | 0.23793 | 0.3 | 24 | 9.5671 | 9.8542 | 147.8491 | 4.5189 | 146.1291 | 1.4247 | 58.0753 | 0.16968 | 6.65 | 6.68 | 6.39 | 5.1 | 104.6 | 141.2 | 147.6 | -4.5326 | 95.1359 | 146.745 | 96.5246 | 0.003 | 0.071 | 0.101 | 0.10371 | -2.6874 | 95.9184 | 0.10311 | 97.0905 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 213.35 | --- | 100 | 211.5792 | 100 | SDS-HAA6 | mg/L | 0 | --- | 581.8636 | --- | 100 | 577.7726 | 100 | SDS-HAA6 | mg/L | 0 | --- | 130.6224 | --- | 100 | 129.7659 | 100 | SDS-HAA6 | mg/L | 0 | --- | 91.4357 | --- | 100 | 90.8871 | 100 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-10-13 | 16:00 | 149 | 21.6 | 59 | 60 | 350 | 4.3 | 9.6 |  | 13.9 | 0.23793 | 0.30935 | 24.1799 | 9.7949 | 9.9997 | 149.7643 | 4.5761 | 147.9806 | 1.443 | 58.057 | 0.17224 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.069809 | 0.069809 | 0.06991 | 0.069859 | UV254 b, cm-1 | 0.034905 | 0.034905 | 0.035955 | 0.03543
[45 empty] | 1998-10-14 | 8:00 | 161 | 20.5 | 59 | 60 | 340 | 4.2 | 10.2 |  | 14.4 | 0.23113 | 0.29167 | 22.6111 | 9.5671 | 10.09 | 146.1844 | 4.4664 | 144.4338 | 1.4084 | 58.0916 | 0.17369 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | #DIV/0! | 54.7337 | #VALUE! | #VALUE! | Bromideb, ug/L | #DIV/0! | 40.8669 | #VALUE! | #VALUE!
[45 empty] | 1998-10-15 | 8:00 | 178 | 21.5 | 56 | 57 | 350 | 7.3 | 17.1 | x | 24.4 | 0.23793 | 0.29918 | 13.3443 | 16.6286 | 17.0265 | 147.7001 | 4.4751 | 144.7129 | 1.4173 | 55.0827 | 0.30911 | [66 empty] | Alkb, mg/L CaCO3 | 2.4021 | 2.4146 | #VALUE! | 2.4146 | Alkb, mg/L CaCO3 | 1.476 | 1.6073 | #VALUE! | 1.6073
[45 empty] | 1998-10-15 | 9:00 | 179 | 21.6 | 56 | 57 | 350 | 7.2 | 17.3 |  | 24.5 | 0.23793 | 0.29388 | 13.2857 | 16.4008 | 16.7437 | 146.6374 | 4.4441 | 143.7123 | 1.4073 | 55.0927 | 0.30392 | 6.8 | 6.63 | 6.69 | 5.4 | 104.5 | 141.2 | 146.2396 | -3.5691 | 94.8498 | 144.791 | 96.2705 | 0.001 | 0.066 | 0.097 | 0.10367 | -6.8798 | 98.6395 | 0.10262 | 99.0255 | [47 empty] | T-Hdb, mg/L CaCO3 | 27.2115 | 27.2141 | 27.5354 | 27.199 | T-Hdb, mg/L CaCO3 | 14.0808 | 14.107 | 17.4677 | 13.9495
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | 15.3292 | 15.3317 | 15.6531 | 15.3116 | Ca-Hdb, mg/L CaCO3 | 8.0396 | 8.0659 | 11.4265 | 7.8558
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on U6: C. Hill (8/30/99): Reviewer added chemical formula and dose. This information was copied from the pretreatment data for the NF200 membrane used during this study. All other pre-treatment information for these two membranes was identical, so it was assumed the alum formula and dose were also identical.
Note on DG17: C. Hill (8/30/99): TDS permeate and concentrate data during Runs 1 (70%) and 2 (90%), permeate and concentrate UV data during Run 2 (90%) and permeate and concentrate total and calcium hardness data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ17: C. Hill (8/30/99): TDS permeate and concentrate data during Runs 1 (70%) and 2 (90%), permeate and concentrate UV data during Run 2 (90%) and permeate and concentrate total and calcium hardness data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ23: C. Hill (8/30/99): TDS permeate and concentrate data during Runs 1 (70%) and 2 (90%), permeate and concentrate UV data during Run 2 (90%) and permeate and concentrate total and calcium hardness data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on EA18: C. Hill (8/30/99): TDS permeate and concentrate data during Runs 1 (70%) and 2 (90%), permeate and concentrate UV data during Run 2 (90%) and permeate and concentrate total and calcium hardness data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on EA19: C. Hill (8/30/99): TDS permeate and concentrate data during Runs 1 (70%) and 2 (90%), permeate and concentrate UV data during Run 2 (90%) and permeate and concentrate total and calcium hardness data during Run 3 (50%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."

## XLE. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-2.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | Dow-Filmtec | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 1.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.98 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.9648 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | BW30-XLE | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 16.1 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1999-01-14 | 1999-01-21 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.4 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.3 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.5 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 100 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -5.12 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 12:00 | 8:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 350 | [10 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [7 empty] | Influent flow rate during sample collection (mL/min) | 350 | [6 empty] | SDS-THM4F, ug/L | 47.73 | 47.73 | 47.73 | 47.73 | SDS-THM4F, ug/L | 47.73 | 47.73 | 47.73 | 47.73 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 106 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 2 | 156 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 0 | 1.14 | 0 | 0 | SDS-THM4p, ug/L | 0 | 1.14 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.98 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.61 | 5.81 | 5.71 | 3.5026 | 1999-01-12 | 9:00 | 0 | 23.8 | 50 | 50 | 350 | 7.6 | 3.3 | 10.9 | 0.23793 | 0.69725 | 31.1101 | 17.312 | 16.5612 | 2.5284 | 0.049492 | 2.4746 | 0.02452 | 49.9755 | 0.33139 | 1999-01-14 | 10:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 31.41 | 31.41 | 31.41 | 31.41 | SDS-HAA5F, ug/L | 31.41 | 31.41 | 31.41 | 31.41 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21328 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 4 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | 22.2 | 21.7 | 21.95 | 2.2779 | 1999-01-12 | 11:00 | 2 | 23.8 | 51 | 51 | 350 | 7.4 | 3.3 | 10.7 | 0.23793 | 0.69159 | 31.7103 | 16.8564 | 16.1253 | 2.4848 | 0.048666 | 2.4333 | 0.024104 | 50.9759 | 0.31633 | 1999-01-14 | 12:00 | 2 | 23 | 52 | 52 | 350 | 6.5 | 2.7 |  | 9.2 | 0.23793 | 0.70652 | 37.0435 | 14.8063 | 14.5031 | 334.2247 | 11.5528 | 328.2322 | 3.1968 | 48.8032 | 0.29717 | 5.42 | 5.61 | 6.11 | 18.8 | 106.5 | 261 | 316.7778 | -21.3708 | 82.3059 | 314.0108 | 94.0129 | 0.001 | 0.055 | 0.151 | 0.185 | -22.5166 | 98.1818 | 0.18329 | 99.4544 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 0 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 2.5 | 2 | 2.25 | 22.2222 | 1999-01-12 | 14:00 | 5 | 24.8 | 51 | 51 | 350 | 7.7 | 3.4 | 11.1 | 0.23793 | 0.69369 | 30.5315 | 17.5398 | 16.2904 | 2.5009 | 0.04894 | 2.447 | 0.02425 | 50.9757 | 0.31957 | 1999-01-14 | 14:00 | 4 | 23.9 | 52 | 52 | 350 | 6.4 | 2.6 |  | 9 | 0.23793 | 0.71111 | 37.8889 | 14.5785 | 13.9051 | 338.9413 | 11.7192 | 332.9578 | 3.2423 | 48.7577 | 0.28519 | [27 empty] | Sampling date | MM/DD/YY | 1999-01-17 | 1999-01-17 | --- | --- | 1999-01-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-18 | 1999-01-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 172.5 | 172.5 | 172.5 | 172.5 | SDS-TOXF, ug Cl- /L | 172.5 | 172.5 | 172.5 | 172.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 106.5 | 106 | 106.25 | 0.47059 | 1999-01-12 | 16:00 | 7 | 24.9 | 51 | 51 | 350 | 7.8 | 3.5 | 11.3 | 0.23793 | 0.69027 | 29.9735 | 17.7675 | 16.4532 | 2.475 | 0.048418 | 2.4209 | 0.023995 | 50.976 | 0.32276 | 1999-01-14 | 17:00 | 7 | 24.1 | 52 | 52 | 350 | 6.6 | 2.7 |  | 9.3 | 0.23793 | 0.70968 | 36.6344 | 15.0341 | 14.2551 | 337.4661 | 11.6616 | 331.3224 | 3.2273 | 48.7727 | 0.29228 | [27 empty] | Sampling time | hh:mm | 11:30 | 11:30 | --- | --- | 11:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 23.2 | 24.2 | 23.7 | 4.2194 | 1999-01-12 | 17:00 | 8 | 25 | 50 | 51 | 350 | 7.7 | 3.3 | 11 | 0.23793 | 0.7 | 30.8182 | 17.5398 | 16.1943 | 2.5502 | 0.049904 | 2.4952 | 0.024728 | 50.4753 | 0.32084 | 1999-01-15 | 7:00 | 21 | 23.7 | 52 | 52 | 350 | 6.3 | 2.7 |  | 9 | 0.23793 | 0.7 | 37.8889 | 14.3507 | 13.769 | 327.7199 | 11.3343 | 322.0249 | 3.1354 | 48.8646 | 0.28178 | 6.13 |  |  | 11.4 |  |  | 327.5667 |  | 89.2706 | 324.7212 | 96.4893 | 0.002 |  |  | 0.17867 |  | 96.3636 | 0.17708 | 98.8705 | [8 empty] | Operation time | hh.hh | 73.5 | 73.5 | --- | --- | 73.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 98.5 | 98.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122 | 122 | --- | --- | --- | --- | --- | Cumulative time | hr | 146 | 146 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 1.935 | 1.935 | 1.935 | 1.935 | SDS-CDF, mg/L | 1.935 | 1.935 | 1.935 | 1.935 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 30(15 ave) |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 15.1 | 15.3 | 15.2 | 1.3158 | 1999-01-13 | 8:00 | 23 | 24 | 51 | 51 | 350 | 7.5 | 3.3 | 10.8 | 0.23793 | 0.69444 | 31.4074 | 17.0842 | 16.2469 | 2.5066 | 0.04908 | 2.454 | 0.024312 | 50.9757 | 0.31872 | 1999-01-15 | 9:00 | 23 | 23.9 | 52 | 52 | 350 | 6.3 | 2.7 |  | 9 | 0.23793 | 0.7 | 37.8889 | 14.3507 | 13.6878 | 327.7199 | 11.3343 | 322.0249 | 3.1354 | 48.8646 | 0.28012 | [27 empty] | pH | --- | 6.48 | 6.39 | 6.435 | 1.3986 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 6.04 | 6.87 | --- | --- | --- | --- | --- | pH | --- | 6.28 | 6.62 | --- | --- | --- | --- | --- | pH | --- | 5.61 | 6.06 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.145 | 0.14 | 0.14 | 0.18 | SDS-CDp, mg/L | 0.145 | 0.14 | 0.14 | 0.18 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 130 | 1 | 0.7 | 15 | 3.4839 | 73.8137 | 335.6684 | 6.5843 | 9.4062 | 2.8219 | Calcium (mg/L) | 6.4 |  |  |  | Turbidity | ntu | 0.1 | 0.14 | 0.12 | 33.3333 | 1999-01-13 | 10:00 | 25 | 24.4 | 51 | 52 | 350 | 7.5 | 3.3 | 10.8 | 0.23793 | 0.69444 | 31.4074 | 17.0842 | 16.0559 | 2.5066 | 0.04908 | 2.454 | 0.024312 | 51.4757 | 0.31191 | 1999-01-15 | 11:00 | 25 | 23.9 | 52 | 52 | 350 | 6.4 | 2.7 |  | 9.1 | 0.23793 | 0.7033 | 37.4615 | 14.5785 | 13.9051 | 330.9759 | 11.4437 | 325.1331 | 3.1661 | 48.8339 | 0.28474 | 6.11 | 6.55 | 6.77 | 10.8 | 106.6 | 318 | 332.5019 | -4.5603 | 89.8353 | 329.5606 | 96.7229 | 0.002 | 0.057 | 0.19 | 0.18063 | 4.9318 | 96.3636 | 0.179 | 98.8827 | [8 empty] | Temperature | oC | 22.2 | 21.9 | 22.05 | 1.3605 | 21.6 | --- | --- | --- | --- | --- | Temperature | oC | 20.8 | 20.4 | --- | --- | --- | --- | --- | Temperature | oC | 22.4 | 22.4 | --- | --- | --- | --- | --- | Temperature | oC | 21.2 | 21.6 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.2 | 3.2 | 3.2 | 3.2 | TOCF, mg/L | 3.2 | 3.2 | 3.2 | 3.2 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.231 | 2 | 0.9 | 15 | 10.4092 | 80.7391 | 335.6684 | 6.5843 | 7.3159 | 0.73159 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-01-13 | 12:00 | 27 | 24.3 | 51 | 52 | 350 | 7.6 | 3.3 | 10.9 | 0.23793 | 0.69725 | 31.1101 | 17.312 | 16.3182 | 2.5284 | 0.049492 | 2.4746 | 0.02452 | 51.4755 | 0.31701 | 1999-01-15 | 13:00 | 27 | 24.4 | 52 | 52 | 350 | 6.3 | 2.7 |  | 9 | 0.23793 | 0.7 | 37.8889 | 14.3507 | 13.487 | 327.7199 | 11.3343 | 322.0249 | 3.1354 | 48.8646 | 0.27601 | [27 empty] | Alkalinity | mg/L as CaCO3 | 1 | 1 | 1 | 0 | 5 | 5.1667 | -3.3333 | 55.5556 | 5.1317 | 80.5132 | Alkalinity | mg/L as CaCO3 | BMRL | 14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | BMRL | 3.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 0.5 | 3 | 3 | 0 | 77.7778 | 2.9802 | 83.2225 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 2.0988 | 72.4287 | 335.6684 | 6.5843 | 13.1686 | 6.5843 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.2 | 3.2 | 3.2 | 0 | 1999-01-13 | 15:00 | 30 | 24.9 | 51 | 52 | 350 | 7.6 | 3.3 | 10.9 | 0.23793 | 0.69725 | 31.1101 | 17.312 | 16.0313 | 2.5284 | 0.049492 | 2.4746 | 0.02452 | 51.4755 | 0.31144 | 1999-01-15 | 15:00 | 29 | 24.3 | 52 | 52 | 350 | 6.5 | 2.8 |  | 9.3 | 0.23793 | 0.69892 | 36.6344 | 14.8063 | 13.9563 | 326.6875 | 11.2923 | 320.8302 | 3.1247 | 48.8753 | 0.28555 | [27 empty] | Total dissolved solids | mg/L | 10.7 | 10.8 | 10.75 | 0.93023 | 320 | 329.0833 | -2.8385 | 89.8824 | 326.4093 | 96.7066 | Total dissolved solids | mg/L | 20.7 | 744 | 876.2 | -17.7688 | 80.5176 | 869.6004 | 97.6196 | Total dissolved solids | mg/L | 6.2 | 200 | 206.3 | -3.15 | 94.1647 | 204.6849 | 96.971 | Total dissolved solids | mg/L | 7.1 | 142.7 | 148.7429 | -4.2347 | 93.3176 | 147.6198 | 95.1903 | UV254 F, cm-1 | 0.055 | 0.055 | 0.055 | 0.055 | UV254 F, cm-1 | 0.055 | 0.055 | 0.055 | 0.055 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 1.5052 | 71.8351 | 335.6684 | 6.5843 | 21.9477 | 15.3634 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.055 | 0.055 | 0.055 | 0 | 1999-01-13 | 17:00 | 32 | 24.6 | 51 | 52 | 350 | 7.6 | 3.3 | 10.9 | 0.23793 | 0.69725 | 31.1101 | 17.312 | 16.1741 | 2.5284 | 0.049492 | 2.4746 | 0.02452 | 51.4755 | 0.31421 | 1999-01-15 | 17:00 | 31 | 24.4 | 52 | 52 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.7011 | 323.5379 | 11.1866 | 317.8263 | 3.095 | 48.905 | 0.28016 | 6.05 |  |  | 10.9 |  |  | 324.1929 |  | 89.7412 | 321.3285 | 96.6078 | 0.002 |  |  | 0.17614 |  | 96.3636 | 0.17455 | 98.8542 | [8 empty] | Total hardness | mg/L as CaCO3 | 0.1 | BMRL | 0.1 | #VALUE! | 85.6 | 78.7667 | 7.9829 | 99.5781 | 78.1059 | 99.872 | Total hardness | mg/L as CaCO3 | 0.7 | 237.8 | 230.7 | 2.9857 | 97.0464 | 228.9257 | 99.6942 | Total hardness | mg/L as CaCO3 | BMRL | 48.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | BMRL | 32.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 p, cm-1 | 0.001 | 0.003 | 0.001 | 0 | UV254 p, cm-1 | 0.001 | 0.003 | 0.001 | 0 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.15 |  |  |  | SUVA | L/(mg*m) | 1.7188 | 1.7188 | 1.7188 | 0 | 1999-01-14 | 8:00 | 47 | 22.6 | 51 | 52 | 350 | 7.1 | 3.1 | 10.2 | 0.23793 | 0.69608 | 33.3137 | 16.173 | 16.0302 | 2.5192 | 0.049381 | 2.4691 | 0.024447 | 51.4756 | 0.31141 | 1999-01-16 | 7:00 | 45 | 24.8 | 52 | 52 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.54 | 323.5379 | 11.1866 | 317.8263 | 3.095 | 48.905 | 0.27686 | 6.1 |  |  | 14 |  |  | 317.1071 |  | 86.8235 | 314.3359 | 95.5462 | 0.002 |  |  | 0.17614 |  | 96.3636 | 0.17455 | 98.8542 | [8 empty] | Calcium hardness | mg/L as CaCO3 | BMRL | BMRL | #DIV/0! | #VALUE! | 55.4 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calcium hardness | mg/L as CaCO3 | 0.4 | 153.6 | 148.4 | 3.3854 | 97.3684 | 147.2583 | 99.7284 | Calcium hardness | mg/L as CaCO3 | BMRL | 30.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | BMRL | 21.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | BromideF, ug/L | 53 | 53 | 53 | 53 | BromideF, ug/L | 53 | 53 | 53 | 53 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 52 | 54 | 53 | 3.7736 | 1999-01-14 | 10:00 | 49 | 23.2 | 51 | 52 | 350 | 7.2 | 3.2 | 10.4 | 0.23793 | 0.69231 | 32.6538 | 16.4008 | 15.9703 | 2.4902 | 0.0488 | 2.44 | 0.024163 | 51.4758 | 0.31025 | 1999-01-16 | 9:00 | 47 | 24.8 | 52 | 52 | 350 | 6.5 | 2.8 |  | 9.3 | 0.23793 | 0.69892 | 36.6344 | 14.8063 | 13.7516 | 326.6875 | 11.2923 | 320.8302 | 3.1247 | 48.8753 | 0.28136 | [27 empty] | Turbidity | ntu | 0.06 | 0.08 | 0.07 | 28.5714 | 0.13 | 0.23667 | -82.0513 | 41.6667 | 0.23527 | 70.2465 | Turbidity | ntu | 0.06 | 0.17 | 0.66 | -288.2353 | 50 | 0.65537 | 90.8449 | Turbidity | ntu | 0.08 | 0.13 | 0.16 | -23.0769 | 33.3333 | 0.15935 | 49.7974 | Turbidity | ntu | 0.1 | 0.12 | 0.12857 | -7.1429 | 16.6667 | 0.12834 | 22.0849 | Bromidep, ug/L | #DIV/0! | 31 | BMRL | BMRL | Bromidep, ug/L | #DIV/0! | 31 | BMRL | BMRL | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 18.8 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4.5 | 3.8 | 4.15 | 16.8675 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 11:00 | 49 | 24.8 | 52 | 52 | 350 | 6.4 | 2.7 |  | 9.1 | 0.23793 | 0.7033 | 37.4615 | 14.5785 | 13.54 | 330.9759 | 11.4437 | 325.1331 | 3.1661 | 48.8339 | 0.27727 | 6.09 | 6.6 | 6.77 | 14.2 | 107.7 | 303 | 324.4426 | -7.0768 | 86.6353 | 321.6061 | 95.5847 | 0.002 | 0.056 | 0.184 | 0.18063 | 1.8317 | 96.3636 | 0.179 | 98.8827 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25 | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.6 | [9 empty] | Total Hardness (mg/L as CaCO3) | 25.4 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 2.5 | 1.93 | 2.215 | 25.7336 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 13:00 | 51 | 24.8 | 52 | 52 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.54 | 323.5379 | 11.1866 | 317.8263 | 3.095 | 48.905 | 0.27686 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 15.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 1 | BMRL | BMRL | 0.5 | Alkp, mg/L CaCO3 | 1 | BMRL | BMRL | 0.5
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0026 | [9 empty] | pH | 5.36 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 2 | 1.87 | 1.935 | 6.7183 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 15:00 | 53 | 24.8 | 52 | 52 | 350 | 6.4 | 2.8 |  | 9.2 | 0.23793 | 0.69565 | 37.0435 | 14.5785 | 13.54 | 323.5379 | 11.1866 | 317.8263 | 3.095 | 48.905 | 0.27686 | [27 empty] | UV254 | cm-1 | 0.001 | 0.001 | 0.001 | 0 | 0.19 | 0.181 | 4.7368 | 98.1818 | 0.17949 | 99.4429 | UV254 | cm-1 | 0.003 | 0.524 | 0.523 | 0.19084 | 94.5455 | 0.51899 | 99.422 | UV254 | cm-1 | 0.001 | 0.109 | 0.109 | 0 | 98.1818 | 0.10813 | 99.0752 | UV254 | cm-1 | 0 | 0.079 | 0.078571 | 0.5425 | 100 | 0.077948 | 100 | T-HdF, mg/L CaCO3 | 23.7 | 23.7 | 23.7 | 23.7 | T-HdF, mg/L CaCO3 | 23.7 | 23.7 | 23.7 | 23.7
Treatment Plant Category | CONV | [11 empty] | Ammonia (mg/L) | BMRL | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 11.6 | 11.6 | 11.6 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 17:00 | 55 | 23.9 | 52 | 52 | 350 | 6.3 | 2.8 |  | 9.1 | 0.23793 | 0.69231 | 37.4615 | 14.3507 | 13.6878 | 320.3813 | 11.0805 | 314.8139 | 3.0652 | 48.9348 | 0.27972 | 6.05 |  |  | 14.2 |  |  | 313.3625 |  | 86.6353 | 310.67 | 95.4292 | 0.002 |  |  | 0.17425 |  | 96.3636 | 0.1727 | 98.8419 | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.7273 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.3806 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.7581 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.7174 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 0.1 | 0.7 | BMRL | BMRL | T-Hdp, mg/L CaCO3 | 0.1 | 0.7 | BMRL | BMRL
Process Train Name | Conventional Train | Additional Information | [10 empty] | TOC (mg/L) | 3.1 |  |  |  | SDS-Chlorination pH | --- | 8.11 | 8.06 | 8.085 | 0.61843 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 7:00 | 69 | 21.5 | 52 | 52 | 350 | 5.9 | 2.8 |  | 8.7 | 0.23793 | 0.67816 | 39.2299 | 13.4396 | 13.7611 | 307.6857 | 10.6534 | 302.6786 | 2.9453 | 49.0547 | 0.28053 | 6.28 |  |  | 8.3 |  |  | 312.6446 |  | 92.1882 | 310.0795 | 97.3233 | 0.001 |  |  | 0.16879 |  | 98.1818 | 0.16737 | 99.4025 | [8 empty] | Bromide | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromide | mg/L | 31 | --- | 251 | --- | 41.5094 | 249.3029 | 87.5653 | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Bromide | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-HdF, mg/L CaCO3 | 15.2 | 15.2 | 15.2 | 15.2 | Ca-HdF, mg/L CaCO3 | 15.2 | 15.2 | 15.2 | 15.2
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | UV254 (cm-1) | 0.055 |  |  |  | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 9:00 | 71 | 21.7 | 52 | 52 | 350 | 5.9 | 2.4 |  | 8.3 | 0.23793 | 0.71084 | 41.1687 | 13.4396 | 13.68 | 338.6248 | 11.7247 | 333.1142 | 3.2414 | 48.7586 | 0.28057 | [27 empty] | SDS-Cl2 dose | mg/L | 2 | 2 | 2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | #DIV/0! | 0.4 | BMRL | BMRL | Ca-Hdp, mg/L CaCO3 | #DIV/0! | 0.4 | BMRL | BMRL
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | 6.7 | [9 empty] | Bromide (ug/L) | 51 |  |  |  | SDS-TOX | mg Cl- /L | 185 | 160 | 172.5 | 14.4928 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 11:00 | 73 | 21.7 | 53 | 53 | 350 | 5.9 | 2.5 |  | 8.4 | 0.23793 | 0.70238 | 40.6667 | 13.4396 | 13.68 | 330.032 | 11.4271 | 324.6612 | 3.1592 | 49.8408 | 0.27447 | 6.08 | 6.5 | 6.82 | 8.4 | 105.5 | 323 | 337.176 | -4.3889 | 92.0941 | 334.4049 | 97.4881 | 0.001 | 0.055 | 0.187 | 0.18244 | 2.4385 | 98.1818 | 0.18091 | 99.4472 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.85 | 1.86 | 1.855 | 0.53908 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.86 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.86 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.82 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 34.08 | 29.3 | 31.69 | 15.0836 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 13:00 | 75 | 22.4 | 53 | 53 | 350 | 5.9 | 2.4 |  | 8.3 | 0.23793 | 0.71084 | 41.1687 | 13.4396 | 13.3999 | 338.6248 | 11.7247 | 333.1142 | 3.2414 | 49.7586 | 0.2693 | [27 empty] | SDS-Cl2 demand | mg/L | 0.15 | 0.14 | 0.145 | 6.8966 | --- | 6.1117 | --- | 92.5065 | 6.0615 | 97.6079 | SDS-Cl2 demand | mg/L | 0.14 | --- | 18.09 | --- | 92.7649 | 17.9515 | 99.2201 | SDS-Cl2 demand | mg/L | 0.14 | --- | 3.73 | --- | 92.7649 | 3.701 | 96.2173 | SDS-Cl2 demand | mg/L | 0.18 | --- | 2.6871 | --- | 90.6977 | 2.6673 | 93.2515 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 12 | 13.34 | 12.67 | 10.5762 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 15:00 | 77 | 22.1 | 53 | 54 | 350 | 5.9 | 2.5 |  | 8.4 | 0.23793 | 0.70238 | 40.6667 | 13.4396 | 13.5192 | 330.032 | 11.4271 | 324.6612 | 3.1592 | 50.3408 | 0.26855 | 5.88 |  |  | 8.4 |  |  | 337.176 |  | 92.0941 | 334.4049 | 97.4881 | 0.001 |  |  | 0.18244 |  | 98.1818 | 0.18091 | 99.4472 | [8 empty] | SDS-Chlorination temp. | oC | 11.6 | 11.6 | 11.6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 11.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 11.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 11.6 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | -50.8485 | -52.0927 | -50.8485 | -50.8485 | Qp/QT (THM4), % | 24.5757 | 25.1771 | 24.5757 | 24.5757
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 2000 ppm | [14 empty] | SDS-DBCM | mg/L | 3 | 3.74 | 3.37 | 21.9585 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 16:00 | 78 | 22.2 | 53 | 54 | 350 | 5.8 | 2.5 |  | 8.3 | 0.23793 | 0.6988 | 41.1687 | 13.2118 | 13.2509 | 326.5143 | 11.3085 | 321.2909 | 3.1259 | 50.3741 | 0.26305 | [27 empty] | SDS-Chlorination pH | --- | 8.04 | 8.09 | 8.065 | 0.61996 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.08 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.02 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.06 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | NaCl | [14 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 8:00 | 94 | 22 | 54 | 54 | 350 | 5.7 | 0.77 |  | 6.47 | 0.23793 | 0.88099 | 53.0958 | 12.984 | 13.0996 | 710.5522 | 24.6162 | 699.3813 | 6.8035 | 47.1965 | 0.27756 | [27 empty] | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 23.6908 | 23.5019 | 23.6908 | 23.6908
|  | Variability of rejection of reference solute (%) | 3 | [14 empty] | SDS-THM4 | mg/L | 49.08 | 46.38 | 47.73 | 5.6568 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 9:00 | 95 | 21.9 | 54 | 54 | 350 | 5.6 | 0.6 |  | 6.2 | 0.23793 | 0.90323 | 55.4516 | 12.7562 | 12.9079 | 829.5979 | 28.7484 | 816.7843 | 7.9444 | 46.0556 | 0.28027 | 5.75 |  |  | 16.1 |  |  | 947.65 |  | 84.8471 | 940.1976 | 98.2876 | 0.001 |  |  | 0.559 |  | 98.1818 | 0.55454 | 99.8197 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 15 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 10:00 | 96 | 22.1 | 54 | 54 | 350 | 5.5 | 0.6 |  | 6.1 | 0.23793 | 0.90164 | 56.377 | 12.5284 | 12.6027 | 819.7396 | 28.4148 | 807.3044 | 7.8511 | 46.1489 | 0.27309 | 5.71 |  |  | 18 |  |  | 915.2083 |  | 83.0588 | 908.1588 | 98.018 | 0.002 |  |  | 0.54083 |  | 96.3636 | 0.5366 | 99.6273 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.4951 | 1.4831 | 1.4939 | 1.5037
|  | Standard testing pH | 7 | [14 empty] | SDS-DCAA* | mg/L | 15.72 | 17.55 | 16.635 | 11.0009 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 11:00 | 97 | 22 | 54 | 54 | 350 | 5.5 | 0.6 |  | 6.1 | 0.23793 | 0.90164 | 56.377 | 12.5284 | 12.64 | 819.7396 | 28.4148 | 807.3044 | 7.8511 | 46.1489 | 0.2739 | 5.79 |  |  | 19.1 |  |  | 905.125 |  | 82.0235 | 898.1634 | 97.8734 | 0.002 |  |  | 0.54083 |  | 96.3636 | 0.5366 | 99.6273 | [8 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | < 600 PSI | [14 empty] | SDS-TCAA* | mg/L | 12.28 | 14.72 | 13.5 | 18.0741 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 12:00 | 98 | 22.1 | 53 | 54 | 350 | 5.4 | 0.6 |  | 6 | 0.23793 | 0.9 | 57.3333 | 12.3006 | 12.3735 | 809.7978 | 28.078 | 797.7369 | 7.7569 | 45.7431 | 0.2705 | 5.88 | 6.02 | 6.69 | 19.7 | 105.6 | 631 | 885.2 | -40.2853 | 81.4588 | 878.5233 | 97.7576 | 0.003 | 0.056 | 0.429 | 0.523 | -21.9114 | 94.5455 | 0.51899 | 99.422 | [8 empty] | SDS-DBCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBCM | mg/L | 1.14 | --- | 23.44 | --- | 66.1721 | 23.268 | 95.1006 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.041729 | 0.041908 | 0.041729 | 0.041483
|  | Acceptable range of operating pH values | pH 2-11 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 16:00 | 102 | 21.9 | 54 | 54 | 350 | 5.4 | 0.57 |  | 5.97 | 0.23793 | 0.90452 | 57.6265 | 12.3006 | 12.4469 | 837.6708 | 29.0445 | 825.1949 | 8.0239 | 45.9761 | 0.27073 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | #DIV/0! | 47.461 | #VALUE! | #VALUE!
|  | Typical pressure drop across a single element (psi) | 6 | [14 empty] | SDS-DBAA* | mg/L | 1.13 | 1.42 | 1.275 | 22.7451 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 8:00 | 118 | 21.4 | 54 | 54 | 350 | 5.4 | 5.5 |  | 10.9 | 0.23793 | 0.49541 | 31.1101 | 12.3006 | 12.6322 | 203.6359 | 7.0606 | 200.603 | 1.9506 | 52.0494 | 0.2427 | [27 empty] | SDS-THM4 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 159.1 | --- | 100 | 157.7636 | 100 | SDS-THM4 | mg/L | 1.14 | --- | 467.04 | --- | 97.6116 | 463.4459 | 99.754 | SDS-THM4 | mg/L | 0 | --- | 95.46 | --- | 100 | 94.6895 | 100 | SDS-THM4 | mg/L | 0 | --- | 68.1857 | --- | 100 | 67.6451 | 100 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 1.9428 | #VALUE! | #VALUE! | 1.8199
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 4.86 | 6.26 | 5.56 | 25.1799 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 9:00 | 119 | 21.3 | 54 | 54 | 350 | 5.6 | 5.5 |  | 11.1 | 0.23793 | 0.5045 | 30.5315 | 12.7562 | 13.1389 | 207.1238 | 7.1776 | 203.9246 | 1.9835 | 52.0165 | 0.25259 | 5.83 |  |  | 5.2 |  |  | 209.1373 |  | 95.1059 | 207.5058 | 97.494 | 0.001 |  |  | 0.10998 |  | 98.1818 | 0.10911 | 99.0835 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 17.9001 | 17.9093 | #VALUE! | #VALUE!
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 10:00 | 120 | 21.2 | 54 | 54 | 350 | 5.6 | 5.5 |  | 11.1 | 0.23793 | 0.5045 | 30.5315 | 12.7562 | 13.1778 | 207.1238 | 7.1776 | 203.9246 | 1.9835 | 52.0165 | 0.25334 | 5.88 |  |  | 5.2 |  |  | 209.1373 |  | 95.1059 | 207.5058 | 97.494 | 0.001 |  |  | 0.10998 |  | 98.1818 | 0.10911 | 99.0835 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | #DIV/0! | 11.4738 | #VALUE! | #VALUE!
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm/hours | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 11:00 | 121 | 21.1 | 54 | 54 | 350 | 5.7 | 5.6 |  | 11.3 | 0.23793 | 0.50442 | 29.9735 | 12.984 | 13.4528 | 207.0947 | 7.1745 | 203.8388 | 1.9829 | 52.0171 | 0.25862 | 5.79 |  |  | 5 |  |  | 209.308 |  | 95.2941 | 207.6444 | 97.592 | 0.001 |  |  | 0.10996 |  | 98.1818 | 0.10908 | 99.0832 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 12:00 | 122 | 21.6 | 54 | 54 | 350 | 5.7 | 5.6 |  | 11.3 | 0.23793 | 0.50442 | 29.9735 | 12.984 | 13.2554 | 207.0947 | 7.1745 | 203.8388 | 1.9829 | 52.0171 | 0.25483 | 5.86 | 6.46 | 6.49 | 5.1 | 106.7 | 203 | 209.2063 | -3.0573 | 95.2 | 207.5442 | 97.5427 | 0.001 | 0.056 | 0.111 | 0.10996 | 0.93308 | 98.1818 | 0.10908 | 99.0832 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 29.13 | 33.69 | 31.41 | 14.5177 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 16:00 | 126 | 21.9 | 53 | 53 | 350 | 5.7 | 5.8 |  | 11.5 | 0.23793 | 0.49565 | 29.4348 | 12.984 | 13.1384 | 203.7318 | 7.058 | 200.5288 | 1.9507 | 51.0493 | 0.25737 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 33.99 | 39.95 | 36.97 | 16.1212 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 8:00 | 142 | 21.6 | 52 | 52 | 350 | 5.7 | 13.2 |  | 18.9 | 0.23793 | 0.30159 | 17.5185 | 12.984 | 13.2554 | 149.8884 | 5.1927 | 147.5319 | 1.4352 | 50.5648 | 0.26215 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -71.9198 | -71.9198 | -71.9198 | -71.9198 | Qp/QT (HAA5), % | 14.0401 | 14.0401 | 14.0401 | 14.0401
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 9:00 | 143 | 21 | 52 | 52 | 350 | 5.6 | 13 |  | 18.6 | 0.23793 | 0.30108 | 17.8172 | 12.7562 | 13.2559 | 149.7833 | 5.1905 | 147.4698 | 1.4344 | 50.5656 | 0.26215 | 5.49 |  |  | 8.6 |  |  | 148.3146 |  | 91.9059 | 147.1969 | 94.1575 | 0.002 |  |  | 0.077831 |  | 96.3636 | 0.077224 | 97.4101 | [8 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 41.0287 | 41.1887 | 41.0287 | 41.0287
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 10:00 | 144 | 21 | 52 | 52 | 350 | 5.5 | 13 |  | 18.5 | 0.23793 | 0.2973 | 17.9189 | 12.5284 | 13.0192 | 149.0166 | 5.1654 | 146.756 | 1.4272 | 50.5728 | 0.25743 | 5.37 |  |  | 8.2 |  |  | 147.7327 |  | 92.2824 | 146.6364 | 94.4079 | 0.001 |  |  | 0.077846 |  | 98.1818 | 0.077242 | 98.7054 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 11:00 | 145 | 21.4 | 52 | 52 | 340 | 5.5 | 13 |  | 18.5 | 0.23113 | 0.2973 | 17.3784 | 12.5284 | 12.8662 | 149.0175 | 5.1631 | 146.6905 | 1.4269 | 50.5731 | 0.25441 | 5.48 |  |  | 7.8 |  |  | 147.9019 |  | 92.6588 | 146.7687 | 94.6855 | 0.002 |  |  | 0.077423 |  | 96.3636 | 0.076813 | 97.3963 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1999-01-20 | 12:00 | 146 | 21 | 52 | 52 | 350 | 5.5 | 13 |  | 18.5 | 0.23793 | 0.2973 | 17.9189 | 12.5284 | 13.0192 | 149.0166 | 5.1654 | 146.756 | 1.4272 | 50.5728 | 0.25743 | 5.64 | 5.82 | 6.07 | 7.6 | 107.3 | 142 | 147.9865 | -4.2159 | 92.8471 | 146.8835 | 94.8258 | 0.002 | 0.057 | 0.081 | 0.077423 | 4.416 | 96.3636 | 0.07683 | 97.3969 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 104.7 | --- | 100 | 103.8205 | 100 | SDS-HAA5 | mg/L | 0 | --- | 314.1 | --- | 100 | 311.6769 | 100 | SDS-HAA5 | mg/L | 0 | --- | 62.82 | --- | 100 | 62.313 | 100 | SDS-HAA5 | mg/L | 0 | --- | 44.8714 | --- | 100 | 44.5157 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.6837 | 1.683 | 1.683 | 1.6886
[45 empty] | 1999-01-20 | 17:30 | 151.5 | 22.2 | 52 | 52 | 350 | 5.9 | 13.4 |  | 19.3 | 0.23793 | 0.3057 | 17.1347 | 13.4396 | 13.4793 | 150.7338 | 5.2191 | 148.2808 | 1.4429 | 50.5571 | 0.26662 | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 123.2333 | --- | 100 | 122.1982 | 100 | SDS-HAA6 | mg/L | 0 | --- | 369.7 | --- | 100 | 366.848 | 100 | SDS-HAA6 | mg/L | 0 | --- | 73.94 | --- | 100 | 73.3432 | 100 | SDS-HAA6 | mg/L | 0 | --- | 52.8143 | --- | 100 | 52.3955 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1999-01-20 | 22:00 | 156 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.047418 | 0.047699 | 0.047418 | 0.047278
[45 empty] | 1999-01-22 | 8:00 | 176 | 22.8 | 52 | 52 | 350 | 5.9 | 13.8 | X | 19.7 | 0.23793 | 0.29949 | 16.7665 | 13.4396 | 13.2424 | 149.4632 | 5.1751 | 147.0309 | 1.4307 | 50.5693 | 0.26187 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | #DIV/0! | 49.9112 | #VALUE! | #VALUE!
[45 empty] | 1999-01-22 | 10:00 | 178 | 22.6 | 52 | 52 | 350 | 5.9 | 13.8 |  | 19.7 | 0.23793 | 0.29949 | 16.7665 | 13.4396 | 13.3209 | 149.4632 | 5.1751 | 147.0309 | 1.4307 | 50.5693 | 0.26342 | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 2.0745 | #VALUE! | #VALUE! | 2.0043
[45 empty] | 1999-01-22 | 12:00 | 180 | 21.9 | 52 | 52 | 350 | 5.9 | 13.8 |  | 19.7 | 0.23793 | 0.29949 | 16.7665 | 13.4396 | 13.5994 | 149.4632 | 5.1751 | 147.0309 | 1.4307 | 50.5693 | 0.26893 | 5.4 | 5.93 | 6.09 | 5.6 | 105.8 | 143.8 | 149.2815 | -3.8119 | 94.7294 | 148.0705 | 96.218 | 0.001 | 0.057 | 0.08 | 0.078087 | 2.3913 | 98.1818 | 0.077437 | 98.7086 | [47 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 20.3865 | 20.4708 | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | #DIV/0! | 13.1221 | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on R8: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R9: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R10: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R11: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R12: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R13: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R14: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R16: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R17: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on R18: C. Hill (8/30/99): This foulant was actually measured during the 3rd quarter. It was inserted for this quarter by the reviewer.
Note on U6: C. Hill (8/30/99): Reviewer added chemical formula and dose. This information was copied from the pretreatment data for the NF200 membrane used during this study. All other pre-treatment information for these two membranes was identical, so it was assumed the alum formula and dose were also identical.
Note on CY29: C. Hill (8/30/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when SDS temperatures were apparently lower than the previous year).
Note on DL29: C. Hill (8/30/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when SDS temperatures were apparently lower than the previous year).
Note on DV29: C. Hill (8/30/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when SDS temperatures were apparently lower than the previous year).
Note on EF29: C. Hill (8/30/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when SDS temperatures were apparently lower than the previous year).

## NF200. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 1.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 850 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.8024 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 19.3 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1998-04-09 | 1998-04-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.5 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.83 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.4 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -4.96 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 6:30 | 14:15 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 580 | [10 empty] | Influent flow rate during sample collection (mL/min) | 590 | [7 empty] | Influent flow rate during sample collection (mL/min) | 580 | [7 empty] | Influent flow rate during sample collection (mL/min) | 590 | [6 empty] | SDS-THM4F, ug/L | 71.08 | 71.08 | 71.08 | 71.08 | SDS-THM4F, ug/L | 71.08 | 71.08 | 71.08 | 71.08 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 112 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 0 | 174.75 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 6.015 | 11.09 | 3.14 | 2.41 | SDS-THM4p, ug/L | 6.015 | 11.09 | 3.14 | 2.41 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.96 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.97 | 6.29 | 6.13 | 5.2202 | 1998-04-07 | 10:15 | 0 | 23.8 | 50 | 50 | 600 | 7.1 | 47 | 54.1 | 0.46109 | 0.13124 | 10.0906 | 16.173 | 15.4716 | 972.5941 | 38.4616 | 961.5402 | 9.2861 | 40.7139 | 0.38001 | 1998-04-09 | 7:00 | 0 | 22.1 | 55 | 56 | 590 | 8 | 2.1 |  | 10.1 | 0.4534 | 0.79208 | 57.4158 | 18.2231 | 18.3312 | 308.0803 | 60.2133 | 304.7193 | 2.4619 | 53.0381 | 0.34562 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 41.17 | 41.17 | 41.17 | 41.17 | SDS-HAA5F, ug/L | 41.17 | 41.17 | 41.17 | 41.17 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21697 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | 20 | 21 | 20.5 | 4.878 | 1998-04-07 | 11:00 | 0.75 | 23.8 | 48 | 49 | 600 | 6.9 | 40.9 | 47.8 | 0.46109 | 0.14435 | 11.5523 | 15.7174 | 15.0358 | 986.8129 | 39.0365 | 975.9135 | 9.4233 | 39.0767 | 0.38478 | 1998-04-09 | 9:00 | 2 | 23.1 | 42 | 42 | 580 | 7.1 | 3.2 |  | 10.3 | 0.44572 | 0.68932 | 55.3107 | 16.173 | 15.7951 | 250.8137 | 49.0734 | 248.3441 | 2.0051 | 39.9949 | 0.39493 | 6.45 | 6.07 | 6.52 | 56.9 | 108.4 | 291 | 233.4484 | 19.7772 | 49.0828 | 232.3678 | 75.513 | 0.007 | 0.065 | 0.18 | 0.213 | -18.3333 | 90.1408 | 0.21174 | 96.694 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 1.28 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 1.28 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 2 | 2.5 | 2.25 | 22.2222 | 1998-04-07 | 12:00 | 1.75 | 22.6 | 48 | 49 | 600 | 6.9 | 40.9 | 47.8 | 0.46109 | 0.14435 | 11.5523 | 15.7174 | 15.5787 | 986.8129 | 39.0365 | 975.9135 | 9.4233 | 39.0767 | 0.39867 | 1998-04-09 | 11:00 | 5 | 22.1 | 42 | 43 | 580 | 7.2 | 3.1 |  | 10.3 | 0.44572 | 0.69903 | 55.3107 | 16.4008 | 16.4981 | 255.2993 | 49.944 | 252.7501 | 2.0408 | 40.4592 | 0.40777 | [27 empty] | Sampling date | MM/DD/YY | 1998-04-12 | 1998-04-12 | --- | --- | 1998-04-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-13 | 1998-04-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-14 | 1998-04-14 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-04-15 | 1998-04-15 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 417.5 | 417.5 | 417.5 | 417.5 | SDS-TOXF, ug Cl- /L | 417.5 | 417.5 | 417.5 | 417.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 112.4 | 111.1 | 111.75 | 1.1633 | 1998-04-07 | 13:40 | 3.41 | 23.2 | 48 | 49 | 600 | 7 | 40.6 | 47.6 | 0.46109 | 0.14706 | 11.605 | 15.9452 | 15.5266 | 989.802 | 39.1484 | 978.711 | 9.4511 | 39.0489 | 0.39762 | 1998-04-09 | 13:00 | 7 | 23 | 44 | 44 | 580 | 7.4 | 3.3 |  | 10.7 | 0.44572 | 0.69159 | 53.2056 | 16.8564 | 16.5112 | 251.8774 | 49.2608 | 249.2922 | 2.0132 | 41.9868 | 0.39325 | 6.45 |  |  | 52.9 |  |  | 243.7167 |  | 52.6622 | 242.4994 | 78.1855 | 0.0045 |  |  | 0.22012 |  | 93.662 | 0.21875 | 97.9428 | [8 empty] | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 27.2 | 23.6 | 25.4 | 14.1732 | 1998-04-07 | 16:00 | 6.41 | 23.7 | 48 | 49 | 590 | 6.9 | 40.5 | 47.4 | 0.4534 | 0.14557 | 11.4473 | 15.7174 | 15.0803 | 988.1564 | 39.0823 | 977.057 | 9.4352 | 39.0648 | 0.38603 | 1998-04-09 | 15:00 | 9 | 22.5 | 42 | 43 | 580 | 7.2 | 3.1 |  | 10.3 | 0.44572 | 0.69903 | 55.3107 | 16.4008 | 16.3041 | 255.2993 | 49.944 | 252.7501 | 2.0408 | 40.4592 | 0.40298 | 6.41 |  |  | 49.8 |  |  | 255.6339 |  | 55.4362 | 254.3563 | 80.4212 | 0.003 |  |  | 0.22894 |  | 95.7746 | 0.22753 | 98.6815 | [8 empty] | Operation time | hh.hh | 82 | 82 | --- | --- | 82 | --- | --- | --- | --- | --- | Operation time | hh.hh | 106.5 | 106.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 131 | 131 | --- | --- | --- | --- | --- | Cumulative time | hr | 153 | 153 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 1.589 | 1.589 | 1.589 | 1.589 | SDS-CDF, mg/L | 1.589 | 1.589 | 1.589 | 1.589 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 14.5 | 11 | 12.75 | 27.451 | 1998-04-08 | 7:00 | 21.41 | 23.3 | 49 | 50 | 590 | 7 | 41 | 48 | 0.4534 | 0.14583 | 11.2917 | 15.9452 | 15.4808 | 988.4485 | 39.0874 | 977.1849 | 9.4373 | 40.0627 | 0.38641 | 1998-04-09 | 17:00 | 11 | 22.5 | 43 | 44 | 580 | 7.3 | 3.2 |  | 10.5 | 0.44572 | 0.69524 | 54.2381 | 16.6286 | 16.5306 | 253.544 | 49.5937 | 250.9771 | 2.0267 | 41.4733 | 0.39858 | [27 empty] | pH | --- | 6.55 | 6.52 | 6.535 | 0.45907 | 6.45 | --- | --- | --- | --- | --- | pH | --- | 6.62 | 6.63 | --- | --- | --- | --- | --- | pH | --- | 6.04 | 6.4 | --- | --- | --- | --- | --- | pH | --- | 6.11 | 5.89 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.2375 | 0.46 | 0.131 | 0.288 | SDS-CDp, mg/L | 0.2375 | 0.46 | 0.131 | 0.288 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 16.5 | 3.6288 | 79.6748 | 606.4586 | 7.2428 | 10.3468 | 3.104 | Calcium (mg/L) | 5.6 |  |  |  | Turbidity | ntu | 0.23 | 0.45 | 0.34 | 64.7059 | 1998-04-08 | 10:00 | 24.41 | 23.4 | 49 | 50 | 590 | 7 | 41 | 48 | 0.4534 | 0.14583 | 11.2917 | 15.9452 | 15.4351 | 988.4485 | 39.0874 | 977.1849 | 9.4373 | 40.0627 | 0.38527 | 1998-04-10 | 7:00 | 24 | 24 | 31 | 31 | 580 | 4.9 | 2.3 |  | 7.2 | 0.44572 | 0.68056 | 79.5556 | 11.1617 | 10.6147 | 246.6829 | 48.4142 | 245.0078 | 1.9743 | 29.0257 | 0.3657 | 6.45 | 6.47 | 6.51 | 48.5 | 109.1 | 192.4 | 246.5 | -28.1185 | 56.5996 | 245.6636 | 80.2576 | 0.005 | 0.066 | 0.202 | 0.21161 | -4.7568 | 92.9577 | 0.21074 | 97.6274 | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | Temperature | oC | 21 | 21 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.75 | 3.75 | 3.75 | 3.75 | TOCF, mg/L | 3.75 | 3.75 | 3.75 | 3.75 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 16.5 | 10.7968 | 86.8428 | 606.4586 | 7.2428 | 8.0475 | 0.80475 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-04-08 | 12:00 | 26.41 | 23.5 | 49 | 50 | 590 | 6.9 | 40.5 | 47.4 | 0.4534 | 0.14557 | 11.4473 | 15.7174 | 15.1697 | 988.1564 | 39.0823 | 977.057 | 9.4352 | 40.0648 | 0.37863 | 1998-04-10 | 9:00 | 26 | 23.5 | 33 | 33 | 580 | 5.3 | 2.6 |  | 7.9 | 0.44572 | 0.67089 | 72.4177 | 12.0728 | 11.6521 | 242.561 | 47.5786 | 240.7792 | 1.9409 | 31.0591 | 0.37516 | [27 empty] | Alkalinity | mg/L as CaCO3 | 1.5 | 1 | 1.25 | 40 | 3 | 4.4758 | -49.1935 | 44.4444 | 4.4576 | 71.9579 | Alkalinity | mg/L as CaCO3 | 1.5 | 5 | 8.3182 | -66.3636 | 33.3333 | 8.2831 | 81.8907 | Alkalinity | mg/L as CaCO3 | 0.5 | 2.5 | 4 | -60 | 77.7778 | 3.9825 | 87.4451 | Alkalinity | mg/L as CaCO3 | 1.5 | 2 | 2.5714 | -28.5714 | 33.3333 | 2.5664 | 41.5527 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 16.5 | 2.1952 | 78.2412 | 606.4586 | 7.2428 | 14.4855 | 7.2428 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.7 | 3.8 | 3.75 | 2.6667 | 1998-04-08 | 15:00 | 29.41 | 23.5 | 49 | 50 | 590 | 7 | 40.9 | 47.9 | 0.4534 | 0.14614 | 11.3173 | 15.9452 | 15.3896 | 988.7847 | 39.1007 | 977.5173 | 9.4405 | 40.0595 | 0.38417 | 1998-04-10 | 11:00 | 28 | 23.5 | 40 | 40 | 580 | 6.4 | 3 |  | 9.4 | 0.44572 | 0.68085 | 60.7021 | 14.5785 | 14.0705 | 246.9651 | 48.3679 | 244.7737 | 1.975 | 38.025 | 0.37003 | 6.04 |  |  | 47.9 |  |  | 247.9633 |  | 57.1365 | 246.8595 | 80.5963 | 0.003 |  |  | 0.21607 |  | 95.7746 | 0.21489 | 98.6039 | [8 empty] | Total dissolved solids | mg/L | 43.2 | 43.9 | 43.55 | 1.6073 | 194.5 | 263.55 | -35.5013 | 61.0291 | 262.3068 | 83.3973 | Total dissolved solids | mg/L | 50.9 | 504 | 604.0818 | -19.8575 | 54.4519 | 601.2321 | 91.5341 | Total dissolved solids | mg/L | 37.6 | 157.1 | 185.9 | -18.3323 | 66.3535 | 185.1585 | 79.6931 | Total dissolved solids | mg/L | 35.8 | 137.5 | 144.3 | -4.9455 | 67.9642 | 143.7924 | 75.103 | UV254 F, cm-1 | 0.071 | 0.071 | 0.071 | 0.071 | UV254 F, cm-1 | 0.071 | 0.071 | 0.071 | 0.071 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 16.5 | 1.5808 | 77.6268 | 606.4586 | 7.2428 | 24.1425 | 16.8998 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.073 | 0.069 | 0.071 | 5.6338 | 1998-04-08 | 17:00 | 31.41 | 24.1 | 49 | 50 | 590 | 7.1 | 41 | 48.1 | 0.4534 | 0.14761 | 11.2661 | 16.173 | 15.335 | 990.414 | 39.1587 | 978.9667 | 9.4553 | 40.0447 | 0.38295 | 1998-04-10 | 13:00 | 30 | 22.3 | 42 | 43 | 580 | 6.7 | 3.1 |  | 9.8 | 0.44572 | 0.68367 | 58.1837 | 15.2619 | 15.2619 | 248.2412 | 48.5974 | 245.9349 | 1.9849 | 40.5151 | 0.3767 | [27 empty] | Total hardness | mg/L as CaCO3 | 5 | 5.1 | 5.05 | 1.9802 | 47.9 | 70.6952 | -47.5891 | 80.1181 | 70.3242 | 92.819 | Total hardness | mg/L as CaCO3 | 2.9 | 156 | 207.4455 | -32.9779 | 88.5827 | 206.3918 | 98.5949 | Total hardness | mg/L as CaCO3 | 4.3 | 50.5 | 46.5 | 7.9208 | 83.0709 | 46.289 | 90.7105 | Total hardness | mg/L as CaCO3 | 4.2 | 36.6 | 34.4857 | 5.7767 | 83.4646 | 34.344 | 87.7708 | UV254 p, cm-1 | 0.01 | 0.017 | 0.01 | 0.004 | UV254 p, cm-1 | 0.01 | 0.017 | 0.01 | 0.004 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.12 |  |  |  | SUVA | L/(mg*m) | 1.973 | 1.8158 | 1.8944 | 8.2974 | 1998-04-09 | 6:00 | 44.41 | 23 | 49 | 50 | 590 | 7 | 40.8 | 47.8 | 0.4534 | 0.14644 | 11.3431 | 15.9452 | 15.6187 | 989.1226 | 39.1141 | 977.8513 | 9.4437 | 40.0563 | 0.38992 | 1998-04-10 | 15:00 | 32 | 24 | 42 | 43 | 580 | 6.8 | 3 |  | 9.8 | 0.44572 | 0.69388 | 58.1837 | 15.4897 | 14.7305 | 252.8615 | 49.4949 | 250.4772 | 2.0217 | 40.4783 | 0.36391 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 2.6 | 2.7 | 2.65 | 3.7736 | 79.4 | 35.2306 | 55.6289 | 79.2157 | 35.0465 | 92.4386 | Calcium hardness | mg/L as CaCO3 | 2.4 | 136.1 | 96.4909 | 29.1029 | 81.1765 | 96.0062 | 97.5002 | Calcium hardness | mg/L as CaCO3 | 2.2 | 27.7 | 23.3 | 15.8845 | 82.7451 | 23.1945 | 90.515 | Calcium hardness | mg/L as CaCO3 | 2.1 | 18.5 | 17.3143 | 6.4093 | 83.5294 | 17.2431 | 87.8212 | BromideF, ug/L | 60 | 60 | 60 | 60 | BromideF, ug/L | 60 | 60 | 60 | 60 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 62 | 58 | 60 | 6.6667 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-10 | 17:00 | 34 | 24 | 42 | 43 | 580 | 6.5 | 2.9 |  | 9.4 | 0.44572 | 0.69149 | 60.7021 | 14.8063 | 14.0807 | 251.735 | 49.2952 | 249.4663 | 2.0131 | 40.4869 | 0.34778 | 6.06 |  |  | 46.9 |  |  | 257.1034 |  | 58.0313 | 255.9256 | 81.6744 | 0.001 |  |  | 0.2279 |  | 98.5915 | 0.22663 | 99.5587 | [8 empty] | Turbidity | ntu | 0.11 | 0.11 | 0.11 | 0 | 0.22 | 0.85194 | -287.2434 | 67.6471 | 0.84774 | 87.0244 | Turbidity | ntu | 0.1 | 0.32 | 2.2818 | -613.0682 | 70.5882 | 2.2706 | 95.5958 | Turbidity | ntu | 0.13 | 0.22 | 0.55 | -150 | 61.7647 | 0.5479 | 76.273 | Turbidity | ntu | 0.12 | 0.21 | 0.43429 | -106.8027 | 64.7059 | 0.43282 | 72.2746 | Bromidep, ug/L | 63 | 62 | 57 | 59 | Bromidep, ug/L | 63 | 62 | 57 | 59 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4 | 2.5 | 3.25 | 46.1538 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 7:00 | 48 | 22.2 | 43 | 43 | 570 | 6.3 | 3 |  | 9.3 | 0.43803 | 0.67742 | 60.2903 | 14.3507 | 14.3932 | 245.4692 | 48.0742 | 243.2874 | 1.963 | 41.037 | 0.35074 | 6.47 | 6.15 | 6.25 | 45.5 | 112.3 | 194 | 250.875 | -29.317 | 59.2841 | 249.74 | 81.7811 | 0.001 | 0.07 | 0.197 | 0.218 | -10.6599 | 98.5915 | 0.2168 | 99.5387 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25 | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | Total Hardness (mg/L as CaCO3) | 31.8 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 2.5 | 0.822 | 1.661 | 101.0235 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 9:00 | 50 | 23.1 | 48 | 49 | 580 | 7 | 3.4 |  | 10.4 | 0.44572 | 0.67308 | 54.7692 | 15.9452 | 15.5726 | 243.6585 | 47.6802 | 241.2933 | 1.948 | 46.552 | 0.33452 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 1.25 | 1.5 | 0.5 | 1.5 | Alkp, mg/L CaCO3 | 1.25 | 1.5 | 0.5 | 1.5
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | pH | 5.47 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 1.5 | 1.678 | 1.589 | 11.202 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 11:00 | 52 | 23.5 | 48 | 49 | 580 | 7 | 2.9 |  | 9.9 | 0.44572 | 0.70707 | 57.5859 | 15.9452 | 15.3896 | 259.1052 | 50.7028 | 256.59 | 2.0714 | 46.4286 | 0.33147 | 6.45 |  |  | 46.4 |  |  | 269.4914 |  | 58.4787 | 268.1451 | 82.6959 | 0 | [15 empty] | UV254 | cm-1 | 0.011 | 0.009 | 0.01 | 20 | 0.208 | 0.20677 | 0.58933 | 85.9155 | 0.20566 | 95.1377 | UV254 | cm-1 | 0.017 | 0.527 | 0.50791 | 3.6226 | 76.0563 | 0.50538 | 96.6362 | UV254 | cm-1 | 0.01 | 0.117 | 0.132 | -12.8205 | 85.9155 | 0.13139 | 92.3891 | UV254 | cm-1 | 0.004 | 0.091 | 0.099714 | -9.5761 | 94.3662 | 0.099267 | 95.9704 | T-HdF, mg/L CaCO3 | 25.4 | 25.4 | 25.4 | 25.4 | T-HdF, mg/L CaCO3 | 25.4 | 25.4 | 25.4 | 25.4
Treatment Plant Category | CONV | [11 empty] | Ammonia (mg/L) | BMRL | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 20.9 | 20.9 | 20.9 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 13:00 | 54 | 22.9 | 48 | 49 | 580 | 7 | 2.9 |  | 9.9 | 0.44572 | 0.70707 | 57.5859 | 15.9452 | 15.6649 | 259.1052 | 50.7028 | 256.59 | 2.0714 | 46.4286 | 0.3374 | [27 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.7333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.597 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.625 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.82 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 5.05 | 2.9 | 4.3 | 4.2 | T-Hdp, mg/L CaCO3 | 5.05 | 2.9 | 4.3 | 4.2
Process Train Name | Conventional Train | Additional Information | [10 empty] | TOC (mg/L) | 3.8 |  |  |  | SDS-Chlorination pH | --- | 7.7 | 7.7 | 7.7 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 15:00 | 56 | 24.5 | 48 | 49 | 580 | 6.9 | 2.9 |  | 9.8 | 0.44572 | 0.70408 | 58.1837 | 15.7174 | 14.7279 | 257.6574 | 50.4266 | 255.1921 | 2.06 | 46.44 | 0.31714 | [27 empty] | Bromide | mg/L | 63 | 63 | 63 | 0 | --- | 53.3226 | --- | -5 | 53.3773 | -18.0278 | Bromide | mg/L | 62 | --- | 43.8182 | --- | -3.3333 | 43.9118 | -41.192 | Bromide | mg/L | 57 | --- | 63 | --- | 5 | 62.97 | 9.4807 | Bromide | mg/L | 59 | --- | 60.4286 | --- | 1.6667 | 60.4219 | 2.3533 | Ca-HdF, mg/L CaCO3 | 12.75 | 12.75 | 12.75 | 12.75 | Ca-HdF, mg/L CaCO3 | 12.75 | 12.75 | 12.75 | 12.75
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | UV254 (cm-1) | 0.075 |  |  |  | SDS-Incubation time | hours | 6.75 | 6.8 | 6.775 | 0.73801 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-11 | 17:00 | 58 | 23.9 | 48 | 49 | 580 | 6.9 | 2.9 |  | 9.8 | 0.44572 | 0.70408 | 58.1837 | 15.7174 | 14.9914 | 257.6574 | 50.4266 | 255.1921 | 2.06 | 46.44 | 0.32281 | 6.55 |  |  | 45.9 |  |  | 268.4276 |  | 58.9262 | 267.1039 | 82.8157 | 0 | [15 empty] | SDS-Cl2 dose | mg/L | 1 | 1 | 1 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 2.65 | 2.4 | 2.2 | 2.1 | Ca-Hdp, mg/L CaCO3 | 2.65 | 2.4 | 2.2 | 2.1
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | Bromide (ug/L) | 55 |  |  |  | SDS-TOX | mg Cl- /L | 610 | 225 | 417.5 | 92.2156 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-12 | 8:00 | 73 | 23 | 50 | 51 | 580 | 6.7 | 2.7 |  | 9.4 | 0.44572 | 0.71277 | 60.7021 | 15.2619 | 14.9493 | 261.8507 | 51.2617 | 259.418 | 2.0937 | 48.4063 | 0.30883 | 6.11 | 5.92 | 6.01 | 44.8 | 110.4 | 196.9 | 277.8852 | -41.1301 | 59.9105 | 276.5389 | 83.7997 | 0.003 | 0.064 | 0.207 | 0.23974 | -15.8168 | 95.7746 | 0.23837 | 98.7415 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.786 | 0.739 | 0.7625 | 6.1639 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.04 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.869 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.712 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 50.6 | 41.4 | 46 | 20 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-12 | 17:00 | 82 | 23.1 | 50 | 51 | 580 | 6.6 | 2.9 |  | 9.5 | 0.44572 | 0.69474 | 60.0526 | 15.0341 | 14.6827 | 253.2356 | 49.5821 | 250.9182 | 2.0249 | 48.4751 | 0.30289 | 6.36 |  |  | 44.8 |  |  | 264.119 |  | 59.9105 | 262.8711 | 82.9574 | 0.001 |  |  | 0.23031 |  | 98.5915 | 0.22901 | 99.5633 | [8 empty] | SDS-Cl2 demand | mg/L | 0.214 | 0.261 | 0.2375 | 19.7895 | --- | 4.5972 | --- | 85.0535 | 4.5725 | 94.806 | SDS-Cl2 demand | mg/L | 0.46 | --- | 10.7236 | --- | 71.051 | 10.6708 | 95.6892 | SDS-Cl2 demand | mg/L | 0.131 | --- | 3.047 | --- | 91.7558 | 3.0324 | 95.68 | SDS-Cl2 demand | mg/L | 0.288 | --- | 2.1466 | --- | 81.8754 | 2.1379 | 86.5287 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 21.4 | 18.76 | 20.08 | 13.1474 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 7:30 | 97.5 | 23.6 | 50 | 51 | 580 | 6.2 | 2.9 |  | 9.1 | 0.44572 | 0.68132 | 62.7363 | 14.1229 | 13.5905 | 247.1501 | 48.4177 | 245.0257 | 1.9767 | 48.5233 | 0.28008 | [27 empty] | SDS-Chlorination temp. | oC | 20.9 | 20.9 | 20.9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20.9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 20.9 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | -1.414 | -1.5336 | -1.3541 | -1.3397 | Qp/QT (THM4), % | 53.9153 | 58.4764 | 51.6338 | 51.0849
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 45% rejection of CaCl2; 70 psi, 500mg/L CaCl2, 25 degrees C, 15%recovery | [14 empty] | SDS-DBCM | mg/L | 5.3 | 4.7 | 5 | 12 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 9:30 | 99.5 | 23.6 | 58 | 59 | 580 | 6.6 | 0.8 |  | 7.4 | 0.44572 | 0.89189 | 77.3784 | 15.0341 | 14.4673 | 395.2459 | 77.3869 | 391.6289 | 3.1605 | 55.3395 | 0.26143 | [27 empty] | SDS-Chlorination pH | --- | 7.75 | 7.75 | 7.75 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.63 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.86 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.65 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | [15 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 10:00 | 100 | 21.5 | 58 | 59 | 580 | 6.5 | 0.8 |  | 7.3 | 0.44572 | 0.89041 | 78.4521 | 14.8063 | 15.1606 | 393.5541 | 77.0664 | 390.0073 | 3.1471 | 55.3529 | 0.27389 | 6.54 |  |  | 48.2 |  |  | 628.0938 |  | 56.868 | 624.8443 | 92.2861 | 0.004 |  |  | 0.61538 |  | 94.3662 | 0.61195 | 99.3464 | [8 empty] | SDS-Incubation time | hours | 6.75 | 6.75 | 6.75 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.8 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.8 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.8 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 18.9731 | 17.8438 | 19.9124 | 20.1383
|  | Variability of rejection of reference solute (%) | 45 | [14 empty] | SDS-THM4 | mg/L | 77.3 | 64.86 | 71.08 | 17.5014 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 12:30 | 102.5 | 22.5 | 58 | 59 | 590 | 6.5 | 0.8 |  | 7.3 | 0.4534 | 0.89041 | 79.8219 | 14.8063 | 14.719 | 393.5168 | 77.071 | 390.0305 | 3.147 | 55.353 | 0.26591 | 6.58 |  |  | 51.3 |  |  | 602.9062 |  | 54.094 | 599.8677 | 91.4481 | 0.005 |  |  | 0.60725 |  | 92.9577 | 0.60393 | 99.1721 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | [15 empty] | SDS-MCAA* | mg/L | BMRL | 2.04 | 2.04 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-13 | 16:30 | 106.5 | 21.7 | 58 | 59 | 590 | 6.1 | 0.73 |  | 6.83 | 0.4534 | 0.89312 | 85.3836 | 13.8951 | 14.1438 | 396.4217 | 77.6827 | 393.1262 | 3.1709 | 55.3291 | 0.25563 | [27 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 1.55 | --- | 405.6409 | --- | 96.6304 | 403.5593 | 99.6159 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 0.86033 | 0.9288 | 0.83618 | 0.92439
|  | Standard testing pH | [15 empty] | SDS-DCAA* | mg/L | 20.38 | 19.87 | 20.125 | 2.5342 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 9:00 | 123 | 21.8 | 59 | 60 | 590 | 6 | 5.9 |  | 11.9 | 0.4534 | 0.5042 | 48.5798 | 13.6673 | 13.8708 | 187.9367 | 36.8331 | 186.4 | 1.5034 | 57.9966 | 0.23917 | 5.87 | 5.8 | 5.96 | 40.5 | 112.4 | 164.2 | 184.2076 | -12.1849 | 63.7584 | 183.4769 | 77.9264 | 0.002 | 0.071 | 0.134 | 0.14117 | -5.3504 | 97.1831 | 0.14046 | 98.5761 | [8 empty] | SDS-BDCM | mg/L | 1.49 | 1.32 | 1.405 | 12.0996 | --- | 61.6469 | --- | 93.003 | 61.3065 | 97.7082 | SDS-BDCM | mg/L | 3.13 | --- | 157.2209 | --- | 84.4124 | 156.4271 | 97.9991 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 22.75 | 16.26 | 19.505 | 33.2735 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 11:00 | 125 | 21.1 | 59 | 60 | 590 | 6 | 5.8 |  | 11.8 | 0.4534 | 0.50847 | 49 | 13.6673 | 14.1608 | 189.0288 | 37.0472 | 187.4832 | 1.5121 | 57.9879 | 0.2442 | 5.89 |  |  | 40 |  |  | 185.9741 |  | 64.2058 | 185.2319 | 78.4054 | 0.004 |  |  | 0.14031 |  | 94.3662 | 0.13962 | 97.135 | [8 empty] | SDS-DBCM | mg/L | 2.81 | 2.53 | 2.67 | 10.4869 | --- | 10.1861 | --- | 46.6 | 10.1437 | 73.6781 | SDS-DBCM | mg/L | 4.46 | --- | 9.3691 | --- | 10.8 | 9.3438 | 52.2678 | SDS-DBCM | mg/L | 1.76 | --- | 8.24 | --- | 64.8 | 8.2076 | 78.5565 | SDS-DBCM | mg/L | 1.33 | --- | 6.5729 | --- | 73.4 | 6.5483 | 79.6895 | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.038112 | 0.039423 | 0.039503 | 0.036773
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 13:00 | 127 | 22.9 | 59 | 60 | 590 | 5.9 | 5.9 |  | 11.8 | 0.4534 | 0.5 | 49 | 13.4396 | 13.2033 | 186.8708 | 36.6292 | 185.3683 | 1.4949 | 58.0051 | 0.22762 |  |  |  | 39.7 |  |  | 183.8 |  | 64.4743 | 183.0795 | 78.3154 | [16 empty] | SDS-CHBr3 | mg/L | 2.05 | 1.83 | 1.94 | 11.3402 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.95 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.38 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.08 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 61.6175 | 61.1695 | 58.451 | 59.4892
|  | Typical pressure drop across a single element (psi) | [15 empty] | SDS-DBAA* | mg/L | 1.04 | BMRL | 1.04 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 15:00 | 129 | 21.8 | 58 | 59 | 590 | 5.9 | 5.9 |  | 11.8 | 0.4534 | 0.5 | 49 | 13.4396 | 13.6397 | 186.8708 | 36.6292 | 185.3683 | 1.4949 | 57.0051 | 0.23927 | 5.87 | [10 empty] | 0.004 |  |  | 0.138 |  | 94.3662 | 0.13733 | 97.0873 | [8 empty] | SDS-THM4 | mg/L | 6.35 | 5.68 | 6.015 | 11.1388 | --- | 215.9021 | --- | 91.5377 | 214.7161 | 97.1986 | SDS-THM4 | mg/L | 11.09 | --- | 556.4536 | --- | 84.3979 | 553.6442 | 97.9969 | SDS-THM4 | mg/L | 3.14 | --- | 139.02 | --- | 95.5824 | 138.3406 | 97.7302 | SDS-THM4 | mg/L | 2.41 | --- | 100.51 | --- | 96.6095 | 100.0511 | 97.5912 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 1.7108 | 1.8114 | 1.3464 | 1.8669
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 5.44 | 6.32 | 5.88 | 14.966 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-14 | 17:00 | 131 | 22.9 | 58 | 59 | 580 | 5.8 | 5.8 |  | 11.6 | 0.44572 | 0.5 | 49 | 13.2118 | 12.9795 | 186.8708 | 36.6292 | 185.3683 | 1.4949 | 57.0051 | 0.22769 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 14.4282 | 12.2428 | 14.5053 | 14.57
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 8:00 | 144 | 22.9 | 58 | 59 | 570 | 5.6 | 13 |  | 18.6 | 0.43803 | 0.30108 | 29.6452 | 12.7562 | 12.5319 | 147.4375 | 28.9039 | 146.273 | 1.1795 | 57.3205 | 0.21863 | [27 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 7.3046 | 6.6977 | 7.3026 | 7.3095
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 9:00 | 145 | 22.8 | 58 | 59 | 580 | 5.7 | 13.7 |  | 19.4 | 0.44572 | 0.29381 | 28.8969 | 12.984 | 12.7935 | 146.3107 | 28.6829 | 145.1547 | 1.1705 | 57.3295 | 0.22316 | 6.14 | 6.26 | 6.3 | 32.4 | 107.8 | 134.6 | 144.7642 | -7.5514 | 71.0067 | 144.2121 | 77.5331 | 0.001 | 0.07 | 0.091 | 0.10012 | -10.0265 | 98.5915 | 0.099637 | 98.9964 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 11:00 | 147 | 22.3 | 58 | 59 | 570 | 5.7 | 13 |  | 18.7 | 0.43803 | 0.30481 | 29.4813 | 12.984 | 12.984 | 148.026 | 29.0152 | 146.8359 | 1.1842 | 57.3158 | 0.22653 | 6.18 |  |  | 32.4 |  |  | 146.5419 |  | 71.0067 | 145.9712 | 77.8038 | 0.002 |  |  | 0.10125 |  | 97.1831 | 0.10076 | 98.015 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 44.17 | 38.17 | 41.17 | 14.5737 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 13:00 | 149 | 21.9 | 58 | 59 | 570 | 5.9 | 13.1 |  | 19 | 0.43803 | 0.31053 | 29 | 13.4396 | 13.5994 | 148.9357 | 29.1851 | 147.6962 | 1.1913 | 57.3087 | 0.2373 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.28 | --- | -0.90182 | --- | -23.0769 | -0.89058 | 243.7268 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 49.61 | 44.49 | 47.05 | 10.882 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 15:00 | 151 | 22.3 | 58 | 59 | 580 | 5.8 | 13 |  | 18.8 | 0.44572 | 0.30851 | 29.8511 | 13.2118 | 13.2118 | 148.6113 | 29.1299 | 147.4165 | 1.1888 | 57.3112 | 0.23053 | 6.19 |  |  | 32.1 |  |  | 147.2862 |  | 71.2752 | 146.7102 | 78.1201 | 0.001 |  |  | 0.10223 |  | 98.5915 | 0.10172 | 99.017 | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -31.1635 | -32.1634 | -31.1635 | -31.1635 | Qp/QT (HAA5), % | 34.4183 | 35.5227 | 34.4183 | 34.4183
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-15 | 17:00 | 153 | 22 | 58 | 58 | 590 | 5.6 | 12.8 |  | 18.4 | 0.4534 | 0.30435 | 31.0652 | 12.7562 | 12.8698 | 147.948 | 29.0118 | 146.8191 | 1.1837 | 56.8163 | 0.22652 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 48.6858 | 49.7699 | 47.6962 | 47.445
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-18 | 10:30 | 171.5 | 21.8 | 50 | 50 | 590 | 9.6 | 15 | x | 24.6 | 0.4534 | 0.39024 | 22.9837 | 21.8678 | 22.1933 | 162.9343 | 31.7745 | 160.8002 | 1.3009 | 48.6991 | 0.45572 | [27 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-04-18 | 12:00 | 173 | 21.9 | 50 | 50 | 590 | 9.7 | 23 |  | 32.7 | 0.4534 | 0.29664 | 17.0428 | 22.0955 | 22.3583 | 146.8069 | 28.6255 | 144.8639 | 1.1721 | 48.8279 | 0.4579 | 6.26 | 6.39 | 6.35 | 51.5 | 115.8 | 136.2 | 137.1598 | -0.70469 | 53.915 | 136.4556 | 62.2588 | 0.0045 | 0.069 | 0.091 | 0.099046 | -8.8414 | 93.662 | 0.098268 | 95.4207 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-04-18 | 14:00 | 175 | 22.8 | 50 | 50 | 590 | 9.4 | 18 |  | 27.4 | 0.4534 | 0.34307 | 20.5328 | 21.4122 | 21.098 | 154.3816 | 30.115 | 152.4018 | 1.2328 | 48.7672 | 0.43263 | [27 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 132.8065 | --- | 100 | 132.056 | 100 | SDS-HAA5 | mg/L | 1.28 | --- | 363.9164 | --- | 96.8909 | 362.0483 | 99.6465 | SDS-HAA5 | mg/L | 0 | --- | 82.34 | --- | 100 | 81.9283 | 100 | SDS-HAA5 | mg/L | 0 | --- | 58.8143 | --- | 100 | 58.5392 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.1238 | 1.1879 | 1.0872 | 1.1412
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 151.7742 | --- | 100 | 150.9165 | 100 | SDS-HAA6 | mg/L | 1.28 | --- | 417.3709 | --- | 97.2795 | 415.2274 | 99.6917 | SDS-HAA6 | mg/L | 0 | --- | 94.1 | --- | 100 | 93.6295 | 100 | SDS-HAA6 | mg/L | 0 | --- | 67.2143 | --- | 100 | 66.8999 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.050005 | 0.051818 | 0.050005 | 0.04794
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 61.0325 | 60.7105 | 58.9675 | 59.6558
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 1.9058 | 1.9836 | 1.6477 | 1.9919
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 18.3959 | 17.4074 | 18.1377 | 18.1033
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 9.2738 | 9.0734 | 9.1189 | 9.0845
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on R8: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R9: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R10: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R11: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R12: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R13: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R14: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R15: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R16: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R17: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R18: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on X27: C. Hill (8/26/99): The primary and feed TOX concentrations were verified by the consultant. The high TOX concentration in the primary feed sample may be due to contamination, though there is no evidence to support this in any of the QC samples during the run, i.e. method blanks. The QC samples for both TOX runs met the ICR QC criteria.
Note on DG17: C. Hill (8/26/99): TDS, calcium and total hardness, and UV permeate and concentrate data during Runs 1 (70%) and 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DG18: C. Hill (8/26/99): TDS, calcium and total hardness, and UV permeate and concentrate data during Runs 1 (70%) and 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DG19: C. Hill (8/26/99): TDS, calcium and total hardness, and UV permeate and concentrate data during Runs 1 (70%) and 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ17: C. Hill (8/26/99): TDS, calcium and total hardness, and UV permeate and concentrate data during Runs 1 (70%) and 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ18: C. Hill (8/26/99): TDS, calcium and total hardness, and UV permeate and concentrate data during Runs 1 (70%) and 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."
Note on DQ19: C. Hill (8/26/99): TDS, calcium and total hardness, and UV permeate and concentrate data during Runs 1 (70%) and 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low, or 3) Ca and total hardness concentrations in the permeate were generally very low due to low feed concentrations and high rejection by the membrane and "measurements near the MRL will not be as accurate and reproducible as measurements at a median concentration."

## NF200. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 5.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.82775 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 16.4 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-15 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.8 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.83 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.5 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.6 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -4.2 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 12:00 | 10:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 89.285 | 89.285 | 89.285 | 89.285 | SDS-THM4F, ug/L | 89.285 | 89.285 | 89.285 | 89.285 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 112 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 0 | 159 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 5.9095 | 10.748 | 2.808 | 1.177 | SDS-THM4p, ug/L | 5.9095 | 10.748 | 2.808 | 1.177 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.96 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.87 | 6.31 | 6.09 | 7.225 | 1998-07-06 | 10:00 | 0 | 22.4 | 60 | 61 | 600 | 7.6 | 3.5 | 11.1 | 0.46109 | 0.68468 | 53.0541 | 17.312 | 17.2609 | 2.3367 | 0.092329 | 2.3082 | 0.022301 | 60.4777 | 0.28541 | 1998-07-08 | 12:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 41.033 | 41.033 | 41.033 | 41.033 | SDS-HAA5F, ug/L | 41.033 | 41.033 | 41.033 | 41.033 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21697 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | 20 | 23 | 21.5 | 13.9535 | 1998-07-06 | 12:00 | 2 | 22.6 | 60 | 61 | 600 | 7.9 | 2.9 | 10.8 | 0.46109 | 0.73148 | 54.5556 | 17.9953 | 17.8365 | 2.6899 | 0.10624 | 2.6559 | 0.025667 | 60.4743 | 0.29494 | 1998-07-08 | 13:00 | 1 | 23.5 | 60 | 61 | 600 | 7.8 | 3.6 |  | 11.4 | 0.46109 | 0.68421 | 51.6316 | 17.7675 | 17.1484 | 259.1491 | 44.1581 | 256.3543 | 2.1359 | 58.3641 | 0.29382 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 1.552 | 1.5655 | 0 | 0 | SDS-HAA5p, ug/L | 1.552 | 1.5655 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 5.3 | 6.5 | 5.9 | 20.339 | 1998-07-06 | 14:00 | 4 | 23.1 | 60 | 61 | 600 | 8.5 | 3.3 | 11.8 | 0.46109 | 0.72034 | 49.8475 | 19.3621 | 18.9096 | 2.5967 | 0.10245 | 2.5614 | 0.024766 | 60.4752 | 0.31268 | 1998-07-08 | 15:00 | 3 | 24.4 | 60 | 61 | 600 | 7.9 | 3.5 |  | 11.4 | 0.46109 | 0.69298 | 51.6316 | 17.9953 | 16.9123 | 263.5957 | 44.9095 | 260.7164 | 2.1725 | 58.3275 | 0.28995 | 5.83 | 5.87 | 6.29 | 43.3 | 110 | 192.5 | 267.2286 | -38.82 | 61.3565 | 265.7544 | 83.7068 | 0.002 | 0.066 | 0.194 | 0.23651 | -21.9146 | 97.2973 | 0.23497 | 99.1488 | [8 empty] | Sampling date | MM/DD/YY | 1998-07-11 | 1998-07-11 | --- | --- | 1998-07-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-12 | 1998-07-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-14 | 1998-07-14 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 272.5 | 272.5 | 272.5 | 272.5 | SDS-TOXF, ug Cl- /L | 272.5 | 272.5 | 272.5 | 272.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 110 | 114.1 | 112.05 | 3.6591 | 1998-07-06 | 16:00 | 6 | 23.7 | 60 | 60 | 600 | 8.8 | 3.5 | 12.3 | 0.46109 | 0.71545 | 47.7805 | 20.0454 | 19.2328 | 2.5578 | 0.10087 | 2.5218 | 0.024389 | 59.9756 | 0.32068 | 1998-07-08 | 17:00 | 5 | 23.8 | 60 | 61 | 600 | 7.7 | 3.3 |  | 11 | 0.46109 | 0.7 | 53.5455 | 17.5398 | 16.7791 | 267.2348 | 45.5422 | 264.3897 | 2.2027 | 58.2973 | 0.28782 | [27 empty] | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 28.8 | 31.3 | 30.05 | 8.3195 | 1998-07-06 | 17:30 | 7.5 | 23.7 | 60 | 61 | 600 | 9 | 3.9 | 12.9 | 0.46109 | 0.69767 | 45.5116 | 20.501 | 19.67 | 2.4255 | 0.095622 | 2.3905 | 0.023124 | 60.4769 | 0.32525 | 1998-07-09 | 7:00 | 19 | 21.4 | 61 | 62 | 600 | 7.1 | 3.2 |  | 10.3 | 0.46109 | 0.68932 | 57.2524 | 16.173 | 16.609 | 261.6447 | 44.627 | 259.0767 | 2.1573 | 59.3427 | 0.27988 | 6.15 |  |  | 44 |  |  | 263.0359 |  | 60.7318 | 261.74 | 83.1894 | 0.002 |  |  | 0.23375 |  | 97.2973 | 0.23238 | 99.1393 | [8 empty] | Operation time | hh.hh | 73 | 73 | --- | --- | 73 | --- | --- | --- | --- | --- | Operation time | hh.hh | 96 | 96 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122 | 122 | --- | --- | --- | --- | --- | Cumulative time | hr | 144 | 144 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.4115 | 2.4115 | 2.4115 | 2.4115 | SDS-CDF, mg/L | 2.4115 | 2.4115 | 2.4115 | 2.4115 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 19.5 | 20 | 19.75 | 2.5316 | 1998-07-07 | 8:00 | 22 | 22.7 | 60 | 61 | 600 | 8.8 | 3.3 | 12.1 | 0.46109 | 0.72727 | 48.5868 | 20.0454 | 19.8098 | 2.6542 | 0.10467 | 2.6168 | 0.025308 | 60.4747 | 0.32757 | 1998-07-09 | 9:00 | 21 | 21 | 61 | 62 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 16.8066 | 268.7497 | 45.8389 | 266.1119 | 2.2159 | 59.2841 | 0.28349 | [27 empty] | pH | --- | 6.76 | 6.74 | 6.75 | 0.2963 | 6.81 | --- | --- | --- | --- | --- | pH | --- | 6.56 | 7.08 | --- | --- | --- | --- | --- | pH | --- | 6.63 | 6.56 | --- | --- | --- | --- | --- | pH | --- | 6.45 | 6.99 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.333 | 0.402 | 0.382 | 0.323 | SDS-CDp, mg/L | 0.333 | 0.402 | 0.382 | 0.323 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 16.5 | 3.6288 | 79.6748 | 606.4586 | 7.2428 | 10.3468 | 3.104 | Calcium (mg/L) | 6.57 |  |  |  | Turbidity | ntu | 0.17 | 0.16 | 0.165 | 6.0606 | 1998-07-07 | 10:00 | 24 | 22.9 | 60 | 61 | 600 | 8.8 | 3.7 | 12.5 | 0.46109 | 0.704 | 47 | 20.0454 | 19.6931 | 2.4709 | 0.097445 | 2.4361 | 0.023561 | 60.4764 | 0.32563 | 1998-07-09 | 11:00 | 23 | 21.7 | 62 | 62 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 16.4624 | 268.7497 | 45.8389 | 266.1119 | 2.2159 | 59.7841 | 0.27536 | 6.29 | 6.43 | 6.92 | 44.2 | 109.7 | 264 | 272.6283 | -3.2683 | 60.5533 | 271.2768 | 83.7067 | 0.002 | 0.067 | 0.229 | 0.2444 | -6.7249 | 97.2973 | 0.24297 | 99.1768 | [8 empty] | Temperature | oC | 23.2 | 23.2 | 23.2 | 0 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 23.2 | 23.2 | --- | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | Temperature | oC | 23.7 | 23.7 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.65 | 3.65 | 3.65 | 3.65 | TOCF, mg/L | 3.65 | 3.65 | 3.65 | 3.65 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 16.5 | 10.7968 | 86.8428 | 606.4586 | 7.2428 | 8.0475 | 0.80475 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-07-07 | 12:00 | 26 | 22.7 | 61 | 62 | 590 | 9 | 3.7 | 12.7 | 0.4534 | 0.70866 | 45.4567 | 20.501 | 20.26 | 2.5057 | 0.09876 | 2.469 | 0.023886 | 61.4761 | 0.32956 | 1998-07-09 | 13:00 | 25 | 22.6 | 62 | 62 | 600 | 7.2 | 3 |  | 10.2 | 0.46109 | 0.70588 | 57.8235 | 16.4008 | 16.256 | 270.3266 | 46.1014 | 267.6359 | 2.2288 | 59.7712 | 0.27197 | [27 empty] | Alkalinity | mg/L as CaCO3 | 4.1 | 3.6 | 3.85 | 12.987 | 11.3 | 10.4629 | 7.4079 | 34.7458 | 10.4256 | 63.0718 | Alkalinity | mg/L as CaCO3 | 5.1 | 12.2 | 12.3727 | -1.4158 | 13.5593 | 12.3359 | 58.6572 | Alkalinity | mg/L as CaCO3 | 3 | 8.6 | 8.8 | -2.3256 | 49.1525 | 8.7722 | 65.8011 | Alkalinity | mg/L as CaCO3 | 2.4 | 8.2 | 7.3296 | 10.6149 | 59.322 | 7.3062 | 67.1513 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 16.5 | 2.1952 | 78.2412 | 606.4586 | 7.2428 | 14.4855 | 7.2428 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.6 | 3.7 | 3.65 | 2.7397 | 1998-07-07 | 14:00 | 28 | 22.7 | 60 | 61 | 590 | 9 | 3.6 | 12.6 | 0.4534 | 0.71429 | 45.8254 | 20.501 | 20.26 | 2.5488 | 0.10046 | 2.5115 | 0.024297 | 60.4757 | 0.33501 | 1998-07-09 | 15:00 | 27 | 22.9 | 62 | 62 | 600 | 7.3 | 3 |  | 10.3 | 0.46109 | 0.70874 | 57.2524 | 16.6286 | 16.3363 | 271.8914 | 46.3618 | 269.1474 | 2.2416 | 59.7584 | 0.27337 | [27 empty] | Total dissolved solids | mg/L | 44.4 | 44.6 | 44.5 | 0.44944 | 267 | 262.4032 | 1.7216 | 60.2856 | 261.1753 | 82.9616 | Total dissolved solids | mg/L | 52.54 | 490 | 593.54 | -21.1306 | 53.1102 | 590.7995 | 91.107 | Total dissolved solids | mg/L | 36.3 | 165.7 | 187.8 | -13.3374 | 67.6037 | 187.0741 | 80.5959 | Total dissolved solids | mg/L | 31.6 | 143.1 | 144.9099 | -1.2648 | 71.7983 | 144.3731 | 78.1123 | UV254 F, cm-1 | 0.074 | 0.074 | 0.074 | 0.074 | UV254 F, cm-1 | 0.074 | 0.074 | 0.074 | 0.074 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 16.5 | 1.5808 | 77.6268 | 606.4586 | 7.2428 | 24.1425 | 16.8998 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.072 | 0.076 | 0.074 | 5.4054 | 1998-07-07 | 17:00 | 31 | 24.4 | 60 | 61 | 600 | 9.5 | 3.9 | 13.4 | 0.46109 | 0.70896 | 43.7761 | 21.64 | 20.3375 | 2.5081 | 0.098797 | 2.4699 | 0.023902 | 60.4761 | 0.33629 | 1998-07-09 | 17:00 | 29 | 23.3 | 61 | 62 | 600 | 7.4 | 3.2 |  | 10.6 | 0.46109 | 0.69811 | 55.6038 | 16.8564 | 16.3654 | 266.2093 | 45.3865 | 263.4858 | 2.1946 | 59.3054 | 0.27595 | 6.16 |  |  | 44.6 |  |  | 268.0281 |  | 60.1963 | 266.6503 | 83.274 | 0.002 |  |  | 0.2405 |  | 97.2973 | 0.23903 | 99.1633 | [8 empty] | Total hardness | mg/L as CaCO3 | 5.7 | 5.5 | 5.6 | 3.5714 | 84.1 | 84.471 | -0.4411 | 81.3644 | 84.0265 | 93.3354 | Total hardness | mg/L as CaCO3 | 6.3 | 196.8 | 222.2091 | -12.9111 | 79.0349 | 221.1154 | 97.1508 | Total hardness | mg/L as CaCO3 | 5.2 | 55 | 54.9 | 0.18182 | 82.6955 | 54.6619 | 90.487 | Total hardness | mg/L as CaCO3 | 5.2 | 41.9 | 40.2 | 4.0573 | 82.6955 | 40.0342 | 87.0111 | UV254 p, cm-1 | 0.004 | 0.007 | 0.004 | 0.004 | UV254 p, cm-1 | 0.004 | 0.007 | 0.004 | 0.004 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.16 |  |  |  | SUVA | L/(mg*m) | 2 | 2.0541 | 2.027 | 2.6667 | 1998-07-08 | 7:00 | 45 | 22.4 | 60 | 61 | 600 | 9 | 3.6 | 12.6 | 0.46109 | 0.71429 | 46.619 | 20.501 | 20.4405 | 2.5488 | 0.10048 | 2.5121 | 0.024299 | 60.4757 | 0.338 | 1998-07-10 | 7:00 | 43 | 21.9 | 60 | 61 | 600 | 6.9 | 3 |  | 9.9 | 0.46109 | 0.69697 | 59.6061 | 15.7174 | 15.9044 | 265.5584 | 45.3072 | 263.0255 | 2.1898 | 58.3102 | 0.27275 | 6.3 |  |  | 43.8 |  |  | 269.025 |  | 60.9103 | 267.73 | 83.6402 | 0.003 |  |  | 0.2373 |  | 95.9459 | 0.23595 | 98.7286 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 4 | 3.7 | 3.85 | 7.7922 | 52.7 | 55.1403 | -4.6306 | 80.5063 | 54.8513 | 92.981 | Calcium hardness | mg/L as CaCO3 | 4.5 | 122.9 | 143.1364 | -16.4657 | 77.2152 | 142.4341 | 96.8406 | Calcium hardness | mg/L as CaCO3 | 3.7 | 33.2 | 35.8 | -7.8313 | 81.2658 | 35.6462 | 89.6202 | Calcium hardness | mg/L as CaCO3 | 3.7 | 27.5 | 26.3056 | 4.3431 | 81.2658 | 26.1986 | 85.8771 | BromideF, ug/L | 60.5 | 60.5 | 60.5 | 60.5 | BromideF, ug/L | 60.5 | 60.5 | 60.5 | 60.5 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 63 | 58 | 60.5 | 8.2645 | 1998-07-08 | 10:00 | 48 | 22.6 | 60 | 62 | 600 | 9 | 3.6 | 12.6 | 0.46109 | 0.71429 | 46.619 | 20.501 | 20.32 | 2.5488 | 0.10048 | 2.5121 | 0.024299 | 60.9757 | 0.33325 | 1998-07-10 | 9:00 | 45 | 21.6 | 60 | 61 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 16.2786 | 267.1603 | 45.5742 | 264.5751 | 2.2029 | 58.2971 | 0.27924 | [27 empty] | Turbidity | ntu | 0.1 | 0.09 | 0.095 | 10.5263 | 0.19 | 0.32081 | -68.8455 | 42.4242 | 0.31953 | 70.2692 | Turbidity | ntu | 0.08 | 0.23 | 0.85273 | -270.751 | 51.5152 | 0.84881 | 90.5751 | Turbidity | ntu | 0.11 | 0.16 | 0.22 | -37.5 | 33.3333 | 0.21947 | 49.8799 | Turbidity | ntu | 0.07 | 0.14 | 0.2038 | -45.5734 | 57.5758 | 0.20317 | 65.5459 | Bromidep, ug/L | 78 | 79 | 60 | 47 | Bromidep, ug/L | 78 | 79 | 60 | 47 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 3.64 | 3.7 | 3.67 | 1.6349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 11:00 | 47 | 22.1 | 60 | 61 | 600 | 6.9 | 3 |  | 9.9 | 0.46109 | 0.69697 | 59.6061 | 15.7174 | 15.8106 | 265.5584 | 45.3072 | 263.0255 | 2.1898 | 58.3102 | 0.27115 | 6.51 | 6.38 | 6.78 | 44.2 | 111.9 | 258 | 268.105 | -3.9167 | 60.5533 | 266.8175 | 83.4344 | 0.002 | 0.071 | 0.235 | 0.2396 | -1.9574 | 97.2973 | 0.23823 | 99.1605 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 5.9 | 5.9 | 5.9 | 5.9 | AlkF, mg/L CaCO3 | 5.9 | 5.9 | 5.9 | 5.9
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | Total Hardness (mg/L as CaCO3) | 26.6 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.66 | 0.857 | 1.2585 | 63.8061 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 13:00 | 49 | 23 | 61 | 62 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 15.6187 | 267.1603 | 45.5742 | 264.5751 | 2.2029 | 59.2971 | 0.2634 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 13 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 29.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 3.85 | 5.1 | 3 | 2.4 | Alkp, mg/L CaCO3 | 3.85 | 5.1 | 3 | 2.4
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | pH | 5.72 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 1.98 | 2.843 | 2.4115 | 35.7869 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 15:00 | 51 | 23.1 | 60 | 61 | 600 | 7 | 3 |  | 10 | 0.46109 | 0.7 | 59 | 15.9452 | 15.5726 | 267.1603 | 45.5742 | 264.5751 | 2.2029 | 58.2971 | 0.26712 | [27 empty] | UV254 | cm-1 | 0.003 | 0.005 | 0.004 | 50 | 0.237 | 0.22981 | 3.0353 | 94.5946 | 0.22853 | 98.2497 | UV254 | cm-1 | 0.007 | 0.546 | 0.61609 | -12.8372 | 90.5405 | 0.61301 | 98.8581 | UV254 | cm-1 | 0.004 | 0.145 | 0.144 | 0.68966 | 94.5946 | 0.14333 | 97.2092 | UV254 | cm-1 | 0.004 | 0.103 | 0.10259 | 0.39655 | 94.5946 | 0.10212 | 96.0832 | T-HdF, mg/L CaCO3 | 30.05 | 30.05 | 30.05 | 30.05 | T-HdF, mg/L CaCO3 | 30.05 | 30.05 | 30.05 | 30.05
Treatment Plant Category | CONV | [11 empty] | Ammonia (mg/L) | BMRL | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 30 | 30.3 | 30.15 | 0.99502 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 17:00 | 53 | 23.5 | 60 | 61 | 600 | 7.1 | 3 |  | 10.1 | 0.46109 | 0.70297 | 58.4059 | 16.173 | 15.6094 | 268.7497 | 45.8389 | 266.1119 | 2.2159 | 58.2841 | 0.26782 | 6.44 |  |  | 43.8 |  |  | 273.575 |  | 60.9103 | 272.2155 | 83.9098 | 0.002 |  |  | 0.2444 |  | 97.2973 | 0.24297 | 99.1768 | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.8231 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.8508 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.9863 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.9808 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 5.6 | 6.3 | 5.2 | 5.2 | T-Hdp, mg/L CaCO3 | 5.6 | 6.3 | 5.2 | 5.2
Process Train Name | Conventional Train | Additional Information | [10 empty] | TOC (mg/L) | 3.55 |  |  |  | SDS-Chlorination pH | --- | 8 | 8.12 | 8.06 | 1.4888 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 7:00 | 67 | 21.2 | 61 | 62 | 600 | 6.4 | 3 |  | 9.4 | 0.46109 | 0.68085 | 62.8298 | 14.5785 | 15.0603 | 257.3549 | 43.9383 | 255.0785 | 2.1228 | 59.3772 | 0.25364 | 6.33 |  |  | 41.8 |  |  | 261.9167 |  | 62.6952 | 260.7427 | 83.9689 | 0.006 |  |  | 0.21907 |  | 91.8919 | 0.21793 | 97.2468 | [8 empty] | Bromide | mg/L | 81 | 75 | 78 | 7.6923 | --- | 21.5484 | --- | -28.9256 | 21.8665 | -256.7102 | Bromide | mg/L | 79 | --- | -89.1818 | --- | -30.5785 | -88.3299 | 189.4375 | Bromide | mg/L | 60 | --- | 61 | --- | 0.82645 | 60.9952 | 1.6316 | Bromide | mg/L | 47 | --- | 66.0141 | --- | 22.314 | 65.924 | 28.7058 | Ca-HdF, mg/L CaCO3 | 19.75 | 19.75 | 19.75 | 19.75 | Ca-HdF, mg/L CaCO3 | 19.75 | 19.75 | 19.75 | 19.75
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | UV254 (cm-1) | 0.068 |  |  |  | SDS-Incubation time | hours | 6.4 | 6.43 | 6.415 | 0.46765 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 9:00 | 69 | 21.4 | 66 | 67 | 600 | 6.9 | 2.9 |  | 9.8 | 0.46109 | 0.70408 | 60.2245 | 15.7174 | 16.1412 | 269.3234 | 45.9496 | 266.7546 | 2.2209 | 64.2791 | 0.25111 | [27 empty] | SDS-Cl2 dose | mg/L | 1.2 | 1.2 | 1.2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 3.85 | 4.5 | 3.7 | 3.7 | Ca-Hdp, mg/L CaCO3 | 3.85 | 4.5 | 3.7 | 3.7
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | Bromide (ug/L) | 57 |  |  |  | SDS-TOX | mg Cl- /L | 275 | 270 | 272.5 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 11:00 | 71 | 21.3 | 66 | 67 | 600 | 6.8 | 2.9 |  | 9.7 | 0.46109 | 0.70103 | 60.8557 | 15.4897 | 15.9543 | 267.6847 | 45.6764 | 265.1686 | 2.2075 | 64.2925 | 0.24815 | 6.43 | 6.72 | 6.9 | 42.9 | 110.9 | 260 | 274.1948 | -5.4595 | 61.7135 | 272.8842 | 84.279 | 0.003 | 0.069 | 0.227 | 0.24048 | -5.9395 | 95.9459 | 0.23914 | 98.7455 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.873 | 0.861 | 0.867 | 1.3841 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.798 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.818 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.877 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 53.46 | 72.217 | 62.8385 | 29.8495 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 13:00 | 73 | 21.5 | 66 | 67 | 600 | 6.8 | 3 |  | 9.8 | 0.46109 | 0.69388 | 60.2245 | 15.4897 | 15.8603 | 263.9437 | 45.0381 | 261.4628 | 2.1767 | 64.3233 | 0.24657 | [27 empty] | SDS-Cl2 demand | mg/L | 0.327 | 0.339 | 0.333 | 3.6036 | --- | 7.0378 | --- | 86.1912 | 7.0001 | 95.2429 | SDS-Cl2 demand | mg/L | 0.402 | --- | 18.6702 | --- | 83.3299 | 18.5776 | 97.8361 | SDS-Cl2 demand | mg/L | 0.382 | --- | 4.441 | --- | 84.1592 | 4.4216 | 91.3605 | SDS-Cl2 demand | mg/L | 0.323 | --- | 3.2645 | --- | 86.6058 | 3.2506 | 90.0634 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 19.09 | 23.12 | 21.105 | 19.095 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 15:00 | 75 | 21.9 | 66 | 67 | 600 | 6.8 | 2.8 |  | 9.6 | 0.46109 | 0.70833 | 61.5 | 15.4897 | 15.6739 | 271.6145 | 46.347 | 269.0615 | 2.2399 | 64.2601 | 0.24391 | [27 empty] | SDS-Chlorination temp. | oC | 30.3 | 30.3 | 30.3 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 20.7315 | 22.0087 | 19.988 | 19.618 | Qp/QT (THM4), % | 63.9097 | 67.847 | 61.6175 | 60.4769
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 45% rejection of CaCl2; 70 psi, 500mg/L CaCl2, 25 degrees C, 15%recovery | [14 empty] | SDS-DBCM | mg/L | 4.919 | 5.764 | 5.3415 | 15.8195 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-11 | 17:00 | 77 | 21.5 | 58 | 58 | 600 | 6.4 | 2.8 |  | 9.2 | 0.46109 | 0.69565 | 64.2174 | 14.5785 | 14.9273 | 264.8205 | 45.2129 | 262.478 | 2.1844 | 55.8156 | 0.26744 | 6.28 |  |  | 45.3 |  |  | 264.6214 |  | 59.5716 | 263.4517 | 82.8052 | 0.004 |  |  | 0.234 |  | 94.5946 | 0.23277 | 98.2816 | [8 empty] | SDS-Chlorination pH | --- | 8.09 | 8.12 | 8.105 | 0.37014 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.07 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.1 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.02 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | [15 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 7:00 | 91 | 21.1 | 63 | 64 | 600 | 6.2 | 2.7 |  | 8.9 | 0.46109 | 0.69663 | 66.4157 | 14.1229 | 14.6329 | 265.3077 | 45.3088 | 263.0343 | 2.1886 | 61.3114 | 0.23866 | [27 empty] | SDS-Incubation time | hours | 6.43 | 6.43 | 6.43 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.34 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.34 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6.34 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 32.848 | 32.3467 | 32.8313 | 32.9832 | SDS-HAA5b, ug/L | 15.8008 | 14.2555 | 15.7495 | 16.2175
|  | Variability of rejection of reference solute (%) | 45 | [14 empty] | SDS-THM4 | mg/L | 77.469 | 101.101 | 89.285 | 26.4681 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 8:00 | 92 | 21.7 | 63 | 64 | 600 | 6.2 | 0.73 |  | 6.93 | 0.46109 | 0.89466 | 85.5801 | 14.1229 | 14.3756 | 434.0875 | 74.1327 | 430.368 | 3.581 | 59.919 | 0.23992 | [27 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | [15 empty] | SDS-MCAA* | mg/L | 2.548 | 1.75 | 2.149 | 37.1336 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 9:00 | 93 | 21.6 | 63 | 64 | 600 | 6.1 | 0.7 |  | 6.8 | 0.46109 | 0.89706 | 87.2353 | 13.8951 | 14.1856 | 437.4208 | 74.7124 | 433.7333 | 3.6086 | 59.8914 | 0.23686 | 6.81 |  |  | 49.5 |  |  | 657.1286 |  | 55.8233 | 654.0398 | 92.4317 | 0.004 |  |  | 0.684 |  | 94.5946 | 0.68054 | 99.4122 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 1.9806 | 1.9692 | 2.0058 | 2.0018 | SDS-CDb, mg/L | 1.0831 | 1.0481 | 1.161 | 1.1484
|  | Standard testing pH | [15 empty] | SDS-DCAA* | mg/L | 18.985 | 21.73 | 20.3575 | 13.484 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 10:00 | 94 | 21.5 | 63 | 64 | 600 | 6.1 | 0.73 |  | 6.83 | 0.46109 | 0.89312 | 86.8477 | 13.8951 | 14.2276 | 431.912 | 73.7714 | 428.2709 | 3.5632 | 59.9368 | 0.23738 | 6.82 |  |  | 50.7 |  |  | 624.7007 |  | 54.7523 | 621.7828 | 91.846 | 0.006 | 0.075 | 0.486 | 0.64222 | -32.1439 | 91.8919 | 0.63899 | 99.061 | [8 empty] | SDS-BDCM | mg/L | 1.116 | 1.052 | 1.084 | 5.9041 | --- | 65.6679 | --- | 94.8638 | 65.3039 | 98.3401 | SDS-BDCM | mg/L | 2.424 | --- | 172.2513 | --- | 88.5146 | 171.391 | 98.5857 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 18.497 | 16.14 | 17.3185 | 13.6097 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 11:00 | 95 | 21 | 63 | 64 | 600 | 6.1 | 0.73 |  | 6.83 | 0.46109 | 0.89312 | 86.8477 | 13.8951 | 14.4395 | 431.912 | 73.7714 | 428.2709 | 3.5632 | 59.9368 | 0.24091 | 6.75 | 6.09 | 6.83 | 50.9 | 109.8 | 442 | 623.0295 | -40.9569 | 54.5739 | 620.1211 | 91.7919 | 0.004 |  |  | 0.65893 |  | 94.5946 | 0.6556 | 99.3899 | [8 empty] | SDS-DBCM | mg/L | 2.72 | 2.637 | 2.6785 | 3.0987 | --- | 11.2688 | --- | 49.8549 | 11.2204 | 76.1283 | SDS-DBCM | mg/L | 5.116 | --- | 7.166 | --- | 4.2217 | 7.1556 | 28.5037 | SDS-DBCM | mg/L | 1.615 | --- | 9.068 | --- | 69.765 | 9.0323 | 82.1197 | SDS-DBCM | mg/L | 1.177 | --- | 7.0425 | --- | 77.965 | 7.0147 | 83.221 | UV254 b, cm-1 | 0.059488 | 0.059254 | 0.060008 | 0.060267 | UV254 b, cm-1 | 0.029263 | 0.028543 | 0.030868 | 0.031666
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-12 | 15:00 | 99 | 21.5 | 63 | 64 | 600 | 6 | 0.73 |  | 6.73 | 0.46109 | 0.89153 | 88.153 | 13.6673 | 13.9944 | 429.6956 | 73.4031 | 426.1327 | 3.5451 | 59.9549 | 0.23342 | [27 empty] | SDS-CHBr3 | mg/L | 2.194 | 2.1 | 2.147 | 4.3782 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3.208 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.193 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 64.128 | 64.5716 | 60.4001 | 57.8516 | Bromideb, ug/L | 71.6842 | 73.0517 | 60.1919 | 52.3356
|  | Typical pressure drop across a single element (psi) | [15 empty] | SDS-DBAA* | mg/L | 1.106 | 1.31 | 1.208 | 16.8874 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 8:00 | 116 | 21.7 | 63 | 64 | 600 | 5.5 | 5.5 |  | 11 | 0.46109 | 0.5 | 53.5455 | 12.5284 | 12.7526 | 191.3839 | 32.7161 | 189.9294 | 1.5794 | 61.9206 | 0.20595 | [27 empty] | SDS-THM4 | mg/L | 6.03 | 5.789 | 5.9095 | 4.0782 | --- | 274.8627 | --- | 93.3813 | 273.3472 | 97.8381 | SDS-THM4 | mg/L | 10.748 | --- | 724.7207 | --- | 87.9621 | 721.104 | 98.5095 | SDS-THM4 | mg/L | 2.808 | --- | 175.762 | --- | 96.855 | 174.9333 | 98.3948 | SDS-THM4 | mg/L | 1.177 | --- | 125.2728 | --- | 98.6817 | 124.685 | 99.056 | Alkb, mg/L CaCO3 | 5.475 | 5.7239 | 5.3203 | 5.2134 | Alkb, mg/L CaCO3 | 4.5899 | 5.3572 | 4.1131 | 3.7833
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 5.363 | 6.2 | 5.7815 | 14.4772 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 9:00 | 117 | 21.9 | 62 | 63 | 600 | 5.7 | 5.6 |  | 11.3 | 0.46109 | 0.50442 | 52.0973 | 12.984 | 13.1384 | 192.5985 | 32.9146 | 191.0815 | 1.5893 | 60.9107 | 0.2157 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 24.9811 | 24.8229 | 25.083 | 25.1749 | T-Hdb, mg/L CaCO3 | 14.4241 | 13.9363 | 14.738 | 15.0215
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 10:00 | 118 | 21.8 | 62 | 63 | 600 | 5.7 | 5.6 |  | 11.3 | 0.46109 | 0.50442 | 52.0973 | 12.984 | 13.1773 | 192.5985 | 32.9146 | 191.0815 | 1.5893 | 60.9107 | 0.21634 | 6.4 |  |  | 37.3 |  |  | 188.1348 |  | 66.7113 | 187.4184 | 80.098 | 0.002 |  |  | 0.14729 |  | 97.2973 | 0.1466 | 98.6357 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 16.4537 | 16.3937 | 16.5419 | 16.6013 | Ca-Hdb, mg/L CaCO3 | 9.5884 | 9.4033 | 9.8604 | 10.0435
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 12:00 | 120 | 21.9 | 63 | 64 | 600 | 5.8 | 5.6 |  | 11.4 | 0.46109 | 0.50877 | 51.6316 | 13.2118 | 13.3689 | 193.8032 | 33.1158 | 192.2499 | 1.5991 | 61.9009 | 0.21597 | 6.43 |  |  | 37.2 |  |  | 189.5732 |  | 66.8005 | 188.8367 | 80.3004 | 0.002 |  |  | 0.14857 |  | 97.2973 | 0.14786 | 98.6474 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 14:00 | 122 | 23.1 | 62 | 63 | 600 | 5.8 | 5.7 |  | 11.5 | 0.46109 | 0.50435 | 51.1739 | 13.2118 | 12.903 | 192.5814 | 32.9071 | 191.0379 | 1.589 | 60.911 | 0.21183 | 6.51 | 6.56 | 7.08 | 37 | 113 | 167.5 | 188.4167 | -12.4876 | 66.979 | 187.6848 | 80.2861 | 0.002 | 0.07 | 0.145 | 0.14726 | -1.5608 | 97.2973 | 0.14656 | 98.6354 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 41.136 | 40.93 | 41.033 | 0.50203 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-13 | 16:00 | 124 | 24.2 | 62 | 63 | 600 | 5.9 | 5.8 |  | 11.7 | 0.46109 | 0.50427 | 50.2821 | 13.4396 | 12.7056 | 192.565 | 32.8997 | 190.9949 | 1.5888 | 60.9112 | 0.20859 | [27 empty] | SDS-DBAA* | mg/L | 1.45 | 1.654 | 1.552 | 13.1443 | --- | 0.44232 | --- | -28.4768 | 0.44858 | -245.984 | SDS-DBAA* | mg/L | 1.5655 | --- | -1.6845 | --- | -29.5944 | -1.668 | 193.8528 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 46.499 | 47.13 | 46.8145 | 1.3479 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 8:00 | 140 | 22.7 | 62 | 63 | 600 | 5.7 | 14 |  | 19.7 | 0.46109 | 0.28934 | 29.4569 | 12.984 | 12.8314 | 147.4134 | 25.1926 | 146.2523 | 1.2164 | 61.2836 | 0.20938 | [27 empty] | SDS-BCAA* | mg/L | BMRL | 1.03 | 1.03 | #VALUE! | --- | 16.3574 | --- | 82.1846 | 16.271 | 93.6697 | SDS-BCAA* | mg/L | 1.1469 | --- | 43.2796 | --- | 80.1626 | 43.0662 | 97.3369 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -32.8436 | -32.8549 | -31.6014 | -31.6014 | Qp/QT (HAA5), % | 35.5437 | 35.5558 | 34.1993 | 34.1993
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 9:00 | 141 | 22.6 | 63 | 64 | 600 | 5.6 | 13.9 |  | 19.5 | 0.46109 | 0.28718 | 29.7692 | 12.7562 | 12.6436 | 147.0655 | 25.1366 | 145.9275 | 1.2136 | 62.2864 | 0.20299 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 59.6503 | 61.3605 | 59.7105 | 59.1527
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 10:00 | 142 | 24 | 62 | 64 | 600 | 5.7 | 13.9 |  | 19.6 | 0.46109 | 0.29082 | 29.6122 | 12.984 | 12.3477 | 147.6511 | 25.2332 | 146.4882 | 1.2184 | 61.7816 | 0.19986 | 6.4 |  |  | 32.4 |  |  | 144.7122 |  | 71.0843 | 144.1787 | 77.5279 | 0.001 |  |  | 0.10394 |  | 98.6486 | 0.10345 | 99.0333 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-14 | 12:00 | 144 | 22.4 | 62 | 63 | 600 | 5.7 | 13.9 |  | 19.6 | 0.46109 | 0.29082 | 29.6122 | 12.984 | 12.9457 | 147.6511 | 25.2332 | 146.4882 | 1.2184 | 61.2816 | 0.21125 | 6.76 | 5.7 | 7.02 | 33.1 | 113 | 142.9 | 144.4252 | -1.0673 | 70.4596 | 143.8964 | 76.9973 | 0.004 | 0.079 | 0.11 | 0.10271 | 6.6318 | 94.5946 | 0.10224 | 96.0875 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-07-14 | 14:00 | 146 | 23.4 | 62 | 63 | 600 | 5.8 | 13.9 |  | 19.7 | 0.46109 | 0.29442 | 29.4569 | 13.2118 | 12.7891 | 148.2355 | 25.3295 | 147.0474 | 1.2231 | 61.2769 | 0.20871 | 6.56 |  |  | 32.4 |  |  | 145.2853 |  | 71.0843 | 144.7396 | 77.615 | 0.002 |  |  | 0.10404 |  | 97.2973 | 0.10355 | 98.0686 | [8 empty] | SDS-HAA5 | mg/L | 1.45 | 1.654 | 1.552 | 13.1443 | --- | 128.9101 | --- | 96.2177 | 128.1924 | 98.7893 | SDS-HAA5 | mg/L | 1.5655 | --- | 360.361 | --- | 96.1848 | 358.5434 | 99.5634 | SDS-HAA5 | mg/L | 0 | --- | 82.066 | --- | 100 | 81.6728 | 100 | SDS-HAA5 | mg/L | 0 | --- | 57.793 | --- | 100 | 57.5192 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.6727 | 1.697 | 1.7174 | 1.6972
[45 empty] | 1998-07-14 | 16:00 | 148 | 23.8 | 62 | 63 | 600 | 6 | 13.9 |  | 19.9 | 0.46109 | 0.30151 | 29.1508 | 13.6673 | 13.0746 | 149.4004 | 25.5215 | 148.1617 | 1.2326 | 61.2674 | 0.2134 | [27 empty] | SDS-HAA6 | mg/L | 1.45 | 2.684 | 2.067 | 59.7 | --- | 146.4138 | --- | 95.5847 | 145.6004 | 98.5804 | SDS-HAA6 | mg/L | 2.7124 | --- | 403.6406 | --- | 94.2061 | 401.6096 | 99.3246 | SDS-HAA6 | mg/L | 0 | --- | 93.629 | --- | 100 | 93.1804 | 100 | SDS-HAA6 | mg/L | 0 | --- | 65.9359 | --- | 100 | 65.6236 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-07-15 | 16:00 | 165 | 23.2 | 60 | 61 | 600 | 9.1 | 21 | X | 30.1 | 0.46109 | 0.30233 | 18.9336 | 20.7288 | 20.1846 | 149.5803 | 25.4415 | 147.6976 | 1.232 | 59.268 | 0.34057 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.049119 | 0.050178 | 0.05006 | 0.05006
[45 empty] | 1998-07-15 | 17:00 | 166 | 23.3 | 60 | 61 | 600 | 9.3 | 21 |  | 30.3 | 0.46109 | 0.30693 | 18.802 | 21.1844 | 20.5674 | 150.3504 | 25.5653 | 148.4162 | 1.2382 | 59.2618 | 0.34706 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 66.7201 | 67.0778 | 60.329 | 55.8831
[45 empty] | 1998-07-16 | 8:00 | 181 | 22.8 | 57 | 58 | 600 | 8.5 | 20.1 |  | 28.6 | 0.46109 | 0.2972 | 19.979 | 19.3621 | 19.078 | 148.7278 | 25.3178 | 146.9795 | 1.2254 | 56.2746 | 0.33902 | 6.4 | 6.96 | 6.29 | 41.4 | 109.7 | 136.2 | 141.9269 | -4.2047 | 63.0522 | 141.2148 | 70.683 | 0.002 | 0.0714 | 0.1 | 0.10445 | -4.4478 | 97.2973 | 0.10372 | 98.0718 | [47 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 5.1714 | 5.6156 | 4.9082 | 4.703
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 21.3596 | 21.6055 | 21.5515 | 21.5515
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 14.0986 | 14.3277 | 14.261 | 14.261
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on R8: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R9: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R10: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R11: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R12: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R13: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R14: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R16: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R17: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R18: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on DQ17: C. Hill (8/26/99): TDS permeate and concentrate data during Run 2 (90%) was verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.

## NF200. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 1.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.85649 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 14.1 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1998-10-07 | 1998-10-14 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.9 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.6 | [7 empty] | Feed flow rate during sample collection (mL/min) | 16.1 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -5.08 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 12:00 | 8:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 590 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 79.515 | 79.515 | 79.515 | 79.515 | SDS-THM4F, ug/L | 79.515 | 79.515 | 79.515 | 79.515 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 112 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 1 | 161 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 3.835 | 9.99 | 1.2 | 1.02 | SDS-THM4p, ug/L | 3.835 | 9.99 | 1.2 | 1.02 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.96 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.35 | 5.98 | 5.665 | 11.1209 | 1998-10-05 | 10:00 | 0 | 21.9 | 56 | 57 | 600 | 7.6 | 3.3 | 10.9 | 0.46109 | 0.69725 | 54.0459 | 17.312 | 17.5179 | 2.422 | 0.095702 | 2.3926 | 0.023116 | 56.4769 | 0.31018 | 1998-10-07 | 11:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 56.855 | 56.855 | 56.855 | 56.855 | SDS-HAA5F, ug/L | 56.855 | 56.855 | 56.855 | 56.855 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21697 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | NA | 22.5 | 22.5 | #VALUE! | 1998-10-05 | 12:00 | 2 | 21.3 | 56 | 56 | 600 | 8.1 | 3.3 | 11.4 | 0.46109 | 0.71053 | 51.6316 | 18.4509 | 19.0044 | 2.5195 | 0.099472 | 2.4868 | 0.024037 | 55.976 | 0.33951 | 1998-10-07 | 12:00 | 1 | 20.4 | 56 | 57 | 600 | 6 | 2.5 |  | 8.5 | 0.46109 | 0.70588 | 69.5882 | 13.6673 | 14.4569 | 265.7446 | 37.8106 | 263.4652 | 2.2679 | 54.2321 | 0.26657 |  | 5.35 |  |  | 104.6 | [7 empty] | 0.073 | [14 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 1.025 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 1.025 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 2.4 | 2.6 | 2.5 | 8 | 1998-10-05 | 14:00 | 4 | 22 | 56 | 57 | 600 | 8.3 | 3.7 | 12 | 0.46109 | 0.69167 | 49 | 18.9065 | 19.0749 | 2.3836 | 0.094076 | 2.3519 | 0.022736 | 56.4773 | 0.33774 | 1998-10-07 | 14:00 | 3 | 21.4 | 56 | 57 | 600 | 6.2 | 2.6 |  | 8.8 | 0.46109 | 0.70455 | 67.1818 | 14.1229 | 14.5037 | 264.9939 | 37.6929 | 262.6451 | 2.2613 | 54.2387 | 0.2674 | 5.3 |  | 5.83 | 42.4 |  | 185.2 | 253.7692 | -37.0244 | 59.5613 | 252.6772 | 83.2197 | 0.006 |  | 0.213 | 0.23446 | -10.0758 | 91.8367 | 0.23328 | 97.428 | [8 empty] | Sampling date | MM/DD/YY | 1998-10-10 | 1998-10-10 | --- | --- | 1998-10-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-11 | 1998-10-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-12 | 1998-10-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-13 | 1998-10-13 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 267.5 | 267.5 | 267.5 | 267.5 | SDS-TOXF, ug Cl- /L | 267.5 | 267.5 | 267.5 | 267.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 104.6 | 105.1 | 104.85 | 0.47687 | 1998-10-05 | 16:00 | 6 | 21.4 | 56 | 56 | 600 | 8.3 | 3.5 | 11.8 | 0.46109 | 0.70339 | 49.8475 | 18.9065 | 19.4162 | 2.4663 | 0.097341 | 2.4335 | 0.023526 | 55.9765 | 0.34686 | 1998-10-07 | 17:00 | 6 | 21 | 56 | 57 | 600 | 6.2 | 2.5 |  | 8.7 | 0.46109 | 0.71264 | 67.9655 | 14.1229 | 14.6762 | 269.7292 | 38.3665 | 267.3384 | 2.3017 | 54.1983 | 0.27079 | [27 empty] | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 30 | 27.2 | 28.6 | 9.7902 | 1998-10-06 | 7:30 | 21.5 | 21.5 | 55 | 56 | 600 | 8.4 | 3 | 11.4 | 0.46109 | 0.73684 | 51.6316 | 19.1343 | 19.5921 | 2.7375 | 0.10803 | 2.7007 | 0.026111 | 55.4739 | 0.35318 | 1998-10-08 | 7:00 | 20 | 20.4 | 56 | 57 | 600 | 5.8 | 2.5 |  | 8.3 | 0.46109 | 0.6988 | 71.2892 | 13.2118 | 13.975 | 261.6937 | 37.245 | 259.524 | 2.2336 | 54.2664 | 0.25753 | 5.82 |  |  | 38.3 |  |  | 259.246 |  | 63.4716 | 258.1781 | 85.1653 | 0.003 |  |  | 0.23706 |  | 95.9184 | 0.23593 | 98.7284 | [8 empty] | Operation time | hh.hh | 73 | 73 | --- | --- | 73 | --- | --- | --- | --- | --- | Operation time | hh.hh | 97 | 97 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122 | 122 | --- | --- | --- | --- | --- | Cumulative time | hr | 145.5 | 145.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 2.805 | 2.805 | 2.805 | 2.805 | SDS-CDF, mg/L | 2.805 | 2.805 | 2.805 | 2.805 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 17 | 15.2 | 16.1 | 11.1801 | 1998-10-06 | 12:00 | 26 | 21.6 | 55 | 56 | 600 | 8.3 | 3.8 | 12.1 | 0.46109 | 0.68595 | 48.5868 | 18.9065 | 19.3018 | 2.3452 | 0.092561 | 2.314 | 0.022371 | 55.4776 | 0.34792 | 1998-10-08 | 9:00 | 22 | 21.1 | 56 | 57 | 600 | 5.9 | 2.5 |  | 8.4 | 0.46109 | 0.70238 | 70.4286 | 13.4396 | 13.9248 | 263.7275 | 37.529 | 261.5032 | 2.2509 | 54.2491 | 0.25668 | [27 empty] | pH | --- | 5.8 | 5.82 | 5.81 | 0.34423 | 6.14 | --- | --- | --- | --- | --- | pH | --- | 5.73 | 6.35 | --- | --- | --- | --- | --- | pH | --- | 6.56 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 6.16 | 6.52 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.385 | 0.43 | 0.3 | 0.22 | SDS-CDp, mg/L | 0.385 | 0.43 | 0.3 | 0.22 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 16.5 | 3.6288 | 79.6748 | 606.4586 | 7.2428 | 10.3468 | 3.104 | Calcium (mg/L) | 5.6 |  |  |  | Turbidity | ntu | 0.16 | 0.16 | 0.16 | 0 | 1998-10-06 | 14:00 | 28 | 22.3 | 55 | 56 | 600 | 8.4 | 3.7 | 12.1 | 0.46109 | 0.69421 | 48.5868 | 19.1343 | 19.1343 | 2.4011 | 0.094753 | 2.3688 | 0.022902 | 55.4771 | 0.3449 | 1998-10-08 | 11:00 | 24 | 20.4 | 56 | 57 | 600 | 5.9 | 2.6 |  | 8.5 | 0.46109 | 0.69412 | 69.5882 | 13.4396 | 14.2159 | 259.1084 | 36.8717 | 256.9231 | 2.2114 | 54.2886 | 0.26186 | 5.97 | 5.8 | 6.25 | 39.3 | 104.9 | 194.4 | 253.5981 | -30.4517 | 62.5179 | 252.5444 | 84.4384 | 0.004 | 0.072 | 0.219 | 0.23121 | -5.576 | 94.5578 | 0.23009 | 98.2616 | [8 empty] | Temperature | oC | 21.1 | 21.1 | 21.1 | 0 | 21.1 | --- | --- | --- | --- | --- | Temperature | oC | 21.2 | 21.2 | --- | --- | --- | --- | --- | Temperature | oC | 22.8 | 22.8 | --- | --- | --- | --- | --- | Temperature | oC | 22.5 | 22.5 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.525 | 3.525 | 3.525 | 3.525 | TOCF, mg/L | 3.525 | 3.525 | 3.525 | 3.525 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 16.5 | 10.7968 | 86.8428 | 606.4586 | 7.2428 | 8.0475 | 0.80475 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-10-06 | 18:00 | 32 | 21.5 | 56 | 57 | 600 | 8.3 | 3.6 | 11.9 | 0.46109 | 0.69748 | 49.4202 | 18.9065 | 19.3589 | 2.4239 | 0.095667 | 2.3917 | 0.023121 | 56.4769 | 0.34278 | 1998-10-08 | 13:00 | 26 | 20.7 | 56 | 57 | 600 | 5.9 | 2.5 |  | 8.4 | 0.46109 | 0.70238 | 70.4286 | 13.4396 | 14.0904 | 263.7275 | 37.529 | 261.5032 | 2.2509 | 54.2491 | 0.25974 | [27 empty] | Alkalinity | mg/L as CaCO3 | 2 | 1.2 | 1.6 | 50 | 3.5 | 4.6 | -31.4286 | 36 | 4.5856 | 65.108 | Alkalinity | mg/L as CaCO3 | 1.1 | 4.6 | 15.1 | -228.2609 | 56 | 15.0381 | 92.6852 | Alkalinity | mg/L as CaCO3 | 2.4 | 3.8 | 2.6 | 31.5789 | 4 | 2.5992 | 7.6639 | Alkalinity | mg/L as CaCO3 | 1.4 | 2.1 | 2.9714 | -41.4966 | 44 | 2.9651 | 52.7841 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 16.5 | 2.1952 | 78.2412 | 606.4586 | 7.2428 | 14.4855 | 7.2428 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.45 | 3.6 | 3.525 | 4.2553 | 1998-10-07 | 7:30 | 45.5 | 21.1 | 56 | 56 | 600 | 8.1 | 3.6 | 11.7 | 0.46109 | 0.69231 | 50.2821 | 18.4509 | 19.1171 | 2.3879 | 0.094277 | 2.3569 | 0.022781 | 55.9772 | 0.34152 | 1998-10-08 | 15:00 | 28 | 20.7 | 56 | 57 | 600 | 6 | 2.5 |  | 8.5 | 0.46109 | 0.70588 | 69.5882 | 13.6673 | 14.3293 | 265.7446 | 37.8106 | 263.4652 | 2.2679 | 54.2321 | 0.26422 | [27 empty] | Total dissolved solids | mg/L | 36.1 | 36.2 | 36.15 | 0.27663 | 194.4 | 265.15 | -36.394 | 65.5222 | 264.0496 | 86.3094 | Total dissolved solids | mg/L | 45.8 | 479 | 636.3 | -32.8392 | 56.3186 | 633.687 | 92.7725 | Total dissolved solids | mg/L | 30 | 160.4 | 179.7 | -12.0324 | 71.3877 | 179.1012 | 83.2497 | Total dissolved solids | mg/L | 29.8 | 134.9 | 137.0143 | -1.5673 | 71.5784 | 136.5827 | 78.1817 | UV254 F, cm-1 | 0.0735 | 0.0735 | 0.0735 | 0.0735 | UV254 F, cm-1 | 0.0735 | 0.0735 | 0.0735 | 0.0735 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 16.5 | 1.5808 | 77.6268 | 606.4586 | 7.2428 | 24.1425 | 16.8998 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.073 | 0.074 | 0.0735 | 1.3605 | 1998-10-07 | 10:30 | 48.5 | 21.3 | 56 | 56 | 590 | 8.1 | 3.6 | 11.7 | 0.4534 | 0.69231 | 49.4274 | 18.4509 | 19.0044 | 2.3879 | 0.094257 | 2.3564 | 0.022779 | 55.9772 | 0.3395 | 1998-10-08 | 17:00 | 30 | 20.4 | 56 | 57 | 600 | 5.9 | 2.5 |  | 8.4 | 0.46109 | 0.70238 | 70.4286 | 13.4396 | 14.2159 | 263.7275 | 37.529 | 261.5032 | 2.2509 | 54.2491 | 0.26205 | 5.97 |  |  | 38.2 |  |  | 262.144 |  | 63.567 | 261.0429 | 85.3664 | 0.003 |  |  | 0.23988 |  | 95.9184 | 0.23872 | 98.7433 | [8 empty] | Total hardness | mg/L as CaCO3 | 5.1 | 5.6 | 5.35 | 9.3458 | 87.3 | 82.85 | 5.0974 | 81.2937 | 82.4776 | 93.5134 | Total hardness | mg/L as CaCO3 | 5.3 | 215.9 | 238.3 | -10.3752 | 81.4685 | 237.269 | 97.7662 | Total hardness | mg/L as CaCO3 | 4.2 | 60.1 | 53 | 11.8136 | 85.3147 | 52.8048 | 92.0462 | Total hardness | mg/L as CaCO3 | 3.5 | 40.7 | 39.3571 | 3.2994 | 87.7622 | 39.2128 | 91.0743 | UV254 p, cm-1 | 0.002 | 0.004 | 0.005 | 0.003 | UV254 p, cm-1 | 0.002 | 0.004 | 0.005 | 0.003 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.19 |  |  |  | SUVA | L/(mg*m) | 2.1159 | 2.0556 | 2.0857 | 2.8952 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 7:00 | 44 | 20.2 | 56 | 57 | 590 | 5.6 | 2.5 |  | 8.1 | 0.4534 | 0.69136 | 71.8395 | 12.7562 | 13.5731 | 257.5832 | 36.6655 | 255.4864 | 2.1987 | 54.3013 | 0.24996 | 5.52 |  |  | 36.3 |  |  | 258.402 |  | 65.3791 | 257.348 | 85.8946 | 0.003 |  |  | 0.23142 |  | 95.9184 | 0.23034 | 98.6976 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 2.8 | 2.8 | 2.8 | 0 | 51.2 | 47.1333 | 7.9427 | 82.6087 | 46.9203 | 94.0324 | Calcium hardness | mg/L as CaCO3 | 2.8 | 129.8 | 135.8 | -4.6225 | 82.6087 | 135.2115 | 97.9292 | Calcium hardness | mg/L as CaCO3 | 2.1 | 34.2 | 30.1 | 11.9883 | 86.9565 | 29.988 | 92.9972 | Calcium hardness | mg/L as CaCO3 | 1.9 | 23 | 22.1857 | 3.5404 | 88.1988 | 22.1041 | 91.4043 | BromideF, ug/L | 56.2 | 56.2 | 56.2 | 56.2 | BromideF, ug/L | 56.2 | 56.2 | 56.2 | 56.2 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 53.4 | 59 | 56.2 | 9.9644 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 9:00 | 46 | 20.1 | 56 | 57 | 590 | 5.7 | 2.4 |  | 8.1 | 0.4534 | 0.7037 | 71.8395 | 12.984 | 13.8564 | 264.4723 | 37.6406 | 262.2808 | 2.2574 | 54.2426 | 0.25545 | [27 empty] | Turbidity | ntu | 0.13 | 0.08 | 0.105 | 47.619 | 0.16 | 0.28833 | -80.2083 | 34.375 | 0.28745 | 63.4722 | Turbidity | ntu | 0.1 | 0.2 | 0.7 | -250 | 37.5 | 0.69734 | 85.6599 | Turbidity | ntu | 0.15 | 0.17 | 0.17 | 0 | 6.25 | 0.16992 | 11.7232 | Turbidity | ntu | 0.37 | 0.75 | 0.07 | 90.6667 | -131.25 | 0.071208 | -419.6082 | Bromidep, ug/L | 57 | 58 | 48 | 48 | Bromidep, ug/L | 57 | 58 | 48 | 48 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 11:00 | 48 | 20.2 | 56 | 57 | 600 | 5.8 | 2.5 |  | 8.3 | 0.46109 | 0.6988 | 71.2892 | 13.2118 | 14.0579 | 261.6937 | 37.245 | 259.524 | 2.2336 | 54.2664 | 0.25905 | 5.56 | 5.84 | 6.12 | 36.2 | 103.8 | 191.8 | 264.118 | -37.7049 | 65.4745 | 263.0164 | 86.2366 | 0.004 | 0.074 | 0.221 | 0.23474 | -6.2172 | 94.5578 | 0.23362 | 98.2879 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 2.5 | 2.5 | 2.5 | 2.5 | AlkF, mg/L CaCO3 | 2.5 | 2.5 | 2.5 | 2.5
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | MPFI |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 2.16 | 2.23 | 2.195 | 3.1891 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 13:00 | 50 | 20.9 | 57 | 58 | 600 | 5.7 | 2.6 |  | 8.3 | 0.46109 | 0.68675 | 71.2892 | 12.984 | 13.5326 | 255.1052 | 36.3125 | 253.0267 | 2.1775 | 55.3225 | 0.24461 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 31 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 1.6 | 1.1 | 2.4 | 1.4 | Alkp, mg/L CaCO3 | 1.6 | 1.1 | 2.4 | 1.4
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | pH | 5.45 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 2.84 | 2.77 | 2.805 | 2.4955 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 15:00 | 52 | 21.1 | 58 | 58 | 600 | 5.9 | 2.6 |  | 8.5 | 0.46109 | 0.69412 | 69.5882 | 13.4396 | 13.9248 | 259.1084 | 36.8717 | 256.9231 | 2.2114 | 55.7886 | 0.2496 | [27 empty] | UV254 | cm-1 | 0.002 | 0.002 | 0.002 | 0 | 0.231 | 0.24033 | -4.0404 | 97.2789 | 0.23919 | 99.1638 | UV254 | cm-1 | 0.004 | 0.465 | 0.699 | -50.3226 | 94.5578 | 0.69592 | 99.4252 | UV254 | cm-1 | 0.005 | 0.136 | 0.142 | -4.4118 | 93.1973 | 0.14145 | 96.4652 | UV254 | cm-1 | 0.003 | 0.097 | 0.10371 | -6.9219 | 95.9184 | 0.10331 | 97.0961 | T-HdF, mg/L CaCO3 | 28.6 | 28.6 | 28.6 | 28.6 | T-HdF, mg/L CaCO3 | 28.6 | 28.6 | 28.6 | 28.6
Treatment Plant Category | CONV | [11 empty] | UV254 | 0.0625 | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 30.4 | 30.3 | 30.35 | 0.32949 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-09 | 17:00 | 54 | 21 | 58 | 58 | 600 | 5.7 | 2.6 |  | 8.3 | 0.46109 | 0.68675 | 71.2892 | 12.984 | 13.4926 | 255.1052 | 36.3125 | 253.0267 | 2.1775 | 55.8225 | 0.24171 | 5.65 |  |  | 36.2 |  |  | 255.3519 |  | 65.4745 | 254.311 | 85.7655 | 0.004 |  |  | 0.22587 |  | 94.5578 | 0.22481 | 98.2207 | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.925 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.5 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.971 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.94 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 5.35 | 5.3 | 4.2 | 3.5 | T-Hdp, mg/L CaCO3 | 5.35 | 5.3 | 4.2 | 3.5
Process Train Name | Conventional Train | Additional Information | [10 empty] | Ammonia (mg/L) | BMRL |  |  |  | SDS-Chlorination pH | --- | 7.79 | 7.8 | 7.795 | 0.12829 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 7:00 | 68 | 19.6 | 60 | 61 | 590 | 5.8 | 2.6 |  | 8.4 | 0.4534 | 0.69048 | 69.2381 | 13.2118 | 14.3094 | 257.1237 | 36.5894 | 254.9557 | 2.1945 | 58.3055 | 0.24542 | 5.88 |  |  | 36.8 |  |  | 256.6538 |  | 64.9022 | 255.5732 | 85.601 | 0.006 |  |  | 0.22408 |  | 91.8367 | 0.22301 | 97.3095 | [8 empty] | Bromide | mg/L | NR | 57 | 57 | #VALUE! | --- | 54.3333 | --- | -1.4235 | 54.3461 | -4.8832 | Bromide | mg/L | 58 | --- | 40 | --- | -3.2028 | 40.0797 | -44.7118 | Bromide | mg/L | 48 | --- | 64.4 | --- | 14.5907 | 64.3344 | 25.3898 | Bromide | mg/L | 48 | --- | 59.7143 | --- | 14.5907 | 59.6671 | 19.5537 | Ca-HdF, mg/L CaCO3 | 16.1 | 16.1 | 16.1 | 16.1 | Ca-HdF, mg/L CaCO3 | 16.1 | 16.1 | 16.1 | 16.1
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | TDS (mg/L) | 107 |  |  |  | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 9:00 | 70 | 20.5 | 60 | 61 | 590 | 5.8 | 2.6 |  | 8.4 | 0.4534 | 0.69048 | 69.2381 | 13.2118 | 13.9337 | 257.1237 | 36.5894 | 254.9557 | 2.1945 | 58.3055 | 0.23898 | [27 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 2.8 | 2.8 | 2.1 | 1.9 | Ca-Hdp, mg/L CaCO3 | 2.8 | 2.8 | 2.1 | 1.9
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | TOC (mg/L) | 3.4 |  |  |  | SDS-TOX | mg Cl- /L | 270 | 265 | 267.5 | 1.8692 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 11:00 | 72 | 20.8 | 60 | 61 | 590 | 5.8 | 2.6 |  | 8.4 | 0.4534 | 0.69048 | 69.2381 | 13.2118 | 13.8107 | 257.1237 | 36.5894 | 254.9557 | 2.1945 | 58.3055 | 0.23687 | 5.91 | 5.94 | 6.39 | 34.6 | 102.8 | 193 | 261.5615 | -35.5241 | 67.0005 | 260.446 | 86.7151 | 0.006 | 0.073 | 0.214 | 0.22408 | -4.7088 | 91.8367 | 0.22301 | 97.3095 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.98 | 2.25 | 2.115 | 12.766 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.07 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.2 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 2.28 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 50.43 | 63.19 | 56.81 | 22.4608 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 13:00 | 74 | 20.7 | 60 | 61 | 590 | 5.7 | 2.4 |  | 8.1 | 0.4534 | 0.7037 | 71.8395 | 12.984 | 13.6128 | 264.4723 | 37.6406 | 262.2808 | 2.2574 | 58.2426 | 0.23373 | [27 empty] | SDS-Cl2 demand | mg/L | 0.52 | 0.25 | 0.385 | 70.1299 | --- | 8.4517 | --- | 86.2745 | 8.4129 | 95.4237 | SDS-Cl2 demand | mg/L | 0.43 | --- | 24.18 | --- | 84.6702 | 24.0749 | 98.2139 | SDS-Cl2 demand | mg/L | 0.3 | --- | 5.31 | --- | 89.3048 | 5.29 | 94.3289 | SDS-Cl2 demand | mg/L | 0.22 | --- | 3.9129 | --- | 92.1569 | 3.898 | 94.3561 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 16.8 | 20.92 | 18.86 | 21.8452 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 15:00 | 76 | 21.2 | 60 | 61 | 600 | 5.7 | 2.4 |  | 8.1 | 0.46109 | 0.7037 | 73.0741 | 12.984 | 13.4131 | 264.463 | 37.6445 | 262.3082 | 2.2574 | 58.2426 | 0.2303 | [27 empty] | SDS-Chlorination temp. | oC | 30.3 | 30.3 | 30.3 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 30.3 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 9.93 | 10.8091 | 9.5959 | 9.5739 | Qp/QT (THM4), % | 57.4987 | 62.589 | 55.5641 | 55.4367
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 45% rejection of CaCl2; 70 psi, 500mg/L CaCl2, 25 degrees C, 15%recovery | [14 empty] | SDS-DBCM | mg/L | 3.49 | 4.2 | 3.845 | 18.4655 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-10 | 17:00 | 78 | 21.1 | 60 | 61 | 600 | 5.7 | 2.4 |  | 8.1 | 0.46109 | 0.7037 | 73.0741 | 12.984 | 13.4528 | 264.463 | 37.6445 | 262.3082 | 2.2574 | 58.2426 | 0.23098 | 5.99 |  |  | 33.1 |  |  | 275.2563 |  | 68.4311 | 274.106 | 87.9244 | 0.007 |  |  | 0.23144 |  | 90.4762 | 0.23037 | 96.9614 | [8 empty] | SDS-Chlorination pH | --- | 7.79 | 7.8 | 7.795 | 0.12829 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.84 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.82 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.82 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | [15 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 8:00 | 93 | 20.8 | 61 | 62 | 600 | 5.4 | 0.58 |  | 5.98 | 0.46109 | 0.90301 | 99.3344 | 12.3006 | 12.8583 | 464.7955 | 66.1892 | 461.208 | 3.9681 | 57.5319 | 0.2235 | [27 empty] | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 51.2093 | 50.8203 | 51.3993 | 51.4118 | SDS-HAA5b, ug/L | 24.1641 | 21.9116 | 25.264 | 25.3365
|  | Variability of rejection of reference solute (%) | 45 | [14 empty] | SDS-THM4 | mg/L | 70.72 | 88.31 | 79.515 | 22.1216 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 9:00 | 94 | 20.5 | 61 | 62 | 600 | 5.4 | 0.57 |  | 5.97 | 0.46109 | 0.90452 | 99.5025 | 12.3006 | 12.9728 | 467.4837 | 66.572 | 463.8755 | 3.9911 | 57.5089 | 0.22558 | 5.53 |  |  | 43.3 |  |  | 687.9553 |  | 58.7029 | 685.0543 | 93.6793 | 0.003 |  |  | 0.74139 |  | 95.9184 | 0.73807 | 99.5935 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | [15 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 10:00 | 95 | 20.2 | 61 | 62 | 600 | 5.2 | 0.6 |  | 5.8 | 0.46109 | 0.89655 | 102.4483 | 11.845 | 12.6036 | 453.5848 | 64.6114 | 450.2137 | 3.8729 | 57.6271 | 0.21871 | 5.65 |  |  | 45.1 |  |  | 622.6833 |  | 56.9862 | 620.1805 | 92.7279 | 0.003 |  |  | 0.6845 |  | 95.9184 | 0.68155 | 99.5598 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 1.48 | --- | 554.78 | --- | 97.3948 | 552.3316 | 99.732 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 2.5647 | 2.5483 | 2.5646 | 2.5575 | SDS-CDb, mg/L | 1.4135 | 1.3185 | 1.4131 | 1.372
|  | Standard testing pH | [15 empty] | SDS-DCAA* | mg/L | 30.38 | 25.1 | 27.74 | 19.0339 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 11:00 | 96 | 20.6 | 61 | 62 | 600 | 5.3 | 0.6 |  | 5.9 | 0.46109 | 0.89831 | 100.6949 | 12.0728 | 12.695 | 456.5912 | 65.0302 | 453.1324 | 3.8983 | 57.6017 | 0.22039 | 5.73 |  |  | 45.3 |  |  | 630.875 |  | 56.7954 | 628.2887 | 92.7899 | 0.004 |  |  | 0.68742 |  | 94.5578 | 0.6844 | 99.4155 | [8 empty] | SDS-BDCM | mg/L | 1.55 | 1.57 | 1.56 | 1.2821 | --- | 59.2267 | --- | 91.7285 | 58.9496 | 97.3537 | SDS-BDCM | mg/L | 2.9 | --- | 162.5 | --- | 84.6235 | 161.7938 | 98.2076 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 31.73 | 25.47 | 28.6 | 21.8881 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 12:00 | 97 | 20.6 | 61 | 62 | 600 | 5.3 | 0.6 |  | 5.9 | 0.46109 | 0.89831 | 100.6949 | 12.0728 | 12.695 | 456.5912 | 65.0302 | 453.1324 | 3.8983 | 57.6017 | 0.22039 | 5.69 | 5.9 | 6.28 | 45.1 | 102.2 | 419 | 632.6417 | -50.9885 | 56.9862 | 630.0467 | 92.8418 | 0.004 | 0.068 | 0.463 | 0.68742 | -48.4701 | 94.5578 | 0.6844 | 99.4155 | [8 empty] | SDS-DBCM | mg/L | 2.28 | 2.27 | 2.275 | 0.43956 | --- | 7.5083 | --- | 40.8322 | 7.4832 | 69.5985 | SDS-DBCM | mg/L | 4.02 | --- | 2.27 | --- | -4.5514 | 2.2777 | -76.4904 | SDS-DBCM | mg/L | 1.2 | --- | 6.49 | --- | 68.7906 | 6.4688 | 81.4495 | SDS-DBCM | mg/L | 1.02 | --- | 5.0557 | --- | 73.472 | 5.0395 | 79.7598 | UV254 b, cm-1 | 0.0664 | 0.065988 | 0.066927 | 0.06675 | UV254 b, cm-1 | 0.032388 | 0.030001 | 0.035439 | 0.034417
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 13:00 | 98 | 21 | 61 | 62 | 600 | 5.3 | 0.63 |  | 5.93 | 0.46109 | 0.89376 | 100.1804 | 12.0728 | 12.5458 | 448.9715 | 63.945 | 445.5704 | 3.8333 | 57.6667 | 0.21756 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.59 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 56.2794 | 56.3946 | 55.4131 | 55.4149 | Bromideb, ug/L | 56.66 | 57.3266 | 51.6437 | 51.6542
|  | Typical pressure drop across a single element (psi) | [15 empty] | SDS-DBAA* | mg/L | 1.03 | BMRL | 1.03 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-11 | 15:00 | 100 | 20.8 | 61 | 62 | 600 | 5.3 | 0.6 |  | 5.9 | 0.46109 | 0.89831 | 100.6949 | 12.0728 | 12.6202 | 456.5912 | 65.0302 | 453.1324 | 3.8983 | 57.6017 | 0.21909 | [27 empty] | SDS-THM4 | mg/L | 3.83 | 3.84 | 3.835 | 0.26076 | --- | 256.1017 | --- | 95.177 | 254.8895 | 98.4954 | SDS-THM4 | mg/L | 9.99 | --- | 705.24 | --- | 87.4363 | 702.1635 | 98.5773 | SDS-THM4 | mg/L | 1.2 | --- | 157.83 | --- | 98.4909 | 157.2035 | 99.2367 | SDS-THM4 | mg/L | 1.02 | --- | 113.1557 | --- | 98.7172 | 112.7044 | 99.095 | Alkb, mg/L CaCO3 | 2.4106 | 2.3487 | 2.4904 | 2.3947 | Alkb, mg/L CaCO3 | 1.9825 | 1.6238 | 2.4444 | 1.8902
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 8.53 | 5.77 | 7.15 | 38.6014 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 8:00 | 117 | 20 | 59 | 59 | 600 | 4.5 | 5 |  | 9.5 | 0.46109 | 0.47368 | 62.1579 | 10.2505 | 10.9716 | 176.5573 | 25.1753 | 175.4219 | 1.5081 | 57.4919 | 0.19084 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | 26.2913 | 26.0815 | 26.2586 | 26.197 | T-Hdb, mg/L CaCO3 | 15.2316 | 14.0168 | 15.0424 | 14.6854
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 9:00 | 118 | 20.4 | 58 | 59 | 600 | 4.8 | 4.6 |  | 9.4 | 0.46109 | 0.51064 | 62.8298 | 10.9339 | 11.5655 | 186.5187 | 26.5842 | 185.2392 | 1.5929 | 56.9071 | 0.20324 | [27 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 14.7793 | 14.6624 | 14.7566 | 14.7405 | Ca-Hdb, mg/L CaCO3 | 8.4527 | 7.7757 | 8.321 | 8.228
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 10:00 | 119 | 20.6 | 58 | 59 | 600 | 4.9 | 4.9 |  | 9.8 | 0.46109 | 0.5 | 60.2245 | 11.1617 | 11.7369 | 183.5436 | 26.1564 | 182.2583 | 1.5674 | 56.9326 | 0.20615 | 6.46 |  |  | 29.4 |  |  | 180.3 |  | 71.9599 | 179.6838 | 83.6379 | 0.007 |  |  | 0.14 |  | 90.4762 | 0.13946 | 94.9805 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 11:00 | 120 | 20.9 | 58 | 59 | 600 | 4.9 | 4.9 |  | 9.8 | 0.46109 | 0.5 | 60.2245 | 11.1617 | 11.6333 | 183.5436 | 26.1564 | 182.2583 | 1.5674 | 56.9326 | 0.20433 | 6.56 |  |  | 29.4 |  |  | 180.3 |  | 71.9599 | 179.6838 | 83.6379 | 0.007 |  |  | 0.14 |  | 90.4762 | 0.13946 | 94.9805 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 63.14 | 50.57 | 56.855 | 22.1089 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 12:00 | 121 | 21 | 58 | 59 | 600 | 4.8 | 4.8 |  | 9.6 | 0.46109 | 0.5 | 61.5 | 10.9339 | 11.3622 | 183.5403 | 26.1597 | 182.2813 | 1.5675 | 56.9325 | 0.19957 | 6.41 | 6.01 | 6.32 | 29.3 | 103.5 | 159.8 | 180.4 | -12.8911 | 72.0553 | 179.7956 | 83.7037 | 0.008 | 0.071 | 0.136 | 0.139 | -2.2059 | 89.1156 | 0.13848 | 94.2228 | [8 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.025 | --- | 1.075 | --- | 0.48544 | 1.0748 | 4.6315 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 71.67 | 56.34 | 64.005 | 23.9513 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-12 | 15:00 | 124 | 22 | 58 | 59 | 600 | 4.8 | 4.9 |  | 9.7 | 0.46109 | 0.49485 | 60.8557 | 10.9339 | 11.0313 | 182.1312 | 25.9588 | 180.8818 | 1.5555 | 56.9445 | 0.19372 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 5.0215 | 5.1137 | 5.0215 | 5.0215 | Qp/QT (HAA5), % | 52.5108 | 53.4748 | 52.5108 | 52.5108
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-13 | 8:00 | 141 | 20.9 | 56 | 57 | 590 | 4.8 | 11.4 |  | 16.2 | 0.4534 | 0.2963 | 35.4198 | 10.9339 | 11.3958 | 140.5629 | 20.0318 | 139.5823 | 1.2004 | 55.2996 | 0.20607 | [27 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 75.7147 | 75.9597 | 75.5824 | 75.5733 | SDS-THM4b, ug/L | 39.7748 | 42.3366 | 38.3912 | 38.2967
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-13 | 9:00 | 142 | 20.5 | 56 | 56 | 590 | 4.6 | 11.3 |  | 15.9 | 0.4534 | 0.28931 | 36.1069 | 10.4783 | 11.0509 | 139.4405 | 19.8777 | 138.5083 | 1.191 | 54.809 | 0.20163 | [27 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-13 | 10:00 | 143 | 20.3 | 56 | 57 | 590 | 4.7 | 11.4 |  | 16.1 | 0.4534 | 0.29193 | 35.646 | 10.7061 | 11.3581 | 139.859 | 19.9344 | 138.9037 | 1.1945 | 55.3055 | 0.20537 | 7.06 |  |  | 24.6 |  |  | 137.9355 |  | 76.5379 | 137.4841 | 82.107 | 0.003 |  |  | 0.10257 |  | 95.9184 | 0.10217 | 97.0637 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-10-13 | 11:00 | 144 | 20.4 | 56 | 57 | 590 | 4.8 | 11.5 |  | 16.3 | 0.4534 | 0.29448 | 35.1963 | 10.9339 | 11.5655 | 140.2698 | 19.9901 | 139.2913 | 1.1979 | 55.3021 | 0.20913 | 6.48 |  |  | 24.8 |  |  | 138.2622 |  | 76.3472 | 137.8006 | 82.003 | 0.004 |  |  | 0.10251 |  | 94.5578 | 0.10211 | 96.0826 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 189.5167 | --- | 100 | 188.606 | 100 | SDS-HAA5 | mg/L | 1.025 | --- | 559.325 | --- | 98.1972 | 556.8545 | 99.8159 | SDS-HAA5 | mg/L | 0 | --- | 113.71 | --- | 100 | 113.2552 | 100 | SDS-HAA5 | mg/L | 0 | --- | 81.2214 | --- | 100 | 80.8945 | 100 | SDS-CDb, mg/L | 2.6835 | 2.6835 | 2.6792 | 2.6752 | SDS-CDb, mg/L | 1.5342 | 1.535 | 1.4896 | 1.4476
[45 empty] | 1998-10-13 | 12:00 | 145 | 20.5 | 56 | 57 | 600 | 4.7 | 11.4 |  | 16.1 | 0.46109 | 0.29193 | 36.2671 | 10.7061 | 11.2911 | 139.8582 | 19.9366 | 138.9188 | 1.1945 | 55.3055 | 0.20416 | 6.55 | 6.68 | 6.68 | 24.9 | 104.6 | 133.4 | 137.8118 | -3.3072 | 76.2518 | 137.3696 | 81.8737 | 0.004 | 0.071 | 0.097 | 0.10215 | -5.3129 | 94.5578 | 0.10177 | 96.0695 | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 213.35 | --- | 100 | 212.3248 | 100 | SDS-HAA6 | mg/L | 1.025 | --- | 630.825 | --- | 98.3986 | 628.0381 | 99.8368 | SDS-HAA6 | mg/L | 0 | --- | 128.01 | --- | 100 | 127.498 | 100 | SDS-HAA6 | mg/L | 0 | --- | 91.4357 | --- | 100 | 91.0677 | 100 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1998-10-13 | 14:00 | 149 | 21.7 | 56 | 57 | 600 | 4.9 | 11.6 |  | 16.5 | 0.46109 | 0.29697 | 35.3636 | 11.1617 | 11.3614 | 140.672 | 20.0468 | 139.6869 | 1.2013 | 55.2987 | 0.20545 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.06991 | 0.069946 | 0.07006 | 0.06996 | UV254 b, cm-1 | 0.035955 | 0.036335 | 0.03753 | 0.03648
[45 empty] | 1998-10-14 | 8:00 | 161 | 20.4 | 56 | 57 | 590 | 4.8 | 11 |  | 15.8 | 0.4534 | 0.3038 | 36.3418 | 10.9339 | 11.5655 | 141.7855 | 20.2061 | 140.7964 | 1.2108 | 55.2892 | 0.20918 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 56.2402 | 56.292 | 55.7882 | 55.7882 | Bromideb, ug/L | 56.6201 | 57.1625 | 51.8941 | 51.8941
[45 empty] | 1998-10-15 | 8:00 | 178 | 20.6 | 53 | 54 | 600 | 7.8 | 18.4 | x | 26.2 | 0.46109 | 0.29771 | 21.9008 | 17.7675 | 18.6832 | 140.8255 | 19.9848 | 139.2545 | 1.2006 | 52.2994 | 0.35723 | [66 empty] | Alkb, mg/L CaCO3 | 2.4548 | 2.4284 | 2.495 | 2.4448 | Alkb, mg/L CaCO3 | 2.0274 | 1.7514 | 2.4475 | 1.9224
[45 empty] | 1998-10-15 | 9:00 | 179 | 21 | 53 | 54 | 600 | 7.7 | 18.6 |  | 26.3 | 0.46109 | 0.29278 | 21.8137 | 17.5398 | 18.2269 | 140.028 | 19.8745 | 138.4861 | 1.1938 | 52.3062 | 0.34846 | 6.5 | 6.63 | 6.67 | 35.5 | 104.5 | 130.8 | 133.5594 | -2.1096 | 66.1421 | 132.9302 | 73.2943 | 0.002 | 0.066 | 0.096 | 0.1031 | -7.3953 | 97.2789 | 0.10245 | 98.0478 | [47 empty] | T-Hdb, mg/L CaCO3 | 27.4325 | 27.4085 | 27.3747 | 27.3396 | T-Hdb, mg/L CaCO3 | 16.3912 | 16.1404 | 15.7874 | 15.4198
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | 15.4321 | 15.4199 | 15.397 | 15.3869 | Ca-Hdb, mg/L CaCO3 | 9.1161 | 8.9878 | 8.7485 | 8.6435
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on DG17: C. Hill (8/26/99): TDS permeate and concentrate data for Runs 1 (70 %) and 2 (90%), and UV permeate and concentrate UV data for Run 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.
Note on DQ17: C. Hill (8/26/99): TDS permeate and concentrate data for Runs 1 (70 %) and 2 (90%), and UV permeate and concentrate UV data for Run 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.
Note on DQ23: C. Hill (8/26/99): TDS permeate and concentrate data for Runs 1 (70 %) and 2 (90%), and UV permeate and concentrate UV data for Run 2 (90%) were verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from 1) significant fouling during the first 3 quarters of the study, or 2) even though rejection was stable, errors may have been made in flow rate measurements, particularly during the 90% run when waste flow rates are very low.

## NF200. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [80 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | City of Beaumont | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.167 |  |  | Alkalinity (mg/L as CaCO3) | 1.5 | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | 0.96 | [5 empty] | TDS concentration of setting solution (mg/L) | 0.8 | [12 empty] | Average bulk TDS rejection (decimal fraction) | 0.87326 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | TX1230001 | Membrane trade name | NF200B-4040 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.333 |  |  | Calcium Hardness (mg/L as CaCO3) | 16.1 | Rapid Mix | Alum: Al2(SO4)3 18H2O, 58 ppm | Full-scale | Sampling date | MM/DD/YY | 1999-01-14 | 1999-01-21 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.9 | [10 empty] | Feed flow rate during sample collection (mL/min) | 6.03 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.9 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 7.125
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22.3 |  |  | LSI | -5.12 | Pulsator Clarifier | NA | Full-scale | Sampling time | hh:mm | 12:00 | 8:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 600 | [10 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [7 empty] | Influent flow rate during sample collection (mL/min) | 600 | [6 empty] | SDS-THM4F, ug/L | 47.73 | 47.73 | 47.73 | 47.73 | SDS-THM4F, ug/L | 47.73 | 47.73 | 47.73 | 47.73 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 106 |  |  | Dissolved iron (mg/L) | 0.1 | Filtration | Anthracite Sand | Full-scale | Operation time | hh.hh | 2 | 156 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 1.19 | 4.9 | 0 | 0 | SDS-THM4p, ug/L | 1.19 | 4.9 | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.96 |  |  | Total iron (mg/L) | 0.18 | Filtration | 1 um exclusion | Bench-scale | pH | --- | 5.61 | 5.81 | 5.71 | 3.5026 | 1999-01-12 | 9:00 | 0 | 23.4 | 50 | 51 | 600 | 7.1 | 3.6 | 10.7 | 0.46109 | 0.66355 | 55.0748 | 16.173 | 15.6556 | 2.2057 | 0.087227 | 2.1807 | 0.02106 | 50.4789 | 0.31014 | 1999-01-14 | 10:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 31.41 | 31.41 | 31.41 | 31.41 | SDS-HAA5F, ug/L | 31.41 | 31.41 | 31.41 | 31.41 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Membrane hydrophobicity | Hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.21697 |  |  | Dissolved aluminum (mg/L) | 0.091 | Antiscalant Addition | 3 mg/L Hypersperse AF200ul | Bench-scale | Temperature | oC | 22.2 | 21.7 | 21.95 | 2.2779 | 1999-01-12 | 11:00 | 2 | 23.2 | 50 | 51 | 600 | 7.3 | 3 | 10.3 | 0.46109 | 0.70874 | 57.2524 | 16.6286 | 16.1921 | 2.5056 | 0.099054 | 2.4764 | 0.023919 | 50.4761 | 0.32079 | 1999-01-14 | 12:00 | 2 | 22.7 | 52 | 52 | 600 | 5.4 | 2.6 |  | 8 | 0.46109 | 0.675 | 74 | 12.3006 | 12.156 | 259.2237 | 32.596 | 257.1841 | 2.2561 | 49.7439 | 0.24437 | 5.45 | 5.61 | 5.99 | 32 | 106.5 | 216 | 260.4615 | -20.584 | 69.8824 | 259.4335 | 87.6654 | 0.002 | 0.055 | 0.134 | 0.16508 | -23.1917 | 96.3636 | 0.16434 | 98.783 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 1.51 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 1.51 | 0 | 0 | Construction Contingencies (% of construction costs) | 25
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) | 0.13 |  |  |  | Alkalinity | mg/L as CaCO3 | 2.5 | 2 | 2.25 | 22.2222 | 1999-01-12 | 14:00 | 5 | 24.1 | 50 | 51 | 600 | 7.9 | 2.8 | 10.7 | 0.46109 | 0.73832 | 55.0748 | 17.9953 | 17.0629 | 2.7506 | 0.10863 | 2.7159 | 0.026246 | 50.4738 | 0.33806 | 1999-01-14 | 14:00 | 4 | 23.2 | 52 | 52 | 600 | 5.5 | 2.3 |  | 7.8 | 0.46109 | 0.70513 | 75.9231 | 12.5284 | 12.1995 | 277.0355 | 34.8306 | 274.8153 | 2.4109 | 49.5891 | 0.24601 | [27 empty] | Sampling date | MM/DD/YY | 1999-01-17 | 1999-01-17 | --- | --- | 1999-01-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-18 | 1999-01-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-20 | 1999-01-20 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 172.5 | 172.5 | 172.5 | 172.5 | SDS-TOXF, ug Cl- /L | 172.5 | 172.5 | 172.5 | 172.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) | BMRL |  |  |  | Total dissolved solids | mg/L | 106.5 | 106 | 106.25 | 0.47059 | 1999-01-12 | 16:00 | 7 | 24.9 | 50 | 51 | 600 | 7.9 | 3.3 | 11.2 | 0.46109 | 0.70536 | 52.5714 | 17.9953 | 16.6642 | 2.4806 | 0.09797 | 2.4492 | 0.02367 | 50.4763 | 0.33014 | 1999-01-14 | 17:00 | 7 | 24.1 | 52 | 52 | 600 | 5.6 | 2.3 |  | 7.9 | 0.46109 | 0.70886 | 74.9494 | 12.7562 | 12.0952 | 279.4226 | 35.1255 | 277.1425 | 2.4316 | 49.5684 | 0.24401 | [27 empty] | Sampling time | hh:mm | 11:30 | 11:30 | --- | --- | 11:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:30 | 12:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | 56 | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | 56 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920.44
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) | 0.068 |  |  |  | Total hardness | mg/L as CaCO3 | 23.2 | 24.2 | 23.7 | 4.2194 | 1999-01-12 | 17:00 | 8 | 24.9 | 50 | 51 | 600 | 7.9 | 3.5 | 11.4 | 0.46109 | 0.69298 | 51.6316 | 17.9953 | 16.6642 | 2.3924 | 0.094487 | 2.3622 | 0.022828 | 50.4772 | 0.33013 | 1999-01-15 | 7:00 | 21 | 22.7 | 52 | 52 | 600 | 5.4 | 2.3 |  | 7.7 | 0.46109 | 0.7013 | 76.9221 | 12.3006 | 12.156 | 274.6288 | 34.5331 | 272.468 | 2.3902 | 49.6098 | 0.24503 | 6.29 |  |  | 33.2 |  |  | 277.7587 |  | 68.7529 | 276.6582 | 87.9996 | 0.002 |  |  | 0.17943 |  | 96.3636 | 0.17864 | 98.8804 | [8 empty] | Operation time | hh.hh | 73.5 | 73.5 | --- | --- | 73.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 98.5 | 98.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 122 | 122 | --- | --- | --- | --- | --- | Cumulative time | hr | 146 | 146 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 1.935 | 1.935 | 1.935 | 1.935 | SDS-CDF, mg/L | 1.935 | 1.935 | 1.935 | 1.935 | 1998 Producers Price Index (PPI base year 1967 = 100)
E-Mail Address (optional) |  | Design flux, FW (gfd) | 16.5 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) | 36 |  |  |  | Calcium hardness | mg/L as CaCO3 | 15.1 | 15.3 | 15.2 | 1.3158 | 1999-01-13 | 8:00 | 23 | 23.6 | 51 | 52 | 600 | 7.5 | 3.1 | 10.6 | 0.46109 | 0.70755 | 55.6038 | 17.0842 | 16.4401 | 2.4968 | 0.098671 | 2.4668 | 0.023831 | 51.4762 | 0.31937 | 1999-01-15 | 9:00 | 23 | 23.1 | 52 | 52 | 600 | 5.7 | 2.4 |  | 8.1 | 0.46109 | 0.7037 | 73.0741 | 12.984 | 12.6805 | 276.1575 | 34.71 | 273.8638 | 2.403 | 49.597 | 0.25567 | [27 empty] | pH | --- | 6.29 | 6.33 | 6.31 | 0.63391 | 6.44 | --- | --- | --- | --- | --- | pH | --- | 6.21 | 6.57 | --- | --- | --- | --- | --- | pH | --- | 6.17 | 6.25 | --- | --- | --- | --- | --- | pH | --- | 5.83 | 6.15 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.27 | 0.2 | 0.19 | 0.24 | SDS-CDp, mg/L | 0.27 | 0.2 | 0.19 | 0.24 | Labor Rate + Fringe ($/work-hour) | 30.83
|  | Net driving pressure at the design flux, NDP (psi) | 70 | 1 | 0.7 | 16.5 | 3.4344 | 79.4804 | 606.4586 | 7.2428 | 10.3468 | 3.104 | Calcium (mg/L) | 6.4 |  |  |  | Turbidity | ntu | 0.1 | 0.14 | 0.12 | 33.3333 | 1999-01-13 | 10:00 | 25 | 24.2 | 51 | 52 | 600 | 7.5 | 3.5 | 11 | 0.46109 | 0.68182 | 53.5455 | 17.0842 | 16.1511 | 2.318 | 0.091606 | 2.2902 | 0.022125 | 51.4779 | 0.31375 | 1999-01-15 | 11:00 | 25 | 23.5 | 52 | 52 | 600 | 5.7 | 2.4 |  | 8.1 | 0.46109 | 0.7037 | 73.0741 | 12.984 | 12.5315 | 276.1575 | 34.71 | 273.8638 | 2.403 | 49.597 | 0.25267 | 6.31 | 6.55 | 6.64 | 33 | 106.6 | 270 | 280.2188 | -3.7847 | 68.9412 | 279.0445 | 88.1739 | 0.003 | 0.057 | 0.188 | 0.1785 | 5.0532 | 94.5455 | 0.17767 | 98.3114 | [8 empty] | Temperature | oC | 22.1 | 22.3 | 22.2 | 0.9009 | 21.8 | --- | --- | --- | --- | --- | Temperature | oC | 20.9 | 20.4 | --- | --- | --- | --- | --- | Temperature | oC | 22.1 | 22.3 | --- | --- | --- | --- | --- | Temperature | oC | 21.5 | 21.7 | --- | --- | --- | --- | --- | TOCF, mg/L | 3.2 | 3.2 | 3.2 | 3.2 | TOCF, mg/L | 3.2 | 3.2 | 3.2 | 3.2 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.235 | 2 | 0.9 | 16.5 | 10.2184 | 86.2644 | 606.4586 | 7.2428 | 8.0475 | 0.80475 | Barium (mg/L) | 0.052 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-01-13 | 12:00 | 27 | 23.7 | 51 | 52 | 600 | 7.4 | 3.2 | 10.6 | 0.46109 | 0.69811 | 55.6038 | 16.8564 | 16.1731 | 2.4281 | 0.095972 | 2.3993 | 0.023177 | 51.4768 | 0.31418 | 1999-01-15 | 13:00 | 27 | 23.8 | 52 | 52 | 600 | 5.8 | 2.4 |  | 8.2 | 0.46109 | 0.70732 | 72.1707 | 13.2118 | 12.6388 | 278.4534 | 34.9934 | 276.1 | 2.4228 | 49.5772 | 0.25493 | [27 empty] | Alkalinity | mg/L as CaCO3 | 2 | 1.5 | 1.75 | 28.5714 | 4.5 | 3.4167 | 24.0741 | 22.2222 | 3.409 | 48.6651 | Alkalinity | mg/L as CaCO3 | 2 | 5 | 4.5 | 10 | 11.1111 | 4.4887 | 55.4436 | Alkalinity | mg/L as CaCO3 | 0.5 | 3.5 | 4.0714 | -16.3265 | 77.7778 | 4.0547 | 87.6687 | Alkalinity | mg/L as CaCO3 | 0.5 | 2.5 | 3 | -20 | 77.7778 | 2.9882 | 83.2674 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.06
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 16.5 | 2.0776 | 78.1236 | 606.4586 | 7.2428 | 14.4855 | 7.2428 | Strontium (mg/L) | 0.077 |  |  |  | Total organic carbon | mg/L | 3.2 | 3.2 | 3.2 | 0 | 1999-01-13 | 15:00 | 30 | 24.1 | 51 | 52 | 600 | 7.4 | 3.2 | 10.6 | 0.46109 | 0.69811 | 55.6038 | 16.8564 | 15.983 | 2.4281 | 0.095972 | 2.3993 | 0.023177 | 51.4768 | 0.31049 | 1999-01-15 | 15:00 | 29 | 23.9 | 52 | 53 | 600 | 6 | 2.5 |  | 8.5 | 0.46109 | 0.70588 | 69.5882 | 13.6673 | 13.036 | 277.5599 | 34.8709 | 275.133 | 2.4148 | 50.0852 | 0.26028 | [27 empty] | Total dissolved solids | mg/L | 31.9 | 32.2 | 32.05 | 0.93604 | 257 | 279.3833 | -8.7095 | 69.8353 | 278.2435 | 88.4813 | Total dissolved solids | mg/L | 40.6 | 560 | 697.1 | -24.4821 | 61.7882 | 694.131 | 94.151 | Total dissolved solids | mg/L | 26.2 | 181 | 189.5673 | -4.7333 | 75.3412 | 188.8036 | 86.1231 | Total dissolved solids | mg/L | 24.3 | 135.8 | 141.3714 | -4.1027 | 77.1294 | 140.8183 | 82.7437 | UV254 F, cm-1 | 0.055 | 0.055 | 0.055 | 0.055 | UV254 F, cm-1 | 0.055 | 0.055 | 0.055 | 0.055 | Fuel Oil Rate ($/gal) | 1.2
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 16.5 | 1.4961 | 77.5422 | 606.4586 | 7.2428 | 24.1425 | 16.8998 | Reactive silica (mg/L as SiO2) | 12 |  |  |  | UV254 | cm-1 | 0.055 | 0.055 | 0.055 | 0 | 1//13/99 | 17:00 | 32 | 24.4 | 51 | 52 | 600 | 7.5 | 3.2 | 10.7 | 0.46109 | 0.70093 | 55.0748 | 17.0842 | 16.0559 | 2.4482 | 0.096754 | 2.4188 | 0.023368 | 51.4766 | 0.31191 | 1999-01-15 | 17:00 | 31 | 23.9 | 53 | 53 | 600 | 6 | 2.5 |  | 8.5 | 0.46109 | 0.70588 | 69.5882 | 13.6673 | 13.036 | 277.5599 | 34.8709 | 275.133 | 2.4148 | 50.5852 | 0.2577 | 6.3 |  |  | 33.5 |  |  | 280.85 |  | 68.4706 | 279.6132 | 88.0192 | 0.003 |  |  | 0.1798 |  | 94.5455 | 0.17892 | 98.3232 | [8 empty] | Total hardness | mg/L as CaCO3 | 2 | 1.7 | 1.85 | 16.2162 | 72.5 | 74.6833 | -3.0115 | 92.1941 | 74.3477 | 97.5117 | Total hardness | mg/L as CaCO3 | 2.2 | 225.1 | 217.2 | 3.5096 | 90.7173 | 216.2277 | 98.9826 | Total hardness | mg/L as CaCO3 | 1.9 | 47.1 | 46.3898 | 1.5079 | 91.9831 | 46.1818 | 95.8858 | Total hardness | mg/L as CaCO3 | 1.7 | 31.1 | 33.1286 | -6.5227 | 92.827 | 32.9801 | 94.8454 | UV254 p, cm-1 | 0.002 | 0.004 | 0.003 | 0.001 | UV254 p, cm-1 | 0.002 | 0.004 | 0.003 | 0.001 | Natural Gas Rate ($/ft3) | 0.007
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 700 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) | 0.15 |  |  |  | SUVA | L/(mg*m) | 1.7188 | 1.7188 | 1.7188 | 0 | 1999-01-14 | 8:00 | 47 | 21.9 | 51 | 52 | 600 | 7 | 3.1 | 10.1 | 0.46109 | 0.69307 | 58.4059 | 15.9452 | 16.1349 | 2.3928 | 0.094638 | 2.3659 | 0.022847 | 51.4772 | 0.31344 | 1999-01-16 | 7:00 | 45 | 24 | 52 | 52 | 600 | 6.2 | 2.5 |  | 8.7 | 0.46109 | 0.71264 | 67.9655 | 14.1229 | 13.4308 | 281.9334 | 35.4099 | 279.386 | 2.4525 | 49.5475 | 0.27107 | 6.32 |  |  | 32.8 |  |  | 288.406 |  | 69.1294 | 287.0854 | 88.5748 | 0.003 |  |  | 0.18396 |  | 94.5455 | 0.18303 | 98.3609 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 1 | 0.9 | 0.95 | 10.5263 | 44.4 | 48.45 | -9.1216 | 93.75 | 48.2311 | 98.0303 | Calcium hardness | mg/L as CaCO3 | 1.4 | 146.3 | 139.4 | 4.7163 | 90.7895 | 138.7759 | 98.9912 | Calcium hardness | mg/L as CaCO3 | 1.3 | 30.2 | 29.6673 | 1.7638 | 91.4474 | 29.5347 | 95.5984 | Calcium hardness | mg/L as CaCO3 | 1 | 21.3 | 21.2857 | 0.067069 | 93.4211 | 21.1899 | 95.2808 | BromideF, ug/L | 53 | 53 | 53 | 53 | BromideF, ug/L | 53 | 53 | 53 | 53 | Current Process Water Rate ($/1000 gal) | 0.12
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  |  | Bromide | mg/L | 52 | 54 | 53 | 3.7736 | 1999-01-14 | 10:00 | 49 | 22.4 | 51 | 52 | 6000 | 7 | 3.2 | 10.2 | 4.6109 | 0.68627 | 587.2353 | 15.9452 | 15.8982 | 2.345 | 0.093696 | 2.3424 | 0.0225 | 51.4775 | 0.30884 | 1999-01-16 | 9:00 | 47 | 24.5 | 52 | 52 | 600 | 6.2 | 2.4 |  | 8.6 | 0.46109 | 0.72093 | 68.7674 | 14.1229 | 13.2337 | 287.4603 | 36.1041 | 284.863 | 2.5006 | 49.4994 | 0.26735 | [27 empty] | Turbidity | ntu | 0.07 | 0.07 | 0.07 | 0 | 0.1 | 0.23667 | -136.6667 | 41.6667 | 0.2359 | 70.3262 | Turbidity | ntu | 0.06 | 0.16 | 0.66 | -312.5 | 50 | 0.65729 | 90.8716 | Turbidity | ntu | 0.08 | 0.11 | 0.16163 | -46.9388 | 33.3333 | 0.16125 | 50.3879 | Turbidity | ntu | 0.1 | 0.12 | 0.12857 | -7.1429 | 16.6667 | 0.12844 | 22.1405 | Bromidep, ug/L | 53 | 56 | 47 | 46 | Bromidep, ug/L | 53 | 56 | 47 | 46 | Modifications to Existing Plant (% of construction costs) | 25
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 34 | [9 empty] | MFI |  |  |  |  | SDS-Cl2 dose | mg/L | 4.5 | 3.8 | 4.15 | 16.8675 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 11:00 | 49 | 24.3 | 52 | 52 | 600 | 6.2 | 2.7 |  | 8.9 | 0.46109 | 0.69663 | 66.4157 | 14.1229 | 13.3122 | 271.8329 | 34.1413 | 269.3768 | 2.3646 | 49.6354 | 0.2682 | 6.31 | 6.6 | 6.74 | 33.7 | 107.2 | 253 | 272.8463 | -7.8444 | 68.2824 | 271.6107 | 87.5925 | 0.003 | 0.056 | 0.164 | 0.17441 | -6.346 | 94.5455 | 0.17352 | 98.2711 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | BMRL | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | BMRL | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25 | AlkF, mg/L CaCO3 | 2.25 | 2.25 | 2.25 | 2.25
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.67 | [9 empty] | Total Hardness (mg/L as CaCO3) | 25.4 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 2.5 | 1.93 | 2.215 | 25.7336 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 13:00 | 51 | 24.4 | 52 | 52 | 600 | 6.2 | 2.7 |  | 8.9 | 0.46109 | 0.69663 | 66.4157 | 14.1229 | 13.2729 | 271.8329 | 34.1413 | 269.3768 | 2.3646 | 49.6354 | 0.26741 | [27 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 10 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 14.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 1.75 | 2 | 0.5 | 0.5 | Alkp, mg/L CaCO3 | 1.75 | 2 | 0.5 | 0.5
Plant Name | Beaumont Water Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023 | [9 empty] | pH | 5.36 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 2 | 1.87 | 1.935 | 6.7183 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 15:00 | 53 | 24.8 | 52 | 52 | 600 | 6.1 | 2.8 |  | 8.9 | 0.46109 | 0.68539 | 66.4157 | 13.8951 | 12.9053 | 265.1593 | 33.308 | 262.8021 | 2.3067 | 49.6933 | 0.2597 | [27 empty] | UV254 | cm-1 | 0.002 | 0.002 | 0.002 | 0 | 0.177 | 0.17867 | -0.94162 | 96.3636 | 0.17785 | 98.8755 | UV254 | cm-1 | 0.004 | 0.482 | 0.514 | -6.639 | 92.7273 | 0.51169 | 99.2183 | UV254 | cm-1 | 0.003 | 0.109 | 0.10912 | -0.11234 | 94.5455 | 0.10863 | 97.2382 | UV254 | cm-1 | 0.001 | 0.078 | 0.078143 | -0.18315 | 98.1818 | 0.077778 | 98.7143 | T-HdF, mg/L CaCO3 | 23.7 | 23.7 | 23.7 | 23.7 | T-HdF, mg/L CaCO3 | 23.7 | 23.7 | 23.7 | 23.7
Treatment Plant Category | CONV | [11 empty] | Ammonia (mg/L) | BMRL | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 11.6 | 11.6 | 11.6 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-16 | 17:00 | 55 | 23.4 | 52 | 52 | 600 | 6.1 | 2.8 |  | 8.9 | 0.46109 | 0.68539 | 66.4157 | 13.8951 | 13.4506 | 265.1593 | 33.308 | 262.8021 | 2.3067 | 49.6933 | 0.27067 | 6.37 |  |  | 31.2 |  |  | 269.7518 |  | 70.6353 | 268.5391 | 88.3816 | 0.003 |  |  | 0.16829 |  | 94.5455 | 0.16745 | 98.2084 | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.77 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.3241 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.7581 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.7931 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 1.85 | 2.2 | 1.9 | 1.7 | T-Hdp, mg/L CaCO3 | 1.85 | 2.2 | 1.9 | 1.7
Process Train Name | Conventional Train | Additional Information | [10 empty] | TOC (mg/L) | 3.1 |  |  |  | SDS-Chlorination pH | --- | 8.11 | 8.06 | 8.085 | 0.61843 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 7:00 | 69 | 20.3 | 52 | 52 | 600 | 5.4 | 2.8 |  | 8.2 | 0.46109 | 0.65854 | 72.1707 | 12.3006 | 13.0497 | 250.4297 | 31.4902 | 248.4592 | 2.1795 | 49.8205 | 0.26193 | 6.29 |  |  | 30.8 |  |  | 251.7607 |  | 71.0118 | 250.7664 | 87.7177 | 0.002 |  |  | 0.15721 |  | 96.3636 | 0.15652 | 98.7222 | [8 empty] | Bromide | mg/L | 53 | 53 | 53 | 0 | --- | 53 | --- | 0 | 53 | 0 | Bromide | mg/L | 56 | --- | 26 | --- | -5.6604 | 26.1357 | -114.2665 | Bromide | mg/L | 47 | --- | 59.2449 | --- | 11.3208 | 59.1877 | 20.5915 | Bromide | mg/L | 46 | --- | 56 | --- | 13.2075 | 55.9528 | 17.7878 | Ca-HdF, mg/L CaCO3 | 15.2 | 15.2 | 15.2 | 15.2 | Ca-HdF, mg/L CaCO3 | 15.2 | 15.2 | 15.2 | 15.2
ICR Treatment Plant Identification Number | 636 | Design cross-flow velocity (fps) | [10 empty] | UV254 (cm-1) | 0.055 |  |  |  | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 9:00 | 71 | 20.5 | 53 | 54 | 600 | 5.4 | 2.4 |  | 7.8 | 0.46109 | 0.69231 | 75.9231 | 12.3006 | 12.9728 | 269.1602 | 33.8454 | 267.0424 | 2.3426 | 51.1574 | 0.25359 | [27 empty] | SDS-Cl2 dose | mg/L | 2 | 2 | 2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 0.95 | 1.4 | 1.3 | 1 | Ca-Hdp, mg/L CaCO3 | 0.95 | 1.4 | 1.3 | 1
PWSID Number of Plant (if assigned) | TX1230001 | Required influent flow to permeate flow rate ratio, QI:Qp | [10 empty] | Bromide (ug/L) | 51 |  |  |  | SDS-TOX | mg Cl- /L | 185 | 160 | 172.5 | 14.4928 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 11:00 | 73 | 20.4 | 53 | 54 | 600 | 5.5 | 2.4 |  | 7.9 | 0.46109 | 0.6962 | 74.9494 | 12.5284 | 13.2521 | 271.5112 | 34.136 | 269.3352 | 2.3629 | 51.1371 | 0.25915 | 6.35 | 6.5 | 6.71 | 31 | 105.5 | 257 | 278.6979 | -8.4428 | 70.8235 | 277.5626 | 88.8313 | 0.002 | 0.055 | 0.173 | 0.17646 | -1.999 | 96.3636 | 0.17566 | 98.8614 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.75 | 1.71 | 1.73 | 2.3121 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.8 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.81 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.76 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 10 | Maximum element recovery (%) | 15 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | SDS-CHCl3 | mg/L | 34.08 | 29.3 | 31.69 | 15.0836 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 13:00 | 75 | 21.6 | 53 | 54 | 600 | 5.5 | 2.5 |  | 8 | 0.46109 | 0.6875 | 74 | 12.5284 | 12.7903 | 266.333 | 33.485 | 264.1985 | 2.3178 | 51.1822 | 0.2499 | [27 empty] | SDS-Cl2 demand | mg/L | 0.25 | 0.29 | 0.27 | 14.8148 | --- | 5.82 | --- | 86.0465 | 5.7944 | 95.3403 | SDS-Cl2 demand | mg/L | 0.2 | --- | 17.55 | --- | 89.6641 | 17.4715 | 98.8553 | SDS-Cl2 demand | mg/L | 0.19 | --- | 3.7512 | --- | 90.1809 | 3.7346 | 94.9124 | SDS-Cl2 demand | mg/L | 0.24 | --- | 2.6614 | --- | 87.5969 | 2.65 | 90.9434 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 22.3 (1996-97) | Variability of design flux (%) | [10 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | SDS-BDCM | mg/L | 12 | 13.34 | 12.67 | 10.5762 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 15:00 | 77 | 21.7 | 53 | 54 | 600 | 5.6 | 2.5 |  | 8.1 | 0.46109 | 0.69136 | 73.0741 | 12.7562 | 12.9844 | 268.6127 | 33.7667 | 266.4208 | 2.3375 | 51.1625 | 0.25379 | 6.21 |  |  | 32.4 |  |  | 271.674 |  | 69.5059 | 270.5574 | 88.0247 | 0.003 |  |  | 0.17148 |  | 94.5455 | 0.17069 | 98.2425 | [8 empty] | SDS-Chlorination temp. | oC | 11.6 | 11.6 | 11.6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 11.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 11.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 11.6 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | -52.1487 | -56.6659 | -50.8485 | -50.8485 | Qp/QT (THM4), % | 25.2041 | 27.3873 | 24.5757 | 24.5757
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 45% rejection of CaCl2; 70 psi, 500mg/L CaCl2, 25 degrees C, 15%recovery | [14 empty] | SDS-DBCM | mg/L | 3 | 3.74 | 3.37 | 21.9585 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-17 | 16:00 | 78 | 22 | 53 | 54 | 600 | 5.6 | 2.5 |  | 8.1 | 0.46109 | 0.69136 | 73.0741 | 12.7562 | 12.8698 | 268.6127 | 33.7667 | 266.4208 | 2.3375 | 51.1625 | 0.25155 | [27 empty] | SDS-Chlorination pH | --- | 8.03 | 8.09 | 8.06 | 0.74442 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.05 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.04 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.02 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | [15 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 8:00 | 94 | 21.4 | 53 | 54 | 600 | 5.7 | 0.63 |  | 6.33 | 0.46109 | 0.90047 | 93.7867 | 12.984 | 13.334 | 499.5161 | 62.7837 | 495.3671 | 4.3466 | 49.1534 | 0.27127 | [27 empty] | SDS-Incubation time | hours | 6 | 6 | 6 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 6 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 23.4934 | 23.2212 | 23.6908 | 23.6908
|  | Variability of rejection of reference solute (%) | 45 | [14 empty] | SDS-THM4 | mg/L | 49.08 | 46.38 | 47.73 | 5.6568 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 9:00 | 95 | 21.3 | 53 | 54 | 600 | 5.5 | 0.63 |  | 6.13 | 0.46109 | 0.89723 | 96.8793 | 12.5284 | 12.9043 | 492.8609 | 61.9655 | 488.911 | 4.2892 | 49.2108 | 0.26222 | 5.68 |  |  | 37.5 |  |  | 706.4484 |  | 64.7059 | 703.3824 | 94.6686 | 0.002 |  |  | 0.5177 |  | 96.3636 | 0.51533 | 99.6119 | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | 56 | --- | 222.4286 | --- | 67.5362 | 221.6422 | 74.7341 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | 143.8693
|  | Standard testing recovery (%) | [15 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 10:00 | 96 | 21.5 | 53 | 53 | 600 | 5.3 | 0.63 |  | 5.93 | 0.46109 | 0.89376 | 100.1804 | 12.0728 | 12.3617 | 485.9552 | 61.1152 | 482.2024 | 4.2296 | 48.7704 | 0.25347 | 5.88 |  |  | 39.1 |  |  | 671.1627 |  | 63.2 | 668.3711 | 94.15 | 0.004 |  |  | 0.48405 |  | 92.7273 | 0.48193 | 99.17 | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.5154 | 1.4598 | 1.5062 | 1.5184
|  | Standard testing pH | [15 empty] | SDS-DCAA* | mg/L | 15.72 | 17.55 | 16.635 | 11.0009 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 11:00 | 97 | 21.4 | 53 | 54 | 600 | 5.5 | 0.63 |  | 6.13 | 0.46109 | 0.89723 | 96.8793 | 12.5284 | 12.8662 | 492.8609 | 61.9655 | 488.911 | 4.2892 | 49.2108 | 0.26145 | 5.95 |  |  | 39.6 |  |  | 688.1151 |  | 62.7294 | 685.1427 | 94.2202 | 0.003 |  |  | 0.50897 |  | 94.5455 | 0.50665 | 99.4079 | [8 empty] | SDS-BDCM | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BDCM | mg/L | 1.3 | --- | 115 | --- | 89.7395 | 114.4858 | 98.8645 | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BDCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 0 to 600 psi | [14 empty] | SDS-TCAA* | mg/L | 12.28 | 14.72 | 13.5 | 18.0741 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 12:00 | 98 | 21.5 | 53 | 54 | 600 | 5.4 | 0.63 |  | 6.03 | 0.46109 | 0.89552 | 98.5025 | 12.3006 | 12.5949 | 489.4402 | 61.5445 | 485.5892 | 4.2597 | 49.2403 | 0.25579 | 6.02 | 6.02 | 6.37 | 39.5 | 105.6 | 480 | 678.3929 | -41.3318 | 62.8235 | 675.5178 | 94.1526 | 0.003 | 0.056 | 0.4 | 0.50071 | -25.1786 | 94.5455 | 0.49847 | 99.3982 | [8 empty] | SDS-DBCM | mg/L | 1.22 | 1.16 | 1.19 | 5.042 | --- | 8.4567 | --- | 64.6884 | 8.4232 | 85.8723 | SDS-DBCM | mg/L | 2.24 | --- | 13.54 | --- | 33.5312 | 13.4889 | 83.3937 | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBCM | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.041642 | 0.041032 | 0.042221 | 0.041729
|  | Acceptable range of operating pH values | 3 to 10 | [14 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-18 | 16:00 | 102 | 21.9 | 54 | 54 | 600 | 5.5 | 0.63 |  | 6.13 | 0.46109 | 0.89723 | 96.8793 | 12.5284 | 12.6774 | 492.8609 | 61.9655 | 488.911 | 4.2892 | 49.7108 | 0.25502 | [27 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.36 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 53 | 53.8216 | 51.5255 | 51.2797
|  | Typical pressure drop across a single element (psi) | [15 empty] | SDS-DBAA* | mg/L | 1.13 | 1.42 | 1.275 | 22.7451 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 8:00 | 118 | 20.8 | 54 | 54 | 600 | 5.3 | 5.9 |  | 11.2 | 0.46109 | 0.47321 | 52.5714 | 12.0728 | 12.6202 | 181.2216 | 22.791 | 179.8222 | 1.5773 | 52.4227 | 0.24074 | [27 empty] | SDS-THM4 | mg/L | 1.22 | 1.16 | 1.19 | 5.042 | --- | 156.3233 | --- | 97.5068 | 155.6084 | 99.2353 | SDS-THM4 | mg/L | 4.9 | --- | 433.2 | --- | 89.7339 | 431.263 | 98.8638 | SDS-THM4 | mg/L | 0 | --- | 97.4082 | --- | 100 | 96.9528 | 100 | SDS-THM4 | mg/L | 0 | --- | 68.1857 | --- | 100 | 67.8635 | 100 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 2.124 | 2.1815 | 1.8199 | 1.8199
|  | Maximum permissible SDI | 5 | [14 empty] | SDS-BCAA* | mg/L | 4.86 | 6.26 | 5.56 | 25.1799 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 9:00 | 119 | 20.6 | 54 | 54 | 600 | 5.4 | 5.4 |  | 10.8 | 0.46109 | 0.5 | 54.5556 | 12.3006 | 12.9345 | 188.764 | 23.736 | 187.2787 | 1.6429 | 52.3571 | 0.24704 | 5.89 |  |  | 25.9 |  |  | 186.6 |  | 75.6235 | 185.8768 | 86.066 | 0.001 |  |  | 0.109 |  | 98.1818 | 0.10851 | 99.0785 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 18.1929 | 17.8117 | 18.3425 | 18.2933
|  | Maximum permissible turbidity (ntu) | 1 | [14 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 10:00 | 120 | 20.6 | 54 | 54 | 600 | 5.4 | 5.4 |  | 10.8 | 0.46109 | 0.5 | 54.5556 | 12.3006 | 12.9345 | 188.764 | 23.736 | 187.2787 | 1.6429 | 52.3571 | 0.24704 | 5.96 |  |  | 25.6 |  |  | 186.9 |  | 75.9059 | 186.1741 | 86.2494 | 0.002 |  |  | 0.108 |  | 96.3636 | 0.10752 | 98.1399 | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 11.6084 | 11.4205 | 11.784 | 11.7102
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | <0.1 ppm | [14 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 11:00 | 121 | 20.6 | 54 | 54 | 600 | 5.5 | 5.4 |  | 10.9 | 0.46109 | 0.50459 | 54.0459 | 12.5284 | 13.174 | 190.1217 | 23.9033 | 188.598 | 1.6546 | 52.3454 | 0.25167 | 5.9 |  |  | 25.6 |  |  | 188.3935 |  | 75.9059 | 187.6474 | 86.3574 | 0.001 |  |  | 0.11 |  | 98.1818 | 0.1095 | 99.0868 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [15 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 12:00 | 122 | 21 | 54 | 54 | 600 | 5.6 | 5.4 |  | 11 | 0.46109 | 0.50909 | 53.5455 | 12.7562 | 13.2559 | 191.474 | 24.0697 | 189.9115 | 1.6662 | 52.3338 | 0.2533 | 5.94 | 6.46 | 6.43 | 25.7 | 106.7 | 183 | 189.7833 | -3.7067 | 75.8118 | 189.0176 | 86.4034 | 0.002 | 0.056 | 0.11 | 0.10996 | 0.03367 | 96.3636 | 0.10946 | 98.1728 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [15 empty] | SDS-HAA5 | mg/L | 29.13 | 33.69 | 31.41 | 14.5177 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-19 | 16:00 | 126 | 21.3 | 54 | 55 | 600 | 5.7 | 5.8 |  | 11.5 | 0.46109 | 0.49565 | 51.1739 | 12.984 | 13.3735 | 187.5069 | 23.5676 | 185.9494 | 1.6316 | 52.8684 | 0.25296 | [27 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.51 | --- | -0.84 | --- | -18.4314 | -0.82937 | 282.0654 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[18 empty] | SDS-HAA6 | mg/L | 33.99 | 39.95 | 36.97 | 16.1212 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 8:00 | 142 | 21 | 53 | 54 | 600 | 5.7 | 13 |  | 18.7 | 0.46109 | 0.30481 | 31.0856 | 12.984 | 13.4926 | 144.8537 | 18.2065 | 143.6505 | 1.2605 | 52.2395 | 0.25828 | [27 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.13 | --- | 45.43 | --- | 79.6763 | 45.2297 | 97.5016 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | -71.9198 | -75.5518 | -71.9198 | -71.9198 | Qp/QT (HAA5), % | 14.0401 | 14.7492 | 14.0401 | 14.0401
[18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 9:00 | 143 | 20.8 | 53 | 54 | 600 | 5.6 | 13.4 |  | 19 | 0.46109 | 0.29474 | 30.5789 | 12.7562 | 13.3345 | 143.1335 | 17.993 | 141.9656 | 1.2456 | 52.2544 | 0.25518 | 5.44 |  |  | 24.3 |  |  | 140.4978 |  | 77.1294 | 139.9555 | 82.6373 | 0 | [15 empty] | SDS-TBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | 41.1957 | 41.4129 | 41.0287 | 41.0287
[18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 10:00 | 144 | 20.5 | 53 | 54 | 600 | 5.6 | 13.2 |  | 18.8 | 0.46109 | 0.29787 | 30.9149 | 12.7562 | 13.4533 | 143.6641 | 18.0597 | 142.4918 | 1.2502 | 52.2498 | 0.25748 | 5.52 |  |  | 24.2 |  |  | 141.0591 |  | 77.2235 | 140.5137 | 82.7775 | 0.002 |  |  | 0.077485 |  | 96.3636 | 0.077133 | 97.4071 | [8 empty] | SDS-CDBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[18 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-01-20 | 11:00 | 145 | 21.6 | 53 | 54 | 600 | 5.7 | 13.3 |  | 19 | 0.46109 | 0.3 | 30.5789 | 12.984 | 13.2554 | 144.0274 | 18.1027 | 142.8311 | 1.2533 | 52.2467 | 0.25371 | 5.62 |  |  | 24 |  |  | 141.5 |  | 77.4118 | 140.9419 | 82.9717 | 0.002 |  |  | 0.077714 |  | 96.3636 | 0.077355 | 97.4145 | [8 empty] | SDS-DCBAA | mg/L | NA | NA | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | 156.1433
[45 empty] | 1999-01-20 | 12:00 | 146 | 20.9 | 52 | 53 | 600 | 5.6 | 13.3 |  | 18.9 | 0.46109 | 0.2963 | 30.746 | 12.7562 | 13.2951 | 143.3969 | 18.0261 | 142.2268 | 1.2479 | 51.2521 | 0.25941 | 5.77 | 5.82 | 6.03 | 23.8 | 107.3 | 137.3 | 140.9658 | -2.6699 | 77.6 | 140.419 | 83.0507 | 0.002 | 0.057 | 0.079 | 0.077316 | 2.1319 | 96.3636 | 0.076964 | 97.4014 | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 104.7 | --- | 100 | 104.2175 | 100 | SDS-HAA5 | mg/L | 1.51 | --- | 300.51 | --- | 95.1926 | 299.1578 | 99.4952 | SDS-HAA5 | mg/L | 0 | --- | 64.102 | --- | 100 | 63.8024 | 100 | SDS-HAA5 | mg/L | 0 | --- | 44.8714 | --- | 100 | 44.6594 | 100 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | 1.7012 | 1.6791 | 1.69 | 1.697
[45 empty] | 1999-01-20 | 17:30 | 151.5 | 22 | 52 | 53 | 600 | 5.9 | 13.4 |  | 19.3 | 0.46109 | 0.3057 | 30.0881 | 13.4396 | 13.5593 | 145.0092 | 18.2207 | 143.7624 | 1.2617 | 51.2383 | 0.26463 | [27 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 123.2333 | --- | 100 | 122.6654 | 100 | SDS-HAA6 | mg/L | 2.64 | --- | 345.94 | --- | 92.8591 | 344.3874 | 99.2334 | SDS-HAA6 | mg/L | 0 | --- | 75.449 | --- | 100 | 75.0963 | 100 | SDS-HAA6 | mg/L | 0 | --- | 52.8143 | --- | 100 | 52.5647 | 100 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[45 empty] | 1999-01-22 | 8:00 | 176 | 22.6 | 52 | 52 | 600 | 8.6 | 19.7 | x | 28.3 | 0.46109 | 0.30389 | 20.2014 | 19.5899 | 19.4169 | 144.7261 | 18.1128 | 142.9113 | 1.2571 | 50.7429 | 0.38265 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | 0.047559 | 0.047478 | 0.047699 | 0.047418
[45 empty] | 1999-01-22 | 10:00 | 178 | 22.4 | 52 | 52 | 600 | 8.8 | 19.9 |  | 28.7 | 0.46109 | 0.30662 | 19.9059 | 20.0454 | 19.9863 | 145.2013 | 18.1669 | 143.3381 | 1.261 | 50.739 | 0.3939 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | 53 | 53.4425 | 52.1576 | 52.0172
[45 empty] | 1999-01-22 | 12:00 | 180 | 21.4 | 52 | 52 | 600 | 8.7 | 20.8 |  | 29.5 | 0.46109 | 0.29492 | 19.339 | 19.8176 | 20.3519 | 143.1963 | 17.9187 | 141.3797 | 1.2437 | 50.7563 | 0.40097 | 5.76 | 5.93 | 6.1 | 35.4 | 105.8 | 133.5 | 135.8844 | -1.786 | 66.6824 | 135.1559 | 73.808 | 0.002 | 0.057 | 0.078 | 0.077168 | 1.0663 | 96.3636 | 0.076623 | 97.3898 | [47 empty] | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | 2.1798 | 2.2131 | 2.0043 | 2.0043
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | 20.6322 | 20.5289 | 20.6393 | 20.6112
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | 13.1993 | 13.1646 | 13.2484 | 13.2063
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Notes: |  |  |  |  | Notes:
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[55 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on R8: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R9: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R10: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R11: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R12: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R13: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R14: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R16: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R17: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on R18: C. Hill (8/26/99): This foulant was measured during quarter 3, and pasted to this quarter by the reviewer.
Note on DA29: C. Hill (8/26/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when full-scale distribution system temperatures were apparently lower than the previous year).
Note on DN29: C. Hill (8/26/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when full-scale distribution system temperatures were apparently lower than the previous year).
Note on DQ17: C. Hill (8/26/99): TDS permeate and concentrate data for Run 2 (90%) was verified by the consultant. The consultant stated that the high mass balance closure errors could have resulted from errors made in flow rate measurements (though rejections remained stable), particularly during the 90% run when waste flow rates are very low.
Note on DX29: C. Hill (8/26/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when full-scale distribution system temperatures were apparently lower than the previous year).
Note on EH29: C. Hill (8/26/99): SDS-temperature for Quarter 4 (11.6 C) is lower than the yearly minimum temperature (14.4 C) reported in the Summary Report (14.4). The consultant explained this is due to the fact the yearly minimum temperature was measured in 1998, but the sample was taken in January 1999 (when full-scale distribution system temperatures were apparently lower than the previous year).