## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Pasco County Utilities | Carbon manufacturer | Calgon Carbon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | FL6511361 | Carbon trade name | Filtrasorb 816 | mesh size | (mm) | uv disinfection system | Trojen Atvantage 5 @ 22000 uW*sec/cm2 | pilot | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 7
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 |  |  |  |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 3.3 | 6 | 3.35 |  |  |  | START | --- | 1998-03-02 | 9:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-03-02 | 9:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-03-02 | 9:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit (% of construction costs) | 15
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 147 | 8 | 2.36 |  |  |  | A-1 | N | 1998-03-03 | 9:00 | 24 | 72 | 144 | 7.39 | 0.1 | 216 | 23.5 | 239 | 233 | 0.14 | NR | 3.66 | 0.174 | 4.7541 | 6.6 | 3.2 | 3.4 | 24.5 | 7.84 | 24 | 329 | 50 | 10 | BMRL | BMRL | 60 | 16 | 25 | 73 | BMRL | BMRL | 4.5 | NA | NA | NA | 114 | 118.5 | B-1 | N | 1998-03-03 | 9:00 | 24 | 144 | 7.64 | NR | 22.9 | 0.35 | 2.04 | 0.003 | 0.14706 | 2 | 1.25 | 0.75 | 22.5 | 7.82 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 5.3 | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 5.3 | 5.3 | C-1 | N | 1998-03-03 | 9:00 | 24 | 72 | 7.75 | 0.67 | 23.3 | 0.07 | 1.66 | 0.001 | 0.060241 | 1.62 | 1.1 | 0.52 | 22.8 | 7.95 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 4.4 | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 4.4 | 4.4 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 450 | 10 | 2 |  |  |  | A-2 | N | 1998-03-10 | 12:05 | 195.0833 | 585.25 | 1170.5 | 7.45 | 0.19 | 225 | 22.7 | 210 | 213 | 0.17 | 33 | 2.88 | 0.133 | 4.6181 | 2.45 | 0.65 | 1.8 | 23.5 | 7.63 | 24 | 320 | 46 | 9.5 | BMRL | BMRL | 55.5 | 3.8 | 20 | 56 | BMRL | BMRL | 2.7 | NA | NA | NA | 79.8 | 82.5 | B-2 | N | 1998-03-10 | 12:05 | 195.0833 | 1170.5 | 7.34 | 0.17 | 22.3 | 0.16 | 1.49 | 0.062 | 4.1611 | 2.21 | 1.1 | 1.11 | 23.2 | 7.74 | 24 | 150 | 25 | 8.7 | 2.6 | BMRL | 36.3 | BMRL | 9.7 | 17 | BMRL | BMRL | 1.5 | NA | NA | NA | 26.7 | 28.2 | C-2 | N | 1998-03-10 | 12:05 | 195.0833 | 585.25 | 7.31 | 0.11 | 21 | 0.15 | BMRL | BMRL | BMRL | 1.95 | 1.67 | 0.28 | 23.7 | 7.78 | 24 | BMRL | BMRL | 1.5 | 8.7 | BMRL | 10.2 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 30
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A-3 | N | 1998-03-18 | 10:40 | 385.6667 | 1157 | 2314 | 7.34 | 0.04 | 223 | 25.1 | 258 | 187 | 0.17 | 31 | 2.98 | 0.123 | 4.1275 | 2.63 | NR | NA | NR | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B-3 | N | 1998-03-18 | 10:40 | 385.6667 | 2314 | 7.37 | 0.05 | 25.4 | 0.14 | 2 | 0.094 | 4.7 | 1.4 | NR | NA | NR | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-3 | N | 1998-03-18 | 10:40 | 385.6667 | 1157 | 7.37 | 0.08 | 25.6 | 0.2 | 1.02 | 0.04 | 3.9216 | 2.05 | NR | NA | NR | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 16 | 16 | 1.18 |  |  |  | A-4 | N | 1998-03-24 | 10:40 | 529.6667 | 1589 | 3178 | 7.4 | 0.02 | 216 | 24.4 | 255 | 224 | 0.11 | 35 | 3.26 | 0.156 | 4.7853 | 4.4 | 0.25 | 4.15 | 23.5 | 7.62 | 24 | 255 | 22 | 2.9 | BMRL | BMRL | 24.9 | BMRL | 10 | 24 | BMRL | BMRL | 2.6 | NA | NA | NA | 34 | 36.6 | B-4 | N | 1998-03-24 | 10:40 | 529.6667 | 3178 | 7.43 | 0.09 | 24.4 | 0.04 | 2.74 | 0.105 | 3.8321 | 3.15 | 1.2 | 1.95 | 23.7 | 7.61 | 24 | 175 | 13 | 3.1 | BMRL | BMRL | 16.1 | 3 | 7.8 | 20 | BMRL | BMRL | 2.7 | NA | NA | NA | 30.8 | 33.5 | C-4 | N | 1998-03-24 | 10:40 | 529.6667 | 1589 | 7.39 | 0.03 | 24.1 | 0.07 | 2.35 | 0.06 | 2.5532 | 1.8 | 0.88 | 0.92 | 24 | 7.87 | 24 | 119 | 9.2 | 3.4 | 3.1 | BMRL | 15.7 | 2.5 | 5.7 | 8.4 | BMRL | BMRL | 1.6 | NA | NA | NA | 16.6 | 18.2 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Flow rate, Q (L/hr) | 123.5 | 20 | 0.85 |  |  |  | A-5 | N | 1998-03-31 | 9:50 | 696.8333 | 2090.5 | 4181 | 7.48 | 0.08 | 229 | 25.5 | 233 | 210 | 0.25 | 29 | 3.81 | 0.123 | 3.2283 | 4.6 | 1.55 | 3.05 | 25.5 | 7.79 | 24 | 336 | 62 | 11 | BMRL | BMRL | 73 | 6.9 | 17 | 93 | BMRL | BMRL | 2.1 | NA | NA | NA | 116.9 | 119 | B-5 | N | 1998-03-31 | 9:50 | 696.8333 | 4181 | 7.46 | 0.02 | 25.8 | 0.18 | 2.38 | 0.083 | 3.4874 | 3.07 | 1.1 | 1.97 | 24.8 | 7.8 | 24 | 240 | 47 | 11 | 1.4 | BMRL | 59.4 | BMRL | 14 | 32 | BMRL | BMRL | 3.8 | NA | NA | NA | 46 | 49.8 | C-5 | N | 1998-03-31 | 9:50 | 696.8333 | 2090.5 | 7.41 | 0.01 | 26.7 | 0.15 | 1.88 | 0.077 | 4.0957 | 2.5 | 0.9 | 1.6 | 24.3 | 7.62 | 24 | 102 | 17 | 9.6 | 11 | BMRL | 37.6 | BMRL | 4.3 | 8.5 | BMRL | BMRL | 2.2 | NA | NA | NA | 12.8 | 15 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.5
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A-6 | N | 1998-04-07 | 9:40 | 864.6667 | 2594 | 5188 | 7.52 | 0.03 | 214 | 25.3 | 246 | 222 | 0.4 | 30 | 3.09 | 0.133 | 4.3042 | 5.65 | 1.55 | 4.1 | 25.2 | 7.75 | 24 | 358 | 66 | 11 | 1.1 | BMRL | 78.1 | 6.1 | 31 | 100 | BMRL | BMRL | 3.8 | NA | NA | NA | 137.1 | 140.9 | B-6 | N | 1998-04-07 | 9:40 | 864.6667 | 5188 | 7.4 | 0.01 | 25.3 | 0.41 | 2.52 | 0.121 | 4.8016 | 5.55 | 1.65 | 3.9 | 24.7 | 7.72 | 24 | na | 63 | 11 | 1.4 | BMRL | 75.4 | BMRL | 12 | 35 | BMRL | BMRL | BMRL | NA | NA | NA | 47 | 47 | C-6 | N | 1998-04-07 | 9:40 | 864.6667 | 2594 | 7.36 | 0.01 | 25.3 | 0.38 | 1.2 | 0.115 | 9.5833 | 2.5 | 0.75 | 1.75 | 25.2 | 8.07 | 24 | 119 | 24 | 9.7 | 11 | BMRL | 44.7 | BMRL | 6.5 | 13 | BMRL | BMRL | 2.4 | NA | NA | NA | 19.5 | 21.9 | Labor Rate + Fringe ($/work-hour) | 22
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A-7 | N | 1998-04-14 | 10:10 | 1033.1667 | 3099.5 | 6199 | 7.53 | 0.08 | 221 | 24.8 | 246 | 222 | 0.41 | 31 | 3.38 | 0.144 | 4.2604 | 5.5 | 2.1 | 3.4 | 24.8 | 7.85 | 24 | 346 | 84 | 11 | 1.5 | BMRL | 96.5 | 7.9 | 20 | 61 | BMRL | BMRL | 2.8 | NA | NA | NA | 88.9 | 91.7 | B-7 | N | 1998-04-14 | 10:10 | 1033.1667 | 6199 | 7.5 | 0.02 | 25.1 | 0.42 | 3.67 | 0.106 | 2.8883 | 4.8 | 1.75 | 3.05 | 24.8 | 7.78 | 24 | 246 | 66 | 11 | 1.7 | BMRL | 78.7 | 7.9 | 14 | 39 | BMRL | BMRL | 1.6 | NA | NA | NA | 60.9 | 62.5 | C-7 | N | 1998-04-14 | 10:10 | 1033.1667 | 3099.5 | 7.48 | 0.01 | 25.1 | 0.48 | 1.91 | 0.099 | 5.1832 | 2.8 | 0.95 | 1.85 | 24.7 | 7.77 | 24 | 118 | 24 | 9.7 | 11 | BMRL | 44.7 | BMRL | 5.6 | 15 | BMRL | BMRL | 2.3 | NA | NA | NA | 20.6 | 22.9 | Labor Overhead Factor (% of labor) | 130
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 4596.1227 | 50 | 0.3 |  |  |  | A-8 | N | 1998-04-21 | 9:40 | 1200.6667 | 3602 | 7204 | 7.45 | 0.027 | 221 | 25.3 | 240 | 215 | 0.43 | 28 | 3.26 | 0.129 | 3.9571 | 5.2 | 2 | 3.2 | 25.7 | 7.84 | 24 | 348 | 54 | 12 | 1.3 | BMRL | 67.3 | 19 | 26 | 43 | BMRL | BMRL | 5.3 | NA | NA | NA | 88 | 93.3 | B-8 | N | 1998-04-21 | 9:40 | 1200.6667 | 7204 | 7.45 | 0.001 | 25.2 | 0.47 | 2.55 | 0.104 | 4.0784 | 5.6 | 2.2 | 3.4 | 26 | 7.82 | 24 | 228 | 3.7 | 7.6 | 6.3 | BMRL | 17.6 | 17 | 13 | 42 | 2.6 | BMRL | 4.3 | NA | NA | NA | 74.6 | 78.9 | C-8 | N | 1998-04-21 | 9:40 | 1200.6667 | 3602 | 7.48 | 0.001 | 25.3 | 0.54 | 2.46 | 0.089 | 3.6179 | 3.15 | 1.1 | 2.05 | 25.9 | 7.85 | 24 | 125 | 26 | 11 | 7.6 | BMRL | 44.6 | 3.3 | 7.7 | 18 | BMRL | BMRL | 3.2 | NA | NA | NA | 29 | 32.2 | Electric Rate ($/kW-h) | 0.0662
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 9192.2454 | 60 | 0.25 |  |  |  | A-9 | N | 1998-04-28 | 13:00 | 1372 | 4116 | 8232 | 7.5 | 0.01 | 227 | 26 | 250 | 224 | 0.33 | 29 | 3.25 | 0.151 | 4.6462 | 5 | 1.95 | 3.05 | NR | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | B-9 | N | 1998-04-28 | 13:00 | 1372 | 8232 | 7.45 | 0.016 | 26.4 | 0.31 | 2.59 | 0.114 | 4.4015 | 5.1 | 1.54 | 3.56 | NR | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-9 | N | 1998-04-28 | 13:00 | 1372 | 4116 | 7.47 | 0 | 26.9 | 0.19 | 2.89 | 0.086 | 2.9758 | 3.85 | 1.75 | 2.1 | NR | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Fuel Oil Rate ($/gal) | 0.58
|  |  |  | 70 | 0.21 |  |  |  | A-10 | N | 1998-05-05 | 10:10 | 1537.1667 | 4611.5 | 9223 | 7.49 | 0.01 | 224 | 26.3 | 244 | 218 | 0.4 | 29 | 3.09 | 0.146 | 4.7249 | 5.82 | 1.4 | 4.42 | 23.5 | 7.94 | 24 | 314 | 55 | 12 | 1.1 | BMRL | 68.1 | 5.4 | 25 | 49 | BMRL | BMRL | 1.9 | NA | NA | NA | 79.4 | 81.3 | B-10 | N | 1998-05-05 | 10:10 | 1537.1667 | 9223 | 7.45 | 0.01 | 25.8 | 0.37 | 2.66 | 0.123 | 4.6241 | 4.44 | 1.8 | 2.64 | 23.6 | 7.81 | 24 | 243 | 46 | 9.9 | 1.3 | BMRL | 57.2 | 2.2 | 17 | 29 | BMRL | BMRL | 1.7 | NA | NA | NA | 48.2 | 49.9 | C-10 | N | 1998-05-05 | 10:10 | 1537.1667 | 4611.5 | 7.42 | 0.02 | 26.1 | 0.39 | 1.91 | 0.082 | 4.2932 | 3.8 | 1.72 | 2.08 | 23.6 | 7.82 | 24 | 130 | 36 | 11 | 9.9 | BMRL | 56.9 | BMRL | 8.7 | 16 | BMRL | BMRL | 1.8 | NA | NA | NA | 24.7 | 26.5 | Natural Gas Rate ($/ft3) | 0.006
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A-11 | N | 1998-05-12 | 9:30 | 1704.5 | 5113.5 | 10227 | 7.46 | 0.035 | 227 | 26.5 | 237 | 212 | 0.28 | 26 | 3.27 | 0.135 | 4.1284 | 7.25 | 3 | 4.25 | 23.9 | 7.86 | 24 | 381 | 52 | 11 | BMRL | BMRL | 63 | 45 | 23 | 81 | BMRL | BMRL | 1.3 | NA | NA | NA | 149 | 150.3 | B-11 | N | 1998-05-12 | 9:30 | 1704.5 | 10227 | 7.58 | 0.026 | 26.8 | 0.34 | 3. 03 | 0.113 | 3.73 | 5.8 | 3.21 | 2.59 | 24.1 | 7.81 | 24 | 266 | 42 | 11 | 1.2 | BMRL | 54.2 | 2.3 | 16 | 46 | BMRL | BMRL | 1.3 | NA | NA | NA | 64.3 | 65.6 | C-11 | N | 1998-05-12 | 9:30 | 1704.5 | 5113.5 | 7.6 | 0.005 | 27 | 0.47 | 2.02 | 0.083 | 4.1089 | 3.42 | 1.42 | 2 | 23.7 | 7.98 | 24 | 131 | 37 | 11 | 11 | BMRL | 59 | 2.7 | 8.9 | 18 | BMRL | BMRL | 1.6 | NA | NA | NA | 29.6 | 31.2 | Current Process Water Rate ($/1000 gal) | 3.5
FAX Number |  | Carbon particle diameter, d (mm) | 1.77 | [5 empty] | A-12 | Y | 1998-05-19 | 11:00 | 1874 | 5622 | 11244 | 7.525 | 0.02515 | 220.5 | 26.6 | 237.5 | 213 | 0.075 | 75 | 3.43 | 0.134 | 3.9073 | 5.63 | 2 | 3.63 | 24.5 | 7.89 | 24 | 316 | 79 | 12 | 1.35 | NR | 92.35 | NR | 22.5 | 51.5 | NR | NR | 2.65 | NA | NA | NA | 74 | 76.65 | B-12 | Y | 1998-05-19 | 11:10 | 1874.1667 | 11245 | 7.47 | 0.0145 | 26.2 | 0.08 | 3.375 | 0.1315 | 3.8963 | 4.55 | 1.145 | 3.405 | 24.5 | 7.89 | 24 | 282 | 75.5 | 12 | 1.4 | NR | 88.9 | NR | 19.5 | 38 | NR | NR | 2 | NA | NA | NA | 57.5 | 59.5 | C-12 | Y | 1998-05-19 | 11:00 | 1874 | 5622 | 7.495 | 0.03 | 27 | 0.075 | 2.35 | 0.098 | 4.1703 | 4 | 1.375 | 2.625 | 24.95 | 7.88 | 24 | 203 | 61 | 12 | 2.15 | NR | 75.15 | NR | 16 | 29.5 | NR | NR | 2.6 | NA | NA | NA | 45.5 | 48.1 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.016972 | [5 empty] | A-13 | N | 1998-05-26 | 9:00 | 2040 | 6120 | 12240 | 7.46 | 0.033 | 219 | 26.9 | 237 | 213 | 0.48 | 24 | 3.42 | 0.131 | 3.8304 | 5.1 | 1.95 | 3.15 | 24.9 | 7.88 | 24 | 358 | 125 | 11 | 1.2 | BMRL | 137.2 | 2.1 | 25 | 45 | BMRL | BMRL | 3.3 | NA | NA | NA | 72.1 | 75.4 | B-13 | N | 1998-05-26 | 9:00 | 2040 | 12240 | 7.45 | 0.016 | 27.9 | 0.26 | 2.68 | 0.103 | 3.8433 | 4.76 | 1.84 | 2.92 | 25 | 8 | 24 | 267 | 68 | 10 | 1.9 | BMRL | 79.9 | BMRL | 20 | 40 | BMRL | BMRL | 3.3 | NA | NA | NA | 60 | 63.3 | C-13 | N | 1998-05-26 | 9:00 | 2040 | 6120 | 7.46 | 0.012 | 28.4 | 0.41 | 2.24 | 0.088 | 3.9286 | 3.84 | 1.46 | 2.38 | 24.9 | 7.9 | 24 | 174 | 52 | 11 | 10 | BMRL | 73 | 4 | 14 | 21 | BMRL | BMRL | 2.8 | NA | NA | NA | 39 | 41.8
|  | Hydraulic loading rate1, v (m/hr) | 7.2768 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A-14 | Y | 1998-06-02 | 10:00 | 2209 | 6627 | 13254 | 7.43 | 0.0155 | 220 | 27.3 | 213 | 207 | 0.215 | 24 | 3.87 | 0.1315 | 3.3981 | 5.1 | 1.275 | 3.825 | 25.15 | 7.87 | 24 | 366 | 67 | 11 | 1 | NR | 78.5 | NR | 22 | 43 | NR | NR | 2.65 | NA | NA | NA | 65 | 67.65 | B-14 | Y | 1998-06-02 | 10:00 | 2209 | 13254 | 7.46 | 0.0145 | 27.3 | 0.205 | 2.875 | 0.112 | 3.8958 | 4.49 | 1.5 | 2.99 | 24.95 | 7.935 | 24 | 296.5 | 60 | 12 | 1.9 | NR | 73.9 | NR | 19 | 34 | NR | NR | 3.7 | NA | NA | NA | 53 | 56.7 | C-14 | Y | 1998-06-02 | 10:00 | 2209 | 6627 | 7.475 | 0.001 | 27.7 | 0.38 | 2.375 | 0.089 | 3.7473 | 3.375 | 0.875 | 2.5 | 25.05 | 7.86 | 24 | 193 | 40 | 11.5 | 7.7 | NR | 59.2 | NR | 14 | 18 | NR | NR | 3.75 | NA | NA | NA | 32 | 35.75
Plant Name | Little Road Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A-15 | Y | 1998-06-09 | 12:00 | 2379 | 7137 | 14274 | 7.585 | 0.162 | 229 | 27.3 | 247.5 | 221 | 0.17 | 22 | 3.165 | 0.1455 | 4.6037 | 5.025 | 1.79 | 3.235 | 24.45 | 7.97 | 24 | 355.5 | 81.5 | 12.5 | 1.15 | NR | 95.15 | NR | 23 | 43 | NR | NR | 1.4 | NA | NA | NA | 66 | 67.4 | B-15 | Y | 1998-06-09 | 12:00 | 2379 | 14274 | 7.465 | 0.31 | 28.1 | 0.14 | 2.895 | 0.126 | 4.353 | 4.88 | 1.67 | 3.21 | 24.55 | 7.89 | 24 | 299.5 | 53 | 11.5 | 1.4 | NR | 65.9 | NR | 19.5 | 32.5 | NR | NR | 1.45 | NA | NA | NA | 52 | 53.45 | C-15 | Y | 1998-06-09 | 12:00 | 2379 | 7137 | 7.45 | 0.29 | 28.7 | 0.105 | 2.12 | 0.098 | 4.6236 | 3.77 | 1.32 | 2.45 | 24.6 | 7.895 | 24 | 198 | 38 | 11 | 6.8 | NR | 55.8 | NR | 14 | 20 | NR | NR | 1.55 | NA | NA | NA | 34 | 35.55
Treatment Plant Category | Other Ground Water |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A-16 | N | 1998-06-16 | 11:15 | 2546.25 | 7638.75 | 15277.5 | 7.61 | 0.18 | 228 | 27.8 | 242 | 216 | 0.51 | 26 | 3.19 | 0.141 | 4.4201 | 4.7 | 1.42 | 3.28 | 24 | 7.99 | 24 | 318 | 67 | 11 | 1.2 | BMRL | 79.2 | BMRL | 23 | 37 | BMRL | BMRL | 1.4 | NA | NA | NA | 60 | 61.4 | B-16 | N | 1998-06-16 | 11:15 | 2546.25 | 15277.5 | 7.44 | 0.23 | 28.7 | 0.57 | 2.76 | 0.117 | 4.2391 | 4.34 | 1.65 | 2.69 | 24.3 | 7.96 | 24 | 224 | 55 | 12 | 2.2 | BMRL | 69.2 | BMRL | 19 | 29 | BMRL | BMRL | 1.6 | NA | NA | NA | 48 | 49.6 | C-16 | N | 1998-06-16 | 11:15 | 2546.25 | 7638.75 | 7.45 | 0.23 | 29.8 | 0.48 | 2.4 | 0.092 | 3.8333 | 3.56 | 1.15 | 2.41 | 24.1 | 7.9 | 24 | 153 | 41 | 12 | 12 | BMRL | 65 | BMRL | 14 | 17 | BMRL | BMRL | 1.7 | NA | NA | NA | 31 | 32.7
Process Train Name | Air Stripping / Dis / pH add | 10-Minute EBCT Run | [117 empty] | 0 | 0
ICR Treatment Plant Identification Number | 315 | Empty bed contact time, EBCT (min) | 10
PWSID Number of Plant (if assigned) | NA | Estimated run time, t (days) | 63.835
Historical Minimum Water Temperature (oC) | 17 | Pilot column bed length, l (m) | 1.2128
Historical Average Water Temperature (oC) | 20 | Mass GAC required, m (kg) | 9.2625
State Approved Plant Capacity (MGD) | 20.2
20-Minute EBCT Run
|  | Empty bed contact time, EBCT (min) | 20
|  | Estimated run time, t (days) | 127.6701
|  | Pilot column bed length, l (m) | 2.4256 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 18.525 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A-12 | Primary | 1998-05-19 | 11:00 | 1874 | 5622 | 11244 | 7.54 | 0.037 | 220 | 26.6 | 240 | 215 | 0.07 | 7 | 3.4 | 0.135 | 3.9706 | 5.56 | 1.95 | 3.61 | 24.5 | 7.88 | 24 | 344 | 72 | 12 | 1.4 | BMRL | 85.4 | BMRL | 23 | 46 | BMRL | BMRL | 2.9 | NA | NA | NA | 69 | 71.9 | B-12 | Primary | 1998-05-19 | 11:00 | 1874 | 11244 | 7.46 | 0.017 | 26.2 | 0.08 | 3.38 | 0.131 | 3.8757 | 4.7 | 1.34 | 3.36 | 24.5 | 7.93 | 24 | 295 | 74 | 12 | 1.4 | BMRL | 87.4 | BMRL | 20 | 35 | BMRL | BMRL | 2.1 | NA | NA | NA | 55 | 57.1 | C-12 | Primary | 1998-05-19 | 11:00 | 1874 | 5622 | 7.49 | 0.037 | 27 | 0.08 | 2.36 | 0.098 | 4.1525 | 4 | 1.45 | 2.55 | 24.5 | 7.94 | 24 | 203 | 43 | 12 | 2.9 | BMRL | 57.9 | BMRL | 16 | 28 | BMRL | BMRL | 2.7 | NA | NA | NA | 44 | 46.7
[9 empty] | A-12 D | Duplicate | 1998-05-19 | 11:15 | 1874.25 | 5622.75 | 11245.5 | 7.51 | 0.0133 | 221 | 26.6 | 235 | 211 | 0.08 | 8 | 3.46 | 0.133 | 3.8439 | 5.7 | 2.05 | 3.65 | 24.5 | 7.9 | 24 | 288 | 86 | 12 | 1.3 | BMRL | 99.3 | BMRL | 22 | 57 | BMRL | BMRL | 2.4 | NA | NA | NA | 79 | 81.4 | B-12 D | Duplicate | 1998-05-19 | 11:15 | 1874.25 | 11245.5 | 7.48 | 0.012 | 26.2 | 0.08 | 3.37 | 0.132 | 3.9169 | 4.4 | 0.95 | 3.45 | 24.5 | 7.85 | 24 | 269 | 77 | 12 | 1.4 | BMRL | 90.4 | BMRL | 19 | 41 | BMRL | BMRL | 1.9 | NA | NA | NA | 60 | 61.9 | C-12 D | Duplicate | 1998-05-19 | 11:15 | 1874.25 | 5622.75 | 7.5 | 0.023 | 27 | 0.07 | 2.34 | 0.098 | 4.188 | 4 | 1.3 | 2.7 | 25.4 | 7.82 | 24 | 203 | 79 | 12 | 1.4 | BMRL | 92.4 | BMRL | 16 | 31 | BMRL | BMRL | 2.5 | NA | NA | NA | 47 | 49.5
[10 empty] | Average | --- | --- | --- | --- | --- | 7.525 | 0.02515 | 220.5 | 26.6 | 237.5 | 213 | 0.075 | 7.5 | 3.43 | 0.134 | 3.9073 | 5.63 | 2 | 3.63 | 24.5 | 7.89 | 24 | 316 | 79 | 12 | 1.35 | NR | 92.35 | NR | 22.5 | 51.5 | NR | NR | 2.65 |  |  |  | 74 | 76.65 |  | Average | --- | --- | --- | --- | 7.47 | 0.0145 | 26.2 | 0.08 | 3.375 | 0.1315 | 3.8963 | 4.55 | 1.145 | 3.405 | 24.5 | 7.89 | 24 | 282 | 75.5 | 12 | 1.4 | NR | 88.9 | NR | 19.5 | 38 | NR | NR | 2 |  |  |  | 57.5 | 59.5 |  | Average | --- | --- | --- | --- | 7.495 | 0.03 | 27 | 0.075 | 2.35 | 0.098 | 4.1703 | 4 | 1.375 | 2.625 | 24.95 | 7.88 | 24 | 203 | 61 | 12 | 2.15 | NR | 75.15 | NR | 16 | 29.5 | NR | NR | 2.6 |  |  |  | 45.5 | 48.1
[10 empty] | RPD | --- | --- | --- | --- | --- | 0.39867 | 94.2346 | 0.45351 | 0 | 2.1053 | 1.8779 | 13.3333 | 13.3333 | 1.7493 | 1.4925 | 3.2416 | 2.4867 | 5 | 1.1019 | 0 | 0.25349 | 0 | 17.7215 | 17.7215 | 0 | 7.4074 | NR | 15.0514 | NR | 4.4444 | 21.3592 | NR | NR | 18.8679 |  |  |  | 13.5135 | 12.394 |  | RPD | --- | --- | --- | --- | 0.26774 | 34.4828 | 0 | 0 | 0.2963 | 0.76046 | 1.0567 | 6.5934 | 34.0611 | 2.6432 | 0 | 1.0139 | 0 | 9.2199 | 3.9735 | 0 | 0 | NR | 3.3746 | NR | 5.1282 | 15.7895 | NR | NR | 10 |  |  |  | 8.6957 | 8.0672 |  | RPD | --- | --- | --- | --- | 0.13342 | 46.6667 | 0 | 13.3333 | 0.85106 | 0 | 0.85106 | 0 | 10.9091 | 5.7143 | 3.6072 | 1.5228 | 0 | 0 | 59.0164 | 0 | 69.7674 | NR | 45.9082 | NR | 0 | 10.1695 | NR | NR | 7.6923 |  |  |  | 6.5934 | 5.8212
[9 empty] | A-14 | Primary | 1998-06-02 | 10:00 | 2209 | 6627 | 13254 | 7.43 | 0.001 | 218 | 27.3 | 213 | 207 | 0.24 | 2.4 | 3.89 | 0.131 | 3.3676 | 5 | 1.15 | 3.85 | 25.2 | 7.85 | 24 | 359 | 64 | 11 | 1 | BMRL | 76 | BMRL | 23 | 52 | BMRL | BMRL | 2.9 | NA | NA | NA | 75 | 77.9 | B-14 | Primary | 1998-06-02 | 10:15 | 2209.25 | 13255.5 | 7.46 | 0.011 | 27.3 | 0.21 | 2.86 | 0.112 | 3.9161 | 4.48 | 1.4 | 3.08 | 25.1 | 7.95 | 24 | 313 | 65 | 12 | 1.6 | BMRL | 78.6 | BMRL | 21 | 42 | BMRL | BMRL | 3.2 | NA | NA | NA | 63 | 66.2 | C-14 | Primary | 1998-06-02 | 10:24 | 2209.4 | 6628.2 | 7.45 | 0.001 | 27.7 | 0.38 | 2.36 | 0.088 | 3.7288 | 3.45 | 0.85 | 2.6 | 25.1 | 7.92 | 24 | 190 | 46 | 12 | 12 | BMRL | 70 | BMRL | 17 | 22 | BMRL | BMRL | 4.2 | NA | NA | NA | 39 | 43.2
[9 empty] | A-14 D | Duplicate | 1998-06-02 | 10:20 | 2209.3333 | 6628 | 13256 | NR | 0.03 | 222 | 27.3 | 213 | 207 | 0.19 | 2.3 | 3.85 | 0.132 | 3.4286 | 5.2 | 1.4 | 3.8 | 25.1 | 7.89 | 24 | 373 | 70 | 11 | BMRL | BMRL | 81 | BMRL | 21 | 34 | BMRL | BMRL | 2.4 | NA | NA | NA | 55 | 57.4 | B-14 D | Duplicate | 1998-06-02 | 10:20 | 2209.3333 | 13256 | NR | 0.018 | 27.3 | 0.2 | 2.89 | 0.112 | 3.8754 | 4.5 | 1.6 | 2.9 | 24.8 | 7.92 | 24 | 280 | 55 | 12 | 2.2 | BMRL | 69.2 | BMRL | 17 | 26 | BMRL | BMRL | 4.2 | NA | NA | NA | 43 | 47.2 | C-14 D | Duplicate | 1998-06-02 | 10:28 | 2209.4667 | 6628.4 | 7.5 | 0.001 | 27.7 | 0.38 | 2.39 | 0.09 | 3.7657 | 3.3 | 0.9 | 2.4 | 25 | 7.8 | 24 | 196 | 34 | 11 | 3.4 | BMRL | 48.4 | BMRL | 11 | 14 | BMRL | BMRL | 3.3 | NA | NA | NA | 25 | 28.3
[10 empty] | Average | --- | --- | --- | --- | --- | 7.43 | 0.0155 | 220 | 27.3 | 213 | 207 | 0.215 | 2.35 | 3.87 | 0.1315 | 3.3981 | 5.1 | 1.275 | 3.825 | 25.15 | 7.87 | 24 | 366 | 67 | 11 | 1 | NR | 78.5 | NR | 22 | 43 | NR | NR | 2.65 |  |  |  | 65 | 67.65 |  | Average | --- | --- | --- | --- | 7.46 | 0.0145 | 27.3 | 0.205 | 2.875 | 0.112 | 3.8958 | 4.49 | 1.5 | 2.99 | 24.95 | 7.935 | 24 | 296.5 | 60 | 12 | 1.9 | NR | 73.9 | NR | 19 | 34 | NR | NR | 3.7 |  |  |  | 53 | 56.7 |  | Average | --- | --- | --- | --- | 7.475 | 0.001 | 27.7 | 0.38 | 2.375 | 0.089 | 3.7473 | 3.375 | 0.875 | 2.5 | 25.05 | 7.86 | 24 | 193 | 40 | 11.5 | 7.7 | NR | 59.2 | NR | 14 | 18 | NR | NR | 3.75 |  |  |  | 32 | 35.75
[10 empty] | RPD | --- | --- | --- | --- | --- | NR | 187.0968 | 1.8182 | 0 | 0 | 0 | 23.2558 | 4.2553 | 1.0336 | 0.76046 | 1.794 | 3.9216 | 19.6078 | 1.3072 | 0.39761 | 0.50826 | 0 | 3.8251 | 8.9552 | 0 | NR | NR | 6.3694 | NR | 9.0909 | 41.8605 | NR | NR | 18.8679 |  |  |  | 30.7692 | 30.303 |  | RPD | --- | --- | --- | --- | NR | 48.2759 | 0 | 4.878 | 1.0435 | 0 | 1.0435 | 0.44543 | 13.3333 | 6.0201 | 1.2024 | 0.37807 | 0 | 11.1298 | 16.6667 | 0 | 31.5789 | NR | 12.7199 | NR | 21.0526 | 47.0588 | NR | NR | 27.027 |  |  |  | 37.7358 | 33.5097 |  | RPD | --- | --- | --- | --- | 0.6689 | 0 | 0 | 0 | 1.2632 | 2.2472 | 0.9841 | 4.4444 | 5.7143 | 8 | 0.3992 | 1.5267 | 0 | 3.1088 | 30 | 8.6957 | 111.6883 | NR | 36.4865 | NR | 42.8571 | 44.4444 | NR | NR | 24 |  |  |  | 43.75 | 41.6783
[9 empty] | A-15 | Primary | 1998-06-09 | 12:00 | 2379 | 7137 | 14274 | 7.63 | 0.034 | 231 | 27.6 | 248 | 221 | 0.16 | 2.3 | 3.04 | 0.145 | 4.7697 | 4.75 | 1.72 | 3.03 | 24.3 | 8.04 | 24 | 353 | 74 | 12 | 1 | BMRL | 87 | BMRL | 23 | 40 | BMRL | BMRL | 1.4 | NA | NA | NA | 63 | 64.4 | B-15 | Primary | 1998-06-09 | 12:10 | 2379.1667 | 14275 | 7.48 | 0.33 | 28.1 | .1 4 | 2.86 | 0.126 | 4.4056 | 4.92 | 1.74 | 3.18 | 24.4 | 7.91 | 24 | 307 | 54 | 11 | 1.3 | BMRL | 66.3 | BMRL | 20 | 33 | BMRL | BMRL | 1.4 | NA | NA | NA | 53 | 54.4 | C-15 | Primary | 1998-06-09 | 12:20 | 2379.3333 | 7138 | 7.45 | 0.3 | 28.7 | 0.1 | 2.15 | 0.098 | 4.5581 | 3.94 | 1.48 | 2.46 | 24.5 | 7.9 | 24 | 205 | 40 | 11 | 11 | BMRL | 62 | BMRL | 15 | 22 | BMRL | BMRL | 1.6 | NA | NA | NA | 37 | 38.6
[9 empty] | A-15 D | Duplicate | 1998-06-09 | 12:05 | 2379.0833 | 7137.25 | 14274.5 | 7.54 | 0.29 | 227 | 27 | 247 | 221 | 0.18 | 2 | 3.29 | 0.146 | 4.4377 | 5.3 | 1.86 | 3.44 | 24.6 | 7.9 | 24 | 358 | 89 | 13 | 1.3 | BMRL | 103.3 | BMRL | 23 | 46 | BMRL | BMRL | 1.4 | NA | NA | NA | 69 | 70.4 | B-15 D | Duplicate | 1998-06-09 | 12:15 | 2379.25 | 14275.5 | 7.45 | 0.29 | 28.1 | 0.14 | 2.93 | 0.126 | 4.3003 | 4.84 | 1.6 | 3.24 | 24.7 | 7.87 | 24 | 292 | 52 | 12 | 1.5 | BMRL | 65.5 | BMRL | 19 | 32 | BMRL | BMRL | 1.5 | NA | NA | NA | 51 | 52.5 | C-15 D | Duplicate | 1998-06-09 | 12:25 | 2379.4167 | 7138.25 | NR | 0.28 | 28.7 | 0.11 | 2.09 | 0.098 | 4.689 | 3.6 | 1.16 | 2.44 | 24.7 | 7.89 | 24 | 191 | 36 | 11 | 2.6 | BMRL | 49.6 | BMRL | 13 | 18 | BMRL | BMRL | 1.5 | NA | NA | NA | 31 | 32.5
[10 empty] | Average | --- | --- | --- | --- | --- | 7.585 | 0.162 | 229 | 27.3 | 247.5 | 221 | 0.17 | 2.15 | 3.165 | 0.1455 | 4.6037 | 5.025 | 1.79 | 3.235 | 24.45 | 7.97 | 24 | 355.5 | 81.5 | 12.5 | 1.15 | NR | 95.15 | NR | 23 | 43 | NR | NR | 1.4 |  |  |  | 66 | 67.4 |  | Average | --- | --- | --- | --- | 7.465 | 0.31 | 28.1 | 0.14 | 2.895 | 0.126 | 4.353 | 4.88 | 1.67 | 3.21 | 24.55 | 7.89 | 24 | 299.5 | 53 | 11.5 | 1.4 | NR | 65.9 | NR | 19.5 | 32.5 | NR | NR | 1.45 |  |  |  | 52 | 53.45 |  | Average | --- | --- | --- | --- | 7.45 | 0.29 | 28.7 | 0.105 | 2.12 | 0.098 | 4.6236 | 3.77 | 1.32 | 2.45 | 24.6 | 7.895 | 24 | 198 | 38 | 11 | 6.8 | NR | 55.8 | NR | 14 | 20 | NR | NR | 1.55 |  |  |  | 34 | 35.55
[10 empty] | RPD | --- | --- | --- | --- | --- | 1.1866 | 158.0247 | 1.7467 | 2.1978 | 0.40404 | 0 | 11.7647 | 13.9535 | 7.8989 | 0.68729 | 7.2126 | 10.9453 | 7.8212 | 12.6739 | 1.227 | 1.7566 | 0 | 1.4065 | 18.4049 | 8 | 26.087 | NR | 17.1308 | NR | 0 | 13.9535 | NR | NR | 0 |  |  |  | 9.0909 | 8.9021 |  | RPD | --- | --- | --- | --- | 0.40188 | 12.9032 | 0 | #VALUE! | 2.418 | 0 | 2.418 | 1.6393 | 8.3832 | 1.8692 | 1.222 | 0.50697 | 0 | 5.0083 | 3.7736 | 8.6957 | 14.2857 | NR | 1.214 | NR | 5.1282 | 3.0769 | NR | NR | 6.8966 |  |  |  | 3.8462 | 3.5547 |  | RPD | --- | --- | --- | --- | NR | 6.8966 | 0 | 9.5238 | 2.8302 | 0 | 2.8302 | 9.0186 | 24.2424 | 0.81633 | 0.81301 | 0.12666 | 0 | 7.0707 | 10.5263 | 0 | 123.5294 | NR | 22.2222 | NR | 14.2857 | 20 | NR | NR | 6.4516 |  |  |  | 17.6471 | 17.1589
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on V53: M.H. (8/6/99): Consultant verified high results.
Note on AA8: M.H. (8/6/99): Consultant verified variability in ammonia data.
Note on AM53: M.H. (8/6/99): Consultant verified high results.
Note on AQ8: M.H. (8/6/99): Consultant verified dips and spikes in THM data.
Note on AR19: M.H. (8/6/99): Consultant verified this result.
Note on AT45: M.H. (8/6/99): Consultant verified high results.
Note on BA49: M.H. (8/6/99): Consultant verified high results.
Note on BB8: M.H. (8/6/99): Consultant verified dips and spikes in HAA data.
Note on BB49: M.H. (8/6/99): Consultant verified high results.
Note on BN15: M.H. (8/6/99): Consultant verified this result.
Note on BX12: M.H. (8/6/99): Consultant verified this result.
Note on BX16: M.H. (8/6/99): Consultant verified this result.
Note on CB12: M.H. (8/6/99): Consultant verified this result.
Note on CB16: M.H. (8/6/99): Consultant verified this result.
Note on CL49: M.H. (8/6/99): Consultant verified high results.
Note on CM49: M.H. (8/6/99): Consultant verified high results.
Note on DK53: M.H. (8/6/99): Consultant verified high results.
Note on DM45: M.H. (8/6/99): Consultant verified high results.
Note on DW49: M.H. (8/6/99): Consultant verified high results.
Note on DX49: M.H. (8/6/99): Consultant verified high results.