## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of New Bedford Water Department | Carbon manufacturer | Calgon Carbon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | MA4201000 | Carbon trade name | Filtrasorb 300 | mesh size | (mm) | pH Adjustment | lime addition to pH of 5.9 to 6.3, typically 6.0 - 6.3 | Full-scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Carbon type | bituminous | 4 | 4.75 | Coagulation | Alum [Al2(SO4)3 xH20]added at 15 to 17 mg/l | Full-scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 3.5
|  | Pilot GAC influent TOC (mg/L) | 2.7 | 6 | 3.35 | Flocculation | 4 trains of 2 basins in series | Full-scale | START | --- | 1998-04-21 | 13:50 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-22 | 13:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-04-21 | 13:50 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | a | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 8
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 101.6 | 8 | 2.36 | Sedimentation | 4 basins in parallel; 1.6 HOURS @ 45 MGD design capacity; 4.9 hours @ 15 MGD | Full-scale | A1 | N | 1998-04-22 | 14:10 | 24.3333 | 73 | 146 | 5.53 | 0.12 | 2.5 | 15 | 22 | 14 | BMRL | BMRL | 2.2 | 0.038 | 1.7273 | 2.8 | 0.67 | 2.13 | 13 | 9.07 | 100 | 210 | 40 | 6.5 | BMRL | BMRL | 46.5 | 2.8 | 23 | 14 | BMRL | BMRL | 3.3 | NA | NA | NA | 39.8 | 43.1 | B1 | N | 1998-04-22 | 14:07 | 1.1167 | 6.7 | 10.34 | 0.11 | 15 | BMRL | 0.4 | BMRL | #VALUE! | 2.8 | 2.06 | 0.74 | 13 | 9.07 | 100 | BMRL | 2.7 | BMRL | BMRL | BMRL | 2.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C-1 | N | 1998-04-22 | 14:00 | 24.1667 | 72.5 | 10.05 | 0.19 | 16 | BMRL | NA | 0.009 | #VALUE! | 2.8 | 0.67 | 2.13 | 13 | 9.07 | 100 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Special Sitework Factor (% of construction costs) | 12
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 550 | 10 | 2 | Filtration | dual media - 30" anthracite/ 12" sand | Full-scale | A2 | N | 1998-05-02 | 14:10 | 264.3333 | 793 | 1586 | 5.64 | 0.13 | 2 | 15 | 24 | 16 | BMRL | BMRL | 1.9 | 0.039 | 2.0526 | 3.2 | 1.23 | 1.97 | 13 | 9.07 | 100 | NR | 55 | 8.5 | BMRL | BMRL | 63.5 | 3.2 | 21 | 16 | BMRL | BMRL | 2.8 | NA | NA | NA | 40.2 | 43 | B2 | N | 1998-04-27 | 14:15 | 121.25 | 727.5 | 6.92 | 0.13 | 14 | BMRL | BMRL | NR | #VALUE! | NR | NR | #VALUE! | 13 | 9.07 | 100 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C-2 | N | 1998-05-02 | 14:00 | 264.1667 | 792.5 | 6.61 | 0.11 | 16 | BMRL | BMRL | BMRL | #VALUE! | 1.2 | 0.97 | 0.23 | 13 | 9.07 | 100 | BMRL | 1.5 | BMRL | BMRL | BMRL | 1.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 3
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | A3 | N | 1998-05-11 | 14:07 | 480.2833 | 1440.85 | 2881.7 | 5.78 | 0.11 | 2.5 | 15 | 24 | 20 | BMRL | BMRL | 2 | 0.039 | 1.95 | 2.8 | 0.45 | 2.35 | 13 | 6.8 | 100 | 190 | 39 | 7.4 | BMRL | BMRL | 46.4 | 5 | 17 | 30 | BMRL | BMRL | 2 | NA | NA | NA | 52 | 54 | B3 | N | 1998-05-02 | 14:05 | 241.0833 | 1446.5 | 5.68 | 0.11 | 15 | BMRL | BMRL | BMRL | #VALUE! | 1.4 | 1.03 | 0.37 | 13 | 9.07 | 100 | 94 | 3.6 | 1.4 | BMRL | BMRL | 5 | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.4 | 1.4 | C-3 | N | 1998-05-11 | 14:00 | 480.1667 | 1440.5 | 5.82 | 0.12 | 16 | BMRL | BMRL | 0.005 | #VALUE! | 1 | 0.83 | 0.17 | 13 | 7 | 100 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Engineering Fee Factor (% of construction costs) | 2
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 |  |  |  | AVG-A4 | Y | 1998-05-20 | 14:20 | 672.1667 | 2016.5 | 4033 | 6.08 | 0.12 | 3 | 20 | 22 | 20 | NA | NA | 2.35 | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | AVG-B4 | Y | 1998-05-06 | 14:20 | 336.2167 | 2017.3 | 5.71 | 0.07 | 18 | BMRL | 0.58 | 0.009 | 1.5517 | 1.65 | 1.04 | 0.61 | 13 | 9.07 | 100 | BMRL | 4.75 | 2 | BMRL | BMRL | 6.75 | BMRL | 2.45 | 2 | BMRL | BMRL | 1.1 | NA | NA | NA | 4.45 | 5.55 | AVG-C4 | Y | 1998-05-20 | 14:10 | 672.1667 | 2016.5 | 5.81 | 0.12 | 20 | BMRL | BMRL | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1998 ENR Construction Cost Index (CCI base year 1913) | 5991
FAX Number |  | Flow rate, Q (L/hr) | 49.4 | 20 | 0.85 |  |  |  | A5 | N | 1998-05-30 | 12:15 | 934.4167 | 2803.25 | 5606.5 | 6.07 | 0.13 | 3 | 21 | 24 | 20 | BMRL | BMRL | 2.3 | 0.051 | 2.2174 | 2.8 | 0.73 | 2.07 | 13 | 8.87 | 100 | 210 | 60 | 7.7 | BMRL | BMRL | 67.7 | 2.6 | 24 | 16 | BMRL | BMRL | 2.8 | NA | NA | NA | 42.6 | 45.4 | B5 | N | 1998-05-11 | 14:05 | 457.0833 | 2742.5 | 5.62 | 0.08 | 16 | BMRL | 0.68 | 0.009 | 1.3235 | 1.2 | 0.59 | 0.61 | 13 | 7 | 100 | BMRL | 4.8 | 2.6 | BMRL | BMRL | 7.4 | BMRL | 1.9 | 1.2 | BMRL | BMRL | BMRL | NA | NA | NA | 3.1 | 3.1 | C-5 | N | 1998-05-30 | 12:35 | 934.75 | 2804.25 | 5.77 | 0.11 | 21 | BMRL | BMRL | 0.007 | #VALUE! | 1 | 0.77 | 0.23 | 13 | 8.94 | 100 | BMRL | 1.5 | BMRL | BMRL | BMRL | 1.5 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.1 | 1.1 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | A6 | N | 1998-06-08 | 14:00 | 1152.1667 | 3456.5 | 6913 | 5.75 | 0.16 | 2.5 | 19 | 20 | 18 | BMRL | BMRL | 2.5 | 0.056 | 2.24 | 3.8 | 1.28 | 2.52 | 13 | 9.07 | 100 | 260 | 70 | 10 | BMRL | BMRL | 80 | 2.9 | 28 | 24 | BMRL | BMRL | 3.4 | NA | NA | NA | 54.9 | 58.3 | B6 | N | 1998-05-15 | 14:05 | 553.0833 | 3318.5 | 5.7 | 0.11 | 15 | BMRL | 0.8 | 0.015 | 1.875 | 1.2 | 0.63 | 0.57 | 13 | 8.99 | 100 | BMRL | 8.6 | 3.5 | 1.2 | BMRL | 13.3 | BMRL | 3.1 | BMRL | BMRL | BMRL | 1.3 | NA | NA | NA | 3.1 | 4.4 | C-6 | N | 1998-06-08 | 14:10 | 1152.3333 | 3457 | 5.88 | 0.12 | 19 | BMRL | BMRL | 0.009 | #VALUE! | 1.1 | 0.72 | 0.38 | 13 | 9.07 | 100 | BMRL | 3 | 2.4 | 2.1 | BMRL | 7.5 | BMRL | 1.4 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.4 | 1.4 | Labor Rate + Fringe ($/work-hour) | 33.12
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | A7 | N | 1998-06-17 | 14:10 | 1368.3333 | 4105 | 8210 | 5.59 | 0.12 | 2.5 | 20 | 22 | 20 | BMRL | BMRL | 2 | 0.045 | 2.25 | 3.5 | 1.28 | 2.22 | 13 | 7.5 | 100 | 240 | 62 | 9.6 | BMRL | BMRL | 71.6 | 3.7 | 26 | 19 | BMRL | BMRL | 3.9 | NA | NA | NA | 48.7 | 52.6 | AVG-B7 | Y | 1998-05-20 | 15:20 | 674.3333 | 4046 | 5.78 | 0.08 | 20 | BMRL | 0.74 | 0.009 | 1.2162 | 1.3 | 0.7 | 0.6 | 13 | 8.6 | 100 | BMRL | 7.6 | 3.75 | BMRL | BMRL | 11.35 | BMRL | 4.25 | 2.6 | BMRL | BMRL | 1.45 | NA | NA | NA | 6.85 | 8.3 | C-7 | N | 1998-06-17 | 14:10 | 1368.3333 | 4105 | 5.68 | 0.1 | 20 | BMRL | BMRL | 0.006 | #VALUE! | 1.2 | 0.92 | 0.28 | 13 | 7.5 | 100 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Labor Overhead Factor (% of labor) | 48
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 5966.0493 | 50 | 0.3 |  |  |  | AVG-A8 | Y | 1998-06-27 | 12:30 | 1606.6667 | 4820 | 9640 | 5.56 | 0.18 | 2.5 | 24 | 22 | 18 | 0.2 | BMRL | 2.2 | 0.05 | 2.2727 | 3.2 | 0.68 | 2.52 | 13 | 8.42 | 100 | 245 | 67 | 9.9 | BMRL | BMRL | 76.9 | 3.35 | 22 | 18.5 | BMRL | BMRL | 3.45 | NA | NA | NA | 43.85 | 47.3 | B8 | N | 1998-05-25 | 15:00 | 794 | 4764 | 5.88 | 0.11 | 21 | BMRL | 1 | 0.021 | 2.1 | 1.3 | 0.7 | 0.6 | 13 | 8.6 | 100 | 72 | 15 | 5.2 | 1.2 | BMRL | 21.4 | BMRL | 6.3 | 1.7 | BMRL | BMRL | 1.9 | NA | NA | NA | 8 | 9.9 | AVG-C8 | Y | 1998-06-27 | 12:20 | 1606.5 | 4819.5 | 5.57 | 0.08 | 24 | BMRL | BMRL | 0.005 | #VALUE! | 1.1 | 0.66 | 0.44 | 13 | 8.7 | 100 | BMRL | 1 | 1 | 1.25 | BMRL | 3.25 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Electric Rate ($/kW-h) | 0.035
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 11932.0987 | 60 | 0.25 |  |  |  | A9 | N | 1998-07-06 | 14:30 | 1824.6667 | 5474 | 10948 | 5.58 | 0.16 | 2.5 | 24 | 18 | 14 | BMRL | BMRL | 2.3 | 0.049 | 2.1304 | 1.8 | NR | #VALUE! | 13 | 8.82 | 116 | 190 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | B9 | N | 1998-05-29 | 13:45 | 888.75 | 5332.5 | 5.76 | 0.11 | 21 | BMRL | 1.2 | 0.024 | 2 | 1.3 | 0.62 | 0.68 | 13 | 8.92 | 100 | 57 | 15 | 5.2 | 1.4 | BMRL | 21.6 | BMRL | 5.6 | 1.6 | BMRL | BMRL | 1.7 | NA | NA | NA | 7.2 | 8.9 | C-9 | N | 1998-07-06 | 14:35 | 1824.75 | 5474.25 | 5.63 | 0.09 | 24 | BMRL | BMRL | BMRL | #VALUE! | 1.55 | 0.05 | 1.5 | 13 | 8.5 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Fuel Oil Rate ($/gal) | 0.4889
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-07-15 | 14:00 | 2040.1667 | 6120.5 | 12241 | 5.72 | 0.08 | 3 | 23 | 20 | 18 | BMRL | BMRL | 2.2 | 0.054 | 2.4545 | 4.1 | 1.27 | 2.83 | 13 | 8.5 | 100 | 290 | 80 | 11 | BMRL | BMRL | 91 | 5.3 | NR | NR | BMRL | BMRL | 3.7 | NA | NA | NA | NR | NR | B10 | N | 1998-06-03 | 13:05 | 1008.0833 | 6048.5 | 5.72 | 0.1 | 22 | BMRL | 1.4 | 0.03 | 2.1429 | 1.2 | 0.53 | 0.67 | 13 | 7.5 | 100 | 75 | 20 | 6.9 | 1.6 | BMRL | 28.5 | BMRL | 5.5 | 1.8 | BMRL | BMRL | 1.7 | NA | NA | NA | 7.3 | 9 | C-10 | N | 1998-07-16 | 13:30 | 2063.6667 | 6191 | 5.48 | 0.08 | 23 | BMRL | 0.51 | 0.008 | 1.5686 | 1.5 | 0.7 | 0.8 | 13 | 8.5 | 100 | BMRL | 2.9 | BMRL | 2.9 | BMRL | 5.8 | 2 | 22 | 16 | BMRL | BMRL | 2 | NA | NA | NA | 40 | 42 | Natural Gas Rate ($/ft3) | 0.4552
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-07-30 | 13:30 | 2399.6667 | 7199 | 14398 | 5.85 | 0.09 | 4 | 25 | 24 | 20 | BMRL | BMRL | 2.3 | 0.063 | 2.7391 | 3.8 | 0.72 | 3.08 | 13 | 8.5 | 100 | 300 | 80 | 12 | BMRL | BMRL | 92 | 4.8 | 25 | 24 | BMRL | BMRL | 3.9 | NA | NA | NA | 53.8 | 57.7 | B11 | N | 1998-06-09 | 14:10 | 1153.1667 | 6919 | 5.52 | 0.1 | 19 | BMRL | 1.8 | 0.035 | 1.9444 | 1.4 | 0.56 | 0.84 | 13 | 9.07 | 100 | 120 | 32 | 8.6 | 1.2 | BMRL | 41.8 | 1.9 | 13 | 3.9 | BMRL | BMRL | 2.9 | NA | NA | NA | 18.8 | 21.7 | C-11 | N | 1998-07-30 | 13:30 | 2399.6667 | 7199 | 5.77 | 0.13 | 25 | BMRL | BMRL | 0.009 | #VALUE! | 1.7 | 0.88 | 0.82 | 13 | 8.5 | 100 | 44 | 4.7 | 4.7 | 4.3 | 1.4 | 15.1 | 1.8 | 1.7 | 1.3 | BMRL | BMRL | 1.1 | NA | NA | NA | 4.8 | 5.9 | Current Process Water Rate ($/1000 gal) | 0.6358
FAX Number |  | Carbon particle diameter, d (mm) | 1.48 | [5 empty] | AVG-A12 | Y | 1998-08-12 | 14:00 | 2712.1667 | 8136.5 | 16273 | 5.73 | 0.13 | 4 | 26 | 24 | 18 | BMRL | BMRL | 2.75 | 0.066 | 2.4 | 4.4 | 0.955 | 3.445 | 13 | 8.97 | 100 | NA | 76 | 12 | BMRL | BMRL | 88 | 8 | 28 | 27 | BMRL | BMRL | 3.7 | NA | NA | NA | 63 | 66.7 | AVG-B12 | Y | 1998-06-17 | 14:00 | 1345 | 8070 | 5.25 | 0.06 | 20 | BMRL | 1.15 | 0.023 | 2 | 2 | 0.91 | 1.09 | 13 | 7.5 | 100 | 99 | 28.5 | 8.2 | 1.5 | BMRL | 38.2 | 1.45 | 10.5 | 3.95 | BMRL | BMRL | 2.8 | NA | NA | NA | 15.9 | 18.7 | AVG-C12 | Y | 1998-08-12 | 13:30 | 2711.6667 | 8135 | 5.62 | 0.15 | 26 | BMRL | 0.53 | 0.028 | 5.283 | 3.15 | 0.975 | 2.175 | 13 | 9.01 | NR | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | 1.5 | NA | NA | NA | 0 | 1.5 | Modifications to Existing Plant (% of construction costs) | 8
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0081073 | [5 empty] | A-13 | N | 1998-08-26 | 13:45 | 3047.9167 | 9143.75 | 18287.5 | 5.53 | 0.13 | 3 | 24 | 22 | 18 | BMRL | BMRL | 2.5 | 0.055 | 2.2 | 3.8 | 1.2 | 2.6 | 13 | 9.07 | 100 | 460 | 63 | 11 | 1.1 | BMRL | 75.1 | 3.6 | 20 | 24 | BMRL | BMRL | 3.3 | NA | NA | NA | 47.6 | 50.9 | B13 | N | 1998-06-23 | 14:00 | 1489 | 8934 | 5.67 | 0.07 | 23 | BMRL | 1.3 | 0.038 | 2.9231 | 2.2 | 1.06 | 1.14 | 13 | 8 | 100 | 120 | 33 | 8.6 | 1.5 | BMRL | 43.1 | 1.1 | 12 | 3.8 | BMRL | BMRL | 2.2 | NA | NA | NA | 16.9 | 19.1 | C-13 | N | 1998-08-26 | 13:30 | 3047.6667 | 9143 | 5.57 | 0.1 | 24 | BMRL | 0.56 | 0.01 | 1.7857 | 1.8 | 1.2 | 0.6 | 13 | 9.07 | 100 | 67 | 7.9 | 6.3 | 4.5 | BMRL | 18.7 | BMRL | 2.5 | 1.8 | BMRL | BMRL | 1.4 | NA | NA | NA | 4.3 | 5.7
|  | Hydraulic loading rate1, v (m/hr) | 6.0933 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A-14 | N | 1998-09-09 | 13:30 | 3383.6667 | 10151 | 20302 | 5.58 | 0.13 | 1 | 24 | 20 | 12 | BMRL | 23 | 2.5 | 0.056 | 2.24 | 4.3 | 1.19 | 3.11 | 13 | 9.07 | 100 | 470 | 68 | 13 | 2 | BMRL | 83 | 3.2 | 23 | 25 | BMRL | BMRL | 4.4 | NA | NA | NA | 51.2 | 55.6 | B14 | N | 1998-06-30 | 14:00 | 1657 | 9942 | 5.66 | 0.07 | 23 | BMRL | 1.2 | 0.025 | 2.0833 | 1.9 | 0.73 | 1.17 | 13 | 9.07 | 100 | 88 | 24 | 7.6 | 1.6 | BMRL | 33.2 | BMRL | 8.6 | 2.3 | BMRL | BMRL | 2 | NA | NA | NA | 10.9 | 12.9 | C-14 | N | 1998-09-09 | 13:50 | 3384 | 10152 | 5.78 | 0.07 | 25 | BMRL | 1 | 0.016 | 1.6 | 2.1 | 0.78 | 1.32 | 13 | 9.07 | 100 | 120 | 16 | 8.6 | 4.2 | BMRL | 28.8 | 1.1 | 5.3 | 2.6 | BMRL | BMRL | 3 | NA | NA | NA | 9 | 12
Plant Name | Quittacas Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | A-15 | N | 1998-09-23 | 13:00 | 3719.1667 | 11157.5 | 22315 | 5.66 | 0.11 | 3 | 20 | 22 | 16 | BMRL | BMRL | 2.6 | 0.06 | 2.3077 | 4.2 | 1.18 | 3.02 | 13 | 9.07 | 100 | 500 | 61 | 11 | BMRL | BMRL | 72 | 3.3 | 27 | 28 | BMRL | BMRL | 4.7 | NA | NA | NA | 58.3 | 63 | B15 | N | 1998-07-15 | 13:45 | 2016.75 | 12100.5 | 5.47 | 0.06 | 23 | BMRL | 1.6 | 0.027 | 1.6875 | 2.8 | 0.78 | 2.02 | 13 | 8.5 | 100 | 190 | 53 | 11 | 1.3 | BMRL | 65.3 | 3.9 | NR | NR | BMRL | BMRL | 3.9 | NA | NA | NA | NR | NR | C-15 | N | 1998-09-23 | 13:45 | 3719.9167 | 11159.75 | 5.56 | 0.1 | 20 | BMRL | 1.4 | 0.022 | 1.5714 | 2.4 | 1.24 | 1.16 | 13 | 9.07 | 100 | 160 | 17 | 8.2 | 3.1 | BMRL | 28.3 | BMRL | 10 | 3.7 | BMRL | BMRL | 3.5 | NA | NA | NA | 13.7 | 17.2
Treatment Plant Category | CONV |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A-16 | N | 1998-10-07 | 13:00 | 4055.1667 | 12165.5 | 24331 | 5.66 | 0.09 | 3 | 16 | 18 | 10 | BMRL | BMRL | 2.5 | 0.051 | 2.04 | 2.3 | 0.89 | 1.41 | 13 | 9.07 | 100 | 420 | 46 | 8.7 | BMRL | BMRL | 54.7 | 2.1 | 19 | 17 | BMRL | BMRL | 4 | NA | NA | NA | 38.1 | 42.1 | B16 | N | 1998-07-27 | 13:30 | 2304.5 | 13827 | 5.54 | 0.09 | 26 | BMRL | 2.1 | 0.034 | 1.619 | 2.8 | 1.02 | 1.78 | 13 | 8.5 | 100 | 190 | 53 | 11 | 1.4 | BMRL | 65.4 | 2.3 | 17 | 10 | BMRL | BMRL | 2.9 | NA | NA | NA | 29.3 | 32.2 | C-16 | N | 1998-10-07 | 13:45 | 4055.9167 | 12167.75 | 5.67 | 0.06 | 16 | BMRL | 1.5 | 0.02 | 1.3333 | 3.4 | 1.27 | 2.13 | 13 | 9.07 | 100 | 190 | 18 | 6.8 | 2.1 | BMRL | 26.9 | 1.5 | 7.6 | 3.7 | BMRL | BMRL | 3.2 | NA | NA | NA | 12.8 | 16
Process Train Name | Conventional Filtration | 10-Minute EBCT Run | [6 empty] | A-17 | N | 1998-10-21 | 13:00 | 4391.1667 | 13173.5 | 26347 | 5.43 | 0.07 | 3 | 15 | 16 | 10 | BMRL | BMRL | 2.4 | 0.049 | 2.0417 | 3 | 0.64 | 2.36 | 13 | 9.07 | 100 | 280 | 46 | 8.7 | BMRL | BMRL | 54.7 | 1.8 | 21 | 21 | BMRL | BMRL | 4.6 | NA | NA | NA | 43.8 | 48.4 | B17 | N | 1998-08-03 | 14:00 | 2473 | 14838 | 5.53 | 0.08 | 26 | BMRL | 1.5 | 0.028 | 1.8667 | 2.2 | 0.64 | 1.56 | 13 | 8.5 | 100 | 270 | 37 | 11 | 1.7 | BMRL | 49.7 | 2.2 | 13 | 7.4 | BMRL | BMRL | 2.8 | NA | NA | NA | 22.6 | 25.4 | C-17 | N | 1998-10-21 | 13:45 | 4391.9167 | 13175.75 | 5.55 | 0.06 | 15 | BMRL | 1.5 | 0.024 | 1.6 | 3 | 1.64 | 1.36 | 13 | 9.07 | 100 | 230 | 26 | 8.7 | 2.3 | BMRL | 37 | 1.6 | 10 | 6.7 | BMRL | BMRL | 3.7 | NA | NA | NA | 18.3 | 22
ICR Treatment Plant Identification Number | 403 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A-19 | N | 1998-11-04 | 14:00 | 4728.1667 | 14184.5 | 28369 | 5.61 | 0.11 | 3 | 10 | 18 | 10 | BMRL | BMRL | 2.4 | 0.05 | 2.0833 | 3 | 0.61 | 2.39 | 13 | 9.07 | 100 | 370 | 45 | 8.1 | BMRL | BMRL | 53.1 | 1.9 | 20 | 17 | BMRL | BMRL | 4.1 | NA | NA | NA | 38.9 | 43 | B-18 | N | 1998-08-26 | 14:00 | 3025 | 18150 | 5.37 | 0.07 | 24 | BMRL | 1.7 | 0.036 | 2.1176 | 2.8 | 1.2 | 1.6 | 13 | 9.07 | 100 | 270 | 40 | 10 | 2.1 | BMRL | 52.1 | 1.6 | 10 | 8.4 | BMRL | BMRL | 2.9 | NA | NA | NA | 20 | 22.9 | C-18 | N | 1998-11-04 | 13:45 | 4727.9167 | 14183.75 | 5.66 | 0.06 | 10 | BMRL | 1.6 | 0.029 | 1.8125 | 2 | 0.73 | 1.27 | 13 | 9.07 | 100 | 220 | 25 | 6.9 | 1.6 | BMRL | 33.5 | BMRL | 11 | 4.4 | BMRL | BMRL | 3.3 | NA | NA | NA | 15.4 | 18.7
PWSID Number of Plant (if assigned) | NA | Estimated run time, t (days) | 82.8618 | [5 empty] | A-20 | N | 1998-11-18 | 14:00 | 5064.1667 | 15192.5 | 30385 | 5.65 | 0.08 | 3 | 8 | 18 | 12 | BMRL | 21 | 2.4 | 0.047 | 1.9583 | 3.5 | 0.79 | 2.71 | 13 | 9.07 | 100 | 570 | 48 | 8.8 | BMRL | BMRL | 56.8 | 1.9 | 27 | 22 | BMRL | BMRL | 4.2 | NA | NA | NA | 50.9 | 55.1 | B-19 | N | 1998-09-09 | 13:45 | 3360.75 | 20164.5 | 5.58 | 0.07 | 25 | BMRL | 2.1 | 0.047 | 2.2381 | 3.15 | 0.92 | 2.23 | 13 | 9.07 | 100 | 310 | 44 | 11 | 1.8 | BMRL | 56.8 | 1.6 | 15 | 11 | BMRL | BMRL | 3.8 | NA | NA | NA | 27.6 | 31.4 | C-19 | N | 1998-11-18 | 13:45 | 5063.9167 | 15191.75 | 5.63 | 0.06 | 8 | BMRL | 1.3 | 0.024 | 1.8462 | 2 | 1 | 1 | 13 | 9.07 | 100 | 380 | 23 | 7 | 1.8 | BMRL | 31.8 | 1.4 | 12 | 4.7 | BMRL | BMRL | 3 | NA | NA | NA | 18.1 | 21.1
Historical Minimum Water Temperature (oC) | 2 | Pilot column bed length, l (m) | 1.0155 | [5 empty] | A-21 | N | 1998-12-02 | 14:00 | 5400.1667 | 16200.5 | 32401 | 5.56 | 0.08 | 3 | 7 | 18 | 10 | BMRL | BMRL | NR | 0.046 | #VALUE! | 3.5 | 1.22 | 2.28 | 13 | 9.07 | 100 | 460 | 48 | 8.1 | BMRL | BMRL | 56.1 | 1.1 | 22 | 23 | BMRL | BMRL | 2.8 | NA | NA | NA | 46.1 | 48.9 |  |  |  |  | -861781 | -5170686 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | C-20 | N | 1998-12-02 | 13:45 | 5399.9167 | 16199.75 | 5.61 | 0.06 | 7 | BMRL | 1.3 | 0.028 | 2.1538 | 2 | 0.74 | 1.26 | 13 | 9.07 | 100 | 220 | 30 | 7.2 | 1.2 | BMRL | 38.4 | BMRL | 12 | 3.4 | BMRL | BMRL | 2.5 | NA | NA | NA | 15.4 | 17.9
Historical Average Water Temperature (oC) | 12 | Mass GAC required, m (kg) | 4.5283 | [5 empty] | A-22 | N | 1998-12-16 | 14:00 | 5736.1667 | 17208.5 | 34417 | 5.53 | 0.09 | 3 | 5 | 24 | 18 | BMRL | 22 | 2.5 | 0.046 | 1.84 | 3.4 | 0.87 | 2.53 | 13 | 9.07 | 100 | 170 | 59 | 9.4 | BMRL | BMRL | 68.4 | 1.6 | 22 | 21 | BMRL | BMRL | 3.5 | NA | NA | NA | 44.6 | 48.1 |  |  |  |  | -861781 | -5170686 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | C-21 | N | 1998-12-06 | 13:45 | 5495.9167 | 16487.75 | 5.46 | 0.06 | 5 | BMRL | 1.4 | 0.027 | 1.9286 | 2.7 | 1.35 | 1.35 | 13 | 9.07 | 100 | 260 | 30 | 7.2 | 1 | BMRL | 38.2 | BMRL | 11 | 5.7 | BMRL | BMRL | 2.7 | NA | NA | NA | 16.7 | 19.4
State Approved Plant Capacity (MGD) | 45 | [7 empty] | A-23 | N | 1998-12-29 | 14:00 | 6048.1667 | 18144.5 | 36289 | 5.68 | 0.11 | 3 | 3 | 24 | 16 | 0.19 | 20 | 2.4 | 0.044 | 1.8333 | 3.4 | 0.43 | 2.97 | 13 | 9.07 | 100 | 340 | 62 | 9.4 | BMRL | BMRL | 71.4 | 1 | 24 | 12 | BMRL | BMRL | 3.1 | NA | NA | NA | 37 | 40.1 |  |  |  |  | -861781 | -5170686 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | C-22 | N | 1998-12-29 | 13:45 | 6047.9167 | 18143.75 | 5.63 | 0.06 | 3 | 0.18 | 1.6 | 0.031 | 1.9375 | 2.3 | 0.35 | 1.95 | 13 | 9.07 | 100 | 220 | 34 | 7 | BMRL | BMRL | 41 | BMRL | 12 | 3.4 | BMRL | BMRL | 2.4 | NA | NA | NA | 15.4 | 17.8
|  | 20-Minute EBCT Run | [6 empty] | A-24 | N | 1999-01-12 | 14:00 | 6384.1667 | 19152.5 | 38305 | 5.66 | 0.07 | 3 | 4 | 24 | 18 | BMRL | BMRL | 2.2 | 0.042 | 1.9091 | NR | 1.4 | 3 | 13 | 9.07 | 100 | 520 | NR | NR | 1.6 | BMRL | NR | NR | NR | 23 | BMRL | BMRL | NR | NA | NA | NA | NR | NR |  |  |  |  | -861781 | -5170686 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | C-23 | N | 1999-01-12 | 13:45 | 6383.9167 | 19151.75 | 5.61 | 0.04 | 4 | 0.1 | 1.6 | 0.044 | 2.75 | NR | 1.5 | 2.5 | 13 | 9.1 | 100 | 250 | NR | 16 | 2.9 | BMRL | NR | NR | 21 | 8.3 | BMRL | BMRL | 4.6 | NA | NA | NA | 29.3 | 33.9
|  | Empty bed contact time, EBCT (min) | 20 | [9 empty] | -861757.8333 | -2585273.5 | -5170547 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861781 | -5170686 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861757.8333 | -2585273.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Estimated run time, t (days) | 165.7236 | [9 empty] | -861757.8333 | -2585273.5 | -5170547 | [10 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861781 | -5170686 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -861757.8333 | -2585273.5 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Pilot column bed length, l (m) | 2.0311 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 9.0567 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A4 | Primary | 1998-05-20 | 14:20 | 696.5 | 2089.5 | 4179 | 6.08 | 0.12 | 3 | 20 | 22 | 20 | BMRL | NR | 2.3 | NR | #VALUE! | NR | NR | #VALUE! | NR | NR | NR | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | B-4 | Primary | 1998-05-06 | 14:10 | 337.1667 | 2023 | 5.71 | 0.07 | 18 | BMRL | 0.62 | 0.009 | 1.4516 | 1.6 | 1.07 | 0.53 | 13 | 9.07 | 100 | BMRL | 3.2 | 1.3 | BMRL | BMRL | 4.5 | BMRL | 1.6 | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 1.6 | 1.6 | C-4 | Primary | 1998-05-20 | 14:10 | 696.3333 | 2089 | 5.81 | 0.12 | 20 | BMRL | BMRL | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[9 empty] | A4 DUP | Duplicate | 1998-05-20 | 14:20 | 696.5 | 2089.5 | 4179 | 6.08 | 0.12 | 3 | 20 | 22 | 20 | NR | NR | 2.4 | NR | #VALUE! | NR | NR | #VALUE! | NR | NR | NR | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0 | D-4 | Duplicate | 1998-05-06 | 14:20 | 337.3333 | 2024 | 5.71 | 0.07 | 18 | BMRL | 0.54 | 0.008 | 1.4815 | 1.7 | 1 | 0.7 | 13 | 9.07 | 100 | BMRL | 6.3 | 2.7 | BMRL | BMRL | 9 | BMRL | 3.3 | 2 | BMRL | BMRL | 1.1 | NA | NA | NA | 5.3 | 6.4 | C-4DUP | Duplicate | 1998-05-20 | 14:20 | 696.5 | 2089.5 | 5.81 | 0.12 | 20 | BMRL | BMRL | NA | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0
[10 empty] | Average | --- | --- | --- | --- | --- | 6.08 | 0.12 | 3 | 20 | 22 | 20 | #DIV/0! | #DIV/0! | 2.35 | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Average | --- | --- | --- | --- | 5.71 | 0.07 | 18 | #DIV/0! | 0.58 | 0.0085 | 1.4665 | 1.65 | 1.035 | 0.615 | 13 | 9.07 | 100 | #DIV/0! | 4.75 | 2 | #DIV/0! | #DIV/0! | 6.75 | #DIV/0! | 2.45 | 2 | #DIV/0! | #DIV/0! | 1.1 | #DIV/0! | #DIV/0! | #DIV/0! | 3.45 | 4 |  | Average | --- | --- | --- | --- | 5.81 | 0.12 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 4.2553 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 13.7931 | 11.7647 | 2.0367 | 6.0606 | 6.7633 | 27.6423 | 0 | 0 | 0 | #VALUE! | 65.2632 | 70 | #VALUE! | #VALUE! | 66.6667 | #VALUE! | 69.3878 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 107.2464 | 120 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A8 | Primary | 1998-06-27 | 12:20 | 1606.5 | 4819.5 | 9639 | 5.56 | 0.18 | 2.5 | 24 | 22 | 18 | 0.2 | BMRL | 2 | 0.05 | 2.5 | 3.2 | 0.67 | 2.53 | 13 | 8.83 | 100 | 240 | 65 | 9.9 | BMRL | BMRL | 74.9 | 3 | 22 | 20 | BMRL | BMRL | 3.7 | NA | NA | NA | 45 | 48.7 | B-7 | Primary | 1998-05-20 | 15:15 | 674.25 | 4045.5 | 5.78 | 0.08 | 20 | BMRL | 0.73 | 0.006 | 0.82192 | 1.3 | 0.72 | 0.58 | 13 | 8.59 | 100 | BMRL | 7.9 | 3.8 | BMRL | BMRL | 11.7 | BMRL | 4.5 | 2.8 | BMRL | BMRL | 1.5 | NA | NA | NA | 7.3 | 8.8 | C-8 | Primary | 1998-06-27 | 12:00 | 1606.1667 | 4818.5 | 5.57 | 0.08 | 24 | BMRL | BMRL | 0.004 | #VALUE! | 1.1 | 0.66 | 0.44 | 13 | 8.62 | 100 | BMRL | BMRL | BMRL | 1.1 | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | A8 DUP | Duplicate | 1998-06-27 | 12:30 | 1606.6667 | 4820 | 9640 | 5.56 | 0.18 | 2.5 | 24 | 22 | 18 | BMRL | BMRL | 2.4 | 0.05 | 2.0833 | 3.2 | 0.69 | 2.51 | 13 | 8 | 100 | 250 | 69 | 9.9 | BMRL | BMRL | 78.9 | 3.7 | 22 | 17 | BMRL | BMRL | 3.2 | NA | NA | NA | 42.7 | 45.9 | B-DUP | Duplicate | 1998-05-20 | 15:20 | 674.3333 | 4046 | 5.78 | 0.08 | 20 | BMRL | 0.75 | 0.012 | 1.6 | 1.3 | 0.67 | 0.63 | 13 | 8.6 | 100 | BMRL | 7.3 | 3.7 | BMRL | BMRL | 11 | BMRL | 4 | 2.4 | BMRL | BMRL | 1.4 | NA | NA | NA | 6.4 | 7.8 | C-8DUP | Duplicate | 1998-06-27 | 12:20 | 1606.5 | 4819.5 | 5.57 | 0.08 | 24 | BMRL | BMRL | 0.006 | #VALUE! | 1.1 | 0.65 | 0.45 | 13 | 8.78 | 100 | BMRL | 1 | 1 | 1.4 | BMRL | 3.4 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[10 empty] | Average | --- | --- | --- | --- | --- | 5.56 | 0.18 | 2.5 | 24 | 22 | 18 | 0.2 | #DIV/0! | 2.2 | 0.05 | 2.2917 | 3.2 | 0.68 | 2.52 | 13 | 8.415 | 100 | 245 | 67 | 9.9 | #DIV/0! | #DIV/0! | 76.9 | 3.35 | 22 | 18.5 | #DIV/0! | #DIV/0! | 3.45 | #DIV/0! | #DIV/0! | #DIV/0! | 43.85 | 47.3 |  | Average | --- | --- | --- | --- | 5.78 | 0.08 | 20 | #DIV/0! | 0.74 | 0.009 | 1.211 | 1.3 | 0.695 | 0.605 | 13 | 8.595 | 100 | #DIV/0! | 7.6 | 3.75 | #DIV/0! | #DIV/0! | 11.35 | #DIV/0! | 4.25 | 2.6 | #DIV/0! | #DIV/0! | 1.45 | #DIV/0! | #DIV/0! | #DIV/0! | 6.85 | 8.3 |  | Average | --- | --- | --- | --- | 5.57 | 0.08 | 24 | #DIV/0! | #DIV/0! | 0.005 | #VALUE! | 1.1 | 0.655 | 0.445 | 13 | 8.7 | 100 | #DIV/0! | 1 | 1 | 1.25 | #DIV/0! | 2.25 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 18.1818 | 0 | 18.1818 | 0 | 2.9412 | 0.79365 | 0 | 9.8633 | 0 | 4.0816 | 5.9701 | 0 | #VALUE! | #VALUE! | 5.2016 | 20.8955 | 0 | 16.2162 | #VALUE! | #VALUE! | 14.4928 | #VALUE! | #VALUE! | #VALUE! | 5.2452 | 5.9197 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 2.7027 | 66.6667 | 64.2534 | 0 | 7.1942 | 8.2645 | 0 | 0.11635 | 0 | #VALUE! | 7.8947 | 2.6667 | #VALUE! | #VALUE! | 6.1674 | #VALUE! | 11.7647 | 15.3846 | #VALUE! | #VALUE! | 6.8966 | #VALUE! | #VALUE! | #VALUE! | 13.1387 | 12.0482 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | 40 | #VALUE! | 0 | 1.5267 | 2.2472 | 0 | 1.8391 | 0 | #VALUE! | #VALUE! | #VALUE! | 24 | #VALUE! | 102.2222 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A12 | Primary | 1998-08-12 | 13:45 | 2711.9167 | 8135.75 | 16271.5 | 5.73 | 0.13 | 4 | 26 | 24 | 18 | BMRL | BMRL | 2.7 | 0.066 | 2.4444 | 4.4 | 0.85 | 3.55 | 13 | 8.97 | 50 | NR | 75 | 11 | BMRL | BMRL | 86 | 5 | 29 | 29 | BMRL | BMRL | 3.5 | NA | NA | NA | 63 | 66.5 | B-12 | Primary | 1998-06-17 | 14:00 | 1345 | 8070 | 5.25 | 0.06 | 20 | BMRL | 1.1 | 0.023 | 2.0909 | 2 | 0.8 | 1.2 | 13 | 7.5 | 100 | 100 | 28 | 8 | 1.4 | BMRL | 37.4 | 1.4 | 11 | 4.1 | BMRL | BMRL | 2.8 | NA | NA | NA | 16.5 | 19.3 | C-12 | Primary | 1998-08-12 | 13:30 | 2711.6667 | 8135 | 5.62 | 0.15 | 26 | BMRL | 0.53 | 0.041 | 7.7358 | 1.9 | 0.89 | 13 | 13 | 9 | NR | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0
[9 empty] | A12 DUP | Duplicate | 1998-08-12 | 14:00 | 2712.1667 | 8136.5 | 16273 | 5.73 | 0.13 | 4 | 26 | 24 | 18 | BMRL | BMRL | 2.8 | NR | #VALUE! | 4.4 | 1.06 | 3.34 | 13 | 8.98 | 50 | NR | 76 | 12 | BMRL | BMRL | 88 | 11 | 28 | 27 | BMRL | BMRL | 3.7 | NA | NA | NA | 66 | 69.7 | B-DUP | Duplicate | 1998-06-17 | 14:10 | 1345.1667 | 8071 | 5.25 | 0.06 | 20 | BMRL | 1.2 | NA | #VALUE! | 2 | 1.02 | 0.98 | 13 | 7.5 | 100 | 98 | 29 | 8.4 | 1.6 | BMRL | 39 | 1.5 | 10 | 3.8 | BMRL | BMRL | 2.8 | NA | NA | NA | 15.3 | 18.1 | C-12DUP | Duplicate | 1998-08-12 | 13:35 | 2711.75 | 8135.25 | 5.62 | 0.15 | 26 | BMRL | BMRL | 0.015 | #VALUE! | 4.4 | 1.06 | 3.34 | 13 | 9.01 | NR | NR | NR | NR | NR | NR | 0 | NR | NR | NR | NR | NR | NR | NA | NA | NA | 0 | 0
[10 empty] | Average | --- | --- | --- | --- | --- | 5.73 | 0.13 | 4 | 26 | 24 | 18 | #DIV/0! | #DIV/0! | 2.75 | 0.066 | #VALUE! | 4.4 | 0.955 | 3.445 | 13 | 8.975 | 50 | #DIV/0! | 75.5 | 11.5 | #DIV/0! | #DIV/0! | 87 | 8 | 28.5 | 28 | #DIV/0! | #DIV/0! | 3.6 | #DIV/0! | #DIV/0! | #DIV/0! | 64.5 | 68.1 |  | Average | --- | --- | --- | --- | 5.25 | 0.06 | 20 | #DIV/0! | 1.15 | 0.023 | #VALUE! | 2 | 0.91 | 1.09 | 13 | 7.5 | 100 | 99 | 28.5 | 8.2 | 1.5 | #DIV/0! | 38.2 | 1.45 | 10.5 | 3.95 | #DIV/0! | #DIV/0! | 2.8 | #DIV/0! | #DIV/0! | #DIV/0! | 15.9 | 18.7 |  | Average | --- | --- | --- | --- | 5.62 | 0.15 | 26 | #DIV/0! | 0.53 | 0.028 | #VALUE! | 3.15 | 0.975 | 8.17 | 13 | 9.005 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 3.6364 | #VALUE! | #VALUE! | 0 | 21.9895 | 6.0958 | 0 | 0.11142 | 0 | #VALUE! | 1.3245 | 8.6957 | #VALUE! | #VALUE! | 2.2989 | 75 | 3.5088 | 7.1429 | #VALUE! | #VALUE! | 5.5556 | #VALUE! | #VALUE! | #VALUE! | 4.6512 | 4.699 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | 8.6957 | #VALUE! | #VALUE! | 0 | 24.1758 | 20.1835 | 0 | 0 | 0 | 2.0202 | 3.5088 | 4.878 | 13.3333 | #VALUE! | 4.1885 | 6.8966 | 9.5238 | 7.5949 | #VALUE! | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | 7.5472 | 6.4171 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0 | #VALUE! | #VALUE! | 92.8571 | #VALUE! | 79.3651 | 17.4359 | 118.2375 | 0 | 0.11105 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AC5: Reviewer M.H. (9/16/99): Per utility, "TOC – All TOC data is correct and accurate."
Note on AG5: Reviewer M.H. (11/13/99): Per Consultant on target chlorine residual: "Between 0.5 mg/L and 1.0 mg/L."
Note on AG53: Reviewer M.H. (11/13/99): Per Utility, "Cl2 Dose/Residual – correct. No lab error were detected. MCAA – correct. No lab errors were detected."
Note on AJ5: Reviewer M.H. (11/13/99): Per Consultant: "pH levels have been corrected. The laboratory did not list a final pH in the laboratory notebooks for some of the samples. The average final pH of the samples is 8.61. Therefore, it can be assumed that this average can be used in place of 9.07. Samples without a final reported pH were not changed from 9.07. The laboratory did not measure final temperature as was stated previously in the initial comment responses sent to the EPA. DBP samples are reported on a quarterly average. The temperature listed is the sheets (13 deg. C) is the average temperature of the year. Therefore, testing the SDS at this temperature year-round should yield approximately the same results as using separate temperatures for each quarter."
Note on AK5: Reviewer M.H. (11/13/99): Per consultant, "100 hours was selected because it is the length of time water leaving the plant takes to reach the end of the distribution system."
Note on AL6: Reviewer M.H. (9/16/99): Per utility, "TOX– All laboratory QA/QC information checks. No typographical errors were found. From laboratory analysis, we can not explain the high and low spikes for this analyte." Reviewer M.H. (1/5/00): Consultant indicated that TOX values reported are not the average of the original and duplicate analyses, even though the laboratory reported duplicate values. Instead, the reported values are the original values only. This issue did not apply to TOC or UV.
Note on AL10: Lisa Sorgini: Outlier
Note on AL16: Lisa Sorgini: Duplicate sample was 250 (not 290) see below
Note on AR53: Reviewer M.H. (11/13/99): Per Utility, "Cl2 Dose/Residual – correct. No lab error were detected. MCAA – correct. No lab errors were detected."
Note on AS18: Lisa Sorgini: Oulier. Other DBPs seem consistant with trend.
Note on AT18: Lisa Sorgini: Oulier. Other DBPs seem consistant with trend.
Note on BO10: Lisa Sorgini: Outlier
Note on BR5: Reviewer M.H. (11/13/99): Per Consultant on target chlorine residual: "Between 0.5 mg/L and 1.0 mg/L."
Note on BU5: Reviewer M.H. (11/13/99): Per Consultant: "pH levels have been corrected. The laboratory did not list a final pH in the laboratory notebooks for some of the samples. The average final pH of the samples is 8.61. Therefore, it can be assumed that this average can be used in place of 9.07. Samples without a final reported pH were not changed from 9.07. The laboratory did not measure final temperature as was stated previously in the initial comment responses sent to the EPA. DBP samples are reported on a quarterly average. The temperature listed is the sheets (13 deg. C) is the average temperature of the year. Therefore, testing the SDS at this temperature year-round should yield approximately the same results as using separate temperatures for each quarter."
Note on BV5: Reviewer M.H. (11/13/99): Per consultant, "100 hours was selected because it is the length of time water leaving the plant takes to reach the end of the distribution system."
Note on BW5: Reviewer M.H. (11/13/99): Per utility, "TOX– All laboratory QA/QC information checks. No typographical errors were found. From laboratory analysis, we can not explain the high and low spikes for this analyte. TOC – All TOC data is correct and accurate." Reviewer M.H. (1/5/00): Consultant indicated that TOX values reported are not the average of the original and duplicate analyses, even though the laboratory reported duplicate values. Instead, the reported values are the original values only.
Note on BX45: Reviewer M.H. (11/13/99): Per Utility, "HAA – DCAA – Correct. All lab QA/QC checks. THM - Chloroform- Correct. All lab QA/QC checks. BDCM – Correct. All lab QA/QC checks."
Note on BY45: Reviewer M.H. (11/13/99): Per Utility, "HAA – DCAA – Correct. All lab QA/QC checks. THM - Chloroform- Correct. All lab QA/QC checks. BDCM – Correct. All lab QA/QC checks."
Note on CB45: Reviewer M.H. (11/13/99): Per Utility, "HAA – DCAA – Correct. All lab QA/QC checks. THM - Chloroform- Correct. All lab QA/QC checks. BDCM – Correct. All lab QA/QC checks."
Note on CD45: Reviewer M.H. (11/13/99): Per Utility, "HAA – DCAA – Correct. All lab QA/QC checks. THM - Chloroform- Correct. All lab QA/QC checks. BDCM – Correct. All lab QA/QC checks."
Note on CL45: Reviewer M.H. (11/13/99): Per Utility, "HAA – DCAA – Correct. All lab QA/QC checks. THM - Chloroform- Correct. All lab QA/QC checks. BDCM – Correct. All lab QA/QC checks."
Note on CM45: Reviewer M.H. (11/13/99): Per Utility, "HAA – DCAA – Correct. All lab QA/QC checks. THM - Chloroform- Correct. All lab QA/QC checks. BDCM – Correct. All lab QA/QC checks."
Note on DC5: Reviewer M.H. (11/13/99): Per Consultant on target chlorine residual: "Between 0.5 mg/L and 1.0 mg/L."
Note on DF5: Reviewer M.H. (11/13/99): Per Consultant: "pH levels have been corrected. The laboratory did not list a final pH in the laboratory notebooks for some of the samples. The average final pH of the samples is 8.61. Therefore, it can be assumed that this average can be used in place of 9.07. Samples without a final reported pH were not changed from 9.07. The laboratory did not measure final temperature as was stated previously in the initial comment responses sent to the EPA. DBP samples are reported on a quarterly average. The temperature listed is the sheets (13 deg. C) is the average temperature of the year. Therefore, testing the SDS at this temperature year-round should yield approximately the same results as using separate temperatures for each quarter."
Note on DG5: Reviewer M.H. (11/13/99): Per consultant, "100 hours was selected because it is the length of time water leaving the plant takes to reach the end of the distribution system."
Note on DG17: Lisa Sorgini: Incubation time incorrect. All DBPs changed to NR.
Note on DG50: Lisa Sorgini: ncubation time incorrect. All DBPs changed to NR.
Note on DH5: Reviewer M.H. (11/13/99): Per utility, "TOX– All laboratory QA/QC information checks. No typographical errors were found. From laboratory analysis, we can not explain the high and low spikes for this analyte. TOC – All TOC data is correct and accurate." Reviewer M.H. (1/5/00): Consultant indicated that TOX values reported are not the average of the original and duplicate analyses, even though the laboratory reported duplicate values. Instead, the reported values are the original values only.
Note on DH17: Lisa Sorgini: Changed to NR. Appears to be an outlier. May be sampling error.
Note on DO18: Reviewer M.H. (11/13/99): No response from consultant verifying this result.
Note on DP18: Reviewer M.H. (11/13/99): No response from consultant verifying this result.