## Sheet1. Weeks 1-10
FIELD-SET 1: PILOT-SCALE MEMBRANE RESULTS: WEEKS 1-10 (FILE: mempilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 1-4: Foulants And Fouling Indices1 |  | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 1-7: System And Stage Water Quality For Week 2 | [9 empty] | Field 1-7: System And Stage Water Quality For Week 2 (continued) | [7 empty] | Field 1-8: System And Stage Water Quality For Week 4 | [9 empty] | Field 1-8: System And Stage Water Quality For Week 4 (continued) | [7 empty] | Field 1-9: System And Stage Water Quality For Week 6 | [9 empty] | Field 1-9: System And Stage Water Quality For Week 6 (continued) | [7 empty] | Field 1-10: System And Stage Water Quality For Week 8 | [9 empty] | Field 1-10: System And Stage Water Quality For Week 8 (continued) | [7 empty] | Field 1-11: System And Stage Water Quality For Week 10 | [9 empty] | Field 1-11: System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 | [9 empty] | Field 1-12: Duplicate Analysis Of System And Stage Water Quality For Week 10 (continued) | [7 empty] | Field 1-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Fla.Water Services Corp.-Deltona Lakes | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 222 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 | [6 empty] | System recovery during sample collection (decimal) | 0.74 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51 | [6 empty] | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 | [6 empty] | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.51 | [6 empty] | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL3640287 | Membrane trade name | Fluid Systems 4921S | Temperature normalized MTCW (gfd/psi) | 0.27 | Calcium Hardness (mg/L as CaCO3) | 158 | Cartridge filtration | 5 mm exclusion size | Pilot scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 9.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.93 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.78 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.69 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.79 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.96 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.96 |  |  |  |  | Capital Recovery Interest Rate (%) | 7.5 | Pressure Drop
Water Industry Data Base Number (optional) | N/A | Membrane element model number | 4040-TFCS 4921S |  |  | LSI | 0.13 | Sulfuric Acid addition | pH=6.4(@ 75% rec.), 6.2(@ 80% rec.) | Pilot scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 13 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13 | [6 empty] | System influent flow rate during sample collection (gpm) | 13 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 |  |  |  |  | Capital Recovery Period (years) | 20 | System | Stage 1 | Stage 2
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0 |  |  |  | 1998-06-29 | 15:00 | 0 | 27.1 | 55 | 41 | 4.4 | 3.4 | 7.2 | 2.4 |  | 9.6 | 13 | 0.75 | 0.35417 | 14.7692 | 13.8803 | 5.6 | 38 | 0.36527 | NA | 6.4 | 34.32 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 55 | 50 | 4.4 | NA | #VALUE! | 9.6 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | NA | NA | 364.8 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 50 | 41 | 4.4 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15 | 14 | 5 | 9
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0 |  |  |  | 1998-07-01 | 10:00 | 43 | 25.7 | 57 | 44 | 5 | 3.5 | 7 | 2.4 |  | 9.4 | 12.9 | 0.74468 | 0.37234 | 14.359 | 14.0649 | 5.6 | 39.9 | 0.3525 | NA | 7.4 | 30.16 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 57 | 52 | 5 | NA | #VALUE! | 9.4 | 12.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.4 | NA | NA | 364.8 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 52 | 44 | 5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 8 | 13 | 5 | 8
Mailing Address |  | Membrane construction (e.g., thin-film composite) | thin film composite | Design average system flux, FW (gfd) | 13.1 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-07-02 | 10:22 | 67.3667 | 26 | 57 | 44 | 5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.1399 | 5.6 | 39.9 | 0.35438 | NA | 7.8 | 30.16 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 57 | 52 | 5 | NA | #VALUE! | 9.4 | 12.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.8 | NA | NA | 364.8 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 52 | 44 | 5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-sys-2 | CF-sys-2 | CC-sys-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-2 | CI-s1-2 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-4 | CF-sys-4 | CC-sys-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-4 | CI-s1-4 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-6 | CF-sys-6 | CC-sys-6 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-6 | CI-s1-6 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-8 | CF-sys-8 | CC-sys-8 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-8 | CI-s1-8 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 | CF-sys-10 | CC-sys-10 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 | CI-s1-10 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-10 (dup) | CF-sys-10 (dup) | CC-sys-10 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-10 (dup) | CI-s1-10 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25 | 13 | 5 | 8
|  | Membrane hydrophobicity | hydrophilic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | 0 |  |  |  | 1998-07-05 | 12:13 | 141.2167 | 26 | 56 | 43 | 4.7 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 14.1399 | 5.6 | 39.2 | 0.36071 | NA | 6.35 | 32.24 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 56 | 51 | 4.7 | NA | #VALUE! | 9.5 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.35 | NA | NA | 377.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 51 | 43 | 4.7 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | 1998-07-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-27 | 1998-07-27 | 1998-07-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-27 | 1998-07-27 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-10 | 1998-08-10 | 1998-08-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-10 | 1998-08-10 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-24 | 1998-08-24 | 1998-08-24 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-08-24 | 1998-08-24 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | 1998-09-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | 1998-09-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15 | 13 | 5 | 8
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1998-07-06 | 12:00 | 165 | 26.4 | 55 | 42.5 | 4.5 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 13.9737 | 5.6 | 38.65 | 0.36154 | NA | 6.37 | 32.76 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 55 | 50 | 4.5 | NA | #VALUE! | 9.5 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.37 | NA | NA | 377.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 50 | 42.5 | 4.5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 4:40 | 4:40 | 4:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 4:00 | 4:00 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | Sampling time | hh:mm | 2:00 | 1:35 | 2:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 1:54 | 1:45 | --- | --- | --- | --- | Sampling time | hh:mm | 10:15 | 9:05 | 10:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:50 | 9:20 | --- | --- | --- | --- | Sampling time | hh:mm | 10:20 | 9:10 | 10:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:55 | 9:25 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 6007.75 | 12.5 | 5 | 7.5
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-07-07 | 14:15 | 191.25 | 25.3 | 55 | 45 | 5 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 14.4355 | 5.6 | 39.4 | 0.36638 | NA | 6.37 | 32.24 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 55 | 52.5 | 5 | NA | #VALUE! | 9.5 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.37 | NA | NA | 384 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 52.5 | 45 | 5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 350 | 350 | 350 | --- | --- | --- | --- | --- | Operation time | hh.hh | 350 | 350 | --- | --- | --- | --- | Operation time | hh.hh | 678 | 678 | 678 | --- | --- | --- | --- | --- | Operation time | hh.hh | 678 | 678 | --- | --- | --- | --- | Operation time | hh.hh | 1015 | 1015 | 1015 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1015 | 1015 | --- | --- | --- | --- | Operation time | hh.hh | 1352 | 1352 | 1352 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1352 | 1352 | --- | --- | --- | --- | Operation time | hh.hh | 1715 | 1715 | 1715 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1715 | 1715 | --- | --- | --- | --- | Operation time | hh.hh | 1715 | 1715 | 1715 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1715 | 1715 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 124.4 | 10 | 2.5 | 7.5
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.70958 | Sulfate (mg/L) | 6.83 |  |  |  | 1998-07-08 | 12:30 | 213.5 | 26.3 | 56 | 44 | 4.8 | 3.5 | 7 | 2.4 |  | 9.4 | 12.9 | 0.74468 | 0.37234 | 14.359 | 13.8177 | 5.6 | 39.6 | 0.34893 | NA | 6.3 | 32.24 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 56 | 51 | 4.8 | NA | #VALUE! | 9.4 | 12.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.3 | 7.1 | NA | 377.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 51 | 44 | 4.8 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.85 | 6.59 | NA | --- | --- | --- | --- | --- | pH | --- | 6.15 | 6.76 | --- | --- | --- | --- | pH | --- | 5.8 | 6.42 | 6.87 | --- | --- | --- | --- | --- | pH | --- | 5.66 | 6.77 | --- | --- | --- | --- | pH | --- | 5.83 | 6.42 | 6.99 | --- | --- | --- | --- | --- | pH | --- | 5.9 | 6.74 | --- | --- | --- | --- | pH | --- | 5.81 | 6.43 | 6.85 | --- | --- | --- | --- | --- | pH | --- | 5.72 | 6.6 | --- | --- | --- | --- | pH | --- | 5.91 | 6.55 | 6.87 | --- | --- | --- | --- | --- | pH | --- | 6.06 | 6.64 | --- | --- | --- | --- | pH | --- | 6.01 | 6.48 | 6.98 | --- | --- | --- | --- | --- | pH | --- | 5.82 | 6.57 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 15 | 12 | 5 | 7
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4-inch x 40-inch | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.1288 | Calcium (mg/L) | 55 |  |  |  | 1998-07-08 | 12:43 | 213.7167 | 26.1 | 56 | 44 | 4.6 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 14.0982 | 5.6 | 39.8 | 0.35423 | NA | 6.37 | 32.24 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 56 | 51 | 4.6 | NA | #VALUE! | 9.5 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.37 | 7.1 | NA | 377.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 51 | 44 | 4.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.4 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.1 | 24.1 | 24.1 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | Temperature | oC | 25.1 | 25.1 | 25.1 | --- | --- | --- | --- | --- | Temperature | oC | 25.1 | 25.1 | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.4 | 25.4 | --- | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.4 | 25.4 | --- | --- | --- | --- | --- | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | --- | Temperature | oC | 25 | 25 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | Temperature | oC | 25 | 25 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 32 | 12 | 5 | 7
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | Barium (mg/L) | 0 |  |  |  | 1998-07-09 | 3:08 | 228.1333 | 26.4 | 56 | 43 | 4.5 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 13.9737 | 5.6 | 39.4 | 0.35466 | NA | 6.36 | 32.24 | NA | NA | 720 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 56 | 51 | 4.5 | NA | #VALUE! | 9.5 | 13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6.36 | 7 | NA | 377.6 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 51 | 43 | 4.5 | 2.45 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 15.0769 | 14.4657 | #VALUE! | #VALUE! | #VALUE! | 6.5 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 17 | 90 | NA | 309 | #VALUE! | 81.1111 | 228.9808 | 92.5758 | Alkalinity | mg/L as CaCO3 | 16 | 140 | 215.7522 | 82.2222 | 177.8761 | 91.005 | Alkalinity | mg/L as CaCO3 | 17 | 82 | 250 | 267 | -6.8 | 79.2683 | 200.1154 | 91.5049 | Alkalinity | mg/L as CaCO3 | 14 | 130 | 197.455 | 82.9268 | 163.7275 | 91.4492 | Alkalinity | mg/L as CaCO3 | 17 | 86 | 280 | 293 | -4.6429 | 80.2326 | 217.8008 | 92.1947 | Alkalinity | mg/L as CaCO3 | 14 | 130 | 197.0826 | 83.7209 | 163.5413 | 91.4395 | Alkalinity | mg/L as CaCO3 | 16 | 88 | 280 | 316 | -12.8571 | 81.8182 | 232.9302 | 93.131 | Alkalinity | mg/L as CaCO3 | 14 | 130 | 198.5129 | 84.0909 | 164.2565 | 91.4767 | Alkalinity | mg/L as CaCO3 | 18 | 87 | 280 | 305.5 | -9.1071 | 79.3103 | 225.8915 | 92.0316 | Alkalinity | mg/L as CaCO3 | NA | 140 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 32 | 88 | 280 | 265.3333 | 5.2381 | 63.6364 | 200.7235 | 84.0577 | Alkalinity | mg/L as CaCO3 | 39 | 140 | 203.0932 | 55.6818 | 171.5466 | 77.2657 | Electric Rate ($/kW-h) | 0.065 | 13 | 5 | 8
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | Strontium (mg/L) | 0 |  |  |  | 1998-07-10 | 3:05 | 252.0833 | 25.6 | 56 | 44 | 3.79 | 3.5 | 7 | 2.4 |  | 9.4 | 12.9 | 0.74468 | 0.37234 | 14.359 | 14.1066 | 5.9131 | 40.2969 | 0.35007 | NA | 6.4 | 31.72 | 176.9 | 238.9062 | 720 | 843.1991 | -17.111 | 86.7228 | 623.0303 | 94.9088 | 56 | 51 | 3.79 | 4.84 | 8.06 | 9.4 | 12.9 | 0.13131 | 0.51489 | 14.8923 | 14.6305 | 4.8781 | 44.8319 | 0.32634 | 6.4 | 7 | 21.632 | 396.8 | 560 | 622.087 | -11.087 | 90.9454 | 509.4435 | 95.7538 | 51 | 44 | 3.9 | 2.16 | 5.9 | 4.56 | 8.06 | 0.42329 | 0.47368 | 13.2923 | 13.0586 | 6.0608 | 37.5392 | 0.34787 | 6.5 | NA | 47.7 | 560 | 720 | 747.5539 | -3.8269 | 80.034 | 653.7769 | 92.7039 | Total dissolved solids | mg/L | 39 | 250 | NA | 883 | #VALUE! | 84.4 | 651.7115 | 94.0158 | Total dissolved solids | mg/L | 29 | 400 | 626.6456 | 88.4 | 513.3228 | 94.3505 | Total dissolved solids | mg/L | 31 | 250 | 890 | 873.3077 | 1.8755 | 87.6 | 647.958 | 95.2157 | Total dissolved solids | mg/L | 20 | 420 | 652.6034 | 92 | 536.3017 | 96.2708 | Total dissolved solids | mg/L | 39 | 260 | 980 | 923 | 5.8163 | 85 | 682.1445 | 94.2827 | Total dissolved solids | mg/L | 25 | 380 | 585.2959 | 90.3846 | 482.648 | 94.8202 | Total dissolved solids | mg/L | 30 | 250 | 900 | 946.6667 | -5.1852 | 88 | 692.8424 | 95.67 | Total dissolved solids | mg/L | 23 | 380 | 590.8545 | 90.8 | 485.4273 | 95.2619 | Total dissolved solids | mg/L | 32 | 280 | 860 | 1065.3333 | -23.876 | 88.5714 | 779.2041 | 95.8932 | Total dissolved solids | mg/L | 48 | 420 | 652.3829 | 82.8571 | 536.1914 | 91.048 | Total dissolved solids | mg/L | 30 | 250 | 890 | 946.6667 | -6.367 | 88 | 692.8424 | 95.67 | Total dissolved solids | mg/L | 28 | 440 | 697.3703 | 88.8 | 568.6851 | 95.0764 | Fuel Oil Rate ($/gal) | na | 12 | 5 | 7
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Permeate flow rate from system, Qp-sys (gpm) | 6.3863 | Reactive silica (mg/L as SiO2) | 0 |  |  |  | 1998-07-11 | 6:25 | 279.4167 | 25 | 56 | 44 | 5.4 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 14.5641 | 5.8927 | 38.7073 | 0.37626 | NA | 6.39 | 31.72 | 175.16 | 236.5135 | 720 | 842.3611 | -16.9946 | 86.5885 | 620.9937 | 94.8921 | 56 | 51 | 5.4 | 4.96 | 8.04 | 9.5 | 13 | 0.13181 | 0.52211 | 15.2615 | 15.2615 | 4.8245 | 43.2755 | 0.35266 | 6.39 | 7 | 21.684 | 390.4 | 560 | 617.8666 | -10.3333 | 90.8318 | 504.1333 | 95.6988 | 51 | 44 | 5.4 | 2.14 | 5.9 | 4.54 | 8.04 | 0.42269 | 0.47137 | 13.1692 | 13.1692 | 6.0521 | 36.0479 | 0.36533 | 6.5 | NA | 47.7 | 560 | 720 | 745.8173 | -3.5857 | 79.832 | 652.9086 | 92.6942 | Total hardness | mg/L as CaCO3 | 23 | 170 | NA | 611 | #VALUE! | 86.4706 | 449.8654 | 94.8874 | Total hardness | mg/L as CaCO3 | 16 | 280 | 441.2788 | 90.5882 | 360.6394 | 95.5634 | Total hardness | mg/L as CaCO3 | 21 | 170 | 610 | 594.0769 | 2.6103 | 87.6471 | 440.7568 | 95.2355 | Total hardness | mg/L as CaCO3 | 17 | 290 | 448.7518 | 90 | 369.3759 | 95.3976 | Total hardness | mg/L as CaCO3 | 21 | 170 | 620 | 617 | 0.48387 | 87.6471 | 454.6133 | 95.3807 | Total hardness | mg/L as CaCO3 | 14 | 270 | 418.0444 | 91.7647 | 344.0222 | 95.9305 | Total hardness | mg/L as CaCO3 | 25 | 170 | 670 | 629.1667 | 6.0945 | 85.2941 | 461.8734 | 94.5873 | Total hardness | mg/L as CaCO3 | 14 | 270 | 421.201 | 91.7647 | 345.6005 | 95.9491 | Total hardness | mg/L as CaCO3 | 21 | 170 | 630 | 641.8333 | -1.8783 | 87.6471 | 469.9251 | 95.5312 | Total hardness | mg/L as CaCO3 | 16 | 290 | 461.1637 | 90.5882 | 375.5819 | 95.7399 | Total hardness | mg/L as CaCO3 | 21 | 170 | 640 | 641.8333 | -0.28646 | 87.6471 | 469.9251 | 95.5312 | Total hardness | mg/L as CaCO3 | 14 | 290 | 462.4131 | 91.7647 | 376.2065 | 96.2786 | Natural Gas Rate ($/ft3) | na | 12 | 5 | 7
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | Feed flow rate to system, QF-sys (gpm) | 8.515 | Turbidity (ntu) | < 0.10 |  |  |  | 1998-07-13 | 17:00 | 338 | 24.4 | 56 | 44 | 5.3 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 14.8247 | 6.0798 | 38.6202 | 0.38386 | NA | 6.48 | 32.76 | 182.7 | 244.0533 | 720 | 869.1292 | -20.7124 | 86.5767 | 640.7361 | 94.8871 | 56 | 51 | 5.3 | 4.93 | 8.07 | 9.5 | 13 | 0.132 | 0.51895 | 15.1692 | 15.4407 | 4.7944 | 43.4056 | 0.35573 | 6.48 | 7 | 23.14 | 390.4 | 560 | 614.7608 | -9.7787 | 90.5185 | 502.5804 | 95.3958 | 51 | 44 | 5.3 | 2.17 | 5.9 | 4.57 | 8.07 | 0.4236 | 0.47484 | 13.3538 | 13.5928 | 6.0526 | 36.1474 | 0.37604 | 6.5 | NA | 48.76 | 560 | 720 | 748.0323 | -3.8934 | 80.0208 | 654.0162 | 92.5445 | Calcium hardness | mg/L as CaCO3 | 19 | 150 | NA | 543 | #VALUE! | 87.3333 | 399.4038 | 95.2429 | Calcium hardness | mg/L as CaCO3 | 14 | 240 | 378.0644 | 90.6667 | 309.0322 | 95.4697 | Calcium hardness | mg/L as CaCO3 | 19 | 150 | 520 | 522.8462 | -0.54734 | 87.3333 | 388.0479 | 95.1037 | Calcium hardness | mg/L as CaCO3 | 16 | 240 | 370.2579 | 89.3333 | 305.129 | 94.7563 | Calcium hardness | mg/L as CaCO3 | 18 | 150 | 540 | 546 | -1.1111 | 88 | 402.1406 | 95.524 | Calcium hardness | mg/L as CaCO3 | 11 | 230 | 356.6473 | 92.6667 | 293.3237 | 96.2499 | Calcium hardness | mg/L as CaCO3 | 22 | 140 | 540 | 513.6667 | 4.8765 | 84.2857 | 377.5245 | 94.1726 | Calcium hardness | mg/L as CaCO3 | 10 | 230 | 359.9383 | 92.8571 | 294.9692 | 96.6098 | Calcium hardness | mg/L as CaCO3 | 18 | 140 | 530 | 526.3333 | 0.69182 | 87.1429 | 385.5762 | 95.3317 | Calcium hardness | mg/L as CaCO3 | 10 | 240 | 383.6776 | 92.8571 | 311.8388 | 96.7932 | Calcium hardness | mg/L as CaCO3 | 17 | 140 | 550 | 529.5 | 3.7273 | 87.8571 | 387.5891 | 95.6139 | Calcium hardness | mg/L as CaCO3 | 9.6 | 240 | 383.9275 | 93.1429 | 311.9637 | 96.9227 | Current Process Water Rate ($/1000 gal) | 0.45 | 12 | 5 | 7
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.1288 | SDI | na |  |  |  | 1998-07-14 | 10:30 | 355.5 | 25 | 56 | 44 | 4.8 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 14.5641 | 5.8425 | 39.3575 | 0.37005 | NA | 6.4 | 32.24 | 182.7 | 235.2888 | 720 | 835.9748 | -16.1076 | 86.2977 | 616.4934 | 94.7704 | 56 | 51 | 4.8 | 4.88 | 8.12 | 9.5 | 13 | 0.13231 | 0.51368 | 15.0154 | 15.0154 | 4.6997 | 44.0003 | 0.34126 | 6.4 | 7 | 22.62 | 384 | 560 | 601.184 | -7.3543 | 90.3863 | 492.592 | 95.408 | 51 | 44 | 4.8 | 2.22 | 5.9 | 4.62 | 8.12 | 0.42511 | 0.48052 | 13.6615 | 13.6615 | 6.0868 | 36.6132 | 0.37313 | 6.5 | NA | 47.7 | 560 | 720 | 752.7637 | -4.5505 | 79.727 | 656.3819 | 92.7329 | Turbidity | ntu | BMRL | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.2 | 3.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | na | 12 | 5 | 7
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 |  |  | MFI | na |  |  |  | 1998-07-15 | 10:30 | 379.5 | 24.4 | 56 | 44 | 5.1 | 3.6 | 7 | 2.4 |  | 9.4 | 13 | 0.74468 | 0.38298 | 14.359 | 14.6159 | 5.7446 | 39.1554 | 0.37328 | 8.1 | 6.4 | 32.24 | 179.8 | 232.9483 | 720 | 818.3475 | -13.6594 | 86.16 | 606.7032 | 94.686 | 56 | 51 | 5.1 | 4.78 | 8.22 | 9.4 | 13 | 0.13294 | 0.50851 | 14.7077 | 14.9709 | 4.6867 | 43.7133 | 0.34248 | 6.4 | 6.6 | 27.3 | 390.4 | 560 | 601.5457 | -7.4189 | 88.2807 | 495.9729 | 94.4957 | 51 | 44 | 5.1 | 2.22 | 6 | 4.62 | 8.22 | 0.43118 | 0.48052 | 13.6615 | 13.906 | 6.0708 | 36.3292 | 0.38278 | 6.6 | 6.7 | 47.7 | 560 | 720 | 749.551 | -4.1043 | 79.5234 | 654.7755 | 92.7151 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 12 | 5 | 7
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI | na | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-07-16 | 14:50 | 407.8333 | 25.3 | 56 | 44 | 5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.4355 | 5.5421 | 39.4579 | 0.36585 | 7.9 | 6.4 | 31.2 | 174 | 218.2906 | 720 | 795.8313 | -10.5321 | 85.7071 | 585.4095 | 94.6704 | 56 | 51 | 5 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 14.8828 | 4.7031 | 43.7969 | 0.33981 | 6.4 | 6.9 | 23.4 | 384 | 560 | 603.4175 | -7.7531 | 89.2803 | 493.7087 | 95.2604 | 51 | 44 | 5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.5409 | 6.1034 | 36.3966 | 0.37204 | 6.9 | 7 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 78.1484 | 658.0436 | 92.7512 | Total organic carbon | mg/L | BMRL | 1.9 | 7.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2 | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2 | 7.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.4 | 8.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.1 | 8.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.2 | 8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 12 | 5 | 7
Plant Name | Courtland Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 13.76 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 5.6767 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-07-17 | 10:30 | 427.5 | 25.3 | 57 | 42 | 4.7 | 3.6 | 7.1 | 2.4 |  | 9.5 | 13.1 | 0.74737 | 0.37895 | 14.5641 | 14.4355 | 5.3553 | 39.4447 | 0.36597 | 8.1 | 6.3 | 32.24 | 174 | 217.8244 | 720 | 766.845 | -6.5062 | 85.1991 | 567.7727 | 94.3217 | 57 | 51 | 4.7 | 4.88 | 8.22 | 9.5 | 13.1 | 0.13356 | 0.51368 | 15.0154 | 14.8828 | 4.6427 | 44.6573 | 0.33327 | 6.3 | 7 | 26 | 384 | 560 | 596.5353 | -6.5242 | 88.0638 | 490.2676 | 94.6968 | 51 | 42 | 4.7 | 2.22 | 6 | 4.62 | 8.22 | 0.43118 | 0.48052 | 13.6615 | 13.5409 | 6.0708 | 35.7292 | 0.37899 | 7 | 7 | 47.7 | 560 | 720 | 749.551 | -4.1043 | 78.1016 | 654.7755 | 92.7151 | UV254 | cm-1 | 0.01 | 0.087 | 0.31 | 0.318 | -2.5806 | 88.5057 | 0.2336 | 95.7191 | SUVA | L/(mg*m) | NR | 3.9474 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.087 | 0.32 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.1667 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.085 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6842 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.087 | 0.34 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.087 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.0541 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.086 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7838 | --- | --- | --- | --- |  |  | 15 | 6 | 9
Treatment Plant Category | DIS/GW, OTHER/GW | Feed spacer thickness, T (ft) | 0.00267 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 2.8383 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-07-18 | 2:00 | 443 | 26.57 | 55 | 42 | 4 | 3.5 | 7.1 | 2.4 |  | 9.5 | 13 | 0.74737 | 0.36842 | 14.5641 | 13.9037 | 5.2996 | 39.2004 | 0.35468 | 8.2 | 6.3 | 30.68 | 179.8 | 214.8596 | 684 | 759.7242 | -11.0708 | 85.7209 | 560.6391 | 94.5277 | 55 | 50 | 4 | 4.88 | 8.12 | 9.5 | 13 | 0.13231 | 0.51368 | 15.0154 | 14.3345 | 4.5725 | 43.9275 | 0.32632 | 6.3 | 7 | 26 | 377.6 | 525 | 588.9064 | -12.1726 | 87.8991 | 483.2532 | 94.6198 | 50 | 42 | 4 | 2.22 | 5.9 | 4.62 | 8.12 | 0.42511 | 0.48052 | 13.6615 | 13.042 | 5.7025 | 36.2975 | 0.35931 | 7 | 7.1 | 45.05 | 525 | 684 | 705.5914 | -3.1566 | 79.0328 | 615.2957 | 92.6783 | SUVA | L/(mg*m) | NR | 4.5789 | 4.026 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.35 | 4 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.25 | 4.1772 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.625 | 4.0964 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.1429 | 4.0244 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.9091 | 4.125 | --- | --- | --- | --- | --- | [10 empty] | 13 | 5 | 8
Process Train Name | Aeration,Disinfection,Corrosion Control | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | [7 empty] | 1998-07-19 | 12:15 | 477.25 | 26.2 | 54 | 41 | 4.4 | 3.6 | 7.12 | 2.2 |  | 9.32 | 12.92 | 0.76395 | 0.38627 | 14.6051 | 14.0962 | 6.0118 | 37.0882 | 0.38007 | 8.3 | 6.3 | 31.72 | 174 | 227.6047 | 720 | 861.5587 | -19.6609 | 86.0636 | 632.9035 | 94.9882 | 54 | 49 | 4.4 | 4.38 | 8.54 | 9.32 | 12.92 | 0.13444 | 0.46996 | 13.4769 | 13.0073 | 4.4732 | 42.6268 | 0.30514 | 6.3 | 7.1 | 21.58 | 377.6 | 560 | 560.1957 | -0.034953 | 90.5186 | 468.8979 | 95.3977 | 49 | 41 | 4.4 | 2.22 | 6.32 | 4.94 | 8.54 | 0.45058 | 0.44939 | 13.6615 | 13.1854 | 6.0228 | 34.5772 | 0.38133 | 7.1 | 7.2 | 47.7 | 560 | 720 | 739.9535 | -2.7713 | 79.0426 | 649.9767 | 92.6613 | Bromide | mg/L | BMRL | 40 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 43 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 33 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 64 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 59 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 5 | 8
ICR Treatment Plant Identification Number | 1075 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-07-20 | 10:25 | 499.4167 | 25.4 | 55 | 41 | 4.6 | 3.6 | 6.98 | 2.3 |  | 9.28 | 12.88 | 0.75216 | 0.38793 | 14.3179 | 14.1497 | 4.9617 | 38.4383 | 0.36811 | 8.1 | 6.4 | 32.24 | 174 | 200.9183 | 720 | 712.8202 | 0.9972 | 83.9537 | 528.4083 | 93.8987 | 55 | 50 | 4.6 | 3.98 | 8.9 | 9.28 | 12.88 | 0.13645 | 0.42888 | 12.2462 | 12.1022 | 4.497 | 43.403 | 0.27883 | 6.4 | 7.2 | 22.88 | 390.4 | 560 | 554.7516 | 0.93721 | 88.6123 | 472.5758 | 95.1584 | 50 | 41 | 4.6 | 2.22 | 6.68 | 5.3 | 8.9 | 0.47242 | 0.41887 | 13.6615 | 13.501 | 5.9743 | 34.9257 | 0.38656 | 7.2 | 7.3 | 47.7 | 560 | 720 | 730.2554 | -1.4244 | 76.259 | 645.1277 | 92.6061 | SDS-Cl2 dose | mg/L | 3.8 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.6 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.8 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.6 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.8 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.8 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [9 empty] | 14 | 5 | 9
PWSID Number of Plant (if assigned) | N/A |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 2.3233 | [5 empty] | 1998-07-21 | 9:10 | 522.1667 | 26.4 | 54 | 41 | 4.6 | 3.5 | 7.13 | 2.1 |  | 9.23 | 12.73 | 0.77248 | 0.3792 | 14.6256 | 14.0328 | 5.8441 | 37.0559 | 0.37869 | 8.4 | 6.4 | 31.2 | 179.8 | 215.8852 | 720 | 842.9352 | -17.0743 | 85.5479 | 615.6111 | 94.9319 | 54 | 47 | 4.6 | 3.88 | 8.85 | 9.23 | 12.73 | 0.13519 | 0.42037 | 11.9385 | 11.4545 | 4.0222 | 41.8778 | 0.27352 | 6.4 | 7.3 | 22.1 | 352 | 560 | 496.6341 | 11.3153 | 89.7631 | 424.3171 | 94.7916 | 47 | 41 | 4.6 | 2.22 | 6.63 | 5.35 | 8.85 | 0.46938 | 0.41495 | 13.6615 | 13.1077 | 5.9807 | 33.4193 | 0.39222 | 7.3 | 7.4 | 47.7 | 560 | 720 | 731.5394 | -1.6027 | 77.9049 | 645.7697 | 92.6135 | SDS-Free Cl2 residual | mg/L | 0.62 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.61 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.81 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.75 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.3 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.3 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 | [6 empty] | 13 | 7 | 6
Historical Minimum Water Temperature (oC) | 17.8 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.1617 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-07-22 | 10:00 | 547 | 25.5 | 54 | 41 | 4 | 3.6 | 5.8 | 2.2 |  | 8 | 11.6 | 0.725 | 0.45 | 11.8974 | 11.7229 | 5.174 | 38.326 | 0.30587 | 7.7 | 6.4 | 31.72 | 179.8 | 221.4331 | 720 | 721.5859 | -0.22026 | 85.6751 | 549.1194 | 94.2235 | 54 | 49 | 4 | 3.58 | 8.02 | 8 | 11.6 | 0.12291 | 0.4475 | 11.0154 | 10.8538 | 4.4299 | 43.0701 | 0.252 | 6.4 | 6.6 | 21.84 | 384 | 560 | 545.6624 | 2.5603 | 90.137 | 464.8312 | 95.3015 | 49 | 41 | 4 | 2.22 | 5.8 | 4.42 | 8.02 | 0.41905 | 0.50226 | 13.6615 | 13.4611 | 6.1034 | 34.8966 | 0.38574 | 6.6 | 6.7 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 78.4585 | 658.0436 | 92.7512 | SDS-Cl2 demand | mg/L | 3.18 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.7 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.99 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.99 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.85 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.14 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.14 | [6 empty] | 13 | 5 | 8
Historical Average Water Temperature (oC) | 23.5 | Design cross-flow velocity (fps) | 1 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-07-23 | 13:00 | 574 | 26.5 | 53 | 40 | 4 | 3.5 | 7.11 | 2.1 |  | 9.21 | 12.71 | 0.77199 | 0.38002 | 14.5846 | 13.9521 | 6.2411 | 36.2589 | 0.38479 | 7.7 | 6.3 | 30.68 | 174 | 228.2449 | 720 | 897.1432 | -24.6032 | 86.5583 | 654.7925 | 95.3145 | 53 | 46 | 4 | 3.68 | 9.03 | 9.21 | 12.71 | 0.13619 | 0.39957 | 11.3231 | 10.832 | 4.2117 | 41.2883 | 0.26235 | 6.3 | 6.5 | 21.32 | 371.2 | 560 | 513.7868 | 8.2524 | 90.6592 | 442.4934 | 95.1818 | 46 | 40 | 4 | 2.22 | 6.81 | 5.53 | 9.03 | 0.4803 | 0.40145 | 13.6615 | 13.069 | 5.958 | 33.042 | 0.39553 | 6.5 | 6.6 | 47.7 | 560 | 720 | 727.0053 | -0.97296 | 79.1014 | 643.5026 | 92.5874 | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.07 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.22 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.11 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.11 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.94 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.94 | [6 empty] | 13 | 7 | 6
State Approved Plant Capacity (MGD) | N/A | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-07-24 | 8:30 | 593.5 | 24.3 | 56 | 40 | 4 | 3.6 | 7 | 2.4 |  | 9.4 | 13 | 0.74468 | 0.38298 | 14.359 | 14.6592 | 4.8478 | 39.1522 | 0.37442 | 7.8 | 6.45 | 31.2 | 174 | 200.5746 | 720 | 694.584 | 3.53 | 84.4447 | 515.9806 | 93.9533 | 56 | 46 | 4 | 4.78 | 8.22 | 9.4 | 13 | 0.13294 | 0.50851 | 14.7077 | 15.0152 | 4.8465 | 42.1535 | 0.3562 | 6.45 | 6.9 | 21.32 | 396.8 | 560 | 615.1448 | -9.8473 | 89.3705 | 505.9724 | 95.7863 | 46 | 40 | 4 | 2.22 | 6 | 4.62 | 8.22 | 0.43118 | 0.48052 | 13.6615 | 13.9472 | 6.0708 | 32.9292 | 0.42355 | 6.9 | 6.8 | 47.7 | 560 | 720 | 749.551 | -4.1043 | 76.2183 | 654.7755 | 92.7151 | SDS-Chlorination pH | --- | 7.99 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.99 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.9 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.9 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.94 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8 | NR | --- | --- | --- | --- | --- | --- | [10 empty] | 16 | 10 | 6
|  | Maximum element recovery (%) | 10 | [7 empty] | 1998-07-25 | 1:30 | 610.5 | 26.5 | 55 | 42 | 4 | 3.6 | 7 | 2.4 |  | 9.4 | 13 | 0.74468 | 0.38298 | 14.359 | 13.7362 | 5.3995 | 39.1005 | 0.35131 | 7.7 | 6.4 | 29.64 | 174 | 218.2906 | 684 | 768.5216 | -12.357 | 86.4218 | 569.592 | 94.7963 | 55 | 50 | 4 | 4.79 | 8.21 | 9.4 | 13 | 0.13287 | 0.50957 | 14.7385 | 14.0993 | 4.6189 | 43.8811 | 0.32131 | 6.4 | 6.6 | 20.02 | 377.6 | 525 | 586.2246 | -11.6618 | 90.8287 | 481.9123 | 95.8457 | 50 | 42 | 4 | 2.21 | 6 | 4.61 | 8.21 | 0.43088 | 0.47939 | 13.6 | 13.0102 | 5.7148 | 36.2852 | 0.35855 | 6.6 | 6.7 | 42.4 | 525 | 684 | 702.7577 | -2.7423 | 80.5764 | 613.8788 | 93.0931 | SDS-Incubation time | hours | 24 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 24 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 24 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [9 empty] | 13 | 5 | 8
|  | Variability of design flux (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-07-26 | 11:45 | 644.75 | 26.4 | 56 | 42 | 3.9 | 3.6 | 7.06 | 2.3 |  | 9.36 | 12.96 | 0.75427 | 0.38462 | 14.4821 | 13.895 | 6.0878 | 39.0122 | 0.35617 | 7.8 | 6.4 | 30.68 | 174 | 236.2712 | 720 | 867.3469 | -20.4648 | 87.0149 | 639.4585 | 95.2022 | 56 | 50 | 3.9 | 4.38 | 8.58 | 9.36 | 12.96 | 0.13494 | 0.46795 | 13.4769 | 12.9306 | 4.3984 | 44.7016 | 0.28926 | 6.4 | 6.7 | 20.8 | 371.2 | 560 | 550.0755 | 1.7722 | 91.1966 | 460.6378 | 95.4845 | 50 | 42 | 3.9 | 2.22 | 6.36 | 4.98 | 8.58 | 0.45301 | 0.44578 | 13.6615 | 13.1077 | 6.0171 | 36.0829 | 0.36327 | 6.7 | 6.8 | 47.7 | 560 | 720 | 738.8217 | -2.6141 | 79.8113 | 649.4108 | 92.6549 | SDS-TOX | mg Cl- /L | 35 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-2 | CI-s2-2 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 43 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-4 | CI-s2-4 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 23 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-6 | CI-s2-6 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 32 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-8 | CI-s2-8 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 28 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 | CI-s2-10 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 28 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-10 (dup) | CI-s2-10 (dup) | CC(calc) | RF (%) | CB | RB (%) |  |  | 14 | 6 | 8
|  | Rejection of reference solute and conditions of test | 500 mg/L NaCl | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 11.485 | [5 empty] | 1998-07-27 | 9:05 | 666.0833 | 25.1 | 56 | 44 | 4.9 | 3.6 | 7 | 2.4 |  | 9.4 | 13 | 0.74468 | 0.38298 | 14.359 | 14.3166 | 5.1162 | 39.9838 | 0.35806 | 7.7 | 6.4 | 30.68 | 174 | 209.4327 | 720 | 730.7947 | -1.4993 | 85.3509 | 542.3023 | 94.3426 | 56 | 51 | 4.9 | 4.78 | 8.22 | 9.4 | 13 | 0.13294 | 0.50851 | 14.7077 | 14.6643 | 4.688 | 43.912 | 0.33395 | 6.4 | 6.7 | 20.8 | 384 | 560 | 595.2039 | -6.2864 | 90.0684 | 489.6019 | 95.7517 | 51 | 44 | 4.9 | 2.22 | 6 | 4.62 | 8.22 | 0.43118 | 0.48052 | 13.6615 | 13.6212 | 6.0708 | 36.5292 | 0.37289 | 6.7 | 6.9 | 47.7 | 560 | 720 | 749.551 | -4.1043 | 77.2242 | 654.7755 | 92.7151 | SDS-CHCl3 | mg/L | 4.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-13 | 1998-07-13 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-07-27 | 1998-07-27 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 6.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-08-10 | 1998-08-10 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 7.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-08-24 | 1998-08-24 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 7.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 7.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-09 | 1998-09-09 | --- | --- | --- | --- |  |  | 12 | 5 | 7
|  | (e.g., solute type and concentration) |  | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 5.7425 | [5 empty] | 1998-07-28 | 9:00 | 690 | 25.1 | 56 | 44 | 5 | 3.6 | 7 | 2.4 |  | 9.4 | 13 | 0.74468 | 0.38298 | 14.359 | 14.3166 | 5.3698 | 39.6302 | 0.36125 | 7.5 | 6.4 | 30.68 | 174 | 218.2906 | 720 | 765.4883 | -6.3178 | 85.9453 | 567.6553 | 94.5953 | 56 | 51 | 5 | 4.69 | 8.31 | 9.4 | 13 | 0.1335 | 0.49894 | 14.4308 | 14.3882 | 4.7423 | 43.7577 | 0.32881 | 6.4 | 6.6 | 20.54 | 390.4 | 560 | 599.1417 | -6.9896 | 90.5905 | 494.7708 | 95.8486 | 51 | 44 | 5 | 2.31 | 6 | 4.71 | 8.31 | 0.43391 | 0.49045 | 14.2154 | 14.1734 | 6.1092 | 36.3908 | 0.38948 | 6.6 | 6.7 | 47.7 | 560 | 720 | 757.2355 | -5.1716 | 78.1484 | 658.6178 | 92.7576 | SDS-BDCM | mg/L | 2.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 4:00 | 4:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 11:00 | 11:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:00 | 10:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 1:56 | 1:50 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:05 | 9:35 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 10:10 | 9:37 | --- | --- | --- | --- |  |  | 12 | 5 | 7
|  | Variability of rejection of reference solute (%) | 15 | [7 empty] | 1998-07-29 | 0:00 | 705 | 29.9 | 57 | 44 | 5 | 3.6 | 7 | 2.2 |  | 9.2 | 12.8 | 0.76087 | 0.3913 | 14.359 | 12.4228 | 5.7453 | 39.7547 | 0.31249 | 7.4 | 6.4 | 30.16 | 174 | 219.2534 | 720 | 820.9144 | -14.0159 | 86.2442 | 604.6925 | 95.0123 | 57 | 52 | 5 | 4.69 | 8.11 | 9.2 | 12.8 | 0.131 | 0.50978 | 14.4308 | 12.485 | 3.2829 | 46.2171 | 0.27014 | 6.4 | 6.5 | 20.54 | 275.2 | 560 | 422.4695 | 24.559 | 90.6318 | 348.8347 | 94.1118 | 52 | 44 | 5 | 2.31 | 5.8 | 4.51 | 8.11 | 0.42178 | 0.5122 | 14.2154 | 12.2986 | 6.1432 | 36.8568 | 0.33369 | 6.5 | 6.7 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 78.2444 | 662.0184 | 92.7948 | SDS-DBCM | mg/L | 0.79 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 350 | 350 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 678 | 678 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1015 | 1015 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1352 | 1352 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1715 | 1715 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1715 | 1715 | --- | --- | --- | --- |  |  | 13 | 5 | 8
|  | Standard testing recovery (%) | 10 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-07-30 | 9:15 | 738.25 | 25.8 | 57 | 44 | 4.6 | 3.6 | 7.1 | 2.4 |  | 9.5 | 13.1 | 0.74737 | 0.37895 | 14.5641 | 14.2237 | 5.3298 | 40.5702 | 0.3506 | 7.4 | 6.4 | 30.16 | 179.8 | 214.8596 | 720 | 761.2626 | -5.7309 | 85.9629 | 563.1394 | 94.6443 | 57 | 52 | 4.6 | 4.88 | 8.22 | 9.5 | 13.1 | 0.13356 | 0.51368 | 15.0154 | 14.6645 | 4.7135 | 45.1865 | 0.32453 | 6.4 | 6.5 | 20.54 | 384 | 560 | 599.7767 | -7.103 | 90.4403 | 491.8884 | 95.8243 | 52 | 44 | 4.6 | 2.22 | 6 | 4.62 | 8.22 | 0.43118 | 0.48052 | 13.6615 | 13.3423 | 6.0708 | 37.3292 | 0.35742 | 6.5 | 6.6 | 47.7 | 560 | 720 | 749.551 | -4.1043 | 77.7995 | 654.7755 | 92.7151 | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.16 | 6.88 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.88 | 6.75 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.03 | 6.87 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.94 | 6.7 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.01 | 6.73 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.07 | 6.75 | --- | --- | --- | --- |  |  | 13 | 5 | 8
|  | Standard testing pH | 7.5 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 2.3233 | [5 empty] | 1998-07-31 | 7:50 | 760.8333 | 24.1 | 55 | 45 | 5.1 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.9567 | 5.4515 | 39.4485 | 0.37915 | 7.7 | 6.44 | 31.2 | 179.8 | 215.2326 | 727.2 | 783.3331 | -7.7191 | 85.5041 | 576.3507 | 94.5866 | 55 | 51 | 5.1 | 4.9 | 8 | 9.4 | 12.9 | 0.13093 | 0.52128 | 15.0769 | 15.4834 | 5.0719 | 42.8281 | 0.36152 | 6.44 | 6.6 | 21.32 | 409.6 | 560 | 647.4215 | -15.611 | 90.0944 | 528.5108 | 95.966 | 51 | 45 | 5.1 | 2.2 | 5.8 | 4.5 | 8 | 0.41844 | 0.48889 | 13.5385 | 13.9035 | 6.0946 | 36.8054 | 0.37776 | 6.6 | 6.7 | 47.7 | 560 | 727.2 | 754.3207 | -3.7295 | 77.8379 | 657.1603 | 92.7415 | SDS-THM4 | mg/L | 7.99 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 7.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25.1 | 25.1 | --- | --- | --- | --- | SDS-THM4 | mg/L | 8.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 9.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25.4 | 25.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 10.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25 | 25 | --- | --- | --- | --- | SDS-THM4 | mg/L | 10.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 25 | 25 | --- | --- | --- | --- |  |  | 10 | 4 | 6
|  | Acceptable range of operating pressures | 0 - 350 psi | Maximum system recycle flow rate, (QR-sys)max (gpm) | 5.7425 | [5 empty] | 1998-08-01 | 1:00 | 778 | 25.3 | 57 | 44 | 4.3 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.4355 | 5.9609 | 40.2391 | 0.35874 | 7.5 | 6.37 | 31.72 | 179.8 | 232.9483 | 792 | 854.1314 | -7.8449 | 86.3832 | 627.8088 | 94.9475 | 57 | 53 | 4.3 | 4.96 | 7.94 | 9.4 | 12.9 | 0.13056 | 0.52766 | 15.2615 | 15.1268 | 5.0116 | 45.6884 | 0.33109 | 6.37 | 6.5 | 21.32 | 403.2 | 595 | 641.7548 | -7.8579 | 90.8478 | 522.4774 | 95.9194 | 53 | 44 | 4.3 | 2.14 | 5.8 | 4.44 | 7.94 | 0.41662 | 0.48198 | 13.1692 | 13.053 | 6.489 | 37.711 | 0.34613 | 6.5 | 6.6 | 47.17 | 595 | 792 | 797.1304 | -0.64778 | 79.7509 | 696.0652 | 93.2233 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 26 | 210 | 302.514 | 71.1111 | 256.257 | 89.8539 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 25 | 180 | 237.35 | 69.5122 | 208.675 | 88.0196 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 180 | 242.131 | 72.093 | 211.0655 | 88.6291 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 25 | 180 | 241.7328 | 71.5909 | 210.8664 | 88.1442 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 30 | 180 | 235.3448 | 65.5172 | 207.6724 | 85.5542 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 27 | 180 | 236.4517 | 69.3182 | 208.2259 | 87.0333 |  |  | 13 | 4 | 9
|  | Acceptable range of operating pH values | 4-11 | Design system recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1998-08-02 | 11:45 | 812.75 | 25.7 | 56 | 44 | 4 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.2659 | 5.5421 | 40.4579 | 0.35261 | 7.8 | 6.4 | 31.2 | 174 | 218.2906 | 720 | 795.8313 | -10.5321 | 85.7071 | 585.4095 | 94.6704 | 56 | 52 | 4 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 14.4366 | 4.7875 | 45.2125 | 0.31931 | 6.4 | 6.5 | 20.8 | 390.4 | 560 | 608.6964 | -8.6958 | 90.4714 | 499.5482 | 95.8362 | 52 | 44 | 4 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 13.9243 | 6.1432 | 37.8568 | 0.36781 | 6.5 | 6.6 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 78.1484 | 662.0184 | 92.7948 | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 58 | 600 | 872.514 | 76.8 | 736.257 | 92.1223 | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 50 | 580 | 776.1 | 80 | 678.05 | 92.6259 | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 59 | 590 | 801.4845 | 77.3077 | 695.7422 | 91.5198 | SDS-DCAA* | mg/L | 2.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 50 | 570 | 777.1034 | 80 | 673.5517 | 92.5767 | SDS-DCAA* | mg/L | 2.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 46 | 650 | 872.8552 | 83.5714 | 761.4276 | 93.9587 | SDS-DCAA* | mg/L | 1.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 46 | 580 | 777.0276 | 81.6 | 678.5138 | 93.2205 |  |  | 12 | 4 | 8
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 13.515 | [5 empty] | 1998-08-03 | 12:00 | 837 | 25.5 | 57 | 44 | 4.1 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.3504 | 6.2541 | 40.1459 | 0.35746 | 7.6 | 6.4 | 30.68 | 179.8 | 241.806 | 720 | 893.543 | -24.1032 | 87.3121 | 656.0884 | 95.3238 | 57 | 53 | 4.1 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 14.5222 | 4.7908 | 46.1092 | 0.31495 | 6.4 | 6.6 | 20.54 | 390.4 | 560 | 608.85 | -8.7232 | 91.5056 | 499.625 | 95.8889 | 53 | 44 | 4.1 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.0068 | 6.1432 | 38.2568 | 0.36613 | 6.6 | 6.7 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 80.2734 | 662.0184 | 92.7948 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 40 | 420 | 611.0615 | 76.4706 | 515.5307 | 92.241 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 34 | 400 | 535.42 | 80 | 467.71 | 92.7305 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 35 | 380 | 517.4052 | 79.4118 | 448.7026 | 92.1997 | SDS-TCAA* | mg/L | 1.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 34 | 400 | 545.769 | 80 | 472.8845 | 92.8101 | SDS-TCAA* | mg/L | 2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 34 | 330 | 439.2138 | 80 | 384.6069 | 91.1598 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 40 | 380 | 505.4483 | 76.4706 | 442.7241 | 90.965 |  |  | 13 | 4 | 9
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.5872 | [5 empty] | 1998-08-04 | 10:00 | 859 | 25.3 | 56 | 44 | 4 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.4355 | 4.9113 | 41.0887 | 0.35133 | 7.5 | 6.47 | 31.72 | 179.8 | 197.5165 | 720 | 709.3229 | 1.4829 | 83.9406 | 522.8508 | 93.9333 | 56 | 51 | 4 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 14.8828 | 4.8205 | 44.6795 | 0.3331 | 6.47 | 6.5 | 20.8 | 390.4 | 560 | 615.2938 | -9.8739 | 89.4692 | 502.8469 | 95.8636 | 51 | 44 | 4 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.5409 | 6.1034 | 37.3966 | 0.36209 | 6.5 | 6.6 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 75.8501 | 658.0436 | 92.7512 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 31 | 360 | 525.419 | 79.3333 | 442.7095 | 92.9977 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 340 | 454.7 | 80 | 397.35 | 92.45 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 29 | 330 | 449.881 | 80.6667 | 389.9405 | 92.563 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 340 | 463.4655 | 78.5714 | 401.7328 | 92.5323 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 320 | 427 | 78.5714 | 373.5 | 91.9679 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 27 | 320 | 428.1069 | 80.7143 | 374.0534 | 92.7818 |  |  | 12 | 5 | 7
|  | Maximum permissible turbidity (ntu) | 0 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-08-05 | 8:45 | 881.75 | 23.9 | 58 | 45 | 4.8 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 15.0454 | 5.4515 | 41.2485 | 0.36475 | 7.9 | 6.4 | 31.2 | 179.8 | 215.2326 | 720 | 783.3331 | -8.7963 | 85.5041 | 576.3507 | 94.5866 | 58 | 54 | 4.8 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 15.2256 | 4.9499 | 46.2501 | 0.3292 | 6.4 | 6.6 | 21.06 | 403.2 | 560 | 628.9029 | -12.3041 | 90.2152 | 516.0515 | 95.919 | 54 | 45 | 4.8 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.6852 | 6.1432 | 38.5568 | 0.38087 | 6.6 | 6.7 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 77.8379 | 662.0184 | 92.7948 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 2.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 4 | 9
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | maximum system recycle flow rates. | [6 empty] | 1998-08-06 | 9:15 | 906.25 | 24.2 | 58 | 44 | 4.6 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.9126 | 5.4669 | 40.9331 | 0.36432 | 7.8 | 6.4 | 30.68 | 179.8 | 215.2326 | 720 | 784.9383 | -9.0192 | 85.7457 | 577.3711 | 94.6863 | 58 | 53 | 4.6 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 15.0911 | 4.8704 | 46.0296 | 0.32786 | 6.4 | 6.6 | 20.8 | 396.8 | 560 | 618.8764 | -10.5137 | 90.336 | 507.8382 | 95.9042 | 53 | 44 | 4.6 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.5555 | 6.1432 | 37.7568 | 0.38551 | 6.6 | 6.7 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 77.8379 | 662.0184 | 92.7948 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 14 | 5 | 9
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-08-07 | 8:40 | 929.6667 | 24.3 | 57 | 44 | 4.5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.8686 | 5.4669 | 40.5331 | 0.36683 | 7.8 | 6.42 | 30.68 | 179.8 | 215.2326 | 720 | 784.9383 | -9.0192 | 85.7457 | 577.3711 | 94.6863 | 57 | 52 | 4.5 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.3293 | 4.7404 | 45.2596 | 0.3387 | 6.42 | 6.7 | 20.54 | 384 | 560 | 605.1577 | -8.0639 | 90.4568 | 494.5789 | 95.847 | 52 | 44 | 4.5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.9472 | 6.1034 | 37.3966 | 0.37295 | 6.7 | 6.7 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 77.8379 | 658.0436 | 92.7512 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.22 | 0.32358 | 83.908 | 0.27179 | 94.8489 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.015 | 0.21 | 0.28215 | 82.7586 | 0.24607 | 93.9043 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.2 | 0.27567 | 88.2353 | 0.23784 | 95.7954 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.014 | 0.21 | 0.28806 | 83.908 | 0.24903 | 94.3782 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.013 | 0.2 | 0.269 | 85.0575 | 0.2345 | 94.4562 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 5 | 8
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-08-08 | 11:00 | 956 | 26 | 56 | 44 | 4 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.1399 | 5.7139 | 40.2861 | 0.35099 | 7.4 | 6.33 | 31.2 | 179.8 | 224.0905 | 720 | 819.535 | -13.8243 | 86.0771 | 602.5901 | 94.8224 | 56 | 52 | 4 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 14.578 | 4.8171 | 45.1829 | 0.32264 | 6.33 | 6.5 | 21.06 | 390.4 | 560 | 615.1356 | -9.8456 | 90.602 | 502.7678 | 95.8112 | 52 | 44 | 4 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.2636 | 6.1034 | 37.8966 | 0.35 | 6.5 | 6.6 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 78.714 | 658.0436 | 92.7512 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.9286 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.0385 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.9216 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6842 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8462 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8 | --- | --- | --- | --- |  |  | 12 | 4 | 8
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 13.515 | [5 empty] | 1998-08-09 | 6:00 | 975 | 24.5 | 57 | 44 | 4.9 | 3.4 | 7.2 | 2.2 |  | 9.4 | 12.8 | 0.76596 | 0.3617 | 14.7692 | 14.9891 | 5.1875 | 40.4125 | 0.3709 | 7.3 | 6.4 | 28.6 | 179.8 | 197.5165 | 720 | 750.334 | -4.2131 | 85.5202 | 547.3463 | 94.7748 | 57 | 52 | 4.9 | 4.78 | 8.02 | 9.4 | 12.8 | 0.13043 | 0.50851 | 14.7077 | 14.9267 | 4.299 | 45.301 | 0.3295 | 6.4 | 6.5 | 20.8 | 352 | 560 | 549.3985 | 1.8931 | 89.4692 | 450.6993 | 95.3849 | 52 | 44 | 4.9 | 2.33 | 5.69 | 4.62 | 8.02 | 0.41571 | 0.50433 | 14.3385 | 14.5519 | 6.1719 | 36.9281 | 0.39406 | 6.5 | 6.7 | 47.7 | 560 | 720 | 769.7819 | -6.9142 | 75.8501 | 664.8909 | 92.8259 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 5 | 8
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | [5 empty] | 1998-08-10 | 10:15 | 1003.25 | 25.4 | 57 | 44 | 4.1 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.1902 | 5.2474 | 41.1526 | 0.34482 | NA | 6.41 | 31.2 | 174 | 209.8137 | 720 | 753.4205 | -4.6417 | 85.1297 | 555.9383 | 94.3879 | 57 | 53 | 4.1 | 4.69 | 8.11 | 9.3 | 12.8 | 0.131 | 0.5043 | 14.4308 | 14.2612 | 4.7647 | 46.1353 | 0.30912 | 6.41 | 6.4 | 20.8 | 390.4 | 560 | 604.1391 | -7.882 | 90.0864 | 497.2695 | 95.8172 | 53 | 44 | 4.1 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.0483 | 6.1432 | 38.2568 | 0.36721 | 6.4 | 6.7 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 77.2655 | 662.0184 | 92.7948 | SDS-HAA5 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 3.7 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 4.2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 1.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 4 | 9
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.2575 | [5 empty] | 1998-08-11 | 9:15 | 1026.25 | 25.1 | 57 | 44 | 4.4 | 3.4 | 7.1 | 2.3 |  | 9.4 | 12.8 | 0.75532 | 0.3617 | 14.5641 | 14.5211 | 5.1584 | 40.9416 | 0.35468 | 7.7 | 6.4 | 31.72 | 179.8 | 206.3746 | 720 | 745.5256 | -3.5452 | 84.6299 | 547.5561 | 94.207 | 57 | 52 | 4.4 | 4.79 | 8.01 | 9.4 | 12.8 | 0.13037 | 0.50957 | 14.7385 | 14.695 | 4.7112 | 45.3888 | 0.32376 | 6.4 | 6.6 | 21.32 | 384 | 560 | 600.8835 | -7.3006 | 89.6693 | 492.4418 | 95.6706 | 52 | 44 | 4.4 | 2.31 | 5.7 | 4.61 | 8.01 | 0.41571 | 0.50108 | 14.2154 | 14.1734 | 6.1611 | 37.4389 | 0.37857 | 6.6 | 6.7 | 47.7 | 560 | 720 | 767.6163 | -6.6134 | 76.8867 | 663.8082 | 92.8142 | SDS-HAA6 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 5.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 5.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 1.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 5 | 8
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.2575 | [5 empty] | 1998-08-12 | 9:00 | 1050 | 24.6 | 58 | 45 | 4.4 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.5298 | 4.8917 | 42.2083 | 0.34424 | 7.7 | 6.4 | 31.2 | 179.8 | 197.707 | 720 | 704.4673 | 2.1573 | 84.2191 | 520.3707 | 94.0043 | 58 | 52 | 4.4 | 4.78 | 8.02 | 9.3 | 12.8 | 0.13043 | 0.51398 | 14.7077 | 14.8826 | 4.7076 | 45.8924 | 0.32429 | 6.4 | 6.5 | 21.32 | 384 | 560 | 600.1609 | -7.1716 | 89.2164 | 492.0804 | 95.6674 | 52 | 45 | 4.4 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.824 | 6.1034 | 37.9966 | 0.36382 | 6.5 | 6.7 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 75.8734 | 658.0436 | 92.7512 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | 13 | 6 | 7
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | [5 empty] | 1998-08-13 | 9:30 | 1074.5 | 25.1 | 57 | 45 | 4.4 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.3166 | 6.2069 | 40.3931 | 0.35443 | 7.9 | 6.4 | 31.2 | 179.8 | 242.4728 | 720 | 885.4768 | -22.9829 | 87.1326 | 651.8855 | 95.2139 | 57 | 52 | 4.4 | 4.69 | 8.11 | 9.3 | 12.8 | 0.131 | 0.5043 | 14.4308 | 14.3882 | 4.7613 | 45.3387 | 0.31735 | 6.4 | 6.6 | 21.06 | 390.4 | 560 | 603.9887 | -7.8551 | 91.3145 | 497.1944 | 95.7642 | 52 | 45 | 4.4 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.1734 | 6.1432 | 37.9568 | 0.37341 | 6.6 | 6.7 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 80.3277 | 662.0184 | 92.7948 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | 12 | 5 | 7
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 7.1288 | [5 empty] | 1998-08-14 | 12:00 | 1101 | 26 | 57 | 45 | 4 | 3.5 | 7 | 2.2 |  | 9.2 | 12.7 | 0.76087 | 0.38043 | 14.359 | 13.9408 | 4.4204 | 42.5796 | 0.3274 | 7.7 | 6.5 | 28.08 | 174 | 174 | 720 | 638.2909 | 11.3485 | 83.8621 | 470.1225 | 94.0271 | 57 | 51 | 4 | 4.78 | 7.92 | 9.2 | 12.7 | 0.12918 | 0.51957 | 14.7077 | 14.2793 | 4.5275 | 45.4725 | 0.31402 | 6.5 | 6.8 | 23.4 | 371.2 | 595 | 581.1096 | 2.3345 | 86.5517 | 476.1548 | 95.0856 | 51 | 45 | 4 | 2.22 | 5.7 | 4.42 | 7.92 | 0.41299 | 0.50226 | 13.6615 | 13.2636 | 6.5388 | 37.4612 | 0.35406 | 6.8 | 6.7 | 47.7 | 595 | 720 | 808.1589 | -12.2443 | 72.5862 | 701.5795 | 93.2011 | [110 empty] | 12 | 6 | 6
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1998-08-15 | 11:15 | 1124.25 | 25.8 | 57 | 47 | 3.5 | 3.5 | 7.1 | 2.2 |  | 9.3 | 12.8 | 0.76344 | 0.37634 | 14.5641 | 14.2237 | 4.8289 | 43.6711 | 0.3257 | 7.7 | 6.4 | 30.68 | 179.8 | 188.7535 | 720 | 698.8999 | 2.9306 | 83.746 | 513.5733 | 94.0262 | 57 | 51 | 3.5 | 4.79 | 8.01 | 9.3 | 12.8 | 0.13037 | 0.51505 | 14.7385 | 14.394 | 4.7673 | 45.7327 | 0.31474 | 6.4 | 6.8 | 23.4 | 390.4 | 577.5 | 609.8669 | -5.6047 | 87.6029 | 500.1335 | 95.3212 | 51 | 47 | 3.5 | 2.31 | 5.7 | 4.51 | 8.01 | 0.41571 | 0.5122 | 14.2154 | 13.8832 | 6.3715 | 39.1285 | 0.35481 | 6.8 | 6.8 | 47.7 | 577.5 | 720 | 792.2084 | -10.0289 | 74.7289 | 684.8542 | 93.035 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [19 empty] | 10 | 6 | 4
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 2.1288 | [5 empty] | 1998-08-16 | 11:30 | 1148.5 | 26 | 56 | 44 | 4.1 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.1399 | 7.0258 | 38.8742 | 0.36374 | 7.8 | 6.4 | 31.2 | 179.8 | 268.3787 | 792 | 1000.5392 | -26.3307 | 88.3746 | 733.7831 | 95.7481 | 56 | 52 | 4.1 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 14.3092 | 4.867 | 45.033 | 0.31775 | 6.4 | 6.6 | 21.06 | 396.8 | 560 | 618.7229 | -10.4862 | 92.1529 | 507.7614 | 95.8524 | 52 | 44 | 4.1 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 13.8013 | 6.1432 | 37.7568 | 0.36553 | 6.6 | 6.7 | 47.7 | 560 | 792 | 764.0367 | 3.5307 | 82.2266 | 662.0184 | 92.7948 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [14 empty] | 12 | 4 | 8
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 6.3863 | [5 empty] | 1998-08-17 | 9:15 | 1170.25 | 25.1 | 57 | 44 | 4.5 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.3166 | 5.4331 | 40.5669 | 0.35291 | 7.7 | 6.4 | 30.68 | 179.8 | 215.6135 | 720 | 778.4548 | -8.1187 | 85.7708 | 573.9851 | 94.6549 | 57 | 52 | 4.5 | 4.78 | 8.02 | 9.3 | 12.8 | 0.13043 | 0.51398 | 14.7077 | 14.6643 | 4.8839 | 45.1161 | 0.32503 | 6.4 | 6.7 | 20.54 | 396.8 | 560 | 621.0547 | -10.9026 | 90.4737 | 508.9274 | 95.9641 | 52 | 44 | 4.5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.6212 | 6.1034 | 37.3966 | 0.36424 | 6.7 | 6.8 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 77.8771 | 658.0436 | 92.7512 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [13 empty] | 13 | 5 | 8
|  |  |  | System feed flow rate, QF-sys (gpm) | 8.515 | [5 empty] | 1998-08-18 | 9:15 | 1194.25 | 24.6 | 57 | 45 | 4.9 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.7373 | 4.9113 | 41.1887 | 0.3578 | NA | 6.4 | 31.72 | 179.8 | 197.5165 | 720 | 709.3229 | 1.4829 | 83.9406 | 522.8508 | 93.9333 | 57 | 53 | 4.9 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 14.9138 | 4.7774 | 45.3226 | 0.32906 | 6.4 | 6.5 | 21.58 | 390.4 | 560 | 608.2357 | -8.6135 | 89.0743 | 499.3179 | 95.6781 | 53 | 45 | 4.9 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.3845 | 6.1432 | 37.9568 | 0.37897 | 6.4 | 6.8 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 75.8501 | 662.0184 | 92.7948 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [13 empty] | 12 | 4 | 8
[11 empty] | 1998-08-19 | 9:30 | 1218.5 | 24.2 | 57 | 45 | 4.9 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.9126 | 5.4515 | 40.6485 | 0.36687 | 7.5 | 6.4 | 31.2 | 179.8 | 215.2326 | 720 | 783.3331 | -8.7963 | 85.5041 | 576.3507 | 94.5866 | 57 | 53 | 4.9 | 4.74 | 8.16 | 9.4 | 12.9 | 0.13193 | 0.50426 | 14.5846 | 14.9336 | 4.9246 | 45.1754 | 0.33057 | 6.4 | 6.7 | 21.58 | 403.2 | 560 | 624.8763 | -11.5851 | 89.9736 | 514.0382 | 95.8019 | 53 | 45 | 4.9 | 2.33 | 5.83 | 4.66 | 8.16 | 0.4242 | 0.5 | 14.3385 | 14.6816 | 6.1467 | 37.9533 | 0.38683 | 6.7 | 6.8 | 47.7 | 560 | 720 | 764.7443 | -6.2145 | 77.8379 | 662.3721 | 92.7986 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [13 empty] | 12 | 4 | 8
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-08-20 | 9:50 | 1242.8333 | 25 | 57 | 45 | 5 | 3.5 | 7.1 | 2.2 |  | 9.3 | 12.8 | 0.76344 | 0.37634 | 14.5641 | 14.5641 | 6.1796 | 39.8204 | 0.36574 | 7.6 | 6.4 | 28.08 | 185.6 | 230.3666 | 720 | 883.2005 | -22.6667 | 87.8107 | 646.0382 | 95.6535 | 57 | 52 | 5 | 4.88 | 7.92 | 9.3 | 12.8 | 0.1298 | 0.52473 | 15.0154 | 15.0154 | 4.4025 | 45.0975 | 0.33295 | 6.4 | 6.8 | 21.84 | 358.4 | 560 | 565.7754 | -1.0313 | 90.5195 | 462.0877 | 95.2736 | 52 | 45 | 5 | 2.22 | 5.7 | 4.42 | 7.92 | 0.41299 | 0.50226 | 13.6615 | 13.6615 | 6.1206 | 37.3794 | 0.36548 | 6.8 | 6.8 | 47.7 | 560 | 720 | 759.5274 | -5.4899 | 79.2939 | 659.7637 | 92.7701 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [13 empty] | 12 | 5 | 7
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.35 | [5 empty] | 1998-08-21 | 8:00 | 1265 | 23.7 | 57 | 45 | 5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 15.1346 | 5.8105 | 40.1895 | 0.37658 | 7.6 | 6.4 | 30.68 | 191.4 | 226.8323 | 720 | 832.346 | -15.6036 | 86.4746 | 611.7325 | 94.9847 | 57 | 52 | 5 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.6036 | 5.0573 | 44.4427 | 0.35109 | 6.4 | 6.8 | 21.84 | 409.6 | 560 | 645.5437 | -15.2757 | 90.3717 | 527.5719 | 95.8603 | 52 | 45 | 5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 14.1967 | 6.1034 | 37.3966 | 0.37963 | 6.8 | 6.8 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 78.9713 | 658.0436 | 92.7512 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [13 empty] | 12 | 5 | 7
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 4.75 | [5 empty] | 1998-08-22 | 20:00 | 1301 | 24.6 | 58 | 44 | 4.7 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.7373 | 6.2541 | 40.0459 | 0.36801 | 7.5 | 6.41 | 30.68 | 179.8 | 241.806 | 720 | 893.543 | -24.1032 | 87.3121 | 656.0884 | 95.3238 | 58 | 53 | 4.7 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.194 | 4.7268 | 46.0732 | 0.32978 | 6.41 | 6.7 | 21.58 | 384 | 560 | 604.5249 | -7.9509 | 91.0755 | 494.2624 | 95.6339 | 53 | 44 | 4 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.824 | 6.1034 | 38.3966 | 0.36003 | 6.7 | 6.8 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 80.2734 | 658.0436 | 92.7512 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [13 empty] | 14 | 5 | 9
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 10 | [5 empty] | 1998-08-23 | 12:00 | 1317 | 25.6 | 58 | 45 | 3.9 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.3081 | 6.5165 | 41.0835 | 0.34827 | 7.7 | 6.4 | 30.68 | 179.8 | 250.6637 | 720 | 929.7438 | -29.1311 | 87.7605 | 682.327 | 95.5036 | 58 | 52 | 3.9 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 14.4794 | 4.7774 | 46.3226 | 0.31258 | 6.4 | 6.7 | 21.58 | 390.4 | 560 | 608.2357 | -8.6135 | 91.3909 | 499.3179 | 95.6781 | 52 | 45 | 3.9 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 13.9655 | 6.1432 | 38.4568 | 0.36315 | 6.7 | 6.8 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 80.9705 | 662.0184 | 92.7948 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [13 empty] | 13 | 6 | 7
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-08-24 | 11:00 | 1340 | 25.4 | 58 | 45 | 3.9 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.3929 | 5.4669 | 42.1331 | 0.34161 | 7.7 | 6.4 | 30.68 | 179.8 | 215.2326 | 720 | 784.9383 | -9.0192 | 85.7457 | 577.3711 | 94.6863 | 58 | 52 | 3.9 | 4.79 | 8.11 | 9.4 | 12.9 | 0.13162 | 0.50957 | 14.7385 | 14.5652 | 4.7774 | 46.3226 | 0.31443 | 6.4 | 6.7 | 21.58 | 390.4 | 560 | 608.2357 | -8.6135 | 89.9736 | 499.3179 | 95.6781 | 52 | 45 | 3.9 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.0483 | 6.1432 | 38.4568 | 0.3653 | 6.7 | 6.8 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 77.8379 | 662.0184 | 92.7948 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [13 empty] | 13 | 6 | 7
|  |  |  | Design permeate pressure, Pp (psi) | [6 empty] | 1998-08-25 | 11:00 | 1364 | 25 | 56 | 44 | 4 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.5641 | 6.7789 | 39.2211 | 0.37133 | 7.7 | 6.4 | 30.68 | 179.8 | 259.5213 | 720 | 965.9443 | -34.1589 | 88.1782 | 708.5654 | 95.6701 | 56 | 51 | 4 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.0154 | 4.8103 | 44.6897 | 0.33599 | 6.4 | 6.7 | 21.58 | 390.4 | 560 | 614.8192 | -9.7891 | 91.6847 | 502.6096 | 95.7064 | 51 | 44 | 4 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.6615 | 6.1034 | 37.3966 | 0.36532 | 6.7 | 6.8 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 81.62 | 658.0436 | 92.7512 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [13 empty] | 12 | 5 | 7
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 19 | [5 empty] | 1998-08-26 | 8:00 | 1385 | 24.1 | 59 | 45 | 5.9 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.7461 | 4.907 | 41.193 | 0.35798 | 7.4 | 6.3 | 30.68 | 179.8 | 197.707 | 720 | 706.0499 | 1.9375 | 84.4821 | 521.3784 | 94.1156 | 59 | 53 | 5.9 | 4.69 | 8.11 | 9.3 | 12.8 | 0.131 | 0.5043 | 14.4308 | 14.8198 | 5.0089 | 45.0911 | 0.32866 | 6.3 | 6.7 | 21.06 | 409.6 | 560 | 634.2921 | -13.2664 | 89.3479 | 521.946 | 95.9651 | 53 | 45 | 5.9 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.5986 | 6.1432 | 36.9568 | 0.39502 | 6.7 | 6.8 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 75.8734 | 662.0184 | 92.7948 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [13 empty] | 14 | 6 | 8
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 48.5185 | [5 empty] | 1998-08-27 | 10:30 | 1411.5 | 25.6 | 58 | 45 | 5.9 | 3.6 | 7 | 2.2 |  | 9.2 | 12.8 | 0.76087 | 0.3913 | 14.359 | 14.1066 | 5.9057 | 39.6943 | 0.35538 | 7.4 | 6.4 | 30.68 | 179.8 | 225.0533 | 720 | 843.5138 | -17.1547 | 86.3677 | 621.2545 | 95.0616 | 58 | 53 | 5.9 | 4.69 | 8.11 | 9.2 | 12.8 | 0.131 | 0.50978 | 14.4308 | 14.1771 | 4.7608 | 44.8392 | 0.31618 | 6.4 | 6.7 | 21.1 | 390.4 | 560 | 603.9656 | -7.851 | 90.6244 | 497.1828 | 95.7561 | 53 | 45 | 5.9 | 2.31 | 5.8 | 4.51 | 8.11 | 0.42178 | 0.5122 | 14.2154 | 13.9655 | 6.1432 | 36.9568 | 0.37789 | 6.7 | 6.8 | 47.7 | 560 | 720 | 764.0367 | -6.1162 | 78.805 | 662.0184 | 92.7948 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 26.65 | [5 empty] | 1998-08-28 | 8:00 | 1433 | 24.2 | 57 | 45 | 4 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.7026 | 5.17 | 41.83 | 0.35148 | 7.7 | 6.3 | 30.68 | 179.8 | 206.6603 | 792 | 742.2525 | 6.2812 | 85.1544 | 547.6819 | 94.3982 | 57 | 53 | 4 | 4.69 | 8.11 | 9.3 | 12.8 | 0.131 | 0.5043 | 14.4308 | 14.7761 | 5.0055 | 45.9945 | 0.32126 | 6.3 | 6.5 | 21.32 | 409.6 | 560 | 634.1417 | -13.2396 | 89.6836 | 521.8709 | 95.9147 | 53 | 45 | 4 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.5555 | 6.1432 | 38.8568 | 0.37459 | 6.5 | 6.6 | 47.7 | 560 | 792 | 764.0367 | 3.5307 | 76.9186 | 662.0184 | 92.7948 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [13 empty] | 12 | 4 | 8
|  |  |  | Required influent pressure to the system, PI (psi) | 75.1685 | [5 empty] | 1998-08-29 | 8:15 | 1457.25 | 24.5 | 57 | 44 | 4.5 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.5728 | 5.7114 | 40.2886 | 0.36171 | 7.6 | 6.4 | 30.16 | 179.8 | 224.5667 | 720 | 816.2393 | -13.3666 | 86.5697 | 601.2957 | 94.9842 | 57 | 53 | 4.5 | 4.78 | 8.02 | 9.3 | 12.8 | 0.13043 | 0.51398 | 14.7077 | 14.9267 | 4.8805 | 45.6195 | 0.3272 | 6.4 | 6.4 | 20.8 | 396.8 | 560 | 620.8998 | -10.875 | 90.7377 | 508.8499 | 95.9124 | 53 | 44 | 4.5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.8649 | 6.1034 | 37.8966 | 0.36586 | 6.4 | 6.5 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 78.7591 | 658.0436 | 92.7512 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [19 empty] | 13 | 4 | 9
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-08-30 | 9:00 | 1482 | 25.5 | 56 | 44 | 4 | 3.5 | 7.16 | 1.9 |  | 9.06 | 12.56 | 0.79029 | 0.38631 | 14.6872 | 14.4717 | 6.6683 | 39.3317 | 0.36794 | 7.7 | 6.4 | 30.16 | 179.8 | 225.7526 | 792 | 962.8276 | -21.5691 | 86.6402 | 696.9877 | 95.6728 | 56 | 50 | 4 | 3.89 | 8.67 | 9.06 | 12.56 | 0.133 | 0.42936 | 11.9692 | 11.7936 | 4.7539 | 44.2461 | 0.26655 | 6.4 | 6.5 | 21.32 | 409.6 | 560 | 583.811 | -4.252 | 90.556 | 496.7055 | 95.7077 | 50 | 44 | 4 | 2.31 | 6.36 | 5.17 | 8.67 | 0.45574 | 0.44681 | 14.2154 | 14.0068 | 6.0534 | 36.9466 | 0.37911 | 6.5 | 6.6 | 47.7 | 560 | 792 | 746.0712 | 5.7991 | 78.8707 | 653.0356 | 92.6957 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [19 empty] | 12 | 6 | 6
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-08-31 | 9:45 | 1506.75 | 24.9 | 59 | 45 | 4.1 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.6072 | 6.0823 | 41.8177 | 0.34931 | 7.8 | 6.4 | 30.68 | 174 | 236.0063 | 720 | 869.8395 | -20.811 | 87.0003 | 638.908 | 95.1981 | 59 | 54 | 4.1 | 4.7 | 8.2 | 9.4 | 12.9 | 0.13219 | 0.5 | 14.4615 | 14.5043 | 4.7686 | 47.6314 | 0.30451 | 6.4 | 6.7 | 19.76 | 390.4 | 525 | 602.84 | -14.8267 | 91.6273 | 496.62 | 96.0211 | 54 | 45 | 4.1 | 2.4 | 5.8 | 4.7 | 8.2 | 0.42451 | 0.51064 | 14.7692 | 14.813 | 5.7925 | 39.6075 | 0.37399 | 6.7 | 6.7 | 45.05 | 525 | 720 | 723.6 | -0.5 | 80.9115 | 624.3 | 92.7839 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [19 empty] | 14 | 5 | 9
[11 empty] | 1998-09-01 | 9:00 | 1530 | 24.6 | 59 | 45 | 4.5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.7373 | 5.3105 | 42.1895 | 0.34931 | 7.3 | 6.4 | 30.16 | 174 | 209.4327 | 720 | 762.8396 | -5.95 | 85.5992 | 561.2107 | 94.6259 | 59 | 54 | 4.5 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.194 | 4.9209 | 47.0791 | 0.32273 | 6.4 | 6.6 | 19.5 | 396.8 | 560 | 626.3791 | -11.8534 | 90.6891 | 511.5895 | 96.1884 | 54 | 45 | 4.5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.824 | 6.135 | 38.865 | 0.35569 | 6.6 | 6.7 | 45.05 | 560 | 720 | 757.1016 | -5.153 | 78.4895 | 658.5508 | 93.1592 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [19 empty] | 14 | 5 | 9
[11 empty] | 1998-09-02 | 9:15 | 1554.25 | 24.4 | 60 | 45 | 5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.8247 | 5.4977 | 42.0023 | 0.35295 | 7.4 | 6.4 | 29.64 | 179.8 | 215.2326 | 792 | 788.1487 | 0.48627 | 86.2288 | 579.4118 | 94.8845 | 60 | 55 | 5 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.2841 | 4.9976 | 47.5024 | 0.32175 | 6.4 | 6.6 | 20.02 | 403.2 | 560 | 636.3569 | -13.6352 | 90.6984 | 519.7785 | 96.1484 | 55 | 45 | 5 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.906 | 6.1034 | 38.8966 | 0.35751 | 6.6 | 6.7 | 47.7 | 560 | 792 | 756.0872 | 4.5344 | 77.8379 | 658.0436 | 92.7512 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [19 empty] | 15 | 5 | 10
[11 empty] | 1998-09-03 | 9:25 | 1578.4167 | 24.7 | 60 | 45 | 4.6 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.6938 | 6.2695 | 41.6305 | 0.35296 | 7.4 | 6.4 | 30.16 | 179.8 | 241.806 | 720 | 895.1482 | -24.3261 | 87.5272 | 657.1088 | 95.4102 | 60 | 54 | 4.6 | 4.88 | 8.02 | 9.4 | 12.9 | 0.13106 | 0.51915 | 15.0154 | 15.1491 | 4.9107 | 47.4893 | 0.319 | 6.4 | 6.6 | 20.28 | 396.8 | 560 | 625.9044 | -11.7686 | 91.6131 | 511.3522 | 96.034 | 54 | 45 | 4.6 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.7832 | 6.1034 | 38.7966 | 0.35527 | 6.6 | 6.6 | 47.7 | 560 | 720 | 756.0872 | -5.0121 | 80.2734 | 658.0436 | 92.7512 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [19 empty] | 15 | 6 | 9
[11 empty] | 1998-09-05 | 10:00 | 1627 | 25 | 55 | 41 | 3.6 | 3.5 | 6.8 | 1.8 |  | 8.6 | 12.1 | 0.7907 | 0.40698 | 13.9487 | 13.9487 | 6.2813 | 38.1187 | 0.36593 | 7.4 | 7.7 | 26 | 179.8 | 208.8466 | 720 | 899.6003 | -24.9445 | 87.5507 | 654.1258 | 96.0252 | 55 | 50 | 3.6 | 4.58 | 7.52 | 8.6 | 12.1 | 0.12291 | 0.53256 | 14.0923 | 14.0923 | 4.6613 | 44.2387 | 0.31855 | 7.7 | 6.6 | 20.28 | 377.6 | 560 | 595.2231 | -6.2898 | 90.2895 | 486.4115 | 95.8307 | 50 | 41 | 3.6 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 13.6615 | 6.1959 | 35.7041 | 0.38263 | 6.6 | 6.6 | 47.7 | 560 | 720 | 774.586 | -7.5814 | 77.1603 | 667.293 | 92.8517 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [19 empty] | 14 | 5 | 9
[11 empty] | 1998-09-06 | 11:45 | 1652.75 | 25.5 | 58 | 45 | 4.1 | 3.4 | 7.2 | 2.2 |  | 9.4 | 12.8 | 0.76596 | 0.3617 | 14.7692 | 14.5526 | 4.6734 | 42.7266 | 0.3406 | 7.8 | 6.2 | 30.68 | 174 | 182.8583 | 720 | 680.8964 | 5.4311 | 83.222 | 498.023 | 93.8396 | 58 | 54 | 4.1 | 4.98 | 7.82 | 9.4 | 12.8 | 0.12918 | 0.52979 | 15.3231 | 15.0983 | 5.0416 | 46.8584 | 0.32221 | 6.2 | 6.5 | 20.8 | 403.2 | 560 | 646.7233 | -15.4863 | 88.6251 | 524.9616 | 96.0378 | 54 | 45 | 4.1 | 2.22 | 5.6 | 4.42 | 7.82 | 0.40692 | 0.50226 | 13.6615 | 13.4611 | 6.1702 | 39.2298 | 0.34313 | 6.5 | 6.5 | 45.05 | 560 | 720 | 764.1409 | -6.1307 | 75.3634 | 662.0704 | 93.1956 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [19 empty] | 13 | 4 | 9
[90 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio.
[90 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL.
[90 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
Note on A1: S Allgeier 7/19/99: Note that all DBP data reported in this sheet is from SDS tests in which a free chlorine residual was not present at the end of incubation.
Note on H62: sallge: Data not available at this time.
Note on CW29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on CX26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '3.1'.
Note on CX27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was 'NR'.
Note on CX29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '25'.
Note on CX30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.98'.
Note on CX31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '24'.
Note on CX32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '155'.
Note on CX33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '15'.
Note on CX34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '0.78'.
Note on CX35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was 'BMRL'.
Note on CX36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was 'BMRL'.
Note on CX37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '15.78'.
Note on CX38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was 'BMRL'.
Note on CX39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '4.3'.
Note on CX40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '1.6'.
Note on CX41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was 'BMRL'.
Note on CX42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was 'BMRL'.
Note on CX43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.9'.
Note on CX48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual . Original value was '5.9'.
Note on DQ29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on DR26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.6'.
Note on DR27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on DR30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.99'.
Note on DR31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '24'.
Note on DR32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '119'.
Note on DR33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '13'.
Note on DR34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '13'.
Note on DR38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2'.
Note on DR39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.8'.
Note on DR40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.8'.
Note on DR41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.4'.
Note on DR48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.4'.
Note on EK29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on EL26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.8'.
Note on EL27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on EL29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on EL30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.94'.
Note on EL31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '24'.
Note on EL32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '131'.
Note on EL33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17'.
Note on EL34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17'.
Note on EL38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.3'.
Note on EL40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.4'.
Note on EL41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on EL47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.7'.
Note on EL48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.7'.
Note on FE29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on FE31: sallge: SDS incubation time changed to 48 hours beginning 8/24/98.
Note on FF26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.7'.
Note on FF27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on FF29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on FF30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.93'.
Note on FF31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on FF32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '125'.
Note on FF33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '19'.
Note on FF34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '19'.
Note on FF38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.2'.
Note on FF40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.1'.
Note on FF41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on FF47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.3'.
Note on FF48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.3'.
Note on FY29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on FZ26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.5'.
Note on FZ27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on FZ29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on FZ30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.92'.
Note on FZ31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on FZ32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '156'.
Note on FZ33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '23'.
Note on FZ34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.7'.
Note on FZ35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '24.7'.
Note on FZ38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '9.1'.
Note on FZ40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.6'.
Note on FZ41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on FZ47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '13.7'.
Note on FZ48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '13.7'.
Note on GS29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on GT26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.5'.
Note on GT27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on GT29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on GT30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.92'.
Note on GT31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on GT32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '121'.
Note on GT33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '26'.
Note on GT34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.4'.
Note on GT35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '27.4'.
Note on GT38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.2'.
Note on GT40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3'.
Note on GT41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on GT47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '10.2'.
Note on GT48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '10.2'.

## Sheet2. Weeks 11-20
FIELD-SET 2: PILOT-SCALE MEMBRANE RESULTS: WEEKS 11-20 (FILE: mempilot.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 2-4: Foulants And Fouling Indices1 |  | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 2-7: System And Stage Water Quality For Week 12 | [9 empty] | Field 2-7: System And Stage Water Quality For Week 12 (continued) | [7 empty] | Field 2-8: System And Stage Water Quality For Week 14 | [9 empty] | Field 2-8: System And Stage Water Quality For Week 14 (continued) | [7 empty] | Field 2-9: System And Stage Water Quality For Week 16 | [9 empty] | Field 2-9: System And Stage Water Quality For Week 16 (continued) | [7 empty] | Field 2-10: System And Stage Water Quality For Week 18 | [9 empty] | Field 2-10: System And Stage Water Quality For Week 18 (continued) | [7 empty] | Field 2-11: System And Stage Water Quality For Week 20 | [9 empty] | Field 2-11: System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 | [9 empty] | Field 2-12: Duplicate Analysis Of System And Stage Water Quality For Week 20 (continued) | [7 empty] | Field 2-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Fla.Water Services Corp.-Deltona Lakes | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 222 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 | [6 empty] | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 | [6 empty] | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 | [6 empty] | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 | [6 empty] | System recovery during sample collection (decimal) | 0.75 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.5 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL3640287 | Membrane trade name | Fluid Systems 4921S | Temperature normalized MTCW (gfd/psi) | 0.27 | Calcium Hardness (mg/L as CaCO3) | 158 | Cartridge filtration | 5 mm exclusion size | Pilot scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 9.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.98 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.98 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.6 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.06 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.66 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.79 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.5 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.79 |  |  |  |  | Capital Recovery Interest Rate (%) | 7.5 | Pressure Drop
Water Industry Data Base Number (optional) | N/A | Membrane element model number | 4040-TFCS 4921S |  |  | LSI | 0.13 | Sulfuric Acid addition | pH=6.4(@ 75% rec.), 6.2(@ 80% rec.) | Pilot scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 13.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.3 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.3 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.46 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.46 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.4 |  |  |  |  | Capital Recovery Period (years) | 20 | System | Stage 1 | Stage 2
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0 |  |  |  | 1998-09-07 | 11:45 | 1676.75 | 25.6 | 58 | 45 | 4 | 3.5 | 7.1 | 2.2 |  | 9.3 | 12.8 | 0.76344 | 0.37634 | 14.5641 | 14.3081 | 5.7444 | 41.7556 | 0.34266 | 7.8 | 6.4 | 30.68 | 174 | 218.7223 | 720 | 825.5859 | -14.6647 | 85.9731 | 605.1237 | 94.93 | 58 | 53 | 4 | 4.88 | 7.92 | 9.3 | 12.8 | 0.31414 | 0.52473 | 15.0154 | 14.7514 | 4.8381 | 46.6619 | 0.31613 | 6.4 | 6.5 | 20.54 | 390.4 | 560 | 618.2935 | -10.4096 | 90.6091 | 504.3468 | 95.9274 | 53 | 45 | 4 | 2.22 | 5.7 | 4.42 | 7.92 | 0.41299 | 0.50226 | 13.6615 | 13.4214 | 6.1529 | 38.8471 | 0.34549 | 6.5 | 6.5 | 45 | 560 | 720 | 760.5789 | -5.636 | 79.426 | 660.2895 | 93.1848 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15 | 13 | 5 | 8
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0 |  |  |  | 1998-09-08 | 9:15 | 1698.25 | 24.3 | 59 | 45 | 4.5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.8686 | 4.957 | 42.543 | 0.3495 | 7.8 | 6.3 | 30.16 | 179.8 | 197.5005 | 720 | 714.0734 | 0.82313 | 84.7292 | 525.8647 | 94.2647 | 59 | 54 | 4.5 | 4.96 | 7.94 | 9.4 | 12.9 | 0.31595 | 0.52766 | 15.2615 | 15.5806 | 5.015 | 46.985 | 0.33161 | 6.3 | 6.5 | 21.06 | 403.2 | 560 | 641.9172 | -14.6281 | 89.3367 | 522.5586 | 95.9698 | 54 | 45 | 4.5 | 2.14 | 5.8 | 4.44 | 7.94 | 0.41662 | 0.48198 | 13.1692 | 13.4446 | 6.1001 | 38.8999 | 0.34562 | 6.5 | 6.6 | 45 | 560 | 720 | 750.0172 | -4.1691 | 77.2153 | 655.0086 | 93.1299 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 8 | 14 | 5 | 9
Mailing Address |  | Membrane construction (e.g., thin-film composite) | thin film composite | Design average system flux, FW (gfd) | 13.1 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-09-09 | 10:40 | 1723.6667 | 25 | 59 | 45 | 4 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.5641 | 6.3577 | 41.6423 | 0.34974 | 7.7 | 6.4 | 30.16 | 174 | 244.7849 | 720 | 907.3228 | -26.017 | 87.679 | 665.933 | 95.471 | 59 | 54 | 4 | 4.96 | 7.94 | 9.4 | 12.9 | 0.31595 | 0.52766 | 15.2615 | 15.2615 | 5.015 | 47.485 | 0.3214 | 6.4 | 6.5 | 21.06 | 403.2 | 560 | 641.9172 | -14.6281 | 91.3965 | 522.5586 | 95.9698 | 54 | 45 | 4 | 2.14 | 5.8 | 4.44 | 7.94 | 0.41662 | 0.48198 | 13.1692 | 13.1692 | 6.1001 | 39.3999 | 0.33425 | 6.5 | 6.6 | 45 | 560 | 720 | 750.0172 | -4.1691 | 81.6165 | 655.0086 | 93.1299 | Parameter | Units | Cp-sys-12 | CF-sys-12 | CC-sys-12 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-12 | CI-s1-12 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-14 | CF-sys-14 | CC-sys-14 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-14 | CI-s1-14 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-16 | CF-sys-16 | CC-sys-16 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-16 | CI-s1-16 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-18 | CF-sys-18 | CC-sys-18 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-18 | CI-s1-18 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 | CF-sys-20 | CC-sys-20 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 | CI-s1-20 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-20 (dup) | CF-sys-20 (dup) | CC-sys-20 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-20 (dup) | CI-s1-20 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25 | 14 | 5 | 9
|  | Membrane hydrophobicity | hydrophilic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | 0 |  |  |  | 1998-09-10 | 9:15 | 1746.25 | 24.3 | 60 | 46 | 5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.8686 | 5.2192 | 42.7808 | 0.34755 | 7.7 | 6.4 | 30.16 | 179.8 | 206.3496 | 720 | 750.2392 | -4.1999 | 85.384 | 552.0778 | 94.537 | 60 | 54 | 5 | 4.7 | 8.2 | 9.4 | 12.9 | 0.3199 | 0.5 | 14.4615 | 14.7639 | 4.9232 | 47.0768 | 0.31361 | 6.4 | 6.6 | 20.54 | 403.2 | 560 | 622.5295 | -11.166 | 90.046 | 512.8648 | 95.995 | 54 | 46 | 5 | 2.4 | 5.8 | 4.7 | 8.2 | 0.42451 | 0.51064 | 14.7692 | 15.078 | 6.2457 | 38.7543 | 0.38907 | 6.6 | 6.7 | 42.5 | 560 | 720 | 774.1379 | -7.5192 | 79.4039 | 667.069 | 93.6288 | Sampling date | MM/DD/YY | 1998-09-21 | 1998-09-21 | 1998-09-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-21 | 1998-09-21 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-05 | 1998-10-05 | 1998-10-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-05 | 1998-10-05 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-20 | 1998-10-20 | 1998-10-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-20 | 1998-10-20 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-03 | 1998-11-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-03 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-16 | 1998-11-16 | 1998-11-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-16 | 1998-11-16 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-16 | 1998-11-16 | 1998-11-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-16 | 1998-11-16 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15 | 14 | 6 | 8
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1998-09-11 | 8:20 | 1769.3333 | 23.3 | 60 | 46 | 5.2 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 15.0989 | 4.9218 | 42.8782 | 0.35214 | 7.7 | 6.4 | 30.16 | 179.8 | 197.6908 | 720 | 707.5673 | 1.7268 | 84.7439 | 522.3387 | 94.226 | 60 | 55 | 5.2 | 4.69 | 8.11 | 9.3 | 12.8 | 0.31702 | 0.5043 | 14.4308 | 15.1744 | 5.0156 | 47.2844 | 0.32092 | 6.4 | 6.6 | 20.54 | 409.6 | 560 | 634.5928 | -13.3201 | 89.61 | 522.0964 | 96.0659 | 55 | 46 | 5.2 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 14.948 | 6.1876 | 39.1124 | 0.38218 | 6.6 | 6.7 | 44 | 560 | 720 | 765.5103 | -6.3209 | 77.743 | 662.7552 | 93.361 | Sampling time | hh:mm | 9:25 | 9:00 | 9:21 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:12 | 9:05 | --- | --- | --- | --- | Sampling time | hh:mm | 9:15 | 8:50 | 9:10 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:02 | 8:55 | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 8:30 | 8:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:45 | 8:35 | --- | --- | --- | --- | Sampling time | hh:mm | 8:55 | 8:30 | 8:50 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:42 | 8:35 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 9:25 | 9:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:40 | 9:30 | --- | --- | --- | --- | Sampling time | hh:mm | 10:00 | 9:25 | 9:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:40 | 9:30 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 6007.75 | 14 | 5 | 9
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-09-12 | 8:50 | 1793.8333 | 23 | 58 | 45 | 5.4 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 15.2334 | 5.7253 | 40.3747 | 0.3773 | 7.7 | 6.4 | 29.64 | 179.8 | 224.5209 | 720 | 817.6368 | -13.5607 | 86.7986 | 602.1689 | 95.0778 | 58 | 54 | 5.4 | 4.69 | 8.11 | 9.3 | 12.8 | 0.31702 | 0.5043 | 14.4308 | 15.3096 | 5.1806 | 45.4194 | 0.33707 | 6.4 | 6.6 | 20.54 | 422.4 | 560 | 654.795 | -16.9277 | 90.8516 | 538.5975 | 96.1864 | 54 | 45 | 5.4 | 2.31 | 5.8 | 4.61 | 8.11 | 0.42178 | 0.50108 | 14.2154 | 15.0811 | 6.2055 | 37.8945 | 0.39798 | 6.6 | 6.7 | 42.5 | 560 | 720 | 766.1078 | -6.4039 | 81.0708 | 663.0539 | 93.5903 | Operation time | hh.hh | 1991 | 1991 | 1991 | --- | --- | --- | --- | --- | Operation time | hh.hh | 1991 | 1991 | --- | --- | --- | --- | Operation time | hh.hh | 2321 | 2321 | 2321 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2321 | 2321 | --- | --- | --- | --- | Operation time | hh.hh | 2680 | 2680 | 2680 | --- | --- | --- | --- | --- | Operation time | hh.hh | 2680 | 2680 | --- | --- | --- | --- | Operation time | hh.hh | 3017 | 3017 | 3017 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3017 | 3017 | --- | --- | --- | --- | Operation time | hh.hh | 3320 | 3320 | 3320 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3320 | 3320 | --- | --- | --- | --- | Operation time | hh.hh | 3320 | 3320 | 3320 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3320 | 3320 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 124.4 | 13 | 4 | 9
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.70958 | Sulfate (mg/L) | 6.83 |  |  |  | 1998-09-13 | 9:30 | 1818.5 | 25 | 59 | 45 | 4.5 | 3.5 | 7.1 | 2.3 |  | 9.4 | 12.9 | 0.75532 | 0.37234 | 14.5641 | 14.5641 | 6.1111 | 41.3889 | 0.35188 | 7.6 | 6.4 | 29.64 | 174 | 235.9396 | 720 | 872.7776 | -21.2191 | 87.4375 | 640.7514 | 95.3742 | 59 | 53 | 4.5 | 4.96 | 7.94 | 9.4 | 12.9 | 0.31595 | 0.52766 | 15.2615 | 15.2615 | 4.931 | 46.569 | 0.32772 | 6.4 | 6.6 | 21.06 | 396.8 | 560 | 631.5192 | -12.7713 | 91.074 | 514.1596 | 95.904 | 53 | 45 | 4.5 | 2.14 | 5.8 | 4.44 | 7.94 | 0.41662 | 0.48198 | 13.1692 | 13.1692 | 6.1001 | 38.3999 | 0.34295 | 6.6 | 6.6 | 45 | 560 | 720 | 750.0172 | -4.1691 | 80.9273 | 655.0086 | 93.1299 | pH | --- | 6.17 | 6.77 | 7.05 | --- | --- | --- | --- | --- | pH | --- | 6.12 | 6.85 | --- | --- | --- | --- | pH | --- | 5.8 | 6.49 | 6.89 | --- | --- | --- | --- | --- | pH | --- | 5.71 | 6.63 | --- | --- | --- | --- | pH | --- | 5.87 | 6.81 | 7.02 | --- | --- | --- | --- | --- | pH | --- | 6.94 | 6.69 | --- | --- | --- | --- | pH | --- | 5.86 | 6.53 | 7.14 | --- | --- | --- | --- | --- | pH | --- | 6.4 | 7.06 | --- | --- | --- | --- | pH | --- | 5.77 | 6.5 | 6.89 | --- | --- | --- | --- | --- | pH | --- | 5.74 | NA | --- | --- | --- | --- | pH | --- | 5.72 | 6.45 | 6.78 | --- | --- | --- | --- | --- | pH | --- | 5.72 | 6.65 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 15 | 14 | 6 | 8
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4-inch x 40-inch | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.1288 | Calcium (mg/L) | 55 |  |  |  | 1998-09-14 | 11:30 | 1844.5 | 25.4 | 59 | 45 | 4.2 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.1902 | 5.8176 | 41.9824 | 0.338 | 7.6 | 6.4 | 29.64 | 174 | 227.6643 | 756 | 830.3468 | -9.8342 | 86.9808 | 611.4035 | 95.1521 | 59 | 54 | 4.2 | 4.78 | 8.02 | 9.3 | 12.8 | 0.31565 | 0.51398 | 14.7077 | 14.5348 | 4.7907 | 47.5093 | 0.30594 | 6.4 | 6.7 | 21.32 | 390.4 | 560 | 610.3754 | -8.9956 | 90.6353 | 500.3877 | 95.7393 | 54 | 45 | 4.2 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.501 | 6.1654 | 39.1346 | 0.34499 | 6.7 | 6.7 | 42.5 | 560 | 720 | 758.0776 | -5.2886 | 81.3322 | 659.0388 | 93.5512 | Temperature | oC | 24.4 | 24.4 | 24.4 | --- | --- | --- | --- | --- | Temperature | oC | 24.4 | 24.4 | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | 24.6 | --- | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- | Temperature | oC | 23.6 | 23.6 | 23.6 | --- | --- | --- | --- | --- | Temperature | oC | 23.6 | 23.6 | --- | --- | --- | --- | Temperature | oC | 23 | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | 24.6 | --- | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | 24.6 | --- | --- | --- | --- | --- | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 32 | 14 | 5 | 9
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | Barium (mg/L) | 0 |  |  |  | 1998-09-15 | 11:00 | 1868 | 25.5 | 58 | 45 | 4 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.1483 | 6.0803 | 41.4197 | 0.34158 | 7.6 | 6.4 | 29.64 | 174 | 236.6054 | 720 | 866.5002 | -20.3473 | 87.4728 | 637.6712 | 95.3518 | 58 | 52 | 4 | 4.78 | 8.02 | 9.3 | 12.8 | 0.31565 | 0.51398 | 14.7077 | 14.4919 | 4.7941 | 46.2059 | 0.31364 | 6.4 | 6.5 | 21.06 | 390.4 | 560 | 610.5303 | -9.0233 | 91.0991 | 500.4652 | 95.7919 | 52 | 45 | 4 | 2.22 | 5.8 | 4.52 | 8.02 | 0.41905 | 0.49115 | 13.6615 | 13.4611 | 6.1356 | 38.3644 | 0.35088 | 6.5 | 6.5 | 45 | 560 | 720 | 757.1207 | -5.1557 | 80.981 | 658.5603 | 93.1669 | Alkalinity | mg/L as CaCO3 | 17 | 89 | 300 | 305 | -1.6667 | 80.8989 | 227.6269 | 92.5316 | Alkalinity | mg/L as CaCO3 | 14 | 130 | 198.6081 | 84.2697 | 164.304 | 91.4792 | Alkalinity | mg/L as CaCO3 | 16 | 87 | 280 | 311.8333 | -11.369 | 81.6092 | 231.5357 | 93.0896 | Alkalinity | mg/L as CaCO3 | 13 | 140 | 216.0168 | 85.0575 | 178.0084 | 92.697 | Alkalinity | mg/L as CaCO3 | 17 | 90 | 310 | 309 | 0.32258 | 81.1111 | 230.5522 | 92.6264 | Alkalinity | mg/L as CaCO3 | 12 | 140 | 217.6595 | 86.6667 | 178.8297 | 93.2897 | Alkalinity | mg/L as CaCO3 | 17 | 88 | 270 | 301 | -11.4815 | 80.6818 | 224.5669 | 92.4299 | Alkalinity | mg/L as CaCO3 | 12 | 140 | 215.6501 | 86.3636 | 177.8251 | 93.2518 | Alkalinity | mg/L as CaCO3 | 17 | 91 | 310 | 313 | -0.96774 | 81.3187 | 234.306 | 92.7445 | Alkalinity | mg/L as CaCO3 | 14 | NA | #VALUE! | 84.6154 | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 98 | 300 | 338 | -12.6667 | 81.6327 | 252.9254 | 92.8833 | Alkalinity | mg/L as CaCO3 | 14 | 140 | 210.0976 | 85.7143 | 175.0488 | 92.0022 | Electric Rate ($/kW-h) | 0.065 | 13 | 6 | 7
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | Strontium (mg/L) | 0 |  |  |  | 1998-09-16 | 10:45 | 1891.75 | 24.3 | 59 | 46 | 5 | 3.5 | 7 | 2.3 |  | 9.3 | 12.8 | 0.75269 | 0.37634 | 14.359 | 14.6592 | 5.1998 | 42.3002 | 0.34655 | 7.6 | 6.4 | 29.64 | 179.8 | 206.635 | 720 | 745.3155 | -3.516 | 85.6559 | 549.623 | 94.6072 | 59 | 54 | 5 | 4.5 | 8.3 | 9.3 | 12.8 | 0.3199 | 0.48387 | 13.8462 | 14.1356 | 4.8738 | 46.6262 | 0.30317 | 6.4 | 6.7 | 19.76 | 403.2 | 560 | 611.0892 | -9.1231 | 90.4372 | 507.1446 | 96.1037 | 54 | 46 | 5 | 2.5 | 5.8 | 4.8 | 8.3 | 0.42754 | 0.52083 | 15.3846 | 15.7063 | 6.3207 | 38.6793 | 0.40606 | 6.7 | 6.8 | 40 | 560 | 720 | 784.1379 | -8.908 | 80.6422 | 672.069 | 94.0482 | Total dissolved solids | mg/L | 28 | 250 | 840 | 916 | -9.0476 | 88.8 | 677.4328 | 95.8667 | Total dissolved solids | mg/L | 20 | 380 | 592.9216 | 92 | 486.4608 | 95.8887 | Total dissolved solids | mg/L | 26 | 240 | 850 | 917.6667 | -7.9608 | 89.1667 | 675.6429 | 96.1518 | Total dissolved solids | mg/L | 16 | 360 | 565.9038 | 93.3333 | 462.9519 | 96.5439 | Total dissolved solids | mg/L | 32 | 250 | 870 | 904 | -3.908 | 87.2 | 669.7313 | 95.222 | Total dissolved solids | mg/L | 20 | 390 | 614.4844 | 92 | 502.2422 | 96.0179 | Total dissolved solids | mg/L | 30 | 240 | 800 | 870 | -8.75 | 87.5 | 643.9302 | 95.3411 | Total dissolved solids | mg/L | 16 | 380 | 595.13 | 93.3333 | 487.565 | 96.7184 | Total dissolved solids | mg/L | 30 | 240 | 890 | 870 | 2.2472 | 87.5 | 646.6791 | 95.3609 | Total dissolved solids | mg/L | 17 | NA | #VALUE! | 92.9167 | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 26 | 230 | 920 | 842 | 8.4783 | 88.6957 | 625.0597 | 95.8404 | Total dissolved solids | mg/L | 14 | 370 | 568.0534 | 93.913 | 469.0267 | 97.0151 | Fuel Oil Rate ($/gal) | na | 13 | 5 | 8
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Permeate flow rate from system, Qp-sys (gpm) | 6.3863 | Reactive silica (mg/L as SiO2) | 0 |  |  |  | 1998-09-17 | 10:30 | 1915.5 | 24.4 | 59 | 45 | 4.6 | 3.5 | 7.1 | 2.2 |  | 9.3 | 12.8 | 0.76344 | 0.37634 | 14.5641 | 14.8247 | 6.5155 | 40.8845 | 0.3626 | 7.8 | 6.4 | 29.12 | 179.8 | 242.4036 | 720 | 930.7278 | -29.2677 | 87.987 | 680.6725 | 95.7219 | 59 | 54 | 4.6 | 4.88 | 7.92 | 9.3 | 12.8 | 0.31414 | 0.52473 | 15.0154 | 15.2841 | 5.0123 | 46.8877 | 0.32597 | 6.4 | 6.7 | 20.02 | 403.2 | 560 | 639.3008 | -14.1609 | 91.741 | 521.2504 | 96.1592 | 54 | 45 | 4.6 | 2.22 | 5.7 | 4.42 | 7.92 | 0.41299 | 0.50226 | 13.6615 | 13.906 | 6.1828 | 38.7172 | 0.35917 | 6.7 | 6.8 | 42.5 | 560 | 720 | 761.5526 | -5.7712 | 82.4673 | 660.7763 | 93.5682 | Total hardness | mg/L as CaCO3 | 22 | 170 | 620 | 614 | 0.96774 | 87.0588 | 454.9552 | 95.1644 | Total hardness | mg/L as CaCO3 | 14 | 260 | 405.4964 | 91.7647 | 332.7482 | 95.7926 | Total hardness | mg/L as CaCO3 | 18 | 170 | 630 | 651.3333 | -3.3862 | 89.4118 | 479.4286 | 96.2455 | Total hardness | mg/L as CaCO3 | 12 | 270 | 424.4279 | 92.9412 | 347.2139 | 96.5439 | Total hardness | mg/L as CaCO3 | 20 | 180 | 640 | 660 | -3.125 | 88.8889 | 488.0597 | 95.9021 | Total hardness | mg/L as CaCO3 | 11 | 270 | 427.1391 | 93.8889 | 348.5695 | 96.8442 | Total hardness | mg/L as CaCO3 | 20 | 180 | 610 | 660 | -8.1967 | 88.8889 | 487.7563 | 95.8996 | Total hardness | mg/L as CaCO3 | 11 | 280 | 438.9835 | 93.8889 | 359.4917 | 96.9401 | Total hardness | mg/L as CaCO3 | 20 | 180 | 650 | 660 | -1.5385 | 88.8889 | 489.8507 | 95.9171 | Total hardness | mg/L as CaCO3 | 11 | 280 | 429.6527 | 93.8889 | 354.8264 | 96.8999 | Total hardness | mg/L as CaCO3 | 21 | 180 | 650 | 657 | -1.0769 | 88.3333 | 487.9142 | 95.696 | Total hardness | mg/L as CaCO3 | 14 | 270 | 412.4204 | 92.2222 | 341.2102 | 95.897 | Natural Gas Rate ($/ft3) | na | 14 | 5 | 9
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | Feed flow rate to system, QF-sys (gpm) | 8.515 | Turbidity (ntu) | < 0.10 |  |  |  | 1998-09-18 | 11:25 | 1940.4167 | 24.9 | 59 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.813 | 4.4918 | 43.5082 | 0.34046 | 7.2 | 6.4 | 29.12 | 174 | 182.6665 | 720 | 643.3062 | 10.6519 | 84.0584 | 478.3009 | 93.9118 | 59 | 54 | 4 | 4.8 | 8.6 | 9.6 | 13.4 | 0.33354 | 0.5 | 14.7692 | 14.813 | 4.5292 | 47.9708 | 0.30879 | 6.4 | 6.5 | 29.9 | 384 | 560 | 581.6372 | -3.8638 | 83.6314 | 482.8186 | 93.8072 | 54 | 45 | 4 | 2.4 | 6.2 | 4.8 | 8.6 | 0.44877 | 0.5 | 14.7692 | 14.813 | 6.1468 | 39.3532 | 0.37641 | 6.5 | 6.6 | 45 | 560 | 720 | 759.3548 | -5.4659 | 75.3649 | 659.6774 | 93.1785 | Calcium hardness | mg/L as CaCO3 | 16 | 150 | 540 | 552 | -2.2222 | 89.3333 | 408 | 96.0784 | Calcium hardness | mg/L as CaCO3 | 12 | 220 | 343.0214 | 92 | 281.5107 | 95.7373 | Calcium hardness | mg/L as CaCO3 | 14 | 140 | 540 | 539 | 0.18519 | 90 | 396.5 | 96.4691 | Calcium hardness | mg/L as CaCO3 | 10 | 230 | 361.6827 | 92.8571 | 295.8413 | 96.6198 | Calcium hardness | mg/L as CaCO3 | 17 | 150 | 550 | 549 | 0.18182 | 88.6667 | 406.0746 | 95.8136 | Calcium hardness | mg/L as CaCO3 | 11 | 230 | 362.8705 | 92.6667 | 296.4353 | 96.2892 | Calcium hardness | mg/L as CaCO3 | 17 | 150 | 520 | 549 | -5.5769 | 88.6667 | 405.8224 | 95.811 | Calcium hardness | mg/L as CaCO3 | 11 | 240 | 375.3428 | 92.6667 | 307.6714 | 96.4248 | Calcium hardness | mg/L as CaCO3 | 17 | 150 | 560 | 549 | 1.9643 | 88.6667 | 407.5634 | 95.8289 | Calcium hardness | mg/L as CaCO3 | 11 | 240 | 367.3995 | 92.6667 | 303.6998 | 96.378 | Calcium hardness | mg/L as CaCO3 | 18 | 160 | 560 | 586 | -4.6429 | 88.75 | 434.9925 | 95.862 | Calcium hardness | mg/L as CaCO3 | 12 | 230 | 351.2799 | 92.5 | 290.64 | 95.8712 | Current Process Water Rate ($/1000 gal) | 0.45 | 14 | 5 | 9
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.1288 | SDI | na |  |  |  | 1998-09-19 | 10:35 | 1963.5833 | 24.9 | 59 | 45 | 4 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 14.813 | 5.6833 | 42.3167 | 0.35005 | 7.1 | 6.4 | 29.12 | 174 | 217.781 | 720 | 808.3718 | -12.2739 | 86.6288 | 597.4465 | 95.1259 | 59 | 54 | 4 | 4.89 | 8.41 | 9.5 | 13.3 | 0.32914 | 0.51474 | 15.0462 | 15.0907 | 4.739 | 47.761 | 0.31596 | 6.4 | 6.5 | 29.64 | 396.8 | 560 | 610.2854 | -8.9795 | 86.39 | 503.5427 | 94.1137 | 54 | 45 | 4 | 2.31 | 6.1 | 4.61 | 8.41 | 0.43997 | 0.50108 | 14.2154 | 14.2575 | 6.1251 | 39.3749 | 0.3621 | 6.5 | 6.6 | 45 | 560 | 720 | 755.0246 | -4.8645 | 79.337 | 657.5123 | 93.156 | Turbidity | ntu | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.31 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.27 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.12 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | na | 14 | 5 | 9
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 |  |  | MFI | na |  |  |  | 1998-09-20 | 3:00 | 1980 | 27.4 | 59 | 45 | 4.5 | 3.4 | 7.2 | 2.2 |  | 9.4 | 12.8 | 0.76596 | 0.3617 | 14.7692 | 13.7578 | 5.7624 | 41.7376 | 0.32963 | 7.5 | 6.4 | 27.56 | 179.8 | 215.1978 | 720 | 829.2853 | -15.1785 | 87.1932 | 603.8001 | 95.4356 | 59 | 53 | 4.5 | 5.06 | 7.74 | 9.4 | 12.8 | 0.31141 | 0.5383 | 15.5692 | 14.503 | 3.97 | 47.53 | 0.30513 | 6.4 | 6.7 | 20.8 | 320 | 560 | 515.601 | 7.9284 | 90.3345 | 417.8005 | 95.0215 | 53 | 45 | 4.5 | 2.14 | 5.6 | 4.34 | 7.74 | 0.40449 | 0.49309 | 13.1692 | 12.2674 | 6.1936 | 38.3064 | 0.32024 | 6.7 | 6.8 | 40 | 560 | 720 | 758.7143 | -5.377 | 81.4125 | 659.3571 | 93.9335 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 14 | 6 | 8
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI | na | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-09-21 | 10:15 | 2011.25 | 24.4 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.0335 | 5.6601 | 42.2399 | 0.35591 | 7.8 | 6.5 | 29.64 | 179.8 | 223.1237 | 720 | 803.5749 | -11.6076 | 86.7159 | 595.6521 | 95.0239 | 59 | 54 | 4.1 | 4.98 | 8.42 | 9.6 | 13.4 | 0.33081 | 0.51875 | 15.3231 | 15.5973 | 4.8888 | 47.5112 | 0.32829 | 6.5 | 6.8 | 19.5 | 396.8 | 560 | 619.9537 | -10.706 | 91.2605 | 508.3768 | 96.1643 | 54 | 45 | 4.1 | 2.22 | 6.2 | 4.62 | 8.42 | 0.44331 | 0.48052 | 13.6615 | 13.906 | 6.1015 | 39.2985 | 0.35386 | 6.8 | 6.9 | 42.5 | 560 | 720 | 745.2984 | -3.5137 | 80.9523 | 652.6492 | 93.4881 | Total organic carbon | mg/L | BMRL | 1.9 | 7.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.2 | 8.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.3 | 7.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.6 | 8.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.2 | 8.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.3 | 8.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 14 | 5 | 9
Plant Name | Courtland Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 13.76 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 5.6767 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-09-22 | 9:15 | 2034.25 | 24.4 | 59 | 45 | 4.4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.0335 | 5.6601 | 41.9399 | 0.35845 | 7.8 | 6.4 | 29.64 | 179.8 | 223.1237 | 720 | 803.5749 | -11.6076 | 86.7159 | 595.6521 | 95.0239 | 59 | 54 | 4.4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.5903 | 4.9642 | 47.1358 | 0.33075 | 6.4 | 6.8 | 20.02 | 403.2 | 560 | 629.6705 | -12.4412 | 91.0274 | 516.4353 | 96.1234 | 54 | 45 | 4.4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 13.9199 | 6.1024 | 38.9976 | 0.35694 | 6.8 | 6.8 | 42.5 | 560 | 720 | 745.4839 | -3.5394 | 80.9523 | 652.7419 | 93.489 | UV254 | cm-1 | 0.009 | 0.085 | 0.34 | 0.313 | 7.9412 | 89.4118 | 0.23133 | 96.1094 | SUVA | L/(mg*m) | NR | 4.375 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.085 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.087 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.1176 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.083 | 0.31 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.3333 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.086 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | NR | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.086 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8235 | --- | --- | --- | --- |  |  | 14 | 5 | 9
Treatment Plant Category | DIS/GW, OTHER/GW | Feed spacer thickness, T (ft) | 0.00267 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 2.8383 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-09-23 | 10:30 | 2059.5 | 24.8 | 54 | 40 | 4 | 4.2 | 6.6 | 2.1 |  | 8.7 | 12.9 | 0.75862 | 0.48276 | 13.5385 | 13.6187 | 6.0392 | 36.9608 | 0.36846 | 7.5 | 6.4 | 31.72 | 179.8 | 227.6044 | 720 | 843.241 | -17.1168 | 86.0635 | 635.6426 | 95.0098 | 54 | 49 | 4 | 4.6 | 8.3 | 8.7 | 12.9 | 0.32141 | 0.52874 | 14.1538 | 14.2378 | 5.0372 | 42.4628 | 0.3353 | 6.4 | 6.4 | 21.58 | 416 | 560 | 634.5942 | -13.3204 | 90.5186 | 525.2971 | 95.8918 | 49 | 40 | 4 | 2 | 6.3 | 4.1 | 8.3 | 0.4427 | 0.4878 | 12.3077 | 12.3807 | 5.9675 | 34.5325 | 0.35852 | 6.4 | 6.5 | 45 | 560 | 720 | 723.4921 | -0.48501 | 80.2289 | 641.746 | 92.9879 | SUVA | L/(mg*m) | NR | 4.4737 | 4.5333 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.8636 | 3.8824 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.7826 | 4.1772 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.1923 | 3.7805 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.9091 | 4.0741 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.7391 | 3.9286 | --- | --- | --- | --- | --- | [10 empty] | 14 | 5 | 9
Process Train Name | Aeration,Disinfection,Corrosion Control | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | [7 empty] | 1998-09-24 | 11:30 | 2084.5 | 24.2 | 59 | 45 | 4.2 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.1226 | 5.6601 | 42.1399 | 0.35887 | 7.5 | 6.4 | 29.64 | 179.8 | 223.1237 | 720 | 803.5749 | -11.6076 | 86.7159 | 595.6521 | 95.0239 | 59 | 54 | 4.2 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.6827 | 4.9675 | 47.3325 | 0.33133 | 6.4 | 6.5 | 19.76 | 403.2 | 560 | 629.8242 | -12.4686 | 91.1439 | 516.5121 | 96.1743 | 54 | 45 | 4.2 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.0024 | 6.1024 | 39.1976 | 0.35723 | 6.5 | 6.6 | 42.5 | 560 | 720 | 745.4839 | -3.5394 | 80.9523 | 652.7419 | 93.489 | Bromide | mg/L | BMRL | 57 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 64 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 47 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 54 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 53 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 14 | 5 | 9
ICR Treatment Plant Identification Number | 1075 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-09-25 | 7:45 | 2104.75 | 24.2 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.1226 | 5.4219 | 42.4781 | 0.35601 | 7.5 | 6.4 | 29.12 | 179.8 | 214.4605 | 720 | 770.482 | -7.0114 | 86.4217 | 571.3101 | 94.9029 | 59 | 54 | 4.1 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.6827 | 4.9675 | 47.4325 | 0.33063 | 6.4 | 6.6 | 19.76 | 403.2 | 560 | 629.8242 | -12.4686 | 90.7862 | 516.5121 | 96.1743 | 54 | 45 | 4.1 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.0024 | 6.1024 | 39.2976 | 0.35632 | 6.6 | 6.6 | 42.5 | 560 | 720 | 745.4839 | -3.5394 | 80.1828 | 652.7419 | 93.489 | SDS-Cl2 dose | mg/L | 3.6 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.1 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.7 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.9 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4.5 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 4.2 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [9 empty] | 14 | 5 | 9
PWSID Number of Plant (if assigned) | N/A |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 2.3233 | [5 empty] | 1998-09-26 | 8:55 | 2129.9167 | 24.8 | 58 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.8568 | 5.4067 | 42.0933 | 0.35295 | 7.5 | 6.4 | 29.64 | 179.8 | 214.4605 | 720 | 768.922 | -6.7947 | 86.1793 | 570.309 | 94.8028 | 58 | 54 | 4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.4071 | 4.8913 | 47.1087 | 0.32705 | 6.4 | 6.5 | 19.24 | 396.8 | 560 | 619.9489 | -10.7052 | 91.0287 | 508.3745 | 96.2154 | 54 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 13.7563 | 6.1024 | 39.3976 | 0.34917 | 6.5 | 6.6 | 42.5 | 560 | 792 | 745.4839 | 5.8732 | 80.1828 | 652.7419 | 93.489 | SDS-Free Cl2 residual | mg/L | 0.97 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.5 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.77 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.9 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.48 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.71 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.3 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.47 | [6 empty] | 13 | 4 | 9
Historical Minimum Water Temperature (oC) | 17.8 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.1617 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-09-27 | 11:45 | 2156.75 | 25.3 | 59 | 45 | 4.4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.6388 | 5.9973 | 41.6027 | 0.35187 | 7.7 | 6.4 | 29.64 | 174 | 234.6496 | 720 | 849.6785 | -18.0109 | 87.3684 | 629.3696 | 95.2905 | 59 | 54 | 4.4 | 4.8 | 8.6 | 9.6 | 13.4 | 0.33354 | 0.5 | 14.7692 | 14.6388 | 4.8093 | 47.2907 | 0.30955 | 6.4 | 6.5 | 20.8 | 396.8 | 525 | 606.6605 | -15.5544 | 91.1357 | 501.7302 | 95.8543 | 54 | 45 | 4.4 | 2.4 | 6.2 | 4.8 | 8.6 | 0.44877 | 0.5 | 14.7692 | 14.6388 | 5.7887 | 39.3113 | 0.37238 | 6.5 | 6.6 | 40 | 525 | 720 | 712.7419 | 1.0081 | 82.9533 | 618.871 | 93.5366 | SDS-Cl2 demand | mg/L | 2.63 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.33 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.14 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.19 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 2.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 | [6 empty] | 14 | 5 | 9
Historical Average Water Temperature (oC) | 23.5 | Design cross-flow velocity (fps) | 1 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-09-28 | 10:45 | 2179.75 | 25.3 | 59 | 46 | 4.4 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 14.6388 | 5.8423 | 42.2577 | 0.34642 | 7.6 | 6.4 | 29.64 | 179.8 | 223.5797 | 720 | 830.6951 | -15.3743 | 86.743 | 613.8681 | 95.1716 | 59 | 54 | 4.4 | 4.8923 | 8.4077 | 9.5 | 13.3 | 0.32911 | 0.51498 | 15.0533 | 14.9204 | 4.7747 | 47.3253 | 0.31527 | 6.4 | 6.5 | 20.54 | 390.4 | 560 | 605.6159 | -8.1457 | 90.8131 | 498.0079 | 95.8756 | 54 | 46 | 4.4 | 2.3077 | 6.1 | 4.6077 | 8.4077 | 0.4399 | 0.50083 | 14.2012 | 14.0758 | 6.1836 | 39.4164 | 0.35711 | 6.5 | 6.6 | 40 | 560 | 720 | 756.7213 | -5.1002 | 82.1093 | 658.3607 | 93.9243 | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.42 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.32 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.34 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.46 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.61 |  |  |  |  | SDS-Chlorination temp. | oC | 25 | NR | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.61 | [6 empty] | 13 | 5 | 8
State Approved Plant Capacity (MGD) | N/A | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-09-29 | 9:15 | 2202.25 | 24.2 | 59 | 45 | 4.4 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 15.1226 | 5.3148 | 42.2852 | 0.35763 | 7.2 | 6.4 | 29.64 | 179.8 | 206.0701 | 720 | 758.3732 | -5.3296 | 85.6165 | 561.1221 | 94.7177 | 59 | 54 | 4.4 | 4.8923 | 8.4077 | 9.5 | 13.3 | 0.32911 | 0.51498 | 15.0533 | 15.4135 | 4.9366 | 47.1634 | 0.32681 | 6.4 | 6.5 | 20.8 | 403.2 | 560 | 625.7127 | -11.7344 | 89.9063 | 514.4564 | 95.9569 | 54 | 45 | 4.4 | 2.3077 | 6.1 | 4.6077 | 8.4077 | 0.4399 | 0.50083 | 14.2012 | 14.541 | 6.1539 | 38.9461 | 0.37336 | 6.5 | 6.6 | 42.5 | 560 | 720 | 755.7755 | -4.9688 | 79.376 | 657.8878 | 93.5399 | SDS-Chlorination pH | --- | 7.97 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.94 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.02 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.06 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.93 | NR | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.95 | NR | --- | --- | --- | --- | --- | --- | [10 empty] | 14 | 5 | 9
|  | Maximum element recovery (%) | 10 | [7 empty] | 1998-09-30 | 11:11 | 2228.1833 | 25.7 | 60 | 46 | 4.5 | 3.8 | 7.1 | 2.3 |  | 9.4 | 13.2 | 0.75532 | 0.40426 | 14.5641 | 14.2659 | 5.6663 | 42.8337 | 0.33305 | 7.3 | 6.4 | 28.6 | 174 | 218.2466 | 720 | 803.6774 | -11.6219 | 86.8956 | 595.2286 | 95.1951 | 60 | 54 | 4.5 | 4.89 | 8.31 | 9.4 | 13.2 | 0.32611 | 0.52021 | 15.0462 | 14.738 | 4.2898 | 48.2102 | 0.3057 | 6.4 | 6.5 | 20.54 | 352 | 560 | 547.0469 | 2.3131 | 90.5886 | 449.5234 | 95.4307 | 54 | 46 | 4.5 | 2.42 | 5.89 | 4.51 | 8.31 | 0.43057 | 0.53659 | 14.8923 | 14.5873 | 6.2381 | 39.2619 | 0.37154 | 6.5 | 6.5 | 42.5 | 560 | 720 | 772.6231 | -7.3088 | 80.5266 | 666.3115 | 93.6216 | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | NR | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [9 empty] | 14 | 6 | 8
|  | Variability of design flux (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-10-01 | 9:15 | 2250.25 | 24.3 | 59 | 46 | 4.5 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 15.078 | 6.3853 | 41.6147 | 0.36232 | 7.1 | 6.4 | 29.12 | 179.8 | 241.086 | 720 | 904.6318 | -25.6433 | 87.9213 | 667.6511 | 95.6384 | 59 | 54 | 4.5 | 5.0571 | 8.2429 | 9.5 | 13.3 | 0.32661 | 0.53233 | 15.5604 | 15.8858 | 4.9712 | 47.0288 | 0.33779 | 6.4 | 6.6 | 22.776 | 403.2 | 560 | 636.597 | -13.678 | 90.5527 | 519.8985 | 95.6191 | 54 | 46 | 4.5 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 13.4625 | 6.1133 | 39.3867 | 0.3418 | 6.6 | 6.6 | 40 | 560 | 720 | 742.6698 | -3.1486 | 83.4084 | 651.3349 | 93.8588 | SDS-TOX | mg Cl- /L | 17 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-12 | CI-s2-12 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 16 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-14 | CI-s2-14 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 35 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-16 | CI-s2-16 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 22 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-18 | CI-s2-18 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 53 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 | CI-s2-20 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 34 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Parameter | Units | Cp-s2-20 (dup) | CI-s2-20 (dup) | CC(calc) | RF (%) | CB | RB (%) |  |  | 13 | 5 | 8
|  | Rejection of reference solute and conditions of test | 500 mg/L NaCl | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 11.485 | [5 empty] | 1998-10-02 | 8:00 | 2273 | 23.8 | 59 | 45 | 4 | 3.8 | 7.1 | 2.3 |  | 9.4 | 13.2 | 0.75532 | 0.40426 | 14.5641 | 15.09 | 7.1298 | 40.8702 | 0.36922 | 7.1 | 7.8 | 29.64 | 179.8 | 268.2705 | 792 | 1004.9125 | -26.8829 | 88.9515 | 742.6233 | 96.0087 | 59 | 53 | 4 | 4.7923 | 8.4077 | 9.4 | 13.2 | 0.32759 | 0.50982 | 14.7456 | 15.278 | 4.7062 | 47.2938 | 0.32304 | 7.8 | 2.6 | 22.88 | 389.12 | 175 | 597.8734 | -241.642 | 91.4713 | 493.4967 | 95.3637 | 53 | 45 | 4 | 2.3077 | 6.1 | 4.6077 | 8.4077 | 0.4399 | 0.50083 | 14.2012 | 14.7139 | 1.5756 | 43.4244 | 0.33884 | 2.6 | 5.7 | 42.5 | 175 | 720 | 225.1261 | 68.7325 | 84.1578 | 200.0631 | 78.7567 | SDS-CHCl3 | mg/L | 2.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-09-21 | 1998-09-21 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 1.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-10-05 | 1998-10-05 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-10-20 | 1998-10-20 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-03 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 9.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-16 | 1998-11-16 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 6.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling date | MM/DD/YY | 1998-11-16 | 1998-11-16 | --- | --- | --- | --- |  |  | 14 | 6 | 8
|  | (e.g., solute type and concentration) |  | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 5.7425 | [5 empty] | 1998-10-03 | 8:45 | 2297.75 | 24.1 | 56 | 45 | 4.5 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.1674 | 7.6868 | 38.3132 | 0.39588 | 7 | 6.4 | 29.64 | 179.8 | 292.4016 | 720 | 1080.6866 | -50.0954 | 89.8633 | 798.3159 | 96.2872 | 56 | 51 | 4.5 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 15.9799 | 4.326 | 44.674 | 0.3577 | 6.4 | 6.5 | 20.02 | 352 | 560 | 553.2345 | 1.2081 | 93.1533 | 452.6172 | 95.5768 | 51 | 45 | 4.5 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.5423 | 6.0986 | 37.4014 | 0.36208 | 6.5 | 6.5 | 40 | 560 | 720 | 739.7235 | -2.7394 | 86.3202 | 649.8618 | 93.8448 | SDS-BDCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:17 | 9:10 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:06 | 9:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:50 | 8:40 | --- | --- | --- | --- | SDS-BDCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 8:45 | 8:40 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:45 | 9:35 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Sampling time | hh:mm | 9:45 | 9:35 | --- | --- | --- | --- |  |  | 11 | 5 | 6
|  | Variability of rejection of reference solute (%) | 15 | [7 empty] | 1998-10-04 | 12:30 | 2325.5 | 25.5 | 59 | 45 | 4.5 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 14.5526 | 5.5786 | 41.9214 | 0.34714 | 7.9 | 6.4 | 29.64 | 179.8 | 214.8253 | 720 | 794.5358 | -10.3522 | 86.2027 | 587.4963 | 94.9549 | 59 | 54 | 4.5 | 5.0571 | 8.2429 | 9.5 | 13.3 | 0.32661 | 0.53233 | 15.5604 | 15.3322 | 4.9236 | 47.0764 | 0.32569 | 6.4 | 6.5 | 20.02 | 396.8 | 560 | 627.9614 | -12.136 | 90.6808 | 512.3807 | 96.0927 | 54 | 45 | 4.5 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 12.9934 | 6.1133 | 38.8867 | 0.33413 | 6.5 | 6.6 | 40 | 560 | 720 | 742.6698 | -3.1486 | 81.3802 | 651.3349 | 93.8588 | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 1991 | 1991 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2321 | 2321 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 2680 | 2680 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3017 | 3017 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3320 | 3320 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 3320 | 3320 | --- | --- | --- | --- |  |  | 14 | 5 | 9
|  | Standard testing recovery (%) | 10 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-10-05 | 9:30 | 2346.5 | 24.6 | 59 | 45 | 4.4 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 14.9449 | 5.1558 | 42.4442 | 0.35211 | 7.1 | 6.4 | 29.12 | 174 | 200.2709 | 720 | 736.0478 | -2.2289 | 85.4597 | 544.6989 | 94.6539 | 59 | 54 | 4.4 | 4.9778 | 8.3222 | 9.5 | 13.3 | 0.32781 | 0.52398 | 15.3162 | 15.4984 | 4.898 | 47.202 | 0.32834 | 6.4 | 6.6 | 19.76 | 396.8 | 560 | 622.3193 | -11.1284 | 90.1334 | 509.5596 | 96.1221 | 54 | 45 | 4.4 | 2.2222 | 6.1 | 4.5222 | 8.3222 | 0.43731 | 0.4914 | 13.6752 | 13.8379 | 6.1472 | 38.9528 | 0.35525 | 6.6 | 6.6 | 40 | 560 | 720 | 749.4353 | -4.0882 | 80.0271 | 654.7177 | 93.8905 | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.2 | 6.95 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.98 | 6.78 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.07 | 6.89 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.97 | 6.86 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.98 | 6.88 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.89 | 6.76 | --- | --- | --- | --- |  |  | 14 | 5 | 9
|  | Standard testing pH | 7.5 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 2.3233 | [5 empty] | 1998-10-06 | 10:30 | 2371.5 | 25 | 59 | 45 | 4.2 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.7692 | 4.4918 | 43.3082 | 0.34103 | 7.6 | 6.4 | 29.12 | 174 | 182.6665 | 720 | 643.3062 | 10.6519 | 84.0584 | 478.3009 | 93.9118 | 59 | 54 | 4.2 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 15.5604 | 4.8996 | 47.4004 | 0.32828 | 6.4 | 6.6 | 20.8 | 396.8 | 560 | 624.7178 | -11.5568 | 88.6131 | 510.7589 | 95.9276 | 54 | 45 | 4.2 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.1868 | 6.0986 | 39.2014 | 0.33639 | 6.6 | 6.7 | 40 | 560 | 712.8 | 739.7235 | -3.7771 | 78.1022 | 649.8618 | 93.8448 | SDS-THM4 | mg/L | 2.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.4 | 24.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 1.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- | SDS-THM4 | mg/L | 6.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 23.6 | 23.6 | --- | --- | --- | --- | SDS-THM4 | mg/L | 3.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 23 | 23 | --- | --- | --- | --- | SDS-THM4 | mg/L | 11.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- | SDS-THM4 | mg/L | 8.1 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Temperature | oC | 24.6 | 24.6 | --- | --- | --- | --- |  |  | 14 | 5 | 9
|  | Acceptable range of operating pressures | 0 - 350 psi | Maximum system recycle flow rate, (QR-sys)max (gpm) | 5.7425 | [5 empty] | 1998-10-07 | 1:00 | 2386 | 25.7 | 58 | 45 | 4.1 | 3.8 | 7.2 | 2.3 |  | 9.5 | 13.3 | 0.75789 | 0.4 | 14.7692 | 14.4668 | 4.4535 | 42.9465 | 0.33686 | 7.5 | 6.4 | 29.12 | 168.2 | 176.958 | 720 | 639.7553 | 11.1451 | 83.5441 | 474.4706 | 93.8626 | 58 | 54 | 4.1 | 4.9778 | 8.3222 | 9.5 | 13.3 | 0.32781 | 0.52398 | 15.3162 | 15.0026 | 4.8182 | 47.0818 | 0.31865 | 6.4 | 6.5 | 19.5 | 390.4 | 560 | 612.2467 | -9.3298 | 88.9804 | 501.3234 | 96.1103 | 54 | 45 | 4.1 | 2.2222 | 6.1 | 4.5222 | 8.3222 | 0.43731 | 0.4914 | 13.6752 | 13.3952 | 6.1472 | 39.2528 | 0.34125 | 6.5 | 6.6 | 40 | 560 | 720 | 749.4353 | -4.0882 | 77.3958 | 654.7177 | 93.8905 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 190 | 249.4387 | 73.0337 | 219.7194 | 89.077 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 180 | 237.5016 | 74.7126 | 208.7508 | 89.4611 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 25 | 210 | 273.8548 | 72.2222 | 241.9274 | 89.6663 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 190 | 249.0577 | 72.7273 | 219.5288 | 89.0675 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 25 | 200 | 264.1667 | 72.5275 | 232.0833 | 89.228 | SDS-MCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 200 | 264.5333 | 75.5102 | 232.2667 | 89.667 |  |  | 13 | 4 | 9
|  | Acceptable range of operating pH values | 4-11 | Design system recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1998-10-08 | 9:00 | 2418 | 24 | 59 | 45 | 4.1 | 3.7 | 7.2 | 2.4 |  | 9.6 | 13.3 | 0.75 | 0.38542 | 14.7692 | 15.2123 | 5.0002 | 42.8998 | 0.3546 | 7.4 | 6.4 | 28.6 | 174 | 199.9973 | 720 | 714.1892 | 0.80705 | 85.6998 | 528.6162 | 94.5896 | 59 | 54 | 4.1 | 5.0571 | 8.2429 | 9.6 | 13.3 | 0.32661 | 0.52679 | 15.5604 | 16.0273 | 5.0106 | 47.3894 | 0.3382 | 6.4 | 6.5 | 19.76 | 403.2 | 560 | 638.4474 | -14.0085 | 90.1199 | 520.8237 | 96.206 | 54 | 45 | 4.1 | 2.1429 | 6.1 | 4.5429 | 8.2429 | 0.4349 | 0.4717 | 13.1868 | 13.5824 | 6.1133 | 39.2867 | 0.34573 | 6.5 | 6.6 | 40 | 560 | 720 | 742.6698 | -3.1486 | 79.9997 | 651.3349 | 93.8588 | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 46 | 560 | 744.0452 | 81.6 | 652.0226 | 92.945 | SDS-DCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 44 | 530 | 706.8721 | 81.6667 | 618.4361 | 92.8853 | SDS-DCAA* | mg/L | 2.5 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 45 | 570 | 751.2097 | 82 | 660.6048 | 93.1881 | SDS-DCAA* | mg/L | 1.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 48 | 540 | 715.0385 | 80 | 627.5192 | 92.3508 | SDS-DCAA* | mg/L | 2.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 48 | 540 | 720.4 | 80 | 630.2 | 92.3834 | SDS-DCAA* | mg/L | 1.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total dissolved solids | mg/L | 45 | 550 | 735.1667 | 80.4348 | 642.5833 | 92.997 |  |  | 14 | 5 | 9
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 13.515 | [5 empty] | 1998-10-09 | 9:30 | 2442.5 | 24.4 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.0335 | 5.4371 | 42.4629 | 0.35404 | 7.4 | 6.4 | 28.6 | 179.8 | 214.4605 | 720 | 772.042 | -7.2281 | 86.6642 | 572.3113 | 95.0027 | 59 | 54 | 4.1 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.5903 | 5.0471 | 47.3529 | 0.32924 | 6.4 | 6.5 | 20.02 | 409.6 | 560 | 639.8531 | -14.2595 | 90.6649 | 524.7265 | 96.1847 | 54 | 45 | 4.1 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 13.9199 | 6.1319 | 39.2681 | 0.35448 | 6.5 | 6.6 | 40 | 560 | 723.6 | 746.3799 | -3.1481 | 81.3485 | 653.19 | 93.8762 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 37 | 380 | 502.8161 | 78.2353 | 441.4081 | 91.6177 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 32 | 390 | 520.2885 | 81.1765 | 455.1443 | 92.9693 | SDS-TCAA* | mg/L | 2.8 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 32 | 400 | 527.0194 | 82.2222 | 463.5097 | 93.0962 | SDS-TCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 34 | 390 | 516.6538 | 81.1111 | 453.3269 | 92.4999 | SDS-TCAA* | mg/L | 1.6 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 33 | 400 | 534.5667 | 81.6667 | 467.2833 | 92.9379 | SDS-TCAA* | mg/L | 1.4 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total hardness | mg/L as CaCO3 | 34 | 400 | 534.2 | 81.1111 | 467.1 | 92.721 |  |  | 14 | 5 | 9
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.5872 | [5 empty] | 1998-10-10 | 9:30 | 2466.5 | 24.2 | 60 | 45 | 3.96 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.1226 | 4.9916 | 43.5484 | 0.34726 | 7.4 | 6.4 | 29.3644 | 174 | 199.9973 | 720 | 711.896 | 1.1255 | 85.3176 | 528.5293 | 94.4441 | 60 | 53 | 3.96 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 15.9328 | 5.1633 | 47.3767 | 0.3363 | 6.4 | 6.5 | 19.76 | 416 | 560 | 656.1866 | -17.1762 | 90.1199 | 536.0933 | 96.3141 | 53 | 45 | 3.96 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.5024 | 6.0986 | 38.9414 | 0.34674 | 6.5 | 6.6 | 40 | 560 | 720 | 739.7235 | -2.7394 | 79.9997 | 649.8618 | 93.8448 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 320 | 423.8387 | 80 | 371.9194 | 91.9337 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 27 | 330 | 440.2721 | 80.7143 | 385.1361 | 92.9895 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 28 | 340 | 447.6903 | 81.3333 | 393.8452 | 92.8906 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 29 | 340 | 450.6442 | 80.6667 | 395.3221 | 92.6642 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 28 | 340 | 454.4 | 81.3333 | 397.2 | 92.9507 | SDS-MBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 29 | 340 | 454.0333 | 81.875 | 397.0167 | 92.6955 |  |  | 15 | 7 | 8
|  | Maximum permissible turbidity (ntu) | 0 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-10-11 | 12:15 | 2493.25 | 25.6 | 59 | 45 | 4.4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.5096 | 5.4219 | 42.1781 | 0.34401 | 7.8 | 6.4 | 29.12 | 179.8 | 214.4605 | 720 | 770.482 | -7.0114 | 86.4217 | 571.3101 | 94.9029 | 59 | 54 | 4.4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.047 | 4.795 | 47.305 | 0.31808 | 6.4 | 6.6 | 20.28 | 390.4 | 560 | 609.1517 | -8.7771 | 90.5437 | 499.7758 | 95.9422 | 54 | 45 | 4.4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 13.4348 | 6.1319 | 38.9681 | 0.34476 | 6.6 | 6.7 | 40 | 560 | 720 | 746.3799 | -3.6639 | 81.3485 | 653.19 | 93.8762 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.57 | 1.3 | 1.5677 | #VALUE! | 1.4338 | 60.2464 | SDS-DBAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 14 | 5 | 9
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | maximum system recycle flow rates. | [6 empty] | 1998-10-12 | 9:15 | 2514.25 | 23.9 | 59 | 46 | 4.4 | 3.8 | 7.1 | 2.3 |  | 9.4 | 13.2 | 0.75532 | 0.40426 | 14.5641 | 15.0454 | 5.0309 | 43.0691 | 0.34933 | 8 | 6.4 | 29.12 | 179.8 | 197.5005 | 720 | 717.2839 | 0.37724 | 85.2557 | 532.2095 | 94.5285 | 59 | 54 | 4.4 | 4.9571 | 8.2429 | 9.4 | 13.2 | 0.32509 | 0.52736 | 15.2527 | 15.7568 | 5.0503 | 47.0497 | 0.3349 | 6.4 | 6.7 | 21.32 | 409.6 | 560 | 643.1063 | -14.8404 | 89.2051 | 526.3532 | 95.9495 | 54 | 46 | 4.4 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 13.6226 | 6.1133 | 39.4867 | 0.34499 | 6.7 | 6.7 | 40 | 560 | 720 | 742.6698 | -3.1486 | 79.7469 | 651.3349 | 93.8588 | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 5 | 8
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-10-13 | 8:30 | 2537.5 | 23.1 | 59 | 46 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.6224 | 5.4371 | 42.9629 | 0.36363 | 7.9 | 6.4 | 28.6 | 179.8 | 214.4605 | 720 | 772.042 | -7.2281 | 86.6642 | 572.3113 | 95.0027 | 59 | 54 | 4.1 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.201 | 5.1232 | 47.2768 | 0.34269 | 6.4 | 6.7 | 20.54 | 416 | 560 | 649.7283 | -16.0229 | 90.4225 | 532.8642 | 96.1454 | 54 | 46 | 4.1 | 2.22 | 6.2022 | 4.6222 | 8.4222 | 0.44344 | 0.48029 | 13.6615 | 14.4507 | 6.1306 | 39.7694 | 0.36336 | 6.7 | 6.7 | 40 | 560 | 720 | 746.1268 | -3.6287 | 81.3485 | 653.0634 | 93.875 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.013 | 0.2 | 0.26696 | 84.7059 | 0.23348 | 94.432 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.011 | 0.2 | 0.26878 | 87.0588 | 0.23439 | 95.307 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.21 | 0.27834 | 86.2069 | 0.24417 | 95.0854 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.2 | 0.26795 | 89.1566 | 0.23398 | 96.1535 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.2 | 0.26967 | 88.3721 | 0.23483 | 95.7417 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.011 | 0.2 | 0.2693 | 87.2093 | 0.23465 | 95.3122 |  |  | 13 | 5 | 8
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-10-14 | 9:30 | 2562.5 | 23.4 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.4845 | 5.1837 | 42.7163 | 0.3625 | 7.2 | 6.5 | 28.6 | 179.8 | 205.7965 | 720 | 737.3861 | -2.4147 | 86.1028 | 546.966 | 94.7712 | 59 | 54 | 4.1 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.058 | 5.0572 | 47.3428 | 0.33919 | 6.5 | 6.7 | 19.24 | 409.6 | 560 | 640.3141 | -14.3418 | 90.651 | 524.957 | 96.3349 | 54 | 45 | 4.1 | 2.22 | 6.2022 | 4.6222 | 8.4222 | 0.44344 | 0.48029 | 13.6615 | 14.3232 | 6.1306 | 39.2694 | 0.36474 | 6.7 | 6.8 | 40 | 560 | 720 | 746.1268 | -3.6287 | 80.5633 | 653.0634 | 93.875 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.3478 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.1667 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.0385 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7037 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7736 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6364 | --- | --- | --- | --- |  |  | 14 | 5 | 9
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 13.515 | [5 empty] | 1998-10-15 | 9:30 | 2586.5 | 23.2 | 59 | 46 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.5763 | 5.1837 | 43.2163 | 0.36043 | 7.4 | 6.4 | 28.6 | 179.8 | 205.7965 | 720 | 737.3861 | -2.4147 | 86.1028 | 546.966 | 94.7712 | 59 | 54 | 4.1 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.1532 | 5.0437 | 47.3563 | 0.3411 | 6.4 | 6.7 | 20.28 | 409.6 | 560 | 639.6994 | -14.232 | 90.1456 | 524.6497 | 96.1346 | 54 | 46 | 4.1 | 2.22 | 6.2022 | 4.6222 | 8.4222 | 0.44344 | 0.48029 | 13.6615 | 14.4081 | 6.1306 | 39.7694 | 0.36229 | 6.7 | 6.8 | 40 | 560 | 720 | 746.1268 | -3.6287 | 80.5633 | 653.0634 | 93.875 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 5 | 8
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | [5 empty] | 1998-10-16 | 10:00 | 2611 | 23.8 | 59 | 48 | 3.5 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.09 | 5.1498 | 44.8502 | 0.33645 | 7.5 | 6.4 | 28.6 | 179.8 | 206.0701 | 720 | 731.086 | -1.5397 | 86.1212 | 543.5803 | 94.7386 | 59 | 54 | 3.5 | 4.7923 | 8.5077 | 9.5 | 13.3 | 0.33063 | 0.50445 | 14.7456 | 15.278 | 4.8323 | 48.1677 | 0.31718 | 6.4 | 7.2 | 19.76 | 396.8 | 560 | 609.1833 | -8.7827 | 90.411 | 502.9916 | 96.0715 | 54 | 48 | 3.5 | 2.31 | 6.1977 | 4.7077 | 8.5077 | 0.4459 | 0.49069 | 14.2154 | 14.7287 | 6.1691 | 41.3309 | 0.35636 | 7.2 | 6.8 | 40 | 560 | 720 | 753.8141 | -4.6964 | 80.5891 | 656.907 | 93.9109 | SDS-HAA5 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 5.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 1.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 3.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 3.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 11 | 5 | 6
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.2575 | [5 empty] | 1998-10-17 | 9:15 | 2634.25 | 24 | 57 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.2123 | 5.4219 | 41.5781 | 0.36587 | 7.4 | 6.4 | 29.12 | 179.8 | 214.4605 | 720 | 770.482 | -7.0114 | 86.4217 | 571.3101 | 94.9029 | 57 | 52 | 4 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 16.0273 | 5.1532 | 45.3468 | 0.35344 | 6.4 | 6.7 | 20.54 | 416 | 560 | 655.7138 | -17.0917 | 90.4225 | 535.8569 | 96.1669 | 52 | 45 | 4 | 2.14 | 6.2029 | 4.5429 | 8.3429 | 0.44105 | 0.47107 | 13.1692 | 13.5643 | 6.097 | 38.403 | 0.35321 | 6.7 | 6.8 | 40 | 560 | 720 | 739.4012 | -2.6946 | 81.3485 | 649.7006 | 93.8433 | SDS-HAA6 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 5.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 1.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 3.9 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 3.3 | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 12 | 5 | 7
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.2575 | [5 empty] | 1998-10-18 | 12:00 | 2661 | 25.3 | 58 | 46 | 4.2 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.6388 | 4.7453 | 43.0547 | 0.34001 | 7.7 | 6.4 | 29.12 | 174 | 191.3323 | 720 | 677.9692 | 5.8376 | 84.7804 | 503.6515 | 94.2182 | 58 | 54 | 4.2 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 15.4231 | 4.8433 | 46.9567 | 0.32845 | 6.4 | 6.7 | 18.72 | 390.4 | 525 | 615.6992 | -17.276 | 90.216 | 503.0496 | 96.2787 | 54 | 46 | 4.2 | 2.14 | 6.2029 | 4.5429 | 8.3429 | 0.44105 | 0.47107 | 13.1692 | 13.053 | 5.6866 | 40.1134 | 0.3254 | 6.7 | 6.8 | 40 | 525 | 720 | 692.3261 | 3.8436 | 79.094 | 608.6631 | 93.4282 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | 12 | 4 | 8
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | [5 empty] | 1998-10-19 | 10:30 | 2683.5 | 24.4 | 59 | 45 | 4.4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.0335 | 5.1837 | 42.4163 | 0.35443 | 7.8 | 6.4 | 28.6 | 179.8 | 205.7965 | 720 | 737.3861 | -2.4147 | 86.1028 | 546.966 | 94.7712 | 59 | 54 | 4.4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 15.5903 | 4.9709 | 47.1291 | 0.3308 | 6.4 | 6.7 | 19.5 | 403.2 | 525 | 629.9778 | -19.9958 | 90.5246 | 516.5889 | 96.2252 | 54 | 45 | 4.4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 13.9199 | 5.7192 | 39.3808 | 0.35347 | 6.7 | 6.7 | 40 | 525 | 720 | 698.8351 | 2.9396 | 80.5633 | 611.9176 | 93.4632 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | 14 | 5 | 9
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 7.1288 | [5 empty] | 1998-10-20 | 9:30 | 2706.5 | 23.6 | 59 | 46 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.3932 | 5.4371 | 42.9629 | 0.35829 | 7.6 | 6.4 | 28.6 | 179.8 | 214.4605 | 720 | 772.042 | -7.2281 | 86.6642 | 572.3113 | 95.0027 | 59 | 54 | 4.1 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 16.2179 | 5.0765 | 47.3235 | 0.3427 | 6.4 | 6.7 | 20.02 | 409.6 | 560 | 645.7495 | -15.3124 | 90.6649 | 527.6748 | 96.206 | 54 | 46 | 4.1 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.744 | 6.0986 | 39.8014 | 0.34531 | 6.7 | 6.8 | 40 | 560 | 720 | 739.7235 | -2.7394 | 81.3485 | 649.8618 | 93.8448 | [110 empty] | 13 | 5 | 8
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1998-10-21 | 10:30 | 2731.5 | 24.3 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.078 | 4.7605 | 43.1395 | 0.34952 | 7.7 | 6.4 | 28.6 | 174 | 191.3323 | 720 | 679.5292 | 5.6209 | 85.0522 | 504.6527 | 94.3327 | 59 | 54 | 4.1 | 4.77 | 8.63 | 9.6 | 13.4 | 0.334 | 0.49688 | 14.6769 | 14.9838 | 4.8124 | 47.5876 | 0.31487 | 6.4 | 6.7 | 19.76 | 396.8 | 560 | 605.1987 | -8.0712 | 89.6724 | 500.9994 | 96.0559 | 54 | 45 | 4.1 | 2.43 | 6.2 | 4.83 | 8.63 | 0.44967 | 0.50311 | 14.9538 | 15.2665 | 6.219 | 39.181 | 0.38964 | 6.7 | 6.7 | 40 | 560 | 720 | 763.8065 | -6.0842 | 79.094 | 661.9032 | 93.9568 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [19 empty] | 14 | 5 | 9
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 2.1288 | [5 empty] | 1998-10-22 | 8:15 | 2753.25 | 22.8 | 60 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.7616 | 5.0998 | 43.4002 | 0.36317 | 6.9 | 6.4 | 28.6 | 185.6 | 202.9313 | 792 | 725.9251 | 8.3428 | 85.9066 | 538.584 | 94.6898 | 60 | 55 | 4 | 4.8923 | 8.5077 | 9.6 | 13.4 | 0.33214 | 0.50962 | 15.0533 | 16.0647 | 5.1084 | 48.3916 | 0.33197 | 6.4 | 6.8 | 19.24 | 416 | 595 | 644.1549 | -8.2613 | 90.519 | 530.0775 | 96.3703 | 55 | 45 | 4 | 2.3077 | 6.2 | 4.7077 | 8.5077 | 0.44597 | 0.4902 | 14.2012 | 15.1554 | 6.5532 | 39.4468 | 0.3842 | 6.8 | 6.7 | 42.5 | 595 | 792 | 800.6452 | -1.0916 | 79.0569 | 697.8226 | 93.9096 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [14 empty] | 15 | 5 | 10
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 6.3863 | [5 empty] | 1998-10-23 | 8:00 | 2777 | 22.6 | 60 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.855 | 4.9302 | 43.5698 | 0.3639 | 6.9 | 6.4 | 28.6 | 179.8 | 197.1318 | 720 | 702.7272 | 2.399 | 85.4919 | 521.6184 | 94.5171 | 60 | 55 | 4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.4423 | 5.1367 | 48.3633 | 0.33997 | 6.4 | 6.9 | 19.5 | 416 | 595 | 650.343 | -9.3013 | 90.1081 | 533.1715 | 96.3426 | 55 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.6806 | 6.5151 | 39.4849 | 0.3718 | 6.9 | 6.8 | 42.5 | 595 | 720 | 793.0287 | -10.1429 | 78.4408 | 694.0143 | 93.8762 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [13 empty] | 15 | 5 | 10
|  |  |  | System feed flow rate, QF-sys (gpm) | 8.515 | [5 empty] | 1998-10-24 | 8:00 | 2801 | 21.9 | 58 | 45 | 4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.9617 | 4.9815 | 42.5185 | 0.37541 | 7.6 | 6.4 | 28.6 | 174 | 200.2709 | 720 | 708.1308 | 1.6485 | 85.7193 | 526.7522 | 94.5705 | 58 | 54 | 4 | 4.8778 | 8.4222 | 9.5 | 13.3 | 0.32933 | 0.51345 | 15.0085 | 16.4488 | 4.8622 | 47.1378 | 0.34895 | 6.4 | 6.7 | 19.76 | 396.8 | 560 | 615.1649 | -9.8509 | 90.1334 | 505.9824 | 96.0947 | 54 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.9875 | 6.1319 | 39.3681 | 0.3807 | 6.7 | 6.7 | 40 | 560 | 720 | 746.3799 | -3.6639 | 80.0271 | 653.19 | 93.8762 | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [11 empty] | Qp/QT (THM4), % | #VALUE! | #VALUE! |  | Qp/QT (HAA5), % | #VALUE! | #VALUE! | [13 empty] | 13 | 4 | 9
[11 empty] | 1998-10-25 | 11:00 | 2828 | 24.8 | 59 | 46 | 4.4 | 3.8 | 7.1 | 2.3 |  | 9.4 | 13.2 | 0.75532 | 0.40426 | 14.5641 | 14.6505 | 5.0464 | 43.0536 | 0.34028 | 7.9 | 6.4 | 28.6 | 179.8 | 197.5005 | 720 | 718.8891 | 0.15429 | 85.519 | 533.2432 | 94.6366 | 59 | 54 | 4.4 | 4.9571 | 8.2429 | 9.4 | 13.2 | 0.32509 | 0.52736 | 15.2527 | 15.3432 | 4.9041 | 47.1959 | 0.3251 | 6.4 | 6.7 | 19.76 | 396.8 | 525 | 623.5468 | -18.7708 | 89.995 | 510.1734 | 96.1268 | 54 | 46 | 4.4 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 13.265 | 5.7019 | 39.8981 | 0.33247 | 6.7 | 6.8 | 40 | 525 | 720 | 695.3747 | 3.4202 | 79.7469 | 610.1874 | 93.4446 | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-THM4b, mg/L | #VALUE! | #VALUE! |  | SDS-THM4b, mg/L | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1998-10-26 | 9:00 | 2850 | 23.4 | 59 | 46 | 4.4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.2694 | 5.1498 | 42.9502 | 0.35552 | 7.8 | 6.4 | 28.6 | 179.8 | 206.0701 | 720 | 731.086 | -1.5397 | 86.1212 | 543.5803 | 94.7386 | 59 | 54 | 4.4 | 4.9571 | 8.3429 | 9.5 | 13.3 | 0.32813 | 0.5218 | 15.2527 | 15.9914 | 5.0498 | 47.0502 | 0.33988 | 6.4 | 6.6 | 20.28 | 409.6 | 560 | 640.9254 | -14.451 | 90.1587 | 525.2627 | 96.1391 | 54 | 46 | 4.4 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.8255 | 6.0986 | 39.5014 | 0.35 | 6.6 | 6.7 | 40 | 560 | 720 | 739.7235 | -2.7394 | 80.5891 | 649.8618 | 93.8448 | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-HAA5b, mg/L | #VALUE! | #VALUE! |  | SDS-HAA5b, mg/L | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.35 | [5 empty] | 1998-10-27 | 9:15 | 2874.25 | 23.4 | 59 | 46 | 4.5 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.2694 | 5.4189 | 42.5811 | 0.3586 | 7.8 | 6.4 | 28.08 | 179.8 | 214.8253 | 720 | 767.2801 | -6.5667 | 86.9289 | 569.9748 | 95.0735 | 59 | 54 | 4.5 | 4.9571 | 8.3429 | 9.5 | 13.3 | 0.32813 | 0.5218 | 15.2527 | 15.9914 | 5.0127 | 46.9873 | 0.34034 | 6.4 | 6.7 | 23.14 | 409.6 | 560 | 639.2261 | -14.1475 | 89.2285 | 524.413 | 95.5874 | 54 | 46 | 4.5 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.8255 | 6.0986 | 39.4014 | 0.35089 | 6.7 | 6.8 | 40 | 560 | 720 | 739.7235 | -2.7394 | 81.3802 | 649.8618 | 93.8448 | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [11 empty] | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! |  | SDS-TOXb, mg Cl- /L | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 4.75 | [5 empty] | 1998-10-28 | 9:30 | 2898.5 | 24.1 | 59 | 46 | 4.1 | 3.8 | 7 | 2.3 |  | 9.3 | 13.1 | 0.75269 | 0.4086 | 14.359 | 14.7461 | 5.8363 | 42.5637 | 0.34645 | 7.8 | 6.4 | 27.56 | 179.8 | 224.5209 | 720 | 823.9672 | -14.4399 | 87.725 | 611.1867 | 95.4907 | 59 | 54 | 4.1 | 4.8571 | 8.2429 | 9.3 | 13.1 | 0.32358 | 0.52227 | 14.9451 | 15.348 | 4.6394 | 47.7606 | 0.32135 | 6.4 | 6.7 | 19.24 | 377.6 | 560 | 588.7653 | -5.1367 | 91.4306 | 483.1827 | 96.0181 | 54 | 46 | 4.1 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 13.5423 | 6.1133 | 39.7867 | 0.34037 | 6.7 | 6.7 | 40 | 560 | 720 | 742.6698 | -3.1486 | 82.1843 | 651.3349 | 93.8588 | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [11 empty] | SDS-CDb, mg/L | #VALUE! | #VALUE! |  | SDS-CDb, mg/L | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 10 | [5 empty] | 1998-10-29 | 9:15 | 2922.25 | 23.2 | 59 | 46 | 4.1 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 15.36 | 5.6733 | 42.7267 | 0.35949 | 7.8 | 6.4 | 28.6 | 179.8 | 223.5797 | 720 | 800.3944 | -11.1659 | 87.2081 | 595.9265 | 95.2008 | 59 | 54 | 4.1 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 16.0863 | 5.0429 | 47.3571 | 0.33968 | 6.4 | 6.7 | 19.76 | 409.6 | 560 | 638.4908 | -14.0162 | 91.162 | 524.0454 | 96.2293 | 54 | 46 | 4.1 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 13.9074 | 6.0844 | 39.8156 | 0.3493 | 6.7 | 6.7 | 40 | 560 | 720 | 736.8707 | -2.3432 | 82.1093 | 648.4354 | 93.8313 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1998-10-30 | 10:30 | 2947.5 | 23.2 | 57 | 45 | 4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.36 | 5.1498 | 41.8502 | 0.36702 | 7.7 | 6.4 | 28.6 | 179.8 | 206.0701 | 720 | 731.086 | -1.5397 | 86.1212 | 543.5803 | 94.7386 | 57 | 52 | 4 | 4.8778 | 8.4222 | 9.5 | 13.3 | 0.32933 | 0.51345 | 15.0085 | 15.8287 | 4.5354 | 45.9646 | 0.34437 | 6.4 | 6.7 | 19.5 | 371.2 | 560 | 574.8891 | -2.6588 | 90.5372 | 473.0445 | 95.8778 | 52 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.4225 | 6.1319 | 38.3681 | 0.3759 | 6.7 | 6.7 | 40 | 560 | 720 | 746.3799 | -3.6639 | 80.5891 | 653.19 | 93.8762 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [13 empty] | 12 | 5 | 7
|  |  |  | Design permeate pressure, Pp (psi) | [6 empty] | 1998-10-31 | 9:15 | 2970.25 | 23.3 | 57 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.5303 | 5.4523 | 41.5477 | 0.3738 | 7.8 | 6.4 | 28.08 | 179.8 | 214.4605 | 720 | 773.602 | -7.4447 | 86.9067 | 573.3125 | 95.1021 | 57 | 52 | 4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.1055 | 4.5563 | 45.9437 | 0.35055 | 6.4 | 6.7 | 19.5 | 371.2 | 560 | 579.0649 | -3.4044 | 90.9074 | 475.1325 | 95.8959 | 52 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.38 | 6.1319 | 38.3681 | 0.37479 | 6.7 | 6.7 | 40 | 560 | 720 | 746.3799 | -3.6639 | 81.3485 | 653.19 | 93.8762 | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [13 empty] | 12 | 5 | 7
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 19 | [5 empty] | 1998-11-01 | 11:30 | 2996.5 | 25 | 58 | 46 | 4.3 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 14.7692 | 6.02 | 41.68 | 0.35435 | 7.7 | 6.4 | 26 | 179.8 | 231.7861 | 712.8 | 849.1446 | -19.128 | 88.7828 | 628.0013 | 95.8599 | 58 | 54 | 4.3 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 15.5604 | 4.9267 | 46.7733 | 0.33268 | 6.4 | 6.6 | 18.72 | 396.8 | 553 | 625.9786 | -13.1969 | 91.9236 | 511.3893 | 96.3394 | 54 | 46 | 4.3 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.1868 | 6.0165 | 39.6835 | 0.3323 | 6.6 | 6.7 | 40 | 553 | 712.8 | 730.3041 | -2.4557 | 82.7427 | 641.6521 | 93.7661 | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Alkb, mg/L CaCO3 | #VALUE! | #VALUE! | [13 empty] | 12 | 4 | 8
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 48.5185 | [5 empty] | 1998-11-02 | 9:45 | 3018.75 | 24 | 59 | 46 | 4.4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.001 | 5.434 | 42.666 | 0.35159 | 7.8 | 6.4 | 27.56 | 179.8 | 214.8253 | 720 | 768.8184 | -6.7803 | 87.171 | 570.9637 | 95.1731 | 59 | 54 | 4.4 | 4.9571 | 8.3429 | 9.5 | 13.3 | 0.32813 | 0.5218 | 15.2527 | 15.7103 | 4.9736 | 47.1264 | 0.33337 | 6.4 | 6.6 | 19.76 | 403.2 | 560 | 631.0316 | -12.6842 | 90.8018 | 517.1158 | 96.1788 | 54 | 46 | 4.4 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.5824 | 6.0986 | 39.5014 | 0.34385 | 6.6 | 6.7 | 40 | 560 | 720 | 739.7235 | -2.7394 | 81.3802 | 649.8618 | 93.8448 | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | T-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 26.65 | [5 empty] | 1998-11-03 | 8:45 | 3041.75 | 23 | 58 | 45 | 4 | 3.8 | 7.22 | 2.44 |  | 9.66 | 13.46 | 0.74741 | 0.39337 | 14.8103 | 15.7122 | 5.484 | 42.016 | 0.37396 | 7.4 | 6.4 | 24.96 | 179.8 | 214.2453 | 720 | 774.3435 | -7.5477 | 88.3498 | 573.3573 | 95.6467 | 58 | 53 | 4 | 5 | 8.46 | 9.66 | 13.46 | 0.33233 | 0.5176 | 15.3846 | 16.3215 | 4.6527 | 46.8473 | 0.3484 | 6.4 | 6.6 | 18.46 | 377.6 | 553 | 589.8577 | -6.665 | 91.3837 | 483.7288 | 96.1838 | 53 | 45 | 4 | 2.2222 | 6.2378 | 4.66 | 8.46 | 0.44567 | 0.47687 | 13.6752 | 14.508 | 6.0438 | 38.9562 | 0.37242 | 6.6 | 6.7 | 40 | 553 | 720 | 735.7574 | -2.1885 | 81.3298 | 644.3787 | 93.7925 | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [11 empty] | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! |  | Ca-Hdb, mg/L CaCO3 | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Required influent pressure to the system, PI (psi) | 75.1685 | [5 empty] | 1998-11-04 | 8:40 | 3065.6667 | 23.4 | 59 | 46 | 4.2 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.2694 | 5.7571 | 42.5429 | 0.35892 | 7.5 | 6.4 | 28.08 | 182.7 | 226.479 | 723.6 | 813.4094 | -12.4115 | 87.6015 | 603.7914 | 95.3494 | 59 | 54 | 4.2 | 4.8778 | 8.4222 | 9.5 | 13.3 | 0.32933 | 0.51345 | 15.0085 | 15.7354 | 4.5844 | 47.7156 | 0.32978 | 6.4 | 6.7 | 22.1 | 377.6 | 616 | 583.4898 | 5.2776 | 90.2419 | 480.5449 | 95.4011 | 54 | 46 | 4.2 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.3375 | 6.7923 | 39.0077 | 0.36756 | 6.7 | 6.8 | 40 | 616 | 723.6 | 822.4516 | -13.6611 | 82.3383 | 719.2258 | 94.4385 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [19 empty] | 13 | 5 | 8
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1998-11-05 | 9:00 | 3090 | 22.9 | 59 | 46 | 4.4 | 3.8 | 7.1 | 2.3 |  | 9.4 | 13.2 | 0.75532 | 0.40426 | 14.5641 | 15.4968 | 5.8706 | 42.2294 | 0.36697 | 7.5 | 6.4 | 27.56 | 179.8 | 224.0453 | 720 | 830.5868 | -15.3593 | 87.6989 | 614.6213 | 95.5159 | 59 | 53 | 4.4 | 4.9571 | 8.2429 | 9.4 | 13.2 | 0.32509 | 0.52736 | 15.2527 | 16.2295 | 5.074 | 46.526 | 0.34883 | 6.4 | 6.6 | 19.5 | 409.6 | 560 | 644.2009 | -15.0359 | 91.2964 | 526.9004 | 96.2991 | 53 | 46 | 4.4 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 14.0313 | 6.1133 | 38.9867 | 0.3599 | 6.6 | 6.6 | 40 | 560 | 720 | 742.6698 | -3.1486 | 82.1465 | 651.3349 | 93.8588 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [19 empty] | 13 | 6 | 7
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1998-11-06 | 7:45 | 3112.75 | 20.3 | 59 | 46 | 4.4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 16.7347 | 4.9393 | 43.1607 | 0.38773 | 7.5 | 6.3 | 27.56 | 179.8 | 197.3142 | 720 | 699.5038 | 2.8467 | 86.0324 | 521.4888 | 94.7151 | 59 | 53 | 4.4 | 4.8778 | 8.5222 | 9.5 | 13.4 | 0.33236 | 0.51345 | 15.0085 | 17.2454 | 5.014 | 46.586 | 0.37018 | 6.3 | 6.6 | 19.76 | 409.6 | 560 | 632.7288 | -12.9873 | 89.9855 | 521.1644 | 96.2085 | 53 | 46 | 4.4 | 2.2222 | 6.3 | 4.6222 | 8.5222 | 0.44944 | 0.48077 | 13.6752 | 15.7134 | 6.1171 | 38.9829 | 0.40308 | 6.6 | 6.7 | 40 | 560 | 720 | 743.4215 | -3.253 | 79.7278 | 651.7108 | 93.8623 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [19 empty] | 13 | 6 | 7
[11 empty] | 1998-11-07 | 10:15 | 3139.25 | 21.8 | 58 | 45 | 4 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 16.2344 | 5.6372 | 41.8628 | 0.3878 | 7.4 | 6.3 | 27.56 | 185.6 | 220.2595 | 720 | 798.3579 | -10.883 | 87.4875 | 591.2779 | 95.3389 | 58 | 52 | 4 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.8357 | 4.3838 | 46.6162 | 0.36116 | 6.3 | 6.6 | 20.02 | 358.4 | 560 | 558.3924 | 0.28707 | 90.9107 | 458.3962 | 95.6326 | 52 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 15.0319 | 6.1319 | 38.3681 | 0.39178 | 6.6 | 6.6 | 40 | 560 | 720 | 746.3799 | -3.6639 | 81.8396 | 653.19 | 93.8762 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [19 empty] | 13 | 6 | 7
[11 empty] | 1998-11-08 | 11:30 | 3164.5 | 24.2 | 59 | 46 | 4.4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 14.9126 | 5.7895 | 42.3105 | 0.35246 | 7.6 | 6.4 | 27.56 | 174 | 226.5348 | 720 | 815.1685 | -13.2179 | 87.8341 | 606.511 | 95.456 | 59 | 54 | 4.4 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 15.6177 | 4.9668 | 47.1332 | 0.33135 | 6.4 | 6.7 | 19.24 | 403.2 | 553 | 628.6384 | -13.6778 | 91.5068 | 515.9192 | 96.2707 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 13.5024 | 6.0024 | 39.5976 | 0.34099 | 6.7 | 6.8 | 40 | 553 | 720 | 727.4898 | -1.0402 | 82.3427 | 640.2449 | 93.7524 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [19 empty] | 13 | 5 | 8
[11 empty] | 1998-11-09 | 10:15 | 3187.25 | 23.7 | 59 | 46 | 4.4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.1346 | 5.434 | 42.666 | 0.35472 | 7.5 | 6.4 | 27.56 | 179.8 | 214.8253 | 720 | 768.8184 | -6.7803 | 87.171 | 570.9637 | 95.1731 | 59 | 54 | 4.4 | 4.96 | 8.34 | 9.5 | 13.3 | 0.32808 | 0.52211 | 15.2615 | 15.8594 | 4.9746 | 47.1254 | 0.33654 | 6.4 | 6.7 | 19.76 | 403.2 | 560 | 631.2411 | -12.7216 | 90.8018 | 517.2205 | 96.1796 | 54 | 46 | 4.4 | 2.14 | 6.2 | 4.54 | 8.34 | 0.44088 | 0.47137 | 13.1692 | 13.6851 | 6.0974 | 39.5026 | 0.34644 | 6.7 | 6.8 | 40 | 560 | 720 | 739.4839 | -2.7061 | 81.3802 | 649.7419 | 93.8437 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [19 empty] | 13 | 5 | 8
[11 empty] | 1998-11-10 | 10:30 | 3211.5 | 24.2 | 59 | 46 | 4.3 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 14.9126 | 5.6884 | 42.5116 | 0.35079 | 7.5 | 6.4 | 28.08 | 179.8 | 223.5797 | 720 | 801.9328 | -11.3796 | 87.4407 | 596.9195 | 95.2958 | 59 | 54 | 4.3 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 15.6177 | 4.9702 | 47.2298 | 0.33067 | 6.4 | 6.6 | 18.98 | 403.2 | 525 | 628.7911 | -19.7697 | 91.5109 | 515.9955 | 96.3217 | 54 | 46 | 4.3 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 13.5024 | 5.6748 | 40.0252 | 0.33735 | 6.6 | 6.8 | 40 | 525 | 720 | 689.966 | 4.1714 | 82.1093 | 607.483 | 93.4155 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [19 empty] | 13 | 5 | 8
[11 empty] | 1998-11-11 | 9:15 | 3234.25 | 22.2 | 59 | 46 | 4.1 | 3.8 | 7.1 | 2.3 |  | 9.4 | 13.2 | 0.75532 | 0.40426 | 14.5641 | 15.8208 | 5.6063 | 42.7937 | 0.3697 | 7.5 | 6.5 | 27.56 | 179.8 | 215.1978 | 720 | 794.4277 | -10.3372 | 87.1932 | 588.1867 | 95.3144 | 59 | 54 | 4.1 | 4.9571 | 8.2429 | 9.4 | 13.2 | 0.32509 | 0.52736 | 15.2527 | 16.5688 | 4.9806 | 47.4194 | 0.34941 | 6.5 | 6.7 | 20.28 | 403.2 | 560 | 633.4829 | -13.1219 | 90.5761 | 518.3415 | 96.0875 | 54 | 46 | 4.1 | 2.1429 | 6.1 | 4.4429 | 8.2429 | 0.4349 | 0.48232 | 13.1868 | 14.3247 | 6.1133 | 39.7867 | 0.36004 | 6.7 | 6.8 | 40 | 560 | 720 | 742.6698 | -3.1486 | 81.4125 | 651.3349 | 93.8588 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [19 empty] | 13 | 5 | 8
[11 empty] | 1998-11-12 | 10:00 | 3259 | 23.8 | 58 | 46 | 4.4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.09 | 5.2356 | 42.3644 | 0.35619 | 7.4 | 6.4 | 28.6 | 174 | 209.0263 | 720 | 742.7876 | -3.1649 | 86.3175 | 552.1586 | 94.8203 | 58 | 53 | 4.4 | 4.9571 | 8.3429 | 9.5 | 13.3 | 0.32813 | 0.5218 | 15.2527 | 15.8035 | 4.9668 | 46.1332 | 0.34256 | 6.4 | 6.6 | 20.28 | 403.2 | 560 | 630.7227 | -12.629 | 90.2979 | 516.9613 | 96.0771 | 53 | 46 | 4.4 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.663 | 6.0986 | 39.0014 | 0.35032 | 6.6 | 6.8 | 40 | 560 | 720 | 739.7235 | -2.7394 | 80.8637 | 649.8618 | 93.8448 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [19 empty] | 12 | 5 | 7
[11 empty] | 1998-11-13 | 8:30 | 3281.5 | 22.7 | 59 | 46 | 4.1 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 15.5887 | 5.2633 | 43.1367 | 0.36138 | 7.5 | 6.4 | 28.08 | 182.7 | 208.9698 | 720 | 744.102 | -3.3475 | 86.5626 | 554.4096 | 94.9352 | 59 | 54 | 4.1 | 4.7923 | 8.6077 | 9.5 | 13.4 | 0.33366 | 0.50445 | 14.7456 | 15.7829 | 4.9869 | 47.4131 | 0.33288 | 6.4 | 6.7 | 19.5 | 409.6 | 595 | 626.787 | -5.3424 | 90.6685 | 518.1935 | 96.2369 | 54 | 46 | 4.1 | 2.3077 | 6.3 | 4.7077 | 8.6077 | 0.45203 | 0.4902 | 14.2012 | 15.2002 | 6.5369 | 39.3631 | 0.38615 | 6.7 | 6.8 | 42.5 | 595 | 720 | 797.381 | -10.7474 | 79.6621 | 696.1905 | 93.8953 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [19 empty] | 13 | 5 | 8
[11 empty] | 1998-11-14 | 10:55 | 3307.9167 | 24 | 59 | 46 | 4.2 | 3.9 | 7.1 | 2.3 |  | 9.4 | 13.3 | 0.75532 | 0.41489 | 14.5641 | 15.001 | 5.4205 | 42.8795 | 0.34984 | 7.5 | 6.4 | 28.08 | 174 | 209 | 720 | 767.4922 | -6.5961 | 86.5646 | 570.1303 | 95.0748 | 59 | 54 | 4.2 | 4.7923 | 8.5077 | 9.4 | 13.3 | 0.33063 | 0.50982 | 14.7456 | 15.1879 | 4.9177 | 47.3823 | 0.32054 | 6.4 | 6.7 | 19.5 | 403.2 | 595 | 619.3348 | -4.0899 | 90.6699 | 511.2674 | 96.1859 | 54 | 46 | 4.2 | 2.3077 | 6.2 | 4.6077 | 8.5077 | 0.44597 | 0.50083 | 14.2012 | 14.6272 | 6.5532 | 39.2468 | 0.3727 | 6.7 | 6.8 | 42.5 | 595 | 720 | 800.6452 | -11.2007 | 79.6651 | 697.8226 | 93.9096 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [19 empty] | 13 | 5 | 8
[11 empty] | 1998-11-15 | 12:00 | 3333 | 24.7 | 58 | 46 | 4.1 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 14.6938 | 5.1671 | 42.7329 | 0.34385 | 7.6 | 6.4 | 28.6 | 162.4 | 206.1836 | 720 | 731.5349 | -1.6021 | 86.1289 | 545.3096 | 94.7553 | 58 | 53 | 4.1 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 15.3886 | 4.8638 | 46.5362 | 0.33068 | 6.4 | 6.6 | 20.8 | 396.8 | 560 | 617.5648 | -10.2794 | 89.9119 | 507.1824 | 95.8989 | 53 | 46 | 4.1 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 13.3043 | 6.0844 | 39.3156 | 0.3384 | 6.6 | 6.8 | 40 | 560 | 720 | 736.8707 | -2.3432 | 80.5998 | 648.4354 | 93.8313 | [110 empty] | 12 | 5 | 7
Note on A1: S Allgeier 7/19/99: Note that all DBP data reported in this sheet is from SDS tests in which a free chlorine residual was not present at the end of incubation.
Note on CW29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on CX26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on CX27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on CX29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on CX30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.95'.
Note on CX31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on CX32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '116'.
Note on CX33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.9'.
Note on CX34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '5.9'.
Note on CX38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on CX40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on CX47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on CX48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on DQ29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on DR26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.5'.
Note on DR27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on DR30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.03'.
Note on DR31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on DR32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '109'.
Note on DR33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.5'.
Note on DR34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.5'.
Note on DR38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.8'.
Note on DR40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.2'.
Note on DR41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on DR43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'. 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on DR47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.0'.
Note on DR48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.0'.
Note on EK29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on EL26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4'.
Note on EL27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on EL29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on EL30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.97'.
Note on EL31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on EL32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '132'.
Note on EL33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '18'.
Note on EL34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.2'.
Note on EL35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '20.2'.
Note on EL38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.2'.
Note on EL40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '6.1'.
Note on EL41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on EL47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '14.3'.
Note on EL48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '14.3'.
Note on FE29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on FF26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on FF27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on FF29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on FF30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '8.12'.
Note on FF31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on FF32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '101'.
Note on FF33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.5'.
Note on FF34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '2.5'.
Note on FF38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on FF40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FF47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on FF48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.8'.
Note on FY29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on FZ26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.9'.
Note on FZ27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on FZ29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on FZ30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.97'.
Note on FZ31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on FZ32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '165'.
Note on FZ33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '14'.
Note on FZ34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '14'.
Note on FZ38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '13'.
Note on FZ40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.6'.
Note on FZ41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on FZ43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.4'.
Note on FZ47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '17.6'.
Note on FZ48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '19'.
Note on GS29: C. Rice 7/15/99: Verified by Craig Anderson (7/14/99) and Brian Matthews (7/15/99) that SDS temp, pH, and time are measured values.
Note on GT26: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '3.7'.
Note on GT27: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT28: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'NR'.
Note on GT29: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '25'.
Note on GT30: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '7.98'.
Note on GT31: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '48'.
Note on GT32: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '160'.
Note on GT33: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '12'.
Note on GT34: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT35: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT36: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT37: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '12'.
Note on GT38: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT39: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '11'.
Note on GT40: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '4.3'.
Note on GT41: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT42: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was 'BMRL'.
Note on GT43: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '1.4'.
Note on GT47: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '15.3'.
Note on GT48: 11/19/99: Data changed to NR due to incorrect SDS test with no free Cl2 residual. Original value was '16.7'.

## Sheet3. Weeks 21-30
FIELD-SET 3: PILOT-SCALE MEMBRANE RESULTS: WEEKS 21-30 (FILE: mempilot.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 3-4: Foulants And Fouling Indices1 |  | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 3-7: System And Stage Water Quality For Week 22 | [9 empty] | Field 3-7: System And Stage Water Quality For Week 22 (continued) | [7 empty] | Field 3-8: System And Stage Water Quality For Week 24 | [9 empty] | Field 3-8: System And Stage Water Quality For Week 24 (continued) | [7 empty] | Field 3-9: System And Stage Water Quality For Week 26 | [9 empty] | Field 3-9: System And Stage Water Quality For Week 26 (continued) | [7 empty] | Field 3-10: System And Stage Water Quality For Week 28 | [9 empty] | Field 3-10: System And Stage Water Quality For Week 28 (continued) | [7 empty] | Field 3-11: System And Stage Water Quality For Week 30 | [9 empty] | Field 3-11: System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 | [9 empty] | Field 3-12: Duplicate Analysis Of System And Stage Water Quality For Week 30 (continued) | [7 empty] | Field 3-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Fla.Water Services Corp.-Deltona Lakes | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 222 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.52 | [6 empty] | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.76 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.53 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.56 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.56 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL3640287 | Membrane trade name | Fluid Systems 4921S | Temperature normalized MTCW (gfd/psi) | 0.27 | Calcium Hardness (mg/L as CaCO3) | 158 | Cartridge filtration | 5 mm exclusion size | Pilot scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 9.47 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.95 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.96 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 4.96 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.38 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.29 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.29 |  |  |  |  | Capital Recovery Interest Rate (%) | 7.5 | Pressure Drop
Water Industry Data Base Number (optional) | N/A | Membrane element model number | 4040-TFCS 4921S |  |  | LSI | 0.13 | Sulfuric Acid addition | pH=6.4(@ 75% rec.), 6.2(@ 80% rec.) | Pilot scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 13.27 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.27 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 13.4 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13.4 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 |  |  |  |  | Capital Recovery Period (years) | 20 | System | Stage 1 | Stage 2
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0 |  |  |  | 1998-11-16 | 10:50 | 3355.8333 | 24.6 | 59 | 46 | 4.2 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 14.7373 | 5.5078 | 42.7922 | 0.34439 | 7.6 | 6.4 | 28.6 | 156.6 | 217.8933 | 720 | 777.886 | -8.0397 | 86.8743 | 579.3811 | 95.0637 | 59 | 54 | 4.2 | 4.7923 | 8.6077 | 9.5 | 13.4 | 0.33366 | 0.50445 | 14.7456 | 14.9209 | 4.9652 | 47.3348 | 0.31522 | 6.4 | 6.6 | 20.8 | 409.2 | 560 | 625.4406 | -11.6858 | 90.454 | 517.3203 | 95.9793 | 54 | 46 | 4.2 | 2.3077 | 6.3 | 4.7077 | 8.6077 | 0.45203 | 0.4902 | 14.2012 | 14.3701 | 6.1145 | 39.6855 | 0.3621 | 6.6 | 6.7 | 43.2 | 560 | 720 | 749.304 | -4.07 | 80.1738 | 654.652 | 93.4011 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15 | 13 | 5 | 8
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0 |  |  |  | 1998-11-17 | 10:50 | 3379.8333 | 24.2 | 58 | 45 | 4.2 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 14.9126 | 5.0811 | 42.2189 | 0.35322 | 7.4 | 6.4 | 28.6 | 168.2 | 203.2274 | 720 | 719.8334 | 0.023145 | 85.9271 | 536.7081 | 94.6712 | 58 | 52 | 4.2 | 4.7923 | 8.6077 | 9.5 | 13.4 | 0.33366 | 0.50445 | 14.7456 | 15.0984 | 5.0695 | 45.7305 | 0.33016 | 6.4 | 6.7 | 19.24 | 415.8 | 553 | 636.5836 | -15.1146 | 90.5328 | 526.1918 | 96.3435 | 52 | 45 | 4.2 | 2.3077 | 6.3 | 4.7077 | 8.6077 | 0.45203 | 0.4902 | 14.2012 | 14.541 | 6.0447 | 38.2553 | 0.3801 | 6.7 | 6.8 | 42.1 | 553 | 720 | 740.1429 | -2.7976 | 79.2843 | 646.5714 | 93.4887 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 8 | 13 | 6 | 7
Mailing Address |  | Membrane construction (e.g., thin-film composite) | thin film composite | Design average system flux, FW (gfd) | 13.1 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1998-11-18 | 10:30 | 3403.5 | 24.4 | 58 | 45 | 4.2 | 3.9 | 7.1 | 2.3 |  | 9.4 | 13.3 | 0.75532 | 0.41489 | 14.5641 | 14.8247 | 5.682 | 41.618 | 0.35621 | 7.4 | 6.4 | 28.6 | 174 | 218.2466 | 720 | 803.6774 | -11.6219 | 86.8956 | 596.7958 | 95.2077 | 58 | 52 | 4.2 | 4.8778 | 8.4222 | 9.4 | 13.3 | 0.32933 | 0.51891 | 15.0085 | 15.2771 | 5.1106 | 45.6894 | 0.33437 | 6.4 | 6.7 | 19.5 | 415.8 | 553 | 645.3194 | -16.6943 | 91.0652 | 530.5597 | 96.3246 | 52 | 45 | 4.2 | 2.2222 | 6.2 | 4.5222 | 8.4222 | 0.44337 | 0.4914 | 13.6752 | 13.9199 | 6.0116 | 38.2884 | 0.36355 | 6.7 | 6.8 | 43.2 | 553 | 720 | 735.724 | -2.1839 | 80.2059 | 644.362 | 93.2957 | Parameter | Units | Cp-sys-22 | CF-sys-22 | CC-sys-22 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-22 | CI-s1-22 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-24 | CF-sys-24 | CC-sys-24 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-24 | CI-s1-24 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-26 | CF-sys-26 | CC-sys-26 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-26 | CI-s1-26 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-28 | CF-sys-28 | CC-sys-28 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-28 | CI-s1-28 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 | CF-sys-30 | CC-sys-30 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 | CI-s1-30 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-30 (dup) | CF-sys-30 (dup) | CC-sys-30 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-30 (dup) | CI-s1-30 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25 | 13 | 6 | 7
|  | Membrane hydrophobicity | hydrophilic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | 0 |  |  |  | 1998-11-19 | 7:45 | 3424.75 | 22.5 | 59 | 47 | 4.2 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 15.6811 | 5.4337 | 43.3663 | 0.3616 | 7.4 | 6.5 | 28.08 | 179.8 | 214.8253 | 720 | 767.2801 | -6.5667 | 86.9289 | 571.4472 | 95.0862 | 59 | 54 | 4.2 | 4.8778 | 8.5222 | 9.5 | 13.4 | 0.33236 | 0.51345 | 15.0085 | 16.1596 | 5.2769 | 47.0231 | 0.34365 | 6.5 | 6.8 | 18.72 | 429 | 560 | 663.8278 | -18.5407 | 91.2859 | 546.4139 | 96.574 | 54 | 47 | 4.2 | 2.2222 | 6.3 | 4.6222 | 8.5222 | 0.44944 | 0.48077 | 13.6752 | 14.724 | 6.0371 | 40.2629 | 0.3657 | 6.8 | 6.9 | 46.8 | 560 | 720 | 741.0229 | -2.9199 | 78.2149 | 650.5115 | 92.8057 | Sampling date | MM/DD/YY | 1998-11-30 | 1998-11-30 | 1998-11-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-11-30 | 1998-11-30 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-15 | 1998-12-15 | 1998-12-15 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-15 | 1998-12-15 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-28 | 1998-12-28 | 1998-12-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-28 | 1998-12-28 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-11 | 1999-01-11 | 1999-01-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-11 | 1999-01-11 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-25 | 1999-01-25 | 1999-01-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-25 | 1999-01-25 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-25 | 1999-01-25 | 1999-01-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-01-25 | 1999-01-25 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15 | 12 | 5 | 7
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1998-11-20 | 9:30 | 3450.5 | 23.7 | 60 | 45 | 4 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.1346 | 6.0952 | 42.4048 | 0.35691 | 7.4 | 6.4 | 28.08 | 185.6 | 238.1317 | 720 | 859.5345 | -19.3798 | 88.2082 | 637.6049 | 95.596 | 60 | 52 | 4 | 4.8778 | 8.4222 | 9.5 | 13.3 | 0.32933 | 0.51345 | 15.0085 | 15.5965 | 5.2024 | 46.7976 | 0.33328 | 6.4 | 6.9 | 18.98 | 422.4 | 560 | 656.043 | -17.1505 | 92.0296 | 539.2215 | 96.4801 | 52 | 45 | 4 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.2109 | 6.0517 | 38.4483 | 0.36961 | 6.9 | 6.9 | 46.8 | 560 | 720 | 743.9427 | -3.3254 | 80.347 | 651.9713 | 92.8218 | Sampling time | hh:mm | 8:43 | 8:25 | 8:39 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:34 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 9:08 | 8:50 | 9:05 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:58 | 8:53 | --- | --- | --- | --- | Sampling time | hh:mm | 8:58 | 8:30 | 8:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:50 | 8:34 | --- | --- | --- | --- | Sampling time | hh:mm | 9:15 | 8:50 | 9:10 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:03 | 8:55 | --- | --- | --- | --- | Sampling time | hh:mm | 10:34 | 10:05 | 10:26 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:20 | 10:08 | --- | --- | --- | --- | Sampling time | hh:mm | 11:00 | 10:45 | 10:55 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:52 | 10:47 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 6007.75 | 15 | 8 | 7
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1998-11-21 | 9:30 | 3474.5 | 23.7 | 57 | 45 | 4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 15.1346 | 5.3509 | 41.6491 | 0.36339 | 7.4 | 6.4 | 28.08 | 168.2 | 211.9823 | 720 | 756.0264 | -5.0037 | 86.7536 | 563.1749 | 95.014 | 57 | 52 | 4 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 15.8503 | 4.4468 | 46.0532 | 0.34417 | 6.4 | 6.7 | 19.24 | 363 | 553 | 564.8354 | -2.1402 | 90.9238 | 463.9177 | 95.8527 | 52 | 45 | 4 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 13.7034 | 5.965 | 38.535 | 0.35561 | 6.7 | 6.8 | 43.2 | 553 | 720 | 726.4014 | -0.88908 | 79.6209 | 639.7007 | 93.2468 | Operation time | hh.hh | 3655 | 3655 | 3655 | --- | --- | --- | --- | --- | Operation time | hh.hh | 3655 | 3655 | --- | --- | --- | --- | Operation time | hh.hh | 4015 | 4015 | 4015 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4015 | 4015 | --- | --- | --- | --- | Operation time | hh.hh | 4322 | 4322 | 4322 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4322 | 4322 | --- | --- | --- | --- | Operation time | hh.hh | 4655 | 4655 | 4655 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4655 | 4655 | --- | --- | --- | --- | Operation time | hh.hh | 4973 | 4973 | 4973 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4973 | 4973 | --- | --- | --- | --- | Operation time | hh.hh | 4973 | 4973 | 4973 | --- | --- | --- | --- | --- | Operation time | hh.hh | 4973 | 4973 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 124.4 | 12 | 5 | 7
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.70958 | Sulfate (mg/L) | 6.83 |  |  |  | 1998-11-22 | 1:30 | 3490.5 | 24.2 | 59 | 46 | 4.1 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 14.9126 | 5.5047 | 42.8953 | 0.34765 | 7.7 | 6.5 | 28.08 | 174 | 217.781 | 720 | 778.9796 | -8.1916 | 87.1063 | 578.5515 | 95.1465 | 59 | 54 | 4.1 | 4.8778 | 8.4222 | 9.5 | 13.3 | 0.32933 | 0.51345 | 15.0085 | 15.3677 | 4.3962 | 48.0038 | 0.32013 | 6.5 | 6.8 | 22.1 | 363 | 560 | 560.4342 | -0.07753 | 89.8522 | 461.7171 | 95.2135 | 54 | 46 | 4.1 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.0024 | 6.0942 | 39.8058 | 0.35177 | 6.8 | 6.9 | 43.2 | 560 | 720 | 745.233 | -3.5046 | 80.1636 | 652.6165 | 93.3805 | pH | --- | 6.11 | 6.54 | 7.04 | --- | --- | --- | --- | --- | pH | --- | 5.61 | 6.69 | --- | --- | --- | --- | pH | --- | 5.83 | 6.6 | 7 | --- | --- | --- | --- | --- | pH | --- | 5.72 | 6.71 | --- | --- | --- | --- | pH | --- | 5.72 | 6.5 | 6.76 | --- | --- | --- | --- | --- | pH | --- | 6.05 | 6.57 | --- | --- | --- | --- | pH | --- | 5.57 | 6.49 | 6.82 | --- | --- | --- | --- | --- | pH | --- | 5.79 | 6.49 | --- | --- | --- | --- | pH | --- | 5.6 | 6.11 | 6.7 | --- | --- | --- | --- | --- | pH | --- | 5.45 | 6.32 | --- | --- | --- | --- | pH | --- | 5.66 | 6.26 | 6.74 | --- | --- | --- | --- | --- | pH | --- | 5.64 | 6.46 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 15 | 13 | 5 | 8
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4-inch x 40-inch | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.1288 | Calcium (mg/L) | 55 |  |  |  | 1998-11-23 | 10:45 | 3523.75 | 24 | 59 | 46 | 4.3 | 3.8 | 7.1 | 2.4 |  | 9.5 | 13.3 | 0.74737 | 0.4 | 14.5641 | 15.001 | 4.9966 | 43.2034 | 0.34722 | 7.6 | 6.4 | 28.08 | 174 | 200.2709 | 720 | 709.6691 | 1.4348 | 85.979 | 527.7412 | 94.6792 | 59 | 54 | 4.3 | 4.9571 | 8.3429 | 9.5 | 13.3 | 0.32813 | 0.5218 | 15.2527 | 15.7103 | 4.0207 | 48.1793 | 0.32608 | 6.4 | 6.8 | 20.02 | 330 | 560 | 514.1833 | 8.1815 | 90.0035 | 422.0917 | 95.257 | 54 | 46 | 4.3 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.5824 | 6.0611 | 39.6389 | 0.34265 | 6.8 | 6.8 | 43.2 | 560 | 720 | 738.6175 | -2.5858 | 78.4292 | 649.3088 | 93.3468 | Temperature | oC | 22.9 | 22.9 | 22.9 | --- | --- | --- | --- | --- | Temperature | oC | 22.9 | 22.9 | --- | --- | --- | --- | Temperature | oC | 21.2 | 21.2 | 21.2 | --- | --- | --- | --- | --- | Temperature | oC | 21.2 | 21.2 | --- | --- | --- | --- | Temperature | oC | 22 | 22 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 22 | 22 | --- | --- | --- | --- | Temperature | oC | 20.3 | 20.3 | 20.3 | --- | --- | --- | --- | --- | Temperature | oC | 20.3 | 20.3 | --- | --- | --- | --- | Temperature | oC | 22.2 | 22.2 | 22.2 | --- | --- | --- | --- | --- | Temperature | oC | 22.2 | 22.2 | --- | --- | --- | --- | Temperature | oC | 22.2 | 22.2 | 22.2 | --- | --- | --- | --- | --- | Temperature | oC | 22.2 | 22.2 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 32 | 13 | 5 | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | Barium (mg/L) | 0 |  |  |  | 1998-11-24 | 10:45 | 3547.75 | 24.7 | 59 | 46 | 4.4 | 3.8 | 7 | 2.3 |  | 9.3 | 13.1 | 0.75269 | 0.4086 | 14.359 | 14.4869 | 4.7592 | 43.3408 | 0.33425 | 7.6 | 7.8 | 25.48 | 168.2 | 186.0919 | 705.6 | 674.9107 | 4.3494 | 86.3078 | 501.3987 | 94.9182 | 59 | 54 | 4.4 | NA | #VALUE! | 9.3 | 13.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.8 | 7.8 | 16.12 | 442.2 | 525 | #VALUE! | #VALUE! | 91.3376 | #VALUE! | #VALUE! | 54 | 46 | 4.4 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 7.8 | 7.9 | 43.2 | 525 | 705.6 | #VALUE! | #VALUE! | 76.7857 | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 16 | 100 | 340 | 366 | -7.6471 | 84 | 271.0859 | 94.0978 | Alkalinity | mg/L as CaCO3 | 11 | 160 | 248.6478 | 89 | 204.3239 | 94.6164 | Alkalinity | mg/L as CaCO3 | 18 | 100 | 340 | 359.6667 | -5.7843 | 82 | 269.5585 | 93.3224 | Alkalinity | mg/L as CaCO3 | 15 | 160 | 245.2133 | 85 | 202.6066 | 92.5965 | Alkalinity | mg/L as CaCO3 | 18 | 89 | 300 | 313.8333 | -4.6111 | 79.7753 | 235.8128 | 92.3668 | Alkalinity | mg/L as CaCO3 | 14 | 130 | 198.1706 | 84.2697 | 164.0853 | 91.4679 | Alkalinity | mg/L as CaCO3 | 16 | 84 | 320 | 373.8947 | -16.8421 | 80.9524 | 268.2742 | 94.036 | Alkalinity | mg/L as CaCO3 | 12 | 140 | 231.5745 | 85.7143 | 185.7872 | 93.541 | Alkalinity | mg/L as CaCO3 | 16 | 75 | 270 | 326.5263 | -20.9357 | 78.6667 | 234.8849 | 93.1882 | Alkalinity | mg/L as CaCO3 | 11 | 120 | 195.77 | 85.3333 | 157.885 | 93.0329 | Alkalinity | mg/L as CaCO3 | 16 | 74 | 270 | 321.2632 | -18.9864 | 78.3784 | 231.175 | 93.0788 | Alkalinity | mg/L as CaCO3 | 12 | 130 | 212.0263 | 83.7838 | 171.0131 | 92.983 | Electric Rate ($/kW-h) | 0.065 | 13 | 5 | 8
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | Strontium (mg/L) | 0 |  |  |  | 1998-11-25 | 7:35 | 3568.5833 | 21.7 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 16.2825 | 5.7058 | 42.1942 | 0.38589 | 7.4 | 6.3 | 28.08 | 179.8 | 223.1237 | 720 | 808.2549 | -12.2576 | 87.4151 | 598.6556 | 95.3095 | 59 | 52 | 4.1 | 4.8923 | 8.5077 | 9.6 | 13.4 | 0.33214 | 0.50962 | 15.0533 | 16.5956 | 5.3674 | 46.0326 | 0.36052 | 6.3 | 6.8 | 18.72 | 435.6 | 595 | 675.3248 | -13.5 | 91.61 | 555.4624 | 96.6298 | 52 | 45 | 4.1 | 2.3077 | 6.2 | 4.7077 | 8.5077 | 0.44597 | 0.4902 | 14.2012 | 15.6562 | 6.5022 | 37.8978 | 0.41312 | 6.8 | 6.7 | 46.8 | 595 | 720 | 799.0447 | -10.9784 | 79.0251 | 697.0223 | 93.2857 | Total dissolved solids | mg/L | 29 | 230 | 780 | 866.5 | -11.0897 | 87.3913 | 639.3841 | 95.4644 | Total dissolved solids | mg/L | 13 | 390 | 614.2969 | 94.3478 | 502.1484 | 97.4111 | Total dissolved solids | mg/L | 16 | 180 | 670 | 699.3333 | -4.3781 | 91.1111 | 519.1169 | 96.9178 | Total dissolved solids | mg/L | 18 | 320 | 497.4787 | 90 | 408.7393 | 95.5962 | Total dissolved solids | mg/L | 36 | 240 | 960 | 886 | 7.7083 | 85 | 661.8284 | 94.5605 | Total dissolved solids | mg/L | 29 | 340 | 522.7678 | 87.9167 | 431.3839 | 93.2774 | Total dissolved solids | mg/L | 28 | 230 | 1100 | 1091.1579 | 0.80383 | 87.8261 | 777.4027 | 96.3983 | Total dissolved solids | mg/L | 14 | 420 | 710.4628 | 93.913 | 565.2314 | 97.5231 | Total dissolved solids | mg/L | 54 | 260 | 1200 | 1138.2105 | 5.1491 | 79.2308 | 818.2424 | 93.4005 | Total dissolved solids | mg/L | 23 | 470 | 780.7267 | 91.1538 | 625.3633 | 96.3221 | Total dissolved solids | mg/L | 34 | 270 | 1200 | 1276.1053 | -6.3421 | 87.4074 | 909.5398 | 96.2618 | Total dissolved solids | mg/L | 22 | 470 | 781.4218 | 91.8519 | 625.7109 | 96.484 | Fuel Oil Rate ($/gal) | na | 14 | 7 | 7
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Permeate flow rate from system, Qp-sys (gpm) | 6.3863 | Reactive silica (mg/L as SiO2) | 0 |  |  |  | 1998-11-26 | 8:30 | 3593.5 | 22.6 | 59 | 45 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.855 | 6.8736 | 41.0264 | 0.38646 | 7.4 | 6.3 | 28.6 | 185.6 | 263.5665 | 720 | 968.4661 | -34.5092 | 89.1488 | 715.9647 | 96.0054 | 59 | 52 | 4.1 | 4.9778 | 8.4222 | 9.6 | 13.4 | 0.33085 | 0.51852 | 15.3162 | 16.4423 | 5.6573 | 45.7427 | 0.35945 | 6.3 | 6.8 | 18.72 | 455.4 | 595 | 713.4906 | -19.9144 | 92.8974 | 584.4453 | 96.797 | 52 | 45 | 4.1 | 2.2222 | 6.2 | 4.6222 | 8.4222 | 0.44337 | 0.48077 | 13.6752 | 14.6806 | 6.4644 | 37.9356 | 0.38699 | 6.8 | 6.6 | 46.8 | 595 | 720 | 791.4875 | -9.9288 | 82.2436 | 693.2437 | 93.2491 | Total hardness | mg/L as CaCO3 | 20 | 180 | 650 | 686.6667 | -5.641 | 88.8889 | 505.8779 | 96.0465 | Total hardness | mg/L as CaCO3 | 11 | 300 | 471.9411 | 93.8889 | 385.9706 | 97.15 | Total hardness | mg/L as CaCO3 | 20 | 180 | 630 | 686.6667 | -8.9947 | 88.8889 | 510.8458 | 96.0849 | Total hardness | mg/L as CaCO3 | 13 | 290 | 452.7867 | 92.7778 | 371.3934 | 96.4997 | Total hardness | mg/L as CaCO3 | 21 | 180 | 670 | 683.5 | -2.0149 | 88.3333 | 508.778 | 95.8725 | Total hardness | mg/L as CaCO3 | 13 | 270 | 421.0332 | 92.7778 | 345.5166 | 96.2375 | Total hardness | mg/L as CaCO3 | 21 | 170 | 660 | 805.2105 | -22.0016 | 87.6471 | 573.7772 | 96.34 | Total hardness | mg/L as CaCO3 | 13 | 310 | 522.4814 | 92.3529 | 416.2407 | 96.8768 | Total hardness | mg/L as CaCO3 | 23 | 180 | 760 | 849.3158 | -11.7521 | 87.2222 | 605.4565 | 96.2012 | Total hardness | mg/L as CaCO3 | 14 | 320 | 532.7122 | 92.2222 | 426.3561 | 96.7164 | Total hardness | mg/L as CaCO3 | 22 | 180 | 760 | 853.5789 | -12.313 | 87.7778 | 608.1665 | 96.3826 | Total hardness | mg/L as CaCO3 | 14 | 340 | 566.615 | 92.2222 | 453.3075 | 96.9116 | Natural Gas Rate ($/ft3) | na | 14 | 7 | 7
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | Feed flow rate to system, QF-sys (gpm) | 8.515 | Turbidity (ntu) | < 0.10 |  |  |  | 1998-11-27 | 8:00 | 3617 | 20.8 | 56 | 45 | 4.4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 16.4892 | 5.5197 | 40.5803 | 0.40634 | 7.3 | 6.4 | 28.08 | 174 | 217.781 | 720 | 778.9796 | -8.1916 | 87.1063 | 580.0472 | 95.159 | 56 | 52 | 4.4 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 17.2689 | 5.7274 | 43.8726 | 0.39361 | 6.4 | 6.7 | 19.24 | 462 | 595 | 721.9623 | -21.3382 | 91.1654 | 591.9812 | 96.7499 | 52 | 45 | 4.4 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 14.9299 | 6.4143 | 37.6857 | 0.39617 | 6.7 | 6.7 | 46.8 | 595 | 720 | 781.4626 | -8.5365 | 78.5105 | 688.2313 | 93.2 | Calcium hardness | mg/L as CaCO3 | 17 | 160 | 550 | 612.8333 | -11.4242 | 89.375 | 451.2534 | 96.2327 | Calcium hardness | mg/L as CaCO3 | 11 | 260 | 408.143 | 93.125 | 334.0715 | 96.7073 | Calcium hardness | mg/L as CaCO3 | 17 | 150 | 540 | 571.1667 | -5.7716 | 88.6667 | 425.0155 | 96.0001 | Calcium hardness | mg/L as CaCO3 | 11 | 240 | 374.5782 | 92.6667 | 307.2891 | 96.4203 | Calcium hardness | mg/L as CaCO3 | 18 | 160 | 570 | 609.6667 | -6.9591 | 88.75 | 453.6256 | 96.032 | Calcium hardness | mg/L as CaCO3 | 11 | 230 | 358.7014 | 93.125 | 294.3507 | 96.263 | Calcium hardness | mg/L as CaCO3 | 18 | 150 | 560 | 712.7368 | -27.2744 | 88 | 507.7087 | 96.4547 | Calcium hardness | mg/L as CaCO3 | 11 | 260 | 438.141 | 92.6667 | 349.0705 | 96.8488 | Calcium hardness | mg/L as CaCO3 | 20 | 160 | 650 | 756.8421 | -16.4372 | 87.5 | 539.388 | 96.2921 | Calcium hardness | mg/L as CaCO3 | 12 | 270 | 449.3456 | 92.5 | 359.6728 | 96.6636 | Calcium hardness | mg/L as CaCO3 | 19 | 160 | 650 | 761.1053 | -17.0931 | 88.125 | 542.0979 | 96.4951 | Calcium hardness | mg/L as CaCO3 | 12 | 300 | 500.1997 | 92.5 | 400.0999 | 97.0007 | Current Process Water Rate ($/1000 gal) | 0.45 | 11 | 4 | 7
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.1288 | SDI | na |  |  |  | 1998-11-28 | 8:40 | 3641.6667 | 20.6 | 58 | 45 | 4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 16.587 | 5.5197 | 41.9803 | 0.39511 | 7.4 | 6.4 | 28.08 | 174 | 217.781 | 720 | 778.9796 | -8.1916 | 87.1063 | 580.0472 | 95.159 | 58 | 52 | 4 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 17.3713 | 5.1399 | 45.8601 | 0.37879 | 6.4 | 6.7 | 18.46 | 415.8 | 595 | 649.0944 | -9.0915 | 91.5236 | 532.4472 | 96.533 | 52 | 45 | 4 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 15.0184 | 6.4143 | 38.0857 | 0.39433 | 6.7 | 6.7 | 46.8 | 595 | 720 | 781.4626 | -8.5365 | 78.5105 | 688.2313 | 93.2 | Turbidity | ntu | BMRL | BMRL | 0.12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.12 | 0.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | 0.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | na | 13 | 6 | 7
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 |  |  | MFI | na |  |  |  | 1998-11-29 | 12:15 | 3669.25 | 24.2 | 58 | 46 | 4.1 | 3.8 | 7.2 | 2.4 |  | 9.6 | 13.4 | 0.75 | 0.39583 | 14.7692 | 15.1226 | 5.5361 | 42.3639 | 0.35697 | 7.6 | 6.4 | 28.08 | 174 | 217.325 | 720 | 785.06 | -9.0361 | 87.0793 | 581.6922 | 95.1727 | 58 | 54 | 4.1 | 5.0571 | 8.3429 | 9.6 | 13.4 | 0.32964 | 0.52679 | 15.5604 | 15.9328 | 4.4727 | 47.4273 | 0.33594 | 6.4 | 6.6 | 19.76 | 363 | 560 | 571.0599 | -1.975 | 90.9076 | 467.0299 | 95.769 | 54 | 46 | 4.1 | 2.1429 | 6.2 | 4.5429 | 8.3429 | 0.44097 | 0.4717 | 13.1868 | 13.5024 | 6.0611 | 39.8389 | 0.33892 | 6.6 | 6.8 | 43.2 | 560 | 720 | 738.6175 | -2.5858 | 80.1219 | 649.3088 | 93.3468 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 12 | 4 | 8
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI | na | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1998-11-30 | 9:45 | 3690.75 | 22.9 | 59 | 46 | 4.1 | 3.8 | 7.17 | 2.3 |  | 9.47 | 13.27 | 0.75713 | 0.40127 | 14.7077 | 15.6496 | 5.7204 | 42.6796 | 0.36668 | 7.7 | 6.4 | 27.56 | 174 | 217.9196 | 720 | 811.345 | -12.6868 | 87.3531 | 599.599 | 95.4036 | 59 | 53 | 4.1 | 4.95 | 8.32 | 9.47 | 13.27 | 0.32733 | 0.5227 | 15.2308 | 16.2062 | 4.4467 | 47.4533 | 0.34152 | 6.4 | 6.6 | 20.28 | 363 | 560 | 566.9019 | -1.2325 | 90.6938 | 464.951 | 95.6382 | 53 | 46 | 4.1 | 2.2222 | 6.0978 | 4.52 | 8.32 | 0.43718 | 0.49164 | 13.6752 | 14.551 | 6.1097 | 39.2903 | 0.37035 | 6.6 | 6.7 | 43.2 | 560 | 720 | 748.3382 | -3.9359 | 80.1762 | 654.1691 | 93.3962 | Total organic carbon | mg/L | BMRL | 2.5 | 8.5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.4 | 8.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.5 | 9.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.13 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.5 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2 | 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 1.9 | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 6 | 7
Plant Name | Courtland Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 13.76 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 5.6767 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1998-12-01 | 9:00 | 3714 | 21.8 | 59 | 46 | 4.2 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 16.0089 | 5.5348 | 42.7652 | 0.37435 | 7.7 | 6.4 | 27.56 | 174 | 217.781 | 720 | 780.5179 | -8.4053 | 87.3451 | 581.0403 | 95.2568 | 59 | 54 | 4.2 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 16.7659 | 4.4501 | 47.8499 | 0.35039 | 6.4 | 6.6 | 18.98 | 363 | 560 | 564.9881 | -0.89072 | 91.2848 | 463.994 | 95.9094 | 54 | 46 | 4.2 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 14.495 | 6.0469 | 39.7531 | 0.36463 | 6.6 | 6.7 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.1636 | 647.8912 | 93.3322 | UV254 | cm-1 | BMRL | 0.089 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.084 | 0.34 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.088 | 0.34 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4211 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.084 | 0.41 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.75 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.085 | 0.41 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6364 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.083 | 0.39 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8095 | --- | --- | --- | --- |  |  | 13 | 5 | 8
Treatment Plant Category | DIS/GW, OTHER/GW | Feed spacer thickness, T (ft) | 0.00267 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 2.8383 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1998-12-02 | 9:00 | 3738 | 22.7 | 59 | 46 | 4.1 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 15.5887 | 5.5348 | 42.8652 | 0.36367 | 7.3 | 6.4 | 27.56 | 174 | 217.781 | 720 | 780.5179 | -8.4053 | 87.3451 | 581.0403 | 95.2568 | 59 | 54 | 4.1 | 4.9571 | 8.4429 | 9.5 | 13.4 | 0.33116 | 0.5218 | 15.2527 | 16.3258 | 5.3106 | 47.0894 | 0.3467 | 6.4 | 6.8 | 18.46 | 429 | 560 | 670.0446 | -19.6508 | 91.5236 | 549.5223 | 96.6407 | 54 | 46 | 4.1 | 2.1429 | 6.3 | 4.5429 | 8.4429 | 0.44703 | 0.4717 | 13.1868 | 14.1145 | 6.0469 | 39.8531 | 0.35416 | 6.8 | 6.9 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.1636 | 647.8912 | 93.3322 | SUVA | L/(mg*m) | NR | 3.56 | 3.8824 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5 | 3.908 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.52 | 3.6559 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.36 | 3.7273 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.25 | 4.1 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.3684 | 3.25 | --- | --- | --- | --- | --- | [10 empty] | 13 | 5 | 8
Process Train Name | Aeration,Disinfection,Corrosion Control | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | [7 empty] | 1998-12-03 | 9:45 | 3762.75 | 23.3 | 58 | 46 | 4.4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 15.3146 | 5.5197 | 42.0803 | 0.36394 | 7.4 | 6.4 | 28.08 | 174 | 217.781 | 720 | 778.9796 | -8.1916 | 87.1063 | 580.0472 | 95.159 | 58 | 54 | 4.4 | 4.8778 | 8.5222 | 9.5 | 13.4 | 0.33236 | 0.51345 | 15.0085 | 15.782 | 5.2669 | 46.3331 | 0.34062 | 6.4 | 6.7 | 19.5 | 429 | 560 | 663.3814 | -18.461 | 91.046 | 546.1907 | 96.4298 | 54 | 46 | 4.4 | 2.2222 | 6.3 | 4.6222 | 8.5222 | 0.44944 | 0.48077 | 13.6752 | 14.38 | 6.0795 | 39.5205 | 0.36386 | 6.7 | 6.8 | 43.2 | 560 | 720 | 742.2928 | -3.0962 | 80.1636 | 651.1464 | 93.3655 | Bromide | mg/L | BMRL | 46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 49 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 50 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 46 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 12 | 4 | 8
ICR Treatment Plant Identification Number | 1075 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1998-12-04 | 8:00 | 3785 | 21.6 | 58 | 45 | 4 | 3.9 | 7.1 | 2.4 |  | 9.5 | 13.4 | 0.74737 | 0.41053 | 14.5641 | 16.1039 | 5.5348 | 41.9652 | 0.38374 | 7.4 | 6.4 | 27.56 | 174 | 217.781 | 720 | 780.5179 | -8.4053 | 87.3451 | 581.0403 | 95.2568 | 58 | 55 | 4 | 4.8778 | 8.5222 | 9.5 | 13.4 | 0.33236 | 0.51345 | 15.0085 | 16.5953 | 5.4367 | 47.0633 | 0.35262 | 6.4 | 6.7 | 19.5 | 442.2 | 560 | 684.1365 | -22.1672 | 91.046 | 563.1683 | 96.5374 | 55 | 45 | 4 | 2.2222 | 6.3 | 4.6222 | 8.5222 | 0.44944 | 0.48077 | 13.6752 | 15.121 | 6.0795 | 39.9205 | 0.37878 | 6.7 | 6.8 | 43.2 | 560 | 720 | 742.2928 | -3.0962 | 80.1636 | 651.1464 | 93.3655 | SDS-Cl2 dose | mg/L | 5.4 | 8.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 6 | 8.1 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.2 | 8 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 6.1 | 9.1 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.9 | 8.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 6 | 8.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [9 empty] | 13 | 3 | 10
PWSID Number of Plant (if assigned) | N/A |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 2.3233 | [5 empty] | 1998-12-05 | 9:30 | 3810.5 | 23.1 | 58 | 45 | 4 | 4 | 7.1 | 2.2 |  | 9.3 | 13.3 | 0.76344 | 0.43011 | 14.5641 | 15.4055 | 5.9079 | 41.5921 | 0.37039 | 7.4 | 6.5 | 28.08 | 174 | 218.7223 | 720 | 833.9768 | -15.8301 | 87.1618 | 618.869 | 95.4627 | 58 | 52 | 4 | 4.8778 | 8.4222 | 9.3 | 13.3 | 0.32933 | 0.52449 | 15.0085 | 15.8756 | 5.451 | 45.549 | 0.34854 | 6.5 | 6.7 | 19.5 | 442.2 | 560 | 687.0091 | -22.6802 | 91.0846 | 564.6046 | 96.5463 | 52 | 45 | 4 | 2.2222 | 6.2 | 4.4222 | 8.4222 | 0.44337 | 0.50251 | 13.6752 | 14.4652 | 6.0942 | 38.4058 | 0.37664 | 6.7 | 6.8 | 43.2 | 560 | 720 | 745.233 | -3.5046 | 80.2489 | 652.6165 | 93.3805 | SDS-Free Cl2 residual | mg/L | 0.68 | 1.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.3 | 0.87 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | 0.82 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.49 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | 1.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.3 | 1.1 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | 1.3 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.56 | [6 empty] | 13 | 6 | 7
Historical Minimum Water Temperature (oC) | 17.8 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.1617 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1998-12-06 | 1:00 | 3826 | 25 | 58 | 45 | 4.3 | 4 | 7.1 | 2.2 |  | 9.3 | 13.3 | 0.76344 | 0.43011 | 14.5641 | 14.5641 | 5.696 | 41.504 | 0.35091 | 7.4 | 6.4 | 29.12 | 168.2 | 212.9236 | 720 | 806.1079 | -11.9594 | 86.3237 | 598.7164 | 95.1363 | 58 | 53 | 4.3 | 4.8778 | 8.4222 | 9.3 | 13.3 | 0.32933 | 0.52449 | 15.0085 | 15.0085 | 5.1924 | 46.0076 | 0.32622 | 6.4 | 6.6 | 19.76 | 422.4 | 560 | 655.5912 | -17.0699 | 90.7197 | 538.9956 | 96.3339 | 53 | 45 | 4.3 | 2.2222 | 6.2 | 4.4222 | 8.4222 | 0.44337 | 0.50251 | 13.6752 | 13.6752 | 6.0942 | 38.6058 | 0.35423 | 6.6 | 6.7 | 43.2 | 560 | 720 | 745.233 | -3.5046 | 79.711 | 652.6165 | 93.3805 | SDS-Cl2 demand | mg/L | 4.72 | 7.5 | --- | 16.3033 | --- | 37.0667 | 13.1621 | 64.1395 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.7 | 7.23 | --- | 15.2417 | --- | 34.9931 | 12.4615 | 62.2838 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.14 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.8 | 7.18 | --- | 17.8833 | --- | 47.0752 | 14.1691 | 73.1811 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.14 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.7 | 7.8 | --- | 21.0158 | --- | 39.7436 | 16.2007 | 70.989 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.6 | 7.5 | --- | 19.8632 | --- | 38.6667 | 15.3588 | 70.0496 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.6 | 7.3 | --- | 18.8105 | --- | 36.9863 | 14.6168 | 68.5293 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 | [6 empty] | 13 | 5 | 8
Historical Average Water Temperature (oC) | 23.5 | Design cross-flow velocity (fps) | 1 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1998-12-07 | 10:00 | 3859 | 23.2 | 58 | 46 | 4.1 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.36 | 5.9078 | 41.9922 | 0.36578 | 7.3 | 6.4 | 28.6 | 174 | 218.7223 | 720 | 832.2987 | -15.597 | 86.9241 | 619.3785 | 95.3825 | 58 | 53 | 4.1 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 16.0863 | 5.3926 | 46.0074 | 0.34965 | 6.4 | 6.6 | 18.72 | 435.6 | 560 | 680.3671 | -21.4941 | 91.4412 | 557.9836 | 96.6451 | 53 | 46 | 4.1 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 13.9074 | 6.0469 | 39.3531 | 0.3534 | 6.6 | 6.7 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.2489 | 647.8912 | 93.3322 | SDS-Chlorination temp. | oC | 25 | 25 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.32 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.44 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 8.14 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.52 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.61 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.61 | [6 empty] | 12 | 5 | 7
State Approved Plant Capacity (MGD) | N/A | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1998-12-08 | 10:00 | 3883 | 23.3 | 58 | 46 | 4.1 | 4 | 7.1 | 2.2 |  | 9.3 | 13.3 | 0.76344 | 0.43011 | 14.5641 | 15.3146 | 5.8918 | 42.0082 | 0.36456 | 7.2 | 6.4 | 28.6 | 174 | 218.7223 | 727.2 | 832.2987 | -14.4525 | 86.9241 | 617.7776 | 95.3705 | 58 | 53 | 4.1 | 5.031 | 8.269 | 9.3 | 13.3 | 0.32701 | 0.54097 | 15.4801 | 16.2779 | 5.5095 | 45.8905 | 0.35471 | 6.4 | 6.6 | 19.76 | 442.2 | 560 | 699.2225 | -24.8612 | 90.9657 | 570.7113 | 96.5377 | 53 | 46 | 4.1 | 2.069 | 6.2 | 4.269 | 8.269 | 0.43873 | 0.48465 | 12.7321 | 13.3882 | 6.0303 | 39.3697 | 0.34006 | 6.6 | 6.8 | 43.2 | 560 | 727.2 | 732.4583 | -0.72309 | 80.2489 | 646.2291 | 93.3151 | SDS-Chlorination pH | --- | 8.17 | 7.98 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.17 | 8.2 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.04 | 8.09 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.17 | 8.18 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.15 | 8.18 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.1 | 8.2 | --- | --- | --- | --- | --- | --- | [10 empty] | 12 | 5 | 7
|  | Maximum element recovery (%) | 10 | [7 empty] | 1998-12-09 | 9:45 | 3906.75 | 23.2 | 58 | 46 | 4.1 | 4 | 7.1 | 2.3 |  | 9.4 | 13.4 | 0.75532 | 0.42553 | 14.5641 | 15.36 | 5.6974 | 42.2026 | 0.36396 | 7.2 | 6.4 | 28.6 | 174 | 218.2466 | 720 | 803.6774 | -11.6219 | 86.8956 | 598.3397 | 95.2201 | 58 | 54 | 4.1 | 4.9571 | 8.4429 | 9.4 | 13.4 | 0.33116 | 0.52736 | 15.2527 | 16.0863 | 5.4715 | 46.4285 | 0.34647 | 6.4 | 6.6 | 19.24 | 442.22 | 560 | 690.5687 | -23.3158 | 91.1843 | 566.3943 | 96.6031 | 54 | 46 | 4.1 | 2.1429 | 6.3 | 4.4429 | 8.4429 | 0.44703 | 0.48232 | 13.1868 | 13.9074 | 6.0469 | 39.8531 | 0.34897 | 6.6 | 6.7 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.2059 | 647.8912 | 93.3322 | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [9 empty] | 12 | 4 | 8
|  | Variability of design flux (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1998-12-10 | 10:00 | 3931 | 22.1 | 59 | 45 | 4.2 | 4 | 7.16 | 2.26 |  | 9.42 | 13.42 | 0.76008 | 0.42463 | 14.6872 | 16.0017 | 5.7916 | 42.0084 | 0.38092 | 7.4 | 6.4 | 28.652 | 174 | 218.1527 | 720 | 818.5177 | -13.683 | 86.8661 | 607.8083 | 95.286 | 59 | 51 | 4.2 | 4.94 | 8.48 | 9.42 | 13.42 | 0.33203 | 0.52442 | 15.2 | 16.5604 | 5.2 | 45.6 | 0.36317 | 6.4 | 6.6 | 19.5 | 422.2 | 560 | 656.7917 | -17.2842 | 91.0613 | 539.4959 | 96.3855 | 51 | 45 | 4.2 | 2.22 | 6.26 | 4.48 | 8.48 | 0.44695 | 0.49554 | 13.6615 | 14.8843 | 6.0844 | 37.7156 | 0.39464 | 6.6 | 6.7 | 43.2 | 560 | 720 | 743.2741 | -3.2325 | 80.1974 | 651.6371 | 93.3705 | SDS-TOX | mg Cl- /L | 30 | 401 | --- | 1575.8333 | --- | 92.5187 | 1156.6294 | 97.4063 | Parameter | Units | Cp-s2-22 | CI-s2-22 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 54 | 350 | --- | 1287.3333 | --- | 84.5714 | 962.0647 | 94.3871 | Parameter | Units | Cp-s2-24 | CI-s2-24 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 23 | 308 | --- | 1210.5 | --- | 92.5325 | 897.319 | 97.4368 | Parameter | Units | Cp-s2-26 | CI-s2-26 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 26 | 406 | --- | 2026 | --- | 93.5961 | 1435.7674 | 98.1891 | Parameter | Units | Cp-s2-28 | CI-s2-28 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 29 | 216 | --- | 1013.2105 | --- | 86.5741 | 722.754 | 95.9876 | Parameter | Units | Cp-s2-30 | CI-s2-30 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 29 | 346 | --- | 1697.4211 | --- | 91.6185 | 1205.0428 | 97.5934 | Parameter | Units | Cp-s2-30 (dup) | CI-s2-30 (dup) | CC(calc) | RF (%) | CB | RB (%) |  |  | 14 | 8 | 6
|  | Rejection of reference solute and conditions of test | 500 mg/L NaCl | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 11.485 | [5 empty] | 1998-12-11 | 8:30 | 3953.5 | 22.2 | 56 | 45 | 4 | 4 | 7.17 | 2 |  | 9.17 | 13.17 | 0.7819 | 0.43621 | 14.7077 | 15.9768 | 6.2239 | 40.2761 | 0.39668 | 8 | 6.4 | 27.04 | 168.2 | 213.5575 | 720 | 882.2226 | -22.5309 | 87.3383 | 649.4337 | 95.8364 | 56 | 50 | 4 | 5.1 | 8.07 | 9.17 | 13.17 | 0.32202 | 0.55616 | 15.6923 | 17.0463 | 5.1387 | 43.8613 | 0.38864 | 6.4 | 6.5 | 18.72 | 409.2 | 525 | 655.9717 | -24.947 | 91.2342 | 532.5859 | 96.4851 | 50 | 45 | 4 | 2.069 | 6.001 | 4.07 | 8.07 | 0.42666 | 0.50835 | 12.7321 | 13.8307 | 5.6485 | 37.8515 | 0.36539 | 6.5 | 6.7 | 43.2 | 525 | 720 | 691.1093 | 4.0126 | 79.7713 | 608.0546 | 92.8954 | SDS-CHCl3 | mg/L | 4.5 | 71 | --- | 281.5833 | --- | 93.662 | 206.443 | 97.8202 | Sampling date | MM/DD/YY | 1998-11-30 | 1998-11-30 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 6.2 | 91 | --- | 359.5333 | --- | 93.1868 | 266.3483 | 97.6722 | Sampling date | MM/DD/YY | 1998-12-15 | 1998-12-15 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.5 | 70 | --- | 280.5833 | --- | 95 | 207.5078 | 98.3133 | Sampling date | MM/DD/YY | 1998-12-28 | 1998-12-28 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 6.7 | 75 | --- | 366.1737 | --- | 91.0667 | 260.0871 | 97.4239 | Sampling date | MM/DD/YY | 1999-01-11 | 1999-01-11 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.2 | 49 | --- | 244.2526 | --- | 93.4694 | 173.1141 | 98.1515 | Sampling date | MM/DD/YY | 1999-01-25 | 1999-01-25 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 4.2 | 50 | --- | 245.2526 | --- | 91.6 | 174.1141 | 97.5878 | Sampling date | MM/DD/YY | 1999-01-25 | 1999-01-25 | --- | --- | --- | --- |  |  | 11 | 6 | 5
|  | (e.g., solute type and concentration) |  | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 5.7425 | [5 empty] | 1998-12-12 | 9:30 | 3978.5 | 23.1 | 57 | 45 | 4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.4055 | 5.7276 | 41.2724 | 0.37326 | 7.4 | 6.4 | 28.6 | 168.2 | 212.9236 | 720 | 807.7861 | -12.1925 | 86.568 | 601.3599 | 95.2441 | 57 | 51 | 4 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 16.1339 | 5.3926 | 44.6074 | 0.36169 | 6.4 | 6.5 | 18.72 | 435.6 | 525 | 680.3671 | -29.5937 | 91.2081 | 557.9836 | 96.6451 | 51 | 45 | 4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 13.9486 | 5.6374 | 38.3626 | 0.3636 | 6.5 | 6.6 | 43.2 | 525 | 720 | 688.8776 | 4.3226 | 79.711 | 606.9388 | 92.8823 | SDS-BDCM | mg/L | 2 | 14 | --- | 52 | --- | 85.7143 | 38.4408 | 94.7972 | Sampling time | hh:mm | 8:36 | 8:32 | --- | --- | --- | --- | SDS-BDCM | mg/L | 3.3 | 16 | --- | 56.2167 | --- | 79.375 | 42.2609 | 92.1914 | Sampling time | hh:mm | 9:02 | 8:55 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | 15 | --- | 56.1667 | --- | 86.6667 | 41.8812 | 95.2246 | Sampling time | hh:mm | 8:52 | 8:48 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2.6 | 16 | --- | 73.1263 | --- | 83.75 | 52.3129 | 95.0299 | Sampling time | hh:mm | 9:05 | 9:00 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.9 | 11 | --- | 49.7947 | --- | 82.7273 | 35.6602 | 94.6719 | Sampling time | hh:mm | 10:23 | 10:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | 2 | 12 | --- | 54.6316 | --- | 83.3333 | 39.0991 | 94.8848 | Sampling time | hh:mm | 10:52 | 10:50 | --- | --- | --- | --- |  |  | 12 | 6 | 6
|  | Variability of rejection of reference solute (%) | 15 | [7 empty] | 1998-12-13 | 12:00 | 4005 | 24.6 | 58 | 46 | 4.4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 14.7373 | 5.7276 | 41.8724 | 0.35196 | 7.6 | 6.4 | 28.6 | 168.2 | 212.9236 | 720 | 807.7861 | -12.1925 | 86.568 | 601.3599 | 95.2441 | 58 | 54 | 4.4 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 15.4342 | 5.3005 | 46.2995 | 0.33336 | 6.4 | 6.5 | 19.24 | 429 | 560 | 669.5867 | -19.569 | 90.9639 | 549.2933 | 96.4973 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 13.3437 | 6.0469 | 39.5531 | 0.33736 | 6.5 | 6.7 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 79.711 | 647.8912 | 93.3322 | SDS-DBCM | mg/L | 1 | 1.7 | --- | 3.9167 | --- | 41.1765 | 3.1257 | 68.0073 | Operation time | hh.hh | 3655 | 3655 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4015 | 4015 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 4322 | 4322 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.4 | 2.3 | --- | 6.1368 | --- | 39.1304 | 4.7389 | 70.4574 | Operation time | hh.hh | 4655 | 4655 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1 | 1.6 | --- | 4.1579 | --- | 37.5 | 3.2259 | 69.0014 | Operation time | hh.hh | 4973 | 4973 | --- | --- | --- | --- | SDS-DBCM | mg/L | 1.4 | 2 | --- | 4.5579 | --- | 30 | 3.6259 | 61.3894 | Operation time | hh.hh | 4973 | 4973 | --- | --- | --- | --- |  |  | 12 | 4 | 8
|  | Standard testing recovery (%) | 10 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1998-12-14 | 10:00 | 4027 | 21.7 | 59 | 46 | 4.4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 16.0563 | 5.9078 | 42.1922 | 0.38055 | 7.6 | 6.4 | 28.6 | 174 | 218.7223 | 720 | 832.2987 | -15.597 | 86.9241 | 619.3785 | 95.3825 | 59 | 54 | 4.4 | 4.8778 | 8.5222 | 9.3 | 13.4 | 0.33236 | 0.52449 | 15.0085 | 16.5463 | 5.6265 | 46.4735 | 0.35604 | 6.4 | 6.6 | 17.94 | 455.4 | 560 | 705.7845 | -26.033 | 91.7978 | 580.5923 | 96.9101 | 54 | 46 | 4.4 | 2.2222 | 6.3 | 4.4222 | 8.5222 | 0.44944 | 0.50251 | 13.6752 | 15.0764 | 6.0795 | 39.5205 | 0.38148 | 6.6 | 6.7 | 43.2 | 560 | 720 | 742.2928 | -3.0962 | 80.2489 | 651.1464 | 93.3655 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.85 | 6.85 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.93 | 6.9 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.87 | 6.65 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.77 | 6.62 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.7 | 6.76 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | 1 | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.69 | 6.94 | --- | --- | --- | --- |  |  | 13 | 5 | 8
|  | Standard testing pH | 7.5 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 2.3233 | [5 empty] | 1998-12-15 | 9:45 | 4050.75 | 21.2 | 59 | 46 | 4.2 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 16.2954 | 6.1041 | 42.1959 | 0.38618 | 7.6 | 6.4 | 28.08 | 179.8 | 224.5209 | 705.6 | 858.4894 | -21.668 | 87.4934 | 638.4929 | 95.6021 | 59 | 54 | 4.2 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 17.0659 | 5.8128 | 46.4872 | 0.36711 | 6.4 | 6.5 | 19.24 | 468.6 | 553 | 732.4374 | -32.448 | 91.4306 | 600.5187 | 96.7961 | 54 | 46 | 4.2 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 14.7544 | 5.965 | 39.835 | 0.37039 | 6.5 | 6.6 | 43.2 | 553 | 705.6 | 726.4014 | -2.948 | 80.759 | 639.7007 | 93.2468 | SDS-THM4 | mg/L | 7.5 | 86.7 | --- | 337.5 | --- | 91.3495 | 248.0096 | 96.9759 | Temperature | oC | 22.9 | 22.9 | --- | --- | --- | --- | SDS-THM4 | mg/L | 9.5 | 108.8 | --- | 423.25 | --- | 91.2684 | 314.1312 | 96.9758 | Temperature | oC | 21.2 | 21.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.5 | 86.6 | --- | 343.4167 | --- | 93.649 | 254.2975 | 97.8372 | Temperature | oC | 22 | 22 | --- | --- | --- | --- | SDS-THM4 | mg/L | 10.7 | 93.3 | --- | 445.4368 | --- | 88.5316 | 317.1389 | 96.6261 | Temperature | oC | 20.3 | 20.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 6.1 | 61.6 | --- | 298.2053 | --- | 90.0974 | 212.0002 | 97.1226 | Temperature | oC | 22.2 | 22.2 | --- | --- | --- | --- | SDS-THM4 | mg/L | 8.6 | 64 | --- | 300.1789 | --- | 86.5625 | 214.1293 | 95.9837 | Temperature | oC | 22.2 | 22.2 | --- | --- | --- | --- |  |  | 13 | 5 | 8
|  | Acceptable range of operating pressures | 0 - 350 psi | Maximum system recycle flow rate, (QR-sys)max (gpm) | 5.7425 | [5 empty] | 1998-12-16 | 9:00 | 4074 | 18.8 | 58 | 46 | 4.1 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 17.4934 | 6.1041 | 41.7959 | 0.41854 | 7.6 | 6.3 | 28.08 | 179.8 | 224.5209 | 720 | 858.4894 | -19.2346 | 87.4934 | 638.4929 | 95.6021 | 58 | 54 | 4.1 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 18.3206 | 6.1543 | 45.7457 | 0.40049 | 6.3 | 6.6 | 19.24 | 495 | 560 | 774.3379 | -38.2746 | 91.4306 | 634.669 | 96.9685 | 54 | 46 | 4.1 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 15.8391 | 6.0469 | 39.8531 | 0.39744 | 6.6 | 6.8 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.759 | 647.8912 | 93.3322 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 25 | 240 | 318.2459 | 75 | 279.123 | 91.0434 | SDS-MCAA* | mg/L | BMRL | 2.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 26 | 220 | 285.8984 | 74 | 252.9492 | 89.7213 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 200 | 262.7733 | 73.0337 | 231.3867 | 89.6278 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 23 | 200 | 274.1396 | 72.619 | 237.0698 | 90.2982 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 180 | 248.8642 | 70.6667 | 214.4321 | 89.7403 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 23 | 180 | 248.4283 | 68.9189 | 214.2142 | 89.2631 |  |  | 12 | 4 | 8
|  | Acceptable range of operating pH values | 4-11 | Design system recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1998-12-17 | 9:00 | 4098 | 19.7 | 58 | 46 | 4.1 | 4.1 | 7 | 2.2 |  | 9.2 | 13.3 | 0.76087 | 0.44565 | 14.359 | 16.7943 | 6.2467 | 41.6533 | 0.40319 | 7.2 | 6.4 | 28.08 | 185.6 | 230.8056 | 756 | 875.8415 | -15.852 | 87.8339 | 652.7464 | 95.6982 | 58 | 54 | 4.1 | 4.8571 | 8.4429 | 9.2 | 13.3 | 0.32964 | 0.52795 | 14.9451 | 17.4797 | 6.0177 | 45.8823 | 0.38097 | 6.4 | 6.5 | 21.06 | 488.4 | 595 | 757.2589 | -27.2704 | 90.8754 | 622.8294 | 96.6187 | 54 | 46 | 4.1 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 15.4233 | 6.4564 | 39.4436 | 0.39102 | 6.5 | 6.6 | 43.2 | 595 | 756 | 782.6871 | -3.53 | 81.2829 | 688.8435 | 93.7286 | SDS-DCAA* | mg/L | 2.2 | 29 | --- | 113.8667 | --- | 92.4138 | 83.5846 | 97.3679 | Total dissolved solids | mg/L | 46 | 560 | 747.0623 | 80 | 653.5311 | 92.9613 | SDS-DCAA* | mg/L | 2.5 | 22 | --- | 83.75 | --- | 88.6364 | 62.3218 | 95.9886 | Total dissolved solids | mg/L | 28 | 420 | 553.1556 | 84.4444 | 486.5778 | 94.2455 | SDS-DCAA* | mg/L | 1 | 23 | --- | 92.6667 | --- | 95.6522 | 68.4913 | 98.54 | Total dissolved solids | mg/L | 52 | 540 | 714.0533 | 78.3333 | 627.0267 | 91.7069 | SDS-DCAA* | mg/L | 2 | 33 | --- | 165.1579 | --- | 93.9394 | 117.0073 | 98.2907 | Total dissolved solids | mg/L | 49 | 620 | 859.1736 | 78.6957 | 739.5868 | 93.3747 | SDS-DCAA* | mg/L | 3.3 | 48 | --- | 238.5632 | --- | 93.125 | 169.1332 | 98.0489 | Total dissolved solids | mg/L | 50 | 750 | 1055.0943 | 80.7692 | 902.5472 | 94.4601 | SDS-DCAA* | mg/L | 3.2 | 32 | --- | 154.7789 | --- | 90 | 110.0455 | 97.0921 | Total dissolved solids | mg/L | 58 | 660 | 922.3811 | 78.5185 | 791.1906 | 92.6693 |  |  | 12 | 4 | 8
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 13.515 | [5 empty] | 1998-12-18 | 7:55 | 4120.9167 | 18.7 | 59 | 46 | 4.1 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 17.5452 | 6.2843 | 42.1157 | 0.4166 | 7.6 | 6.5 | 28.08 | 185.6 | 230.3196 | 792 | 883.002 | -11.4901 | 87.8082 | 656.5114 | 95.7228 | 59 | 53 | 4.1 | 4.7923 | 8.6077 | 9.3 | 13.4 | 0.33366 | 0.5153 | 14.7456 | 17.7638 | 6.0209 | 45.8791 | 0.38719 | 6.5 | 6.9 | 17.42 | 488.4 | 595 | 750.6167 | -26.1541 | 92.4366 | 619.5084 | 97.1881 | 53 | 46 | 4.1 | 2.3077 | 6.3 | 4.5077 | 8.6077 | 0.45203 | 0.51195 | 14.2012 | 17.108 | 6.5286 | 38.8714 | 0.44012 | 6.9 | 6.6 | 43.2 | 595 | 792 | 797.1245 | -0.64704 | 81.2435 | 696.0623 | 93.7937 | SDS-TCAA* | mg/L | 2.8 | 45 | --- | 178.6333 | --- | 93.7778 | 130.9503 | 97.8618 | Total hardness | mg/L as CaCO3 | 33 | 460 | 615.4 | 81.6667 | 537.7 | 93.8627 | SDS-TCAA* | mg/L | 2.2 | 17 | --- | 63.8667 | --- | 87.0588 | 47.6032 | 95.3785 | Total hardness | mg/L as CaCO3 | 33 | 400 | 524.6635 | 81.6667 | 462.3317 | 92.8623 | SDS-TCAA* | mg/L | 2.3 | 26 | --- | 101.05 | --- | 91.1538 | 75.0065 | 96.9336 | Total hardness | mg/L as CaCO3 | 33 | 400 | 530.8967 | 81.6667 | 465.4483 | 92.9101 | SDS-TCAA* | mg/L | 1.6 | 40 | --- | 203.7053 | --- | 96 | 144.0607 | 98.8894 | Total hardness | mg/L as CaCO3 | 36 | 430 | 595.034 | 78.8235 | 512.517 | 92.9758 | SDS-TCAA* | mg/L | 2.4 | 60 | --- | 305.5579 | --- | 96 | 216.0911 | 98.8894 | Total hardness | mg/L as CaCO3 | 39 | 520 | 729.6434 | 78.3333 | 624.8217 | 93.7582 | SDS-TCAA* | mg/L | 2.1 | 26 | --- | 127.8895 | --- | 91.9231 | 90.767 | 97.6864 | Total hardness | mg/L as CaCO3 | 35 | 470 | 659.5943 | 80.5556 | 564.7972 | 93.8031 |  |  | 13 | 6 | 7
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.5872 | [5 empty] | 1998-12-19 | 9:10 | 4146.1667 | 21 | 60 | 46 | 4 | 4.1 | 7 | 2.2 |  | 9.2 | 13.3 | 0.76087 | 0.44565 | 14.359 | 16.1612 | 6.068 | 42.932 | 0.37644 | 7.6 | 6.4 | 28.08 | 179.8 | 225.0069 | 720 | 851.5926 | -18.2767 | 87.5204 | 634.8787 | 95.5771 | 60 | 54 | 4 | 4.7778 | 8.5222 | 9.2 | 13.3 | 0.33085 | 0.51932 | 14.7009 | 16.5459 | 5.7532 | 47.2468 | 0.3502 | 6.4 | 6.6 | 19.24 | 468.6 | 560 | 720.5228 | -28.6648 | 91.4492 | 594.5614 | 96.764 | 54 | 46 | 4 | 2.2222 | 6.3 | 4.4222 | 8.5222 | 0.44944 | 0.50251 | 13.6752 | 15.3916 | 6.0795 | 39.9205 | 0.38556 | 6.6 | 6.8 | 43.2 | 560 | 720 | 742.2928 | -3.0962 | 80.8006 | 651.1464 | 93.3655 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 28 | 390 | 521.7443 | 82.5 | 455.8721 | 93.8579 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 28 | 340 | 445.981 | 81.3333 | 392.9905 | 92.8751 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 28 | 340 | 451.28 | 82.5 | 395.64 | 92.9229 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 370 | 512.4151 | 80 | 441.2075 | 93.2005 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 33 | 440 | 617.3906 | 79.375 | 528.6953 | 93.7582 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 400 | 561.2642 | 81.25 | 480.6321 | 93.7582 |  |  | 14 | 6 | 8
|  | Maximum permissible turbidity (ntu) | 0 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1998-12-20 | 11:45 | 4172.75 | 24.1 | 59 | 46 | 4.4 | 4.1 | 7 | 2.2 |  | 9.2 | 13.3 | 0.76087 | 0.44565 | 14.359 | 14.7461 | 5.6946 | 42.4054 | 0.34774 | 7.2 | 6.4 | 28.6 | 168.2 | 213.4096 | 727.2 | 801.4402 | -10.209 | 86.5985 | 598.0612 | 95.2179 | 59 | 54 | 4.4 | 4.8571 | 8.4429 | 9.2 | 13.3 | 0.32964 | 0.52795 | 14.9451 | 15.348 | 5.3646 | 46.7354 | 0.3284 | 6.4 | 6.6 | 18.98 | 435.6 | 560 | 675.2799 | -20.5857 | 91.1063 | 555.4399 | 96.5829 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 13.5423 | 6.0469 | 39.5531 | 0.34238 | 6.6 | 6.8 | 43.2 | 560 | 727.2 | 735.7823 | -1.1802 | 79.7572 | 647.8912 | 93.3322 | SDS-DBAA* | mg/L | 1.2 | 1.3 | --- | 1.6167 | --- | 7.6923 | 1.5037 | 20.1955 | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.14 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 2.2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 5 | 8
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | maximum system recycle flow rates. | [6 empty] | 1998-12-21 | 8:15 | 4193.25 | 20.2 | 59 | 46 | 4.4 | 4.1 | 7 | 2.2 |  | 9.2 | 13.3 | 0.76087 | 0.44565 | 14.359 | 16.5479 | 5.6946 | 42.4054 | 0.39023 | 7.2 | 6.4 | 28.6 | 168.2 | 213.4096 | 720 | 801.4402 | -11.3111 | 86.5985 | 598.0612 | 95.2179 | 59 | 54 | 4.4 | 4.8571 | 8.4429 | 9.2 | 13.3 | 0.32964 | 0.52795 | 14.9451 | 17.2233 | 4.4264 | 47.6736 | 0.36128 | 6.4 | 6.7 | 19.24 | 363 | 560 | 560.7638 | -0.13639 | 90.9845 | 461.8819 | 95.8344 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 15.197 | 6.0469 | 39.5531 | 0.38422 | 6.7 | 6.8 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 79.7572 | 647.8912 | 93.3322 | SDS-BCAA* | mg/L | 2.2 | 6.6 | --- | 20.5333 | --- | 66.6667 | 15.5616 | 85.8627 | Total organic carbon | mg/L | BMRL | 6.1 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 9.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 5.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.5 | 5.1 | --- | 16.5 | --- | 70.5882 | 12.544 | 88.0421 | Total organic carbon | mg/L | BMRL | 5.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 6.4 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.4 | 7 | --- | 30.8737 | --- | 80 | 22.1755 | 93.6867 | Total organic carbon | mg/L | BMRL | 6.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.3 | 5.5 | --- | 23.4053 | --- | 76.3636 | 16.8816 | 92.2993 | Total organic carbon | mg/L | BMRL | 6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 5 | 8
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1998-12-22 | 9:30 | 4218.5 | 22.7 | 58 | 46 | 4.5 | 4 | 7.1 | 2.2 |  | 9.3 | 13.3 | 0.76344 | 0.43011 | 14.5641 | 15.5887 | 6.0392 | 41.4608 | 0.37599 | 7.4 | 6.4 | 29.64 | 179.8 | 224.5209 | 727.2 | 853.4548 | -17.3618 | 86.7986 | 633.5644 | 95.3217 | 58 | 53 | 4.5 | 4.9571 | 8.3429 | 9.3 | 13.3 | 0.32813 | 0.53303 | 15.2527 | 16.3258 | 5.4761 | 45.5239 | 0.35862 | 6.4 | 6.4 | 20.02 | 442.2 | 560 | 693.0501 | -23.7589 | 91.0832 | 567.6251 | 96.473 | 53 | 46 | 4.5 | 2.1429 | 6.2 | 4.3429 | 8.3429 | 0.44097 | 0.49342 | 13.1868 | 14.1145 | 6.0494 | 38.9506 | 0.36237 | 6.4 | 6.5 | 44.2 | 560 | 727.2 | 738.2719 | -1.5225 | 80.3136 | 649.1359 | 93.1909 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.22 | 0.29679 | 89.8876 | 0.2584 | 96.517 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.21 | 0.27828 | 89.2857 | 0.24414 | 96.3136 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.2 | 0.26705 | 86.3636 | 0.23353 | 94.8614 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.23 | 0.32131 | 85.7143 | 0.27566 | 95.6468 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.011 | 0.26 | 0.36853 | 87.0588 | 0.31426 | 96.4997 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.01 | 0.23 | 0.32589 | 87.9518 | 0.27794 | 96.4021 |  |  | 12 | 5 | 7
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1998-12-23 | 9:00 | 4242 | 22.2 | 58 | 46 | 4.3 | 4 | 7.1 | 2.2 |  | 9.3 | 13.3 | 0.76344 | 0.43011 | 14.5641 | 15.8208 | 5.8757 | 41.8243 | 0.37827 | 7.2 | 6.3 | 29.12 | 174 | 218.7223 | 720 | 830.6205 | -15.364 | 86.6863 | 616.6861 | 95.278 | 58 | 54 | 4.3 | 4.9571 | 8.3429 | 9.3 | 13.3 | 0.32813 | 0.53303 | 15.2527 | 16.5688 | 5.6473 | 46.0527 | 0.35978 | 6.3 | 6.5 | 20.02 | 455.4 | 560 | 714.0933 | -27.5167 | 90.8468 | 584.7466 | 96.5763 | 54 | 46 | 4.3 | 2.1429 | 6.2 | 4.3429 | 8.3429 | 0.44097 | 0.49342 | 13.1868 | 14.3247 | 6.0611 | 39.6389 | 0.36138 | 6.5 | 6.6 | 43.2 | 560 | 720 | 738.6175 | -2.5858 | 80.2489 | 649.3088 | 93.3468 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6066 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.0385 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7736 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6508 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8806 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8333 | --- | --- | --- | --- |  |  | 12 | 4 | 8
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 13.515 | [5 empty] | 1998-12-24 | 7:00 | 4264 | 24.7 | 58 | 45 | 4.1 | 4 | 7.2 | 2.2 |  | 9.4 | 13.4 | 0.76596 | 0.42553 | 14.7692 | 14.9008 | 6.0748 | 41.3252 | 0.36057 | 7.3 | 6.3 | 29.64 | 179.8 | 224.0453 | 727.2 | 860.2808 | -18.3004 | 86.7705 | 637.1235 | 95.3478 | 58 | 53 | 4.1 | 5.0571 | 8.3429 | 9.4 | 13.4 | 0.32964 | 0.53799 | 15.5604 | 15.699 | 5.3395 | 46.0605 | 0.34084 | 6.3 | 6.5 | 19.24 | 429 | 560 | 677.3819 | -20.9611 | 91.4125 | 553.191 | 96.522 | 53 | 45 | 4.1 | 2.1429 | 6.2 | 4.3429 | 8.3429 | 0.44097 | 0.49342 | 13.1868 | 13.3043 | 6.0611 | 38.8389 | 0.34255 | 6.5 | 6.6 | 43.2 | 560 | 727.2 | 738.6175 | -1.5701 | 80.7182 | 649.3088 | 93.3468 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 5 | 8
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | [5 empty] | 1998-12-25 | 10:10 | 4291.1667 | 22.4 | 57 | 45 | 4.4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.7275 | 5.8916 | 40.7084 | 0.38635 | 7.3 | 6.3 | 29.12 | 174 | 218.7223 | 720 | 830.6205 | -15.364 | 86.6863 | 618.2827 | 95.2902 | 57 | 53 | 4.4 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 16.4712 | 5.5567 | 45.0433 | 0.36567 | 6.3 | 6.5 | 19.24 | 448.8 | 560 | 701.012 | -25.1807 | 91.2035 | 574.906 | 96.6534 | 53 | 45 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 14.2402 | 6.0469 | 38.5531 | 0.36937 | 6.5 | 6.6 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.2489 | 647.8912 | 93.3322 | SDS-HAA5 | mg/L | 6.2 | 75.3 | --- | 294.1167 | --- | 91.7663 | 216.0385 | 97.1301 | [8 empty] | SDS-HAA5 | mg/L | 4.7 | 41.9 | --- | 159.7 | --- | 88.7828 | 118.8216 | 96.0445 | [8 empty] | SDS-HAA5 | mg/L | 3.3 | 49 | --- | 193.7167 | --- | 93.2653 | 143.4978 | 97.7003 | [8 empty] | SDS-HAA5 | mg/L | 3.6 | 75.2 | --- | 380.4421 | --- | 95.2128 | 269.2299 | 98.6629 | [8 empty] | SDS-HAA5 | mg/L | 5.7 | 108 | --- | 544.1211 | --- | 94.7222 | 385.2242 | 98.5203 | [8 empty] | SDS-HAA5 | mg/L | 5.3 | 58 | --- | 282.6684 | --- | 90.8621 | 200.8125 | 97.3607 | [10 empty] | 12 | 4 | 8
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.2575 | [5 empty] | 1998-12-26 | 9:20 | 4314.3333 | 22 | 58 | 45 | 4 | 4 | 7.1 | 2.2 |  | 9.3 | 13.3 | 0.76344 | 0.43011 | 14.5641 | 15.9146 | 6.0392 | 41.4608 | 0.38385 | 7.3 | 6.3 | 29.64 | 179.8 | 224.5209 | 720 | 853.4548 | -18.5354 | 86.7986 | 633.5644 | 95.3217 | 58 | 53 | 4 | 4.9571 | 8.3429 | 9.3 | 13.3 | 0.32813 | 0.53303 | 15.2527 | 16.6671 | 5.743 | 45.757 | 0.36425 | 6.3 | 6.5 | 19.24 | 462 | 560 | 725.0783 | -29.4783 | 91.4306 | 593.5391 | 96.7584 | 53 | 45 | 4 | 2.1429 | 6.2 | 4.3429 | 8.3429 | 0.44097 | 0.49342 | 13.1868 | 14.4096 | 6.0611 | 38.9389 | 0.37006 | 6.5 | 6.6 | 43.2 | 560 | 720 | 738.6175 | -2.5858 | 80.759 | 649.3088 | 93.3468 | SDS-HAA6 | mg/L | 8.4 | 81.9 | --- | 314.65 | --- | 89.7436 | 231.6002 | 96.3731 | [8 empty] | SDS-HAA6 | mg/L | 4.7 | 51.2 | --- | 198.45 | --- | 90.8203 | 147.3521 | 96.8104 | [8 empty] | SDS-HAA6 | mg/L | 4.8 | 54.1 | --- | 210.2167 | --- | 91.1275 | 156.0419 | 96.9239 | [8 empty] | SDS-HAA6 | mg/L | 3.6 | 81.6 | --- | 414.1263 | --- | 95.5882 | 292.9733 | 98.7712 | [8 empty] | SDS-HAA6 | mg/L | 7.1 | 115 | --- | 574.9947 | --- | 93.8261 | 407.3998 | 98.2572 | [8 empty] | SDS-HAA6 | mg/L | 6.6 | 63.5 | --- | 306.0737 | --- | 89.6063 | 217.6941 | 96.9682 | [10 empty] | 13 | 5 | 8
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.2575 | [5 empty] | 1998-12-27 | 12:15 | 4341.25 | 22.7 | 58 | 46 | 4.4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.5887 | 6.0718 | 41.5282 | 0.37538 | 7.5 | 6.3 | 29.12 | 179.8 | 224.5209 | 720 | 855.133 | -18.7685 | 87.0302 | 636.3012 | 95.4236 | 58 | 54 | 4.4 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 16.3258 | 5.5567 | 46.0433 | 0.35457 | 6.3 | 6.5 | 19.24 | 448.8 | 560 | 701.012 | -25.1807 | 91.4306 | 574.906 | 96.6534 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 14.1145 | 6.0469 | 39.5531 | 0.35685 | 6.5 | NA | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.759 | 647.8912 | 93.3322 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | 12 | 4 | 8
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | [5 empty] | 1998-12-28 | 9:15 | 4362.25 | 22 | 59 | 46 | 4.1 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.9146 | 6.1619 | 42.2381 | 0.37678 | 7.5 | 6.4 | 29.12 | 182.7 | 227.4203 | 723.6 | 867.3893 | -19.8714 | 87.1955 | 645.3105 | 95.4874 | 59 | 54 | 4.1 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 16.6671 | 5.6252 | 46.7748 | 0.35633 | 6.4 | 6.6 | 20.54 | 455.4 | 595 | 710.7239 | -19.4494 | 90.9683 | 583.0619 | 96.4772 | 54 | 46 | 4.1 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 14.4096 | 6.4447 | 39.4553 | 0.36521 | 6.6 | 6.8 | 44.2 | 595 | 723.6 | 782.3469 | -8.1187 | 80.5646 | 688.6735 | 93.5819 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | 13 | 5 | 8
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 7.1288 | [5 empty] | 1998-12-29 | 9:00 | 4386 | 22.1 | 59 | 46 | 4.5 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.8676 | 6.088 | 41.912 | 0.37859 | 7.4 | 6.4 | 28.6 | 179.8 | 224.5209 | 720 | 856.8112 | -19.0016 | 87.2618 | 637.397 | 95.513 | 59 | 54 | 4.5 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 16.6179 | 5.6286 | 46.3714 | 0.35837 | 6.4 | 6.6 | 20.28 | 455.4 | 560 | 710.8765 | -26.9422 | 90.9674 | 583.1383 | 96.5223 | 54 | 46 | 4.5 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 14.3671 | 6.0469 | 39.4531 | 0.36416 | 6.6 | 6.7 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.759 | 647.8912 | 93.3322 | [110 empty] | 13 | 5 | 8
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1998-12-30 | 10:30 | 4411.5 | 20.7 | 59 | 46 | 4.1 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 16.538 | 6.2682 | 42.1318 | 0.39253 | 7.3 | 6.3 | 28.6 | 185.6 | 230.3196 | 720 | 881.3238 | -22.4061 | 87.5825 | 655.4156 | 95.6364 | 59 | 54 | 4.1 | 5.031 | 8.369 | 9.3 | 13.4 | 0.33004 | 0.54097 | 15.4801 | 17.5782 | 5.9233 | 46.4767 | 0.37822 | 6.3 | 6.6 | 19.76 | 475.2 | 560 | 748.9894 | -33.7481 | 91.4206 | 612.0947 | 96.7717 | 54 | 46 | 4.1 | 2.069 | 6.3 | 4.269 | 8.369 | 0.44479 | 0.48465 | 12.7321 | 14.4577 | 6.0166 | 39.8834 | 0.3625 | 6.6 | 6.7 | 43.2 | 560 | 720 | 729.7209 | -1.3501 | 81.2435 | 644.8604 | 93.3009 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [19 empty] | 13 | 5 | 8
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 2.1288 | [5 empty] | 1998-12-31 | 9:00 | 4434 | 19.5 | 59 | 46 | 4.4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 17.1352 | 6.088 | 42.012 | 0.40786 | 7.2 | 6.3 | 28.6 | 179.8 | 224.5209 | 720 | 856.8112 | -19.0016 | 87.2618 | 637.397 | 95.513 | 59 | 54 | 4.4 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 17.9454 | 6.0622 | 46.0378 | 0.3898 | 6.3 | 6.5 | 19.76 | 488.4 | 560 | 763.5575 | -36.3496 | 91.199 | 625.9787 | 96.8433 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 15.5147 | 6.0469 | 39.5531 | 0.39225 | 6.5 | 6.6 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.759 | 647.8912 | 93.3322 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [14 empty] | 13 | 5 | 8
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 6.3863 | [5 empty] | 1999-01-01 | 10:30 | 4459.5 | 22.2 | 59 | 46 | 4.4 | 4.1 | 7.1 | 2.3 |  | 9.4 | 13.5 | 0.75532 | 0.43617 | 14.5641 | 15.8208 | 5.8873 | 42.2127 | 0.37479 | 7.1 | 6.3 | 28.6 | 179.8 | 224.0453 | 720 | 827.3764 | -14.9134 | 87.2347 | 617.3278 | 95.3671 | 59 | 54 | 4.4 | 4.8778 | 8.6222 | 9.4 | 13.5 | 0.33539 | 0.51891 | 15.0085 | 16.3036 | 6.0087 | 46.0913 | 0.35372 | 6.3 | 6.5 | 20.02 | 488.4 | 560 | 753.3727 | -34.5308 | 91.0643 | 620.8864 | 96.7756 | 54 | 46 | 4.4 | 2.2222 | 6.4 | 4.5222 | 8.6222 | 0.4555 | 0.4914 | 13.6752 | 14.8552 | 6.0652 | 39.5348 | 0.37575 | 6.5 | 6.6 | 43.2 | 560 | 720 | 739.4444 | -2.7006 | 80.7182 | 649.7222 | 93.351 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [13 empty] | 13 | 5 | 8
|  |  |  | System feed flow rate, QF-sys (gpm) | 8.515 | [5 empty] | 1999-01-02 | 9:20 | 4482.3333 | 22.6 | 58 | 45 | 4 | 4.1 | 7.1 | 2.3 |  | 9.4 | 13.5 | 0.75532 | 0.43617 | 14.5641 | 15.6348 | 5.8716 | 41.6284 | 0.37558 | 7.2 | 6.4 | 29.12 | 179.8 | 224.0453 | 720 | 825.7712 | -14.6904 | 87.0026 | 616.2814 | 95.2749 | 58 | 52 | 4 | 4.9571 | 8.5429 | 9.4 | 13.5 | 0.33419 | 0.52736 | 15.2527 | 16.3741 | 6.0461 | 44.9539 | 0.36424 | 6.4 | 6.6 | 19.76 | 488.4 | 560 | 760.3366 | -35.7744 | 91.1804 | 624.3683 | 96.8352 | 52 | 45 | 4 | 2.1429 | 6.4 | 4.4429 | 8.5429 | 0.4531 | 0.48232 | 13.1868 | 14.1563 | 6.0332 | 38.4668 | 0.36801 | 6.6 | 6.6 | 43.2 | 560 | 720 | 733.0357 | -1.8105 | 80.7182 | 646.5179 | 93.318 | Qp/QT (THM4), % | 18.5606 | 64.0152 |  | Qp/QT (HAA5), % | 30.8249 | 69.8987 | [11 empty] | Qp/QT (THM4), % | 37.0594 | 73.3132 |  | Qp/QT (HAA5), % | -32.5269 | 40.0538 | [11 empty] | Qp/QT (THM4), % | 18.0025 | 62.3921 |  | Qp/QT (HAA5), % | -10.9409 | 48.14 | [11 empty] | Qp/QT (THM4), % | 25.7869 | 69.3705 |  | Qp/QT (HAA5), % | 29.6089 | 67.3184 | [11 empty] | Qp/QT (THM4), % | -18.7387 | 46.1261 |  | Qp/QT (HAA5), % | 52.7859 | 79.1789 | [11 empty] | Qp/QT (THM4), % | -14.4404 | 50.5415 |  | Qp/QT (HAA5), % | 7.5901 | 58.8235 | [13 empty] | 13 | 6 | 7
[11 empty] | 1999-01-03 | 12:30 | 4509.5 | 23.5 | 59 | 46 | 4.2 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 15.2244 | 6.1781 | 42.1219 | 0.36144 | 7.6 | 6.4 | 28.6 | 182.7 | 227.4203 | 756 | 869.0675 | -14.956 | 87.4242 | 646.4063 | 95.5755 | 59 | 54 | 4.2 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 15.9442 | 5.3825 | 46.9175 | 0.33984 | 6.4 | 6.7 | 19.5 | 435.6 | 595 | 679.9091 | -14.2704 | 91.4256 | 557.7546 | 96.5038 | 54 | 46 | 4.2 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 13.7846 | 6.4447 | 39.3553 | 0.35026 | 6.7 | 6.8 | 44.2 | 595 | 756 | 782.3469 | -3.485 | 80.5646 | 688.6735 | 93.5819 | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 62.2867 | 31.3402 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 69.0266 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 47.5584 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 68.843 | 37.695 | [11 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 32.3038 | 17.6557 | [11 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 59.7951 | 31.4118 | [13 empty] | 13 | 5 | 8
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1999-01-04 | 10:00 | 4531 | 19 | 59 | 46 | 4.4 | 4.1 | 7 | 2.2 |  | 9.2 | 13.3 | 0.76087 | 0.44565 | 14.359 | 17.1454 | 6.052 | 42.048 | 0.40776 | 7.4 | 6.3 | 28.6 | 179.8 | 225.0069 | 720 | 849.938 | -18.0469 | 87.2893 | 633.7964 | 95.4875 | 59 | 54 | 4.4 | 4.8571 | 8.4429 | 9.2 | 13.3 | 0.32964 | 0.52795 | 14.9451 | 17.8452 | 6.0445 | 46.0555 | 0.38747 | 6.3 | 6.5 | 18.98 | 488.4 | 560 | 758.4555 | -35.4385 | 91.5647 | 623.4277 | 96.9555 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 15.7457 | 6.0469 | 39.5531 | 0.39809 | 6.5 | 6.6 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 80.8006 | 647.8912 | 93.3322 | SDS-HAA5b, mg/L | 62.4746 | 31.0655 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | 28.1139 | 14.6275 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | 40.7729 | 20.4868 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | 56.7366 | 25.5308 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | NA | 60.813 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | NA | 31.3646 |  | SDS-HAA5b, mg/L | 54 | 27 | [13 empty] | 13 | 5 | 8
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.35 | [5 empty] | 1999-01-05 | 9:00 | 4554 | 18.3 | 59 | 46 | 4.4 | 4.1 | 7 | 2.2 |  | 9.2 | 13.3 | 0.76087 | 0.44565 | 14.359 | 17.5038 | 6.2306 | 41.8694 | 0.41806 | 7.4 | 6.3 | 28.6 | 185.6 | 230.8056 | 756 | 874.1869 | -15.6332 | 87.6086 | 651.6641 | 95.6112 | 59 | 54 | 4.4 | 4.8571 | 8.4429 | 9.2 | 13.3 | 0.32964 | 0.52795 | 14.9451 | 18.2183 | 6.1194 | 45.9806 | 0.39622 | 6.3 | 6.5 | 19.76 | 495 | 560 | 768.4037 | -37.215 | 91.4387 | 631.7019 | 96.8719 | 54 | 46 | 4.4 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 16.0749 | 6.0469 | 39.5531 | 0.40641 | 6.5 | 6.6 | 43.2 | 560 | 756 | 735.7823 | 2.6743 | 81.2829 | 647.8912 | 93.3322 | SDS-TOXb, mg Cl- /L | 332.1402 | 163.5038 |  | SDS-TOXb, mg Cl- /L | 286.6397 | 141.6758 | [11 empty] | SDS-TOXb, mg Cl- /L | 240.3041 | 132.993 |  | SDS-TOXb, mg Cl- /L | NA | 231.4409 | [11 empty] | SDS-TOXb, mg Cl- /L | 256.693 | 130.1825 |  | SDS-TOXb, mg Cl- /L | NA | 170.8009 | [11 empty] | SDS-TOXb, mg Cl- /L | 308.0097 | 142.3923 |  | SDS-TOXb, mg Cl- /L | 293.486 | 150.1899 | [11 empty] | SDS-TOXb, mg Cl- /L | NA | 129.7441 |  | SDS-TOXb, mg Cl- /L | 117.2903 | 67.9355 | [11 empty] | SDS-TOXb, mg Cl- /L | NA | 185.7834 |  | SDS-TOXb, mg Cl- /L | 321.9393 | 159.5294 | [13 empty] | 13 | 5 | 8
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 4.75 | [5 empty] | 1999-01-06 | 8:30 | 4577.5 | 17.8 | 59 | 46 | 4 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 18.0182 | 6.088 | 42.412 | 0.42484 | 7.3 | 6.4 | 28.6 | 179.8 | 224.5209 | 727.2 | 856.8112 | -17.8233 | 87.2618 | 637.397 | 95.513 | 59 | 54 | 4 | 4.96 | 8.44 | 9.3 | 13.4 | 0.33112 | 0.53333 | 15.2615 | 18.8811 | 6.2443 | 46.2557 | 0.40819 | 6.4 | 6.6 | 18.98 | 501.6 | 560 | 785.225 | -40.2188 | 91.5464 | 643.4125 | 97.0501 | 54 | 46 | 4 | 2.14 | 6.3 | 4.34 | 8.44 | 0.44695 | 0.49309 | 13.1692 | 16.2925 | 6.0457 | 39.9543 | 0.40778 | 6.6 | 6.7 | 43.2 | 560 | 727.2 | 735.5479 | -1.148 | 80.759 | 647.774 | 93.331 | SDS-CDb, mg/L | 6.984 | 5.7204 |  | SDS-CDb, mg/L | 6.6431 | 5.5568 | [11 empty] | SDS-CDb, mg/L | 6.2924 | 5.3752 |  | SDS-CDb, mg/L | NA | 6.2166 | [11 empty] | SDS-CDb, mg/L | 6.5715 | 5.0711 |  | SDS-CDb, mg/L | NA | 5.5529 | [11 empty] | SDS-CDb, mg/L | 7.0006 | 5.6495 |  | SDS-CDb, mg/L | 6.8821 | 5.7131 | [11 empty] | SDS-CDb, mg/L | NA | 6.1623 |  | SDS-CDb, mg/L | 5.9692 | 5.2038 | [11 empty] | SDS-CDb, mg/L | NA | 5.9354 |  | SDS-CDb, mg/L | 7.0951 | 5.7118 | [13 empty] | 13 | 5 | 8
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 10 | [5 empty] | 1999-01-07 | 9:00 | 4602 | 19.9 | 59 | 46 | 4.3 | 4.1 | 7.1 | 2.2 |  | 9.3 | 13.4 | 0.76344 | 0.44086 | 14.5641 | 16.9338 | 6.252 | 41.948 | 0.40368 | 7.4 | 6.4 | 29.12 | 185.6 | 230.3196 | 720 | 879.6456 | -22.173 | 87.3567 | 654.3198 | 95.5496 | 59 | 54 | 4.3 | 4.9571 | 8.4429 | 9.3 | 13.4 | 0.33116 | 0.53303 | 15.2527 | 17.7345 | 6.042 | 46.158 | 0.38421 | 6.4 | 6.6 | 21.32 | 488.4 | 560 | 762.6416 | -36.186 | 90.7433 | 625.5208 | 96.5916 | 54 | 46 | 4.3 | 2.1429 | 6.3 | 4.3429 | 8.4429 | 0.44703 | 0.49342 | 13.1868 | 15.3324 | 6.0469 | 39.6531 | 0.38666 | 6.6 | 6.8 | 43.2 | 560 | 720 | 735.7823 | -2.192 | 81.2435 | 647.8912 | 93.3322 | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1999-01-08 | 8:00 | 4625 | 19.9 | 59 | 46 | 4.5 | 4.6 | 7 | 4.4 |  | 11.4 | 16 | 0.61404 | 0.40351 | 14.359 | 16.6953 | 3.9164 | 44.0836 | 0.37872 | 7.4 | 6.3 | 28.6 | 185.6 | 222.0833 | 720 | 529.8977 | 26.4031 | 87.122 | 420.2388 | 93.1943 | 59 | 54 | 4.5 | 4.8571 | 11.1429 | 11.4 | 16 | 0.41151 | 0.42607 | 14.9451 | 17.3767 | 5.7945 | 46.2055 | 0.37607 | 6.3 | 6.5 | 19.24 | 495 | 560 | 702.3826 | -25.4255 | 91.3366 | 598.6913 | 96.7863 | 54 | 46 | 4.5 | 2.1429 | 9 | 6.5429 | 11.1429 | 0.61077 | 0.32751 | 13.1868 | 15.3324 | 5.7832 | 39.7168 | 0.38604 | 6.5 | 6.6 | 43.2 | 560 | 720 | 683.0476 | 5.1323 | 80.5478 | 621.5238 | 93.0493 | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Design permeate pressure, Pp (psi) | [6 empty] | 1999-01-08 | 15:30 | 4632.5 | 23.2 | 62 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.4417 | #VALUE! | #VALUE! | #VALUE! | NA | 6.2 | 31.2 | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 62 | 58 | 4.6 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 17.1739 | 6.1461 | 49.2539 | 0.34868 | 6.2 | 6.5 | 19.2 | 475.2 | 560 | 792.4174 | -41.5031 | #VALUE! | 633.8087 | 96.9707 | 58 | 51 | 4.6 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 14.9772 | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [13 empty] | 11 | 4 | 7
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 19 | [5 empty] | 1999-01-09 | 9:00 | 4650 | 20.5 | 62 | 50 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.8076 | 7.0964 | 44.4036 | 0.40104 | 7.2 | 6.2 | 37.21 | 185.6 | 229.844 | 720 | 1043.1874 | -44.8871 | 83.8108 | 746.853 | 95.0178 | 62 | 57 | 4.5 | 5.4571 | 7.4429 | 9.4 | 12.9 | 0.30842 | 0.58055 | 16.7912 | 19.18 | 6.5238 | 48.4762 | 0.39566 | 6.2 | 6.6 | 17.63 | 495 | 552 | 845.0102 | -53.0816 | 92.3296 | 670.0051 | 97.3687 | 57 | 50 | 4.5 | 2.1429 | 5.3 | 3.9429 | 7.4429 | 0.38639 | 0.54348 | 13.1868 | 15.0629 | 6.1166 | 42.8834 | 0.35125 | 6.6 | 6.8 | 43.2 | 552 | 720 | 757.7143 | -5.2381 | 81.2046 | 654.8571 | 93.4031 | Alkb, mg/L CaCO3 | 84.4091 | 46.2273 |  | Alkb, mg/L CaCO3 | 74.1071 | 41.2851 | [11 empty] | Alkb, mg/L CaCO3 | 69.6113 | 39.8832 |  | Alkb, mg/L CaCO3 | NA | 67.1559 | [11 empty] | Alkb, mg/L CaCO3 | 76.2182 | 44.7016 |  | Alkb, mg/L CaCO3 | NA | 54.8206 | [11 empty] | Alkb, mg/L CaCO3 | 66.4649 | 36.8281 |  | Alkb, mg/L CaCO3 | 63.8659 | 38.2235 | [11 empty] | Alkb, mg/L CaCO3 | NA | 47.7856 |  | Alkb, mg/L CaCO3 | 43.8563 | 28.2845 | [11 empty] | Alkb, mg/L CaCO3 | NA | 44.6859 |  | Alkb, mg/L CaCO3 | 69.5977 | 39.8824 | [13 empty] | 12 | 5 | 7
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 48.5185 | [5 empty] | 1999-01-10 | 12:15 | 4677.25 | 18.3 | 63 | 52 | 4.6 | 3.5 | 7.6 | 1.4 |  | 9 | 12.5 | 0.84444 | 0.38889 | 15.5897 | 19.0041 | 8.7342 | 44.1658 | 0.43029 | 7.6 | 6.4 | 36.6 | 185.6 | 231.8099 | 864 | 1291.5208 | -49.4816 | 84.2112 | 910.0249 | 95.9781 | 63 | 59 | 4.6 | 5.2923 | 7.2077 | 9 | 12.5 | 0.29879 | 0.58803 | 16.284 | 19.8505 | 5.3591 | 51.0409 | 0.38891 | 6.4 | 6.5 | 17.2 | 409.2 | 621 | 697.0292 | -12.243 | 92.5801 | 553.1146 | 96.8903 | 59 | 52 | 4.6 | 2.3077 | 4.9 | 3.7077 | 7.2077 | 0.36713 | 0.62241 | 14.2012 | 17.3115 | 7.0719 | 43.8281 | 0.39499 | 6.5 | 6.7 | 48.6 | 621 | 864 | 890.5761 | -3.0759 | 79.0345 | 755.7881 | 93.5696 | T-Hdb, mg/L CaCO3 | 150.303 | 77.5758 |  | T-Hdb, mg/L CaCO3 | 130.6802 | 68.1621 | [11 empty] | T-Hdb, mg/L CaCO3 | 120.7049 | 62.6989 |  | T-Hdb, mg/L CaCO3 | NA | 115.914 | [11 empty] | T-Hdb, mg/L CaCO3 | 151.3761 | 80.7965 |  | T-Hdb, mg/L CaCO3 | NA | 103.4573 | [11 empty] | T-Hdb, mg/L CaCO3 | 131.5775 | 66.638 |  | T-Hdb, mg/L CaCO3 | 125.8827 | 69.6955 | [11 empty] | T-Hdb, mg/L CaCO3 | NA | 107.582 |  | T-Hdb, mg/L CaCO3 | 97.1261 | 55.6891 | [11 empty] | T-Hdb, mg/L CaCO3 | NA | 100.1444 |  | T-Hdb, mg/L CaCO3 | 168.0076 | 87.0588 | [13 empty] | 11 | 4 | 7
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 26.65 | [5 empty] | 1999-01-11 | 9:30 | 4698.5 | 20.3 | 64 | 52 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.9132 | 7.1189 | 46.2811 | 0.38705 | 7.5 | 6.4 | 36.6 | 185.6 | 229.844 | 864 | 1045.763 | -21.0374 | 84.0762 | 748.4901 | 95.1102 | 64 | 59 | 4.6 | 5.3778 | 7.5222 | 9.4 | 12.9 | 0.30962 | 0.5721 | 16.547 | 19.0132 | 6.668 | 50.232 | 0.37851 | 6.4 | 6.5 | 16.985 | 508.2 | 621 | 859.3788 | -38.3863 | 92.6102 | 683.7894 | 97.516 | 59 | 52 | 4.6 | 2.2222 | 5.3 | 4.0222 | 7.5222 | 0.38879 | 0.55249 | 13.6752 | 15.7134 | 6.924 | 43.976 | 0.35732 | 6.5 | 6.7 | 48.6 | 621 | 864 | 861 | 0.34722 | 78.8552 | 741 | 93.4413 | Ca-Hdb, mg/L CaCO3 | 133.4583 | 68.4583 |  | Ca-Hdb, mg/L CaCO3 | 115.9204 | 60.0449 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 100.711 | 52.4935 |  | Ca-Hdb, mg/L CaCO3 | NA | 96.7285 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 134.4365 | 71.4032 |  | Ca-Hdb, mg/L CaCO3 | NA | 91.6411 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 115.9613 | 58.431 |  | Ca-Hdb, mg/L CaCO3 | 110.9162 | 61.1397 | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | 95.4234 |  | Ca-Hdb, mg/L CaCO3 | 86.0997 | 49.1496 | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | 88.7365 |  | Ca-Hdb, mg/L CaCO3 | 149.2979 | 77.0588 | [13 empty] | 12 | 5 | 7
|  |  |  | Required influent pressure to the system, PI (psi) | 75.1685 | [5 empty] | 1999-01-12 | 10:00 | 4723 | 22 | 64 | 53 | 4.5 | 3.4 | 7.7 | 1.6 |  | 9.3 | 12.7 | 0.82796 | 0.36559 | 15.7949 | 17.2595 | 7.5128 | 46.4872 | 0.37127 | 7.3 | 6.2 | 39.04 | 179.8 | 224.5209 | 864 | 1117.1479 | -29.2995 | 82.6119 | 790.3199 | 95.0602 | 64 | 59 | 4.5 | 5.3923 | 7.3077 | 9.3 | 12.7 | 0.30334 | 0.57982 | 16.5917 | 18.1302 | 6.5526 | 50.4474 | 0.35939 | 6.2 | 6.4 | 16.34 | 495 | 621 | 848.2007 | -36.5863 | 92.7223 | 671.6003 | 97.567 | 59 | 53 | 4.5 | 2.3077 | 5 | 3.9077 | 7.3077 | 0.37319 | 0.59055 | 14.2012 | 15.518 | 6.9785 | 44.5215 | 0.34855 | 6.4 | 6.5 | 54 | 621 | 864 | 882.6923 | -2.1635 | 75.9488 | 751.8462 | 92.8177 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [19 empty] | 11 | 5 | 6
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1999-01-13 | 8:20 | 4745.3333 | 20.8 | 64 | 53 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.6504 | 6.8828 | 47.1172 | 0.37461 | 7.3 | 6.2 | 37.21 | 179.8 | 224.0453 | 828 | 1012.9054 | -22.3316 | 83.3918 | 725.4912 | 94.8711 | 64 | 59 | 4.5 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 18.4365 | 6.4515 | 50.5485 | 0.36473 | 6.2 | 6.4 | 16.34 | 495 | 593.4 | 827.9809 | -39.5317 | 92.7068 | 661.4904 | 97.5298 | 59 | 53 | 4.5 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 16.0783 | 6.5683 | 44.9317 | 0.35784 | 6.4 | 6.5 | 54 | 593.4 | 828 | 828.2621 | -0.031657 | 75.8977 | 710.8311 | 92.4033 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [19 empty] | 11 | 5 | 6
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1999-01-14 | 8:10 | 4769.1667 | 21.6 | 62 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.2379 | 7.074 | 44.826 | 0.38455 | 7.2 | 6 | 37.82 | 185.6 | 229.844 | 900 | 1040.6118 | -15.6235 | 83.5454 | 745.2158 | 94.925 | 62 | 58 | 4.6 | 5.3778 | 7.5222 | 9.4 | 12.9 | 0.30962 | 0.5721 | 16.547 | 18.2964 | 6.5755 | 48.8245 | 0.37474 | 6 | 6.2 | 17.2 | 501.6 | 621 | 847.9066 | -36.5389 | 92.5167 | 674.7533 | 97.4509 | 58 | 51 | 4.6 | 2.2222 | 5.3 | 4.0222 | 7.5222 | 0.38879 | 0.55249 | 13.6752 | 15.121 | 6.924 | 42.976 | 0.35185 | 6.2 | 6 | 48.6 | 621 | 900 | 861 | 4.3333 | 78.8552 | 741 | 93.4413 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [19 empty] | 11 | 4 | 7
[11 empty] | 1999-01-15 | 10:00 | 4795 | 22.6 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.7359 | 6.6692 | 45.7308 | 0.36596 | 7.1 | 6.3 | 37.21 | 174 | 218.2466 | 864 | 982.6234 | -13.7296 | 82.9505 | 704.1295 | 94.7155 | 63 | 59 | 4.6 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 17.4812 | 6.1643 | 50.2356 | 0.34798 | 6.3 | 6.2 | 17.845 | 475.2 | 560 | 793.36 | -41.6714 | 91.8235 | 634.28 | 97.1866 | 59 | 51 | 4.6 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.2452 | 7.8104 | 42.5896 | 0.35796 | 6.2 | 6 | 48.6 | 690 | 864 | 969.2743 | -12.1845 | 77.7316 | 829.6372 | 94.142 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [19 empty] | 12 | 4 | 8
[11 empty] | 1999-01-16 | 10:20 | 4819.3333 | 22.6 | 62 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.7359 | 6.6917 | 45.2083 | 0.37019 | 7.2 | 6.4 | 36.6 | 174 | 218.2466 | 864 | 985.1989 | -14.0277 | 83.23 | 705.7667 | 94.8142 | 62 | 59 | 4.6 | 5.3778 | 7.5222 | 9.4 | 12.9 | 0.30962 | 0.5721 | 16.547 | 17.7635 | 6.1392 | 49.7608 | 0.35698 | 6.4 | 6.4 | 16.34 | 468.6 | 560 | 791.9292 | -41.4159 | 92.5131 | 630.2646 | 97.4074 | 59 | 51 | 4.6 | 2.2222 | 5.3 | 4.0222 | 7.5222 | 0.38879 | 0.55249 | 13.6752 | 14.6806 | 6.8587 | 43.5413 | 0.33716 | 6.4 | 6.5 | 54 | 621 | 864 | 858.7358 | 0.60928 | 75.2573 | 739.8679 | 92.7014 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [19 empty] | 11 | 3 | 8
[11 empty] | 1999-01-17 | 12:15 | 4845.25 | 24.1 | 63 | 51 | 4.7 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.01 | 6.478 | 45.822 | 0.3494 | 7.8 | 6.4 | 36.6 | 168.2 | 212.4479 | 792 | 954.9169 | -20.5703 | 82.7722 | 684.4049 | 94.6523 | 63 | 58 | 4.7 | 5.2 | 7.7 | 9.4 | 12.9 | 0.31232 | 0.55319 | 16 | 16.4314 | 5.8818 | 49.9182 | 0.32917 | 6.4 | 6.5 | 15.695 | 455.4 | 558.9 | 752.3436 | -34.6115 | 92.6123 | 603.8718 | 97.4009 | 58 | 51 | 4.7 | 2.4 | 5.3 | 4.2 | 7.7 | 0.39419 | 0.57143 | 14.7692 | 15.1674 | 6.2584 | 43.5416 | 0.34834 | 6.5 | 6.6 | 48.6 | 558.9 | 792 | 789.9792 | 0.25515 | 77.1238 | 674.4396 | 92.794 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [19 empty] | 12 | 5 | 7
[11 empty] | 1999-01-18 | 10:30 | 4867.5 | 23.1 | 62 | 50 | 4.9 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.4903 | 6.6692 | 44.4308 | 0.37115 | 7.8 | 6.1 | 37.21 | 174 | 218.2466 | 792 | 982.6234 | -24.0686 | 82.9505 | 704.1295 | 94.7155 | 62 | 58 | 4.9 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 17.2247 | 6.1383 | 48.9617 | 0.3518 | 6.1 | 6.4 | 19.78 | 475.2 | 552 | 792.0139 | -43.4808 | 90.9369 | 633.607 | 96.8782 | 58 | 50 | 4.9 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.0216 | 6.1299 | 42.9701 | 0.34958 | 6.4 | 6.6 | 48.6 | 552 | 792 | 771.1872 | 2.6279 | 77.7316 | 661.5936 | 92.6541 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [19 empty] | 12 | 4 | 8
[11 empty] | 1999-01-19 | 9:00 | 4890 | 22 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.0353 | 6.6692 | 45.7308 | 0.37251 | 7.5 | 6.1 | 37.21 | 174 | 218.2466 | 864 | 982.6234 | -13.7296 | 82.9505 | 704.1295 | 94.7155 | 63 | 58 | 4.6 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 17.794 | 6.2736 | 49.6264 | 0.35856 | 6.1 | 6.3 | 16.34 | 481.8 | 558.9 | 805.5983 | -44.14 | 92.5131 | 643.6991 | 97.4615 | 58 | 51 | 4.6 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.518 | 6.214 | 43.686 | 0.35522 | 6.3 | 6.6 | 48.6 | 558.9 | 864 | 781.0916 | 9.5959 | 77.7316 | 669.9958 | 92.7462 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [19 empty] | 12 | 5 | 7
[11 empty] | 1999-01-20 | 9:00 | 4914 | 21.1 | 62 | 51 | 4.2 | 3.5 | 7.3 | 1.8 |  | 9.1 | 12.6 | 0.8022 | 0.38462 | 14.9744 | 16.804 | 7.0138 | 45.2862 | 0.37106 | 7.5 | 6.2 | 35.99 | 185.6 | 231.3022 | 864 | 1023.4018 | -18.4493 | 84.4403 | 737.3658 | 95.1191 | 62 | 58 | 4.2 | 4.9923 | 7.6077 | 9.1 | 12.6 | 0.30637 | 0.54861 | 15.3609 | 17.2379 | 6.5353 | 49.2647 | 0.3499 | 6.2 | 6.3 | 16.125 | 508.2 | 586.5 | 831.1087 | -41.7065 | 93.0286 | 669.6543 | 97.592 | 58 | 51 | 4.2 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.9364 | 6.55 | 43.75 | 0.36426 | 6.3 | 6.4 | 48.6 | 586.5 | 864 | 820.709 | 5.0105 | 78.9885 | 703.6045 | 93.0927 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [19 empty] | 11 | 4 | 7
[11 empty] | 1999-01-21 | 8:30 | 4937.5 | 21.3 | 63 | 51 | 4.8 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.3915 | 6.8828 | 45.3172 | 0.38377 | 7.2 | 6.1 | 37.21 | 179.8 | 224.0453 | 864 | 1012.9054 | -17.2344 | 83.3918 | 725.4912 | 94.8711 | 63 | 59 | 4.8 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 18.166 | 6.5492 | 49.6508 | 0.36588 | 6.1 | 6.2 | 15.695 | 501.6 | 586.5 | 839.6209 | -43.1579 | 92.9947 | 670.6104 | 97.6596 | 59 | 51 | 4.8 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.8424 | 6.55 | 43.65 | 0.36294 | 6.2 | 6.3 | 48.6 | 586.5 | 864 | 820.709 | 5.0105 | 78.308 | 703.6045 | 93.0927 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [19 empty] | 12 | 4 | 8
[11 empty] | 1999-01-22 | 10:35 | 4963.5833 | 23.6 | 62 | 51 | 4.2 | 3.5 | 7.7 | 1.8 |  | 9.5 | 13 | 0.81053 | 0.36842 | 15.7949 | 16.4622 | 6.9232 | 45.3768 | 0.36279 | 7.4 | 6.3 | 37.21 | 179.8 | 223.5797 | 864 | 1020.8276 | -18.1513 | 83.3572 | 729.5255 | 94.8994 | 62 | 58 | 4.2 | 5.4778 | 7.5222 | 9.5 | 13 | 0.31114 | 0.57661 | 16.8547 | 17.5668 | 6.7124 | 49.0876 | 0.35787 | 6.3 | 6.3 | 16.125 | 508.2 | 586.5 | 866.5353 | -47.7468 | 92.7878 | 687.3676 | 97.6541 | 58 | 51 | 4.2 | 2.2222 | 5.3 | 4.0222 | 7.5222 | 0.38879 | 0.55249 | 13.6752 | 14.253 | 6.5067 | 43.7933 | 0.32546 | 6.3 | 6.4 | 48.6 | 586.5 | 864 | 812.0346 | 6.0145 | 78.2628 | 699.2673 | 93.0499 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [19 empty] | 11 | 4 | 7
[11 empty] | 1999-01-23 | 8:30 | 4985.5 | 23.1 | 61 | 50 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.4903 | 7.074 | 43.926 | 0.37541 | 7.4 | 6.3 | 37.82 | 185.6 | 229.844 | 792 | 1040.6118 | -31.3904 | 83.5454 | 745.2158 | 94.925 | 61 | 56 | 4.5 | 5.4571 | 7.4429 | 9.4 | 12.9 | 0.30842 | 0.58055 | 16.7912 | 17.7612 | 6.3246 | 47.6754 | 0.37254 | 6.3 | 6.3 | 19 | 481.8 | 586.5 | 821.1274 | -40.0047 | 91.7335 | 651.4637 | 97.0835 | 56 | 50 | 4.5 | 2.1429 | 5.3 | 3.9429 | 7.4429 | 0.38639 | 0.54348 | 13.1868 | 13.9486 | 6.4664 | 42.0336 | 0.33184 | 6.3 | 6.4 | 48.6 | 586.5 | 792 | 803.9798 | -1.5126 | 78.8552 | 695.2399 | 93.0096 | [110 empty] | 11 | 5 | 6
[11 empty] | 1999-01-24 | 12:30 | 5013.5 | 22.6 | 63 | 51 | 4.7 | 3.5 | 7.5 | 1.6 |  | 9.1 | 12.6 | 0.82418 | 0.38462 | 15.3846 | 16.5157 | 5.4645 | 46.8355 | 0.35263 | 7.5 | 6.4 | 37.21 | 174 | 174 | 864 | 815.2031 | 5.6478 | 78.6149 | 583.6576 | 93.6247 | 63 | 59 | 4.7 | 5.1923 | 7.4077 | 9.1 | 12.6 | 0.30334 | 0.57058 | 15.9763 | 17.1509 | 5.5099 | 50.7901 | 0.33768 | 6.4 | 6.5 | 21 | 429 | 621 | 714.9813 | -15.1339 | 87.931 | 571.9907 | 96.3286 | 59 | 51 | 4.7 | 2.3077 | 5.1 | 3.9077 | 7.4077 | 0.37926 | 0.59055 | 14.2012 | 15.2452 | 7.019 | 43.281 | 0.35224 | 6.5 | 6.7 | 48.6 | 621 | 864 | 880.0045 | -1.8524 | 72.069 | 750.5023 | 93.5243 | [110 empty] | 12 | 4 | 8
Note on DR40: S Allgeier 7/20/99: Brian Mathews verified TCAA concentration.
Note on EL40: S Allgeier 7/20/99: Brian Mathews verified TCAA concentration.

## Sheet4. Weeks 31-40
FIELD-SET 4: PILOT-SCALE MEMBRANE RESULTS: WEEKS 31-40 (FILE: mempilot.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: 2-Stage Membrane Pilot System Design Parameters |  | Field 4-4: Foulants And Fouling Indices1 |  | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Membrane Performance Data During Operation With The Test Water | [18 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-6: Membrane Performance Data During Operation With The Test Water (continued) | [23 empty] | Field 4-7: System And Stage Water Quality For Week 32 | [9 empty] | Field 4-7: System And Stage Water Quality For Week 32 (continued) | [7 empty] | Field 4-8: System And Stage Water Quality For Week 34 | [9 empty] | Field 4-8: System And Stage Water Quality For Week 34 (continued) | [7 empty] | Field 4-9: System And Stage Water Quality For Week 36 | [9 empty] | Field 4-9: System And Stage Water Quality For Week 36 (continued) | [7 empty] | Field 4-10: System And Stage Water Quality For Week 38 | [9 empty] | Field 4-10: System And Stage Water Quality For Week 38 (continued) | [7 empty] | Field 4-11: System And Stage Water Quality For Week 40 | [9 empty] | Field 4-11: System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 40 | [9 empty] | Field 4-12: Duplicate Analysis Of System And Stage Water Quality For Week 40 (continued) | [7 empty] | Field 4-13: Membrane Cost Parameters
|  | General Information |  | Calculate Temperature Normalized MTCW |  | Parameters Evaluated Prior to Pretreatment |  |  |  |  | System Operating Parameters | [30 empty] | Stage 1 Operating Parameters | [23 empty] | Stage 2 Operating Parameters | [23 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | System Operating Parameters During Sample Collection | [9 empty] | Stage 1 Operating Parameters During Sample Collection | [7 empty] | General Cost Parameters
PWS Name | Fla.Water Services Corp.-Deltona Lakes | Membrane manufacturer | Fluid Systems | Average yearly temperature of feed water, TavgoC (oC) | 25 | Alkalinity (mg/L as CaCO3) | 222 | Process | Description | Scale | Date | Time | Operation |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  | SYSTEM |  |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 1 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  | STAGE 2 |  |  |  | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.55 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 | [6 empty] | System recovery during sample collection (decimal) | 0.81 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 | [6 empty] | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.58 | [6 empty] | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 | [6 empty] | System recovery during sample collection (decimal) | 0.82 | [8 empty] | Stage 1 recovery during sample collection (decimal) | 0.57 |  |  |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL3640287 | Membrane trade name | Fluid Systems 4921S | Temperature normalized MTCW (gfd/psi) | 0.27 | Calcium Hardness (mg/L as CaCO3) | 158 | Cartridge filtration | 5 mm exclusion size | Pilot scale |  |  | time | Influent | PI | PC | PP | QR | Qp | QW | Cleaning Event | QF | QI | Recovery | Recycle | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) |  |  |  |  | PI | PC | PP | Qp | Qc | QF | QI | vc | Recovery | FW (ToC) | FW (TavgoC) | Dp | NDP | MTCW (TavgoC) | pH |  |  |  |  | TDS (mg/L) | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.2 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.4 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.38 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.28 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.38 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.29 | [6 empty] | System feed flow rate during sample collection (gpm) | 9.3 | [8 empty] | Stage 1 permeate flow rate during sample collection (gpm) | 5.29 |  |  |  |  | Capital Recovery Interest Rate (%) | 7.5 | Pressure Drop
Water Industry Data Base Number (optional) | N/A | Membrane element model number | 4040-TFCS 4921S |  |  | LSI | 0.13 | Sulfuric Acid addition | pH=6.4(@ 75% rec.), 6.2(@ 80% rec.) | Pilot scale | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | Indicate with "X" | (gpm) | (gpm) | (decimal) | ratio | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHF (before acid) | pHF (after acid) | TDSp | TDSF (before acid) | TDSF (after acid) | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | (psi) | (psi) | (psi) | (gpm) | (gpm) | (gpm) | (gpm) | (fps) | (decimal) | (gfd) | (gfd) | (psi) | (psi) | (gfd/psi) | pHI | pHC | TDSp | TDSI | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) |  |  | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 13 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 13 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.8 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.8 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 | [6 empty] | System influent flow rate during sample collection (gpm) | 12.9 | [8 empty] | Stage 1 influent flow rate during sample collection (gpm) | 12.9 |  |  |  |  | Capital Recovery Period (years) | 20 | System | Stage 1 | Stage 2
|  | Molecular weight cutoff (Daltons) | 200 | Calculate System Permeate, Feed and Waste Flow Rates |  | Dissolved iron (mg/L) | 0 |  |  |  | 1999-01-25 | 11:15 | 5036.25 | 22.2 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.9349 | 7.0617 | 45.3383 | 0.37352 | 7.5 | 6.2 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.6 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 17.6891 | 5.3304 | 51.0696 | 0.34637 | 6.2 | 6.4 | 20.52 | 416 | 621 | 691.1165 | -11.2909 | 90.843 | 553.5583 | 96.2931 | 59 | 51 | 4.6 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.4265 | 6.9702 | 43.4298 | 0.35521 | 6.4 | 6.5 | 48.6 | 621 | 864 | 870.2308 | -0.72115 | 78.3123 | 745.6154 | 93.4819 | [108 empty] | Overhead & Profit Factor (% of construction costs) | 15 | 12 | 4 | 8
Official ICR Contact Person |  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | Design system recovery, R (decimal) | 0.75 | Total iron (mg/L) | 0 |  |  |  | 1999-01-26 | 9:30 | 5058.5 | 20.7 | 63 | 51 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.7027 | 7.0617 | 45.4383 | 0.3896 | 7.5 | 6.3 | 32.4 | 179.8 | 224.0905 | 828 | 1033.4503 | -24.8128 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.5 | 5.3778 | 7.5222 | 9.4 | 12.9 | 0.30962 | 0.5721 | 16.547 | 18.7897 | 4.9304 | 51.5696 | 0.36436 | 6.3 | 6.4 | 20.79 | 384 | 586.5 | 643.6656 | -9.7469 | 90.7225 | 513.8328 | 95.9539 | 59 | 51 | 4.5 | 2.2222 | 5.3 | 4.0222 | 7.5222 | 0.38879 | 0.55249 | 13.6752 | 15.5287 | 6.5067 | 43.9933 | 0.35298 | 6.4 | 6.7 | 48.6 | 586.5 | 828 | 812.0346 | 1.9282 | 78.3123 | 699.2673 | 93.0499 | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | System Permeate, Feed and Concentrate-Waste Water Quality Parameters | [9 empty] | Stage 1 Permeate and Influent Water Quality Parameters | [7 empty] | Special Sitework Factor (% of construction costs) | 8 | 12 | 4 | 8
Mailing Address |  | Membrane construction (e.g., thin-film composite) | thin film composite | Design average system flux, FW (gfd) | 13.1 | Dissolved aluminum (mg/L) | 0 |  |  |  | 1999-01-27 | 11:15 | 5084.25 | 23 | 63 | 51 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.5392 | 7.0617 | 45.4383 | 0.36399 | 7.6 | 6.3 | 32.4 | 179.8 | 224.0905 | 828 | 1033.4503 | -24.8128 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.5 | 5.2923 | 7.6077 | 9.4 | 12.9 | 0.31092 | 0.56301 | 16.284 | 17.2757 | 4.8954 | 51.6046 | 0.33477 | 6.3 | 6.4 | 20.79 | 384 | 586.5 | 636.6678 | -8.5538 | 90.7225 | 510.3339 | 95.9262 | 59 | 51 | 4.5 | 2.3077 | 5.3 | 4.1077 | 7.6077 | 0.39139 | 0.5618 | 14.2012 | 15.066 | 6.55 | 43.95 | 0.3428 | 6.4 | 6.6 | 48.6 | 586.5 | 828 | 820.709 | 0.88056 | 78.3123 | 703.6045 | 93.0927 | Parameter | Units | Cp-sys-32 | CF-sys-32 | CC-sys-32 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-32 | CI-s1-32 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-34 | CF-sys-34 | CC-sys-34 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-34 | CI-s1-34 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-36 | CF-sys-36 | CC-sys-36 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-36 | CI-s1-36 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-38 | CF-sys-38 | CC-sys-38 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-38 | CI-s1-38 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 | CF-sys-40 | CC-sys-40 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 | CI-s1-40 | CC(calc) | RF (%) | CB | RB (%) | Parameter | Units | Cp-sys-40 (dup) | CF-sys-40 (dup) | CC-sys-40 (dup) | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-s1-40 (dup) | CI-s1-40 (dup) | CC(calc) | RF (%) | CB | RB (%) | Construction Contingencies (% of construction costs) | 25 | 12 | 4 | 8
|  | Membrane hydrophobicity | hydrophilic | Number of elements per pressure vessel, Ne | 3 | Total aluminum (mg/L) | 0 |  |  |  | 1999-01-28 | 10:00 | 5107 | 23.1 | 63 | 51 | 4.5 | 3.5 | 7.6 | 1.6 |  | 9.2 | 12.7 | 0.82609 | 0.38043 | 15.5897 | 16.4903 | 7.763 | 44.737 | 0.36861 | 7.6 | 6.2 | 32.4 | 179.8 | 225.0533 | 828 | 1140.1564 | -37.7001 | 85.6034 | 808.7018 | 95.9936 | 63 | 59 | 4.5 | 5.3778 | 7.3222 | 9.2 | 12.7 | 0.30356 | 0.58454 | 16.547 | 17.5029 | 4.9733 | 51.5267 | 0.33969 | 6.2 | 6.4 | 20.25 | 384 | 586.5 | 651.1548 | -11.0238 | 91.0021 | 517.5774 | 96.0875 | 59 | 51 | 4.5 | 2.2222 | 5.1 | 3.8222 | 7.3222 | 0.37667 | 0.5814 | 13.6752 | 14.4652 | 6.5509 | 43.9491 | 0.32914 | 6.4 | 6.5 | 48.6 | 586.5 | 828 | 820.8791 | 0.86001 | 78.4051 | 703.6895 | 93.0935 | Sampling date | MM/DD/YY | 1999-02-09 | 1999-02-09 | 1999-02-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-09 | 1999-02-09 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-09 | 1999-03-09 | 1999-03-09 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-09 | 1999-03-09 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-22 | 1999-03-22 | 1999-03-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-22 | 1999-03-22 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- | Engineering Fee Factor (% of construction costs) | 15 | 12 | 4 | 8
Phone Number |  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | negative | Number of parallel pressure vessels in stage 1, Nv-s(1) | 2 | Fluoride (mg/L) | 0.23 |  |  |  | 1999-01-29 | 8:00 | 5129 | 21.3 | 64 | 52 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.3915 | 6.9548 | 46.5452 | 0.37365 | 7.2 | 6.3 | 32.4 | 176.9 | 221.1906 | 864 | 1018.3062 | -17.8595 | 85.352 | 727.8842 | 95.5487 | 64 | 59 | 4.5 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 18.467 | 5.4527 | 51.5473 | 0.35825 | 6.3 | 6.6 | 20.79 | 422.4 | 621 | 709.722 | -14.287 | 90.6009 | 566.061 | 96.3273 | 59 | 52 | 4.5 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.2404 | 6.9228 | 44.0772 | 0.34577 | 6.6 | 6.7 | 48.6 | 621 | 864 | 860.76 | 0.375 | 78.028 | 740.88 | 93.4402 | Sampling time | hh:mm | 8:43 | 8:25 | 8:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 8:34 | 8:30 | --- | --- | --- | --- | Sampling time | hh:mm | 2:50 | 2:15 | 2:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 2:30 | 2:20 | --- | --- | --- | --- | Sampling time | hh:mm | 1:00 | 12:25 | 12:50 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:40 | 12:30 | --- | --- | --- | --- | Sampling time | hh:mm | 1:35 | 1:05 | 1:35 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 1:20 | 1:10 | --- | --- | --- | --- | Sampling time | hh:mm | 3:35 | 3:05 | 3:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 3:20 | 3:10 | --- | --- | --- | --- | Sampling time | hh:mm | 2:45 | 2:00 | 2:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 2:30 | 2:20 | --- | --- | --- | --- | 1998 ENR Construction Cost Index (CCI base year 1913) | 6007.75 | 12 | 5 | 7
FAX Number |  |  |  | Number of parallel pressure vessels in stage 2, Nv-s(2) | 1 | Phosphate (mg/L) | 0 |  |  |  | 1999-01-30 | 8:00 | 5153 | 22 | 62 | 50 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.0353 | 7.0617 | 44.4383 | 0.38335 | 7.6 | 6.2 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 62 | 58 | 4.5 | 5.4571 | 7.4429 | 9.4 | 12.9 | 0.30842 | 0.58055 | 16.7912 | 18.3482 | 4.53 | 50.97 | 0.35998 | 6.2 | 6.4 | 20.52 | 352 | 586.5 | 595.0429 | -1.4566 | 90.843 | 473.5215 | 95.6665 | 58 | 50 | 4.5 | 2.1429 | 5.3 | 3.9429 | 7.4429 | 0.38639 | 0.54348 | 13.1868 | 14.4096 | 6.4664 | 43.0336 | 0.33485 | 6.4 | 6.5 | 48.6 | 586.5 | 792 | 803.9798 | -1.5126 | 78.3123 | 695.2399 | 93.0096 | Operation time | hh.hh | 5331 | 5331 | 5331 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5331 | 5331 | --- | --- | --- | --- | Operation time | hh.hh | 5642 | 5642 | 5642 | --- | --- | --- | --- | --- | Operation time | hh.hh | 5642 | 5642 | --- | --- | --- | --- | Operation time | hh.hh | 6001 | 6001 | 6001 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6001 | 6001 | --- | --- | --- | --- | Operation time | hh.hh | 6262 | 6262 | 6262 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6262 | 6262 | --- | --- | --- | --- | Operation time | hh.hh | 6596 | 6596 | 6596 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6596 | 6596 | --- | --- | --- | --- | Operation time | hh.hh | 6596 | 6596 | 6596 | --- | --- | --- | --- | --- | Operation time | hh.hh | 6596 | 6596 | --- | --- | --- | --- | 1998 Producers Price Index (PPI base year 1967 = 100) | 124.4 | 12 | 4 | 8
E-Mail Address (optional) |  | Design Parameters |  | Permeate flow rate per element, Qp-e (gpm) | 0.70958 | Sulfate (mg/L) | 6.83 |  |  |  | 1999-01-31 | 12:00 | 5181 | 22.7 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.6865 | 7.2753 | 45.1247 | 0.36979 | 7.3 | 6.2 | 32.4 | 185.6 | 229.8903 | 864 | 1063.7384 | -23.1179 | 85.9063 | 759.9333 | 95.7365 | 63 | 59 | 4.6 | 4.8727 | 8.0273 | 9.4 | 12.9 | 0.31728 | 0.51838 | 14.993 | 16.0478 | 5.1586 | 51.2414 | 0.31318 | 6.7 | 6.3 | 20.25 | 416 | 621 | 656.2288 | -5.6729 | 91.1915 | 536.1144 | 96.2228 | 59 | 51 | 4.6 | 2.7273 | 5.3 | 4.5273 | 8.0273 | 0.40411 | 0.60241 | 16.7832 | 17.9639 | 7.1967 | 43.2033 | 0.4158 | 6.3 | 6.4 | 48.6 | 621 | 864 | 915.5455 | -5.9659 | 78.8595 | 768.2727 | 93.6741 | pH | --- | 5.85 | 6.31 | 6.84 | --- | --- | --- | --- | --- | pH | --- | 5.71 | 6.44 | --- | --- | --- | --- | pH | --- | 5.65 | 6.3 | 6.81 | --- | --- | --- | --- | --- | pH | --- | 5.55 | 6.53 | --- | --- | --- | --- | pH | --- | 5.96 | 6.05 | 6.72 | --- | --- | --- | --- | --- | pH | --- | 5.12 | 6.24 | --- | --- | --- | --- | pH | --- | 5.87 | 6.96 | 6.67 | --- | --- | --- | --- | --- | pH | --- | 5.77 | 6.43 | --- | --- | --- | --- | pH | --- | 5.44 | 5.91 | 6.54 | --- | --- | --- | --- | --- | pH | --- | 5.2 | 6.35 | --- | --- | --- | --- | pH | --- | 5.27 | 6.22 | 6.53 | --- | --- | --- | --- | --- | pH | --- | 5.37 | 6.16 | --- | --- | --- | --- | Labor Rate + Fringe ($/work-hour) | 15 | 12 | 4 | 8
|  | Element size (e.g., 2.5" x 40", 4" x 40", etc.) | 4-inch x 40-inch | Permeate flow rate per pressure vessel, Qp-v (gpm) | 2.1288 | Calcium (mg/L) | 55 |  |  |  | 1999-02-01 | 9:15 | 5202.25 | 22.3 | 63 | 51 | 4.6 | 3.4 | 7.6 | 1.7 |  | 9.3 | 12.7 | 0.8172 | 0.36559 | 15.5897 | 16.8849 | 7.5895 | 44.8105 | 0.37681 | 7.4 | 6.2 | 32.4 | 185.6 | 230.3666 | 864 | 1115.3936 | -29.0965 | 85.9355 | 791.3482 | 95.9057 | 63 | 59 | 4.6 | 5.38 | 7.32 | 9.3 | 12.7 | 0.30352 | 0.57849 | 16.5538 | 17.9291 | 5.4118 | 50.9882 | 0.35163 | 6.2 | 6.4 | 20.25 | 416 | 621 | 706.8654 | -13.827 | 91.2097 | 561.4327 | 96.3932 | 59 | 51 | 4.6 | 2.22 | 5.1 | 3.92 | 7.32 | 0.3766 | 0.56633 | 13.6615 | 14.7965 | 6.9698 | 43.4302 | 0.3407 | 6.4 | 6.5 | 48.6 | 621 | 864 | 870.1624 | -0.71324 | 78.9032 | 745.5812 | 93.4816 | Temperature | oC | 22.9 | 22.9 | 22.9 | --- | --- | --- | --- | --- | Temperature | oC | 22.9 | 22.9 | --- | --- | --- | --- | Temperature | oC | 19.3 | 19.3 | 19.3 | --- | --- | --- | --- | --- | Temperature | oC | 19.3 | 19.3 | --- | --- | --- | --- | Temperature | oC | 21.4 | 21.4 | 21.4 | --- | --- | --- | --- | --- | Temperature | oC | 21.4 | 21.4 | --- | --- | --- | --- | Temperature | oC | 22.3 | 22.3 | 22.3 | --- | --- | --- | --- | --- | Temperature | oC | 22.3 | 22.3 | --- | --- | --- | --- | Temperature | oC | 24.7 | 24.7 | 24.7 | --- | --- | --- | --- | --- | Temperature | oC | 24.7 | 24.7 | --- | --- | --- | --- | Temperature | oC | 24.7 | 24.7 | 24.7 | --- | --- | --- | --- | --- | Temperature | oC | 24.7 | 24.7 | --- | --- | --- | --- | Labor Overhead Factor (% of labor) | 32 | 12 | 4 | 8
Technical ICR Contact Person |  | Active membrane area of membrane element used, A (ft2) | 78 | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | Barium (mg/L) | 0 |  |  |  | 1999-02-02 | 9:15 | 5226.25 | 22.5 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.7854 | 7.0617 | 45.3383 | 0.37023 | 7.2 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.6 | 4.8727 | 8.0273 | 9.4 | 12.9 | 0.31728 | 0.51838 | 14.993 | 16.1429 | 4.738 | 51.662 | 0.31247 | 6.1 | 6.2 | 20.52 | 384 | 621 | 604.6402 | 2.6344 | 90.843 | 494.3201 | 95.8488 | 59 | 51 | 4.6 | 2.7273 | 5.3 | 4.5273 | 8.0273 | 0.40411 | 0.60241 | 16.7832 | 18.0704 | 7.1967 | 43.2033 | 0.41827 | 6.2 | 6.4 | 48.6 | 621 | 864 | 915.5455 | -5.9659 | 78.3123 | 768.2727 | 93.6741 | Alkalinity | mg/L as CaCO3 | 15 | 84 | 290 | 378.1579 | -30.3993 | 82.1429 | 270.9841 | 94.4646 | Alkalinity | mg/L as CaCO3 | 12 | 130 | 209.6883 | 85.7143 | 169.8442 | 92.9347 | Alkalinity | mg/L as CaCO3 | 32 | 84 | 280 | 305.6842 | -9.1729 | 61.9048 | 225.5368 | 85.8116 | Alkalinity | mg/L as CaCO3 | 24 | 130 | 204.8399 | 71.4286 | 167.4199 | 85.6648 | Alkalinity | mg/L as CaCO3 | 16 | 72 | 250 | 310.7368 | -24.2947 | 77.7778 | 224.0082 | 92.8574 | Alkalinity | mg/L as CaCO3 | 11 | 120 | 196.5319 | 84.7222 | 158.266 | 93.0497 | Alkalinity | mg/L as CaCO3 | 15 | 65 | 280 | 292.7778 | -4.5635 | 76.9231 | 210.0304 | 92.8582 | Alkalinity | mg/L as CaCO3 | BMRL | 130 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 14 | 56 | 220 | 247.3333 | -12.4242 | 75 | 178.3643 | 92.1509 | Alkalinity | mg/L as CaCO3 | 11 | 100 | 161.8673 | 80.3571 | 130.9336 | 91.5988 | Alkalinity | mg/L as CaCO3 | 13 | 57 | 200 | 257.4444 | -28.7222 | 77.193 | 185.1912 | 92.9802 | Alkalinity | mg/L as CaCO3 | 11 | 100 | 161.8673 | 80.7018 | 130.9336 | 91.5988 | Electric Rate ($/kW-h) | 0.065 | 12 | 4 | 8
Mailing Address |  | Design flux, FW (gfd) | 20.5 | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | Strontium (mg/L) | 0 |  |  |  | 1999-02-03 | 9:15 | 5250.25 | 22.5 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.7854 | 7.0617 | 45.3383 | 0.37023 | 7.3 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.6 | 4.8727 | 8.0273 | 9.4 | 12.9 | 0.31728 | 0.51838 | 14.993 | 16.1429 | 4.738 | 51.662 | 0.31247 | 6.1 | 6.2 | 20.52 | 384 | 621 | 604.6402 | 2.6344 | 90.843 | 494.3201 | 95.8488 | 59 | 51 | 4.6 | 2.7273 | 5.3 | 4.5273 | 8.0273 | 0.40411 | 0.60241 | 16.7832 | 18.0704 | 7.1967 | 43.2033 | 0.41827 | 6.2 | 6.3 | 48.6 | 621 | 864 | 915.5455 | -5.9659 | 78.3123 | 768.2727 | 93.6741 | Total dissolved solids | mg/L | 24 | 230 | 1000 | 1108.2105 | -10.8211 | 89.5652 | 788.2424 | 96.9553 | Total dissolved solids | mg/L | 12 | 360 | 595.013 | 94.7826 | 477.5065 | 97.4869 | Total dissolved solids | mg/L | 46 | 280 | 1300 | 1277.5789 | 1.7247 | 83.5714 | 916.9158 | 94.9832 | Total dissolved solids | mg/L | 26 | 500 | 834.6614 | 90.7143 | 667.3307 | 96.1039 | Total dissolved solids | mg/L | 36 | 270 | 1100 | 1267.5789 | -15.2344 | 86.6667 | 905.1772 | 96.0229 | Total dissolved solids | mg/L | 27 | 460 | 764.0213 | 90 | 612.0106 | 95.5883 | Total dissolved solids | mg/L | 40 | 230 | 1200 | 1095.5556 | 8.7037 | 82.6087 | 781.1155 | 94.8791 | Total dissolved solids | mg/L | 20 | 420 | 710.027 | 91.3043 | 565.0135 | 96.4603 | Total dissolved solids | mg/L | 35 | 230 | 1100 | 1118.3333 | -1.6667 | 84.7826 | 798.1202 | 95.6147 | Total dissolved solids | mg/L | 26 | 400 | 659.9816 | 88.6957 | 529.9908 | 95.0943 | Total dissolved solids | mg/L | 39 | 190 | 1100 | 877.8889 | 20.1919 | 79.4737 | 629.9289 | 93.8088 | Total dissolved solids | mg/L | 35 | 390 | 636.774 | 81.5789 | 513.387 | 93.1825 | Fuel Oil Rate ($/gal) | na | 12 | 4 | 8
|  | Net driving pressure at the design flux, NDP (psi) | 75 | Permeate flow rate from system, Qp-sys (gpm) | 6.3863 | Reactive silica (mg/L as SiO2) | 0 |  |  |  | 1999-02-04 | 9:15 | 5274.25 | 22.7 | 63 | 51 | 4.6 | 3.5 | 7.7 | 1.8 |  | 9.5 | 13 | 0.81053 | 0.36842 | 15.7949 | 16.906 | 7.1035 | 45.2965 | 0.37323 | 7.2 | 6.1 | 32.4 | 179.8 | 223.6243 | 864 | 1041.6392 | -20.5601 | 85.5114 | 742.7492 | 95.6378 | 63 | 59 | 4.6 | 4.9727 | 8.0273 | 9.5 | 13 | 0.31879 | 0.52344 | 15.3007 | 16.3771 | 4.7713 | 51.6287 | 0.31721 | 6.1 | 6.2 | 19.71 | 384 | 621 | 609.67 | 1.8245 | 91.1861 | 496.835 | 96.0329 | 59 | 51 | 4.6 | 2.7273 | 5.3 | 4.5273 | 8.0273 | 0.40411 | 0.60241 | 16.7832 | 17.9639 | 7.1967 | 43.2033 | 0.4158 | 6.2 | 6.3 | 48.6 | 621 | 864 | 915.5455 | -5.9659 | 78.2671 | 768.2727 | 93.6741 | Total hardness | mg/L as CaCO3 | 20 | 180 | 830 | 862.1053 | -3.8681 | 88.8889 | 613.5863 | 96.7405 | Total hardness | mg/L as CaCO3 | 11 | 340 | 562.1818 | 93.8889 | 451.0909 | 97.5615 | Total hardness | mg/L as CaCO3 | 20 | 180 | 820 | 862.1053 | -5.1348 | 88.8889 | 615.498 | 96.7506 | Total hardness | mg/L as CaCO3 | 11 | 340 | 572.2861 | 93.8889 | 456.143 | 97.5885 | Total hardness | mg/L as CaCO3 | 22 | 180 | 870 | 853.5789 | 1.8875 | 87.7778 | 608.8803 | 96.3868 | Total hardness | mg/L as CaCO3 | 12 | 360 | 604.3404 | 93.3333 | 482.1702 | 97.5113 | Total hardness | mg/L as CaCO3 | 20 | 180 | 850 | 908.8889 | -6.9281 | 88.8889 | 644.0972 | 96.8949 | Total hardness | mg/L as CaCO3 | 12 | 350 | 595.0728 | 93.3333 | 472.5364 | 97.4605 | Total hardness | mg/L as CaCO3 | 24 | 210 | 1000 | 1057.3333 | -5.7333 | 88.5714 | 751.8992 | 96.8081 | Total hardness | mg/L as CaCO3 | 16 | 420 | 700.8357 | 92.381 | 560.4179 | 97.145 | Total hardness | mg/L as CaCO3 | 25 | 210 | 1000 | 1052.7778 | -5.2778 | 88.0952 | 748.9858 | 96.6622 | Total hardness | mg/L as CaCO3 | 17 | 400 | 666.2378 | 91.9048 | 533.1189 | 96.8112 | Natural Gas Rate ($/ft3) | na | 12 | 4 | 8
Phone Number |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.27 | Feed flow rate to system, QF-sys (gpm) | 8.515 | Turbidity (ntu) | < 0.10 |  |  |  | 1999-02-05 | 10:00 | 5299 | 22.7 | 63 | 50 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.6865 | 7.0617 | 44.8383 | 0.37215 | 7.1 | 6.1 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 63 | 58 | 4.6 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 17.7184 | 6.072 | 49.828 | 0.35559 | 6.1 | 6.2 | 19.98 | 467.2 | 655.5 | 787.1526 | -20.0843 | 91.084 | 627.1763 | 96.8143 | 58 | 50 | 4.6 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 14.6226 | 7.3401 | 42.0599 | 0.34766 | 6.2 | 6.3 | 48.6 | 655.5 | 792 | 909.7109 | -14.8625 | 78.3123 | 782.6055 | 93.79 | Calcium hardness | mg/L as CaCO3 | 18 | 160 | 720 | 765.3684 | -6.3012 | 88.75 | 544.8078 | 96.6961 | Calcium hardness | mg/L as CaCO3 | 11 | 290 | 478.4156 | 93.125 | 384.2078 | 97.137 | Calcium hardness | mg/L as CaCO3 | 17 | 160 | 710 | 769.6316 | -8.3988 | 89.375 | 549.2263 | 96.9047 | Calcium hardness | mg/L as CaCO3 | 11 | 300 | 504.0446 | 93.125 | 402.0223 | 97.2638 | Calcium hardness | mg/L as CaCO3 | 19 | 160 | 760 | 761.1053 | -0.14543 | 88.125 | 542.735 | 96.4992 | Calcium hardness | mg/L as CaCO3 | 12 | 310 | 519.234 | 92.5 | 414.617 | 97.1058 | Calcium hardness | mg/L as CaCO3 | 18 | 150 | 740 | 751.3333 | -1.5315 | 88 | 532.8802 | 96.6221 | Calcium hardness | mg/L as CaCO3 | 12 | 300 | 508.8194 | 92 | 404.4097 | 97.0327 | Calcium hardness | mg/L as CaCO3 | 21 | 180 | 900 | 904.3333 | -0.48148 | 88.3333 | 643.2364 | 96.7353 | Calcium hardness | mg/L as CaCO3 | 14 | 370 | 617.4691 | 92.2222 | 493.7346 | 97.1645 | Calcium hardness | mg/L as CaCO3 | 22 | 180 | 900 | 899.7778 | 0.024691 | 87.7778 | 640.323 | 96.5642 | Calcium hardness | mg/L as CaCO3 | 15 | 350 | 582.8712 | 91.6667 | 466.4356 | 96.7841 | Current Process Water Rate ($/1000 gal) | 0.45 | 13 | 5 | 8
FAX Number |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | Concentrate-waste flow rate from system, QW-sys (gpm) | 2.1288 | SDI | na |  |  |  | 1999-02-06 | 7:45 | 5320.75 | 20 | 62 | 50 | 4.3 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 18.0728 | 7.0617 | 44.6383 | 0.40487 | 7.1 | 6.1 | 32.4 | 179.8 | 224.0905 | 720 | 1033.4503 | -43.5348 | 85.5416 | 738.5673 | 95.6131 | 62 | 57 | 4.3 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 19.1904 | 6.5064 | 48.6936 | 0.39411 | 6.1 | 6.2 | 19.98 | 499.2 | 648.6 | 842.0462 | -29.8252 | 91.084 | 670.6231 | 97.0207 | 57 | 50 | 4.3 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.8375 | 7.2566 | 41.9434 | 0.37759 | 6.2 | 6.3 | 48.6 | 648.6 | 720 | 899.9208 | -24.989 | 78.3123 | 774.2604 | 93.723 | Turbidity | ntu | 0.4 | 1.2 | 4.3 | 4.6105 | -7.2215 | 66.6667 | 3.3679 | 88.1233 | Turbidity | ntu | 0.22 | 3.1 | 5.0449 | 81.6667 | 4.0725 | 94.5979 | Turbidity | ntu | BMRL | BMRL | 0.11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.9 | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 4.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 2.7 | 4.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 4.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.28 | 1.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 1.1 | 1.3 | 1.439 | -292.8571 | 1.3695 | 19.6795 | Turbidity | ntu | BMRL | BMRL | 0.92 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.75 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Modifications to Existing Plant (% of construction costs) | na | 12 | 5 | 7
E-Mail Address (optional) |  | Maximum flow rate to the element, QI, max (gpm) | 10 |  |  | MFI | na |  |  |  | 1999-02-07 | 12:30 | 5349.5 | 23.9 | 62 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.105 | 6.848 | 45.252 | 0.3559 | 7.3 | 6.1 | 32.4 | 174 | 218.2906 | 828 | 1003.1622 | -21.1549 | 85.1574 | 717.2012 | 95.4824 | 62 | 58 | 4.4 | 5.2 | 7.7 | 9.4 | 12.9 | 0.31232 | 0.55319 | 16 | 16.5288 | 4.8657 | 50.7343 | 0.32579 | 6.1 | 6.2 | 20.25 | 384 | 600.3 | 629.6494 | -4.8891 | 90.7234 | 506.8247 | 96.0045 | 58 | 51 | 4.4 | 2.4 | 5.3 | 4.2 | 7.7 | 0.39419 | 0.57143 | 14.7692 | 15.2573 | 6.7661 | 43.3339 | 0.35209 | 6.2 | 6.3 | 48.6 | 600.3 | 828 | 850.1264 | -2.6723 | 77.7361 | 725.2132 | 93.2985 | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 3.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 4.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.13 | 0.28 | 0.98 | 0.96333 | 1.7007 | 53.5714 | 0.71702 | 81.8693 | Total organic carbon | mg/L | BMRL | 4.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.13 | 0.28 | 0.98 | 0.96333 | 1.7007 | 53.5714 | 0.71702 | 81.8693 | Total organic carbon | mg/L | BMRL | 4.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 11 | 4 | 7
|  | Minimum flow rate to the element, QI, min (gpm) | 4 | Calculate the Feed Flow Rates at the End of Each Stage |  | MPFI | na | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | 1999-02-08 | 9:15 | 5370.25 | 22.6 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.7359 | 7.0617 | 45.3383 | 0.36913 | 7.3 | 6.1 | 32.4 | 179.8 | 224.0905 | 828 | 1033.4503 | -24.8128 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.6 | 5.2 | 7.7 | 9.4 | 12.9 | 0.31232 | 0.55319 | 16 | 17.1763 | 4.873 | 51.527 | 0.33335 | 6.1 | 6.2 | 19.71 | 384 | 621 | 630.014 | -1.4515 | 91.2044 | 507.007 | 96.1125 | 59 | 51 | 4.6 | 2.4 | 5.3 | 4.2 | 7.7 | 0.39419 | 0.57143 | 14.7692 | 15.855 | 7.02 | 43.38 | 0.36549 | 6.2 | 6.3 | 48.6 | 621 | 828 | 880.2 | -6.3043 | 78.3123 | 750.6 | 93.5252 | Total organic carbon | mg/L | BMRL | 2.2 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.16 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.4 | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.1 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.2 | 10 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.4 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.18 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 2.2 | 11 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.17 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 12 | 4 | 8
Plant Name | Courtland Water Treatment Plant | Total width of all membrane envelopes in the element, w (ft) | 13.76 | Feed flow rate at the end of stage 1, (QF-s(1))end (gpm) | 5.6767 |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | 1999-02-09 | 10:30 | 5395.5 | 22.9 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.5881 | 6.7412 | 45.6588 | 0.36331 | 7.1 | 6.1 | 32.4 | 171.1 | 215.3907 | 828 | 988.0181 | -19.3259 | 84.9576 | 706.5182 | 95.4141 | 63 | 59 | 4.6 | 5.2 | 7.7 | 9.4 | 12.9 | 0.31232 | 0.55319 | 16 | 17.0246 | 4.8694 | 51.5306 | 0.33038 | 6.1 | 6.2 | 19.98 | 384 | 614.1 | 629.8317 | -2.5617 | 90.7238 | 506.9158 | 96.0585 | 59 | 51 | 4.6 | 2.4 | 5.3 | 4.2 | 7.7 | 0.39419 | 0.57143 | 14.7692 | 15.7151 | 6.9354 | 43.4646 | 0.36156 | 6.2 | 6.4 | 48.6 | 614.1 | 828 | 870.1755 | -5.0937 | 77.4364 | 742.1377 | 93.4514 | UV254 | cm-1 | BMRL | 0.086 | 0.41 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 4.1026 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.086 | 0.42 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.4694 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.086 | 0.41 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5417 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.084 | 0.43 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6957 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.083 | 0.42 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6735 | --- | --- | --- | --- | UV254 | cm-1 | BMRL | 0.082 | 0.43 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.617 | --- | --- | --- | --- |  |  | 12 | 4 | 8
Treatment Plant Category | DIS/GW, OTHER/GW | Feed spacer thickness, T (ft) | 0.00267 | Feed flow rate at the end of stage 2, (QF-s(2))end (gpm) | 2.8383 |  |  | is to list the pretreatment processes used in this particular pilot-scale run. |  |  | 1999-02-10 | 9:15 | 5418.25 | 22.1 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.9851 | 6.848 | 45.552 | 0.37287 | 7.3 | 6.1 | 32.4 | 174 | 218.2906 | 864 | 1003.1622 | -16.1067 | 85.1574 | 717.2012 | 95.4824 | 63 | 59 | 4.6 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.7337 | 4.9018 | 51.4982 | 0.34436 | 6.1 | 6.2 | 20.25 | 384 | 621 | 636.8564 | -2.5534 | 90.7234 | 510.4282 | 96.0327 | 59 | 51 | 4.6 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.4877 | 6.9714 | 43.4286 | 0.35662 | 6.2 | 6.4 | 48.6 | 621 | 864 | 870.48 | -0.75 | 77.7361 | 745.74 | 93.483 | SUVA | L/(mg*m) | NR | 3.9091 | 3.7273 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.5833 | 3.5 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 4.0952 | 3.7273 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.8182 | 4.3 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.4583 | 3.8182 | --- | --- | --- | --- | --- | [8 empty] | SUVA | L/(mg*m) | NR | 3.7273 | 3.9091 | --- | --- | --- | --- | --- | [10 empty] | 12 | 4 | 8
Process Train Name | Aeration,Disinfection,Corrosion Control | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | [7 empty] | 1999-02-11 | 8:45 | 5441.75 | 22 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.0353 | 6.848 | 45.752 | 0.37234 | 7.3 | 6.1 | 32.4 | 174 | 218.2906 | 849.6 | 1003.1622 | -18.0746 | 85.1574 | 717.2012 | 95.4824 | 63 | 58 | 4.4 | 5.2 | 7.7 | 9.4 | 12.9 | 0.31232 | 0.55319 | 16 | 17.4836 | 4.873 | 51.227 | 0.3413 | 6.1 | 6.2 | 19.71 | 384 | 621 | 630.014 | -1.4515 | 90.9708 | 507.007 | 96.1125 | 58 | 51 | 4.4 | 2.4 | 5.3 | 4.2 | 7.7 | 0.39419 | 0.57143 | 14.7692 | 16.1387 | 7.02 | 43.08 | 0.37462 | 6.2 | 6.3 | 48.6 | 621 | 849.6 | 880.2 | -3.6017 | 77.7361 | 750.6 | 93.5252 | Bromide | mg/L | BMRL | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 48 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 37 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 37 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | BMRL | 38 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 12 | 5 | 7
ICR Treatment Plant Identification Number | 1075 | Purchase price for an equivalent 8" x 40 " element ($) | 790 | Calculate the Minimum Recycle Flow Rates for Each Stage1 | [6 empty] | 1999-02-12 | 8:00 | 5465 | 21 | 64 | 52 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.5464 | 7.0617 | 46.4383 | 0.37784 | 7 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 64 | 59 | 4.5 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 18.6315 | 6.329 | 50.671 | 0.3677 | 6.1 | 6.3 | 20.25 | 486.4 | 621 | 819.8956 | -32.0283 | 90.9635 | 653.1478 | 96.8996 | 59 | 52 | 4.5 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.3762 | 6.9228 | 44.0772 | 0.34885 | 6.3 | 6.3 | 48.6 | 621 | 864 | 860.76 | 0.375 | 78.3123 | 740.88 | 93.4402 | SDS-Cl2 dose | mg/L | 6.3 | 8.8 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.4 | 7.3 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 3.8 | 4.4 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5 | 6.5 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.7 | 7.2 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [7 empty] | SDS-Cl2 dose | mg/L | 5.3 | 7.6 | --- | --- | --- | --- | --- | --- | Stage 2 Operating Parameters During Sample Collection | [9 empty] | 12 | 5 | 7
PWSID Number of Plant (if assigned) | N/A |  |  | Minimum recycle flow rate for stage 1, (QR-s(1))min (gpm) | 2.3233 | [5 empty] | 1999-02-13 | 8:00 | 5489 | 19.8 | 61 | 50 | 4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 18.1799 | 6.848 | 44.652 | 0.40715 | 7.2 | 6.2 | 32.4 | 174 | 218.2906 | 792 | 1003.1622 | -26.6619 | 85.1574 | 717.2012 | 95.4824 | 61 | 56 | 4 | 5.46 | 7.44 | 9.4 | 12.9 | 0.30837 | 0.58085 | 16.8 | 19.5913 | 6.2007 | 48.2993 | 0.40562 | 6.2 | 6.2 | 19.98 | 473.6 | 621 | 806.4985 | -29.8709 | 90.8471 | 640.0493 | 96.8784 | 56 | 50 | 4 | 2.14 | 5.3 | 3.94 | 7.44 | 0.3863 | 0.54315 | 13.1692 | 15.3573 | 6.8796 | 42.1204 | 0.3646 | 6.2 | 6.3 | 48.6 | 621 | 792 | 852.12 | -7.5909 | 77.7361 | 736.56 | 93.4018 | SDS-Free Cl2 residual | mg/L | 1.7 | 0.8 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | 1.2 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.55 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 0.75 | 0.68 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.54 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.2 | 0.77 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.57 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.3 | 1.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.58 |  |  |  |  | SDS-Free Cl2 residual | mg/L | 1.4 | 1.4 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 recovery during sample collection (decimal) | 0.58 | [6 empty] | 11 | 5 | 6
Historical Minimum Water Temperature (oC) | 17.8 | Additional Information |  | Minimum recycle flow rate for stage 2, (QR-s(2))min (gpm) | 1.1617 | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  |  | 1999-02-14 | 12:15 | 5517.25 | 21.6 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.2379 | 7.1685 | 45.4315 | 0.37943 | 7.3 | 6.1 | 32.4 | 182.7 | 226.9904 | 864 | 1048.5944 | -21.3651 | 85.7263 | 749.2503 | 95.6757 | 63 | 59 | 4.4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.9978 | 4.9018 | 51.6982 | 0.34813 | 6.1 | 6.4 | 20.25 | 384 | 621 | 636.8564 | -2.5534 | 91.0789 | 510.4282 | 96.0327 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.7183 | 6.9714 | 43.6286 | 0.36027 | 6.4 | 6.4 | 48.6 | 621 | 864 | 870.48 | -0.75 | 78.5894 | 745.74 | 93.483 | SDS-Cl2 demand | mg/L | 4.6 | 8 | --- | 22.4947 | --- | 42.5 | 17.2137 | 73.2771 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 4 | 6.1 | --- | 15.0526 | --- | 34.4262 | 11.8159 | 66.1473 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.2 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.05 | 3.72 | --- | 6.5763 | --- | 18.0108 | 5.5387 | 44.9326 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.8 | 5.73 | --- | 14.5222 | --- | 33.6824 | 11.3282 | 66.4553 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.22 |  |  |  |  | SDS-Cl2 demand | mg/L | 4.4 | 5.8 | --- | 12.1778 | --- | 24.1379 | 9.8788 | 55.4602 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 |  |  |  |  | SDS-Cl2 demand | mg/L | 3.9 | 6.2 | --- | 16.6778 | --- | 37.0968 | 12.9009 | 69.7696 |  |  | Stage 2 permeate flow rate during sample collection (gpm) | 2.31 | [6 empty] | 12 | 4 | 8
Historical Average Water Temperature (oC) | 23.5 | Design cross-flow velocity (fps) | 1 | 1: A negative minimum recycle flow rate indicates that recycle is not required to |  | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  |  | 1999-02-15 | 10:00 | 5539 | 21.3 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.3915 | 7.0617 | 45.5383 | 0.38191 | 7.4 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.4 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 18.467 | 5.0219 | 51.5781 | 0.35804 | 6.1 | 6.3 | 20.52 | 390.4 | 621 | 655.0216 | -5.4785 | 90.843 | 522.7108 | 96.0743 | 59 | 51 | 4.4 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.2404 | 6.9228 | 43.6772 | 0.34893 | 6.3 | 6.4 | 48.6 | 621 | 864 | 860.76 | 0.375 | 78.3123 | 740.88 | 93.4402 | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.52 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.62 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.52 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.42 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.61 |  |  |  |  | SDS-Chlorination temp. | oC | 20 | 20 | --- | --- | --- | --- | --- | --- |  |  | Stage 2 influent flow rate during sample collection (gpm) | 7.61 | [6 empty] | 12 | 4 | 8
State Approved Plant Capacity (MGD) | N/A | Required influent flow to permeate flow rate ratio, QI:Qp | 4:1 | meet the manufacturer's minimum flow requirement. | [6 empty] | 1999-02-16 | 9:15 | 5562.25 | 21.6 | 63 | 51 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.2379 | 7.0617 | 45.4383 | 0.37937 | 7.2 | 6.1 | 32.4 | 179.8 | 224.0905 | 828 | 1033.4503 | -24.8128 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.5 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.9978 | 4.8981 | 51.6019 | 0.34878 | 6.1 | 6.2 | 20.52 | 384 | 621 | 636.6688 | -2.5231 | 90.843 | 510.3344 | 95.9791 | 59 | 51 | 4.5 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.7183 | 6.9714 | 43.5286 | 0.3611 | 6.2 | 6.3 | 48.6 | 621 | 828 | 870.48 | -5.1304 | 78.3123 | 745.74 | 93.483 | SDS-Chlorination pH | --- | 8.14 | 7.99 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.03 | 8.06 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.18 | 8.16 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.14 | 8.02 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 8.15 | 7.96 | --- | --- | --- | --- | --- | --- | [8 empty] | SDS-Chlorination pH | --- | 7.83 | 8.04 | --- | --- | --- | --- | --- | --- | [10 empty] | 12 | 4 | 8
|  | Maximum element recovery (%) | 10 | [7 empty] | 1999-02-17 | 9:00 | 5586 | 21.5 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.289 | 7.0617 | 45.5383 | 0.37966 | 7.3 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 18.0511 | 4.9054 | 51.6946 | 0.34919 | 6.1 | 6.2 | 19.98 | 384 | 621 | 637.0441 | -2.5836 | 91.084 | 510.5221 | 96.0864 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.7648 | 6.9714 | 43.6286 | 0.36134 | 6.2 | 6.2 | 48.6 | 621 | 864 | 870.48 | -0.75 | 78.3123 | 745.74 | 93.483 | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [7 empty] | SDS-Incubation time | hours | 48 | 48 | --- | --- | --- | --- | --- | --- | Stage 2 Permeate and Influent Water Quality Parameters | [9 empty] | 12 | 4 | 8
|  | Variability of design flux (%) | 15 | Calculate the Maximum Recycle Flow Rates for Each Stage | [6 empty] | 1999-02-18 | 8:45 | 5609.75 | 22.4 | 64 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.8351 | 6.848 | 46.252 | 0.36399 | 7.3 | 6.2 | 32.4 | 174 | 218.2906 | 864 | 1003.1622 | -16.1067 | 85.1574 | 717.2012 | 95.4824 | 64 | 59 | 4.4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.5772 | 4.9054 | 52.1946 | 0.33676 | 6.2 | 6.2 | 19.98 | 384 | 621 | 637.0441 | -2.5836 | 90.8471 | 510.5221 | 96.0864 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.351 | 6.9714 | 43.6286 | 0.35186 | 6.2 | 6.3 | 48.6 | 621 | 864 | 870.48 | -0.75 | 77.7361 | 745.74 | 93.483 | SDS-TOX | mg Cl- /L | 40 | 374 | --- | 1797.8947 | --- | 89.3048 | 1279.1114 | 96.8728 | Parameter | Units | Cp-s2-32 | CI-s2-32 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 28 | 384 | --- | 1901.6842 | --- | 92.7083 | 1352.983 | 97.9305 | Parameter | Units | Cp-s2-34 | CI-s2-34 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 26 | 138 | --- | 615.4737 | --- | 81.1594 | 442.0164 | 94.1179 | Parameter | Units | Cp-s2-36 | CI-s2-36 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 30 | 282 | --- | 1430 | --- | 89.3617 | 1012.9531 | 97.0384 | Parameter | Units | Cp-s2-38 | CI-s2-38 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 57 | 367 | --- | 1779.2222 | --- | 84.4687 | 1270.1654 | 95.5124 | Parameter | Units | Cp-s2-40 | CI-s2-40 | CC(calc) | RF (%) | CB | RB (%) | SDS-TOX | mg Cl- /L | 51 | 381 | --- | 1884.3333 | --- | 86.6142 | 1342.4341 | 96.2009 | Parameter | Units | Cp-s2-40 (dup) | CI-s2-40 (dup) | CC(calc) | RF (%) | CB | RB (%) |  |  | 13 | 5 | 8
|  | Rejection of reference solute and conditions of test | 500 mg/L NaCl | Maximum recycle flow rate for stage 1, (QR-s(1))max (gpm) | 11.485 | [5 empty] | 1999-02-19 | 8:10 | 5633.1667 | 20.7 | 64 | 51 | 4.3 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.7027 | 6.848 | 46.352 | 0.38192 | 7.3 | 6.1 | 32.4 | 174 | 218.2906 | 864 | 1003.1622 | -16.1067 | 85.1574 | 717.2012 | 95.4824 | 64 | 59 | 4.3 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 18.7975 | 6.4122 | 50.7878 | 0.37012 | 6.1 | 6.2 | 20.52 | 492.8 | 621 | 830.6812 | -33.7651 | 90.5997 | 661.7406 | 96.8991 | 59 | 51 | 4.3 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.5131 | 6.9228 | 43.7772 | 0.35437 | 6.2 | 6.3 | 48.6 | 621 | 864 | 860.76 | 0.375 | 77.7361 | 740.88 | 93.4402 | SDS-CHCl3 | mg/L | 4.2 | 48 | --- | 234.7263 | --- | 91.25 | 166.6942 | 97.4804 | Sampling date | MM/DD/YY | 1999-02-09 | 1999-02-09 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.2 | 64 | --- | 323.2 | --- | 95 | 229.4892 | 98.6056 | Sampling date | MM/DD/YY | 1999-02-22 | 1999-02-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.5 | 35 | --- | 169.2895 | --- | 90 | 120.5046 | 97.0955 | Sampling date | MM/DD/YY | 1999-03-09 | 1999-03-09 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.7 | 43 | --- | 222.0333 | --- | 91.3953 | 156.9939 | 97.6432 | Sampling date | MM/DD/YY | 1999-03-22 | 1999-03-22 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3.2 | 53 | --- | 279.8667 | --- | 93.9623 | 198.0891 | 98.3846 | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- | SDS-CHCl3 | mg/L | 3 | 64 | --- | 341.8889 | --- | 95.3125 | 241.7196 | 98.7589 | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- |  |  | 13 | 5 | 8
|  | (e.g., solute type and concentration) |  | Maximum recycle flow rate for stage 2, (QR-s(2))max (gpm) | 5.7425 | [5 empty] | 1999-02-20 | 8:00 | 5657 | 19.7 | 64 | 51 | 4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 18.2338 | 6.848 | 46.652 | 0.39085 | 7.2 | 6.2 | 32.4 | 174 | 218.2906 | 792 | 1003.1622 | -26.6619 | 85.1574 | 717.2012 | 95.4824 | 64 | 58 | 4 | 5.28 | 7.62 | 9.4 | 12.9 | 0.3111 | 0.5617 | 16.2462 | 19.0015 | 6.018 | 50.982 | 0.37271 | 6.2 | 6.2 | 20.25 | 467.2 | 621 | 776.8976 | -25.1043 | 90.7234 | 622.0488 | 96.7446 | 58 | 51 | 4 | 2.22 | 5.4 | 4.12 | 7.62 | 0.39479 | 0.53883 | 13.6615 | 15.9785 | 6.9006 | 43.5994 | 0.36649 | 6.2 | 6.3 | 48.6 | 621 | 792 | 856.32 | -8.1212 | 77.7361 | 738.66 | 93.4205 | SDS-BDCM | mg/L | 2.2 | 12 | --- | 53.7789 | --- | 81.6667 | 38.5572 | 94.2942 | Sampling time | hh:mm | 8:37 | 8:32 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.8 | 14 | --- | 66.0105 | --- | 87.1429 | 47.2067 | 96.187 | Sampling time | hh:mm | 2:35 | 2:25 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.8 | 7.7 | --- | 32.8526 | --- | 76.6234 | 23.7152 | 92.4099 | Sampling time | hh:mm | 12:45 | 12:35 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.7 | 11 | --- | 53.3667 | --- | 84.5455 | 37.9757 | 95.5234 | Sampling time | hh:mm | 1:30 | 1:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.9 | 14 | --- | 69.1222 | --- | 86.4286 | 49.2526 | 96.1423 | Sampling time | hh:mm | 3:25 | 3:15 | --- | --- | --- | --- | SDS-BDCM | mg/L | 1.9 | 14 | --- | 69.1222 | --- | 86.4286 | 49.2526 | 96.1423 | Sampling time | hh:mm | 2:35 | 2:22 | --- | --- | --- | --- |  |  | 13 | 6 | 7
|  | Variability of rejection of reference solute (%) | 15 | [7 empty] | 1999-02-21 | 12:00 | 5685 | 20.9 | 63 | 51 | 4.4 | 3.5 | 7.5 | 1.8 |  | 9.3 | 12.8 | 0.80645 | 0.37634 | 15.3846 | 17.3668 | 7.2317 | 45.3683 | 0.3828 | 7.3 | 6.2 | 32.4 | 185.6 | 230.3666 | 864 | 1055.2272 | -22.1328 | 85.9355 | 755.5708 | 95.7119 | 63 | 58 | 4.4 | 5.28 | 7.52 | 9.3 | 12.8 | 0.30807 | 0.56774 | 16.2462 | 18.3393 | 5.001 | 51.099 | 0.3589 | 6.2 | 6.4 | 20.25 | 390.4 | 621 | 650.2926 | -4.717 | 91.2097 | 520.3463 | 96.1084 | 58 | 51 | 4.4 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.4217 | 6.9228 | 43.1772 | 0.35717 | 6.4 | 6.5 | 48.6 | 621 | 864 | 860.76 | 0.375 | 78.9032 | 740.88 | 93.4402 | SDS-DBCM | mg/L | BMRL | 1.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5331 | 5331 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 2 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 5642 | 5642 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6001 | 6001 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1.6 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6262 | 6262 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6596 | 6596 | --- | --- | --- | --- | SDS-DBCM | mg/L | BMRL | 1.7 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Operation time | hh.hh | 6596 | 6596 | --- | --- | --- | --- |  |  | 12 | 5 | 7
|  | Standard testing recovery (%) | 10 | Select the Design System Recycle Flow Rate2 | [6 empty] | 1999-02-22 | 9:30 | 5706.5 | 19.3 | 64 | 52 | 4.6 | 3.6 | 7.6 | 1.8 |  | 9.4 | 13 | 0.80851 | 0.38298 | 15.5897 | 18.4506 | 7.0844 | 46.3156 | 0.39837 | 7.3 | 6.2 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 740.8356 | 95.6266 | 64 | 59 | 4.6 | 5.38 | 7.62 | 9.4 | 13 | 0.31262 | 0.57234 | 16.5538 | 19.5917 | 4.9717 | 51.9283 | 0.37728 | 6.2 | 6.4 | 22.95 | 390.4 | 621 | 649.8332 | -4.643 | 89.7586 | 520.1166 | 95.5875 | 59 | 52 | 4.6 | 2.2 | 5.42 | 4.02 | 7.62 | 0.3954 | 0.54726 | 13.5385 | 16.0229 | 6.8857 | 44.0143 | 0.36404 | 6.4 | 6.4 | 48.6 | 621 | 864 | 853.3395 | 1.2339 | 78.3123 | 737.1697 | 93.4072 | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.78 | 6.65 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.71 | 6.62 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 6.04 | 6.62 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.94 | 6.71 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.53 | 6.52 | --- | --- | --- | --- | SDS-CHBr3 | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | pH | --- | 5.45 | 6.31 | --- | --- | --- | --- |  |  | 12 | 5 | 7
|  | Standard testing pH | 7.5 | Minimum system recycle flow rate, (QR-sys)min (gpm) | 2.3233 | [5 empty] | 1999-02-23 | 8:45 | 5729.75 | 19.6 | 69 | 52 | 4.4 | 3.4 | 7.6 | 1.6 |  | 9.2 | 12.6 | 0.82609 | 0.36957 | 15.5897 | 18.2877 | 7.9696 | 48.1304 | 0.37996 | 7.2 | 6.1 | 32.4 | 185.6 | 230.8531 | 871.2 | 1173.5056 | -34.6999 | 85.9651 | 829.3626 | 96.0934 | 64 | 60 | 4.4 | 5.46 | 7.14 | 9.2 | 12.6 | 0.29928 | 0.59348 | 16.8 | 19.7074 | 5.6401 | 51.9599 | 0.37928 | 6.1 | 6.2 | 20.79 | 428.8 | 655.5 | 740.8076 | -13.0141 | 90.9943 | 584.8038 | 96.445 | 60 | 52 | 4.4 | 2.14 | 5 | 3.74 | 7.14 | 0.36811 | 0.57219 | 13.1692 | 15.4483 | 7.3678 | 44.2322 | 0.34925 | 6.2 | 6.3 | 48.6 | 655.5 | 871.2 | 915.2532 | -5.0566 | 78.9477 | 785.3766 | 93.8119 | SDS-THM4 | mg/L | 6.4 | 61.9 | --- | 298.5053 | --- | 89.6607 | 212.3002 | 96.9854 | Temperature | oC | 22.9 | 22.9 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5 | 80 | --- | 399.7368 | --- | 93.75 | 284.1397 | 98.2403 | Temperature | oC | 19.3 | 19.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.3 | 44 | --- | 208.9842 | --- | 87.9545 | 149.0485 | 96.4441 | Temperature | oC | 21.4 | 21.4 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.4 | 55.6 | --- | 284.2889 | --- | 90.2878 | 201.2105 | 97.3162 | Temperature | oC | 22.3 | 22.3 | --- | --- | --- | --- | SDS-THM4 | mg/L | 5.1 | 68.8 | --- | 358.9889 | --- | 92.5872 | 254.3859 | 97.9952 | Temperature | oC | 24.7 | 24.7 | --- | --- | --- | --- | SDS-THM4 | mg/L | 4.9 | 79.7 | --- | 420.4556 | --- | 93.8519 | 297.6251 | 98.3536 | Temperature | oC | 24.7 | 24.7 | --- | --- | --- | --- |  |  | 17 | 4 | 8
|  | Acceptable range of operating pressures | 0 - 350 psi | Maximum system recycle flow rate, (QR-sys)max (gpm) | 5.7425 | [5 empty] | 1999-02-24 | 9:00 | 5754 | 20 | 64 | 53 | 4.4 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 18.0728 | 7.6148 | 46.4852 | 0.38879 | 7.3 | 6.1 | 32.4 | 185.6 | 230.3666 | 864 | 1115.3936 | -29.0965 | 85.9355 | 793.8798 | 95.9188 | 64 | 60 | 4.4 | 5.46 | 7.34 | 9.3 | 12.8 | 0.30534 | 0.5871 | 16.8 | 19.4758 | 5.422 | 52.178 | 0.37326 | 6.1 | 6.2 | 20.79 | 416 | 655.5 | 709.9846 | -8.3119 | 90.9753 | 562.9923 | 96.3072 | 60 | 53 | 4.4 | 2.14 | 5.2 | 3.84 | 7.34 | 0.38024 | 0.55729 | 13.1692 | 15.2667 | 7.3178 | 44.7822 | 0.34091 | 6.2 | 6.3 | 48.6 | 655.5 | 864 | 905.2627 | -4.7758 | 78.9032 | 780.3813 | 93.7723 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 180 | 245.3434 | 71.4286 | 212.6717 | 88.715 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 22 | 220 | 300.369 | 73.8095 | 260.1845 | 91.5445 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 24 | 180 | 245.3434 | 66.6667 | 212.6717 | 88.715 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 35 | 200 | 270.4423 | 46.1538 | 235.2212 | 85.1204 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 18 | 140 | 193.1736 | 67.8571 | 166.5868 | 89.1948 | SDS-MCAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Alkalinity | mg/L as CaCO3 | 19 | 140 | 192.7377 | 66.6667 | 166.3689 | 88.5796 |  |  | 11 | 4 | 7
|  | Acceptable range of operating pH values | 4-11 | Design system recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1999-02-25 | 9:15 | 5778.25 | 20.5 | 64 | 52 | 4.6 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 17.8076 | 7.3917 | 46.0083 | 0.38705 | 7.3 | 6.1 | 32.4 | 179.8 | 224.5667 | 864 | 1083.6649 | -25.4242 | 85.5722 | 771.5707 | 95.8008 | 64 | 59 | 4.6 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 18.9089 | 5.0361 | 51.8639 | 0.36459 | 6.1 | 6.2 | 20.79 | 390.4 | 621 | 658.3922 | -6.0213 | 90.7422 | 524.3961 | 96.0354 | 59 | 52 | 4.6 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 15.6051 | 6.9459 | 43.9541 | 0.35503 | 6.2 | 6.3 | 48.6 | 621 | 864 | 865.3708 | -0.15865 | 78.3583 | 743.1854 | 93.4606 | SDS-DCAA* | mg/L | 3.2 | 19 | --- | 86.3579 | --- | 83.1579 | 61.8166 | 94.8234 | Total dissolved solids | mg/L | 48 | 560 | 774.4604 | 79.1304 | 667.2302 | 92.8061 | SDS-DCAA* | mg/L | 1.3 | 26 | --- | 131.3 | --- | 95 | 93.23 | 98.6056 | Total dissolved solids | mg/L | 82 | 740 | 1007.0849 | 70.7143 | 873.5424 | 90.6129 | SDS-DCAA* | mg/L | 1.9 | 8.1 | --- | 34.5316 | --- | 76.5432 | 24.9295 | 92.3785 | Total dissolved solids | mg/L | 61 | 690 | 953.4679 | 77.4074 | 821.734 | 92.5767 | SDS-DCAA* | mg/L | 1.8 | 34 | --- | 180.6889 | --- | 94.7059 | 127.3996 | 98.5871 | Total dissolved solids | mg/L | 44 | 680 | 951.5231 | 80.8696 | 815.7615 | 94.6063 | SDS-DCAA* | mg/L | 1.7 | 24 | --- | 125.5889 | --- | 92.9167 | 88.9696 | 98.0892 | Total dissolved solids | mg/L | 47 | 620 | 869.7415 | 79.5652 | 744.8708 | 93.6902 | SDS-DCAA* | mg/L | 1.8 | 25 | --- | 130.6889 | --- | 92.8 | 92.5917 | 98.056 | Total dissolved solids | mg/L | 63 | 680 | 948.9189 | 66.8421 | 814.4594 | 92.2648 |  |  | 12 | 5 | 7
|  | Typical pressure drop across a single element (psi) | 3 | System influent flow rate, QI-sys (gpm) | 13.515 | [5 empty] | 1999-02-26 | 8:00 | 5801 | 20 | 64 | 52 | 4.6 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 18.0728 | 7.3917 | 46.0083 | 0.39282 | 7.2 | 6.1 | 32.4 | 179.8 | 224.5667 | 864 | 1083.6649 | -25.4242 | 85.5722 | 771.5707 | 95.8008 | 64 | 59 | 4.6 | 5.29 | 7.51 | 9.3 | 12.8 | 0.30792 | 0.56882 | 16.2769 | 18.8694 | 4.9979 | 51.9021 | 0.36356 | 6.1 | 6.2 | 20.79 | 390.4 | 690 | 650.7511 | 5.6882 | 90.7422 | 520.5756 | 96.0063 | 59 | 52 | 4.6 | 2.31 | 5.2 | 4.01 | 7.51 | 0.38539 | 0.57606 | 14.2154 | 16.4795 | 7.8386 | 43.0614 | 0.3827 | 6.2 | 6.3 | 48.6 | 690 | 864 | 974.9296 | -12.8391 | 78.3583 | 832.4648 | 94.1619 | SDS-TCAA* | mg/L | 2.4 | 19 | --- | 89.7684 | --- | 87.3684 | 63.9846 | 96.2491 | Total hardness | mg/L as CaCO3 | 35 | 460 | 638.0189 | 80.5556 | 549.0094 | 93.6249 | SDS-TCAA* | mg/L | 1.3 | 34 | --- | 173.4053 | --- | 96.1765 | 123.0049 | 98.9431 | Total hardness | mg/L as CaCO3 | 34 | 500 | 689.1513 | 81.1111 | 594.5756 | 94.2816 | SDS-TCAA* | mg/L | 1.5 | 5.2 | --- | 20.9737 | --- | 71.1538 | 15.2434 | 90.1597 | Total hardness | mg/L as CaCO3 | 38 | 490 | 679.3283 | 78.8889 | 584.6642 | 93.5005 | SDS-TCAA* | mg/L | 1.3 | 45 | --- | 244.0778 | --- | 97.1111 | 171.7566 | 99.2431 | Total hardness | mg/L as CaCO3 | 37 | 500 | 697.6654 | 79.4444 | 598.8327 | 93.8213 | SDS-TCAA* | mg/L | 1.3 | 26 | --- | 138.5222 | --- | 95 | 97.9619 | 98.673 | Total hardness | mg/L as CaCO3 | 44 | 600 | 842.3321 | 79.0476 | 721.166 | 93.8988 | SDS-TCAA* | mg/L | 1.4 | 24 | --- | 126.9556 | --- | 94.1667 | 89.8437 | 98.4417 | Total hardness | mg/L as CaCO3 | 44 | 660 | 928.483 | 79.0476 | 794.2415 | 94.4601 |  |  | 12 | 5 | 7
|  | Maximum permissible SDI | 5 | Recycle ratio, r | 0.5872 | [5 empty] | 1999-02-27 | 8:45 | 5825.75 | 19.5 | 64 | 51 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 18.3419 | 7.0617 | 45.9383 | 0.39927 | 7.2 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 64 | 59 | 4.5 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 19.4762 | 5.0175 | 51.9825 | 0.37467 | 6.1 | 6.2 | 20.8465 | 390.4 | 621 | 654.788 | -5.4409 | 90.6973 | 522.594 | 96.011 | 59 | 51 | 4.5 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 16.0733 | 6.9228 | 43.5772 | 0.36885 | 6.2 | 6.3 | 48.6 | 621 | 864 | 860.76 | 0.375 | 78.3123 | 740.88 | 93.4402 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 400 | 554.9811 | 81.25 | 477.4906 | 93.7172 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 30 | 430 | 592.3616 | 81.25 | 511.1808 | 94.1312 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 33 | 420 | 582.1019 | 79.375 | 501.0509 | 93.4138 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 32 | 440 | 614.1846 | 78.6667 | 527.0923 | 93.929 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 38 | 530 | 744.4377 | 78.8889 | 637.2189 | 94.0366 | SDS-MBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 38 | 570 | 801.8717 | 78.8889 | 685.9358 | 94.4601 |  |  | 13 | 5 | 8
|  | Maximum permissible turbidity (ntu) | 0 | 2: The design system recycle flow rate must fall between the minimum and | [6 empty] | 1999-02-28 | 11:45 | 5852.75 | 23.9 | 63 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.105 | 7.0617 | 45.3383 | 0.35522 | 7.4 | 6.1 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 63 | 58 | 4.6 | 5.2 | 7.7 | 9.4 | 12.9 | 0.31232 | 0.55319 | 16 | 16.5288 | 4.8621 | 51.0379 | 0.32385 | 6.1 | 6.3 | 20.52 | 384 | 586.5 | 629.467 | -7.326 | 90.843 | 506.7335 | 95.9505 | 58 | 51 | 4.6 | 2.4 | 5.3 | 4.2 | 7.7 | 0.39419 | 0.57143 | 14.7692 | 15.2573 | 6.5969 | 43.3031 | 0.35234 | 6.3 | 6.4 | 48.6 | 586.5 | 792 | 830.0774 | -4.8077 | 78.3123 | 708.2887 | 93.1384 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | 0.7 | 3.6 | 4.8147 | 41.6667 | 4.2074 | 83.3625 | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | BMRL | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 5.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 5 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 1.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | 2.1 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Turbidity | ntu | BMRL | 0.67 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 12 | 5 | 7
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 0 | maximum system recycle flow rates. | [6 empty] | 1999-03-01 | 10:30 | 5875.5 | 22.2 | 64 | 51 | 4.7 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.9349 | 7.0617 | 45.7383 | 0.37026 | 7.3 | 6.1 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 64 | 59 | 4.7 | 5.38 | 7.52 | 9.4 | 12.9 | 0.30959 | 0.57234 | 16.5538 | 17.9822 | 4.924 | 51.876 | 0.34664 | 6.1 | 6.2 | 21.33 | 384 | 586.5 | 643.4634 | -9.7124 | 90.4815 | 513.7317 | 95.848 | 59 | 51 | 4.7 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 14.8403 | 6.5055 | 43.7945 | 0.33886 | 6.2 | 6.4 | 48.6 | 586.5 | 792 | 811.8091 | -2.5011 | 78.3123 | 699.1545 | 93.0487 | SDS-BCAA* | mg/L | 1.5 | 3.8 | --- | 13.6053 | --- | 60.5263 | 10.0328 | 85.049 | Total organic carbon | mg/L | BMRL | 5.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 3.5 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | 1.2 | 2.5 | --- | 8.0421 | --- | 52 | 6.0288 | 80.0954 | Total organic carbon | mg/L | BMRL | 6.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 5.3 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 4.9 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | 4.8 | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 7.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 13 | 5 | 8
|  | 1: All of the information requested in this field may not be available, but values for all of the Design | [8 empty] | 1999-03-02 | 9:30 | 5898.5 | 21.6 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.2379 | 7.0617 | 45.5383 | 0.37854 | 7.4 | 6.1 | 32.4 | 179.8 | 224.0905 | 864 | 1033.4503 | -19.6123 | 85.5416 | 738.5673 | 95.6131 | 63 | 58 | 4.4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.9978 | 4.8545 | 51.2455 | 0.35121 | 6.1 | 6.2 | 23.76 | 384 | 621 | 634.4165 | -2.1605 | 89.3971 | 509.2083 | 95.3339 | 58 | 51 | 4.4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.7183 | 6.9714 | 43.1286 | 0.36445 | 6.2 | 6.4 | 48.6 | 621 | 864 | 870.48 | -0.75 | 78.3123 | 745.74 | 93.483 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.011 | 0.23 | 0.32173 | 87.2093 | 0.27587 | 96.0126 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.25 | 0.34661 | 86.0465 | 0.2983 | 95.9772 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.23 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.012 | 0.26 | 0.36588 | 85.7143 | 0.31294 | 96.1654 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | 0.009 | 0.25 | 0.35504 | 89.1566 | 0.30252 | 97.025 | SDS-TBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.28 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  |  | 12 | 5 | 7
|  | Parameters must be entered in cells E15:E26, since these parameters are used in calculations. |  | Summary of the Stage and System Flow Rates | [6 empty] | 1999-03-03 | 8:35 | 5921.5833 | 21 | 64 | 51 | 4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.5464 | 6.848 | 46.652 | 0.37611 | 7.1 | 6.3 | 32.4 | 174 | 218.2906 | 936 | 1003.1622 | -7.1754 | 85.1574 | 717.2012 | 95.4824 | 64 | 59 | 4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 18.3198 | 4.9127 | 52.5873 | 0.34837 | 6.3 | 6.3 | 19.44 | 384 | 655.5 | 637.4195 | 2.7583 | 91.0944 | 510.7098 | 96.1935 | 59 | 51 | 4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.9995 | 7.3916 | 43.6084 | 0.36689 | 6.3 | 6.5 | 48.6 | 655.5 | 936 | 920.0168 | 1.7076 | 77.7361 | 787.7584 | 93.8306 | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.9655 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.5714 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7097 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.8235 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.7313 | --- | --- | --- | --- | SDS-CDBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SUVA | L/(mg*m) | NR | 3.6364 | --- | --- | --- | --- |  |  | 13 | 5 | 8
|  |  |  | Influent flow rate to stage 1, QI-s(1) (gpm) | 13.515 | [5 empty] | 1999-03-04 | 8:45 | 5945.75 | 19.8 | 64 | 51 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 18.1799 | 7.0617 | 45.8383 | 0.39661 | 7.4 | 6.1 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 64 | 58 | 4.6 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 18.9813 | 4.9127 | 51.4873 | 0.36866 | 6.1 | 6.2 | 19.44 | 384 | 621 | 637.4195 | -2.644 | 91.3249 | 510.7098 | 96.1935 | 58 | 51 | 4.6 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 16.5772 | 6.9714 | 42.9286 | 0.38616 | 6.2 | 6.4 | 48.6 | 621 | 792 | 870.48 | -9.9091 | 78.3123 | 745.74 | 93.483 | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | NA | NA | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | [10 empty] | 13 | 6 | 7
|  |  |  | Permeate flow rate from stage 1, Qp-s(1) (gpm) | 4.2575 | [5 empty] | 1999-03-05 | 11:15 | 5972.25 | 22.1 | 62 | 51 | 4.3 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.9851 | 6.848 | 45.352 | 0.37452 | 7.4 | 6.1 | 32.4 | 174 | 218.2906 | 720 | 1003.1622 | -39.3281 | 85.1574 | 717.2012 | 95.4824 | 62 | 57 | 4.3 | 5.46 | 7.44 | 9.4 | 12.9 | 0.30837 | 0.58085 | 16.8 | 18.3036 | 4.9907 | 50.2093 | 0.36455 | 6.1 | 6.2 | 18.9 | 384 | 621 | 651.9363 | -4.9817 | 91.3418 | 517.9681 | 96.3511 | 57 | 51 | 4.3 | 2.14 | 5.3 | 3.94 | 7.44 | 0.3863 | 0.54315 | 13.1692 | 14.3479 | 6.8796 | 42.8204 | 0.33507 | 6.2 | 6.4 | 48.6 | 621 | 720 | 852.12 | -18.35 | 77.7361 | 736.56 | 93.4018 | SDS-HAA5 | mg/L | 5.6 | 38 | --- | 176.1263 | --- | 85.2632 | 125.8012 | 95.5485 | [8 empty] | SDS-HAA5 | mg/L | 2.6 | 60 | --- | 304.7053 | --- | 95.6667 | 216.2349 | 98.7976 | [8 empty] | SDS-HAA5 | mg/L | 3.4 | 13.3 | --- | 55.5053 | --- | 74.4361 | 40.1729 | 91.5366 | [8 empty] | SDS-HAA5 | mg/L | 3.1 | 79 | --- | 424.7667 | --- | 96.0759 | 299.1561 | 98.9638 | [8 empty] | SDS-HAA5 | mg/L | 3 | 50 | --- | 264.1111 | --- | 94 | 186.9315 | 98.3951 | [8 empty] | SDS-HAA5 | mg/L | 3.2 | 51.1 | --- | 269.3111 | --- | 93.7378 | 190.6536 | 98.3216 | [10 empty] | 11 | 5 | 6
|  |  |  | Concentrate flow rate from stage 1, QC-s(1) (gpm) | 9.2575 | [5 empty] | 1999-03-06 | 9:15 | 5994.25 | 20.9 | 61 | 50 | 4.5 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.5983 | 7.0617 | 43.9383 | 0.40052 | 7.4 | 6.1 | 32.4 | 179.8 | 224.0905 | 720 | 1033.4503 | -43.5348 | 85.5416 | 738.5673 | 95.6131 | 61 | 57 | 4.5 | 5.46 | 7.44 | 9.4 | 12.9 | 0.30837 | 0.58085 | 16.8 | 18.9645 | 4.9685 | 49.5315 | 0.38288 | 6.1 | 6.2 | 20.52 | 384 | 621 | 650.7474 | -4.7902 | 90.843 | 517.3737 | 96.0338 | 57 | 50 | 4.5 | 2.14 | 5.3 | 3.94 | 7.44 | 0.3863 | 0.54315 | 13.1692 | 14.866 | 6.8796 | 42.1204 | 0.35294 | 6.2 | 6.4 | 48.6 | 621 | 720 | 852.12 | -18.35 | 78.3123 | 736.56 | 93.4018 | SDS-HAA6 | mg/L | 7.1 | 41.8 | --- | 189.7316 | --- | 83.0144 | 135.834 | 94.773 | [8 empty] | SDS-HAA6 | mg/L | 2.6 | 63.5 | --- | 323.1263 | --- | 95.9055 | 229.2614 | 98.8659 | [8 empty] | SDS-HAA6 | mg/L | 4.6 | 15.8 | --- | 63.5474 | --- | 70.8861 | 46.2016 | 90.0436 | [8 empty] | SDS-HAA6 | mg/L | 3.1 | 84.3 | --- | 454.2111 | --- | 96.3227 | 319.8293 | 99.0307 | [8 empty] | SDS-HAA6 | mg/L | 3 | 54.9 | --- | 291.3333 | --- | 94.5355 | 206.1074 | 98.5444 | [8 empty] | SDS-HAA6 | mg/L | 3.2 | 55.9 | --- | 295.9778 | --- | 94.2755 | 209.4381 | 98.4721 | [10 empty] | 11 | 4 | 7
|  |  |  | Influent flow rate to stage 2, QI-s(2) (gpm) | 9.2575 | [5 empty] | 1999-03-07 | 11:45 | 6020.75 | 23.6 | 63 | 52 | 4.6 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.2484 | 7.0617 | 45.8383 | 0.35447 | 7.5 | 6.1 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.6 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 16.9646 | 4.8981 | 51.5019 | 0.3294 | 6.1 | 6.2 | 20.52 | 384 | 552 | 636.6688 | -15.3385 | 90.843 | 510.3344 | 95.9791 | 59 | 52 | 4.6 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 14.816 | 6.131 | 44.769 | 0.33094 | 6.2 | 6.3 | 48.6 | 552 | 792 | 771.4064 | 2.6002 | 78.3123 | 661.7032 | 92.6553 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [19 empty] | 11 | 4 | 7
|  |  |  | Permeate flow rate from stage 2, Qp-s(2) (gpm) | 2.1288 | [5 empty] | 1999-03-08 | 9:30 | 6042.5 | 22 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.0353 | 7.0617 | 45.5383 | 0.37409 | 7.5 | 6.1 | 32.4 | 179.8 | 224.0905 | 792 | 1033.4503 | -30.4861 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.7862 | 5.2381 | 51.3619 | 0.34629 | 6.1 | 6.2 | 20.79 | 409.5 | 586.5 | 679.7071 | -15.8921 | 90.7225 | 544.6035 | 96.1825 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.5335 | 6.5512 | 44.0488 | 0.35264 | 6.2 | 6.3 | 48.6 | 586.5 | 792 | 820.9432 | -3.6544 | 78.3123 | 703.7216 | 93.0939 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [19 empty] | 12 | 4 | 8
|  |  |  | Concentrate flow rate from stage 2, QC-s(2) (gpm) | 7.1288 | [5 empty] | 1999-03-09 | 8:45 | 6065.75 | 21.4 | 63 | 51 | 4.4 | 3.5 | 7.5 | 1.8 |  | 9.3 | 12.8 | 0.80645 | 0.37634 | 15.3846 | 17.112 | 7.0198 | 45.5802 | 0.37543 | 7.4 | 6.1 | 32.4 | 179.8 | 224.5667 | 810 | 1025.2613 | -26.5755 | 85.5722 | 734.384 | 95.5881 | 63 | 59 | 4.4 | 5.28 | 7.52 | 9.3 | 12.8 | 0.30807 | 0.56774 | 16.2462 | 18.0703 | 4.9072 | 51.6928 | 0.34957 | 6.1 | 6.3 | 20.79 | 384 | 603.75 | 639.0198 | -5.8418 | 90.7422 | 511.5099 | 95.9356 | 59 | 51 | 4.4 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 15.1955 | 6.7142 | 43.8858 | 0.34625 | 6.3 | 6.4 | 48.6 | 603.75 | 810 | 836.2845 | -3.245 | 78.3583 | 720.0173 | 93.2502 | [110 empty] | 12 | 4 | 8
|  |  |  | System concentrate recycle flow rate, QR-sys (gpm) | 5 | [5 empty] | 1999-03-10 | 10:00 | 6091 | 22.9 | 63 | 51 | 4.3 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 16.5881 | 7.0617 | 45.6383 | 0.36347 | 7.3 | 6.1 | 32.4 | 179.8 | 224.0905 | 810 | 1033.4503 | -27.5865 | 85.5416 | 738.5673 | 95.6131 | 63 | 59 | 4.3 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 17.3193 | 4.8872 | 51.8128 | 0.33427 | 6.1 | 6.2 | 21.33 | 384 | 603.75 | 636.1057 | -5.3591 | 90.4815 | 510.0528 | 95.8181 | 59 | 51 | 4.3 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.1257 | 6.7613 | 43.9387 | 0.34425 | 6.2 | 6.3 | 48.6 | 603.75 | 810 | 845.7116 | -4.4088 | 78.3123 | 724.7308 | 93.2941 | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [17 empty] | Blending Calculations For D-DBP MCLs | [19 empty] | 12 | 4 | 8
|  |  |  | System concentrate waste flow rate, QW-sys (gpm) | 2.1288 | [5 empty] | 1999-03-11 | 9:30 | 6114.5 | 21.5 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.8 |  | 9.4 | 12.9 | 0.80851 | 0.37234 | 15.5897 | 17.289 | 7.2753 | 45.3247 | 0.38145 | 7.6 | 6.1 | 32.4 | 185.6 | 229.8903 | 810 | 1063.7384 | -31.3257 | 85.9063 | 759.9333 | 95.7365 | 63 | 59 | 4.4 | 5.29 | 7.61 | 9.4 | 12.9 | 0.31095 | 0.56277 | 16.2769 | 18.0511 | 4.9844 | 51.6156 | 0.34972 | 6.1 | 6.3 | 20.52 | 390.4 | 621 | 647.5176 | -4.2702 | 91.074 | 518.9588 | 96.0459 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.11 | 7.61 | 0.39146 | 0.56204 | 14.2154 | 15.7648 | 6.9714 | 43.6286 | 0.36134 | 6.3 | 6.4 | 48.6 | 621 | 810 | 870.48 | -7.4667 | 78.8595 | 745.74 | 93.483 |  | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [13 empty] | THM4 Controls |  |  |  | HAA5 Controls | [14 empty] | 12 | 4 | 8
|  |  |  | System permeate flow rate, Qp-sys (gpm) | 6.3863 | [5 empty] | 1999-03-13 | 8:00 | 6161 | 20.9 | 61 | 50 | 4 | 3.5 | 7.5 | 1.8 |  | 9.3 | 12.8 | 0.80645 | 0.37634 | 15.3846 | 17.3668 | 6.808 | 44.692 | 0.38859 | 7.1 | 6 | 32.4 | 174 | 218.7669 | 792 | 995.2954 | -25.6686 | 85.1897 | 713.1972 | 95.4571 | 61 | 56 | 4 | 5.36 | 7.44 | 9.3 | 12.8 | 0.30686 | 0.57634 | 16.4923 | 18.6172 | 5.9888 | 48.5112 | 0.38377 | 6 | 6.1 | 20.52 | 460.8 | 603.75 | 777.991 | -28.8598 | 90.6202 | 619.3955 | 96.6871 | 56 | 50 | 4 | 2.14 | 5.3 | 3.94 | 7.44 | 0.3863 | 0.54315 | 13.1692 | 14.866 | 6.6723 | 42.3277 | 0.35121 | 6.1 | 6.3 | 48.6 | 603.75 | 792 | 827.9049 | -4.5334 | 77.7846 | 715.8275 | 93.2107 |  | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [12 empty] | Stage 1 | Stage 2 |  |  | Stage 1 | Stage 2 | [13 empty] | 11 | 5 | 6
|  |  |  | System feed flow rate, QF-sys (gpm) | 8.515 | [5 empty] | 1999-03-14 | 11:00 | 6188 | 23.4 | 63 | 51 | 4.8 | 3.5 | 7.5 | 1.8 |  | 9.3 | 12.8 | 0.80645 | 0.37634 | 15.3846 | 16.1297 | 6.5961 | 45.6039 | 0.35369 | 7.5 | 6 | 32.4 | 168.2 | 212.967 | 792 | 965.3295 | -21.885 | 84.7864 | 692.0103 | 95.318 | 63 | 58 | 4.8 | 5.28 | 7.52 | 9.3 | 12.8 | 0.30807 | 0.56774 | 16.2462 | 17.033 | 4.9108 | 50.7892 | 0.33537 | 6 | 6.2 | 20.52 | 384 | 552 | 639.2094 | -15.7988 | 90.3647 | 511.6047 | 95.9891 | 58 | 51 | 4.8 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 14.3232 | 6.0883 | 43.6117 | 0.32842 | 6.2 | 6.3 | 48.6 | 552 | 792 | 762.8581 | 3.6795 | 77.1796 | 657.4291 | 92.6076 | Qp/QT (THM4), % | -18.1982 | 46.6667 |  | Qp/QT (HAA5), % | -49.3827 | 33.9506 | [11 empty] | Qp/QT (THM4), % | 10.6667 | 58.6667 |  | Qp/QT (HAA5), % | 10.453 | 57.4913 | [11 empty] | Qp/QT (THM4), % | -72.3514 | 20.6718 |  | Qp/QT (HAA5), % | -411.1111 | -138.3838 | [11 empty] | Qp/QT (THM4), % | -32.6693 | 39.0438 |  | Qp/QT (HAA5), % | 32.9381 | 68.5112 | [11 empty] | Qp/QT (THM4), % | -5.0235 | 51.4914 |  | Qp/QT (HAA5), % | -8.5106 | 48.9362 | [11 empty] | Qp/QT (THM4), % | 10.2941 | 58.4225 |  | Qp/QT (HAA5), % | -6.0543 | 50.3132 | [13 empty] | 12 | 5 | 7
[11 empty] | 1999-03-15 | 9:15 | 6210.25 | 21.4 | 63 | 51 | 4.5 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 17.3402 | 7.1686 | 45.3314 | 0.38252 | 7.4 | 6 | 32.4 | 174 | 218.7669 | 864 | 1051.9363 | -21.7519 | 85.1897 | 749.2615 | 95.6757 | 63 | 58 | 4.5 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 18.4125 | 5.3885 | 50.6115 | 0.3638 | 6 | 6.2 | 20.52 | 416 | 621 | 702.7496 | -13.1642 | 90.6202 | 559.3748 | 96.3316 | 58 | 51 | 4.5 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 15.1955 | 6.9459 | 43.0541 | 0.35294 | 6.2 | 6.3 | 48.6 | 621 | 864 | 865.3708 | -0.15865 | 77.7846 | 743.1854 | 93.4606 | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 43.0574 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | 72.1603 | 36.8815 | [11 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | NA | [11 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | 39.0651 | 21.2074 | [11 empty] | SDS-THM4b, mg/L | NA | 36 |  | SDS-THM4b, mg/L | NA | 37.6277 | [11 empty] | SDS-THM4b, mg/L | 72 | 36 |  | SDS-THM4b, mg/L | NA | 42.0658 | [13 empty] | 12 | 5 | 7
|  |  |  | Calculate the Required System Influent Pressure | [6 empty] | 1999-03-16 | 9:05 | 6234.0833 | 21.9 | 63 | 51 | 4.5 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 17.0858 | 7.3917 | 45.1083 | 0.37877 | 7.5 | 5.9 | 32.4 | 179.8 | 224.5667 | 828 | 1083.6649 | -30.8774 | 85.5722 | 771.5707 | 95.8008 | 63 | 58 | 4.5 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 18.1424 | 4.9378 | 51.0622 | 0.3553 | 5.9 | 6.3 | 21.6 | 384 | 586.5 | 646.7644 | -10.2753 | 90.3815 | 515.3822 | 95.8089 | 58 | 51 | 4.5 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 14.9725 | 6.5272 | 43.4728 | 0.34441 | 6.3 | 6.4 | 48.6 | 586.5 | 828 | 816.1419 | 1.4321 | 78.3583 | 701.321 | 93.0702 | SDS-HAA5b, mg/L | NA | 22.88 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | 53.8773 | 26.3253 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | NA | 11.2535 |  | SDS-HAA5b, mg/L | NA | NA | [11 empty] | SDS-HAA5b, mg/L | NA | 49.3657 |  | SDS-HAA5b, mg/L | 54 | 27 | [11 empty] | SDS-HAA5b, mg/L | NA | 25.7991 |  | SDS-HAA5b, mg/L | NA | 27 | [11 empty] | SDS-HAA5b, mg/L | 46.1691 | 23.1156 |  | SDS-HAA5b, mg/L | NA | 27 | [13 empty] | 12 | 5 | 7
|  |  |  | Osmotic pressure for stage 13, Dp1 (psi) | 4.35 | [5 empty] | 1999-03-19 | 11:00 | 6308 | 23.4 | 62 | 50 | 4.4 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 16.3448 | 6.9455 | 44.6545 | 0.36603 | NA | 6 | 32.4 | 168.2 | 212.967 | 792 | 1020.2077 | -28.8141 | 84.7864 | 726.9523 | 95.543 | 62 | 56 | 4.4 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 17.3556 | 6.0715 | 48.5285 | 0.35764 | 6 | NA | 21.6 | 467.2 | 621 | 790.29 | -27.2609 | 89.8576 | 628.745 | 96.5646 | 56 | 50 | 4.4 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 14.3232 | 6.9459 | 41.6541 | 0.34386 | NA | NA | 48.6 | 621 | 792 | 865.3708 | -9.264 | 77.1796 | 743.1854 | 93.4606 | SDS-TOXb, mg Cl- /L | NA | 218.1333 |  | SDS-TOXb, mg Cl- /L | NA | 260.6049 | [11 empty] | SDS-TOXb, mg Cl- /L | 346.0267 | 175.1467 |  | SDS-TOXb, mg Cl- /L | 346.7875 | 179.331 | [11 empty] | SDS-TOXb, mg Cl- /L | NA | 114.8475 |  | SDS-TOXb, mg Cl- /L | NA | NA | [11 empty] | SDS-TOXb, mg Cl- /L | NA | 183.6096 |  | SDS-TOXb, mg Cl- /L | 198.996 | 109.3518 | [11 empty] | SDS-TOXb, mg Cl- /L | NA | 207.3768 |  | SDS-TOXb, mg Cl- /L | NA | 215.2979 | [11 empty] | SDS-TOXb, mg Cl- /L | 347.0294 | 188.2059 |  | SDS-TOXb, mg Cl- /L | NA | 214.9666 | [13 empty] | 12 | 6 | 6
|  |  |  | Osmotic pressure for stage 23, Dp2 (psi) | 4.75 | [5 empty] | 1999-03-20 | 11:00 | 6332 | 23.8 | 62 | 50 | 4.5 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 16.1526 | 6.9683 | 44.5317 | 0.36272 | 7.7 | 6 | 32.4 | 168.2 | 212.967 | 720 | 1020.2077 | -41.6955 | 84.7864 | 729.2256 | 95.5569 | 62 | 56 | 4.5 | 5.46 | 7.44 | 9.3 | 12.9 | 0.30837 | 0.5871 | 16.8 | 17.4066 | 6.0183 | 48.4817 | 0.35903 | 6 | 6.3 | 20.52 | 460.8 | 621 | 783.9087 | -26.2333 | 90.3647 | 622.3544 | 96.7028 | 56 | 50 | 4.5 | 2.14 | 5.3 | 3.84 | 7.44 | 0.3863 | 0.55729 | 13.1692 | 13.6447 | 6.8796 | 41.6204 | 0.32784 | 6.3 | 6.4 | 48.6 | 621 | 720 | 852.12 | -18.35 | 77.1796 | 736.56 | 93.4018 | SDS-CDb, mg/L | NA | 6.4133 |  | SDS-CDb, mg/L | NA | 6.8457 | [11 empty] | SDS-CDb, mg/L | 5.876 | 4.868 |  | SDS-CDb, mg/L | 5.8805 | 4.8927 | [11 empty] | SDS-CDb, mg/L | NA | 3.5815 |  | SDS-CDb, mg/L | NA | NA | [11 empty] | SDS-CDb, mg/L | NA | 4.9765 |  | SDS-CDb, mg/L | 5.0943 | 4.4077 | [11 empty] | SDS-CDb, mg/L | NA | 5.0791 |  | SDS-CDb, mg/L | NA | 5.1149 | [11 empty] | SDS-CDb, mg/L | 5.9632 | 4.8563 |  | SDS-CDb, mg/L | NA | 5.0428 | [13 empty] | 12 | 6 | 6
|  |  |  | Pressure losses due to stage hardware, DPs (psi) | 10 | [5 empty] | 1999-03-21 | 11:45 | 6356.75 | 24.4 | 63 | 51 | 4.8 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 15.8687 | 6.9455 | 45.2545 | 0.35065 | 7.6 | 6 | 32.4 | 168.2 | 212.967 | 828 | 1020.2077 | -23.2135 | 84.7864 | 726.9523 | 95.543 | 63 | 59 | 4.8 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 16.8501 | 4.9599 | 51.2401 | 0.32884 | 6 | 6.5 | 19.98 | 384 | 607.2 | 647.939 | -6.7093 | 90.6183 | 515.9695 | 96.1277 | 59 | 51 | 4.8 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 13.906 | 6.7784 | 43.4216 | 0.32026 | 6.5 | 6.4 | 48.6 | 607.2 | 828 | 845.6792 | -2.1352 | 77.1796 | 726.4396 | 93.3098 | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | NA | [11 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | #VALUE! | #VALUE! | [11 empty] | TOCb, mg/L | NA | #VALUE! |  | TOCb, mg/L | NA | #VALUE! | [11 empty] | TOCb, mg/L | #VALUE! | #VALUE! |  | TOCb, mg/L | NA | #VALUE! | [13 empty] | 12 | 4 | 8
|  |  |  | Pressure losses in a single element, DPe (psi) | 3 | [5 empty] | 1999-03-22 | 9:15 | 6378.25 | 22.3 | 64 | 51 | 4.6 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 16.8849 | 7.1686 | 45.7314 | 0.36922 | 7.5 | 6 | 32.4 | 174 | 218.7669 | 828 | 1051.9363 | -27.0455 | 85.1897 | 749.2615 | 95.6757 | 64 | 59 | 4.6 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 17.9291 | 4.9601 | 51.9399 | 0.34519 | 6 | 6.4 | 19.9674 | 384 | 621 | 647.9481 | -4.3395 | 90.8727 | 515.9741 | 96.1301 | 59 | 51 | 4.6 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 14.7965 | 6.9459 | 43.4541 | 0.34051 | 6.4 | 6.5 | 48.6 | 621 | 828 | 865.3708 | -4.5134 | 77.7846 | 743.1854 | 93.4606 | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | NA | [11 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | #VALUE! | #VALUE! | [11 empty] | UV254 b, cm-1 | NA | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [11 empty] | UV254 b, cm-1 | #VALUE! | #VALUE! |  | UV254 b, cm-1 | NA | #VALUE! | [13 empty] | 13 | 5 | 8
|  |  |  | Design permeate pressure, Pp (psi) | [6 empty] | 1999-03-23 | 1:00 | 6394 | 24.5 | NA | NA | 4.5 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 15.8219 | #VALUE! | #VALUE! | #VALUE! | NA | 6 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | 51 | NA | NA | #VALUE! | 9.3 | 12.8 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 6 | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 51 | NA | 4.5 | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NA | NA | NA | NA | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | NA | [11 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | #VALUE! | #VALUE! | [11 empty] | Bromideb, mg/L | NA | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [11 empty] | Bromideb, mg/L | #VALUE! | #VALUE! |  | Bromideb, mg/L | NA | #VALUE! | [13 empty] | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Mechanical pressure losses per stage, Ls (psi) | 19 | [5 empty] | 1999-03-24 | 9:00 | 6426 | 22.6 | 64 | 51 | 4.7 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 16.7359 | 7.3917 | 45.4083 | 0.36856 | 7.4 | 6.1 | 32.4 | 179.8 | 224.5667 | 828 | 1083.6649 | -30.8774 | 85.5722 | 771.5707 | 95.8008 | 64 | 59 | 4.7 | 5.28 | 7.52 | 9.3 | 12.8 | 0.30807 | 0.56774 | 16.2462 | 17.4405 | 4.8963 | 51.9037 | 0.33602 | 6.1 | 6.2 | 21.6 | 384 | 595 | 638.4511 | -7.3027 | 90.3815 | 511.2255 | 95.7749 | 59 | 51 | 4.7 | 2.22 | 5.3 | 4.02 | 7.52 | 0.38873 | 0.55224 | 13.6615 | 14.6659 | 6.6083 | 43.6917 | 0.33567 | 6.2 | 6.4 | 48.6 | 595 | 828 | 823.8694 | 0.49886 | 78.3583 | 709.4347 | 93.1495 | Alkb, mg/L CaCO3 | NA | 51.8 |  | Alkb, mg/L CaCO3 | NA | 60.5741 | [11 empty] | Alkb, mg/L CaCO3 | 78.4533 | 53.4933 |  | Alkb, mg/L CaCO3 | 78.5645 | 54.1045 | [11 empty] | Alkb, mg/L CaCO3 | NA | 60.4238 |  | Alkb, mg/L CaCO3 | NA | NA | [11 empty] | Alkb, mg/L CaCO3 | NA | 45.4781 |  | Alkb, mg/L CaCO3 | 48.531 | 30.7444 | [11 empty] | Alkb, mg/L CaCO3 | NA | 34.3736 |  | Alkb, mg/L CaCO3 | NA | 35.4468 | [11 empty] | Alkb, mg/L CaCO3 | 52.4706 | 31.2941 |  | Alkb, mg/L CaCO3 | NA | 34.8622 | [13 empty] | 13 | 5 | 8
|  |  |  | Net driving pressure required for permeation, NDP (psi) | 48.5185 | [5 empty] | 1999-03-25 | 10:00 | 6451 | 23.3 | 64 | 51 | 4.6 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 16.3931 | 6.9683 | 45.9317 | 0.3569 | 7.2 | 6.1 | 32.4 | 168.2 | 212.967 | 828 | 1020.2077 | -23.2135 | 84.7864 | 729.2256 | 95.5569 | 64 | 59 | 4.6 | 5.38 | 7.52 | 9.3 | 12.9 | 0.30959 | 0.57849 | 16.5538 | 17.4069 | 4.913 | 51.987 | 0.33483 | 6.1 | 6.2 | 22.14 | 384 | 595 | 642.8839 | -8.0477 | 89.604 | 513.4419 | 95.6879 | 59 | 51 | 4.6 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 14.3656 | 6.6083 | 43.7917 | 0.32804 | 6.2 | 6.2 | 48.6 | 595 | 828 | 823.8694 | 0.49886 | 77.1796 | 709.4347 | 93.1495 | T-Hdb, mg/L CaCO3 | NA | 105.3333 |  | T-Hdb, mg/L CaCO3 | NA | 125.679 | [11 empty] | T-Hdb, mg/L CaCO3 | 162.9333 | 86.1333 |  | T-Hdb, mg/L CaCO3 | 163.2753 | 88.0139 | [11 empty] | T-Hdb, mg/L CaCO3 | NA | 147.3385 |  | T-Hdb, mg/L CaCO3 | NA | NA | [11 empty] | T-Hdb, mg/L CaCO3 | NA | 117.5299 |  | T-Hdb, mg/L CaCO3 | 127.2991 | 70.3821 | [11 empty] | T-Hdb, mg/L CaCO3 | NA | 114.2261 |  | T-Hdb, mg/L CaCO3 | NA | 118.9787 | [11 empty] | T-Hdb, mg/L CaCO3 | 190.9559 | 101.9184 |  | T-Hdb, mg/L CaCO3 | NA | 116.9207 | [13 empty] | 13 | 5 | 8
|  |  |  | Flow weighted system pressure losses, Lsys (psi) | 26.65 | [5 empty] | 1999-03-26 | 8:20 | 6473.3333 | 22.7 | 63 | 50 | 4.9 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 16.6865 | 6.9455 | 44.6545 | 0.37368 | 7.9 | 5.9 | 32.4 | 168.2 | 212.967 | 936 | 1020.2077 | -8.9966 | 84.7864 | 726.9523 | 95.543 | 63 | 59 | 4.9 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 17.7184 | 6.2459 | 49.8541 | 0.3554 | 5.9 | 6.7 | 21.6 | 480 | 665 | 812.3709 | -22.161 | 89.8576 | 646.1854 | 96.6573 | 59 | 50 | 4.9 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 14.6226 | 7.4798 | 42.1202 | 0.34716 | 6.7 | 6.7 | 48.6 | 665 | 936 | 928.1554 | 0.8381 | 77.1796 | 796.5777 | 93.8989 | Ca-Hdb, mg/L CaCO3 | NA | 93.7333 |  | Ca-Hdb, mg/L CaCO3 | NA | 111.7901 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 144.7467 | 76.1067 |  | Ca-Hdb, mg/L CaCO3 | 145.0523 | 77.7875 | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | 130.8527 |  | Ca-Hdb, mg/L CaCO3 | NA | NA | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | 98.4622 |  | Ca-Hdb, mg/L CaCO3 | 106.5217 | 59.5652 | [11 empty] | Ca-Hdb, mg/L CaCO3 | NA | 98.1287 |  | Ca-Hdb, mg/L CaCO3 | NA | 102.1915 | [11 empty] | Ca-Hdb, mg/L CaCO3 | 163.7353 | 87.6925 |  | Ca-Hdb, mg/L CaCO3 | NA | 100.5052 | [13 empty] | 13 | 4 | 9
|  |  |  | Required influent pressure to the system, PI (psi) | 75.1685 | [5 empty] | 1999-03-27 | 10:00 | 6499 | 22 | 62 | 51 | 4.5 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 17.0353 | 6.9455 | 45.0545 | 0.37811 | 7 | 5.9 | 32.4 | 168.2 | 212.967 | 792 | 1020.2077 | -28.8141 | 84.7864 | 726.9523 | 95.543 | 62 | 56 | 4.5 | 5.38 | 7.42 | 9.3 | 12.8 | 0.30656 | 0.57849 | 16.5538 | 18.0888 | 4.9378 | 49.5622 | 0.36497 | 5.9 | 6.1 | 21.6 | 384 | 595 | 646.7644 | -8.6999 | 89.8576 | 515.3822 | 95.8089 | 56 | 51 | 4.5 | 2.22 | 5.2 | 3.92 | 7.42 | 0.38266 | 0.56633 | 13.6615 | 14.9283 | 6.6304 | 42.3696 | 0.35234 | 6.1 | 6.1 | 48.6 | 595 | 792 | 828.2708 | -4.5796 | 77.1796 | 711.6354 | 93.1707 | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [17 empty] | Notes: | [19 empty] | 11 | 6 | 5
|  |  |  | 3: The osmotic pressure can be estimated from Table 6-5 in Part 3 of the | [6 empty] | 1999-03-28 | 11:15 | 6524.25 | 24.1 | 64 | 51 | 4.7 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 16.01 | 7.4159 | 45.3841 | 0.35277 | 7.4 | 6.2 | 32.4 | 179.8 | 224.5667 | 792 | 1083.6649 | -36.8264 | 85.5722 | 773.99 | 95.8139 | 64 | 59 | 4.7 | 5.2 | 7.7 | 9.3 | 12.9 | 0.31232 | 0.55914 | 16 | 16.4314 | 4.8477 | 51.9523 | 0.31628 | 6.2 | 6.2 | 21.6 | 384 | 630 | 628.7377 | 0.20037 | 90.3815 | 506.3688 | 95.7343 | 59 | 51 | 4.7 | 2.4 | 5.3 | 4.1 | 7.7 | 0.39419 | 0.58537 | 14.7692 | 15.1674 | 7.1304 | 43.1696 | 0.35134 | 6.2 | 6.3 | 48.6 | 630 | 792 | 893.2755 | -12.7873 | 78.3583 | 761.6377 | 93.619 | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [17 empty] | This field uses the feed and permeate water quality parameters entered above to determine the percentage of total flow that must be | [19 empty] | 13 | 5 | 8
|  |  |  | "ICR Manual for Bench- and Pilot-Scale Treatment Studies." | [6 empty] | 1999-03-29 | 12:15 | 6549.25 | 24.5 | 63 | 51 | 4.4 | 3.5 | 7.6 | 1.7 |  | 9.3 | 12.8 | 0.8172 | 0.37634 | 15.5897 | 15.8219 | 7.1686 | 45.4314 | 0.34826 | 7.4 | 6.2 | 32.4 | 174 | 218.7669 | 792 | 1051.9363 | -32.8202 | 85.1897 | 749.2615 | 95.6757 | 63 | 59 | 4.4 | 5.29 | 7.51 | 9.3 | 12.8 | 0.30792 | 0.56882 | 16.2769 | 16.5193 | 4.9004 | 51.6996 | 0.31952 | 6.2 | 6.2 | 21.6 | 384 | 630 | 639.2724 | -1.4718 | 90.1265 | 511.6362 | 95.7783 | 59 | 51 | 4.4 | 2.31 | 5.2 | 4.01 | 7.51 | 0.38539 | 0.57606 | 14.2154 | 14.427 | 7.1054 | 43.4946 | 0.3317 | 6.2 | 6.3 | 48.6 | 630 | 792 | 888.2758 | -12.156 | 77.7846 | 759.1379 | 93.598 | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [17 empty] | treated by the membrane process to meet the Stage 1 and proposed Stage 2 DBP MCLs. | [19 empty] | 12 | 4 | 8
[11 empty] | 1999-03-30 | 9:15 | 6570.25 | 23 | 64 | 51 | 4.4 | 3.6 | 7.5 | 1.7 |  | 9.2 | 12.8 | 0.81522 | 0.3913 | 15.3846 | 16.3215 | 7.1495 | 45.9505 | 0.3552 | 7.3 | 6.2 | 32.4 | 174 | 219.2534 | 828 | 1043.6069 | -26.0395 | 85.2226 | 747.3548 | 95.6647 | 64 | 59 | 4.4 | 5.19 | 7.61 | 9.2 | 12.8 | 0.30944 | 0.56413 | 15.9692 | 16.9418 | 5.3179 | 51.7821 | 0.32717 | 6.2 | 6.3 | 19.44 | 416 | 595 | 686.4529 | -15.3702 | 91.1335 | 551.2264 | 96.4733 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.01 | 7.61 | 0.39146 | 0.57606 | 14.2154 | 15.0811 | 6.6547 | 43.9453 | 0.34318 | 6.3 | 6.3 | 48.6 | 595 | 828 | 833.1479 | -0.62173 | 77.8339 | 714.074 | 93.194 | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [17 empty] | A 10% factor of safety has been applied all the MCLs. i.e., MCLs for Stage 1 are 72 / 54 mg/L and Stage 2 are 36 / 27 mg/L for THM4 and HAA5. | [19 empty] | 13 | 5 | 8
[11 empty] | 1999-03-31 | 8:45 | 6593.75 | 23.2 | 64 | 51 | 4.8 | 3 | 7.5 | 1.7 |  | 9.2 | 12.2 | 0.81522 | 0.32609 | 15.3846 | 16.2253 | 7.0039 | 45.6961 | 0.35507 | 7.4 | 6 | 32.4 | 174 | 219.2534 | 828 | 1043.6069 | -26.0395 | 85.2226 | 732.7851 | 95.5785 | 64 | 59 | 4.8 | 5.19 | 7.01 | 9.2 | 12.2 | 0.29124 | 0.56413 | 15.9692 | 16.8419 | 5.4188 | 51.2812 | 0.32842 | 6 | 6.2 | 20.52 | 416 | 595 | 708.8019 | -19.1264 | 90.641 | 562.4009 | 96.3514 | 59 | 51 | 4.8 | 2.31 | 4.7 | 4.01 | 7.01 | 0.35507 | 0.57606 | 14.2154 | 14.9922 | 6.8067 | 43.3933 | 0.3455 | 6.2 | 6.3 | 48.6 | 595 | 828 | 863.5498 | -4.2935 | 77.8339 | 729.2749 | 93.3358 | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [17 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for both parameters. | [19 empty] | 13 | 5 | 8
[11 empty] | 1999-04-01 | 9:30 | 6618.5 | 24 | 64 | 51 | 4.6 | 3.6 | 7.5 | 1.7 |  | 9.2 | 12.8 | 0.81522 | 0.3913 | 15.3846 | 15.8462 | 6.9276 | 45.9724 | 0.34469 | 7.4 | 6.4 | 32.4 | 168.2 | 213.4536 | 828 | 1012.2194 | -22.2487 | 84.8211 | 725.163 | 95.532 | 64 | 58 | 4.6 | 5.28 | 7.52 | 9.2 | 12.8 | 0.30807 | 0.57391 | 16.2462 | 16.7335 | 4.8744 | 51.5256 | 0.32476 | 6.4 | 6.5 | 23.22 | 384 | 595 | 637.3136 | -7.1115 | 89.1218 | 510.6568 | 95.4529 | 58 | 51 | 4.6 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 14.0714 | 6.6083 | 43.2917 | 0.32504 | 6.5 | 6.6 | 48.6 | 595 | 828 | 823.8694 | 0.49886 | 77.2316 | 709.4347 | 93.1495 | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [17 empty] | The maximum (Qp/QT) ratio controls the design. | [19 empty] | 13 | 6 | 7
[11 empty] | 1999-04-02 | 8:00 | 6641 | 22.9 | 63 | 51 | 4.7 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 16.5881 | 6.9683 | 45.3317 | 0.36593 | 7.4 | 5.8 | 32.4 | 168.2 | 212.967 | 864 | 1020.2077 | -18.0796 | 84.7864 | 729.2256 | 95.5569 | 63 | 58 | 4.7 | 5.38 | 7.52 | 9.3 | 12.9 | 0.30959 | 0.57849 | 16.5538 | 17.614 | 6.028 | 49.772 | 0.35389 | 5.8 | 6.5 | 23.22 | 467.2 | 630 | 784.8346 | -24.5769 | 89.0969 | 626.0173 | 96.2908 | 58 | 51 | 4.7 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 14.5364 | 7.0316 | 42.7684 | 0.33989 | 6.5 | 6.6 | 48.6 | 630 | 864 | 873.5298 | -1.103 | 77.1796 | 751.7649 | 93.5352 | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [17 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. | [19 empty] | 12 | 5 | 7
[11 empty] | 1999-04-03 | 11:15 | 6668.25 | 24.7 | 61 | 50 | 4 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 15.7286 | 6.9683 | 44.5317 | 0.3532 | 7.3 | 6 | 32.4 | 168.2 | 212.967 | 792 | 1020.2077 | -28.8141 | 84.7864 | 729.2256 | 95.5569 | 61 | 56 | 4 | 5.38 | 7.52 | 9.3 | 12.9 | 0.30959 | 0.57849 | 16.5538 | 16.7013 | 4.8984 | 49.6016 | 0.33671 | 6 | 6.5 | 23.22 | 384 | 595 | 642.1112 | -7.9179 | 89.0969 | 513.0556 | 95.4742 | 56 | 50 | 4 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 13.7832 | 6.6083 | 42.3917 | 0.32514 | 6.5 | 6.6 | 48.6 | 595 | 792 | 823.8694 | -4.0239 | 77.1796 | 709.4347 | 93.1495 | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [17 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. | [19 empty] | 11 | 5 | 6
[11 empty] | 1999-04-04 | 7:30 | 6688.5 | 21.7 | 62 | 50 | 4.5 | 3.6 | 7.5 | 1.7 |  | 9.2 | 12.8 | 0.81522 | 0.3913 | 15.3846 | 16.9609 | 7.1495 | 44.3505 | 0.38243 | 7.2 | 6.1 | 32.4 | 174 | 219.2534 | 792 | 1043.6069 | -31.7685 | 85.2226 | 747.3548 | 95.6647 | 62 | 57 | 4.5 | 5.28 | 7.52 | 9.2 | 12.8 | 0.30807 | 0.57391 | 16.2462 | 17.9107 | 5.0546 | 49.9454 | 0.35861 | 6.1 | 6.5 | 22.68 | 396.8 | 595 | 659.48 | -10.837 | 89.6558 | 528.14 | 95.7057 | 57 | 50 | 4.5 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 15.0613 | 6.6083 | 42.3917 | 0.35529 | 6.5 | 6.5 | 48.6 | 595 | 792 | 823.8694 | -4.0239 | 77.8339 | 709.4347 | 93.1495 | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [17 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. | [19 empty] | 12 | 5 | 7
[11 empty] | 1999-04-05 | 11:05 | 6716.0833 | 24.7 | 62 | 51 | 4.6 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 15.7286 | 6.7444 | 45.1556 | 0.34832 | 8.2 | 6.3 | 32.4 | 162.4 | 207.1672 | 864 | 988.4791 | -14.4073 | 84.3605 | 706.8434 | 95.4162 | 62 | 59 | 4.6 | 5.29 | 7.61 | 9.3 | 12.9 | 0.31095 | 0.56882 | 16.2769 | 16.4219 | 5.7315 | 50.1685 | 0.32733 | 6.3 | 7.1 | 22.68 | 448 | 595 | 743.6561 | -24.9842 | 89.0523 | 595.828 | 96.1935 | 59 | 51 | 4.6 | 2.31 | 5.3 | 4.01 | 7.61 | 0.39146 | 0.57606 | 14.2154 | 14.342 | 6.6547 | 43.7453 | 0.32785 | 7.1 | 7.1 | 48.6 | 595 | 864 | 833.1479 | 3.5708 | 76.5407 | 714.074 | 93.194 | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [17 empty] | If the permeate quality does not meet the MCL prior to blending, then these calculations are meaningless for that MCL. | [19 empty] | 11 | 3 | 8
[11 empty] | 1999-04-06 | 8:00 | 6737 | 23 | 62 | 51 | 4.5 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 16.5392 | 7.1921 | 44.8079 | 0.36911 | 8.3 | 5.1 | 32.4 | 174 | 218.7669 | 864 | 1051.9363 | -21.7519 | 85.1897 | 751.6078 | 95.6892 | 62 | 59 | 4.5 | 5.29 | 7.61 | 9.3 | 12.9 | 0.31095 | 0.56882 | 16.2769 | 17.2682 | 5.9902 | 50.0098 | 0.3453 | 5.1 | 7.1 | 22.68 | 467.2 | 630 | 776.2027 | -23.2068 | 89.6328 | 621.7014 | 96.3519 | 59 | 51 | 4.5 | 2.31 | 5.3 | 4.01 | 7.61 | 0.39146 | 0.57606 | 14.2154 | 15.0811 | 7.081 | 43.419 | 0.34734 | 7.1 | 7.1 | 48.6 | 630 | 864 | 883.4026 | -2.2457 | 77.7846 | 756.7013 | 93.5774 | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [17 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. | [19 empty] | 11 | 3 | 8
[11 empty] | 1999-04-07 | 8:15 | 6761.25 | 22 | 63 | 51 | 4.5 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 17.0353 | 7.1921 | 45.3079 | 0.37599 | 7.9 | 6 | 32.4 | 174 | 218.7669 | 864 | 1051.9363 | -21.7519 | 85.1897 | 751.6078 | 95.6892 | 63 | 59 | 4.5 | 5.38 | 7.52 | 9.3 | 12.9 | 0.30959 | 0.57849 | 16.5538 | 18.0888 | 6.2091 | 50.2909 | 0.35968 | 6 | 6.5 | 22.68 | 480 | 630 | 807.1784 | -28.1236 | 89.6328 | 643.5892 | 96.476 | 59 | 51 | 4.5 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 14.9283 | 7.0316 | 43.4684 | 0.34343 | 6.5 | 6.7 | 48.6 | 630 | 864 | 873.5298 | -1.103 | 77.7846 | 751.7649 | 93.5352 | [110 empty] | 12 | 4 | 8
[11 empty] | 1999-04-08 | 10:40 | 6787.6667 | 24.2 | 63 | 51 | 4.7 | 3.6 | 7.5 | 1.7 |  | 9.2 | 12.8 | 0.81522 | 0.3913 | 15.3846 | 15.7528 | 6.9276 | 45.3724 | 0.34719 | 7.4 | 5.4 | 32.4 | 168.2 | 213.4536 | 792 | 1012.2194 | -27.8055 | 84.8211 | 725.163 | 95.532 | 63 | 59 | 4.7 | 5.28 | 7.52 | 9.2 | 12.8 | 0.30807 | 0.57391 | 16.2462 | 16.6349 | 5.8401 | 50.4599 | 0.32967 | 5.4 | 6.7 | 22.14 | 454.4 | 630 | 757.9017 | -20.3019 | 89.6277 | 606.1509 | 96.3474 | 59 | 51 | 4.7 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 13.9884 | 7.0316 | 43.2684 | 0.3233 | 6.7 | 6.7 | 48.6 | 630 | 792 | 873.5298 | -10.2942 | 77.2316 | 751.7649 | 93.5352 | [110 empty] | 12 | 4 | 8
[11 empty] | 1999-04-09 | 10:40 | 6811.6667 | 24.4 | 63 | 51 | 4.9 | 3.6 | 7.5 | 1.7 |  | 9.2 | 12.8 | 0.81522 | 0.3913 | 15.3846 | 15.6599 | 6.7057 | 45.3943 | 0.34498 | 7.8 | 6.5 | 32.4 | 162.4 | 207.6537 | 864 | 980.832 | -13.5222 | 84.3971 | 702.9711 | 95.391 | 63 | 60 | 4.9 | 5.19 | 7.61 | 9.2 | 12.8 | 0.30944 | 0.56413 | 15.9692 | 16.255 | 5.8183 | 50.7817 | 0.3201 | 6.5 | 6.7 | 20.52 | 454.4 | 665 | 750.305 | -12.8278 | 90.1182 | 602.3525 | 96.5934 | 60 | 51 | 4.9 | 2.31 | 5.3 | 4.01 | 7.61 | 0.39146 | 0.57606 | 14.2154 | 14.4697 | 7.5073 | 43.0927 | 0.33578 | 6.7 | 6.8 | 48.6 | 665 | 864 | 933.6574 | -8.0622 | 76.5957 | 799.3287 | 93.9199 | [110 empty] | 12 | 3 | 9
[11 empty] | 1999-04-10 | 11:30 | 6836.5 | 24.8 | 61 | 50 | 4.5 | 3.6 | 7.5 | 1.7 |  | 9.2 | 12.8 | 0.81522 | 0.3913 | 15.3846 | 15.4758 | 6.9276 | 44.0724 | 0.35115 | 7.4 | 5.4 | 32.4 | 168.2 | 213.4536 | 792 | 1012.2194 | -27.8055 | 84.8211 | 725.163 | 95.532 | 61 | 57 | 4.5 | 5.28 | 7.52 | 9.2 | 12.8 | 0.30807 | 0.57391 | 16.2462 | 16.3425 | 5.7536 | 48.7464 | 0.33526 | 5.4 | 6.6 | 22.14 | 448 | 630 | 747.0081 | -18.5727 | 89.6277 | 597.504 | 96.2946 | 57 | 50 | 4.5 | 2.22 | 5.3 | 3.92 | 7.52 | 0.38873 | 0.56633 | 13.6615 | 13.7425 | 7.0316 | 41.9684 | 0.32745 | 6.6 | 6.6 | 48.6 | 630 | 792 | 873.5298 | -10.2942 | 77.2316 | 751.7649 | 93.5352 | [110 empty] | 11 | 4 | 7
[11 empty] | 1999-04-11 | 10:15 | 6859.25 | 24 | 63 | 51 | 4.4 | 3.6 | 7.6 | 1.7 |  | 9.3 | 12.9 | 0.8172 | 0.3871 | 15.5897 | 16.0574 | 6.7444 | 45.8556 | 0.35017 | 7.5 | 6.2 | 32.4 | 162.4 | 207.1672 | 720 | 988.4791 | -37.2888 | 84.3605 | 706.8434 | 95.4162 | 63 | 59 | 4.4 | 5.29 | 7.61 | 9.3 | 12.9 | 0.31095 | 0.56882 | 16.2769 | 16.7652 | 4.4742 | 52.1258 | 0.32163 | 6.2 | 6.3 | 19.98 | 352 | 560 | 582.7997 | -4.0714 | 90.3556 | 467.3999 | 95.7253 | 59 | 51 | 4.4 | 2.31 | 5.3 | 4.01 | 7.61 | 0.39146 | 0.57606 | 14.2154 | 14.6418 | 6.2285 | 44.3715 | 0.32998 | 6.3 | 6.4 | 48.6 | 560 | 720 | 782.8932 | -8.7352 | 76.5407 | 671.4466 | 92.7619 | [110 empty] | 12 | 4 | 8
Note on BZ4: Please note that reviewer modified formulas for Stage 2 concentrate and feed flow rates.
Note on CX25: S Allgeier 7/20/99: Brian Mathews stated that bromide was BMRL, but the MRL was 100 ug/L for this analysis -- so result changed to NR.
Note on EL26: C. Rice 7/15/99: SDS Cl2 dose verified by Brian Matthews (7/15/99).
Note on EL32: J. Foster: Values verified with Laboratory.
Note on EL37: C. Rice 7/15/99: Brian Matthews (7/15/99) verified the low THM and HAA concentrations for week 36. He stated that the SDS Cl2 dose both before and after week 36 was 8-9 mg/L. The lower SDS Cl2 dose at 36 weeks (4.4 mg/L) explains the lower values.
Note on EL47: C. Rice 7/15/99: Brian Matthews (7/15/99) verified the low THM and HAA concentrations for week 36. He stated that the SDS Cl2 dose both before and after week 36 was 8-9 mg/L. The lower SDS Cl2 dose at 36 weeks (4.4 mg/L) explains the lower values.