## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Sweetwater Authority | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 5.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-05-14 | [12 empty] | 20-min. EBCT Start Date | 1998-05-14 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA3710025 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 12.6 | mesh size | (mm) | Coagulation | 12 mg/L ferric chloride; 2.5 mg/L polymer; 0.85 mg/L ammonia | Full-Scale | 10-min. EBCT Start Time | 18:10 | [12 empty] | 20-min. EBCT Start Time | 18:10 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1253 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.55 | 4 | 4.75 | Flocculation | 2-Stage tapered | Full-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 20 | 6 | 3.35 | Sedimentation | 72.6 minutes retention time | Full-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-05-14 | 21:04 | 2.9 | 164.256 | 8.45 | 23 | 0.19 | 0.0014 | 0.73684 | 1.7 | 0.79 | 0.91 | 18.3 | 8.0743 | 23.6 | 5.25 | BMRL | 1.1718 | BMRL | 1.91 | 3.0818 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | C1-20 | N | 1998-05-14 | 21:03 | 2.8833 | 163.312 | 8.43 | 22.7 | 0.175 | 0.0004 | 0.22857 | 1.7 | 0.7 | 1 | 18.3 | 8.1282 | 23.8 | 2.7 | BMRL | BMRL | BMRL | 1.34 | 1.34 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Filtration | Dual media (sand/anthracite) | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-05-15 | 09:23 | 15.2167 | 861.872 | 8.28 | 21.4 | 0.545 | 0.00445 | 0.81651 | 1.91 | 0.72 | 1.19 | 18.3 | 7.999 | 23.6 | 18.8 | BMRL | 4.6953 | 1.2548 | 8.53 | 14.4801 | BMRL | BMRL | BMRL | BMRL | 1.883 | BMRL | BMRL | BMRL | BMRL | 1.883 | 1.883 | C2-20 | N | 1998-05-16 | 11:52 | 41.7 | 2361.888 | 8.14 | 21.4 | 0.515 | 0.00545 | 1.0583 | 1.89 | 0.68 | 1.21 | 18.3 | 8.0327 | 23.8 | 16.55 | BMRL | 4.4185 | 1.1867 | 8.61 | 14.2152 | BMRL | BMRL | BMRL | BMRL | 2.267 | BMRL | BMRL | BMRL | BMRL | 2.267 | 2.267 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.522 | 10 | 2 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Sampling date | MM/DD/YY | 1998-05-14 | 1998-05-17 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-05-14 | 1998-05-17 | [7 empty] | --- | --- |  | C3-10 | N | 1998-05-15 | 12:05 | 17.9167 | 1014.8 | 8.24 | 21.7 | 0.765 | 0.00795 | 1.0392 | 2.02 | 0.77 | 1.25 | 18.3 | 7.979 | 23.7 | 27.5 | BMRL | 7.3739 | 1.7622 | 11.9 | 21.0361 | BMRL | 1.067 | BMRL | BMRL | 3.0236 | 1.2177 | BMRL | BMRL | BMRL | 4.0906 | 5.3083 | Avg-C3-20 | Y | 1998-05-16 | 22:08 | 51.9667 | 2943.392 | 8.055 | 22.6 | 0.915 | 0.0111 | 1.2131 | 2.1 | 0.76 | 1.34 | 18.3 | 8.0177 | 23.8 | 37.425 | BMRL | 10.8695 | 2.5391 | 17.9 | 31.3085 | BMRL | 1.678 | BMRL | BMRL | 3.9123 | 2.1325 | BMRL | BMRL | BMRL | 5.5903 | 7.7228 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 20:20 | 13:35 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 20:20 | 13:35 | [7 empty] | --- | --- |  | Avg-C4-10 | Y | 1998-05-15 | 14:40 | 20.5 | 1161.12 | 8.23 | 22.85 | 1.0425 | 0.013 | 1.247 | 2.165 | 0.77 | 1.395 | 18.3 | 7.9608 | 23.7 | 45.525 | BMRL | 13 | 3.1908 | 18.05 | 34.2408 | BMRL | 1.4459 | BMRL | BMRL | 4.9857 | 2.2546 | BMRL | BMRL | BMRL | 6.4315 | 8.6862 | C4-20 | N | 1998-05-17 | 08:15 | 62.0833 | 3516.4 | 8.52 | 20.5 | 1.31 | 0.0181 | 1.3817 | 2.27 | 0.76 | 1.51 | 18.1 | 7.9636 | 24.2 | 68.85 | 1.01 | 17.3305 | 4.5347 | 21.7 | 44.5752 | BMRL | 1.225 | BMRL | BMRL | 6.192 | 3.1664 | BMRL | BMRL | BMRL | 7.417 | 10.5835 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 2.1667 | 67.4167 | [7 empty] | --- | --- |  | Operation time | hh.hh | 2.1667 | 67.4167 | [7 empty] | --- | --- |  | C5-10 | N | 1998-05-15 | 18:01 | 23.85 | 1350.864 | 8.21 | 23.9 | 1.43 | 0.02135 | 1.493 | 2.36 | 0.7 | 1.66 | 18.3 | 7.9336 | 23.7 | 77.5 | 1.32 | 21.4064 | 5.9887 | 24.3 | 53.0151 | BMRL | 2.1541 | BMRL | BMRL | 8.3934 | 4.1373 | 4.1163 | 3.7696 | 1.9924 | 10.5475 | 14.6848 | C5-20 | N | 1998-05-17 | 15:00 | 68.8333 | 3898.72 | 8.54 | 21.3 | 1.635 | 0.0232 | 1.419 | 2.42 | 0.75 | 1.67 | 18.1 | 7.9982 | 24.2 | 85.55 | 1.34 | 23.8708 | 6.8407 | 26.1 | 58.1516 | BMRL | 1.6056 | BMRL | BMRL | 8.7061 | 4.1443 | 4.7548 | 4.4501 | 1.9822 | 10.3117 | 14.4561 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 122.72 | 3818.48 | [7 empty] | --- | --- |  | Bed volumes | (20 minutes) | 61.36 | 1909.24 | [7 empty] | --- | --- |  | C6-10 | N | 1998-05-15 | 20:55 | 26.75 | 1515.12 | 8.23 | 23.4 | 1.785 | 0.0281 | 1.5742 | 2.54 | 0.79 | 1.75 | 18.3 | 8.0527 | 23.7 | 103.7 | 1.96 | 30.0927 | 9.2259 | 29.9 | 71.1787 | BMRL | 2.7727 | BMRL | BMRL | 10.4103 | 5.3367 | 4.4738 | 4.8901 | 2.2143 | 13.1831 | 18.5197 | C6-20 | N | 1998-05-18 | 04:21 | 82.1833 | 4654.864 | 7.4 | 20.5 | 2.045 | 0.03105 | 1.5183 | 2.61 | 0.89 | 1.72 | 18.1 | 7.9836 | 24.2 | 118.25 | 2.34 | 32.9689 | 10.9017 | 28.1 | 74.3106 | BMRL | 1.9807 | BMRL | BMRL | 9.382 | 5.2437 | 4.49 | 5.2957 | 2.5418 | 11.3627 | 16.6063 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 127 | 117.5 | [7 empty] | 122.25 | 5.4949 |  | Alkalinity | mg/L as CaCO3 | 127 | 117.5 | [7 empty] | 122.25 | 5.4949 |  | C7-10 | N | 1998-05-15 | 23:48 | 29.6333 | 1678.432 | 8.25 | 22.8 | 2.13 | 0.0341 | 1.6009 | 2.68 | 0.73 | 1.95 | 18.3 | 8.0336 | 23.7 | 130.15 | 2.86 | 35.5229 | 12.892 | 28.9 | 80.175 | BMRL | 3.3409 | BMRL | BMRL | 11.1903 | 6.4511 | 4.9955 | 6.2591 | 3.4508 | 14.5312 | 20.9823 | Avg-C7-20 | Y | 1998-05-18 | 11:14 | 89.0667 | 5044.736 | 8.165 | 21.05 | 2.345 | 0.036425 | 1.5533 | 2.745 | 0.85 | 1.895 | 18.1 | 7.9532 | 24.35 | 141.775 | 3.355 | 40.7706 | 15.5113 | 30.2 | 89.8369 | BMRL | 3.3191 | BMRL | BMRL | 12.2726 | 7.2762 | 4.8685 | 8.2583 | 5.1987 | 15.5917 | 22.8678 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2365.8556 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 223 | 223 | [7 empty] | 223 | 0 |  | Total hardness | mg/L as CaCO3 | 223 | 223 | [7 empty] | 223 | 0 |  | Avg-C8-10 | Y | 1998-05-16 | 05:05 | 34.9167 | 1977.68 | 8.245 | 21.2 | 2.5525 | 0.042575 | 1.668 | 2.93 | 0.84 | 2.09 | 18.3 | 8.0136 | 23.75 | 162.025 | 4.77 | 42.5205 | 18.6503 | 27 | 92.9408 | BMRL | 4.8765 | 1.2881 | BMRL | 13.9065 | 9.0357 | 5.823 | 9.4051 | 6.5985 | 20.0711 | 29.1068 | C8-20 | N | 1998-05-19 | 00:53 | 102.7167 | 5817.872 | 8.23 | 20.5 | 2.65 | 0.04125 | 1.5566 | 2.88 | 0.91 | 1.97 | 18.1 | 7.999 | 24.4 | 167.55 | 4.12 | 42.4442 | 18.0988 | 26.8 | 91.463 | BMRL | 4.0488 | 1.4333 | 1.1189 | 12.174 | 8.1978 | 4.5823 | 8.6646 | 6.1828 | 18.775 | 26.9727 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 4731.7112 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 120 | 120 | [7 empty] | 120 | 0 |  | Calcium hardness | mg/L as CaCO3 | 120 | 120 | [7 empty] | 120 | 0 |  | C9-10 | N | 1998-05-16 | 10:25 | 40.25 | 2279.76 | 8.17 | 21.8 | 2.835 | 0.0499 | 1.7601 | 3.08 | 0.89 | 2.19 | 18.3 | 7.9882 | 23.8 | 203.5 | 7.13 | 47.3197 | 23.9102 | 25 | 103.36 | BMRL | 6.2749 | 2.8174 | 1.2691 | 14.621 | 10.5389 | 5.7571 | 11.3099 | 9.8496 | 24.9823 | 35.5213 | C9-20 | N | 1998-05-19 | 17:54 | 119.7333 | 6781.696 | 8.27 | 23.4 | 3.085 | 0.0543 | 1.7601 | 3.09 | 0.83 | 2.26 | 18.1 | 8.0327 | 24.4 | 217.5 | 7.74 | 50.7351 | 26.3522 | 25.3 | 110.1274 | BMRL | 5.9544 | 5.9348 | 1.2496 | 13.7815 | 10.63 | 4.3156 | 10.138 | 9.0685 | 26.9203 | 37.5503 | Electric Rate ($/kW-h) | 0.087
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 6151.2246 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.18 | 0.52 | [7 empty] | 0.35 | 68.6904 |  | Ammonia | mg NH3-N / L | 0.18 | 0.52 | [7 empty] | 0.35 | 68.6904 |  | C10-10 | N | 1998-05-16 | 16:59 | 46.8167 | 2651.696 | 8.17 | 23.6 | 3.22 | 0.0588 | 1.8261 | 3.28 | 0.94 | 2.34 | 18.3 | 7.9736 | 23.8 | 230.55 | 10 | 49.878 | 27.4818 | 21.7 | 109.0598 | BMRL | 8.0221 | 5.9244 | BMRL | 14.5669 | 12.046 | 4.9853 | 13.0281 | 13.8548 | 28.5134 | 40.5594 | C10-20 | N | 1998-05-21 | 04:27 | 154.2833 | 8738.608 | 8.25 | 20.3 | 3.395 | 0.06365 | 1.8748 | 3.19 | 0.8 | 2.39 | 19.4 | 7.9547 | 24 | 250.3 | 12.3 | 54.7128 | 34.0522 | 22.4 | 123.465 | BMRL | 7.9736 | 12.2056 | 1.1492 | 12.9931 | 11.7716 | BMRL | 10.5221 | 12.7065 | 34.3215 | 46.0931 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 200 | 200 | [7 empty] | 200 | 0 |  | Bromide | mg/L | 200 | 200 | [7 empty] | 200 | 0 |  | Avg-C11-10 | Y | 1998-05-17 | 06:22 | 60.2 | 3409.728 | 8.18 | 21.9 | 3.6375 | 0.067925 | 1.8674 | 3.34 | 0.83 | 2.51 | 18.1 | 7.978 | 24.15 | 266.65 | 14.6 | 53.7104 | 34.9581 | 19.15 | 122.4185 | BMRL | 9.3284 | 8.7859 | BMRL | 11.7338 | 11.3357 | BMRL | 10.0145 | 12.8266 | 29.8481 | 41.1838 | Avg-C11-20 | Y | 1998-05-23 | 03:51 | 201.6833 | 11423.344 | 7.885 | 20.95 | 3.945 | 0.076425 | 1.9373 | 3.435 | 0.745 | 2.69 | 19.4 | 7.9773 | 23.95 | 315.45 | 19.25 | 56.15 | 40.6627 | 17.85 | 133.9127 | BMRL | 10.8597 | 17.1843 | 1.239 | 13.0078 | 13.5732 | BMRL | 11.2503 | 18.4722 | 42.2909 | 55.8641 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-05-18 | 05:58 | 83.8 | 4746.432 | 8.2 | 21 | 4.205 | 0.07965 | 1.8942 | 3.59 | 0.86 | 2.73 | 18.1 | 7.9736 | 24.2 | 322.75 | 20.5 | 51.957 | 39.2879 | 15.3 | 127.0449 | BMRL | 11.9295 | 13.6793 | BMRL | 10.4893 | 12.3468 | BMRL | 10.2836 | 16.5475 | 36.0982 | 48.4451 | C12-20 | N | 1998-05-24 | 06:24 | 228.2333 | 12927.136 | 8.48 | 21.2 | 4.315 | 0.0832 | 1.9282 | 3.6 | 0.72 | 2.88 | 19.4 | 7.9799 | 24 | 329.1 | 22.9 | 56.0792 | 43.648 | 16.4 | 139.0272 | BMRL | 12.1806 | 18.4002 | 1.4169 | 12.8289 | 14.2313 | BMRL | 10.6725 | 19.3457 | 44.8265 | 59.0578 | Current Process Water Rate ($/1000 gal) | 0.196
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.0266e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-05-19 | 19:00 | 120.8333 | 6844 | 8.23 | 23.6 | 4.5 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C13-20 | N | 1998-05-25 | 22:04 | 267.9 | 15173.856 | 8.51 | 20.9 | 4.47 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD
|  |  |  | Scaling factor, SF | 9.44 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-05-14 | 1998-05-15 | 1998-05-16 | 1998-05-17 | 1998-05-19 | 1998-05-24 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-05-14 | 1998-05-15 | 1998-05-16 | 1998-05-17 | 1998-05-19 | 1998-05-24 |  |  |  |  | --- | ---
Plant Name | Robert A. Perdue Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 8.1308 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 20:15 | 17:50 | 15:00 | 13:30 | 09:50 | 10:05 |  |  |  |  | --- | --- | Sampling time | hh:mm | 20:15 | 17:50 | 15:00 | 13:30 | 09:50 | 10:05 |  |  |  |  | --- | ---
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 16.8972 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 2.0833 | 23.6667 | 44.8333 | 67.3333 | 111.6667 | 231.9167 |  |  |  |  | --- | --- | Operation time | hh.hh | 2.0833 | 23.6667 | 44.8333 | 67.3333 | 111.6667 | 231.9167 |  |  |  |  | --- | ---
Process Train Name | Perdue Treatment Plant |  |  | Estimated total influent volume required, VSCT (L) | 330.3135 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 118 | 1340.48 | 2539.36 | 3813.76 | 6324.8 | 13135.76 |  |  |  |  | --- | --- | Bed volumes | (20 minute) | 59 | 670.24 | 1269.68 | 1906.88 | 3162.4 | 6567.88 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 221 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8 | 7.97 | 8.01 | 7.99 | 7.91 | 8.01 |  |  |  |  | 7.9817 | 0.47817 | pH | --- | 8 | 7.97 | 8.01 | 7.99 | 7.91 | 8.01 |  |  |  |  | 7.9817 | 0.47817 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.1 | NA | NA | 0.2 | NA | 0.1 |  |  |  |  | 0.13333 | 43.3013 | Turbidity | ntu | 0.1 | NA | NA | 0.2 | NA | 0.1 |  |  |  |  | 0.13333 | 43.3013 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 16.5 | 16.5 | 16.2 | 17.2 | 15.3 | 18 |  |  |  |  | 16.6167 | 5.508 | Temperature | oC | 16.5 | 16.5 | 16.2 | 17.2 | 15.3 | 18 |  |  |  |  | 16.6167 | 5.508
Historical Average Water Temperature (oC) | 22 |  |  | Estimated full-scale run time, tLCT (days) | 42.7168 | [5 empty] | Total organic carbon | mg/L | 5.86 | 5.93 | 5.745 | 5.62 | 5.755 | 5.76 |  |  |  |  | 5.7783 | 1.8435 | Total organic carbon | mg/L | 5.86 | 5.93 | 5.745 | 5.62 | 5.755 | 5.76 |  |  |  |  | 5.7783 | 1.8435 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 30 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0593 | [5 empty] | UV254 | cm-1 | 0.1274 | NA | NA | 0.1269 | NA | 0.1263 |  |  |  |  | 0.12687 | 0.43412 | UV254 | cm-1 | 0.1274 | NA | NA | 0.1269 | NA | 0.1263 |  |  |  |  | 0.12687 | 0.43412 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 4.5251 | [5 empty] | SUVA | L/(mg*m) | 2.1741 | NR | NR | 2.258 | NR | 2.1927 |  |  |  |  | 2.2083 | 1.9962 | SUVA | L/(mg*m) | 2.1741 | NR | NR | 2.258 | NR | 2.1927 |  |  |  |  | 2.2083 | 1.9962 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 14.3553 | [5 empty] | SDS-Cl2 dose | mg/L | 4.63 | NA | NA | 4.24 | NA | 4.35 |  |  |  |  | 4.4067 | 4.5631 | SDS-Cl2 dose | mg/L | 4.63 | NA | NA | 4.24 | NA | 4.35 |  |  |  |  | 4.4067 | 4.5631 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 110.1045 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.82 | NA | NA | 0.63 | NA | 0.6 |  |  |  |  | 0.68333 | 17.4591 | SDS-Free Cl2 residual | mg/L | 0.82 | NA | NA | 0.63 | NA | 0.6 |  |  |  |  | 0.68333 | 17.4591 | C4-10 | Primary | 1998-05-15 | 14:40 | 20.5 | 1161.12 | 8.24 | 22.8 | 1.055 | 0.0128 | 1.2133 | 2.17 | 0.76 | 1.41 | 18.3 | 7.959 | 23.7 | 44.4 | BMRL | 13.1401 | 3.2398 | 18.4 | 34.7798 | BMRL | 1.4196 | BMRL | BMRL | 5.088 | 2.3202 | BMRL | BMRL | BMRL | 6.5076 | 8.8278 | C3-20 | Primary | 1998-05-16 | 22:08 | 51.9667 | 2943.392 | 8.08 | 22.6 | 0.915 | 0.01115 | 1.2186 | 2.1 | 0.84 | 1.26 | 18.3 | 8.0227 | 23.8 | 38.05 | BMRL | 11.3627 | 2.4846 | 18.3 | 32.1473 | BMRL | 1.5437 | BMRL | BMRL | 3.3769 | 1.9594 | BMRL | BMRL | BMRL | 4.9206 | 6.8801
|  |  |  | Mass GAC required, mSC (g) | 9.3436 | [5 empty] | SDS-Cl2 demand | mg/L | 3.81 | NR | NR | 3.61 | NR | 3.75 |  |  |  |  | 3.7233 | 2.7565 | SDS-Cl2 demand | mg/L | 3.81 | NR | NR | 3.61 | NR | 3.75 |  |  |  |  | 3.7233 | 2.7565 | D-C4-10 | Duplicate | 1998-05-15 | 14:40 | 20.5 | 1161.12 | 8.22 | 22.9 | 1.03 | 0.0132 | 1.2816 | 2.16 | 0.78 | 1.38 | 18.3 | 7.9627 | 23.7 | 46.65 | BMRL | 12.86 | 3.1418 | 17.7 | 33.7019 | BMRL | 1.4722 | BMRL | BMRL | 4.8833 | 2.1891 | BMRL | BMRL | BMRL | 6.3555 | 8.5446 | D-C3-10 | Duplicate | 1998-05-16 | 22:08 | 51.9667 | 2943.392 | 8.03 | 22.6 | 0.915 | 0.01105 | 1.2077 | 2.1 | 0.68 | 1.42 | 18.3 | 8.0127 | 23.8 | 36.8 | BMRL | 10.3762 | 2.5936 | 17.5 | 30.4698 | BMRL | 1.8122 | BMRL | BMRL | 4.4477 | 2.3056 | BMRL | BMRL | BMRL | 6.26 | 8.5656
[11 empty] | SDS-Chlorination temp. | oC | 18.3 | NA | NA | 18.1 | NA | 19.4 |  |  |  |  | 18.6 | 3.7634 | SDS-Chlorination temp. | oC | 18.3 | NA | NA | 18.1 | NA | 19.4 |  |  |  |  | 18.6 | 3.7634 | Avg-C4-10 | Average | --- | --- | --- | --- | 8.23 | 22.85 | 1.0425 | 0.013 | 1.2474 | 2.165 | 0.77 | 1.395 | 18.3 | 7.9608 | 23.7 | 45.525 | BMRL | 13 | 3.1908 | 18.05 | 34.2408 | BMRL | 1.4459 | BMRL | BMRL | 4.9857 | 2.2546 | BMRL | BMRL | BMRL | 6.4315 | 8.6862 | Avg-C3-20 | Average | --- | --- | --- | --- | 8.055 | 22.6 | 0.915 | 0.0111 | 1.2131 | 2.1 | 0.76 | 1.34 | 18.3 | 8.0177 | 23.8 | 37.425 | BMRL | 10.8695 | 2.5391 | 17.9 | 31.3085 | BMRL | 1.678 | BMRL | BMRL | 3.9123 | 2.1325 | BMRL | BMRL | BMRL | 5.5903 | 7.7228
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.9482 | NA | NA | 7.9136 | NA | 7.9199 |  |  |  |  | 7.9272 | 0.23227 | SDS-Chlorination pH | --- | 7.9482 | NA | NA | 7.9136 | NA | 7.9199 |  |  |  |  | 7.9272 | 0.23227 | RPD-C4-10 | RPD | --- | --- | --- | --- | 0.24301 | 0.43764 | 2.3981 | 3.0769 | 5.474 | 0.46189 | 2.5974 | 2.1505 | 0 | 0.04658 | 0 | 4.9423 |  | 2.1543 | 3.069 | 3.8781 | 3.1482 |  | 3.6415 |  |  | 4.1073 | 5.8147 |  |  |  | 2.3653 | 3.2606 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0.62073 | 0 | 0 | 0.9009 | 0.9009 | 0 | 21.0526 | 11.9403 | 0 | 0.12472 | 0 | 3.34 |  | 9.0759 | 4.295 | 4.4693 | 5.3578 |  | 16.001 |  |  | 27.371 | 16.2343 |  |  |  | 23.9582 | 21.8253
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 23.8 | NA | NA | 24.4 | NA | 24 |  |  |  |  | 24.0667 | 1.2694 | SDS-Incubation time | hours | 23.8 | NA | NA | 24.4 | NA | 24 |  |  |  |  | 24.0667 | 1.2694 | C8-10 | Primary | 1998-05-16 | 05:05 | 34.9167 | 1977.68 | 8.23 | 21.2 | 2.54 | 0.04255 | 1.6752 | 2.91 | 0.8 | 2.11 | 18.3 | 8.0136 | 23.7 | 163.65 | 4.67 | 41.926 | 18.3553 | 27 | 91.9513 | BMRL | 4.672 | 1.0358 | BMRL | 13.2635 | 8.6949 | 5.4562 | 8.7413 | 5.8524 | 18.9713 | 27.6662 | C7-20 | Primary | 1998-05-18 | 11:14 | 89.0667 | 5044.736 | 8.15 | 21 | 2.335 | 0.03645 | 1.561 | 2.74 | 0.88 | 1.86 | 18.1 | 7.9682 | 24.3 | 141.65 | 3.39 | 40.3411 | 15.1948 | 30.1 | 89.0259 | BMRL | 3.272 | BMRL | BMRL | 12.5152 | 7.3491 | 4.7505 | 8.1298 | 5.1439 | 15.7872 | 23.1363
|  |  |  | Estimated full-scale run time, tLCT (days) | 85.4337 | [5 empty] | SDS-TOX | mg Cl- /L | 551.2 | NA | NA | 542.9 | NA | 509.8 |  |  |  |  | 534.6333 | 4.0968 | SDS-TOX | mg Cl- /L | 551.2 | NA | NA | 542.9 | NA | 509.8 |  |  |  |  | 534.6333 | 4.0968 | D-C8-10 | Duplicate | 1998-05-16 | 05:05 | 34.9167 | 1977.68 | 8.26 | 21.2 | 2.565 | 0.0426 | 1.6608 | 2.95 | 0.88 | 2.07 | 18.3 | 8.0136 | 23.8 | 160.4 | 4.87 | 43.115 | 18.9453 | 27 | 93.9303 | BMRL | 5.0811 | 1.5404 | BMRL | 14.5495 | 9.3764 | 6.1898 | 10.0688 | 7.3447 | 21.171 | 30.5474 | D-C7-20 | Duplicate | 1998-05-18 | 11:14 | 89.0667 | 5044.736 | 8.18 | 21.1 | 2.355 | 0.0364 | 1.5456 | 2.75 | 0.82 | 1.93 | 18.1 | 7.9382 | 24.4 | 141.9 | 3.32 | 41.2001 | 15.8277 | 30.3 | 90.6478 | BMRL | 3.3662 | BMRL | BMRL | 12.0299 | 7.2033 | 4.9866 | 8.3867 | 5.2535 | 15.3961 | 22.5994
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1186 | [5 empty] | SDS-CHCl3 | mg/L | 65 | NA | NA | 62.5 | NA | 66.4 |  |  |  |  | 64.6333 | 3.0568 | SDS-CHCl3 | mg/L | 65 | NA | NA | 62.5 | NA | 66.4 |  |  |  |  | 64.6333 | 3.0568 | Avg-C8-10 | Average | --- | --- | --- | --- | 8.245 | 21.2 | 2.5525 | 0.042575 | 1.668 | 2.93 | 0.84 | 2.09 | 18.3 | 8.0136 | 23.75 | 162.025 | 4.77 | 42.5205 | 18.6503 | 27 | 92.9408 | BMRL | 4.8765 | 1.2881 | BMRL | 13.9065 | 9.0357 | 5.823 | 9.4051 | 6.5985 | 20.0711 | 29.1068 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.165 | 21.05 | 2.345 | 0.036425 | 1.5533 | 2.745 | 0.85 | 1.895 | 18.1 | 7.9532 | 24.35 | 141.775 | 3.355 | 40.7706 | 15.5113 | 30.2 | 89.8369 | BMRL | 3.3191 | BMRL | BMRL | 12.2726 | 7.2762 | 4.8685 | 8.2583 | 5.1987 | 15.5917 | 22.8678
|  |  |  | Estimated RSSCT run time, tSCT (days) | 9.0502 | [5 empty] | SDS-BDCM | mg/L | 54.6152 | NA | NA | 55.0359 | NA | 55.9622 |  |  |  |  | 55.2044 | 1.2484 | SDS-BDCM | mg/L | 54.6152 | NA | NA | 55.0359 | NA | 55.9622 |  |  |  |  | 55.2044 | 1.2484 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.36386 | 0 | 0.97943 | 0.11744 | 0.86199 | 1.3652 | 9.5238 | 1.9139 | 0 | 0 | 0.42105 | 2.0059 | 4.1929 | 2.7964 | 3.1633 | 0 | 2.1293 |  | 8.3882 | 39.1724 |  | 9.2478 | 7.5425 | 12.5978 | 14.1147 | 22.6163 | 10.9594 | 9.8987 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.36742 | 0.47506 | 0.85288 | 0.13727 | 0.99014 | 0.3643 | 7.0588 | 3.6939 | 0 | 0.37721 | 0.41068 | 0.17634 | 2.0864 | 2.1068 | 4.0805 | 0.66225 | 1.8054 |  | 2.8385 |  |  | 3.9545 | 2.0037 | 4.8484 | 3.1107 | 2.1076 | 2.5084 | 2.3478
|  |  |  | RSSCT bed length, lSC (cm) | 28.7106 | [5 empty] | SDS-DBCM | mg/L | 68.0591 | NA | NA | 68.3279 | NA | 72.9315 |  |  |  |  | 69.7728 | 3.9253 | SDS-DBCM | mg/L | 68.0591 | NA | NA | 68.3279 | NA | 72.9315 |  |  |  |  | 69.7728 | 3.9253 | C11-10 | Primary | 1998-05-17 | 06:22 | 60.2 | 3409.728 | 8.17 | 21.9 | 3.6 | 0.0678 | 1.8833 | 3.32 | 0.82 | 2.5 | 18.1 | 7.9771 | 24.2 | 267.65 | 15.1 | 54.9878 | 36.1039 | 19.7 | 125.8917 | BMRL | 8.7704 | 7.8915 | BMRL | 10.8783 | 10.7654 | BMRL | 8.938 | 11.4002 | 27.5401 | 38.3056 | C11-20 | Primary | 1998-05-23 | 03:51 | 201.6833 | 11423.344 | 7.87 | 20.9 | 3.96 | 0.07655 | 1.9331 | 3.44 | 0.74 | 2.7 | 19.4 | 7.9747 | 23.9 | 309.2 | 20 | 57.7949 | 41.9026 | 18.3 | 137.9975 | BMRL | 10.5894 | 16.4628 | 1.2548 | 12.5394 | 13.2347 | BMRL | 10.9556 | 18.197 | 40.8464 | 54.0811
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 220.209 | [5 empty] | SDS-CHBr3 | mg/L | 8.54 | NA | NA | 8.74 | NA | 8.61 |  |  |  |  | 8.63 | 1.176 | SDS-CHBr3 | mg/L | 8.54 | NA | NA | 8.74 | NA | 8.61 |  |  |  |  | 8.63 | 1.176 | D-C11-10 | Duplicate | 1998-05-17 | 06:22 | 60.2 | 3409.728 | 8.19 | 21.9 | 3.675 | 0.06805 | 1.8517 | 3.36 | 0.84 | 2.52 | 18.1 | 7.979 | 24.1 | 265.65 | 14.1 | 52.4329 | 33.8123 | 18.6 | 118.9453 | BMRL | 9.8865 | 9.6803 | BMRL | 12.5892 | 11.906 | BMRL | 11.0911 | 14.2531 | 32.156 | 44.062 | D-C11-20 | Duplicate | 1998-05-23 | 03:51 | 201.6833 | 11423.344 | 7.9 | 21 | 3.93 | 0.0763 | 1.9415 | 3.43 | 0.75 | 2.68 | 19.4 | 7.9799 | 24 | 321.7 | 18.5 | 54.505 | 39.4228 | 17.4 | 129.8278 | BMRL | 11.1301 | 17.9058 | 1.2232 | 13.4762 | 13.9118 | BMRL | 11.545 | 18.7473 | 43.7353 | 57.6471
|  |  |  | Mass GAC required, mSC (g) | 18.6872 | [5 empty] | SDS-THM4 | mg/L | 196.2142 | NA | NA | 194.6038 | NA | 203.9037 |  |  |  |  | 198.2406 | 2.5071 | SDS-THM4 | mg/L | 196.2142 | NA | NA | 194.6038 | NA | 203.9037 |  |  |  |  | 198.2406 | 2.5071 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.18 | 21.9 | 3.6375 | 0.067925 | 1.8675 | 3.34 | 0.83 | 2.51 | 18.1 | 7.978 | 24.15 | 266.65 | 14.6 | 53.7104 | 34.9581 | 19.15 | 122.4185 | BMRL | 9.3284 | 8.7859 | BMRL | 11.7338 | 11.3357 | BMRL | 10.0145 | 12.8266 | 29.8481 | 41.1838 | Avg-C11-20 | Average | --- | --- | --- | --- | 7.885 | 20.95 | 3.945 | 0.076425 | 1.9373 | 3.435 | 0.745 | 2.69 | 19.4 | 7.9773 | 23.95 | 315.45 | 19.25 | 56.15 | 40.6627 | 17.85 | 133.9127 | BMRL | 10.8597 | 17.1843 | 1.239 | 13.0078 | 13.5732 | BMRL | 11.2503 | 18.4722 | 42.2909 | 55.8641
[11 empty] | SDS-MCAA* | mg/L | 3.3652 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 3.3652 | #DIV/0! | SDS-MCAA* | mg/L | 3.3652 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 3.3652 | #DIV/0! | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.2445 | 0 | 2.0619 | 0.36805 | 1.6938 | 1.1976 | 2.4096 | 0.79681 | 0 | 0.02302 | 0.41408 | 0.75005 | 6.8493 | 4.7568 | 6.5552 | 5.7441 | 5.6744 |  | 11.9651 | 20.3599 |  | 14.5811 | 10.0616 |  | 21.4994 | 22.242 | 15.4645 | 13.9774 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.38047 | 0.47733 | 0.76046 | 0.32712 | 0.43334 | 0.29112 | 1.3423 | 0.74349 | 0 | 0.064481 | 0.41754 | 3.9626 | 7.7922 | 5.8592 | 6.0985 | 5.042 | 6.1008 |  | 4.9792 | 8.397 | 2.5503 | 7.202 | 4.9885 |  | 5.2385 | 2.9788 | 6.8311 | 6.3834
[11 empty] | SDS-DCAA* | mg/L | 31.2947 | NA | NA | 31.5611 | NA | 27.3673 |  |  |  |  | 30.0744 | 7.8079 | SDS-DCAA* | mg/L | 31.2947 | NA | NA | 31.5611 | NA | 27.3673 |  |  |  |  | 30.0744 | 7.8079 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 37.6587 | NA | NA | 28.2762 | NA | 28.0579 |  |  |  |  | 31.331 | 17.4941 | SDS-TCAA* | mg/L | 37.6587 | NA | NA | 28.2762 | NA | 28.0579 |  |  |  |  | 31.331 | 17.4941 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 1.2202 | NA | NA | 1.1469 | NA | 1.182 |  |  |  |  | 1.1831 | 3.0983 | SDS-MBAA* | mg/L | 1.2202 | NA | NA | 1.1469 | NA | 1.182 |  |  |  |  | 1.1831 | 3.0983
[11 empty] | SDS-DBAA* | mg/L | 12.9954 | NA | NA | 11.1865 | NA | 9.659 |  |  |  |  | 11.2803 | 14.8059 | SDS-DBAA* | mg/L | 12.9954 | NA | NA | 11.1865 | NA | 9.659 |  |  |  |  | 11.2803 | 14.8059
[11 empty] | SDS-BCAA* | mg/L | 22.0233 | NA | NA | 21.2431 | NA | 18.5144 |  |  |  |  | 20.5936 | 8.9467 | SDS-BCAA* | mg/L | 22.0233 | NA | NA | 21.2431 | NA | 18.5144 |  |  |  |  | 20.5936 | 8.9467
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | 16.822 | NA | NA | 13.9623 | NA | 12.3663 |  |  |  |  | 14.3835 | 15.6949 | SDS-CDBAA | mg/L | 16.822 | NA | NA | 13.9623 | NA | 12.3663 |  |  |  |  | 14.3835 | 15.6949
[11 empty] | SDS-DCBAA | mg/L | 37.7847 | NA | NA | 32.9786 | NA | 30.8232 |  |  |  |  | 33.8622 | 10.5246 | SDS-DCBAA | mg/L | 37.7847 | NA | NA | 32.9786 | NA | 30.8232 |  |  |  |  | 33.8622 | 10.5246
[11 empty] | SDS-HAA5 | mg/L | 86.5342 | NA | NA | 72.1708 | NA | 66.2662 |  |  |  |  | 74.9904 | 13.9005 | SDS-HAA5 | mg/L | 86.5342 | NA | NA | 72.1708 | NA | 66.2662 |  |  |  |  | 74.9904 | 13.9005
[11 empty] | SDS-HAA6 | mg/L | 108.5575 | NA | NA | 93.4139 | NA | 84.7806 |  |  |  |  | 95.584 | 12.5922 | SDS-HAA6 | mg/L | 108.5575 | NA | NA | 93.4139 | NA | 84.7806 |  |  |  |  | 95.584 | 12.5922
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on A1: S&H comment: 1. Seasonal variability was evaluated over three quarters – spring, summer and fall. During the fall, two sessions were conducted: one to evaluate conventional treatment prior to GAC and one to evaluate enhanced coagulation prior to GAC. 2. During the spring and fall (conventional treatment) sessions, influent water to the treatment study was sampled after full-scale sand filtration. During summer, pre-chlorination could not be turned off and the raw plant source water was sampled and batch treated in the lab to simulate full-scale treatment. During the fall (enhanced coagulation) session, the raw plant source water was sampled and batch treated in the lab to simulate enhanced coagulation. 3. During the spring session, SDS-TCAA occurred at higher concentration than observed during the other three sessions. This may be related to the slightly lower feed bromide concentrations observed during the spring session 4. During the summer session, batch pretreatment resulted in 27% TOC removal. However, the target TOC removal for conventional treatment was 11%. Thus, TOC removal during the summer session more closely matched enhanced coagulation conditions rather than conventional treatment. However, the TOC, UV-254 and influent pH were significantly lower during the enhanced coagulation fall session compared to the summer session. 5. For the analysis of UV-254, TOC and TOX, values below the MRL of 0.009 1/cm, 0.50 mg/L and 25ug/L as Cl-, respectively, have been reported and should be considered estimates.
Note on H22: Reviewer M.H. (11/13/99): Per Consultant: "Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS".
Note on N6: Reviewer M.H. (11/13/99): Per Consultant: "Ammonia feed was on as noted in cell N6 of the DCS. The chlorine demand would be lower if the ammonia feed were off".

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Sweetwater Authority | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 5.4 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-08-17 | [12 empty] | 20-min. EBCT Start Date | 1998-08-17 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA3710025 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 12.6 | mesh size | (mm) | Coagulation | 16 mg/L ferric chloride; 1.9 mg/L polymer | Bench-Scale | 10-min. EBCT Start Time | 14:25 | [12 empty] | 20-min. EBCT Start Time | 14:25 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1253 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.6 | 4 | 4.75 | Flocculation | 2-Stage tapered | Bench-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 26 | 6 | 3.35 | Sedimentation | 60 minutes | Bench-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-08-17 | 18:46 | 4.35 | 138.591 | 8.28 | 23.4 | 0.265 | 0.0011 | 0.41509 | 1.15 | 0.73 | 0.42 | 25.2 | 7.9382 | 24.1 | 4.15 | BMRL | BMRL | BMRL | 2.1 | 2.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | C1-20 | N | 1998-08-17 | 18:14 | 3.8167 | 121.599 | 8.85 | 23.5 | 0.215 | 0.00295 | 1.3721 | 1.25 | 0.86 | 0.39 | 25.2 | 7.9615 | 24.2 | 8.9 | BMRL | 1.1044 | BMRL | 1.8516 | 2.9559 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | Avg-C2-10 | Y | 1998-08-19 | 08:53 | 42.4667 | 1352.988 | 8.025 | 22.4 | 0.56 | 0.00395 | 0.70536 | 1.39 | 0.655 | 0.735 | 25.1 | 8.0347 | 23.7 | 20.375 | BMRL | 5.4596 | BMRL | 14.1892 | 19.6488 | BMRL | BMRL | BMRL | BMRL | 3.1769 | BMRL | BMRL | BMRL | BMRL | 3.1769 | 3.1769 | C2-20 | N | 1998-08-21 | 22:17 | 103.8667 | 3309.192 | 8.11 | 22.8 | 0.505 | 0.0036 | 0.71287 | 1.4 | 0.66 | 0.74 | 25.1 | 8.0499 | 23.4 | 17.15 | BMRL | 3.8883 | BMRL | 11.3051 | 15.1934 | BMRL | BMRL | BMRL | BMRL | 2.957 | BMRL | BMRL | BMRL | BMRL | 2.957 | 2.957 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.481 | 10 | 2 |  |  |  | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-28 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-28 | [7 empty] | --- | --- |  | C3-10 | N | 1998-08-19 | 15:04 | 48.65 | 1549.989 | 8.08 | 22.7 | 0.805 | 0.00815 | 1.0124 | 1.55 | 0.67 | 0.88 | 25.1 | 8.0795 | 23.7 | 36.3 | BMRL | 10.4273 | 1.5608 | 25.0172 | 37.0053 | BMRL | BMRL | BMRL | BMRL | 4.5675 | 1.4895 | BMRL | BMRL | BMRL | 4.5675 | 6.0569 | Avg-C3-20 | Y | 1998-08-22 | 23:31 | 129.1 | 4113.126 | 8.06 | 22.7 | 0.865 | 0.008525 | 0.98555 | 1.67 | 0.675 | 0.995 | 25.1 | 8.0849 | 23.45 | 34.2 | BMRL | 9.8923 | 1.5798 | 22.226 | 33.698 | BMRL | BMRL | BMRL | BMRL | 4.784 | 1.4943 | BMRL | BMRL | BMRL | 4.784 | 6.2783 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 60 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 16:20 | 10:45 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 16:20 | 10:45 | [7 empty] | --- | --- |  | C4-10 | N | 1998-08-19 | 21:07 | 54.7 | 1742.742 | 8.09 | 22.4 | 1.05 | 0.0124 | 1.181 | 1.73 | 0.63 | 1.1 | 25.1 | 8.0647 | 23.8 | 50.3 | BMRL | 16.877 | 2.9519 | 33.3091 | 53.138 | BMRL | BMRL | BMRL | BMRL | 6.6689 | 2.2796 | BMRL | 2.1885 | 1.4519 | 6.6689 | 8.9485 | C4-20 | N | 1998-08-23 | 12:24 | 141.9833 | 4523.589 | 8.06 | 23.4 | 1.14 | 0.01195 | 1.0482 | 1.86 | 0.76 | 1.1 | 25.1 | 8.0195 | 23.4 | 48.1 | BMRL | 16.5385 | 3.2903 | 32.1 | 51.9288 | BMRL | BMRL | BMRL | BMRL | 6.6408 | 2.2061 | BMRL | 2.2039 | 1.4671 | 6.6408 | 8.8469 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 100 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 1.9167 | 260.3333 | [7 empty] | --- | --- |  | Operation time | hh.hh | 1.9167 | 260.3333 | [7 empty] | --- | --- |  | C5-10 | N | 1998-08-20 | 03:15 | 60.8333 | 1938.15 | 8.07 | 22.4 | 1.37 | 0.017 | 1.2409 | 1.95 | 0.67 | 1.28 | 25.1 | 8.0595 | 23.8 | 74.3 | BMRL | 26.4043 | 5.4033 | 44.2689 | 76.0765 | BMRL | BMRL | BMRL | BMRL | 8.8847 | 3.1993 | BMRL | 2.5211 | 1.6306 | 8.8847 | 12.0839 | C5-20 | N | 1998-08-24 | 01:15 | 154.8333 | 4932.99 | 8.07 | 22.4 | 1.49 | 0.01725 | 1.1577 | 2.11 | 0.82 | 1.29 | 25.1 | 8.0547 | 23.4 | 69.6 | BMRL | 22.1877 | 4.8936 | 33.3 | 60.3813 | BMRL | BMRL | BMRL | BMRL | 8.5517 | 3.2197 | BMRL | 2.8121 | 1.7034 | 8.5517 | 11.7714 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 61.065 | 8294.22 | [7 empty] | --- | --- |  | Bed volumes | (20 minutes) | 30.5325 | 4147.11 | [7 empty] | --- | --- |  | C6-10 | N | 1998-08-20 | 09:29 | 67.0667 | 2136.744 | 7.94 | 22.6 | 1.665 | 0.02195 | 1.3183 | 2.16 | 0.64 | 1.52 | 25.1 | 8.0395 | 23.8 | 92.2 | 1.4619 | 38.3847 | 9.3359 | 54.3389 | 103.5213 | BMRL | 1.2377 | BMRL | BMRL | 10.0738 | 4.0366 | BMRL | 3.0704 | 1.8703 | 11.3115 | 15.3482 | C6-20 | N | 1998-08-24 | 19:09 | 172.7333 | 5503.284 | 8.09 | 23.1 | 1.76 | 0.02145 | 1.2188 | 2.31 | 0.7 | 1.61 | 25.8 | 8.0782 | 24 | 88.25 | 1.1276 | 29.3875 | 7.6885 | 37.6 | 75.8036 | BMRL | 1.2486 | BMRL | BMRL | 9.6471 | 4.0371 | BMRL | 2.9247 | 1.8306 | 10.8957 | 14.9328 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 132 | 119 | [7 empty] | 125.5 | 7.3246 |  | Alkalinity | mg/L as CaCO3 | 132 | 119 | [7 empty] | 125.5 | 7.3246 |  | Avg-C7-10 | Y | 1998-08-20 | 22:04 | 79.65 | 2537.649 | 8.065 | 22.3 | 2.0325 | 0.029225 | 1.4379 | 2.41 | 0.655 | 1.755 | 25.1 | 8.0623 | 23.85 | 125.825 | 2.3859 | 47.2197 | 13.8231 | 51.4718 | 114.9005 | BMRL | 1.7189 | 1.047 | BMRL | 10.6767 | 5.1465 | BMRL | 3.8634 | 2.3712 | 13.4425 | 18.589 | Avg-C7-20 | Y | 1998-08-26 | 03:14 | 204.8167 | 6525.459 | 7.915 | 22 | 2.135 | 0.028325 | 1.3267 | 2.57 | 0.775 | 1.795 | 25 | 8.0321 | 23.95 | 122.7 | 2.5501 | 41.3791 | 13.7174 | 42.25 | 99.8965 | BMRL | 1.8447 | 1.0655 | BMRL | 10.4855 | 5.6098 | 4.4859 | 4.4058 | 2.5915 | 13.3957 | 19.0055 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2422.9689 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 237 | 246 | [7 empty] | 241.5 | 2.6352 |  | Total hardness | mg/L as CaCO3 | 237 | 246 | [7 empty] | 241.5 | 2.6352 |  | C8-10 | N | 1998-08-21 | 10:58 | 92.55 | 2948.643 | 7.97 | 22.5 | 2.475 | 0.0366 | 1.4788 | 2.72 | 0.71 | 2.01 | 25.1 | 8.059 | 23.9 | 160.7 | 4.4939 | 62.5936 | 21.6399 | 51.7556 | 140.483 | BMRL | 2.7454 | 1.3079 | BMRL | 12.6449 | 7.1711 | 4.1564 | 4.4979 | 3.1168 | 16.6981 | 23.8693 | C8-20 | N | 1998-08-26 | 22:44 | 224.3167 | 7146.729 | 8.04 | 21.4 | 2.355 | 0.0312 | 1.3248 | 2.73 | 0.8 | 1.93 | 25.1 | 8.0895 | 24 | 127.15 | 3.3162 | 45.9861 | 17.0332 | 45.7 | 112.0354 | BMRL | 2.0206 | 1.1604 | BMRL | 11.6533 | 6.1088 | 4.2125 | 4.6049 | 2.6932 | 14.8344 | 20.9431 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 4845.9378 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 130 | 135 | [7 empty] | 132.5 | 2.6683 |  | Calcium hardness | mg/L as CaCO3 | 130 | 135 | [7 empty] | 132.5 | 2.6683 |  | C9-10 | N | 1998-08-22 | 05:43 | 111.3 | 3546.018 | 8.03 | 22.1 | 2.875 | 0.0447 | 1.5548 | 3.1 | 0.69 | 2.41 | 25.8 | 8.0395 | 23.9 | 194.25 | 8.0453 | 56.6296 | 28.723 | 38.6 | 131.9978 | BMRL | 3.861 | 1.7938 | BMRL | 12.5536 | 8.5342 | BMRL | 5.2074 | 3.9229 | 18.2085 | 26.7427 | C9-20 | N | 1998-08-28 | 19:35 | 269.1667 | 8575.65 | 8.1 | 22.2 | 2.785 | 0.04065 | 1.4596 | 3.03 | 0.72 | 2.31 | 25.1 | 8.1099 | 24 | 179.2 | 6.5505 | 56.2647 | 26.0689 | 43.2 | 132.0841 | BMRL | 3.5346 | 1.7359 | BMRL | 14.3677 | 8.9512 | 4.8993 | 6.4964 | 4.4606 | 19.6383 | 28.5895 | Electric Rate ($/kW-h) | 0.087
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 6299.7191 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | [7 empty] | BMRL |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | [7 empty] | BMRL |  |  | Avg-C10-10 | Y | 1998-08-22 | 18:18 | 123.8833 | 3946.923 | 8.115 | 23.8 | 3.09 | 0.050925 | 1.6481 | 3.26 | 0.75 | 2.51 | 25.1 | 8.0825 | 23.35 | 213.925 | 11.776 | 74.6232 | 38.5035 | 41.45 | 166.3527 | BMRL | 5.0948 | 2.3366 | BMRL | 14.1058 | 10.4587 | BMRL | 6.227 | 4.9198 | 21.5373 | 31.9959 | C10-20 | N | 1998-08-29 | 20:16 | 293.85 | 9362.061 | 8.07 | 21.7 | 3.125 | 0.04715 | 1.5088 | 3.26 | 0.73 | 2.53 | 25.1 | 8.1047 | 24 | 202.1 | 9.8394 | 62.7772 | 33.027 | 40.4 | 146.0436 | BMRL | 4.5325 | 2.1464 | BMRL | 14.289 | 10.381 | 4.5274 | 7.0648 | 5.1645 | 20.9678 | 31.3488 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 260 | 290 | [7 empty] | 275 | 7.7139 |  | Bromide | mg/L | 260 | 290 | [7 empty] | 275 | 7.7139 |  | C11-10 | N | 1998-08-23 | 19:05 | 148.6667 | 4736.52 | 8.05 | 24 | 3.52 | 0.05855 | 1.6634 | 3.55 | 0.81 | 2.74 | 25.8 | 8.0736 | 24 | 247.75 | 16.2594 | 65.1893 | 41.5943 | 33.8 | 156.843 | BMRL | 6.2224 | 2.7798 | BMRL | 12.6861 | 10.9771 | BMRL | 5.6295 | 5.4619 | 21.6883 | 32.6655 | Avg-C11-20 | Y | 1998-09-03 | 02:11 | 395.7667 | 12609.126 | 7.925 | 20.9 | 3.5625 | 0.057575 | 1.6161 | 3.58 | 0.885 | 2.695 | 26.2 | 8.0609 | 24.05 | 250.85 | 17.4015 | 74.3007 | 43.6111 | 32.65 | 167.9633 | BMRL | 6.4597 | 3.0424 | BMRL | 14.4958 | 12.2335 | 4.2287 | 7.5021 | 7.7148 | 23.9979 | 36.2314 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-08-27 | 04:06 | 229.6833 | 7317.711 | 8.05 | 21.1 | 3.835 | 0.0713 | 1.8592 | 3.77 | 0.78 | 2.99 | 25 | 8.0436 | 23.8 | 278.1 | 25.9912 | 65.8635 | 50.0818 | 25.8 | 167.7365 | BMRL | 9.5325 | 4.7173 | BMRL | 14.4731 | 14.7472 | BMRL | 7.6502 | 9.342 | 28.7229 | 43.47 | C12-20 | N | 1998-09-06 | 12:58 | 478.55 | 15246.603 | 8.09 | 22.9 | 3.895 | 0.06795 | 1.7445 | 3.81 | 0.85 | 2.96 | 26 | 7.9895 | 24 | 294.6 | 26.6085 | 79.7166 | 53.8967 | 27.7 | 187.9219 | BMRL | 9.2504 | 4.3325 | BMRL | 14.37 | 13.9503 | 4.0595 | 7.9266 | 9.54 | 27.9528 | 41.9031 | Current Process Water Rate ($/1000 gal) | 0.196
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 8.8923e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-08-30 | 01:04 | 298.65 | 9514.989 | 8.04 | 21.5 | 4.26 | NA | NR | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C13-20 | N | 1998-09-09 | 09:37 | 547.2 | 17433.792 | 7.92 | 21.4 | 3.985 | 0.07065 | 1.7729 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.2 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD
|  |  |  | Scaling factor, SF | 5.31 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-19 | 1998-08-23 | 1998-08-28 | 1998-08-31 | 1998-09-07 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-08-17 | 1998-08-19 | 1998-08-23 | 1998-08-28 | 1998-08-31 | 1998-09-07 |  |  |  |  | --- | ---
Plant Name | Robert A. Perdue Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 4.3216 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:20 | 09:12 | 12:35 | 10:40 | 12:25 | 15:45 |  |  |  |  | --- | --- | Sampling time | hh:mm | 16:20 | 09:12 | 12:35 | 10:40 | 12:25 | 15:45 |  |  |  |  | --- | ---
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 8.9811 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1.9167 | 42.7833 | 142.1667 | 260.25 | 334 | 505.3333 |  |  |  |  | --- | --- | Operation time | hh.hh | 1.9167 | 42.7833 | 142.1667 | 260.25 | 334 | 505.3333 |  |  |  |  | --- | ---
Process Train Name | Perdue Treatment Plant |  |  | Estimated total influent volume required, VSCT (L) | 319.6508 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 61.065 | 1363.077 | 4529.43 | 8291.565 | 10641.24 | 16099.92 |  |  |  |  | --- | --- | Bed volumes | (20 minute) | 30.5325 | 681.5385 | 2264.715 | 4145.7825 | 5320.62 | 8049.96 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 221 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.56 | 7.38 | 7.41 | 7.39 | 7.38 | 7.44 |  |  |  |  | 7.4267 | 0.93159 | pH | --- | 7.56 | 7.38 | 7.41 | 7.39 | 7.38 | 7.44 |  |  |  |  | 7.4267 | 0.93159 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.1 | NA | NA | 0.2 | NA | 0.15 |  |  |  |  | 0.15 | 33.3333 | Turbidity | ntu | 0.1 | NA | NA | 0.2 | NA | 0.15 |  |  |  |  | 0.15 | 33.3333 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 22.4 | 18.4 | 19.7 | 16.3 | 19.3 | 19.6 |  |  |  |  | 19.2833 | 10.2853 | Temperature | oC | 22.4 | 18.4 | 19.7 | 16.3 | 19.3 | 19.6 |  |  |  |  | 19.2833 | 10.2853
Historical Average Water Temperature (oC) | 22 |  |  | Estimated full-scale run time, tLCT (days) | 43.748 | [5 empty] | Total organic carbon | mg/L | 5.4 | 5.4 | 5.18 | 5.1 | 5.305 | 5.18 |  |  |  |  | 5.2608 | 2.3987 | Total organic carbon | mg/L | 5.4 | 5.4 | 5.18 | 5.1 | 5.305 | 5.18 |  |  |  |  | 5.2608 | 2.3987 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 30 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.8832 | [5 empty] | UV254 | cm-1 | 0.1181 | NA | NA | 0.11875 | NA | 0.11965 |  |  |  |  | 0.11883 | 0.655 | UV254 | cm-1 | 0.1181 | NA | NA | 0.11875 | NA | 0.11965 |  |  |  |  | 0.11883 | 0.655 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.2388 | [5 empty] | SUVA | L/(mg*m) | 2.187 | NR | NR | 2.3284 | NR | 2.3098 |  |  |  |  | 2.2751 | 3.3771 | SUVA | L/(mg*m) | 2.187 | NR | NR | 2.3284 | NR | 2.3098 |  |  |  |  | 2.2751 | 3.3771 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.5645 | [5 empty] | SDS-Cl2 dose | mg/L | 5.25 | NA | NA | 5.25 | NA | 5.25 |  |  |  |  | 5.25 | 0 | SDS-Cl2 dose | mg/L | 5.25 | NA | NA | 5.25 | NA | 5.25 |  |  |  |  | 5.25 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 106.5503 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.73 | NA | NA | 0.69 | NA | 0.55 |  |  |  |  | 0.65667 | 14.3933 | SDS-Free Cl2 residual | mg/L | 0.73 | NA | NA | 0.69 | NA | 0.55 |  |  |  |  | 0.65667 | 14.3933 | C2-10 | Primary | 1998-08-19 | 08:53 | 42.4667 | 1352.988 | 7.99 | 22.4 | 0.55 | 0.00385 | 0.7 | 1.39 | 0.66 | 0.73 | 25.1 | 8.0099 | 23.7 | 20.4 | BMRL | 5.4267 | BMRL | 13.9573 | 19.384 | BMRL | BMRL | BMRL | BMRL | 3.0242 | BMRL | BMRL | BMRL | BMRL | 3.0242 | 3.0242 | C3-20 | Primary | 1998-08-22 | 23:31 | 129.1 | 4113.126 | 8.06 | 22.7 | 0.85 | 0.0085 | 1 | 1.67 | 0.63 | 1.04 | 25.1 | 8.085 | 23.5 | 35.15 | BMRL | 10.3221 | 1.5761 | 22.352 | 34.2502 | BMRL | BMRL | BMRL | BMRL | 5.1811 | 1.6112 | BMRL | BMRL | BMRL | 5.1811 | 6.7923
|  |  |  | Mass GAC required, mSC (g) | 8.1354 | [5 empty] | SDS-Cl2 demand | mg/L | 4.52 | NR | NR | 4.56 | NR | 4.7 |  |  |  |  | 4.5933 | 2.0577 | SDS-Cl2 demand | mg/L | 4.52 | NR | NR | 4.56 | NR | 4.7 |  |  |  |  | 4.5933 | 2.0577 | D-C2-10 | Duplicate | 1998-08-19 | 08:53 | 42.4667 | 1352.988 | 8.06 | 22.4 | 0.57 | 0.00405 | 0.71053 | 1.39 | 0.65 | 0.74 | 25.1 | 8.0595 | 23.7 | 20.35 | BMRL | 5.4926 | BMRL | 14.4211 | 19.9137 | BMRL | BMRL | BMRL | BMRL | 3.3297 | BMRL | BMRL | BMRL | BMRL | 3.3297 | 3.3297 | D-C3-10 | Duplicate | 1998-08-22 | 23:31 | 129.1 | 4113.126 | 8.06 | 22.7 | 0.88 | 0.00855 | 0.97159 | 1.67 | 0.72 | 0.95 | 25.1 | 8.0847 | 23.4 | 33.25 | BMRL | 9.4625 | 1.5834 | 22.1 | 33.1459 | BMRL | BMRL | BMRL | BMRL | 4.3869 | 1.3775 | BMRL | BMRL | BMRL | 4.3869 | 5.7643
[11 empty] | SDS-Chlorination temp. | oC | 25.2 | NA | NA | 25.1 | NA | 26 |  |  |  |  | 25.4333 | 1.9395 | SDS-Chlorination temp. | oC | 25.2 | NA | NA | 25.1 | NA | 26 |  |  |  |  | 25.4333 | 1.9395 | Avg-C2-10 | Average | --- | --- | --- | --- | 8.025 | 22.4 | 0.56 | 0.00395 | 0.70526 | 1.39 | 0.655 | 0.735 | 25.1 | 8.0347 | 23.7 | 20.375 | BMRL | 5.4596 | BMRL | 14.1892 | 19.6488 | BMRL | BMRL | BMRL | BMRL | 3.1769 | BMRL | BMRL | BMRL | BMRL | 3.1769 | 3.1769 | Avg-C3-20 | Average | --- | --- | --- | --- | 8.06 | 22.7 | 0.865 | 0.008525 | 0.9858 | 1.67 | 0.675 | 0.995 | 25.1 | 8.0849 | 23.45 | 34.2 | BMRL | 9.8923 | 1.5798 | 22.226 | 33.698 | BMRL | BMRL | BMRL | BMRL | 4.784 | 1.4943 | BMRL | BMRL | BMRL | 4.784 | 6.2783
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.915 | NA | NA | 7.9447 | NA | 7.915 |  |  |  |  | 7.9249 | 0.21688 | SDS-Chlorination pH | --- | 7.915 | NA | NA | 7.9447 | NA | 7.915 |  |  |  |  | 7.9249 | 0.21688 | RPD-C2-10 | RPD | --- | --- | --- | --- | 0.87227 | 0 | 3.5714 | 5.0633 | 1.4925 | 0 | 1.5267 | 1.3605 | 0 | 0.618 | 0 | 0.2454 |  | 1.2065 |  | 3.2693 | 2.6961 |  |  |  |  | 9.6167 |  |  |  |  | 9.6167 | 9.6167 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0 | 0 | 3.4682 | 0.58651 | 2.8818 | 0 | 13.3333 | 9.0452 | 0 | 0.0028474 | 0.42644 | 5.5556 |  | 8.6895 | 0.45838 | 1.1337 | 3.2771 |  |  |  |  | 16.6031 | 15.6381 |  |  |  | 16.6031 | 16.3735
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 24.2 | NA | NA | 24 | NA | 24 |  |  |  |  | 24.0667 | 0.47979 | SDS-Incubation time | hours | 24.2 | NA | NA | 24 | NA | 24 |  |  |  |  | 24.0667 | 0.47979 | C7-10 | Primary | 1998-08-20 | 22:04 | 79.65 | 2537.649 | 8.03 | 22.3 | 2.035 | 0.0293 | 1.4398 | 2.41 | 0.73 | 1.68 | 25.1 | 8.0299 | 23.8 | 128.45 | 2.5333 | 49.0198 | 14.5328 | 53.7455 | 119.8314 | BMRL | 1.8908 | 1.0731 | BMRL | 11.4961 | 5.5982 | BMRL | 3.941 | 2.4366 | 14.46 | 20.0582 | C7-20 | Primary | 1998-08-26 | 03:14 | 204.8167 | 6525.459 | 7.89 | 22 | 2.16 | 0.0283 | 1.3102 | 2.57 | 0.75 | 1.82 | 25 | 8.0243 | 23.9 | 123.85 | 2.6811 | 41.6471 | 14.2784 | 43.5 | 102.1066 | BMRL | 1.821 | 1.0669 | BMRL | 9.6092 | 5.5128 | 4.438 | 4.4136 | 2.5557 | 12.4971 | 18.0098
|  |  |  | Estimated full-scale run time, tLCT (days) | 87.4961 | [5 empty] | SDS-TOX | mg Cl- /L | 445.15 | NA | NA | 457.85 | NA | 491.6 |  |  |  |  | 464.8667 | 5.1642 | SDS-TOX | mg Cl- /L | 445.15 | NA | NA | 457.85 | NA | 491.6 |  |  |  |  | 464.8667 | 5.1642 | D-C7-10 | Duplicate | 1998-08-20 | 22:04 | 79.65 | 2537.649 | 8.1 | 22.3 | 2.03 | 0.02915 | 1.436 | 2.41 | 0.58 | 1.83 | 25.1 | 8.0947 | 23.9 | 123.2 | 2.2385 | 45.4195 | 13.1135 | 49.1981 | 109.9696 | BMRL | 1.547 | 1.0209 | BMRL | 9.8573 | 4.6947 | BMRL | 3.7858 | 2.3058 | 12.4251 | 17.1198 | D-C7-20 | Duplicate | 1998-08-26 | 03:14 | 204.8167 | 6525.459 | 7.94 | 22 | 2.11 | 0.02835 | 1.3436 | 2.57 | 0.8 | 1.77 | 25 | 8.0399 | 24 | 121.55 | 2.4191 | 41.111 | 13.1564 | 41 | 97.6865 | BMRL | 1.8685 | 1.0641 | BMRL | 11.3618 | 5.7068 | 4.5339 | 4.398 | 2.6272 | 14.2943 | 20.0011
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 3.7665 | [5 empty] | SDS-CHCl3 | mg/L | 82.5485 | NA | NA | 66.9877 | NA | 74.4678 |  |  |  |  | 74.668 | 10.4226 | SDS-CHCl3 | mg/L | 82.5485 | NA | NA | 66.9877 | NA | 74.4678 |  |  |  |  | 74.668 | 10.4226 | Avg-C7-10 | Average | --- | --- | --- | --- | 8.065 | 22.3 | 2.0325 | 0.029225 | 1.4379 | 2.41 | 0.655 | 1.755 | 25.1 | 8.0623 | 23.85 | 125.825 | 2.3859 | 47.2197 | 13.8231 | 51.4718 | 114.9005 | BMRL | 1.7189 | 1.047 | BMRL | 10.6767 | 5.1465 | BMRL | 3.8634 | 2.3712 | 13.4425 | 18.589 | Avg-C7-20 | Average | --- | --- | --- | --- | 7.915 | 22 | 2.135 | 0.028325 | 1.3269 | 2.57 | 0.775 | 1.795 | 25 | 8.0321 | 23.95 | 122.7 | 2.5501 | 41.3791 | 13.7174 | 42.25 | 99.8965 | BMRL | 1.8447 | 1.0655 | BMRL | 10.4855 | 5.6098 | 4.4859 | 4.4058 | 2.5915 | 13.3957 | 19.0055
|  |  |  | Estimated RSSCT run time, tSCT (days) | 16.4776 | [5 empty] | SDS-BDCM | mg/L | 69.0892 | NA | NA | 67.9255 | NA | 69.9363 |  |  |  |  | 68.9837 | 1.4634 | SDS-BDCM | mg/L | 69.0892 | NA | NA | 67.9255 | NA | 69.9363 |  |  |  |  | 68.9837 | 1.4634 | RPD-C7-10 | RPD | --- | --- | --- | --- | 0.86795 | 0 | 0.246 | 0.51326 | 0.26726 | 0 | 22.9008 | 8.547 | 0 | 0.80444 | 0.41929 | 4.1725 | 12.3562 | 7.6246 | 10.2675 | 8.8346 | 8.5828 |  | 20.0028 | 4.9893 |  | 15.3491 | 17.5564 |  | 4.0168 | 5.5187 | 15.1373 | 15.807 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.63171 | 0 | 2.3419 | 0.17652 | 2.5184 | 0 | 6.4516 | 2.7855 | 0 | 0.19427 | 0.41754 | 1.8745 | 10.2746 | 1.2956 | 8.1795 | 5.9172 | 4.4247 |  | 2.5712 | 0.26457 |  | 16.715 | 3.4585 | 2.1386 | 0.35417 | 2.7561 | 13.4167 | 10.4774
|  |  |  | RSSCT bed length, lSC (cm) | 27.1289 | [5 empty] | SDS-DBCM | mg/L | 92.4124 | NA | NA | 77.0469 | NA | 85.4609 |  |  |  |  | 84.9734 | 9.055 | SDS-DBCM | mg/L | 92.4124 | NA | NA | 77.0469 | NA | 85.4609 |  |  |  |  | 84.9734 | 9.055 | C10-10 | Primary | 1998-08-22 | 18:18 | 123.8833 | 3946.923 | 8.15 | 23.8 | 3.09 | 0.05105 | 1.6521 | 3.26 | 0.75 | 2.51 | 25.1 | 8.09 | 23.3 | 215.4 | 10.9923 | 71.8491 | 36.3528 | 39.3 | 158.4941 | BMRL | 4.7009 | 2.0889 | BMRL | 13.1019 | 9.7629 | BMRL | 6.1651 | 5.0041 | 19.8917 | 29.6546 | C11-20 | Primary | 1998-09-03 | 02:11 | 395.7667 | 12609.126 | 7.9 | 20.9 | 3.555 | 0.05735 | 1.6132 | 3.58 | 0.84 | 2.74 | 26.2 | 8.0736 | 24 | 248.2 | 17.383 | 74.612 | 43.0806 | 32.4 | 167.4756 | BMRL | 6.5699 | 3.3097 | BMRL | 15.4076 | 12.4904 | 4.4105 | 8.2834 | 8.6027 | 25.2872 | 37.7776
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 213.1005 | [5 empty] | SDS-CHBr3 | mg/L | 12.8 | NA | NA | 12.9 | NA | 12.5 |  |  |  |  | 12.7333 | 1.6348 | SDS-CHBr3 | mg/L | 12.8 | NA | NA | 12.9 | NA | 12.5 |  |  |  |  | 12.7333 | 1.6348 | D-C10-10 | Duplicate | 1998-08-22 | 18:18 | 123.8833 | 3946.923 | 8.08 | 23.8 | 3.09 | 0.0508 | 1.644 | 3.26 | 0.75 | 2.51 | 25.1 | 8.075 | 23.4 | 212.45 | 12.5597 | 77.3973 | 40.6542 | 43.6 | 174.2113 | BMRL | 5.4888 | 2.5842 | BMRL | 15.1098 | 11.1545 | BMRL | 6.289 | 4.8355 | 23.1828 | 34.3373 | D-C11-20 | Duplicate | 1998-09-03 | 02:11 | 395.7667 | 12609.126 | 7.95 | 20.9 | 3.57 | 0.0578 | 1.619 | 3.58 | 0.93 | 2.65 | 26.2 | 8.0482 | 24.1 | 253.5 | 17.4199 | 73.9894 | 44.1417 | 32.9 | 168.451 | BMRL | 6.3495 | 2.7751 | BMRL | 13.5839 | 11.9766 | 4.0468 | 6.7208 | 6.8269 | 22.7085 | 34.6851
|  |  |  | Mass GAC required, mSC (g) | 16.2708 | [5 empty] | SDS-THM4 | mg/L | 256.8501 | NA | NA | 224.8601 | NA | 242.365 |  |  |  |  | 241.3584 | 6.6369 | SDS-THM4 | mg/L | 256.8501 | NA | NA | 224.8601 | NA | 242.365 |  |  |  |  | 241.3584 | 6.6369 | Avg-C10-10 | Average | --- | --- | --- | --- | 8.115 | 23.8 | 3.09 | 0.050925 | 1.6481 | 3.26 | 0.75 | 2.51 | 25.1 | 8.0825 | 23.35 | 213.925 | 11.776 | 74.6232 | 38.5035 | 41.45 | 166.3527 | BMRL | 5.0948 | 2.3366 | BMRL | 14.1058 | 10.4587 | BMRL | 6.227 | 4.9198 | 21.5373 | 31.9959 | Avg-C11-20 | Average | --- | --- | --- | --- | 7.925 | 20.9 | 3.5625 | 0.057575 | 1.6161 | 3.58 | 0.885 | 2.695 | 26.2 | 8.0609 | 24.05 | 250.85 | 17.4015 | 74.3007 | 43.6111 | 32.65 | 167.9633 | BMRL | 6.4597 | 3.0424 | BMRL | 14.4958 | 12.2335 | 4.2287 | 7.5021 | 7.7148 | 23.9979 | 36.2314
[11 empty] | SDS-MCAA* | mg/L | 3.7535 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 3.7535 | #DIV/0! | SDS-MCAA* | mg/L | 3.7535 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 3.7535 | #DIV/0! | RPD-C10-10 | RPD | --- | --- | --- | --- | 0.8626 | 0 | 0 | 0.49092 | 0.49092 | 0 | 0 | 0 | 0 | 0.18594 | 0.42827 | 1.379 | 13.3105 | 7.435 | 11.1717 | 10.3739 | 9.4481 |  | 15.464 | 21.1981 |  | 14.2348 | 13.306 |  | 1.9907 | 3.4271 | 15.281 | 14.6354 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.63091 | 0 | 0.42105 | 0.78159 | 0.36054 | 0 | 10.1695 | 3.3395 | 0 | 0.31548 | 0.4158 | 2.1128 | 0.21182 | 0.83792 | 2.4332 | 1.5314 | 0.58072 |  | 3.413 | 17.5726 |  | 12.5805 | 4.2004 | 8.6016 | 20.8289 | 23.0191 | 10.7457 | 8.5357
[11 empty] | SDS-DCAA* | mg/L | 24.1855 | NA | NA | 21.0424 | NA | 20.8822 |  |  |  |  | 22.0367 | 8.4525 | SDS-DCAA* | mg/L | 24.1855 | NA | NA | 21.0424 | NA | 20.8822 |  |  |  |  | 22.0367 | 8.4525 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 14.8566 | NA | NA | 10.4008 | NA | 9.2164 |  |  |  |  | 11.4913 | 25.8805 | SDS-TCAA* | mg/L | 14.8566 | NA | NA | 10.4008 | NA | 9.2164 |  |  |  |  | 11.4913 | 25.8805 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 2.6818 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 2.6818 | #DIV/0! | SDS-MBAA* | mg/L | 2.6818 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 2.6818 | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 13.0798 | NA | NA | 10.8588 | NA | 10.3644 |  |  |  |  | 11.4343 | 12.6488 | SDS-DBAA* | mg/L | 13.0798 | NA | NA | 10.8588 | NA | 10.3644 |  |  |  |  | 11.4343 | 12.6488
[11 empty] | SDS-BCAA* | mg/L | 22.9489 | NA | NA | 19.7377 | NA | 18.8232 |  |  |  |  | 20.5033 | 10.5679 | SDS-BCAA* | mg/L | 22.9489 | NA | NA | 19.7377 | NA | 18.8232 |  |  |  |  | 20.5033 | 10.5679
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | 9.5612 | NA | NA | 7.51 | NA | 6.4562 |  |  |  |  | 7.8424 | 20.1338 | SDS-CDBAA | mg/L | 9.5612 | NA | NA | 7.51 | NA | 6.4562 |  |  |  |  | 7.8424 | 20.1338
[11 empty] | SDS-DCBAA | mg/L | 18.7753 | NA | NA | 14.5473 | NA | 13.7461 |  |  |  |  | 15.6896 | 17.2229 | SDS-DCBAA | mg/L | 18.7753 | NA | NA | 14.5473 | NA | 13.7461 |  |  |  |  | 15.6896 | 17.2229
[11 empty] | SDS-HAA5 | mg/L | 58.5573 | NA | NA | 42.302 | NA | 40.4631 |  |  |  |  | 47.1075 | 21.1397 | SDS-HAA5 | mg/L | 58.5573 | NA | NA | 42.302 | NA | 40.4631 |  |  |  |  | 47.1075 | 21.1397
[11 empty] | SDS-HAA6 | mg/L | 81.5062 | NA | NA | 62.0397 | NA | 59.2863 |  |  |  |  | 67.6107 | 17.9148 | SDS-HAA6 | mg/L | 81.5062 | NA | NA | 62.0397 | NA | 59.2863 |  |  |  |  | 67.6107 | 17.9148
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H22: Reviewer M.H. (11/13/99): Per Consultant: "Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS".

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Sweetwater Authority | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 5.55 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-11-03 | [12 empty] | 20-min. EBCT Start Date | 1998-11-03 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA3710025 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 12.6 | mesh size | (mm) | Coagulation | 16 mg/L ferric chloride; 1.8 mg/L polymer | Full-Scale | 10-min. EBCT Start Time | 15:35 | [12 empty] | 20-min. EBCT Start Time | 15:45 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1253 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.6 | 4 | 4.75 | Flocculation | 2-Stage tapered | Full-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 24 | 6 | 3.35 | Sedimentation | 74.7 minutes | Full-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-11-03 | 18:25 | 2.8333 | 160.48 | 8.38 | 21.9 | 0.2 | 0.00055 | 0.275 | 1.55 | 0.7 | 0.85 | 23.5 | 7.9795 | 24.1 | 4.6 | BMRL | BMRL | BMRL | 1.8871 | 1.8871 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | C1-20 | N | 1998-11-03 | 18:23 | 2.6333 | 149.152 | 8.94 | 21.8 | 0.13 | 0.0006 | 0.46154 | 1.65 | 0.98 | 0.67 | 23.5 | 7.989 | 24.1 | 4.1 | BMRL | BMRL | BMRL | 1.5147 | 1.5147 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Filtration | Dual media (sand/anthracite) | Full-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-11-04 | 22:04 | 30.4833 | 1726.576 | 8.11 | 21.3 | 0.555 | 0.0041 | 0.73874 | 1.85 | 0.65 | 1.2 | 23.5 | 7.9647 | 24.1 | 19.65 | BMRL | 5.4885 | 1.0303 | 11 | 17.5188 | BMRL | BMRL | BMRL | BMRL | 3.0495 | BMRL | BMRL | BMRL | BMRL | 3.0495 | 3.0495 | C2-20 | N | 1998-11-06 | 09:22 | 65.6167 | 3716.528 | 8.02 | 21.2 | 0.415 | 0.00375 | 0.90361 | 1.74 | 0.76 | 0.98 | 23.6 | 7.9295 | 23.7 | 17.25 | BMRL | 4.1475 | BMRL | 8.359 | 12.5065 | BMRL | BMRL | BMRL | BMRL | 2.6834 | BMRL | BMRL | BMRL | BMRL | 2.6834 | 2.6834 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.467 | 10 | 2 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-10 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-10 | [7 empty] | --- | --- |  | C3-10 | N | 1998-11-05 | 04:51 | 37.2667 | 2110.784 | 8.1 | 21.3 | 0.865 | 0.00855 | 0.98844 | 2.05 | 0.73 | 1.32 | 23.6 | 7.9647 | 23.6 | 37.85 | BMRL | 10.7608 | 2.1142 | 19.55 | 32.425 | BMRL | 1.4221 | BMRL | BMRL | 6.5364 | 2.4359 | BMRL | BMRL | 1.1289 | 7.9585 | 10.3944 | C3-20 | N | 1998-11-07 | 01:56 | 82.1833 | 4654.864 | 8.04 | 21.1 | 0.77 | 0.0075 | 0.97403 | 1.98 | 0.78 | 1.2 | 23.6 | 7.9343 | 23.8 | 29.75 | BMRL | 10.4461 | 1.9734 | 20.3 | 32.7195 | BMRL | 1.5054 | BMRL | BMRL | 4.239 | 1.9288 | BMRL | BMRL | BMRL | 5.7445 | 7.6732 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 16:55 | 14:05 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 16:55 | 14:05 | [7 empty] | --- | --- |  | C4-10 | N | 1998-11-05 | 11:43 | 44.1333 | 2499.712 | 8.1 | 21.2 | 1.245 | 0.0141 | 1.1325 | 2.32 | 0.87 | 1.45 | 23.6 | 7.9299 | 23.7 | 62.15 | BMRL | 19.007 | 4.5822 | 27.8 | 51.3892 | BMRL | 2.3432 | BMRL | BMRL | 8.4136 | 3.6467 | 4.7122 | 2.3691 | 1.5777 | 10.7568 | 14.4035 | Avg-C4-20 | Y | 1998-11-07 | 11:52 | 92.1167 | 5217.488 | 8.035 | 21.4 | 1.115 | 0.01165 | 1.0448 | 2.23 | 0.85 | 1.38 | 23.6 | 7.9471 | 23.8 | 48.3 | BMRL | 13.5628 | 2.7271 | 23.05 | 39.3399 | BMRL | 1.2101 | BMRL | BMRL | 7.54 | 3.3689 | 4.15 | 2.26 | 1.2085 | 8.7502 | 12.1191 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 1.3333 | 166.5 | [7 empty] | --- | --- |  | Operation time | hh.hh | 1.1667 | 166.3333 | [7 empty] | --- | --- |  | Avg-C5-10 | Y | 1998-11-05 | 15:13 | 47.6333 | 2697.952 | 8.065 | 21.7 | 1.495 | 0.017475 | 1.1689 | 2.49 | 0.82 | 1.67 | 23.6 | 7.9471 | 23.7 | 76.875 | BMRL | 23.673 | 6.3469 | 29.9 | 59.9199 | BMRL | 3.2686 | BMRL | BMRL | 9.1646 | 4.4981 | 5.4847 | 2.7901 | 1.8449 | 12.4332 | 16.9313 | C5-20 | N | 1998-11-08 | 04:33 | 108.8 | 6162.432 | 8.02 | 21 | 1.51 | 0.0179 | 1.1854 | 2.43 | 0.81 | 1.62 | 23.6 | 7.9471 | 23.9 | 79.85 | BMRL | 23.1167 | 5.6693 | 30.8 | 59.586 | BMRL | 3.4635 | BMRL | BMRL | 10.1217 | 4.2305 | 4.814 | 2.7845 | 1.6779 | 13.5852 | 17.8156 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 75.52 | 9430.56 | [7 empty] | --- | --- |  | Bed volumes | (20 minutes) | 33.04 | 4710.56 | [7 empty] | --- | --- |  | C6-10 | N | 1998-11-05 | 22:09 | 54.5667 | 3090.656 | 8.13 | 21 | 1.845 | 0.0228 | 1.2358 | 2.73 | 0.77 | 1.96 | 23.6 | 7.9595 | 23.7 | 105.1 | 1.9061 | 34.6862 | 10.5868 | 38.4 | 85.5792 | BMRL | 5.1034 | BMRL | BMRL | 12.8333 | 6.8783 | 6.7624 | 4.2539 | 2.6989 | 17.9368 | 24.815 | C6-20 | N | 1998-11-08 | 20:55 | 125.1667 | 7089.44 | 8.1 | 21.2 | 1.91 | 0.02345 | 1.2277 | 2.69 | 0.77 | 1.92 | 23.6 | 7.9559 | 23.9 | 105.55 | 1.5344 | 33.968 | 9.9688 | 37.4 | 82.8712 | BMRL | 4.3655 | BMRL | BMRL | 11.1747 | 5.644 | 5.0462 | 3.6879 | 2.3483 | 15.5402 | 21.1842 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 141 | 135 | [7 empty] | 138 | 3.0744 |  | Alkalinity | mg/L as CaCO3 | 141 | 135 | [7 empty] | 138 | 3.0744 |  | C7-10 | N | 1998-11-06 | 05:07 | 61.5333 | 3485.248 | 8.12 | 21.1 | 2.235 | 0.02815 | 1.2595 | 2.99 | 0.82 | 2.17 | 23.6 | 7.9395 | 23.7 | 137 | 2.6692 | 39.0045 | 13.8755 | 34.9 | 90.4491 | BMRL | 6.9301 | 1.0756 | BMRL | 13.1583 | 8.9499 | 6.7688 | 4.9115 | 3.7561 | 21.164 | 30.1139 | Avg-C7-20 | Y | 1998-11-09 | 13:35 | 141.8333 | 8033.44 | 8.02 | 22.55 | 2.215 | 0.028275 | 1.2765 | 2.89 | 0.76 | 2.13 | 23.6 | 7.9843 | 23.9 | 137.625 | 2.3526 | 40.931 | 13.9109 | 40.05 | 97.2444 | BMRL | 4.4329 | 1.1 | BMRL | 14.6639 | 10.069 | 6.7374 | 5.0658 | 3.3619 | 20.1968 | 30.2659 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2338.1848 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 221 | 222 | [7 empty] | 221.5 | 0.31924 |  | Total hardness | mg/L as CaCO3 | 221 | 222 | [7 empty] | 221.5 | 0.31924 |  | Avg-C8-10 | Y | 1998-11-06 | 15:29 | 71.9 | 4072.416 | 8.03 | 21.7 | 2.6625 | 0.03425 | 1.2864 | 3.29 | 0.875 | 2.415 | 23.6 | 7.9471 | 23.7 | 169.925 | 4.4067 | 48.3048 | 20.1738 | 36.4 | 109.2853 | BMRL | 6.9299 | 2.2861 | BMRL | 16.0753 | 12.2168 | 7.9561 | 6.9117 | 5.6398 | 25.2913 | 37.5081 | C8-20 | N | 1998-11-10 | 13:09 | 165.4 | 9368.256 | 7.99 | 23.1 | 2.495 | 0.0334 | 1.3387 | 3.08 | 0.66 | 2.42 | 23.4 | 7.9527 | 24 | 165.95 | 3.3222 | 42.843 | 17.8231 | 37.9 | 101.8884 | BMRL | 4.3739 | 1.8905 | BMRL | 17.643 | 10.828 | 7.3307 | 6.2604 | 4.3019 | 23.9074 | 34.7354 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 4676.3696 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 120 | 123 | [7 empty] | 121.5 | 1.7459 |  | Calcium hardness | mg/L as CaCO3 | 120 | 123 | [7 empty] | 121.5 | 1.7459 |  | C9-10 | N | 1998-11-07 | 05:13 | 85.6333 | 4850.272 | 8.03 | 21.5 | 3.13 | 0.04165 | 1.3307 | 3.61 | 0.86 | 2.75 | 23.6 | 7.9395 | 23.7 | 202.6 | 7.0996 | 57.5492 | 27.5589 | 36 | 128.2077 | BMRL | 7.5223 | 4.5579 | BMRL | 16.8412 | 13.6403 | 7.9986 | 8.2237 | 7.8349 | 28.9214 | 42.5617 | C9-20 | N | 1998-11-12 | 06:06 | 206.35 | 11687.664 | 8.03 | 21.3 | 2.82 | 0.039 | 1.383 | 3.31 | 0.62 | 2.69 | 23.5 | 7.9495 | 24.2 | 191.25 | 5.1184 | 53.2708 | 22.6182 | 38.8 | 119.8074 | BMRL | 4.8127 | 6.0273 | BMRL | 15.4487 | 9.9415 | 5.7015 | 4.9767 | 4.6332 | 26.2888 | 36.2303 | Electric Rate ($/kW-h) | 0.087
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 6079.2805 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.09 | 0.1 | [7 empty] | 0.095 | 7.4432 |  | Ammonia | mg NH3-N / L | 0.09 | 0.1 | [7 empty] | 0.095 | 7.4432 |  | C10-10 | N | 1998-11-08 | 05:17 | 109.7 | 6213.408 | 8.01 | 21.4 | 3.43 | 0.0509 | 1.484 | 3.68 | 0.72 | 2.96 | 23.6 | 8.0095 | 23.9 | 244.15 | 10.5626 | 63.3334 | 34.9373 | 35.3 | 144.1333 | BMRL | 7.6335 | 7.4305 | BMRL | 16.6571 | 13.3537 | 6.7326 | 8.147 | 9.6158 | 31.7211 | 45.0748 | C10-20 | N | 1998-11-13 | 01:59 | 226.2333 | 12813.856 | 8.18 | 20.2 | 3.195 | 0.0455 | 1.4241 | 3.55 | 0.63 | 2.92 | 23.5 | 7.995 | 24.2 | 215.6 | 7.6061 | 60.9516 | 29.048 | 37.7 | 135.3057 | BMRL | 5.631 | 6.3378 | BMRL | 15.1334 | 10.7175 | 5.3492 | 5.3774 | 6.1285 | 27.1022 | 37.8197 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 300 | 300 | [7 empty] | 300 | 0 |  | Bromide | mg/L | 300 | 300 | [7 empty] | 300 | 0 |  | Avg-C11-10 | Y | 1998-11-09 | 02:03 | 130.4667 | 7389.632 | 8.05 | 21.45 | 3.7925 | 0.0585 | 1.5425 | 3.92 | 0.72 | 3.2 | 23.6 | 7.9489 | 23.9 | 273.075 | 14.4578 | 64.5184 | 39.6151 | 30.75 | 149.3414 | BMRL | 9.2798 | 9.5335 | BMRL | 18.5568 | 15.6485 | 6.8992 | 9.9927 | 14.2251 | 37.37 | 53.0185 | Avg-C11-20 | Y | 1998-11-14 | 08:10 | 256.4167 | 14523.44 | 8.19 | 21 | 3.4375 | 0.052 | 1.5127 | 3.74 | 0.8 | 2.94 | 23.5 | 7.9416 | 23.8 | 239.65 | 10.1178 | 61.077 | 33.1199 | 33 | 137.3147 | BMRL | 6.7434 | 6.363 | BMRL | 15.5575 | 12.1328 | 5.2785 | 5.9067 | 8.05 | 28.6639 | 40.7968 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | C12-10 | N | 1998-11-09 | 19:38 | 148.05 | 8385.552 | 8.1 | 22.4 | 4.06 | 0.0636 | 1.5665 | 4.11 | 0.65 | 3.46 | 23.4 | 7.9547 | 24 | 290.75 | 16.0096 | 59.9513 | 40.8108 | 28.4 | 145.1717 | BMRL | 10.0784 | 10.9934 | BMRL | 20.0488 | 16.9229 | 6.2286 | 10.1319 | 16.0192 | 41.1207 | 58.0436 | C12-20 | N | 1998-11-16 | 10:20 | 306.5833 | 17364.88 | 8.21 | 21.3 | 3.995 | 0.0595 | 1.4894 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Current Process Water Rate ($/1000 gal) | 0.196
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 9.3225e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-11-11 | 10:09 | 186.5667 | 10567.136 | 8 | 21.2 | 4.455 | 0.07115 | 1.5971 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | C13-20 | N | 1998-11-18 | 02:50 | 347.0833 | 19658.8 | 8.05 | 21 | 4.085 | 0.0607 | 1.4859 | 4.16 | 0.85 | 3.31 | 23.5 | 7.945 | 24 | 280.2 | 16.9288 | 69.4382 | 42.9099 | 34.1 | 163.3769 | BMRL | 9.2167 | 6.7759 | BMRL | 16.1342 | 14.3949 | 4.4563 | 6.2439 | 11.1304 | 32.1268 | 46.5217 | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD
|  |  |  | Scaling factor, SF | 9.44 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-06 | 1998-11-07 | 1998-11-10 | 1998-11-16 | 1998-11-17 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-11-03 | 1998-11-06 | 1998-11-07 | 1998-11-10 | 1998-11-16 | 1998-11-17 |  |  |  |  | --- | ---
Plant Name | Robert A. Perdue Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 8.0546 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:55 | 09:30 | 15:40 | 14:00 | 12:45 | 16:25 |  |  |  |  | --- | --- | Sampling time | hh:mm | 16:55 | 09:30 | 15:40 | 14:00 | 12:45 | 16:25 |  |  |  |  | --- | ---
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 16.7388 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 1.3333 | 65.9167 | 96.0833 | 166.4167 | 309.1667 | 336.8333 |  |  |  |  | --- | --- | Operation time | hh.hh | 1.1667 | 65.75 | 95.9167 | 166.25 | 309 | 336.6667 |  |  |  |  | --- | ---
Process Train Name | Perdue Treatment Plant |  |  | Estimated total influent volume required, VSCT (L) | 323.3898 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 75.52 | 3733.52 | 5442.16 | 9425.84 | 17511.2 | 19078.24 |  |  |  |  | --- | --- | Bed volumes | (20 minute) | 33.04 | 1862.04 | 2716.36 | 4708.2 | 8750.88 | 9534.4 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 221 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.63 | 7.61 | 7.55 | 7.61 | 7.98 | 7.7 |  |  |  |  | 7.68 | 2.0138 | pH | --- | 7.63 | 7.61 | 7.55 | 7.61 | 7.98 | 7.7 |  |  |  |  | 7.68 | 2.0138 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.15 | NA | NA | 0.15 | NA | 0.15 |  |  |  |  | 0.15 | 0 | Turbidity | ntu | 0.15 | NA | NA | 0.15 | NA | 0.15 |  |  |  |  | 0.15 | 0 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 23.8 | 16.4 | 16.4 | 17.3 | 18.2 | 18.6 |  |  |  |  | 18.45 | 15.0273 | Temperature | oC | 23.8 | 16.4 | 16.4 | 17.3 | 18.2 | 18.6 |  |  |  |  | 18.45 | 15.0273
Historical Average Water Temperature (oC) | 22 |  |  | Estimated full-scale run time, tLCT (days) | 42.2172 | [5 empty] | Total organic carbon | mg/L | 5.67 | 5.595 | 5.685 | 5.53 | 5.565 | 5.44 |  |  |  |  | 5.5808 | 1.6358 | Total organic carbon | mg/L | 5.67 | 5.595 | 5.685 | 5.53 | 5.565 | 5.44 |  |  |  |  | 5.5808 | 1.6358 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 30 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0593 | [5 empty] | UV254 | cm-1 | 0.10905 | NA | NA | 0.1084 | NA | 0.10885 |  |  |  |  | 0.10877 | 0.30608 | UV254 | cm-1 | 0.10905 | NA | NA | 0.1084 | NA | 0.10885 |  |  |  |  | 0.10877 | 0.30608 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 4.4722 | [5 empty] | SUVA | L/(mg*m) | 1.9233 | NR | NR | 1.9602 | NR | 2.0009 |  |  |  |  | 1.9615 | 1.9799 | SUVA | L/(mg*m) | 1.9233 | NR | NR | 1.9602 | NR | 2.0009 |  |  |  |  | 1.9615 | 1.9799 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 14.2207 | [5 empty] | SDS-Cl2 dose | mg/L | 5.65 | NA | NA | 5.35 | NA | 5.35 |  |  |  |  | 5.45 | 3.1781 | SDS-Cl2 dose | mg/L | 5.65 | NA | NA | 5.35 | NA | 5.35 |  |  |  |  | 5.45 | 3.1781 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 107.7966 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.04 | NA | NA | 0.69 | NA | 0.74 |  |  |  |  | 0.82333 | 22.9915 | SDS-Free Cl2 residual | mg/L | 1.04 | NA | NA | 0.69 | NA | 0.74 |  |  |  |  | 0.82333 | 22.9915 | C5-10 | Primary | 1998-11-05 | 15:13 | 47.6333 | 2697.952 | 8.05 | 21.7 | 1.5 | 0.01735 | 1.1567 | 2.49 | 0.81 | 1.68 | 23.6 | 7.9447 | 23.7 | 76.8 | BMRL | 22.8671 | 6.0243 | 29.3 | 58.1914 | BMRL | 3.0407 | BMRL | BMRL | 8.6656 | 4.1203 | 5.2987 | 2.6255 | 1.8544 | 11.7062 | 15.8265 | C4-20 | Primary | 1998-11-07 | 11:52 | 92.1167 | 5217.488 | 8.03 | 21.4 | 1.11 | 0.0117 | 1.0541 | 2.23 | 0.82 | 1.41 | 23.6 | 7.9547 | 23.8 | 47.45 | BMRL | 13.8976 | 2.7584 | 23.7 | 40.3561 | BMRL | 1.0859 | BMRL | BMRL | 6.2356 | 2.9835 | BMRL | BMRL | 1.032 | 7.3215 | 10.305
|  |  |  | Mass GAC required, mSC (g) | 8.2808 | [5 empty] | SDS-Cl2 demand | mg/L | 4.61 | NR | NR | 4.66 | NR | 4.61 |  |  |  |  | 4.6267 | 0.62394 | SDS-Cl2 demand | mg/L | 4.61 | NR | NR | 4.66 | NR | 4.61 |  |  |  |  | 4.6267 | 0.62394 | D-C5-10 | Duplicate | 1998-11-05 | 15:13 | 47.6333 | 2697.952 | 8.08 | 21.7 | 1.49 | 0.0176 | 1.1812 | 2.49 | 0.83 | 1.66 | 23.6 | 7.9495 | 23.7 | 76.95 | BMRL | 24.479 | 6.6695 | 30.5 | 61.6484 | BMRL | 3.4965 | BMRL | BMRL | 9.6636 | 4.8759 | 5.6707 | 2.9546 | 1.8354 | 13.1602 | 18.036 | D-C4-10 | Duplicate | 1998-11-07 | 11:52 | 92.1167 | 5217.488 | 8.04 | 21.4 | 1.12 | 0.0116 | 1.0357 | 2.23 | 0.88 | 1.35 | 23.6 | 7.9395 | 23.8 | 49.15 | BMRL | 13.2279 | 2.6958 | 22.4 | 38.3237 | BMRL | 1.3344 | BMRL | BMRL | 8.8445 | 3.7543 | 4.1546 | 2.2604 | 1.385 | 10.1789 | 13.9332
[11 empty] | SDS-Chlorination temp. | oC | 23.5 | NA | NA | 23.4 | NA | 23.5 |  |  |  |  | 23.4667 | 0.24603 | SDS-Chlorination temp. | oC | 23.5 | NA | NA | 23.4 | NA | 23.5 |  |  |  |  | 23.4667 | 0.24603 | Avg-C5-10 | Average | --- | --- | --- | --- | 8.065 | 21.7 | 1.495 | 0.017475 | 1.1689 | 2.49 | 0.82 | 1.67 | 23.6 | 7.9471 | 23.7 | 76.875 | BMRL | 23.673 | 6.3469 | 29.9 | 59.9199 | BMRL | 3.2686 | BMRL | BMRL | 9.1646 | 4.4981 | 5.4847 | 2.7901 | 1.8449 | 12.4332 | 16.9313 | Avg-C4-20 | Average | --- | --- | --- | --- | 8.035 | 21.4 | 1.115 | 0.01165 | 1.0449 | 2.23 | 0.85 | 1.38 | 23.6 | 7.9471 | 23.8 | 48.3 | BMRL | 13.5628 | 2.7271 | 23.05 | 39.3399 | BMRL | 1.2101 | BMRL | BMRL | 7.54 | 3.3689 | 4.1546 | 2.2604 | 1.2085 | 8.7502 | 12.1191
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.955 | NA | NA | 7.9495 | NA | 7.965 |  |  |  |  | 7.9565 | 0.098381 | SDS-Chlorination pH | --- | 7.955 | NA | NA | 7.9495 | NA | 7.965 |  |  |  |  | 7.9565 | 0.098381 | RPD-C5-10 | RPD | --- | --- | --- | --- | 0.37198 | 0 | 0.6689 | 1.4306 | 2.0995 | 0 | 2.439 | 1.1976 | 0 | 0.060382 | 0 | 0.19512 |  | 6.8088 | 10.1648 | 4.0134 | 5.7694 |  | 13.9469 |  |  | 10.8906 | 16.7983 | 6.7828 | 11.7962 | 1.033 | 11.6941 | 13.0501 | RPD-C4-20 | RPD | --- | --- | --- | --- | 0.12446 | 0 | 0.89686 | 0.85837 | 1.7552 | 0 | 7.0588 | 4.3478 | 0 | 0.19128 | 0 | 3.5197 |  | 4.9379 | 2.295 | 5.6399 | 5.166 |  | 20.5277 |  |  | 34.6011 | 22.8806 |  |  | 29.2081 | 32.6548 | 29.9377
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 24.1 | NA | NA | 24.1 | NA | 24.1 |  |  |  |  | 24.1 | 0 | SDS-Incubation time | hours | 24.1 | NA | NA | 24.1 | NA | 24.1 |  |  |  |  | 24.1 | 0 | C8-10 | Primary | 1998-11-06 | 15:29 | 71.9 | 4072.416 | 8.02 | 21.7 | 2.65 | 0.03425 | 1.2925 | 3.29 | 0.87 | 2.42 | 23.6 | 7.9447 | 23.7 | 168 | 4.292 | 47.1161 | 19.6673 | 36.1 | 107.1753 | BMRL | 7.2602 | 2.4677 | BMRL | 16.7217 | 12.4935 | 7.7545 | 7.0845 | 5.8232 | 26.4496 | 38.9431 | C7-20 | Primary | 1998-11-09 | 13:35 | 141.8333 | 8033.44 | 8.01 | 22.6 | 2.21 | 0.02805 | 1.2692 | 2.89 | 0.76 | 2.13 | 23.6 | 7.9815 | 23.9 | 134.45 | 2.4037 | 41.2091 | 14.0961 | 40.3 | 98.0089 | BMRL | 4.7124 | 1.0979 | BMRL | 15.6506 | 10.8121 | 7.356 | 5.4895 | 3.5044 | 21.4609 | 32.2731
|  |  |  | Estimated full-scale run time, tLCT (days) | 84.4345 | [5 empty] | SDS-TOX | mg Cl- /L | 495.1 | NA | NA | 489.15 | NA | 474.15 |  |  |  |  | 486.1333 | 2.2208 | SDS-TOX | mg Cl- /L | 495.1 | NA | NA | 489.15 | NA | 474.15 |  |  |  |  | 486.1333 | 2.2208 | D-C8-10 | Duplicate | 1998-11-06 | 15:29 | 71.9 | 4072.416 | 8.04 | 21.7 | 2.675 | 0.03425 | 1.2804 | 3.29 | 0.88 | 2.41 | 23.6 | 7.9495 | 23.7 | 171.85 | 4.5214 | 49.4936 | 20.6803 | 36.7 | 111.3953 | BMRL | 6.5996 | 2.1046 | BMRL | 15.4289 | 11.94 | 8.1577 | 6.7389 | 5.4563 | 24.1331 | 36.0731 | D-C7-20 | Duplicate | 1998-11-09 | 13:35 | 141.8333 | 8033.44 | 8.03 | 22.5 | 2.22 | 0.0285 | 1.2838 | 2.89 | 0.76 | 2.13 | 23.6 | 7.9871 | 23.9 | 140.8 | 2.3015 | 40.6529 | 13.7256 | 39.8 | 96.48 | BMRL | 4.1534 | BMRL | BMRL | 13.6772 | 9.3259 | 6.1189 | 4.6422 | 3.2194 | 17.8306 | 27.1566
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1186 | [5 empty] | SDS-CHCl3 | mg/L | 54.1016 | NA | NA | 52.1782 | NA | 50.9468 |  |  |  |  | 52.4089 | 3.0338 | SDS-CHCl3 | mg/L | 54.1016 | NA | NA | 52.1782 | NA | 50.9468 |  |  |  |  | 52.4089 | 3.0338 | Avg-C8-10 | Average | --- | --- | --- | --- | 8.03 | 21.7 | 2.6625 | 0.03425 | 1.2864 | 3.29 | 0.875 | 2.415 | 23.6 | 7.9471 | 23.7 | 169.925 | 4.4067 | 48.3048 | 20.1738 | 36.4 | 109.2853 | BMRL | 6.9299 | 2.2861 | BMRL | 16.0753 | 12.2168 | 7.9561 | 6.9117 | 5.6398 | 25.2913 | 37.5081 | Avg-C7-20 | Average | --- | --- | --- | --- | 8.02 | 22.55 | 2.215 | 0.028275 | 1.2765 | 2.89 | 0.76 | 2.13 | 23.6 | 7.9843 | 23.9 | 137.625 | 2.3526 | 40.931 | 13.9109 | 40.05 | 97.2444 | BMRL | 4.4329 | 1.0979 | BMRL | 14.6639 | 10.069 | 6.7374 | 5.0658 | 3.3619 | 19.6458 | 29.7148
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.9443 | [5 empty] | SDS-BDCM | mg/L | 65.3763 | NA | NA | 59.7112 | NA | 70.6904 |  |  |  |  | 65.2593 | 8.4134 | SDS-BDCM | mg/L | 65.3763 | NA | NA | 59.7112 | NA | 70.6904 |  |  |  |  | 65.2593 | 8.4134 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.24907 | 0 | 0.93897 | 0 | 0.93897 | 0 | 1.1429 | 0.41408 | 0 | 0.060382 | 0 | 2.2657 | 5.2044 | 4.922 | 5.0217 | 1.6484 | 3.8614 |  | 9.5322 | 15.8835 |  | 8.0421 | 4.5307 | 5.0669 | 4.9993 | 6.5054 | 9.1592 | 7.6516 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.24938 | 0.44346 | 0.45147 | 1.5915 | 1.1401 | 0 | 0 | 0 | 0 | 0.070156 | 0 | 4.614 | 4.3435 | 1.3589 | 2.6636 | 1.2484 | 1.5722 |  | 12.6105 |  |  | 13.4575 | 14.7601 | 18.3609 | 16.7251 | 8.477 | 18.4789 | 17.2188
|  |  |  | RSSCT bed length, lSC (cm) | 28.4415 | [5 empty] | SDS-DBCM | mg/L | 65.9478 | NA | NA | 65.7963 | NA | 66.792 |  |  |  |  | 66.1787 | 0.81068 | SDS-DBCM | mg/L | 65.9478 | NA | NA | 65.7963 | NA | 66.792 |  |  |  |  | 66.1787 | 0.81068 | C11-10 | Primary | 1998-11-09 | 02:03 | 130.4667 | 7389.632 | 8.04 | 21.5 | 3.78 | 0.0585 | 1.5476 | 3.92 | 0.74 | 3.18 | 23.6 | 7.9536 | 23.9 | 272.5 | 14.2453 | 63.9122 | 39.2202 | 30.1 | 147.4777 | BMRL | 9.1363 | 8.9183 | BMRL | 17.5033 | 15.0394 | 6.5715 | 9.4931 | 13.4966 | 35.5579 | 50.5973 | C11-20 | Primary | 1998-11-14 | 08:10 | 256.4167 | 14523.44 | 8.17 | 21 | 3.43 | 0.052 | 1.516 | 3.74 | 0.79 | 2.95 | 23.5 | 7.939 | 23.8 | 241.05 | 9.774 | 61.3311 | 32.2571 | 32.9 | 136.2622 | BMRL | 6.8179 | 6.7114 | BMRL | 16.3062 | 12.5912 | 5.5802 | 6.1531 | 8.5171 | 29.8355 | 42.4267
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 215.5932 | [5 empty] | SDS-CHBr3 | mg/L | 14.7 | NA | NA | 16.5 | NA | 16.9 |  |  |  |  | 16.0333 | 7.3091 | SDS-CHBr3 | mg/L | 14.7 | NA | NA | 16.5 | NA | 16.9 |  |  |  |  | 16.0333 | 7.3091 | D-C11-10 | Duplicate | 1998-11-09 | 02:03 | 130.4667 | 7389.632 | 8.06 | 21.4 | 3.805 | 0.0585 | 1.5375 | 3.92 | 0.7 | 3.22 | 23.6 | 7.9443 | 23.9 | 273.65 | 14.6704 | 65.1247 | 40.01 | 31.4 | 151.2051 | BMRL | 9.4232 | 10.1487 | BMRL | 19.6102 | 16.2575 | 7.2269 | 10.4923 | 14.9535 | 39.1821 | 55.4396 | D-C11-20 | Duplicate | 1998-11-14 | 08:10 | 256.4167 | 14523.44 | 8.21 | 21 | 3.445 | 0.052 | 1.5094 | 3.74 | 0.81 | 2.93 | 23.5 | 7.9443 | 23.8 | 238.25 | 10.4616 | 60.8228 | 33.9827 | 33.1 | 138.3671 | BMRL | 6.6689 | 6.0146 | BMRL | 14.8089 | 11.6744 | 4.9768 | 5.6603 | 7.5828 | 27.4924 | 39.1668
|  |  |  | Mass GAC required, mSC (g) | 16.5615 | [5 empty] | SDS-THM4 | mg/L | 200.1257 | NA | NA | 194.1857 | NA | 205.3292 |  |  |  |  | 199.8802 | 2.7896 | SDS-THM4 | mg/L | 200.1257 | NA | NA | 194.1857 | NA | 205.3292 |  |  |  |  | 199.8802 | 2.7896 | Avg-C11-10 | Average | --- | --- | --- | --- | 8.05 | 21.45 | 3.7925 | 0.0585 | 1.5425 | 3.92 | 0.72 | 3.2 | 23.6 | 7.9489 | 23.9 | 273.075 | 14.4578 | 64.5184 | 39.6151 | 30.75 | 149.3414 | BMRL | 9.2798 | 9.5335 | BMRL | 18.5568 | 15.6485 | 6.8992 | 9.9927 | 14.2251 | 37.37 | 53.0185 | Avg-C11-20 | Average | --- | --- | --- | --- | 8.19 | 21 | 3.4375 | 0.052 | 1.5127 | 3.74 | 0.8 | 2.94 | 23.5 | 7.9416 | 23.8 | 239.65 | 10.1178 | 61.077 | 33.1199 | 33 | 137.3147 | BMRL | 6.7434 | 6.363 | BMRL | 15.5575 | 12.1328 | 5.2785 | 5.9067 | 8.05 | 28.6639 | 40.7968
[11 empty] | SDS-MCAA* | mg/L | 4.7731 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 4.7731 | #DIV/0! | SDS-MCAA* | mg/L | 4.7731 | NA | NA | BMRL | NA | BMRL |  |  |  |  | 4.7731 | #DIV/0! | RPD-C11-10 | RPD | --- | --- | --- | --- | 0.24845 | 0.4662 | 0.6592 | 0 | 0.6592 | 0 | 5.5556 | 1.25 | 0 | 0.11713 | 0 | 0.42113 | 2.9402 | 1.8793 | 1.9938 | 4.2276 | 2.4959 |  | 3.0913 | 12.9056 |  | 11.354 | 7.7843 | 9.499 | 9.9992 | 10.2418 | 9.698 | 9.1332 | RPD-C11-20 | RPD | --- | --- | --- | --- | 0.4884 | 0 | 0.43636 | 0 | 0.43636 | 0 | 2.5 | 0.68027 | 0 | 0.066941 | 0 | 1.1684 | 6.7956 | 0.83218 | 5.2101 | 0.60606 | 1.5329 |  | 2.2096 | 10.9507 |  | 9.6241 | 7.5564 | 11.4316 | 8.3429 | 11.6053 | 8.1743 | 7.9905
[11 empty] | SDS-DCAA* | mg/L | 29.3153 | NA | NA | 23.9129 | NA | 22.7581 |  |  |  |  | 25.3288 | 13.8198 | SDS-DCAA* | mg/L | 29.3153 | NA | NA | 23.9129 | NA | 22.7581 |  |  |  |  | 25.3288 | 13.8198 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 17.3467 | NA | NA | 20.1154 | NA | 17.431 |  |  |  |  | 18.2977 | 8.6062 | SDS-TCAA* | mg/L | 17.3467 | NA | NA | 20.1154 | NA | 17.431 |  |  |  |  | 18.2977 | 8.6062 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-DBAA* | mg/L | 16.0238 | NA | NA | 17.3712 | NA | 16.0683 |  |  |  |  | 16.4878 | 4.6422 | SDS-DBAA* | mg/L | 16.0238 | NA | NA | 17.3712 | NA | 16.0683 |  |  |  |  | 16.4878 | 4.6422
[11 empty] | SDS-BCAA* | mg/L | 24.9758 | NA | NA | 23.8711 | NA | 22.1996 |  |  |  |  | 23.6822 | 5.9021 | SDS-BCAA* | mg/L | 24.9758 | NA | NA | 23.8711 | NA | 22.1996 |  |  |  |  | 23.6822 | 5.9021
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | 11.719 | NA | NA | 13.4954 | NA | 9.962 |  |  |  |  | 11.7255 | 15.0675 | SDS-CDBAA | mg/L | 11.719 | NA | NA | 13.4954 | NA | 9.962 |  |  |  |  | 11.7255 | 15.0675
[11 empty] | SDS-DCBAA | mg/L | 25.361 | NA | NA | 28.7927 | NA | 25.8956 |  |  |  |  | 26.6831 | 6.9197 | SDS-DCBAA | mg/L | 25.361 | NA | NA | 28.7927 | NA | 25.8956 |  |  |  |  | 26.6831 | 6.9197
[11 empty] | SDS-HAA5 | mg/L | 67.4588 | NA | NA | 61.3995 | NA | 56.2574 |  |  |  |  | 61.7053 | 9.0867 | SDS-HAA5 | mg/L | 67.4588 | NA | NA | 61.3995 | NA | 56.2574 |  |  |  |  | 61.7053 | 9.0867
[11 empty] | SDS-HAA6 | mg/L | 92.4347 | NA | NA | 85.2706 | NA | 78.457 |  |  |  |  | 85.3874 | 8.1857 | SDS-HAA6 | mg/L | 92.4347 | NA | NA | 85.2706 | NA | 78.457 |  |  |  |  | 85.3874 | 8.1857
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H22: Reviewer M.H. (11/13/99): Per Consultant: "Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS".
Note on N6: Reviewer M.H. (11/13/99): Per consultant, "The chlorine and ammonia feeds were off for third quarter influent sampling."
Note on DB36: S&H comment: HAA results verified.
Note on DE36: S&H comment: HAA results verified" .
Note on DF36: S&H comment: HAA results verified.
Note on DI36: S&H comment: HAA results verified.

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [13 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [13 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [33 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [32 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | Sweetwater Authority | Carbon manufacturer | Calgon Carbon Co. | RSSCT influent TOC (mg/L) | 4.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-11-06 | [12 empty] | 20-min. EBCT Start Date | 1998-11-06 | [12 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | CA3710025 | Carbon trade name | F-400 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | 25 mg/L sulfuric acid; 30 mg/L ferric chloride; 1.8 mg/L polymer | Bench-Scale | 10-min. EBCT Start Time | 14:15 | [12 empty] | 20-min. EBCT Start Time | 14:15 | [12 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5.3
Water Industry Data Base Number (optional) | 1253 | Carbon type | Bituminous | Minimum RSSCT Reynolds number, ReSC, min | 0.6 | 4 | 4.75 | Flocculation | 2-Stage tapered | Bench-Scale | [29 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 24 | 6 | 3.35 | Sedimentation | 60 minutes | Bench-Scale | Group A, 2 samples per batch | [13 empty] | Group A, 2 samples per batch | [13 empty] | C1-10 | N | 1998-11-06 | 17:37 | 3.3667 | 190.688 | 7.62 | 21.6 | 0.11 | 0.00025 | 0.22727 | 1.25 | 0.63 | 0.62 | 23.6 | 7.96 | 23.5 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | C1-20 | N | 1998-11-06 | 17:33 | 3.3 | 186.912 | 7.94 | 21.5 | 0.13 | 0.00025 | 0.19231 | 1.4 | 0.76 | 0.64 | 23.6 | 8.1295 | 23.9 | 2.15 | BMRL | BMRL | BMRL | 2.01 | 2.01 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 1.0 µm pore size | Bench-Scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Sample A3-10 | Sample A4-10 | Sample A5-10 | Sample A6-10 | Sample A7-10 | Sample A8-10 | Sample A9-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Sample A3-20 | Sample A4-20 | Sample A5-20 | Sample A6-20 | Sample A7-20 | Sample A8-20 | Sample A9-20 | Average | RPD |  | C2-10 | N | 1998-11-07 | 23:51 | 33.6 | 1903.104 | 7.56 | 20.3 | 0.255 | 0.00145 | 0.56863 | 1.51 | 0.71 | 0.8 | 23.6 | 7.9647 | 24 | 8.9 | BMRL | 1.3267 | BMRL | 6.34 | 7.6667 | BMRL | BMRL | BMRL | BMRL | 1.5273 | BMRL | BMRL | BMRL | BMRL | 1.5273 | 1.5273 | C2-20 | N | 1998-11-12 | 05:05 | 134.8333 | 7636.96 | 7.55 | 20 | 0.42 | 0.0032 | 0.7619 | 1.68 | 0.75 | 0.93 | 23.5 | 7.98 | 23.9 | 15.9 | BMRL | 3.0229 | BMRL | 9.56 | 12.5829 | BMRL | BMRL | BMRL | BMRL | 3.0003 | BMRL | BMRL | BMRL | BMRL | 3.0003 | 3.0003 | Special Sitework Factor (% of construction costs) | 20
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.467 | 10 | 2 |  |  |  | Sampling date | MM/DD/YY | 1998-11-06 | 1998-11-16 | [7 empty] | --- | --- |  | Sampling date | MM/DD/YY | 1998-11-06 | 1998-11-16 | [7 empty] | --- | --- |  | C3-10 | N | 1998-11-08 | 21:08 | 54.8833 | 3108.592 | 7.54 | 20.6 | 0.375 | 0.00285 | 0.76 | 1.61 | 0.57 | 1.04 | 23.6 | 7.9643 | 24 | 14 | BMRL | 2.5725 | BMRL | 9.88 | 12.4525 | BMRL | BMRL | BMRL | BMRL | 2.6408 | BMRL | BMRL | BMRL | BMRL | 2.6408 | 2.6408 | Avg-C3-20 | Y | 1998-11-12 | 22:11 | 151.9333 | 8605.504 | 7.615 | 20.1 | 0.69 | 0.005275 | 0.76449 | 1.89 | 0.79 | 1.1 | 23.5 | 8.01 | 23.9 | 29.8 | BMRL | 6.2585 | 1.0382 | 17.8269 | 25.1236 | BMRL | BMRL | BMRL | BMRL | 4.2487 | 1.1782 | BMRL | BMRL | BMRL | 4.2487 | 5.4269 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 16:30 | 08:25 | [7 empty] | --- | --- |  | Sampling time | hh:mm | 16:30 | 08:25 | [7 empty] | --- | --- |  | C4-10 | N | 1998-11-09 | 10:01 | 67.7667 | 3838.304 | 7.45 | 20.6 | 0.725 | 0.0057 | 0.78621 | 1.89 | 0.69 | 1.2 | 23.6 | 7.9247 | 24 | 31 | BMRL | 7.6434 | 1.1095 | 19.2 | 27.9529 | BMRL | BMRL | BMRL | BMRL | 5.4455 | 1.454 | BMRL | BMRL | BMRL | 5.4455 | 6.8994 | C4-20 | N | 1998-11-13 | 20:02 | 173.7833 | 9843.088 | 7.5 | 20.8 | 0.99 | 0.0085 | 0.85859 | 2.07 | 0.74 | 1.33 | 23.5 | 7.925 | 23.8 | 44 | BMRL | 10.3325 | 1.9835 | 20.6 | 32.916 | BMRL | BMRL | BMRL | BMRL | 6.7094 | 2.09 | BMRL | BMRL | 1.1298 | 6.7094 | 8.7993 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 2.25 | 234.1667 | [7 empty] | --- | --- |  | Operation time | hh.hh | 2.25 | 234.1667 | [7 empty] | --- | --- |  | Avg-C5-10 | Y | 1998-11-09 | 14:19 | 72.0667 | 4081.856 | 7.495 | 21.85 | 0.9625 | 0.00815 | 0.84675 | 2.09 | 0.75 | 1.34 | 23.6 | 7.9839 | 24 | 41.75 | BMRL | 10.7616 | 1.8107 | 24.3332 | 36.9055 | BMRL | BMRL | BMRL | BMRL | 7.5088 | 2.2051 | BMRL | BMRL | BMRL | 7.5088 | 9.7139 | C5-20 | N | 1998-11-14 | 13:29 | 191.2333 | 10831.456 | 7.37 | 20.7 | 1.23 | 0.0111 | 0.90244 | 2.23 | 0.8 | 1.43 | 23.5 | 7.935 | 23.8 | 60.9 | BMRL | 13.6272 | 2.9523 | 25.9 | 42.4795 | BMRL | BMRL | BMRL | BMRL | 7.5239 | 2.4972 | BMRL | BMRL | 1.2725 | 7.5239 | 10.0211 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5986
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 127.44 | 13263.2 | [7 empty] | --- | --- |  | Bed volumes | (20 minutes) | 63.72 | 6631.6 | [7 empty] | --- | --- |  | C6-10 | N | 1998-11-09 | 18:35 | 76.3333 | 4323.52 | 7.58 | 21.7 | 1.185 | 0.01045 | 0.88186 | 2.27 | 0.74 | 1.53 | 23.6 | 7.9847 | 24 | 56.55 | BMRL | 16.4381 | 3.1656 | 30 | 49.6037 | BMRL | 1.0915 | BMRL | BMRL | 8.9491 | 2.8562 | BMRL | BMRL | 1.1446 | 10.0406 | 12.8968 | C6-20 | N | 1998-11-15 | 11:20 | 213.0833 | 12069.04 | 7.42 | 20.4 | 1.54 | 0.01465 | 0.9513 | 2.44 | 0.7 | 1.74 | 23.5 | 7.91 | 23.8 | 76.5 | BMRL | 18.9051 | 4.7307 | 28.8 | 52.4358 | BMRL | 1.0409 | BMRL | BMRL | 7.7444 | 3.1425 | BMRL | 2.0076 | 1.4522 | 8.7853 | 11.9278 | 1998 Producers Price Index (PPI base year 1967 = 100) | 369
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 100.75 | 80.9 | [7 empty] | 90.825 | 15.454 |  | Alkalinity | mg/L as CaCO3 | 100.75 | 80.9 | [7 empty] | 90.825 | 15.454 |  | C7-10 | N | 1998-11-10 | 03:09 | 84.9 | 4808.736 | 7.49 | 20.5 | 1.475 | 0.01385 | 0.93898 | 2.52 | 0.75 | 1.77 | 23.5 | 8.0199 | 24.4 | 74.25 | BMRL | 19.1092 | 4.5102 | 32.8 | 56.4193 | BMRL | 1.1926 | BMRL | BMRL | 9.3776 | 3.2269 | 4.5785 | 2.1896 | 1.5787 | 10.5702 | 13.797 | Avg-C7-20 | Y | 1998-11-16 | 04:27 | 230.2 | 13038.528 | 7.39 | 20 | 1.7825 | 0.0172 | 0.96494 | 2.6 | 0.86 | 1.74 | 23.5 | 7.9299 | 23.85 | 90.85 | 1.2571 | 25.4617 | 6.8219 | 32 | 65.5407 | BMRL | 1.1679 | BMRL | BMRL | 9.7807 | 4.0868 | BMRL | 2.4248 | 1.7681 | 10.9486 | 15.0354 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3071.0258 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 223 | 223 | [7 empty] | 223 | 0 |  | Total hardness | mg/L as CaCO3 | 223 | 223 | [7 empty] | 223 | 0 |  | Avg-C8-10 | Y | 1998-11-10 | 11:52 | 93.6167 | 5302.448 | 7.45 | 21.7 | 1.815 | 0.0183 | 1.0083 | 2.78 | 0.87 | 1.91 | 23.5 | 8.0375 | 24.4 | 98.95 | 1.307 | 26.492 | 7.4366 | 36.35 | 71.5856 | BMRL | 1.5026 | BMRL | BMRL | 11.3352 | 4.4952 | 4.9991 | 2.5979 | 1.8057 | 12.8379 | 17.3331 | C8-20 | N | 1998-11-16 | 17:30 | 243.25 | 13777.68 | 7.51 | 21.6 | 2.02 | 0.0213 | 1.0545 | 2.77 | 0.83 | 1.94 | 23.5 | 7.975 | 24.1 | 111.35 | 1.4955 | 33.0705 | 9.8036 | 41.4 | 85.7696 | BMRL | 1.635 | BMRL | BMRL | 12.6032 | 5.2845 | 4.9868 | 2.6751 | 1.8754 | 14.2382 | 19.5228 | Labor Overhead Factor (% of labor) | 12
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 6142.0516 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 121 | 124 | [7 empty] | 122.5 | 1.7317 |  | Calcium hardness | mg/L as CaCO3 | 121 | 124 | [7 empty] | 122.5 | 1.7317 |  | C9-10 | N | 1998-11-10 | 20:31 | 102.2667 | 5792.384 | 7.61 | 21.2 | 2.07 | 0.0214 | 1.0338 | 2.98 | 0.94 | 2.04 | 23.5 | 7.9847 | 24.5 | 116.8 | 1.7977 | 31.5805 | 10.0141 | 35.7 | 79.0923 | BMRL | 1.7603 | BMRL | BMRL | 12.2603 | 5.4059 | 5.2425 | 3.0945 | 2.2549 | 14.0206 | 19.4265 | C9-20 | N | 1998-11-18 | 09:06 | 282.85 | 16020.624 | 7.41 | 20.1 | 2.28 | 0.0254 | 1.114 | 2.95 | 0.88 | 2.07 | 23.5 | 7.9995 | 24.2 | 130.9 | 2.3571 | 40.459 | 13.4536 | 46.1042 | 102.3738 | BMRL | 1.8464 | BMRL | BMRL | 13.0194 | 5.9993 | 4.6952 | 2.8335 | 2.2482 | 14.8658 | 20.8652 | Electric Rate ($/kW-h) | 0.087
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7984.6671 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.11 | 0.08 | [7 empty] | 0.095 | 22.3297 |  | Ammonia | mg NH3-N / L | 0.11 | 0.08 | [7 empty] | 0.095 | 22.3297 |  | C10-10 | N | 1998-11-11 | 09:46 | 115.5167 | 6542.864 | 7.45 | 20.7 | 2.355 | 0.0267 | 1.1338 | 3.2 | 0.96 | 2.24 | 23.5 | 7.97 | 24.4 | 137.65 | 2.7921 | 36.5656 | 14.0177 | 34.8 | 88.1754 | BMRL | 2.2331 | BMRL | BMRL | 11.5612 | 6.2895 | 4.5593 | 3.1293 | 2.7702 | 13.7943 | 20.0838 | Avg-C10-20 | Y | 1998-11-19 | 20:24 | 318.15 | 18020.016 | 7.495 | 21 | 2.66 | 0.030725 | 1.1551 | 3.15 | 0.9 | 2.25 | 23.5 | 7.9869 | 24 | 152.225 | 3.9282 | 50.2568 | 18.965 | 43.225 | 116.375 | BMRL | 2.716 | 1.1419 | BMRL | 15.4452 | 8.0577 | 5.8181 | 4.0466 | 3.4579 | 19.3031 | 27.3608 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 330 | 340 | [7 empty] | 335 | 2.1108 |  | Bromide | mg/L | 330 | 340 | [7 empty] | 335 | 2.1108 |  | C11-10 | N | 1998-11-12 | 07:27 | 137.2 | 7771.008 | 7.43 | 20.3 | 2.675 | 0.0337 | 1.2598 | 3.45 | 1.16 | 2.29 | 23.5 | 7.95 | 23.9 | 167.3 | 4.5838 | 44.3496 | 19.7439 | 34.2 | 102.8773 | BMRL | 3.3522 | 1.4624 | BMRL | 15.1126 | 8.847 | 5.66 | 4.7451 | 4.2275 | 19.9272 | 28.7742 | C11-20 | N | 1998-11-22 | 08:36 | 378.35 | 21429.744 | 7.34 | 20.6 | 2.93 | 0.03925 | 1.3396 | 3.3 | 0.81 | 2.49 | 23.5 | 7.9199 | 24.4 | 184 | 6.3796 | 56.2442 | 26.3141 | 39.1 | 128.038 | BMRL | 3.1857 | 1.1196 | BMRL | 14.5068 | 8.8155 | 5.7802 | 4.1336 | 4.4753 | 18.8121 | 27.6276 | Natural Gas Rate ($/ft3) | NA
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [31 empty] | Avg-C12-10 | Y | 1998-11-13 | 09:18 | 163.05 | 9235.152 | 7.51 | 20.1 | 3.0225 | 0.041775 | 1.3821 | 3.74 | 1.08 | 2.66 | 23.5 | 7.9875 | 23.9 | 200.25 | 7.5489 | 55.6822 | 27.814 | 37.5 | 128.5451 | BMRL | 4.1101 | 1.6631 | BMRL | 14.4967 | 9.7381 | 5.5116 | 5.0942 | 4.7762 | 20.2699 | 30.008 | C12-20 | N | 1998-11-23 | 09:59 | 403.7333 | 22867.456 | 7.32 | 20.8 | 3.195 | 0.0429 | 1.3427 | 3.47 | 0.86 | 2.61 | 23.5 | 8.0095 | 24.5 | 201.2 | 8.5666 | 62.696 | 31.553 | 40.6747 | 143.4904 | BMRL | 4.3063 | 1.5235 | BMRL | 17.0252 | 10.6825 | 7.0743 | 5.6956 | 5.3812 | 22.855 | 33.5374 | Current Process Water Rate ($/1000 gal) | 0.196
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 9.3225e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [13 empty] | Group B, 3 samples per batch | [13 empty] | C13-10 | N | 1998-11-15 | 12:00 | 213.75 | 12106.8 | 7.39 | 20.4 | 3.49 | 0.05085 | 1.457 | 3.73 | 0.81 | 2.92 | 23.5 | 7.9247 | 23.8 | 224.5 | 10.5237 | 55.1756 | 31.9868 | 30.9 | 128.5861 | BMRL | 5.2349 | 2.1155 | BMRL | 13.7954 | 10.8766 | 4.5092 | 4.7684 | 5.3718 | 21.1458 | 32.0224 | C13-20 | N | 1998-11-24 | 21:55 | 439.6667 | 24902.72 | 7.4 | 22.4 | 3.595 | 0.0521 | 1.4492 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Modifications to Existing Plant (% of construction costs) | 10
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Sample B4-20 | Sample B5-20 | Sample B6-20 | Sample B7-20 | Sample B8-20 | Sample B9-20 | Sample B20-20 | Average | %SD | C14-10 | N | 1998-11-17 | 02:31 | 252.2667 | 14288.384 | 7.37 | 19.4 | 3.75 | 0.05585 | 1.4893 | NA | NA | NR | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
|  |  |  | Scaling factor, SF | 9.44 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-11-06 | 1998-11-10 | 1998-11-13 | 1998-11-16 | 1998-11-20 | 1998-11-23 |  |  |  |  | --- | --- | Sampling date | MM/DD/YY | 1998-11-06 | 1998-11-10 | 1998-11-13 | 1998-11-16 | 1998-11-20 | 1998-11-23 |  |  |  |  | --- | ---
Plant Name | Robert A. Perdue Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 8.0546 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:25 | 13:45 | 09:35 | 08:20 | 14:05 | 14:30 |  |  |  |  | --- | --- | Sampling time | hh:mm | 16:25 | 13:45 | 09:35 | 08:20 | 14:05 | 14:30 |  |  |  |  | --- | ---
Treatment Plant Category | CONV |  |  | RSSCT flow rate, QSC (mL/min) | 12.7576 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 2.1667 | 95.5 | 163.3333 | 234.0833 | 335.8333 | 408.25 |  |  |  |  | --- | --- | Operation time | hh.hh | 2.1667 | 95.5 | 163.3333 | 234.0833 | 335.8333 | 408.25 |  |  |  |  | --- | ---
Process Train Name | Perdue Treatment Plant |  |  | Estimated total influent volume required, VSCT (L) | 323.7243 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 122.72 | 5409.12 | 9251.2 | 13258.48 | 19021.6 | 23123.28 |  |  |  |  | --- | --- | Bed volumes | (20 minute) | 61.36 | 2704.56 | 4625.6 | 6629.24 | 9510.8 | 11561.64 |  |  |  |  | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 221 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 6.82 | 6.83 | 6.88 | 6.82 | 6.75 | 6.68 |  |  |  |  | 6.7967 | 1.039 | pH | --- | 6.82 | 6.83 | 6.88 | 6.82 | 6.75 | 6.68 |  |  |  |  | 6.7967 | 1.039 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.15 | NA | NA | 0.1 | NA | 0.15 |  |  |  |  | 0.13333 | 21.6506 | Turbidity | ntu | 0.15 | NA | NA | 0.1 | NA | 0.15 |  |  |  |  | 0.13333 | 21.6506 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 12 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 20.2 | 17.8 | 16 | 15.5 | 19.8 | 19.1 |  |  |  |  | 18.0667 | 10.9458 | Temperature | oC | 20.2 | 17.8 | 16 | 15.5 | 19.8 | 19.1 |  |  |  |  | 18.0667 | 10.9458
Historical Average Water Temperature (oC) | 22 |  |  | Estimated full-scale run time, tLCT (days) | 55.4491 | [5 empty] | Total organic carbon | mg/L | 4.555 | 4.485 | 4.45 | 4.46 | 4.785 | 4.665 |  |  |  |  | 4.5667 | 2.9237 | Total organic carbon | mg/L | 4.555 | 4.485 | 4.45 | 4.46 | 4.785 | 4.665 |  |  |  |  | 4.5667 | 2.9237 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 30 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0593 | [5 empty] | UV254 | cm-1 | 0.08975 | NA | NA | 0.0894 | NA | 0.091 |  |  |  |  | 0.09005 | 0.93407 | UV254 | cm-1 | 0.08975 | NA | NA | 0.0894 | NA | 0.091 |  |  |  |  | 0.09005 | 0.93407 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 5.8738 | [5 empty] | SUVA | L/(mg*m) | 1.9704 | NR | NR | 2.0045 | NR | 1.9507 |  |  |  |  | 1.9752 | 1.3779 | SUVA | L/(mg*m) | 1.9704 | NR | NR | 2.0045 | NR | 1.9507 |  |  |  |  | 1.9752 | 1.3779 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 14.2207 | [5 empty] | SDS-Cl2 dose | mg/L | 5.31 | NA | NA | 4.85 | NA | 4.95 |  |  |  |  | 5.0367 | 4.8035 | SDS-Cl2 dose | mg/L | 5.31 | NA | NA | 4.85 | NA | 4.95 |  |  |  |  | 5.0367 | 4.8035 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 107.9081 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.12 | NA | NA | 0.87 | NA | 0.98 |  |  |  |  | 0.99 | 12.6565 | SDS-Free Cl2 residual | mg/L | 1.12 | NA | NA | 0.87 | NA | 0.98 |  |  |  |  | 0.99 | 12.6565 | C5-10 | Primary | 1998-11-09 | 14:19 | 72.0667 | 4081.856 | 7.48 | 22 | 0.955 | 0.0083 | 0.86911 | 2.09 | 0.8 | 1.29 | 23.6 | 8.0195 | 24 | 42.55 | BMRL | 10.8601 | 1.8053 | 24.9 | 37.5655 | BMRL | BMRL | BMRL | BMRL | 7.8816 | 2.2112 | BMRL | BMRL | BMRL | 7.8816 | 10.0928 | C3-20 | Primary | 1998-11-12 | 22:11 | 151.9333 | 8605.504 | 7.6 | 20.1 | 0.69 | 0.0051 | 0.73913 | 1.89 | 0.77 | 1.12 | 23.5 | 8.01 | 23.9 | 30.5 | BMRL | 6.2734 | 1.0242 | 18.1312 | 25.4288 | BMRL | BMRL | BMRL | BMRL | 4.1173 | 1.1386 | BMRL | BMRL | BMRL | 4.1173 | 5.2559
|  |  |  | Mass GAC required, mSC (g) | 6.3112 | [5 empty] | SDS-Cl2 demand | mg/L | 4.19 | NR | NR | 3.98 | NR | 3.97 |  |  |  |  | 4.0467 | 3.07 | SDS-Cl2 demand | mg/L | 4.19 | NR | NR | 3.98 | NR | 3.97 |  |  |  |  | 4.0467 | 3.07 | D-C5-10 | Duplicate | 1998-11-09 | 14:19 | 72.0667 | 4081.856 | 7.51 | 21.7 | 0.97 | 0.008 | 0.82474 | 2.09 | 0.7 | 1.39 | 23.6 | 7.9482 | 24 | 40.95 | BMRL | 10.6631 | 1.8161 | 23.7663 | 36.2456 | BMRL | BMRL | BMRL | BMRL | 7.136 | 2.1989 | BMRL | BMRL | BMRL | 7.136 | 9.335 | D-C3-10 | Duplicate | 1998-11-12 | 22:11 | 151.9333 | 8605.504 | 7.63 | 20.1 | 0.69 | 0.00545 | 0.78986 | 1.89 | 0.81 | 1.08 | 23.5 | 8.01 | 23.9 | 29.1 | BMRL | 6.2435 | 1.0522 | 17.5226 | 24.8184 | BMRL | BMRL | BMRL | BMRL | 4.3801 | 1.2178 | BMRL | BMRL | BMRL | 4.3801 | 5.598
[11 empty] | SDS-Chlorination temp. | oC | 23.6 | NA | NA | 23.5 | NA | 23.5 |  |  |  |  | 23.5333 | 0.24533 | SDS-Chlorination temp. | oC | 23.6 | NA | NA | 23.5 | NA | 23.5 |  |  |  |  | 23.5333 | 0.24533 | Avg-C5-10 | Average | --- | --- | --- | --- | 7.495 | 21.85 | 0.9625 | 0.00815 | 0.84693 | 2.09 | 0.75 | 1.34 | 23.6 | 7.9839 | 24 | 41.75 | BMRL | 10.7616 | 1.8107 | 24.3332 | 36.9055 | BMRL | BMRL | BMRL | BMRL | 7.5088 | 2.2051 | BMRL | BMRL | BMRL | 7.5088 | 9.7139 | Avg-C3-20 | Average | --- | --- | --- | --- | 7.615 | 20.1 | 0.69 | 0.005275 | 0.76449 | 1.89 | 0.79 | 1.1 | 23.5 | 8.01 | 23.9 | 29.8 | BMRL | 6.2585 | 1.0382 | 17.8269 | 25.1236 | BMRL | BMRL | BMRL | BMRL | 4.2487 | 1.1782 | BMRL | BMRL | BMRL | 4.2487 | 5.4269
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 7.9247 | NA | NA | 7.9302 | NA | 7.9859 |  |  |  |  | 7.9469 | 0.4258 | SDS-Chlorination pH | --- | 7.9247 | NA | NA | 7.9302 | NA | 7.9859 |  |  |  |  | 7.9469 | 0.4258 | RPD-C5-10 | RPD | --- | --- | --- | --- | 0.40027 | 1.373 | 1.5584 | 3.681 | 5.2387 | 0 | 13.3333 | 7.4627 | 0 | 0.89404 | 0 | 3.8323 |  | 1.8308 | 0.5977 | 4.6589 | 3.5763 |  |  |  |  | 9.9296 | 0.55597 |  |  |  | 9.9296 | 7.8018 | RPD-C3-20 | RPD | --- | --- | --- | --- | 0.39396 | 0 | 0 | 6.6351 | 6.6351 | 0 | 5.0633 | 3.6364 | 0 | 0 | 0 | 4.698 |  | 0.47844 | 2.6981 | 3.4136 | 2.4299 |  |  |  |  | 6.1871 | 6.7216 |  |  |  | 6.1871 | 6.3032
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 23.9 | NA | NA | 23.8 | NA | 24.5 |  |  |  |  | 24.0667 | 1.5731 | SDS-Incubation time | hours | 23.9 | NA | NA | 23.8 | NA | 24.5 |  |  |  |  | 24.0667 | 1.5731 | C8-10 | Primary | 1998-11-10 | 11:52 | 93.6167 | 5302.448 | 7.44 | 21.7 | 1.815 | 0.0182 | 1.0028 | 2.78 | 0.84 | 1.94 | 23.5 | 8.005 | 24.4 | 96.25 | 1.2749 | 25.9348 | 7.279 | 35.8 | 70.2887 | BMRL | 1.4677 | BMRL | BMRL | 10.509 | 4.2824 | 4.7174 | 2.5017 | 1.6162 | 11.9767 | 16.2591 | C7-20 | Primary | 1998-11-16 | 04:27 | 230.2 | 13038.528 | 7.38 | 20 | 1.775 | 0.0172 | 0.96901 | 2.6 | 0.87 | 1.73 | 23.5 | 7.9199 | 23.8 | 91 | 1.2864 | 25.6716 | 6.9333 | 32.4 | 66.2914 | BMRL | 1.0809 | BMRL | BMRL | 8.6345 | 3.7564 | BMRL | 2.1891 | 1.5981 | 9.7155 | 13.4718
|  |  |  | Estimated full-scale run time, tLCT (days) | 110.8982 | [5 empty] | SDS-TOX | mg Cl- /L | 387.6 | NA | NA | 368.05 | NA | 384.8 |  |  |  |  | 380.15 | 2.781 | SDS-TOX | mg Cl- /L | 387.6 | NA | NA | 368.05 | NA | 384.8 |  |  |  |  | 380.15 | 2.781 | D-C8-10 | Duplicate | 1998-11-10 | 11:52 | 93.6167 | 5302.448 | 7.46 | 21.7 | 1.815 | 0.0184 | 1.0138 | 2.78 | 0.9 | 1.88 | 23.5 | 8.07 | 24.4 | 101.65 | 1.3391 | 27.0492 | 7.5941 | 36.9 | 72.8825 | BMRL | 1.5376 | BMRL | BMRL | 12.1615 | 4.708 | 5.2808 | 2.6942 | 1.9952 | 13.699 | 18.407 | D-C7-20 | Duplicate | 1998-11-16 | 04:27 | 230.2 | 13038.528 | 7.4 | 20 | 1.79 | 0.0172 | 0.96089 | 2.6 | 0.85 | 1.75 | 23.5 | 7.9399 | 23.9 | 90.7 | 1.2277 | 25.2518 | 6.7104 | 31.6 | 64.79 | BMRL | 1.2549 | BMRL | BMRL | 10.9268 | 4.4173 | BMRL | 2.6606 | 1.938 | 12.1816 | 16.599
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1186 | [5 empty] | SDS-CHCl3 | mg/L | 39.0213 | NA | NA | 34.6001 | NA | 41.5163 |  |  |  |  | 38.3792 | 9.1261 | SDS-CHCl3 | mg/L | 39.0213 | NA | NA | 34.6001 | NA | 41.5163 |  |  |  |  | 38.3792 | 9.1261 | Avg-C8-10 | Average | --- | --- | --- | --- | 7.45 | 21.7 | 1.815 | 0.0183 | 1.0083 | 2.78 | 0.87 | 1.91 | 23.5 | 8.0375 | 24.4 | 98.95 | 1.307 | 26.492 | 7.4366 | 36.35 | 71.5856 | BMRL | 1.5026 | BMRL | BMRL | 11.3352 | 4.4952 | 4.9991 | 2.5979 | 1.8057 | 12.8379 | 17.3331 | Avg-C7-20 | Average | --- | --- | --- | --- | 7.39 | 20 | 1.7825 | 0.0172 | 0.96495 | 2.6 | 0.86 | 1.74 | 23.5 | 7.9299 | 23.85 | 90.85 | 1.2571 | 25.4617 | 6.8219 | 32 | 65.5407 | BMRL | 1.1679 | BMRL | BMRL | 9.7807 | 4.0868 | BMRL | 2.4248 | 1.7681 | 10.9486 | 15.0354
|  |  |  | Estimated RSSCT run time, tSCT (days) | 11.7477 | [5 empty] | SDS-BDCM | mg/L | 62.1026 | NA | NA | 53.8433 | NA | 61.0505 |  |  |  |  | 58.9988 | 7.6199 | SDS-BDCM | mg/L | 62.1026 | NA | NA | 53.8433 | NA | 61.0505 |  |  |  |  | 58.9988 | 7.6199 | RPD-C8-10 | RPD | --- | --- | --- | --- | 0.26846 | 0 | 0 | 1.0929 | 1.0929 | 0 | 6.8966 | 3.1414 | 0 | 0.80907 | 0 | 5.4573 | 4.9166 | 4.2067 | 4.2371 | 3.0261 | 3.6233 |  | 4.6504 |  |  | 14.578 | 9.4665 | 11.2702 | 7.412 | 20.9874 | 13.416 | 12.3917 | RPD-C7-20 | RPD | --- | --- | --- | --- | 0.27064 | 0 | 0.84151 | 0 | 0.84151 | 0 | 2.3256 | 1.1494 | 0 | 0.25221 | 0.41929 | 0.33021 | 4.6709 | 1.6488 | 3.2675 | 2.5 | 2.2908 |  | 14.8911 |  |  | 23.4365 | 16.173 |  | 19.4445 | 19.225 | 22.5249 | 20.7984
|  |  |  | RSSCT bed length, lSC (cm) | 28.4415 | [5 empty] | SDS-DBCM | mg/L | 57.7187 | NA | NA | 53.632 | NA | 61.2927 |  |  |  |  | 57.5478 | 6.6609 | SDS-DBCM | mg/L | 57.7187 | NA | NA | 53.632 | NA | 61.2927 |  |  |  |  | 57.5478 | 6.6609 | C12-10 | Primary | 1998-11-13 | 09:18 | 163.05 | 9235.152 | 7.52 | 20 | 3.03 | 0.04185 | 1.3812 | 3.74 | 1.1 | 2.64 | 23.5 | 7.975 | 23.9 | 199.85 | 7.6511 | 56.206 | 28.1673 | 39 | 131.0244 | BMRL | 3.9915 | 1.641 | BMRL | 13.9353 | 9.4944 | 5.4377 | 5.0441 | 4.5322 | 19.5678 | 29.0622 | C10-20 | Primary | 1998-11-19 | 20:24 | 318.15 | 18020.016 | 7.47 | 21 | 2.675 | 0.0309 | 1.1551 | 3.15 | 0.88 | 2.27 | 23.5 | 7.939 | 24 | 152 | 4.1022 | 50.2868 | 19.4642 | 43.25 | 117.1032 | BMRL | 2.7214 | 1.2176 | BMRL | 15.6192 | 8.1805 | 5.7901 | 4.1394 | 3.5266 | 19.5581 | 27.7385
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 215.8162 | [5 empty] | SDS-CHBr3 | mg/L | 17.9 | NA | NA | 17 | NA | 20.8 |  |  |  |  | 18.5667 | 10.6954 | SDS-CHBr3 | mg/L | 17.9 | NA | NA | 17 | NA | 20.8 |  |  |  |  | 18.5667 | 10.6954 | D-C12-10 | Duplicate | 1998-11-13 | 09:18 | 163.05 | 9235.152 | 7.5 | 20.2 | 3.015 | 0.0417 | 1.3831 | 3.74 | 1.06 | 2.68 | 23.5 | 8 | 23.9 | 200.65 | 7.4467 | 55.1585 | 27.4607 | 36 | 126.0658 | BMRL | 4.2287 | 1.6853 | BMRL | 15.0581 | 9.9817 | 5.5856 | 5.1444 | 5.0202 | 20.972 | 30.9538 | D-C10-20 | Duplicate | 1998-11-19 | 20:24 | 318.15 | 18020.016 | 7.52 | 21 | 2.645 | 0.03055 | 1.155 | 3.15 | 0.92 | 2.23 | 23.5 | 8.0347 | 24 | 152.45 | 3.7542 | 50.2268 | 18.4658 | 43.2 | 115.6468 | BMRL | 2.7106 | 1.0662 | BMRL | 15.2713 | 7.935 | 5.8461 | 3.9537 | 3.3892 | 19.0482 | 26.9831
|  |  |  | Mass GAC required, mSC (g) | 12.6225 | [5 empty] | SDS-THM4 | mg/L | 176.7426 | NA | NA | 159.0754 | NA | 184.6595 |  |  |  |  | 173.4925 | 7.5496 | SDS-THM4 | mg/L | 176.7426 | NA | NA | 159.0754 | NA | 184.6595 |  |  |  |  | 173.4925 | 7.5496 | Avg-C12-10 | Average | --- | --- | --- | --- | 7.51 | 20.1 | 3.0225 | 0.041775 | 1.3821 | 3.74 | 1.08 | 2.66 | 23.5 | 7.9875 | 23.9 | 200.25 | 7.5489 | 55.6822 | 27.814 | 37.5 | 128.5451 | BMRL | 4.1101 | 1.6631 | BMRL | 14.4967 | 9.7381 | 5.5116 | 5.0942 | 4.7762 | 20.2699 | 30.008 | Avg-C10-20 | Average | --- | --- | --- | --- | 7.495 | 21 | 2.66 | 0.030725 | 1.1551 | 3.15 | 0.9 | 2.25 | 23.5 | 7.9869 | 24 | 152.225 | 3.9282 | 50.2568 | 18.965 | 43.225 | 116.375 | BMRL | 2.716 | 1.1419 | BMRL | 15.4452 | 8.0577 | 5.8181 | 4.0466 | 3.4579 | 19.3031 | 27.3608
[11 empty] | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MCAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | RPD-C12-10 | RPD | --- | --- | --- | --- | 0.26631 | 0.99502 | 0.49628 | 0.35907 | 0.13721 | 0 | 3.7037 | 1.5038 | 0 | 0.31335 | 0 | 0.3995 | 2.7081 | 1.8813 | 2.5404 | 8 | 3.8574 |  | 5.7712 | 2.6607 |  | 7.7453 | 5.0039 | 2.6843 | 1.9674 | 10.2169 | 6.9278 | 6.3035 | RPD-C10-20 | RPD | --- | --- | --- | --- | 0.66711 | 0 | 1.1278 | 1.1391 | 0.011318 | 0 | 4.4444 | 1.7778 | 0 | 1.1992 | 0 | 0.29562 | 8.8593 | 0.11936 | 5.2645 | 0.11567 | 1.2515 |  | 0.39582 | 13.2518 |  | 2.2521 | 3.0469 | 0.96086 | 4.5891 | 3.9723 | 2.6416 | 2.761
[11 empty] | SDS-DCAA* | mg/L | 14.6166 | NA | NA | 13.0955 | NA | 13.2193 |  |  |  |  | 13.6438 | 6.1915 | SDS-DCAA* | mg/L | 14.6166 | NA | NA | 13.0955 | NA | 13.2193 |  |  |  |  | 13.6438 | 6.1915 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 7.8526 | NA | NA | 6.4042 | NA | 6.2797 |  |  |  |  | 6.8455 | 12.7728 | SDS-TCAA* | mg/L | 7.8526 | NA | NA | 6.4042 | NA | 6.2797 |  |  |  |  | 6.8455 | 12.7728 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-MBAA* | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-DBAA* | mg/L | 15.5448 | NA | NA | 14.7011 | NA | 14.0433 |  |  |  |  | 14.7631 | 5.0985 | SDS-DBAA* | mg/L | 15.5448 | NA | NA | 14.7011 | NA | 14.0433 |  |  |  |  | 14.7631 | 5.0985
[11 empty] | SDS-BCAA* | mg/L | 18.7892 | NA | NA | 17.8027 | NA | 17.2433 |  |  |  |  | 17.9451 | 4.3617 | SDS-BCAA* | mg/L | 18.7892 | NA | NA | 17.8027 | NA | 17.2433 |  |  |  |  | 17.9451 | 4.3617
[11 empty] | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL |  | SDS-TBAA | mg/L | BMRL | NA | NA | BMRL | NA | BMRL |  |  |  |  | BMRL
[11 empty] | SDS-CDBAA | mg/L | 9.2376 | NA | NA | 6.2909 | NA | 5.9181 |  |  |  |  | 7.1489 | 25.437 | SDS-CDBAA | mg/L | 9.2376 | NA | NA | 6.2909 | NA | 5.9181 |  |  |  |  | 7.1489 | 25.437
[11 empty] | SDS-DCBAA | mg/L | 13.8616 | NA | NA | 11.2307 | NA | 10.796 |  |  |  |  | 11.9627 | 13.8659 | SDS-DCBAA | mg/L | 13.8616 | NA | NA | 11.2307 | NA | 10.796 |  |  |  |  | 11.9627 | 13.8659
[11 empty] | SDS-HAA5 | mg/L | 38.0141 | NA | NA | 34.2009 | NA | 33.5423 |  |  |  |  | 35.2524 | 6.8484 | SDS-HAA5 | mg/L | 38.0141 | NA | NA | 34.2009 | NA | 33.5423 |  |  |  |  | 35.2524 | 6.8484
[11 empty] | SDS-HAA6 | mg/L | 56.8032 | NA | NA | 52.0036 | NA | 50.7856 |  |  |  |  | 53.1974 | 5.9806 | SDS-HAA6 | mg/L | 56.8032 | NA | NA | 52.0036 | NA | 50.7856 |  |  |  |  | 53.1974 | 5.9806
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [13 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [13 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H22: Reviewer M.H. (11/13/99): Per Consultant: "Scaling Factor was determined using opening dimensions given by the sieve manufacturer, which differ slightly from dimensions in the DCS".