## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.wk4)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC(1) |  |  | Field 1-4: Influent Water Quality For The Pilot-Scale GAC Contactors(1) | [14 empty] | Field 1-4: Influent Water Quality For The Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The Pilot-Scale GAC Contactor(1) | [16 empty] | Field 1-5: Effluent Water Quality For The Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor(1) | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | Manchester Water Works | Carbon manufacturer | Calgon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | WTP LS | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV-254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV-254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV-254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value | Cost Estimates on the operation of Manchester Water Works GAC Filters
Public Water System Identification Number | 1471010 | Carbon trade name | Filtrasorb 300 | mesh size | (mm) | Coagulation | Alum/Polyaluminum Chloride Flocculation 22/5 mg/l | Full scale (40 MGD) | ID | duplicated? | date | time | time | volumes | Totalizer |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | NA |  | Capital Costs Filters and Building (20 yr straight line) 1 | Reactivation Cost based on a 4 year replacement cycle4 | Electrical and Backwash | Repair and Maintenance | Total
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 | Sedimentation | Unassisted Gravity Sedimentation (80 minutes @15 MGD) | Full scale (40 MGD) |  | Y/N | MM/DD/YY | hh:mm | hh.hh |  | MG |  | ntu | mg/L as CaCO3 | C | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | ug/L | mg/L | 1/cm | L/(mg*m) | mg/L | mg/L | mg/L | C | --- | hours | ug Cl- /L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh |  | --- | ntu | C | mg NH3-N / L | mg/L | 1/cm | L/(mg*m) | mg/L | mg/L | mg/L | C | --- | hours | ug Cl- /L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | C | mg NH3-N / L | mg/L | 1/cm | L/(mg*m) | mg/L | mg/L | mg/L | C | --- | hours | ug Cl- /L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | Capital Recovery Period (years) | NA | $ / MG (based on a flow of 15 MGD) | 11.25 | 10 | 4.56 | 1.83 | 27.64
|  | Pilot GAC influent TOC (mg/L) | 2.4 | 6 | 3.35 | Disinfection | Chlorination with sodium hypochlorite following Sedimentation | Full scale (40 MGD) | START | N | 1999-01-05 | 11:15 | 0 | 0 | 29 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1999-01-05 | 11:15 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- |  |  | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | NA | $/Yr (1998) 2 | 61594 | 60000 | 25000 | 10000 | 156594
Official ICR Contact Person |  | Inner diameter of the pilot GAC column (mm) | NA | 8 | 2.36 | Sand Filtration | Rapid sand filters - 4 gpm/ft2 @ 11 inch x 0.7 mm media | Full scale (40 MGD) | IN02 | N | 1999-01-06 | 9:20 | 22.0833 | 85.2273 | 34 | 6.61 | 0.08 | NR | 4.5 | NR | NR | BMRL | BMRL | 2.81 | 0.038 | 1.3523 | 2.4 | 1.75 | 0.65 | 4.5 | 7.56 | 24 | 182 | 30.8 | 4.25 | BMRL | BMRL | 35.05 | 2.66 | 33.4 | 20.9 | BMRL | BMRL | 1.52 | NA | NA | NA | 56.96 | 58.48 | EFF02 | N | 1999-01-06 | 9:20 | 22.0833 | 85.2273 | 7.45 | 0.06 | 4.5 | BMRL | 0.7 | BMRL | #VALUE! | 1.92 | 1.22 | 0.7 | 4.5 | 7.22 | 24 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Special Sitework Factor (% of construction costs) | NA | $/lb reactivate (1998) 3 |  | 0.25
Mailing Address |  | Manufacturer reported dry bed density (kg/m^3) | 480 | 10 | 2 |  |  |  | IN03 | N | 1999-01-11 | 10:05 | 142.8333 | 542.9293 | 66 | 6.56 | 0.09 | 8 | 4.5 | 12 | 10 | BMRL | BMRL | 2.84 | 0.034 | 1.1972 | 2.34 | 1.82 | 0.52 | 4.5 | 7.31 | 24 | 221.5 | 19.2 | 3.24 | BMRL | BMRL | 22.44 | 3.39 | 26.9 | 19.1 | 1.07 | BMRL | 1.74 | NA | NA | NA | 50.46 | 52.2 | EFF03 | N | 1999-01-11 | 10:05 | 142.8333 | 542.9293 | 7.21 | 0.05 | 4.5 | BMRL | 0.74 | BMRL | #VALUE! | 2.34 | 2.08 | 0.26 | 4.5 | 7.56 | 24 | BMRL | 1.72 | BMRL | BMRL | BMRL | 1.72 | BMRL | 2.33 | 1.63 | BMRL | BMRL | BMRL | NA | NA | NA | 3.96 | 3.96 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Construction Contingencies (% of construction costs) | NA
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 |  |  |  | IN04 | N | 1999-01-13 | 9:45 | 190.5 | 713.3838 | 79 | 6.62 | 0.08 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 2.82 | 0.03 | 1.0638 | 1.66 | 1.51 | 0.15 | 4.5 | 7.42 | 24 | 231 | 29.1 | 4.53 | BMRL | BMRL | 33.63 | 3.22 | 24.8 | 17.6 | 1.11 | BMRL | 1.42 | NA | NA | NA | 46.73 | 48.15 | EFF04 | N | 1999-01-13 | 9:45 | 190.5 | 713.3838 | 6.96 | 0.05 | 4.5 | BMRL | 0.82 | BMRL | #VALUE! | 1.66 | 1.76 | -0.1 | 4.5 | 7.24 | 24 | 33.5 | 2.6 | BMRL | BMRL | BMRL | 2.6 | BMRL | 4.09 | 3.92 | BMRL | 1.22 | 1.32 | NA | NA | NA | 9.23 | 10.55 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Engineering Fee Factor (% of construction costs) | NA | Notes:
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 |  |  |  | IN05 | N | 1999-01-18 | 9:25 | 310.1667 | 1142.6768 | 108 | 6.63 | 0.15 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 3.07 | 0.059 | 1.9218 | 1.2 | 0.84 | 0.36 | 4.5 | 7.48 | 24 | 222 | 23.7 | 3.55 | BMRL | BMRL | 27.25 | 3.45 | 29.8 | 20.1 | BMRL | BMRL | 1.34 | NA | NA | NA | 53.35 | 54.69 | EFF05 | N | 1999-01-18 | 9:25 | 310.1667 | 1142.6768 | 6.83 | 0.09 | 4.5 | BMRL | 1.33 | 0.014 | 1.0526 | 1.2 | 0.94 | 0.26 | 4.5 | 7.36 | 24 | 46 | 5.1 | 1.13 | BMRL | BMRL | 6.23 | 2.12 | 6.29 | 3.99 | BMRL | BMRL | BMRL | NA | NA | NA | 12.4 | 12.4 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | NA | 1 Capital cost figures for this unit process have been somewhat problematic to obtain. The filters were built in 1974 as a fraction of a single bid and I have not been able to come up with a table of values to estimate their 1974 worth.
FAX Number |  | Flow rate (L/hr) | 788542 | 20 | 0.85 |  |  |  | IN06 | N | 1999-01-20 | 10:12 | 358.95 | 1319.4444 | 118 | 6.59 | 0.09 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 2.82 | 0.037 | 1.3121 | 1.2 | 0.54 | 0.66 | 4.5 | 7.4 | 24 | 206 | 26.8 | 4.31 | BMRL | BMRL | 31.11 | 2.52 | 46.5 | 23.7 | 1.13 | BMRL | 1.98 | NA | NA | NA | 73.85 | 75.83 | EFF06 | N | 1999-01-20 | 10:30 | 359.25 | 1319.4444 | 6.85 | 0.05 | 4.5 | BMRL | 1.22 | 0.014 | 1.1475 | 1.2 | 0.9 | 0.3 | 4.5 | 7.22 | 24 | 60 | 5.03 | 1.16 | BMRL | BMRL | 6.19 | BMRL | 5.62 | 3.69 | BMRL | BMRL | BMRL | NA | NA | NA | 9.31 | 9.31 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA | Based upon their overall fraction of the WTP expense, my estimate would have put their capital structure at about $750,000 (including building and filters) of the overall WTP expense ($5,900,000). Add to that an initial charge of GAC valued at approximately $400,000 and the total cost for this system is estimated at $1,150,000.
E-Mail Address (optional) |  |  |  | 30 | 0.6 |  |  |  | IN07 | N | 1999-01-25 | 10:30 | 479.25 | 1756.9444 | 145.6 | 6.6 | 0.13 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 3.09 | 0.041 | 1.3269 | 1.37 | 0.93 | 0.44 | 4.5 | 7.93 | 24 | 226 | 29.5 | 4.46 | BMRL | BMRL | 33.96 | 2.86 | 27.2 | 16.8 | BMRL | BMRL | 1.31 | NA | NA | NA | 46.86 | 48.17 | EFF07 | N | 1999-01-25 | 10:45 | 479.5 | 1756.9444 | 6.91 | 0.08 | 4.5 | BMRL | 1.49 | 0.015 | 1.0067 | 1.37 | 0.9 | 0.47 | 4.5 | 7.63 | 24 | 59 | 7.01 | 1.44 | BMRL | BMRL | 8.45 | BMRL | 8.71 | 5.2 | BMRL | BMRL | BMRL | NA | NA | NA | 13.91 | 13.91 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Labor Rate + Fringe ($/work-hour) | NA | 2 Values based upon straight line depreciation for equipment and structure, a reactivation expense of approximately $0.25 / lb, power expense at $0.10 / KWH backwash water at $350 / MG and repair and maintenance reflecting filter maintenance and backwash pump repairs
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | IN08 | Y | 1999-01-28 | 11:00 | 551.75 | 2050.8838 | 167.53 | 6.65 | 0.11 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 2.85 | 0.039 | 1.3682 | 1.36 | 0.86 | 0.5 | 4.5 | 7.6 | 24 | 247 | 28.2 | 6.715 | 0.325 | BMRL | 35.24 | 3.355 | 59.1 | 29.1 | 1.305 | BMRL | 2.39 | NA | NA | NA | 92.86 | 95.25 | EFF08 | Y | 1999-01-28 | 11:30 | 552.25 | 2050.947 | 6.655 | 0.07 | 4.5 | BMRL | 1.4 | 0.013 | 0.92862 | 1.36 | 1.05 | 0.31 | 4.5 | 7.75 | 24 | 80 | 10.23 | 2.92 | BMRL | BMRL | 13.15 | 2.08 | 18.5 | 9.55 | 0.665 | BMRL | BMRL | NA | NA | NA | 30.795 | 30.795 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Labor Overhead Factor (% of labor) | NA | 3 Reactivation cost is based upon all utility, repair and maintenance, labor and depreciation costs divided by the total mass of spent GAC reactivated that year.
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough | 6953.2064 | 50 | 0.3 |  |  |  | IN09 | N | 1999-02-03 | 10:00 | 694.75 | 2581.4394 | 204.7 | 6.65 | 0.1 | 6 | 4.5 | 14 | 10 | BMRL | BMRL | 2.97 | 0.041 | 1.3805 | 1.18 | 1.03 | 0.15 | 4.5 | 7.76 | 24 | 270 | 29.8 | 6.55 | BMRL | BMRL | 36.35 | 2.92 | 43.2 | 30 | BMRL | BMRL | 1.34 | NA | NA | NA | 76.12 | 77.46 | EFF09 | N | 1999-02-03 | 10:30 | 695.25 | 2581.4394 | 6.76 | 0.07 | 4.5 | BMRL | 1.79 | 0.014 | 0.78212 | 1.18 | 0.69 | 0.49 | 4.5 | 7.77 | 24 | 100 | 11.4 | 3.37 | BMRL | BMRL | 14.77 | BMRL | 19.5 | BMRL | BMRL | BMRL | 1.22 | NA | NA | NA | 19.5 | 20.72 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Electric Rate ($/kW-h) | NA | As such it depends entirely on how often the GAC is replaced or reactivated. Since 1981 this value has ranged from approximately $8 to $10 per million gallons processed. This reflects the reactivation of a single carbon filter (estimated 200,000 # virgin: 246,000 # spent) each year at a total cost of about $60,000. For Manchester this is a four (4) year replacement frequency.
Mailing Address |  | Estimated run length | 13906.4127 | 60 | 0.25 |  |  |  | IN10 | N | 1999-02-10 | 10:20 | 863.0833 | 3197.601 | 246.9 | 6.49 | 0.08 | 4 | 4.5 | 10 | 8 | BMRL | BMRL | 2.47 | 0.029 | 1.1741 | 1.19 | 0.69 | 0.5 | 4.5 | 7.7 | 24 | 177 | 18.8 | 4.53 | BMRL | BMRL | 23.33 | 3.12 | 36.9 | 19.7 | 1.57 | BMRL | 2.76 | NA | NA | NA | 61.29 | 64.05 | EFF10 | N | 1999-02-10 | 10:30 | 863.25 | 3197.601 | 6.83 | 0.05 | 4.5 | BMRL | 1.44 | 0.014 | 0.97222 | 1.19 | 0.78 | 0.41 | 4.5 | 7.39 | 24 | 75 | 7.04 | 1.93 | BMRL | BMRL | 8.97 | 3.07 | 12.8 | 7.7 | BMRL | BMRL | 1.08 | NA | NA | NA | 23.57 | 24.65 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Fuel Oil Rate ($/gal) | NA
|  |  |  | 70 | 0.21 |  |  |  | IN11 | N | 1999-02-19 | 13:40 | 1082.4167 | 3905.303 | 294.1 | 6.65 | 0.18 | 4 | 5 | 10 | 8 | BMRL | BMRL | 2.47 | 0.018 | 0.72874 | 1.15 | 0.72 | 0.43 | 5 | 7.08 | 24 | 172 | 30 | 4.32 | BMRL | BMRL | 34.32 | 3.54 | 45.5 | 23.1 | 1.41 | BMRL | 2.22 | NA | NA | NA | 73.55 | 75.77 | EFF11 | N | 1999-02-19 | 14:10 | 1082.9167 | 3905.303 | 6.72 | 0.07 | 5 | BMRL | 1.69 | 0.012 | 0.71006 | 1.15 | 0.46 | 0.69 | 5 | 7.24 | 24 | 85 | 12.4 | 2.44 | BMRL | BMRL | 14.84 | 2.46 | 21 | 8.96 | BMRL | BMRL | 1.46 | NA | NA | NA | 32.42 | 33.88 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Natural Gas Rate ($/ft^3) | NA
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | IN12 | Y | 1999-02-24 | 9:30 | 1198.25 | 4448.2323 | 331.1 | 6.215 | 0.14 | 6 | 5 | 12 | 8 | BMRL | BMRL | 2.365 | 0.021 | 0.88804 | 0.95 | 0.675 | 0.275 | 5 | 7.325 | 24 | 151 | 26 | 3.335 | BMRL | BMRL | 29.335 | 3.055 | 37.95 | 16.2 | 0 | BMRL | 2.14 | NA | NA | NA | 57.205 | 59.345 | EFF12 | Y | 1999-02-24 | 10:00 | 1198.75 | 4448.2323 | 6.815 | 0.05 | 5 | BMRL | 1.46 | 0.012 | 0.82192 | 0.95 | 0.635 | 0.315 | 5 | 7.325 | 24 | 64 | 13.05 | 2.525 | BMRL | BMRL | 15.575 | 3.35 | 18.25 | 7.865 | BMRL | BMRL | 0.6 | NA | NA | NA | 29.465 | 30.065 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Current Process Water Rate ($/1000 gal) | NA
FAX Number |  | Carbon particle diameter (mm) | 1.48 | [5 empty] | IN13 | N | 1999-03-03 | 11:10 | 1367.9167 | 5002.5253 | 381.3 | 6.69 | 0.14 | 6 | 5 | 12 | 10 | BMRL | BMRL | 2.43 | 0.036 | 1.4815 | 1.03 | 0.62 | 0.41 | 5 | 7.62 | 24 | 124 | 23.2 | 4.02 | BMRL | BMRL | 27.22 | 3.99 | 45.9 | 26.3 | BMRL | BMRL | 2.58 | NA | NA | NA | 76.19 | 78.77 | EFF13 | N | 1999-03-03 | 12:00 | 1368.75 | 5002.5253 | 6.86 | 0.06 | 5 | BMRL | 1.59 | 0.01 | 0.62893 | 0.95 | 0.55 | 0.4 | 5 | 7.73 | 24 | 115 | 25.9 | 3.63 | BMRL | BMRL | 29.53 | BMRL | 17.1 | 7.82 | BMRL | BMRL | 1.01 | NA | NA | NA | 24.92 | 25.93 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | NA
E-Mail Address (optional) |  | Column cross-sectional area (m^2) | NA | [5 empty] | IN14 | N | 1999-03-10 | 10:00 | 1534.75 | 5604.798 | 424.5 | 6.43 | 0.12 | 6 | 4 | 12 | 10 | BMRL | BMRL | 2.34 | 0.033 | 1.4103 | 1.21 | 0.63 | 0.58 | 4 | 7.55 | 24 | 179 | 20.9 | 3.79 | BMRL | BMRL | 24.69 | 2.53 | 33.3 | 16.1 | BMRL | BMRL | 1.73 | NA | NA | NA | 51.93 | 53.66 | EFF14 | N | 1999-03-10 | 10:45 | 1535.5 | 5604.798 | 6.56 | 0.05 | 4 | BMRL | 1.53 | BMRL | #VALUE! | 1.21 | 0.72 | 0.49 | 4 | 7.63 | 24 | 88 | 12.6 | 2.66 | BMRL | BMRL | 15.26 | 6.09 | 13.3 | 9.46 | BMRL | BMRL | BMRL | NA | NA | NA | 28.85 | 28.85 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Hydraulic loading rate(1) (m/hr) | 5 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | IN15 | N | 1999-03-24 | 9:00 | 1869.75 | 6786.6162 | 510 | 6.58 | 0.16 | 6 | 4.5 | NR | NR | BMRL | BMRL | 2.32 | 0.042 | 1.8103 | 1.16 | 0.68 | 0.48 | 4.5 | 7.56 | 24 | 208 | 33.6 | 5.7 | BMRL | BMRL | 39.3 | 4.66 | 43.3 | 22.2 | BMRL | BMRL | 2.17 | NA | NA | NA | 70.16 | 72.33 | EFF15 | N | 1999-03-24 | 10:00 | 1870.75 | 6786.6162 | 6.62 | 0.07 | 4.5 | BMRL | 1.59 | 0.025 | 1.5723 | 1.16 | 0.71 | 0.45 | 4.5 | 7.68 | 24 | 110 | 29.5 | 4.33 | BMRL | BMRL | 33.83 | 3.64 | 12 | 7.95 | BMRL | BMRL | 1.27 | NA | NA | NA | 23.59 | 24.86 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Manchester Water Treatment Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | IN16 | Y | 1999-03-31 | 9:45 | 2038.5 | 7400.8838 | 554.2 | 6.365 | 0.13 | NR | 6.5 | NR | NR | BMRL | BMRL | 2.48 | 0.0375 | 1.512 | 1.26 | 0.83 | 0.43 | 6.5 | 7.595 | 24 | 257 | 38.15 | 4.92 | BMRL | BMRL | 43.07 | 5.245 | 46.85 | 31.3 | 0.84 | BMRL | 1.56 | NA | NA | NA | 84.235 | 85.795 | EFF16 | Y | 1999-03-31 | 10:15 | 2039 | 7400.8838 | 6.51 | 0.07 | 6.5 | BMRL | 1.99 | 0.0245 | 1.2313 | 1.26 | 0.46 | 0.8 | 6.5 | 7.72 | 24 | 142.5 | 19.05 | 4.09 | BMRL | BMRL | 23.14 | 3.09 | 22.5 | 13.3 | BMRL | BMRL | 1.065 | NA | NA | NA | 38.89 | 39.955 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | Conv |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. | [7 empty] | -410.3535 | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 | [5 empty] | -410.3535 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | ALUM & PAC | Pilot run | [10 empty] | -867971.25 | -410.3535 | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | -410.3535 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
ICR Treatment Plant Identification Number | 456 | Empty bed contact time (min) | 15 | [9 empty] | -867971.25 | -410.3535 | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | -410.3535 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
PWSID Number of Plant (if assigned) | 1471010 | Estimated run time (days) | 120 | [9 empty] | -867971.25 | -410.3535 | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Minimum Water Temperature (C) | 3 | Pilot column bed length (m) | 1.25 | [9 empty] | -867971.25 | #VALUE! | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Historical Average Water Temperature (C) | 8.6 | Mass GAC required (kg) | 84059 | [9 empty] | -867971.25 | #VALUE! | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
State Approved Plant Capacity (MGD) | 40 | [11 empty] | -867971.25 | #VALUE! | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | 20-Minute EBCT Run | [10 empty] | -867971.25 | #VALUE! | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Empty bed contact time, EBCT (min) | NA | [9 empty] | -867971.25 | #VALUE! | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Estimated run time (days) | NA | [9 empty] | -867971.25 | -5207827.5 | [11 empty] | #DIV/0! | [11 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | -867971.25 | #VALUE! | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 |  |  |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  | Pilot column bed length (m) | NA | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required (kg) | NA | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | WTP LS | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV-254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV-254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV-254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | Totalizer |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 10 minute) | MG | --- | ntu | mg/L as CaCO3 | C | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | ug/L | mg/L | 1/cm | L/(mg*m) | mg/L | mg/L | mg/L | C | --- | hours | ug Cl- /L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L |  |  | MM/DD/YY | hh:mm | hh.hh |  | --- | ntu | C | mg NH3-N / L | mg/L | 1/cm | L/(mg*m) | mg/L | mg/L | mg/L | C | --- | hours | ug Cl- /L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | C | mg NH3-N / L | mg/L | 1/cm | L/(mg*m) | mg/L | mg/L | mg/L | C | --- | hours | ug Cl- /L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L
[9 empty] | IN08 | Primary | 1999-01-28 | 11:00 | 551.75 | 2050.9 | 167.53 | 6.64 | 0.11 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 2.87 | 0.04 | 1.3937 | 1.36 | 0.83 | 0.53 | 4.5 | 7.56 | 24 | 241 | 26.1 | 6.41 | 0.65 | BMRL | 33.16 | 2.96 | 58.2 | 25.3 | 1.15 | BMRL | 2.11 | NA | NA | NA | 87.61 | 89.72 | EF08 | Primary | 1999-01-28 | 11:30 | 552.25 | 2050.9 | 6.66 | 0.07 | 4.5 | BMRL | 1.41 | 0.013 | 0.92199 | 1.36 | 1.07 | 0.29 | 4.5 | 7.83 | 24 | 83 | 10.6 | 3.26 | BMRL | BMRL | 13.86 | 2.04 | 18.6 | 9.16 | 1.33 | BMRL | BMRL | NA | NA | NA | 31.13 | 31.13 |  | Primary |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
[9 empty] | IN08-2 | Duplicate | 1999-01-28 | 11:00 | 551.75 | 2050.9 | 167.53 | 6.66 | 0.11 | 8 | 4.5 | 14 | 10 | BMRL | BMRL | 2.83 | 0.038 | 1.3428 | 1.36 | 0.89 | 0.47 | 4.5 | 7.64 | 24 | 253 | 30.3 | 7.02 | BMRL | BMRL | 37.32 | 3.75 | 60 | 32.9 | 1.46 | BMRL | 2.67 | NA | NA | NA | 98.11 | 100.78 | EF08-2 | Duplicate | 1999-01-28 | 11:30 | 552.25 | #VALUE! | 6.65 | 0.07 | 4.5 | BMRL | 1.39 | 0.013 | 0.93525 | 1.36 | 1.03 | 0.33 | 4.5 | 7.67 | 24 | 77 | 9.86 | 2.58 | BMRL | BMRL | 12.44 | 2.12 | 18.4 | 9.94 | BMRL | BMRL | BMRL | NA | NA | NA | 30.46 | 30.46 |  | Duplicate |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
[10 empty] | Average | --- | --- | --- | #VALUE! | --- | 6.65 | 0.11 | 8 | 4.5 | 14 | 10 | 0 | 0 | 2.85 | 0.039 | 1.3682 | 1.36 | 0.86 | 0.5 | 4.5 | 7.6 | 24 | 247 | 28.2 | 6.715 | 0.325 | 0 | 35.24 | 3.355 | 59.1 | 29.1 | 1.305 | 0 | 2.39 | 0 | 0 | 0 | 92.86 | 95.25 |  | Average | --- | --- | --- | #VALUE! | 6.655 | 0.07 | 4.5 | 0 | 1.4 | 0.013 | 0.92862 | 1.36 | 1.05 | 0.31 | 4.5 | 7.75 | 24 | 80 | 10.23 | 2.92 | 0 | 0 | 13.15 | 2.08 | 18.5 | 9.55 | 0.665 | 0 | 0 | 0 | 0 | 0 | 30.795 | 30.795 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | #VALUE! | --- | 0.30075 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 1.4035 | 5.1282 | 3.7254 | 0 | 6.9767 | 12 | 0 | 1.0526 | 0 | 4.8583 | 14.8936 | 9.0841 | #VALUE! | #VALUE! | 11.8048 | 23.5469 | 3.0457 | 26.1168 | 23.7548 | #VALUE! | 23.431 | #VALUE! | #VALUE! | #VALUE! | 11.3073 | 11.6115 |  | RPD | --- | --- | --- | #VALUE! | 0.15026 | 0 | 0 | #VALUE! | 1.4286 | 0 | 1.4286 | 0 | 3.8095 | 12.9032 | 0 | 2.0645 | 0 | 7.5 | 7.2336 | 23.2877 | #VALUE! | #VALUE! | 10.7985 | 3.8462 | 1.0811 | 8.1675 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.1757 | 2.1757 |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | IN12 | Primary | 1999-02-24 | 9:30 | 1198.25 | 4448.2 | 331.1 | 6.22 | 0.14 | 6 | 5 | 12 | 8 | BMRL | BMRL | 2.36 | 0.022 | 0.9322 | 0.95 | 0.68 | 0.27 | 5 | 7.37 | 24 | 172 | 26.4 | 3.63 | BMRL | BMRL | 30.03 | 3.27 | 41.2 | 17.4 | BMRL | BMRL | 2.72 | NA | NA | NA | 61.87 | 64.59 | EFF12 | Primary | 1999-02-24 | 10:00 | 1198.75 | #VALUE! | 6.83 | 0.05 | 5 | BMRL | 1.46 | 0.012 | 0.82192 | 0.95 | 0.62 | 0.33 | 5 | 7.25 | 24 | 62 | 14.2 | 2.73 | BMRL | BMRL | 16.93 | 3.67 | 19.3 | 8.34 | BMRL | BMRL | 1.2 | NA | NA | NA | 31.31 | 32.51 |  | Primary |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
[9 empty] | IN12-2 | Duplicate | 1999-02-24 | 9:30 | 1198.25 | 4448.2 | 331.1 | 6.21 | 0.14 | 6 | 5 | 12 | 8 | BMRL | BMRL | 2.37 | 0.02 | 0.84388 | 0.95 | 0.67 | 0.28 | 5 | 7.28 | 24 | 130 | 25.6 | 3.04 | BMRL | BMRL | 28.64 | 2.84 | 34.7 | 15 | BMRL | BMRL | 1.56 | NA | NA | NA | 52.54 | 54.1 | EFF12-2 | Duplicate | 1999-02-24 | 10:00 | 1198.75 | #VALUE! | 6.8 | 0.05 | 5 | BMRL | 1.46 | 0.012 | 0.82192 | 0.95 | 0.65 | 0.3 | 5 | 7.4 | 24 | 66 | 11.9 | 2.32 | BMRL | BMRL | 14.22 | 3.03 | 17.2 | 7.39 | BMRL | BMRL | BMRL | NA | NA | NA | 27.62 | 27.62 |  | Duplicate |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
[10 empty] | Average | --- | --- | --- | #VALUE! | --- | 6.215 | 0.14 | 6 | 5 | 12 | 8 | 0 | 0 | 2.365 | 0.021 | 0.88804 | 0.95 | 0.675 | 0.275 | 5 | 7.325 | 24 | 151 | 26 | 3.335 | 0 | 0 | 29.335 | 3.055 | 37.95 | 16.2 | 0 | 0 | 2.14 | 0 | 0 | 0 | 57.205 | 59.345 |  | Average | --- | --- | --- | #VALUE! | 6.815 | 0.05 | 5 | 0 | 1.46 | 0.012 | 0.82192 | 0.95 | 0.635 | 0.315 | 5 | 7.325 | 24 | 64 | 13.05 | 2.525 | 0 | 0 | 15.575 | 3.35 | 18.25 | 7.865 | 0 | 0 | 0.6 | 0 | 0 | 0 | 29.465 | 30.065 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | #VALUE! | --- | 0.1609 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 0.42283 | 9.5238 | 9.9456 | 0 | 1.4815 | 3.6364 | 0 | 1.2287 | 0 | 27.8146 | 3.0769 | 17.6912 | #VALUE! | #VALUE! | 4.7384 | 14.0753 | 17.1278 | 14.8148 | #VALUE! | #VALUE! | 54.2056 | #VALUE! | #VALUE! | #VALUE! | 16.3098 | 17.6763 |  | RPD | --- | --- | --- | #VALUE! | 0.44021 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | 4.7244 | 9.5238 | 0 | 2.0478 | 0 | 6.25 | 17.6245 | 16.2376 | #VALUE! | #VALUE! | 17.3997 | 19.1045 | 11.5068 | 12.0788 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 12.5233 | 16.2648 |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | IN16 | Primary | 1999-03-31 | 9:45 | 2038.5 | 7400.9 | 554.2 | 6.33 | 0.13 | NR | 6.5 | NR | NR | BMRL | BMRL | 2.47 | 0.037 | 1.498 | 1.26 | 0.79 | 0.47 | 6.5 | 7.51 | 24 | 260 | 37.2 | 4.47 | BMRL | BMRL | 41.67 | 4.97 | 45 | 28.8 | 1.68 | BMRL | 1.68 | NA | NA | NA | 80.45 | 82.13 | EFF16 | Primary | 1999-03-31 | 10:15 | 2039 | #VALUE! | 6.5 | 0.07 | 6.5 | BMRL | 2 | 0.024 | 1.2 | 1.26 | 0.45 | 0.81 | 6.5 | 7.48 | 24 | 142 | 17.8 | 3.54 | BMRL | BMRL | 21.34 | 2.64 | 23.6 | 14.7 | BMRL | BMRL | 1.12 | NA | NA | NA | 40.94 | 42.06 |  | Primary |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
[9 empty] | IN 16-2 | Duplicate | 1999-03-31 | 9:45 | 2038.5 | 7400.9 | 554.2 | 6.4 | 0.13 | NR | 6.5 | NR | NR | BMRL | BMRL | 2.49 | 0.038 | 1.5261 | 1.26 | 0.87 | 0.39 | 6.5 | 7.68 | 24 | 254 | 39.1 | 5.37 | BMRL | BMRL | 44.47 | 5.52 | 48.7 | 33.8 | BMRL | BMRL | 1.44 | NA | NA | NA | 88.02 | 89.46 | EFF 16-2 | Duplicate | 1999-03-31 | 10:15 | 2039 | #VALUE! | 6.52 | 0.07 | 6.5 | BMRL | 1.98 | 0.025 | 1.2626 | 1.26 | 0.47 | 0.79 | 6.5 | 7.96 | 24 | 143 | 20.3 | 4.64 | BMRL | BMRL | 24.94 | 3.54 | 21.4 | 11.9 | BMRL | BMRL | 1.01 | NA | NA | NA | 36.84 | 37.85 |  | Duplicate |  |  | 0 | 0 | [6 empty] | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
[10 empty] | Average | --- | --- | --- | #VALUE! | --- | 6.365 | 0.13 | 0 | 6.5 | 0 | 0 | 0 | 0 | 2.48 | 0.0375 | 1.512 | 1.26 | 0.83 | 0.43 | 6.5 | 7.595 | 24 | 257 | 38.15 | 4.92 | 0 | 0 | 43.07 | 5.245 | 46.85 | 31.3 | 0.84 | 0 | 1.56 | 0 | 0 | 0 | 84.235 | 85.795 |  | Average | --- | --- | --- | #VALUE! | 6.51 | 0.07 | 6.5 | 0 | 1.99 | 0.0245 | 1.2313 | 1.26 | 0.46 | 0.8 | 6.5 | 7.72 | 24 | 142.5 | 19.05 | 4.09 | 0 | 0 | 23.14 | 3.09 | 22.5 | 13.3 | 0 | 0 | 1.065 | 0 | 0 | 0 | 38.89 | 39.955 |  | Average | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[10 empty] | RPD | --- | --- | --- | #VALUE! |  | 1.0998 | 0 | #VALUE! | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.80645 | 2.6667 | 1.8603 | 0 | 9.6386 | 18.6047 | 0 | 2.2383 | 0 | 2.3346 | 4.9803 | 18.2927 | #VALUE! | #VALUE! | 6.501 | 10.4862 | 7.8975 | 15.9744 | #VALUE! | #VALUE! | 15.3846 | #VALUE! | #VALUE! | #VALUE! | 8.9868 | 8.5436 |  | RPD | --- | --- | --- | --- | 0.30722 | 0 | 0 | #VALUE! | 1.005 | 4.0816 | 5.0861 | 0 | 4.3478 | 2.5 | 0 | 6.2176 | 0 | 0.70175 | 13.1234 | 26.8949 | #VALUE! | #VALUE! | 15.5575 | 29.1262 | 9.7778 | 21.0526 | #VALUE! | #VALUE! | 10.3286 | #VALUE! | #VALUE! | #VALUE! | 10.5426 | 10.5369 |  | RPD | --- | --- | --- | --- | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | WTP LS | WTP HS | [39 empty] | WTP LS | WTP HS
[9 empty] | Totalizer | Totalizer | [39 empty] | Totalizer | Totalizer
[9 empty] | MG | MG | [39 empty] | MG | MG
[9 empty] | 29 | 36 | [39 empty] | 29 | 36
[9 empty] | 34 | 44.5 | [39 empty] | 34 | 44.5
[9 empty] | 66 | 85 | [39 empty] | 66 | 85
[9 empty] | 79 | 99 | [39 empty] | 79 | 99
[9 empty] | 108 | 138 | [39 empty] | 108 | 138
[9 empty] | 118 | 156 | [39 empty] | 118 | 156
[9 empty] | 145.6 | 197.7 | [39 empty] | 145.6 | 197.7
[9 empty] | 167.53 | 222.33 | [39 empty] | 167.53 | 222.34
[9 empty] | 204.7 | 269.2 | [39 empty] | 204.7 | 269.2
[9 empty] | 246.9 | 324.6 | [39 empty] | 246.9 | 324.6
[9 empty] | 294.1 | 389.5 | [39 empty] | 294.1 | 389.5
[9 empty] | 331.1 | 438.5 | [39 empty] | 331.1 | 438.5
[9 empty] | 381.3 | 476.1 | [39 empty] | 381.3 | 476.1
[9 empty] | 424.5 | 528.3 | [39 empty] | 424.5 | 528.3
[9 empty] | 510 | 630 | [39 empty] | 510 | 630
[9 empty] | 554.2 | 683.1 | [39 empty] | 554.2 | 683.1
Note on A1: Reviewer M.H. (1/10/00): 1. This study presents results obtained from a full-scale GAC contactor operating at an EBCT of 15 minutes in post-filter adsorber mode. This was the only EBCT and GAC run examined. The contactor used was maintained at a constant flow resulting in a 15 minute EBCT for 4 hours prior to each sample taken. At other times, the filter was placed into general service. Therefore, the contactor EBCT when not being sampled varied based on plant water demand (range: 9.1 - 45 minutes). The average EBCT over the course of the study was 16.5 minutes. The GAC used was 40 percent virgin Calgon F-300 and 60 percent plant reactivated GAC.
Note on E6: Reviewer M.H. (10/13/99): Per summary report, "40% virgin Calgon F300 and 60% plant reactivated."
Note on E9: Reviewer M.H. (10/13/99): Per summary report, "Full-scale contactor dimensions: 39 m x 5.8 m"
Note on EA6: Reviewer M.H. (1/13/00): Since the utility has GAC installed at the plant, the utility submitted actual captital and O&M costs in lieu of the design cost parameters. The utility-supplied costs appear to the right of this comment.