## NTR7450. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.3036 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 3.3 mg/L | plant | Sampling date | MM/DD/YY | 1998-03-18 | 1998-03-25 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.35 | [7 empty] | Feed flow rate during sample collection (mL/min) | 12.14 | [7 empty] | Feed flow rate during sample collection (mL/min) | 20.17 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI | Coagulation | 123 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 9:00 | 10:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 123.8 | 123.8 | 123.8 | 123.8 | SDS-THM4F, ug/L | 123.8 | 123.8 | 123.8 | 123.8 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.54 mg/L | plant | Operation time | hh.hh | 2 | 2 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 62.5 | 59 | 59.2 | 35.8 | SDS-THM4p, ug/L | 62.5 | 59 | 59.2 | 35.8 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 6.9 | 7.8 | 7.35 | 12.2449 | 1998-03-24 | 7:30 | 0 | 22 | 82 | 80 | 263 | 8.35 | 3.5 | 11.85 | 0.20103 | 0.70464 | 21.1941 | 19.0584 | 19.0584 | 0 | 0 | 0 | 0 | 81 | 0.23529 | 1998-03-25 | 8:00 | 0 | 22 | 63 | 61.5 | 263 | 6.71 | 2.85 |  | 9.56 | 0.20103 | 0.70188 | 26.5105 | 15.3152 | 15.3152 | 274.5669 | 189.6996 | 272.4017 | 0.83785 | 61.4122 | 0.24938 |  |  |  | 6 |  |  | 707.0667 |  | 97.2093 | 698.1234 | 99.1406 | [16 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 90.75 | 90.75 | 90.75 | 90.75 | SDS-HAA5F, ug/L | 90.75 | 90.75 | 90.75 | 90.75 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.29285 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 23 | 23 | 0 | 1998-03-24 | 8:30 | 1 | 22 | 82 | 80.5 | 263 | 8.3 | 3.4 | 11.7 | 0.20103 | 0.7094 | 21.4786 | 18.9443 | 18.9443 | 0 | 0 | 0 | 0 | 81.25 | 0.23316 | 1998-03-25 | 9:00 | 1 | 22 | 64 | 62 | 263 | 7 | 2.6 |  | 9.6 | 0.20103 | 0.72917 | 26.3958 | 15.9771 | 15.9771 | 277.6193 | 191.7414 | 275.3336 | 0.84735 | 62.1526 | 0.25706 |  |  |  | 151 |  | 185 | 387.3077 | -109.3555 | 29.7674 | 384.1629 | 60.6938 | 0.028 | 0.124 | 0.132 | 0.37877 | -186.9464 | 77.2358 | 0.3741 | 92.5154 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 19.6 | 18.2 | 12.5 | 10.2 | SDS-HAA5p, ug/L | 19.6 | 18.2 | 12.5 | 10.2 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 40 | 46 | 43 | 13.9535 | 1998-03-24 | 9:30 | 2 | 22 | 81 | 80 | 263 | 8.33 | 3.4 | 11.73 | 0.20103 | 0.71014 | 21.4211 | 19.0128 | 19.0128 | 0 | 0 | 0 | 0 | 80.5 | 0.23618 | 1998-03-25 | 10:00 | 2 | 22 | 64 | 62 | 263 | 6.78 | 3.43 |  | 10.21 | 0.20103 | 0.66405 | 24.7591 | 15.475 | 15.475 | 270.5406 | 186.902 | 268.3844 | 0.82561 | 62.1744 | 0.2489 |  |  |  | 190 |  | 233 | 264.4169 | -13.4837 | 11.6279 | 263.4577 | 27.8822 | 0.04 |  | 0.223 | 0.28706 | -28.7283 | 67.4797 | 0.28388 | 85.9095 | [8 empty] | Sampling date | MM/DD/YY | 1998-03-26 | 1998-03-27 | --- | --- | 1998-03-26 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-29 | 1998-03-29 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-30 | 1998-03-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-30 | 1998-03-30 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 540 | 540 | 540 | 540 | SDS-TOXF, ug Cl- /L | 540 | 540 | 540 | 540 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 213 | 217 | 215 | 1.8605 | 1998-03-24 | 10:30 | 3 | 22 | 69 | 68 | 263 | 7.13 | 2.25 | 9.38 | 0.20103 | 0.76013 | 27.0384 | 16.2738 | 16.2738 | 0 | 0 | 0 | 0 | 68.5 | 0.23757 | 1998-03-25 | 11:00 | 3 | 22 | 64 | 62 | 263 | 6.8 | 3.26 |  | 10.06 | 0.20103 | 0.67594 | 25.1431 | 15.5206 | 15.5206 | 271.8016 | 187.7686 | 269.6289 | 0.82947 | 62.1705 | 0.24965 | 7.04 | 6.84 | 7.02 | 192 | 207 | 241 | 262.9755 | -9.1184 | 10.6977 | 262.0579 | 26.7338 | 0.048 |  | 0.254 | 0.27944 | -10.0164 | 60.9756 | 0.27645 | 82.637 | [8 empty] | Sampling time | hh:mm | 10:00 | 9:00 | --- | --- | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 21:30 | 21:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:45 | 10:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:30 | 20:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 167.5 | 185 | 125 | 120 | SDS-TOXp, ug Cl- /L | 167.5 | 185 | 125 | 120 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 134 | 148 | 141 | 9.9291 | 1998-03-24 | 11:30 | 4 | 22 | 68 | 67 | 263 | 7.09 | 3.15 | 10.24 | 0.20103 | 0.69238 | 24.6836 | 16.1825 | 16.1825 | 0 | 0 | 0 | 0 | 67.5 | 0.23974 | 1998-03-25 | 12:30 | 4.5 | 22 | 64 | 62 | 263 | 6.67 | 3 |  | 9.67 | 0.20103 | 0.68976 | 26.1975 | 15.2239 | 15.2239 | 273.2515 | 188.7999 | 271.1097 | 0.83381 | 62.1662 | 0.24489 | 6.96 |  | 6.94 | 194 |  | 242 | 261.69 | -8.1364 | 9.7674 | 260.8316 | 25.6225 | 0.048 |  | 0.266 | 0.28975 | -8.9286 | 60.9756 | 0.28668 | 83.2569 | [8 empty] | Operation time | hh.hh | 26 | 49 | --- | --- | 26 | --- | --- | --- | --- | --- | Operation time | hh.hh | 85.25 | 85.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 98.5 | 98.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 108.25 | 108.25 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 6.095 | 6.095 | 6.095 | 6.095 | SDS-CDF, mg/L | 6.095 | 6.095 | 6.095 | 6.095 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 100 | 108 | 104 | 7.6923 | 1998-03-24 | 12:15 | 4.75 | 22 | 68 | 67 | 263 | 7.08 | 3.14 | 10.22 | 0.20103 | 0.69276 | 24.7339 | 16.1597 | 16.1597 | 0 | 0 | 0 | 0 | 67.5 | 0.2394 | 1998-03-25 | 14:00 | 6 | 22 | 64 | 62 | 263 | 6.625 | 2.8923 |  | 9.5173 | 0.20103 | 0.6961 | 26.6339 | 15.1212 | 15.1212 | 273.9244 | 189.2751 | 271.7921 | 0.83583 | 62.1642 | 0.24325 | 7.03 |  | 7.02 | 192 |  | 242 | 267.6828 | -10.6127 | 10.6977 | 266.7296 | 28.017 | 0.05 |  | 0.275 | 0.29021 | -5.5312 | 59.3496 | 0.28719 | 82.5896 | [8 empty] | pH | --- | 7.8 | 7.8 | 7.8 | 0 | 7.7 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 7.7 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 7.8 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 7.9 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.865 | 2.02 | 1.69 | 1.68 | SDS-CDp, mg/L | 1.865 | 2.02 | 1.69 | 1.68 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 57.7216 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.15 | 0.13 | 0.14 | 14.2857 | 1998-03-24 | 14:00 | 6.5 | 22 | 68.5 | 67 | 263 | 7.1 | 2.62 | 9.72 | 0.20103 | 0.73045 | 26.0576 | 16.2054 | 16.2054 | 0 | 0 | 0 | 0 | 67.75 | 0.23919 | 1998-03-25 | 15:00 | 7 | 22 | 64 | 62 | 263 | 6.7273 | 2.8 |  | 9.5273 | 0.20103 | 0.70611 | 26.605 | 15.3546 | 15.3546 | 275.029 | 190.0149 | 272.8545 | 0.83927 | 62.1607 | 0.24702 | 6.95 |  | 6.99 | 193 |  | 241 | 267.8571 | -11.144 | 10.2326 | 266.8998 | 27.6882 | 0.051 | 0.125 | 0.276 | 0.29599 | -7.2417 | 58.5366 | 0.29285 | 82.5852 | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.3 | 6.3 | 6.3 | 6.3 | TOCF, mg/L | 6.3 | 6.3 | 6.3 | 6.3 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 67.7216 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.09 | 0.07 | 0.08 | 25 | 1998-03-24 | 15:00 | 7.5 | 22 | 68.5 | 67 | 263 | 7.1 | 3.89 | 10.99 | 0.20103 | 0.64604 | 22.9308 | 16.2054 | 16.2054 | 0 | 0 | 0 | 0 | 67.75 | 0.23919 | 1998-03-25 | 16:15 | 8.25 | 22 | 63 | 62 | 263 | 6.5 | 2.5143 |  | 9.0143 | 0.20103 | 0.72108 | 28.1759 | 14.8359 | 14.8359 | 276.6182 | 191.1653 | 274.5063 | 0.84397 | 61.656 | 0.24062 |  |  |  | 189 |  |  | 282.2159 |  | 12.093 | 281.064 | 32.7555 | [16 empty] | Alkalinity | mg/L as CaCO3 | 48 | 38 | 43 | 23.2558 | 56 | 43 | 23.2143 | 0 | 43 | 0 | Alkalinity | mg/L as CaCO3 | 38 | 46 | 83.4545 | -81.4229 | 11.6279 | 82.8893 | 54.1557 | Alkalinity | mg/L as CaCO3 | 36 | 48 | 50 | -4.1667 | 16.2791 | 49.8384 | 27.7666 | Alkalinity | mg/L as CaCO3 | 34 | 42 | 46.6761 | -11.1335 | 20.9302 | 46.5351 | 26.9369 | TOCp, mg/L | 2.25 | 3 | 1.6 | 1.5 | TOCp, mg/L | 2.25 | 3 | 1.6 | 1.5 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 55.7216 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6.4 | 6.2 | 6.3 | 3.1746 | 1998-03-24 | 16:00 | 8.5 | 22 | 69 | 67.5 | 263 | 7.08 | 3.5 | 10.58 | 0.20103 | 0.66919 | 23.8582 | 16.1597 | 16.1597 | 0 | 0 | 0 | 0 | 68.25 | 0.23677 | 1998-03-25 | 17:30 | 9.5 | 22 | 63 | 62 | 263 | 6.5 | 2.4 |  | 8.9 | 0.20103 | 0.73034 | 28.5506 | 14.8359 | 14.8359 | 277.64 | 191.8714 | 275.5203 | 0.84709 | 61.6529 | 0.24064 | [27 empty] | Total dissolved solids | mg/L | 204 | 193 | 198.5 | 5.5416 | 250 | 255.3966 | -2.1586 | 7.6744 | 254.6977 | 22.0645 | Total dissolved solids | mg/L | 203 | 270 | 312.0909 | -15.5892 | 5.5814 | 310.7342 | 34.6709 | Total dissolved solids | mg/L | 181 | 249 | 249 | 0 | 15.814 | 248.2153 | 27.0794 | Total dissolved solids | mg/L | 169 | 229 | 233.7887 | -2.0911 | 21.3953 | 233.0683 | 27.4891 | UV254 F, cm-1 | 0.123 | 0.123 | 0.123 | 0.123 | UV254 F, cm-1 | 0.123 | 0.123 | 0.123 | 0.123 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 54.8644 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.121 | 0.125 | 0.123 | 3.252 | 1998-03-24 | 17:00 | 9.5 | 22 | 62.5 | 60.5 | 263 | 6.48 | 2.9 | 9.38 | 0.20103 | 0.69083 | 27.0384 | 14.7903 | 14.7903 | 0 | 0 | 0 | 0 | 61.5 | 0.24049 | 1998-03-26 | 8:00 | 24 | 22 | 64 | 62 | 263 | 6.35 | 3.3 |  | 9.65 | 0.20103 | 0.65803 | 26.2539 | 14.4935 | 14.4935 | 269.8283 | 186.5065 | 267.8166 | 0.82316 | 62.1768 | 0.2331 |  |  |  | 194 | 209 |  | 255.4091 |  | 9.7674 | 254.6677 | 23.8223 | 0.055 | 0.126 |  | 0.25385 |  | 55.2846 | 0.25145 | 78.1267 | [8 empty] | Total hardness | mg/L as CaCO3 | 136 | 124 | 130 | 9.2308 | 177 | 167.931 | 5.1237 | 7.8014 | 167.4651 | 22.3719 | Total hardness | mg/L as CaCO3 | 126 | 190 | 262.3636 | -38.0861 | 10.6383 | 260.6678 | 51.6626 | Total hardness | mg/L as CaCO3 | 110 | 174 | 172 | 1.1494 | 21.9858 | 171.2845 | 35.7794 | Total hardness | mg/L as CaCO3 | 100 | 154 | 157.7465 | -2.4328 | 29.078 | 157.1043 | 36.348 | UV254 p, cm-1 | 0.0485 | 0.06 | 0.031 | 0.027 | UV254 p, cm-1 | 0.0485 | 0.06 | 0.031 | 0.027 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 1.8906 | 2.0161 | 1.9534 | 6.425 | 1998-03-24 | 17:10 | 9.6667 | 22 | 50 | 48 | 263 | 5.02 | 1.85 | 6.87 | 0.20103 | 0.73071 | 37.2824 | 11.4579 | 11.4579 | 0 | 0 | 0 | 0 | 49 | 0.23383 | 1998-03-26 | 8:30 | 24.5 | 22 | 64 | 62 | 263 | 6.43 | 3.08 |  | 9.51 | 0.20103 | 0.67613 | 26.6551 | 14.6761 | 14.6761 | 271.7498 | 187.8166 | 269.6977 | 0.82907 | 62.1709 | 0.23606 |  |  |  | 185 |  |  | 277.6299 |  | 13.9535 | 276.4975 | 33.0916 | 0.047 |  |  | 0.28166 |  | 61.7886 | 0.27879 | 83.1417 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 102 | 90 | 96 | 12.5 | 131 | 123.5862 | 5.6594 | 7.6923 | 123.2474 | 22.1079 | Calcium hardness | mg/L as CaCO3 | 92 | 146 | 201.0909 | -37.7335 | 11.5385 | 199.7342 | 53.9388 | Calcium hardness | mg/L as CaCO3 | 80 | 132 | 128 | 3.0303 | 23.0769 | 127.4461 | 37.2284 | Calcium hardness | mg/L as CaCO3 | 76 | 110 | 115.4366 | -4.9424 | 26.9231 | 114.9981 | 33.9119 | BromideF, ug/L | 110 | 110 | 110 | 110 | BromideF, ug/L | 110 | 110 | 110 | 110 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 110 | 110 | 110 | 0 | 1998-03-24 | 17:30 | 10 | 22 | 40 | 38 | 263 | 4 | 1.25 | 5.25 | 0.20103 | 0.7619 | 49.0952 | 9.1298 | 9.1298 | 0 | 0 | 0 | 0 | 39 | 0.2341 | 1998-03-26 | 9:30 | 25.5 | 22 | 64 | 62 | 263 | 6.35 | 2.85 |  | 9.2 | 0.20103 | 0.69022 | 27.587 | 14.4935 | 14.4935 | 273.2366 | 188.8623 | 271.1994 | 0.83356 | 62.1664 | 0.23314 | [27 empty] | Turbidity | ntu | 0.05 | 0.047 | 0.0485 | 6.1856 | 0.282 | 0.36402 | -29.0841 | 65.3571 | 0.36014 | 86.5331 | Turbidity | ntu | 0.07 | 0.18 | 0.70636 | -292.4242 | 50 | 0.69845 | 89.9778 | Turbidity | ntu | 0.12 | 0.14 | 0.16 | -14.2857 | 14.2857 | 0.15954 | 24.783 | Turbidity | ntu | 0.05 | 0.12 | 0.17676 | -47.3005 | 64.2857 | 0.17535 | 71.4858 | Bromidep, ug/L | 110 | 110 | 100 | 100 | Bromidep, ug/L | 110 | 110 | 100 | 100 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 7 | 7 | 7 | 0 | 1998-03-24 | 17:45 | 10.25 | 22 | 62 | 60 | 263 | 6.4 | 2.6 | 9 | 0.20103 | 0.71111 | 28.2222 | 14.6077 | 14.6077 | 0 | 0 | 0 | 0 | 61 | 0.23947 | 1998-03-26 | 10:00 | 26 | 22 | 64 | 62 | 263 | 6.46 | 2.04 |  | 8.5 | 0.20103 | 0.76 | 29.9412 | 14.7446 | 14.7446 | 280.9555 | 194.172 | 278.8238 | 0.85718 | 62.1428 | 0.23727 | 7 |  |  | 195 |  |  | 278.3333 |  | 9.3023 | 277.3099 | 29.6816 | 0.051 |  | 0.286 | 0.351 | -22.7273 | 58.5366 | 0.34732 | 85.3159 | [8 empty] | Ammonia | mg NH3-N / L | 0.07 | 0.08 | 0.075 | 13.3333 | NA | 0.092241 | #VALUE! | 6.25 | 0.09203 | 18.5045 | Ammonia | mg NH3-N / L | 0.09 | NA | -0.00090909 | #VALUE! | -12.5 | 0.00022148 | -40535.1931 | Ammonia | mg NH3-N / L | 0.08 | NA | 0.08 | #VALUE! | 0 | 0.08 | 0 | Ammonia | mg NH3-N / L | 0.08 | NA | 0.08 | #VALUE! | 0 | 0.08 | 0 | AlkF, mg/L CaCO3 | 43 | 43 | 43 | 43 | AlkF, mg/L CaCO3 | 43 | 43 | 43 | 43
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.89 | 0.92 | 0.905 | 3.3149 | 1998-03-25 | 7:30 | 24 | 22 | 64 | 62 | 263 | 6.5714 | 3.4857 | 10.0571 | 0.20103 | 0.65341 | 25.1506 | 14.9989 | 14.9989 | 0 | 0 | 0 | 0 | 63 | 0.23808 | 1998-03-26 | 11:00 | 27 | 22 | 64 | 62 | 263 | 6.4 | 2.36 |  | 8.76 | 0.20103 | 0.73059 | 29.0228 | 14.6077 | 14.6077 | 277.6466 | 191.8991 | 275.56 | 0.84704 | 62.153 | 0.23503 | [11 empty] | 0.049 |  | 0.286 | 0.32368 | -13.1741 | 60.1626 | 0.32034 | 84.7036 | [8 empty] | Total organic carbon | mg/L | 2.3 | 2.2 | 2.25 | 4.4444 | 14.3 | 16.2155 | -13.3952 | 64.2857 | 16.044 | 85.976 | Total organic carbon | mg/L | 3 | 29.1 | 33 | -13.4021 | 52.381 | 32.6269 | 90.8051 | Total organic carbon | mg/L | 1.6 | 10.7 | 11 | -2.8037 | 74.6032 | 10.8915 | 85.3097 | Total organic carbon | mg/L | 1.5 | 8.2 | 8.2606 | -0.73858 | 76.1905 | 8.1854 | 81.6747 | Alkp, mg/L CaCO3 | 43 | 38 | 36 | 34 | Alkp, mg/L CaCO3 | 43 | 38 | 36 | 34
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 6.11 | 6.08 | 6.095 | 0.49221 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-26 | 12:00 | 28 | 22 | 64 | 62 | 263 | 6.35 | 3.07 |  | 9.42 | 0.20103 | 0.6741 | 26.9193 | 14.4935 | 14.4935 | 271.5189 | 187.6751 | 269.4946 | 0.82832 | 62.1717 | 0.23312 | 6.98 |  |  | 193 | 210 | 248 | 260.5049 | -5.0423 | 10.2326 | 259.69 | 25.6806 | 0.048 |  | 0.287 | 0.27813 | 3.0905 | 60.9756 | 0.27535 | 82.5678 | [8 empty] | UV254 | cm-1 | 0.05 | 0.047 | 0.0485 | 6.1856 | 0.282 | 0.3054 | -8.2966 | 60.5691 | 0.30224 | 83.9532 | UV254 | cm-1 | 0.06 | 0.565 | 0.63273 | -11.9871 | 51.2195 | 0.6256 | 90.4093 | UV254 | cm-1 | 0.031 | 0.216 | 0.215 | 0.46296 | 74.7967 | 0.21288 | 85.4376 | UV254 | cm-1 | 0.027 | 0.162 | 0.16221 | -0.13041 | 78.0488 | 0.16071 | 83.1993 | T-HdF, mg/L CaCO3 | 141 | 141 | 141 | 141 | T-HdF, mg/L CaCO3 | 141 | 141 | 141 | 141
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-26 | 13:00 | 29 | 22 | 64 | 62 | 263 | 6.53 | 2.73 |  | 9.26 | 0.20103 | 0.70518 | 27.4017 | 14.9044 | 14.9044 | 274.888 | 189.9626 | 272.7793 | 0.83871 | 62.1613 | 0.23977 | [27 empty] | SUVA | L/(mg*m) | 2.1739 | 2.1364 | 2.1551 | 1.7423 | 1.972 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 1.9416 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.9375 | 2.0187 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8 | 1.9756 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 130 | 126 | 110 | 100 | T-Hdp, mg/L CaCO3 | 130 | 126 | 110 | 100
Process Train Name | Enhanced Coagulation/Lime Softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8 | 7.9 | 7.95 | 1.2579 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-26 | 14:00 | 30 | 22 | 64 | 62 | 263 | 6.4 | 2.54 |  | 8.94 | 0.20103 | 0.71588 | 28.4183 | 14.6077 | 14.6077 | 276.0273 | 190.7798 | 273.9528 | 0.8421 | 62.1579 | 0.23501 | [27 empty] | Bromide | mg/L | 110 | NA | 110 | #VALUE! | --- | 110 | --- | 0 | 110 | 0 | Bromide | mg/L | 110 | --- | 110 | --- | 0 | 110 | 0 | Bromide | mg/L | 100 | --- | 120 | --- | 9.0909 | 119.7692 | 16.5061 | Bromide | mg/L | 100 | --- | 114.0845 | --- | 9.0909 | 113.9279 | 12.2252 | Ca-HdF, mg/L CaCO3 | 104 | 104 | 104 | 104 | Ca-HdF, mg/L CaCO3 | 104 | 104 | 104 | 104
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-26 | 16:00 | 32 | 22 | 64 | 62 | 263 | 6.33 | 3.37 |  | 9.7 | 0.20103 | 0.65258 | 26.1134 | 14.4479 | 14.4479 | 269.2556 | 186.1151 | 267.2545 | 0.8214 | 62.1786 | 0.23236 | 6.93 | 6.85 | 6.96 | 192 |  | 243 | 258.2018 | -6.2559 | 10.6977 | 257.4051 | 25.4094 | [16 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 96 | 92 | 80 | 76 | Ca-Hdp, mg/L CaCO3 | 96 | 92 | 80 | 76
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 560 | 520 | 540 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 8:00 | 48 | 22 | 63 | 61 | 263 | 6.1 | 3 |  | 9.1 | 0.20103 | 0.67033 | 27.9011 | 13.9229 | 13.9229 | 271.0729 | 187.4231 | 269.1328 | 0.8268 | 61.1732 | 0.2276 |  |  |  | 199 |  | 253 | 247.5333 | 2.1607 | 7.4419 | 246.9705 | 19.4236 | 0.052 |  |  | 0.26737 |  | 57.7236 | 0.26487 | 80.3677 | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.62 | 0.65 | 0.635 | 4.7244 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.48 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.81 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.82 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 74 | 81 | 77.5 | 9.0323 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 9:00 | 49 | 22 | 63 | 61 | 263 | 6.2 | 2.9 |  | 9.1 | 0.20103 | 0.68132 | 27.9011 | 14.1512 | 14.1512 | 272.2564 | 188.2188 | 270.2753 | 0.83047 | 61.1695 | 0.23134 |  |  |  | 190 |  |  | 268.4483 |  | 11.6279 | 267.5236 | 28.9782 | 0.048 |  |  | 0.28334 |  | 60.9756 | 0.28057 | 82.892 | [8 empty] | SDS-Cl2 demand | mg/L | 1.88 | 1.85 | 1.865 | 1.6086 | --- | 16.4512 | --- | 69.4011 | 16.272 | 88.5386 | SDS-Cl2 demand | mg/L | 2.02 | --- | 39.0655 | --- | 66.8581 | 38.6047 | 94.7675 | SDS-Cl2 demand | mg/L | 1.69 | --- | 10.5 | --- | 72.2724 | 10.3983 | 83.7474 | SDS-Cl2 demand | mg/L | 1.68 | --- | 7.8983 | --- | 72.4364 | 7.8292 | 78.5418 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 35 | 33 | 34 | 5.8824 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 10:15 | 50.25 | 22 | 64 | 62 | 263 | 6.2 | 2.9 |  | 9.1 | 0.20103 | 0.68132 | 27.9011 | 14.1512 | 14.1512 | 272.2564 | 188.2188 | 270.2753 | 0.83047 | 62.1695 | 0.22762 | 7.1 |  | 7.13 | 193 | 209 | 246 | 262.0345 | -6.5181 | 10.2326 | 261.2208 | 26.1161 | 0.047 | 0.124 |  | 0.28548 |  | 61.7886 | 0.28267 | 83.3729 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 84.5024 | 79.9383 | 80.1858 | 58.8636 | Qp/QT (THM4), % | 143.23 | 135.4938 | 135.9133 | 99.7727
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 12 | 12 | 12 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 11:15 | 51.25 | 22 | 64 | 62 | 263 | 6.19 | 2.67 |  | 8.86 | 0.20103 | 0.69865 | 28.684 | 14.1283 | 14.1283 | 274.1108 | 189.5031 | 272.1195 | 0.83612 | 62.1639 | 0.22728 | 7.11 |  | 7.11 | 197 |  | 244 | 256.7303 | -5.2174 | 8.3721 | 256.0274 | 23.0551 | 0.046 |  | 0.301 | 0.30151 | -0.17047 | 62.6016 | 0.29851 | 84.5899 | [8 empty] | SDS-Chlorination pH | --- | 7.9 | 8 | 7.95 | 1.2579 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | 36
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | 0.6 | 0.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 12:15 | 52.25 | 22 | 64 | 62 | 263 | 6.2 | 2.87 |  | 9.07 | 0.20103 | 0.68357 | 27.9967 | 14.1512 | 14.1512 | 272.4964 | 188.3847 | 270.5136 | 0.8312 | 62.1688 | 0.22762 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 30.6265 | 32.7548 | 28.0046 | 43.3353 | SDS-HAA5b, ug/L | NA | NA | NA | 10.3831
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 121 | 126.6 | 123.8 | 4.5234 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 13:45 | 53.75 | 22 | 64 | 62 | 263 | 6.2 | 3.07 |  | 9.27 | 0.20103 | 0.66882 | 27.3711 | 14.1512 | 14.1512 | 270.9332 | 187.304 | 268.9617 | 0.82643 | 62.1736 | 0.22761 | 7.02 |  |  | 191 |  | 245 | 263.4691 | -7.5384 | 11.1628 | 262.6149 | 27.2699 | 0.046 |  | 0.28 | 0.2785 | 0.53397 | 62.6016 | 0.27576 | 83.3191 | [8 empty] | SDS-TOX | mg Cl- /L | 165 | 170 | 167.5 | 2.9851 | --- | 1451.9828 | --- | 68.9815 | 1436.2051 | 88.3373 | SDS-TOX | mg Cl- /L | 185 | --- | 3412.2727 | --- | 65.7407 | 3372.1374 | 94.5139 | SDS-TOX | mg Cl- /L | 125 | --- | 955 | --- | 76.8519 | 945.4219 | 86.7784 | SDS-TOX | mg Cl- /L | 120 | --- | 711.5493 | --- | 77.7778 | 704.9711 | 82.978 | SDS-TOXb, ug Cl- /L | 225.2284 | 256.2191 | 207.2291 | 292.7727 | SDS-TOXb, ug Cl- /L | NA | NA | NA | 120.9545
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 5.4 | 5.1 | 5.25 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-27 | 15:15 | 55.25 | 22 | 64 | 62 | 263 | 6.1 | 2.72 |  | 8.82 | 0.20103 | 0.69161 | 28.8186 | 13.9229 | 13.9229 | 273.336 | 188.9879 | 271.3797 | 0.8337 | 62.1663 | 0.22396 |  |  |  | 195 |  | 246 | 259.8529 | -5.6313 | 9.3023 | 259.1008 | 24.7397 | 0.044 |  | 0.28 | 0.30017 | -7.2033 | 64.2276 | 0.2972 | 85.1951 | [8 empty] | SDS-CHCl3 | mg/L | 25 | 22 | 23.5 | 12.766 | --- | 209.7069 | --- | 69.6774 | 207.4197 | 88.6703 | SDS-CHCl3 | mg/L | 23 | --- | 518.4545 | --- | 70.3226 | 512.2929 | 95.5104 | SDS-CHCl3 | mg/L | 14 | --- | 141 | --- | 81.9355 | 139.5344 | 89.9666 | SDS-CHCl3 | mg/L | 9 | --- | 105.4789 | --- | 88.3871 | 104.406 | 91.3798 | SDS-CDb, mg/L | 2.5205 | 2.8375 | 2.5628 | 3.4962 | SDS-CDb, mg/L | NA | NA | NA | 1.69
|  | Standard testing pH | 6.5 | [13 empty] | SDS-DCAA* | mg/L | 35 | 36 | 35.5 | 2.8169 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-28 | 17:40 | 81.6667 | 22 | 64 | 62 | 263 | 6.1 | 2.72 |  | 8.82 | 0.20103 | 0.69161 | 28.8186 | 13.9229 | 13.9229 | 273.336 | 188.9879 | 271.3797 | 0.8337 | 62.1663 | 0.22396 | [27 empty] | SDS-BDCM | mg/L | 20 | 19 | 19.5 | 5.1282 | --- | 69.5 | --- | 42.6471 | 68.8858 | 71.6923 | SDS-BDCM | mg/L | 20 | --- | 147.2727 | --- | 41.1765 | 145.6899 | 86.2722 | SDS-BDCM | mg/L | 19 | --- | 49 | --- | 44.1176 | 48.6538 | 60.9486 | SDS-BDCM | mg/L | 10 | --- | 43.8028 | --- | 70.5882 | 43.4269 | 76.9728 | TOCb, mg/L | 2.8777 | 3.662 | 2.5313 | 3.4745 | TOCb, mg/L | NA | NA | NA | 1.5109
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 48 | 42 | 45 | 13.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 18:15 | 82 | 29 | 63 | 62 | 263 | 7.2 | 0.6 |  | 7.8 | 0.20103 | 0.92308 | 32.7179 | 16.4336 | 13.362 | 300.9923 | 207.834 | 298.442 | 0.91883 | 61.5812 | 0.21698 | [27 empty] | SDS-DBCM | mg/L | 16 | 16 | 16 | 0 | --- | 2.2069 | --- | -33.3333 | 2.3763 | -573.3097 | SDS-DBCM | mg/L | 13 | --- | 3.9091 | --- | -8.3333 | 4.0221 | -223.2104 | SDS-DBCM | mg/L | 20 | --- | 4 | --- | -66.6667 | 4.1846 | -377.9385 | SDS-DBCM | mg/L | 12 | --- | 12 | --- | 0 | 12 | 0 | UV254 b, cm-1 | 0.060046 | 0.072639 | 0.049229 | 0.066491 | UV254 b, cm-1 | NA | NA | NA | 0.027218
|  | Acceptable range of operating pH values | 2 - 11 | [13 empty] | SDS-MBAA* | mg/L | 2 | 1.8 | 1.9 | 10.5263 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 19:00 | 82.75 | 29 | 64 | 63 | 263 | 7.25 | 0.94 |  | 8.19 | 0.20103 | 0.88523 | 31.1123 | 16.5477 | 13.4548 | 296.1506 | 204.4784 | 293.6235 | 0.90409 | 62.5959 | 0.21495 | 7.05 |  |  | 200 |  |  | 330.6915 |  | 6.9767 | 328.8901 | 39.1894 | 0.051 |  | 0.329 | 0.67832 | -106.176 | 58.5366 | 0.66967 | 92.3843 | [8 empty] | SDS-CHBr3 | mg/L | 3.1 | 3.9 | 3.5 | 22.8571 | --- | -6.5 | --- | -483.3333 | -6.3772 | 154.8833 | SDS-CHBr3 | mg/L | 3 | --- | -18.8182 | --- | -400 | -18.5468 | 116.1753 | SDS-CHBr3 | mg/L | 6.2 | --- | -5 | --- | -933.3333 | -4.8708 | 227.2904 | SDS-CHBr3 | mg/L | 4.8 | --- | -1.1155 | --- | -700 | -1.0497 | 557.2689 | Bromideb, ug/L | 110 | 110 | 101.9814 | 104.1136 | Bromideb, ug/L | NA | NA | NA | 100.0227
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 2.9 | 3.3 | 3.1 | 12.9032 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 19:20 | 83.0833 | 29 | 64 | 63 | 263 | 7.22 | 0.93 |  | 8.15 | 0.20103 | 0.88589 | 31.2699 | 16.4793 | 13.3991 | 296.2253 | 204.5375 | 293.7083 | 0.90429 | 62.5957 | 0.21406 |  |  |  | 201 |  |  | 323.6882 |  | 6.5116 | 322.0041 | 37.5784 | [16 empty] | SDS-THM4 | mg/L | 64.1 | 60.9 | 62.5 | 5.12 | --- | 273.8793 | --- | 49.5153 | 271.2829 | 76.9613 | SDS-THM4 | mg/L | 59 | --- | 648.0909 | --- | 52.3425 | 640.7648 | 90.7923 | SDS-THM4 | mg/L | 59.2 | --- | 188.4 | --- | 52.1809 | 186.909 | 68.3268 | SDS-THM4 | mg/L | 35.8 | --- | 159.7437 | --- | 71.0824 | 158.3654 | 77.394 | Alkb, mg/L CaCO3 | 43 | 39.0031 | 37.387 | 37.7023 | Alkb, mg/L CaCO3 | NA | NA | NA | 34.0205
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 14 | 14 | 14 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 19:40 | 83.4167 | 29 | 64 | 63 | 263 | 7.25 | 1.27 |  | 8.52 | 0.20103 | 0.85094 | 29.8685 | 16.5477 | 13.4548 | 291.8834 | 201.5321 | 289.3928 | 0.89106 | 62.6089 | 0.2149 |  |  |  | 204 |  |  | 277.7953 |  | 5.1163 | 276.7781 | 26.2948 | 0.055 |  |  | 0.51119 |  | 55.2846 | 0.5049 | 89.1068 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 131.7047 | 129.0093 | 116.1424 | 116.8659 | T-Hdb, mg/L CaCO3 | NA | NA | NA | 100.0932
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 20:00 | 83.75 | 29 | 64 | 63 | 263 | 7.2 | 1.125 |  | 8.325 | 0.20103 | 0.86486 | 30.5916 | 16.4336 | 13.362 | 293.5872 | 202.7208 | 291.0996 | 0.89623 | 62.6038 | 0.21344 | 7.08 |  |  | 206 |  |  | 272.6 |  | 4.186 | 271.6884 | 24.1778 | 0.056 | 0.124 | 0.371 | 0.5518 | -48.7332 | 54.4715 | 0.54501 | 89.725 | [8 empty] | SDS-DCAA* | mg/L | 8.4 | 7.4 | 7.9 | 12.6582 | --- | 103.0724 | --- | 77.7465 | 101.9034 | 92.2476 | SDS-DCAA* | mg/L | 7.9 | --- | 258.8091 | --- | 77.7465 | 255.6887 | 96.9103 | SDS-DCAA* | mg/L | 4.7 | --- | 66.3 | --- | 86.7606 | 65.5891 | 92.8342 | SDS-DCAA* | mg/L | 3.8 | --- | 48.4479 | --- | 89.2958 | 47.9514 | 92.0753 | Ca-Hdb, mg/L CaCO3 | 97.2398 | 94.4074 | 84.7554 | 87.5182 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | 76.0636
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 6.3 | 5.8 | 6.05 | 8.2645 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 20:30 | 84.25 | 29 | 64 | 63 | 263 | 7.3 | 0.82 |  | 8.12 | 0.20103 | 0.89901 | 31.3892 | 16.6619 | 13.5476 | 297.9176 | 205.686 | 295.3575 | 0.90952 | 62.5905 | 0.21645 |  |  |  | 206 | 209 |  | 295.122 |  | 4.186 | 293.8851 | 29.9046 | 0.059 |  |  | 0.69276 |  | 52.0325 | 0.68396 | 91.3738 | [8 empty] | SDS-TCAA* | mg/L | 6 | 5.1 | 5.55 | 16.2162 | --- | 141.5845 | --- | 87.6667 | 139.9135 | 96.0333 | SDS-TCAA* | mg/L | 5.4 | --- | 365.4 | --- | 88 | 360.9229 | 98.5038 | SDS-TCAA* | mg/L | 3.1 | --- | 86.9 | --- | 93.1111 | 85.933 | 96.3925 | SDS-TCAA* | mg/L | 2.1 | --- | 62.5225 | --- | 95.3333 | 61.8506 | 96.6047
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 25 | 20 | 22.5 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 21:00 | 84.75 | 29 | 64 | 63 | 263 | 7.25 | 0.82 |  | 8.07 | 0.20103 | 0.89839 | 31.5898 | 16.5477 | 13.4548 | 297.8221 | 205.6325 | 295.2808 | 0.90919 | 62.5908 | 0.21496 | [11 empty] | 0.057 |  | 0.382 | 0.70654 | -84.9572 | 53.6585 | 0.69758 | 91.8289 | [8 empty] | SDS-MBAA* | mg/L | 1.4 | 1.1 | 1.25 | 24 | --- | 3.4914 | --- | 34.2105 | 3.4638 | 63.913 | SDS-MBAA* | mg/L | 1.2 | --- | 7.5636 | --- | 36.8421 | 7.4845 | 83.9669 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 93.3 | 88.2 | 90.75 | 5.6198 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-29 | 21:30 | 85.25 | 29 | 64 | 63 | 263 | 7.2 | 0.82 |  | 8.02 | 0.20103 | 0.89776 | 31.793 | 16.4336 | 13.362 | 297.7258 | 205.5785 | 295.2031 | 0.90886 | 62.5911 | 0.21348 | 7.1 | 6.9 | 7.02 | [8 empty] | 0.059 |  |  | 0.68495 |  | 52.0325 | 0.67638 | 91.2771 | [8 empty] | SDS-DBAA* | mg/L | 4.9 | 4.9 | 4.9 | 0 | --- | -1.3069 | --- | -58.0645 | -1.2307 | 498.1618 | SDS-DBAA* | mg/L | 3.7 | --- | -1.7545 | --- | -19.3548 | -1.6867 | 319.3618 | SDS-DBAA* | mg/L | 4.7 | --- | 1.5 | --- | -51.6129 | 1.5369 | -205.8049 | SDS-DBAA* | mg/L | 4.3 | --- | 2.6099 | --- | -38.7097 | 2.6287 | -63.5818 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 107.3 | 102.2 | 104.75 | 4.8687 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-30 | 7:30 | 95.25 | 23 | 63 | 61 | 263 | 6.1 | 0.89 |  | 6.99 | 0.20103 | 0.87268 | 36.6252 | 13.9229 | 13.5174 | 294.2371 | 203.4392 | 292.1312 | 0.89745 | 61.1026 | 0.22122 | 7.15 |  |  | 202 | 210 |  | 304.1011 |  | 6.0465 | 302.9171 | 33.3151 | 0.057 | 0.124 |  | 0.57536 |  | 53.6585 | 0.56935 | 89.9886 | [8 empty] | SDS-BCAA* | mg/L | 8.1 | 7.3 | 7.7 | 10.3896 | --- | 29.4241 | --- | 45 | 29.1573 | 73.5915 | SDS-BCAA* | mg/L | 6.5 | --- | 74.6818 | --- | 53.5714 | 73.8339 | 91.1965 | SDS-BCAA* | mg/L | 5.4 | --- | 22.6 | --- | 61.4286 | 22.4015 | 75.8945 | SDS-BCAA* | mg/L | 4.2 | --- | 18.0028 | --- | 70 | 17.8493 | 76.4697 | Qp/QT (HAA5), % | 51.6514 | 50.6547 | 46.9649 | 45.6238 | Qp/QT (HAA5), % | 89.5994 | 87.8704 | 81.4696 | 79.1434
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-30 | 8:15 | 96 | 23 | 63 | 61 | 263 | 6.14 | 0.89 |  | 7.03 | 0.20103 | 0.8734 | 36.4111 | 14.0142 | 13.606 | 294.3389 | 203.4997 | 292.2182 | 0.89779 | 61.1022 | 0.22268 |  |  |  | 204 |  |  | 290.8876 |  | 5.1163 | 289.8734 | 29.6245 | 0.056 |  |  | 0.58522 |  | 54.4715 | 0.57905 | 90.3289 | [8 empty] | SDS-TBAA | mg/L | BMRL | 4 | 4 | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 92.1377 | 90.9757 | 93.4607 | 83.651 | SDS-THM4b, ug/L | 68.8755 | 66.86 | 71.1706 | 54.1538
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-30 | 8:30 | 96.25 | 23 | 64 | 62 | 263 | 6.2 | 6.34 |  | 12.54 | 0.20103 | 0.49442 | 19.9729 | 14.1512 | 13.739 | 253.721 | 175.4047 | 251.8747 | 0.77393 | 62.2261 | 0.22079 | 7.1 |  | 7.01 | 193 | 209 | 264 | 236.5142 | 10.4113 | 10.2326 | 236.0013 | 18.2208 | 0.054 |  | 0.586 | 0.19048 | 67.4955 | 56.0976 | 0.18887 | 71.4086 | [8 empty] | SDS-CDBAA | mg/L | 4.1 | 3.9 | 4 | 5 | --- | 11.069 | --- | 33.8843 | 10.9821 | 63.5772 | SDS-CDBAA | mg/L | 3.1 | --- | 29.9182 | --- | 48.7603 | 29.5847 | 89.5216 | SDS-CDBAA | mg/L | 3.2 | --- | 8.9 | --- | 47.1074 | 8.8342 | 63.7772 | SDS-CDBAA | mg/L | 2.9 | --- | 7.3366 | --- | 52.0661 | 7.2873 | 60.2046 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-30 | 9:00 | 96.75 | 23 | 64 | 63 | 263 | 6.1 | 5.73 |  | 11.83 | 0.20103 | 0.51564 | 21.2316 | 13.9229 | 13.5174 | 255.6844 | 176.7833 | 253.8544 | 0.77986 | 62.7201 | 0.21552 |  |  |  | 187 |  |  | 244.808 |  | 13.0233 | 244.1376 | 23.4039 | 0.043 |  |  | 0.20817 |  | 65.0407 | 0.20625 | 79.1516 | [8 empty] | SDS-DCBAA | mg/L | 6.1 | 5.2 | 5.65 | 15.9292 | --- | 63.7534 | --- | 74.8889 | 63.0397 | 91.0374 | SDS-DCBAA | mg/L | 4.6 | --- | 167.3273 | --- | 79.5556 | 165.3035 | 97.2172 | SDS-DCBAA | mg/L | 3.5 | --- | 41.5 | --- | 84.4444 | 41.0615 | 91.4762 | SDS-DCBAA | mg/L | 3 | --- | 30.4648 | --- | 86.6667 | 30.1594 | 90.0528 | SDS-TOXb, ug Cl- /L | 347.5984 | 360.1757 | 345.0958 | 348.3799 | SDS-TOXb, ug Cl- /L | 206.2421 | 228.06 | 201.901 | 207.5978
[44 empty] | 1998-03-30 | 9:30 | 97.25 | 23 | 65 | 64 | 263 | 6.2 | 5.8 |  | 12 | 0.20103 | 0.51667 | 20.9167 | 14.1512 | 13.739 | 255.794 | 176.8379 | 253.9327 | 0.78025 | 63.7197 | 0.21562 |  |  |  | 181 |  |  | 251.3448 |  | 15.814 | 250.5157 | 27.749 | 0.036 |  |  | 0.216 |  | 70.7317 | 0.21388 | 83.168 | [8 empty] | SDS-HAA5 | mg/L | 20.7 | 18.5 | 19.6 | 11.2245 | --- | 264.9448 | --- | 78.4022 | 261.9312 | 92.5171 | SDS-HAA5 | mg/L | 18.2 | --- | 677.7455 | --- | 79.9449 | 669.5431 | 97.2817 | SDS-HAA5 | mg/L | 12.5 | --- | 169 | --- | 86.2259 | 167.194 | 92.5237 | SDS-HAA5 | mg/L | 10.2 | --- | 123.6507 | --- | 88.7603 | 122.3891 | 91.6659 | SDS-CDb, mg/L | 3.9101 | 4.0308 | 4.0262 | 4.0807 | SDS-CDb, mg/L | 2.3049 | 2.5143 | 2.5063 | 2.6008
[44 empty] | 1998-03-30 | 10:15 | 98 | 23 | 62 | 60 | 263 | 5.7 | 5 |  | 10.7 | 0.20103 | 0.53271 | 23.5794 | 13.0099 | 12.631 | 257.242 | 177.9456 | 255.5234 | 0.78437 | 60.2156 | 0.20976 |  |  |  | 182 |  |  | 252.62 |  | 15.3488 | 251.8547 | 27.7361 | 0.035 |  | 0.253 | 0.22332 | 11.7312 | 71.5447 | 0.22128 | 84.1829 | [8 empty] | SDS-HAA6 | mg/L | 28.8 | 25.8 | 27.3 | 10.989 | --- | 294.369 | --- | 73.9379 | 291.0885 | 90.6214 | SDS-HAA6 | mg/L | 24.7 | --- | 752.4273 | --- | 76.42 | 743.377 | 96.6773 | SDS-HAA6 | mg/L | 17.9 | --- | 191.6 | --- | 82.9117 | 189.5955 | 90.5588 | SDS-HAA6 | mg/L | 14.4 | --- | 141.6535 | --- | 86.253 | 140.2384 | 89.7318 | TOCb, mg/L | 4.2081 | 4.6284 | 4.0927 | 4.1101 | TOCb, mg/L | 2.6712 | 3.4003 | 2.4709 | 2.5011
[44 empty] | 1998-03-30 | 10:30 | 98.25 | 23 | 63 | 62 | 263 | 6 | 7.76 |  | 13.76 | 0.20103 | 0.43605 | 18.1134 | 13.6947 | 13.2958 | 248.4178 | 171.7797 | 246.6694 | 0.75764 | 61.7424 | 0.21534 |  |  |  | 178 |  |  | 243.6082 |  | 17.2093 | 242.8599 | 26.7067 | 0.034 |  | 0.248 | 0.19181 | 22.6555 | 72.3577 | 0.19001 | 82.1066 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.08452 | 0.091088 | 0.079792 | 0.079201 | UV254 b, cm-1 | 0.056248 | 0.067642 | 0.048048 | 0.047022
[44 empty] | 1998-03-30 | 10:45 | 98.5 | 23 | 63 | 62 | 263 | 6 | 7.6 |  | 13.6 | 0.20103 | 0.44118 | 18.3382 | 13.6947 | 13.2958 | 248.8728 | 172.0944 | 247.1212 | 0.75903 | 61.741 | 0.21535 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 110 | 110 | 105.3035 | 105.4376 | Bromideb, ug/L | 110 | 110 | 101.853 | 102.0857
[44 empty] | 1998-03-30 | 11:30 | 99.25 | 23 | 64 | 62 | 263 | 6 | 6 |  | 12 | 0.20103 | 0.5 | 20.9167 | 13.6947 | 13.2958 | 254.2129 | 175.7871 | 252.4238 | 0.77531 | 62.2247 | 0.21367 | [66 empty] | Alkb, mg/L CaCO3 | 43 | 40.4673 | 39.7125 | 38.8939 | Alkb, mg/L CaCO3 | 43 | 38.6065 | 37.2971 | 35.8771
[44 empty] | 1998-03-30 | 12:30 | 100.25 | 23 | 64 | 62 | 263 | 6 | 5.93 |  | 11.93 | 0.20103 | 0.50293 | 21.0453 | 13.6947 | 13.2958 | 254.4853 | 175.9754 | 252.6942 | 0.77614 | 62.2239 | 0.21368 |  |  |  | 179 |  |  | 251.425 |  | 16.7442 | 250.5988 | 28.5711 | [55 empty] | T-Hdb, mg/L CaCO3 | 135.3183 | 133.4018 | 126.4409 | 122.2942 | T-Hdb, mg/L CaCO3 | 131.1441 | 127.8194 | 115.7444 | 108.5512
[44 empty] | 1998-03-30 | 13:15 | 101 | 23 | 63 | 62 | 263 | 6 | 6.5 |  | 12.5 | 0.20103 | 0.48 | 20.04 | 13.6947 | 13.2958 | 252.3718 | 174.5139 | 250.5956 | 0.7697 | 61.7303 | 0.21539 | [66 empty] | Ca-Hdb, mg/L CaCO3 | 99.8679 | 97.9214 | 92.7284 | 91.2253 | Ca-Hdb, mg/L CaCO3 | 96.832 | 93.4555 | 84.4473 | 81.8399
[44 empty] | 1998-03-30 | 14:30 | 102.25 | 23 | 63 | 62 | 263 | 5.85 | 5.2 |  | 11.05 | 0.20103 | 0.52941 | 22.8009 | 13.3523 | 12.9634 | 256.9496 | 177.7114 | 255.1871 | 0.78357 | 61.7164 | 0.21005 | 7.07 |  |  | 182 |  | 234 | 252.125 | -7.7457 | 15.3488 | 251.3451 | 27.5896 | 0.034 |  |  | 0.22312 |  | 72.3577 | 0.22102 | 84.6169 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-03-30 | 16:00 | 103.75 | 23 | 63 | 62 | 263 | 6 | 6 |  | 12 | 0.20103 | 0.5 | 20.9167 | 13.6947 | 13.2958 | 254.2129 | 175.7871 | 252.4238 | 0.77531 | 61.7247 | 0.2154 | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-03-30 | 17:00 | 104.75 | 23 | 63 | 62 | 263 | 6 | 6 |  | 12 | 0.20103 | 0.5 | 20.9167 | 13.6947 | 13.2958 | 254.2129 | 175.7871 | 252.4238 | 0.77531 | 61.7247 | 0.2154 |  |  | 6.99 |  |  | 235 |  | #VALUE! | [58 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-03-30 | 18:30 | 106.25 | 23 | 63 | 62 | 263 | 6.2222 | 5.7882 |  | 12.0105 | 0.20103 | 0.51807 | 20.8976 | 14.2019 | 13.7882 | 255.9285 | 176.9261 | 254.0594 | 0.78068 | 61.7193 | 0.2234 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-03-30 | 18:45 | 106.5 | 23 | 64 | 62.5 | 263 | 6 | 16 |  | 22 | 0.20103 | 0.27273 | 10.9545 | 13.6947 | 13.2958 | 234.7514 | 162.3295 | 233.0992 | 0.71596 | 62.534 | 0.21262 |  |  |  | 178 |  | 238 | 228.875 | 3.834 | 17.2093 | 228.2947 | 22.0306 | 0.03 |  | 0.215 | 0.15787 | 26.5698 | 75.6098 | 0.15642 | 80.8204 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-03-30 | 19:00 | 106.75 | 23 | 65 | 64 | 263 | 6.06 | 14 |  | 20.06 | 0.20103 | 0.30209 | 12.1107 | 13.8316 | 13.4288 | 237.1007 | 163.9422 | 235.415 | 0.72316 | 63.7768 | 0.21056 | 7.02 |  |  | 166 | 209 | 224 | 236.21 | -5.4509 | 22.7907 | 235.4011 | 29.4821 | 0.028 |  |  | 0.16412 |  | 77.2358 | 0.16255 | 82.7749 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-03-30 | 19:15 | 107 | 23 | 64 | 63 | 263 | 6 | 13.75 |  | 19.75 | 0.20103 | 0.3038 | 12.3165 | 13.6947 | 13.2958 | 237.2343 | 164.0464 | 235.5646 | 0.72353 | 62.7765 | 0.2118 |  |  |  | 165 |  |  | 236.8182 |  | 23.2558 | 235.999 | 30.0844 | 0.026 |  |  | 0.16533 |  | 78.8618 | 0.16374 | 84.121 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-03-30 | 19:30 | 107.25 | 23 | 64 | 63 | 263 | 5.8 | 13.6 |  | 19.4 | 0.20103 | 0.29897 | 12.5567 | 13.2382 | 12.8526 | 236.8321 | 163.8076 | 235.2216 | 0.72219 | 62.7778 | 0.20473 |  |  |  | 166 |  |  | 235.8971 |  | 22.7907 | 235.1263 | 29.3997 | 0.026 |  |  | 0.16437 |  | 78.8618 | 0.16284 | 84.0336 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-03-30 | 20:00 | 107.75 | 23 | 63 | 62 | 263 | 6 | 14 |  | 20 | 0.20103 | 0.3 | 12.15 | 13.6947 | 13.2958 | 236.928 | 163.8346 | 235.2605 | 0.7226 | 61.7774 | 0.21522 |  |  |  | 168 |  |  | 235.1429 |  | 21.8605 | 234.377 | 28.3206 | 0.026 |  |  | 0.16457 |  | 78.8618 | 0.16299 | 84.0482 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-03-30 | 20:30 | 108.25 | 23 | 63 | 62 | 263 | 6 | 14 |  | 20 | 0.20103 | 0.3 | 12.15 | 13.6947 | 13.2958 | 236.928 | 163.8346 | 235.2605 | 0.7226 | 61.7774 | 0.21522 |  |  |  | 167 |  |  | 235.5714 |  | 22.3256 | 234.7892 | 28.8724 | 0.026 |  |  | 0.16457 |  | 78.8618 | 0.16299 | 84.0482 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-03-31 | 8:15 | 120 | 23 | 64 | 62 | 263 | 5.77 | 14.57 | X | 20.34 | 0.20103 | 0.28368 | 11.9302 | 13.1697 | 12.7861 | 235.6066 | 162.9658 | 234.0129 | 0.71844 | 62.2816 | 0.2053 | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-03-31 | 14:00 |  | 23 | 62 | 61 | 263 | 6.12 | 2.76 |  | 8.88 | 0.20103 | 0.68919 | 28.6171 | 13.9686 | 13.5617 | 273.0806 | 188.8068 | 271.1196 | 0.83293 | 60.6671 | 0.22354 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-03-31 | 14:15 |  | 23 | 75 | 74 | 263 | 7.4 | 4.05 |  | 11.45 | 0.20103 | 0.64629 | 21.9694 | 16.8901 | 16.3982 | 268.796 | 185.5576 | 266.4539 | 0.82067 | 73.6793 | 0.22256
[44 empty] | 1998-03-31 | 14:25 |  | 23 | 45 | 43 | 263 | 4.35 | 1.58 |  | 5.93 | 0.20103 | 0.73356 | 43.3508 | 9.9286 | 9.6395 | 277.5289 | 192.2884 | 276.119 | 0.84536 | 43.1546 | 0.22337
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: Alison Gusses: NTR7450 membrane was used during quarters 1 and 2; NF200B membrane was used during quarters 3 and 4.
Note on R5: C. Hill (7/22/99): Consultant confirmed potential foulants were not measured during the study because they were not required under the ICR.
Note on X26: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on CE8: C. Hill (7/26/99): Rejections are higher for the 3rd and 4th quarter because the membrane was switched from the NTR7450 to the NF200B
Note on CG8: C. Hill (7/26/99): Rejections are higher for the 3rd and 4th quarter because the membrane was switched from the NTR7450 to the NF200B
Note on CY31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DL31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DQ10: Alison Gusses: Consultant verified all water quality parameters with high mass balance errors during the 90% recovery run - no changes were made and no explanation was given. High mass balance closure errors may suggest that the membrane was not operated at steady-state.
Note on DV31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on EF31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.

## NTR7450. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.33542 | [45 empty] | Recovery during sample collection (decimal) | 0.67 | [10 empty] | Recovery during sample collection (decimal) | 0.91 | [7 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 4.6 mg/L | plant | Sampling date | MM/DD/YY | 1998-06-24 | 1998-07-06 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.52 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.95 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.89 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.08 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI | Coagulation | 127 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 9:30 | 10:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 418 | [10 empty] | Influent flow rate during sample collection (mL/min) | 302 | [7 empty] | Influent flow rate during sample collection (mL/min) | 302 | [7 empty] | Influent flow rate during sample collection (mL/min) | 302 | [6 empty] | SDS-THM4F, ug/L | 216 | 216 | 216 | 216 | SDS-THM4F, ug/L | 216 | 216 | 216 | 216 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.53 mg/L | plant | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 101.7 | 137.1 | 93 | 83 | SDS-THM4p, ug/L | 101.7 | 137.1 | 93 | 83 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 6.68 | 7.7 | 7.19 | 14.1864 | 1998-07-06 | 10:30 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-07 | 9:00 | 0 | 24 | 62 | 63 | 439 | 9.1 | 3.95 |  | 13.05 | 0.33557 | 0.69732 | 32.6398 | 20.7703 | 19.578 | 332.9677 | 219.7228 | 330.6202 | 1.1207 | 61.3793 | 0.31897 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 100.3 | 100.3 | 100.3 | 100.3 | SDS-HAA5F, ug/L | 100.3 | 100.3 | 100.3 | 100.3 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.29285 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-07-06 | 13:00 | 2.5 | 24 | 57 | 58 | 439 | 8.07 | 3.96 | 12.03 | 0.33557 | 0.67082 | 35.4921 | 18.4193 | 17.362 | 0 | 0 | 0 | 0 | 57.5 | 0.30195 | 1998-07-07 | 10:00 | 1 | 24 | 62 | 63 | 439 | 8.55 | 3.7 |  | 12.25 | 0.33557 | 0.69796 | 34.8367 | 19.5149 | 18.3947 | 332.9755 | 219.8235 | 330.7717 | 1.1205 | 61.3795 | 0.29969 | 7.4 | 7.36 | 7.36 | 226 | 252 | 277 | 318.7027 | -15.0551 | 11.0236 | 317.8 | 28.8861 | 0.037 | 0.106 | 0.214 | 0.28531 | -33.3228 | 66.9643 | 0.28289 | 86.9208 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 24.65 | 22.9 | 13.5 | 12.4 | SDS-HAA5p, ug/L | 24.65 | 22.9 | 13.5 | 12.4 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 58 | 62 | 60 | 6.6667 | 1998-07-06 | 14:30 | 4 | 24 | 57 | 58 | 439 | 8.03 | 3.87 | 11.9 | 0.33557 | 0.67479 | 35.8908 | 18.328 | 17.2759 | 0 | 0 | 0 | 0 | 57.5 | 0.30045 | 1998-07-07 | 10:30 | 1.5 | 24 | 62 | 63 | 439 | 8.2 | 3.6 |  | 11.8 | 0.33557 | 0.69492 | 36.2034 | 18.7161 | 17.6417 | 332.4694 | 219.55 | 330.3602 | 1.1186 | 61.3814 | 0.28741 | 7.18 | 7.24 | 7.26 | 227 | 252 | 282 | 315.5 | -11.8794 | 10.6299 | 314.6735 | 27.8617 | 0.04 | 0.11 | 0.239 | 0.276 | -15.4812 | 64.2857 | 0.2738 | 85.3906 | [8 empty] | Sampling date | MM/DD/YY | 1998-07-08 | 1998-07-09 | --- | --- | 1998-07-08 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-10 | 1998-07-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-11 | 1998-07-11 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-12 | 1998-07-12 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 545 | 545 | 545 | 545 | SDS-TOXF, ug Cl- /L | 545 | 545 | 545 | 545 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 255 | 253 | 254 | 0.7874 | 1998-07-06 | 15:30 | 5 | 24 | 57 | 59 | 439 | 8.16 | 3.72 | 11.88 | 0.33557 | 0.68687 | 35.9529 | 18.6248 | 17.5556 | 0 | 0 | 0 | 0 | 58 | 0.30268 | 1998-07-07 | 11:00 | 2 | 24 | 62 | 63 | 439 | 8.22 | 3.63 |  | 11.85 | 0.33557 | 0.69367 | 36.0464 | 18.7617 | 17.6847 | 332.2887 | 219.4272 | 330.1755 | 1.118 | 61.382 | 0.28811 | 7.27 | 7.07 | 7.28 | 228 | 251 | 282 | 312.876 | -10.9489 | 10.2362 | 312.0814 | 26.9421 | 0.04 | 0.11 | 0.243 | 0.27504 | -13.1857 | 64.2857 | 0.27284 | 85.3394 | [8 empty] | Sampling time | hh:mm | 8:00 | 8:30 | --- | --- | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:45 | 15:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:30 | 14:30 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 185 | 230 | 135 | 125 | SDS-TOXp, ug Cl- /L | 185 | 230 | 135 | 125 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 190 | 204 | 197 | 7.1066 | 1998-07-06 | 16:00 | 5.5 | 24 | 51 | 52 | 418 | 7.17 | 3.13 | 10.3 | 0.31951 | 0.69612 | 39.5825 | 16.3651 | 15.4257 | 0 | 0 | 0 | 0 | 51.5 | 0.29953 | 1998-07-07 | 11:30 | 2.5 | 24 | 62 | 63 | 439 | 8.07 | 3.75 |  | 11.82 | 0.33557 | 0.68274 | 36.1404 | 18.4193 | 17.362 | 330.6598 | 218.3774 | 328.5958 | 1.1125 | 61.3875 | 0.28283 | 7.26 | 7.08 | 7.28 | 228 | 252 | 286 | 309.952 | -8.3748 | 10.2362 | 309.1988 | 26.261 | 0.041 | 0.11 | 0.248 | 0.26479 | -6.771 | 63.3929 | 0.26274 | 84.3949 | [8 empty] | Operation time | hh.hh | 23 | 47.5 | --- | --- | 23 | --- | --- | --- | --- | --- | Operation time | hh.hh | 79.5 | 79.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 102.75 | 102.75 | --- | --- | --- | --- | --- | Cumulative time | hr | 125.5 | 125.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 7.575 | 7.575 | 7.575 | 7.575 | SDS-CDF, mg/L | 7.575 | 7.575 | 7.575 | 7.575 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 128 | 146 | 137 | 13.1387 | 1998-07-06 | 16:20 | 5.8333 | 24 | 70 | 72 | 439 | 10.2 | 5.2 | 15.4 | 0.33557 | 0.66234 | 27.5065 | 23.281 | 21.9445 | 0 | 0 | 0 | 0 | 71 | 0.30908 | 1998-07-07 | 12:00 | 3 | 24 | 62 | 64 | 439 | 8.6 | 4.07 |  | 12.67 | 0.33557 | 0.67877 | 33.6488 | 19.629 | 18.5023 | 330.1606 | 217.9566 | 327.9625 | 1.111 | 61.889 | 0.29896 | [27 empty] | pH | --- | 7.83 | 7.89 | 7.86 | 0.76336 | 7.83 | --- | --- | --- | --- | --- | pH | --- | 8.02 | 7.94 | --- | --- | --- | --- | --- | pH | --- | 7.95 | 8 | --- | --- | --- | --- | --- | pH | --- | 8.16 | 7.35 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 4.235 | 4.24 | 3.54 | 3.24 | SDS-CDp, mg/L | 4.235 | 4.24 | 3.54 | 3.24 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 6.5 | 57.7216 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.206 | 0.19 | 0.198 | 8.0808 | 1998-07-06 | 17:00 | 6.5 | 24 | 59 | 60 | 439 | 8.52 | 3.95 | 12.47 | 0.33557 | 0.68324 | 34.2045 | 19.4464 | 18.3301 | 0 | 0 | 0 | 0 | 59.5 | 0.30807 | 1998-07-07 | 13:30 | 4.5 | 24 | 62 | 64 | 439 | 7.79 | 3.5 |  | 11.29 | 0.33557 | 0.68999 | 37.884 | 17.7803 | 16.7596 | 331.6794 | 219.0991 | 329.6817 | 1.1158 | 61.8842 | 0.27082 | 7.43 | 7.35 | 7.39 | 229 | 249 | 286 | 309.6429 | -8.2667 | 9.8425 | 308.9274 | 25.8725 | 0.038 | 0.11 | 0.256 | 0.2767 | -8.0871 | 66.0714 | 0.27458 | 86.1609 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 5.8 | 5.8 | 5.8 | 5.8 | TOCF, mg/L | 5.8 | 5.8 | 5.8 | 5.8 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 16.5 | 67.7216 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.19 | BMRL | 0.19 | #VALUE! | 1998-07-07 | 8:00 | 21.5 | 24 | 58 | 59 | 439 | 8.13 | 3.85 | 11.98 | 0.33557 | 0.67863 | 35.6444 | 18.5563 | 17.4911 | 0 | 0 | 0 | 0 | 58.5 | 0.29899 | 1998-07-07 | 16:00 | 7 | 24 | 62 | 63 | 439 | 7.42 | 3.46 |  | 10.88 | 0.33557 | 0.68199 | 39.3493 | 16.9358 | 15.9636 | 330.4503 | 218.3507 | 328.5555 | 1.1115 | 61.3885 | 0.26004 | 7.42 | 7.35 |  | 228 | 251 | 291 | 309.7572 | -6.4458 | 10.2362 | 309.0663 | 26.2294 | 0.034 | 0.111 | 0.255 | 0.27927 | -9.5183 | 69.6429 | 0.2772 | 87.7344 | [8 empty] | Alkalinity | mg/L as CaCO3 | 56 | 52 | 54 | 7.4074 | 82 | 72.1818 | 11.9734 | 10 | 72.0431 | 25.0449 | Alkalinity | mg/L as CaCO3 | 70 | 94 | -41.1111 | 143.7352 | -16.6667 | -40.1151 | 274.498 | Alkalinity | mg/L as CaCO3 | 48 | 68 | 71.5294 | -5.1903 | 20 | 71.3215 | 32.6992 | Alkalinity | mg/L as CaCO3 | 54 | 60 | 62.5714 | -4.2857 | 10 | 62.4945 | 13.5923 | TOCp, mg/L | 1.6 | 2.3 | 1 | 0.9 | TOCp, mg/L | 1.6 | 2.3 | 1 | 0.9 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 55.7216 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 5.8 | 5.8 | 5.8 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-07 | 16:30 | 7.5 | 24 | 63 | 64 | 418 | 7.14 | 3.35 |  | 10.49 | 0.31951 | 0.68065 | 38.8475 | 16.2967 | 15.3612 | 330.2673 | 218.2163 | 328.3533 | 1.1109 | 62.3891 | 0.24622 | 7.46 | 7.35 | 7.3 | 222 | 250 | 288 | 322.203 | -11.876 | 12.5984 | 321.3472 | 30.9158 | 0.034 | 0.107 | 0.257 | 0.27824 | -8.2664 | 69.6429 | 0.27616 | 87.6882 | [8 empty] | Total dissolved solids | mg/L | 222 | 224 | 223 | 0.89686 | 303 | 316.9394 | -4.6005 | 12.2047 | 316.2227 | 29.4801 | Total dissolved solids | mg/L | 237 | 332 | 425.8889 | -28.2798 | 6.6929 | 424.1956 | 44.1295 | Total dissolved solids | mg/L | 196 | 292 | 309.7255 | -6.0704 | 22.8346 | 308.7208 | 36.5122 | Total dissolved solids | mg/L | 183 | 270 | 284.4286 | -5.3439 | 27.9528 | 283.5177 | 35.4538 | UV254 F, cm-1 | 0.112 | 0.112 | 0.112 | 0.112 | UV254 F, cm-1 | 0.112 | 0.112 | 0.112 | 0.112 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 3.6429 | 54.8644 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.113 | 0.111 | 0.112 | 1.7857 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 8:00 | 23 | 24 | 63 | 64 | 418 | 7.3 | 3.95 |  | 11.25 | 0.31951 | 0.64889 | 36.1556 | 16.6619 | 15.7054 | 325.7277 | 215.1884 | 323.7972 | 1.0957 | 62.4043 | 0.25167 | [27 empty] | Total hardness | mg/L as CaCO3 | 166 | 164 | 165 | 1.2121 | 251 | 261.9697 | -4.3704 | 16.2437 | 261.2299 | 36.8372 | Total hardness | mg/L as CaCO3 | 176 | 286 | 409.3333 | -43.1235 | 10.6599 | 407.2416 | 56.7824 | Total hardness | mg/L as CaCO3 | 156 | 226 | 236.3922 | -4.5983 | 20.8122 | 235.6819 | 33.8091 | Total hardness | mg/L as CaCO3 | 116 | 194 | 231.7143 | -19.4404 | 41.1168 | 230.6752 | 49.7128 | UV254 p, cm-1 | 0.0295 | 0.05 | 0.022 | 0.017 | UV254 p, cm-1 | 0.0295 | 0.05 | 0.022 | 0.017 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 1.9483 | 1.9138 | 1.931 | 1.7857 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 9:00 | 24 | 24 | 63 | 64 | 418 | 6.53 | 3.48 |  | 10.01 | 0.31951 | 0.65235 | 40.7582 | 14.9044 | 14.0488 | 326.1041 | 215.574 | 324.3773 | 1.0967 | 62.4033 | 0.22513 | 7.56 | 7.5 | 7.53 | 221 | 252 | 292 | 315.9224 | -8.1926 | 12.9921 | 315.181 | 29.8816 | 0.03 | 0.109 | 0.249 | 0.26587 | -6.7742 | 73.2143 | 0.26403 | 88.6375 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 110 | 124 | 117 | 11.9658 | 213 | 177.6061 | 16.6169 | 14.5985 | 177.1437 | 33.9519 | Calcium hardness | mg/L as CaCO3 | 142 | 256 | 86.4444 | 66.2326 | -3.6496 | 86.9425 | -63.3264 | Calcium hardness | mg/L as CaCO3 | 96 | 156 | 176.3922 | -13.0719 | 29.927 | 175.6819 | 45.3558 | Calcium hardness | mg/L as CaCO3 | 86 | 150 | 158.8571 | -5.9048 | 37.2263 | 158.2029 | 45.6394 | BromideF, ug/L | 180 | 180 | 180 | 180 | BromideF, ug/L | 180 | 180 | 180 | 180 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 180 | 180 | 180 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 10:00 | 25 | 24 | 63 | 64 | 418 | 6.58 | 3.27 |  | 9.85 | 0.31951 | 0.66802 | 41.4365 | 15.0185 | 14.1564 | 328.3511 | 217.0504 | 326.599 | 1.1042 | 62.3958 | 0.22688 | 7.51 | 7.48 | 7.47 | 221 | 251 | 288 | 320.4037 | -11.2513 | 12.9921 | 319.6213 | 30.8557 | 0.031 | 0.11 | 0.256 | 0.27499 | -7.4183 | 72.3214 | 0.27307 | 88.6476 | [8 empty] | Turbidity | ntu | 0.072 | 0.096 | 0.084 | 28.5714 | 0.265 | 0.42945 | -62.0583 | 57.5758 | 0.42682 | 80.3195 | Turbidity | ntu | 0.095 | 0.472 | 1.2394 | -162.5942 | 52.0202 | 1.2292 | 92.2713 | Turbidity | ntu | 0.085 | 0.198 | 0.30657 | -54.8326 | 57.0707 | 0.30461 | 72.0956 | Turbidity | ntu | 0.085 | 0.171 | 0.24643 | -44.1103 | 57.0707 | 0.24498 | 65.3031 | Bromidep, ug/L | 170 | 180 | 160 | 160 | Bromidep, ug/L | 170 | 180 | 160 | 160 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 9 | 8 | 8.5 | 11.7647 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 11:00 | 26 | 24 | 63 | 64 | 418 | 6.29 | 3.09 |  | 9.38 | 0.31951 | 0.67058 | 43.5629 | 14.3566 | 13.5325 | 328.6742 | 217.3159 | 326.9985 | 1.1052 | 62.3948 | 0.21688 | 8.42 | 8.17 | 8.18 | 214 | 253 | 303 | 335.4239 | -10.701 | 15.748 | 334.5104 | 36.0259 | 0.03 | 0.112 | 0.262 | 0.27892 | -6.4577 | 73.2143 | 0.27705 | 89.1715 | [8 empty] | Ammonia | mg NH3-N / L | 0.17 | 0.14 | 0.155 | 19.3548 | NA | 0.26106 | #VALUE! | 18.4211 | 0.26025 | 40.4422 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 60 | 60 | 60 | 60 | AlkF, mg/L CaCO3 | 60 | 60 | 60 | 60
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.06 | 0.79 | 0.925 | 29.1892 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 13:30 | 28.5 | 24 | 63 | 64 | 418 | 6.26 | 3.01 |  | 9.27 | 0.31951 | 0.6753 | 44.0917 | 14.2881 | 13.4679 | 329.3511 | 217.7689 | 327.6801 | 1.1075 | 62.3925 | 0.21586 | 7.58 | 7.47 | 7.57 | 223 | 252 | 301 | 318.4718 | -5.8046 | 12.2047 | 317.7569 | 29.8206 | 0.029 | 0.111 | 0.269 | 0.28462 | -5.8059 | 74.1071 | 0.2827 | 89.7419 | [8 empty] | Total organic carbon | mg/L | 1.5 | 1.7 | 1.6 | 12.5 | 13.95 | 14.3273 | -2.7045 | 72.4138 | 14.2302 | 88.7563 | Total organic carbon | mg/L | 2.3 | 38.1 | 41.1889 | -8.1073 | 60.3448 | 40.8403 | 94.3683 | Total organic carbon | mg/L | 1 | 10 | 10.4118 | -4.1176 | 82.7586 | 10.3286 | 90.3182 | Total organic carbon | mg/L | 0.9 | 7.6 | 7.9 | -3.9474 | 84.4828 | 7.8371 | 88.5162 | Alkp, mg/L CaCO3 | 54 | 70 | 48 | 54 | Alkp, mg/L CaCO3 | 54 | 70 | 48 | 54
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 7.94 | 7.21 | 7.575 | 9.637 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 14:30 | 29.5 | 24 | 63 | 64 | 418 | 6.33 | 3.06 |  | 9.39 | 0.31951 | 0.67412 | 43.5154 | 14.4479 | 13.6185 | 329.1921 | 217.6512 | 327.503 | 1.107 | 62.393 | 0.21827 | 7.53 | 7.48 | 7.49 | 221 | 250 | 301 | 322.2647 | -7.0647 | 12.9921 | 321.498 | 31.2593 | 0.028 | 0.111 | 0.265 | 0.28576 | -7.8357 | 75 | 0.28381 | 90.1343 | [8 empty] | UV254 | cm-1 | 0.029 | 0.03 | 0.0295 | 3.3898 | 0.269 | 0.2795 | -3.9033 | 73.6607 | 0.27759 | 89.3729 | UV254 | cm-1 | 0.05 | 0.714 | 0.73889 | -3.4858 | 55.3571 | 0.73271 | 93.176 | UV254 | cm-1 | 0.022 | 0.198 | 0.19847 | -0.23767 | 80.3571 | 0.19691 | 88.8275 | UV254 | cm-1 | 0.017 | 0.146 | 0.15271 | -4.5988 | 84.8214 | 0.1515 | 88.7785 | T-HdF, mg/L CaCO3 | 197 | 197 | 197 | 197 | T-HdF, mg/L CaCO3 | 197 | 197 | 197 | 197
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 15:30 | 30.5 | 24 | 63 | 64 | 418 | 6.18 | 3.01 |  | 9.19 | 0.31951 | 0.67247 | 44.4842 | 14.1055 | 13.2958 | 328.9302 | 217.5049 | 327.2828 | 1.106 | 62.394 | 0.21309 | 7.76 | 7.63 | 7.68 | 223 | 250 | 302 | 317.6478 | -5.1814 | 12.2047 | 316.9482 | 29.6415 | 0.028 | 0.114 | 0.272 | 0.28447 | -4.5828 | 75 | 0.28257 | 90.0909 | [8 empty] | SUVA | L/(mg*m) | 1.9333 | 1.7647 | 1.849 | 9.1198 | 1.9283 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.1739 | 1.874 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.2 | 1.98 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8889 | 1.9211 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 165 | 176 | 156 | 116 | T-Hdp, mg/L CaCO3 | 165 | 176 | 156 | 116
Process Train Name | Enhanced Coagulation/Lime Softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-08 | 16:30 | 31.5 | 24 | 63 | 64 | 418 | 6.05 | 3 |  | 9.05 | 0.31951 | 0.66851 | 45.1878 | 13.8088 | 13.0161 | 328.3395 | 217.1375 | 326.73 | 1.104 | 62.396 | 0.2086 | 7.56 | 7.49 | 7.58 | 244 | 255 | 321 | 274.1667 | 14.5898 | 3.937 | 273.9484 | 10.9321 | 0.03 | 0.112 | 0.273 | 0.27737 | -1.5995 | 73.2143 | 0.27558 | 89.1137 | [8 empty] | Bromide | mg/L | 170 | 170 | 170 | 0 | --- | 200.303 | --- | 5.5556 | 200.0718 | 15.0305 | Bromide | mg/L | 180 | --- | 180 | --- | 0 | 180 | 0 | Bromide | mg/L | 160 | --- | 199.2157 | --- | 11.1111 | 198.8692 | 19.5451 | Bromide | mg/L | 160 | --- | 188.5714 | --- | 11.1111 | 188.3149 | 15.0359 | Ca-HdF, mg/L CaCO3 | 137 | 137 | 137 | 137 | Ca-HdF, mg/L CaCO3 | 137 | 137 | 137 | 137
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 8:00 | 47 | 24 | 63 | 64 | 418 | 5.83 | 2.43 |  | 8.26 | 0.31951 | 0.70581 | 49.6053 | 13.3067 | 12.5428 | 333.7537 | 220.7579 | 332.1777 | 1.1221 | 62.3779 | 0.20108 | [27 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 4.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 117 | 142 | 96 | 86 | Ca-Hdp, mg/L CaCO3 | 117 | 142 | 96 | 86
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 550 | 540 | 545 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 8:30 | 47.5 | 24 | 63 | 64 | 418 | 5.83 | 2.43 |  | 8.26 | 0.31951 | 0.70581 | 49.6053 | 13.3067 | 12.5428 | 333.7537 | 220.7579 | 332.1777 | 1.1221 | 62.3779 | 0.20108 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.81 | 0.72 | 0.765 | 11.7647 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.76 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.96 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.26 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 140 | 130 | 135 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 9:00 | 48 | 23.8 | 63 | 64 | 418 | 6.03 | 2.79 |  | 8.82 | 0.31951 | 0.68367 | 46.3923 | 13.7632 | 13.05 | 330.5308 | 218.5902 | 328.916 | 1.1113 | 62.3887 | 0.20917 | 7.66 | 7.55 | 7.52 | 223 | 254 | 316 | 321 | -1.5823 | 12.2047 | 320.2931 | 30.3763 | 0.029 | 0.111 | 0.294 | 0.29139 | 0.88874 | 74.1071 | 0.28949 | 89.9825 | [8 empty] | SDS-Cl2 demand | mg/L | 4.19 | 4.28 | 4.235 | 2.1251 | --- | 14.3562 | --- | 44.0924 | 14.279 | 70.341 | SDS-Cl2 demand | mg/L | 4.24 | --- | 41.2956 | --- | 44.0264 | 40.9634 | 89.6493 | SDS-Cl2 demand | mg/L | 3.54 | --- | 11.4518 | --- | 53.2673 | 11.3819 | 68.8979 | SDS-Cl2 demand | mg/L | 3.24 | --- | 9.4329 | --- | 57.2277 | 9.3772 | 65.4483 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 55 | 59 | 57 | 7.0175 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 10:00 | 49 | 23.8 | 63 | 64 | 302 | 5.88 | 2.82 |  | 8.7 | 0.23084 | 0.67586 | 33.7126 | 13.4208 | 12.7254 | 329.7293 | 217.6809 | 327.5477 | 1.1096 | 62.3904 | 0.20396 | 7.55 | 7.5 | 7.49 | 223 | 252 | 304 | 318.6383 | -4.8152 | 12.2047 | 317.7072 | 29.8096 | 0.029 | 0.11 | 0.284 | 0.28506 | -0.37459 | 74.1071 | 0.28257 | 89.7371 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 125.9843 | 182.5095 | 117.0732 | 108.2707 | Qp/QT (THM4), % | 157.4803 | 228.1369 | 146.3415 | 135.3383
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 22 | 22 | 22 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 11:00 | 50 | 23.8 | 63 | 64 | 302 | 5.55 | 2.78 |  | 8.33 | 0.23084 | 0.66627 | 35.2545 | 12.6676 | 12.0112 | 328.2688 | 216.7987 | 326.2202 | 1.1045 | 62.3955 | 0.1925 | 7.78 | 7.68 | 7.74 | 219 | 251 | 296 | 323.8741 | -9.4169 | 13.7795 | 322.9104 | 32.1793 | 0.031 | 0.109 | 0.268 | 0.27371 | -2.1301 | 72.3214 | 0.27148 | 88.581 | [8 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | NA | NA | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | 2.1 | 1.9 | 2 | 10 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 12:00 | 51 | 23.8 | 63 | 64 | 302 | 5.97 | 2.77 |  | 8.74 | 0.23084 | 0.68307 | 33.5538 | 13.6262 | 12.9202 | 330.8006 | 218.3656 | 328.5779 | 1.1132 | 62.3868 | 0.2071 | 7.57 | 7.55 | 7.54 | 220 | 250 | 298 | 327.278 | -9.8248 | 13.3858 | 326.2176 | 32.5604 | 0.03 | 0.11 | 0.27 | 0.28873 | -6.9368 | 73.2143 | 0.28617 | 89.5168 | [8 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | NA | NA | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 219.1 | 212.9 | 216 | 2.8704 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 13:30 | 52.5 | 24 | 63 | 64 | 302 | 5.89 | 2.77 |  | 8.66 | 0.23084 | 0.68014 | 33.873 | 13.4436 | 12.6719 | 330.3547 | 218.0913 | 328.1652 | 1.1117 | 62.3883 | 0.20311 | 7.54 | 7.5 | 7.49 | 219 | 250 | 303 | 328.4224 | -8.3902 | 13.7795 | 327.3553 | 33.1002 | 0.029 | 0.111 | 0.271 | 0.28849 | -6.4529 | 74.1071 | 0.28596 | 89.8586 | [8 empty] | SDS-TOX | mg Cl- /L | 190 | 180 | 185 | 5.4054 | --- | 1275.9091 | --- | 66.055 | 1267.5858 | 85.4053 | SDS-TOX | mg Cl- /L | 230 | --- | 3730 | --- | 57.7982 | 3698.6246 | 93.7815 | SDS-TOX | mg Cl- /L | 135 | --- | 938.9216 | --- | 75.2294 | 931.8192 | 85.5122 | SDS-TOX | mg Cl- /L | 125 | --- | 725 | --- | 77.0642 | 719.6119 | 82.6295 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 5.1 | 5.6 | 5.35 | 9.3458 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 14:30 | 53.5 | 23.9 | 63 | 64 | 302 | 5.98 | 2.83 |  | 8.81 | 0.23084 | 0.67877 | 33.2792 | 13.649 | 12.9036 | 330.1755 | 217.9504 | 327.9532 | 1.1111 | 62.3889 | 0.20683 | 7.63 | 7.53 | 7.61 | 222 | 250 | 302 | 321.6184 | -6.4962 | 12.5984 | 320.6321 | 30.7618 | 0.029 | 0.11 | 0.274 | 0.28739 | -4.8851 | 74.1071 | 0.28483 | 89.8184 | [8 empty] | SDS-CHCl3 | mg/L | 29 | 27 | 28 | 7.1429 | --- | 352.2424 | --- | 79.2593 | 349.7686 | 91.9947 | SDS-CHCl3 | mg/L | 64 | --- | 852.8889 | --- | 52.5926 | 845.817 | 92.4334 | SDS-CHCl3 | mg/L | 25 | --- | 240.6863 | --- | 81.4815 | 238.7808 | 89.5301 | SDS-CHCl3 | mg/L | 17 | --- | 185.5714 | --- | 87.4074 | 184.0576 | 90.7638 | SDS-CDb, mg/L | NA | NA | NA | NA | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7 | [13 empty] | SDS-DCAA* | mg/L | 43 | 38 | 40.5 | 12.3457 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 15:30 | 54.5 | 23.9 | 63 | 64 | 302 | 5.88 | 2.75 |  | 8.63 | 0.23084 | 0.68134 | 33.9942 | 13.4208 | 12.6878 | 330.5286 | 218.2086 | 328.3417 | 1.1123 | 62.3877 | 0.20337 | 7.71 | 7.57 | 7.65 | 232 | 255 | 318 | 301.04 | 5.3333 | 8.6614 | 300.3679 | 22.7614 | 0.03 | 0.11 | 0.271 | 0.28733 | -6.0262 | 73.2143 | 0.28483 | 89.4672 | [8 empty] | SDS-BDCM | mg/L | 34 | 31 | 32.5 | 9.2308 | --- | 106.7424 | --- | 42.9825 | 106.176 | 69.3904 | SDS-BDCM | mg/L | 44 | --- | 188.4444 | --- | 22.807 | 187.1496 | 76.4894 | SDS-BDCM | mg/L | 29 | --- | 83.902 | --- | 49.1228 | 83.4169 | 65.2349 | SDS-BDCM | mg/L | 25 | --- | 70.7143 | --- | 56.1404 | 70.3038 | 64.44 | TOCb, mg/L | NA | NA | NA | NA | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 48 | 47 | 47.5 | 2.1053 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-09 | 16:30 | 55.5 | 23.9 | 63 | 64 | 302 | 6 | 2.87 |  | 8.87 | 0.23084 | 0.67644 | 33.0474 | 13.6947 | 12.9468 | 329.8393 | 217.7235 | 327.6118 | 1.11 | 62.39 | 0.20751 | 7.71 | 7.56 | 7.71 | 229 | 250 | 307 | 306.2648 | 0.23948 | 9.8425 | 305.4973 | 25.0402 | 0.029 | 0.11 | 0.273 | 0.28552 | -4.5858 | 74.1071 | 0.28297 | 89.7516 | [8 empty] | SDS-DBCM | mg/L | 34 | 29 | 31.5 | 15.873 | --- | 2.7121 | --- | -43.1818 | 2.9318 | -974.4388 | SDS-DBCM | mg/L | 20 | --- | 42.2222 | --- | 9.0909 | 42.023 | 52.407 | SDS-DBCM | mg/L | 27 | --- | 17.1961 | --- | -22.7273 | 17.2827 | -56.2257 | SDS-DBCM | mg/L | 28 | --- | 19.4286 | --- | -27.2727 | 19.5055 | -43.5489 | UV254 b, cm-1 | NA | NA | NA | NA | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 35837 | [13 empty] | SDS-MBAA* | mg/L | 2.1 | 1.7 | 1.9 | 21.0526 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 8:00 | 71 | 23.9 | 63 | 64 | 302 | 5.75 | 3.8 |  | 9.55 | 0.23084 | 0.60209 | 30.623 | 13.1241 | 12.4073 | 319.3137 | 210.8362 | 317.2483 | 1.0744 | 62.4256 | 0.19875 | [27 empty] | SDS-CHBr3 | mg/L | 12 | 7.4 | 9.7 | 47.4227 | --- | -13.6333 | --- | -385 | -13.4553 | 172.0905 | SDS-CHBr3 | mg/L | 9.1 | --- | -69.7889 | --- | -355 | -69.0817 | 113.1728 | SDS-CHBr3 | mg/L | 12 | --- | -7.6078 | --- | -500 | -7.4346 | 261.4071 | SDS-CHBr3 | mg/L | 13 | --- | -2.7143 | --- | -550 | -2.5732 | 605.2135 | Bromideb, ug/L | NA | NA | NA | NA | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 5.1 | 5 | 5.05 | 1.9802 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 9:00 | 72 | 23.8 | 63 | 64 | 302 | 5.67 | 2.38 |  | 8.05 | 0.23084 | 0.70435 | 36.5155 | 12.9415 | 12.2709 | 333.8762 | 220.4717 | 331.7471 | 1.1234 | 62.3766 | 0.19672 | [27 empty] | SDS-THM4 | mg/L | 109 | 94.4 | 101.7 | 14.3559 | --- | 448.0636 | --- | 52.9167 | 445.421 | 77.1677 | SDS-THM4 | mg/L | 137.1 | --- | 1013.7667 | --- | 36.5278 | 1005.9079 | 86.3705 | SDS-THM4 | mg/L | 93 | --- | 334.1765 | --- | 56.9444 | 332.0458 | 71.9918 | SDS-THM4 | mg/L | 83 | --- | 273 | --- | 61.5741 | 271.2938 | 69.4059 | Alkb, mg/L CaCO3 | NA | NA | NA | NA | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 19 | 18 | 18.5 | 5.4054 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 10:00 | 73 | 23.8 | 63 | 64 | 302 | 5.6 | 2.28 |  | 7.88 | 0.23084 | 0.71066 | 37.3249 | 12.7817 | 12.1194 | 334.8032 | 221.1016 | 332.6948 | 1.1265 | 62.3735 | 0.1943 | 8.26 | 7.82 | 7.81 | 219 | 250 | 313 | 339.9649 | -8.615 | 13.7795 | 338.8434 | 35.3684 | 0.027 | 0.109 | 0.288 | 0.32077 | -11.3791 | 75.8929 | 0.31805 | 91.5107 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 11:00 | 74 | 23.8 | 63 | 64 | 302 | 5.73 | 2.27 |  | 8 | 0.23084 | 0.71625 | 36.75 | 13.0784 | 12.4008 | 335.6744 | 221.6438 | 333.5108 | 1.1295 | 62.3705 | 0.19882 | 7.67 | 7.57 | 7.63 | 224 | 250 | 307 | 329.7269 | -7.4029 | 11.811 | 328.7239 | 31.8577 | 0.027 | 0.11 | 0.292 | 0.32656 | -11.8354 | 75.8929 | 0.32372 | 91.6594 | [8 empty] | SDS-DCAA* | mg/L | 8.2 | 10 | 9.1 | 19.7802 | --- | 104.2515 | --- | 77.5309 | 103.5255 | 91.2099 | SDS-DCAA* | mg/L | 12 | --- | 328.6667 | --- | 70.3704 | 325.8279 | 96.3171 | SDS-DCAA* | mg/L | 5.7 | --- | 73.9353 | --- | 85.9259 | 73.3325 | 92.2272 | SDS-DCAA* | mg/L | 4.4 | --- | 55.9714 | --- | 89.1358 | 55.5083 | 92.0733 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 7.4 | 8.6 | 8 | 15 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 13:30 | 76.5 | 23.9 | 63 | 64 | 302 | 5.64 | 2.3 |  | 7.94 | 0.23084 | 0.71033 | 37.0353 | 12.873 | 12.17 | 334.7629 | 221.0648 | 332.6395 | 1.1264 | 62.3736 | 0.19511 | 7.65 | 7.58 | 7.58 | 215 | 251 | 310 | 349.6348 | -12.7854 | 15.3543 | 348.3776 | 38.2854 | 0.028 | 0.11 | 0.298 | 0.31798 | -6.7056 | 75 | 0.31527 | 91.1189 | [8 empty] | SDS-TCAA* | mg/L | 5.2 | 8 | 6.6 | 42.4242 | --- | 130.5394 | --- | 86.1053 | 129.5938 | 94.9072 | SDS-TCAA* | mg/L | 3.6 | --- | 491.3778 | --- | 92.4211 | 487.0051 | 99.2608 | SDS-TCAA* | mg/L | 1.8 | --- | 91.4078 | --- | 96.2105 | 90.6162 | 98.0136 | SDS-TCAA* | mg/L | 1.6 | --- | 67.1714 | --- | 96.6316 | 66.5826 | 97.597
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 27 | 32 | 29.5 | 16.9492 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 13:45 | 76.75 | 23.9 | 63 | 64 | 302 | 5.89 | 0.48 |  | 6.37 | 0.23084 | 0.92465 | 46.4097 | 13.4436 | 12.7094 | 370.3811 | 244.5156 | 367.9263 | 1.2464 | 62.2536 | 0.20416 | [27 empty] | SDS-MBAA* | mg/L | 1 | 1.4 | 1.2 | 33.3333 | --- | 3.3212 | --- | 36.8421 | 3.305 | 63.6917 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 103.3 | 97.3 | 100.3 | 5.9821 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 14:00 | 77 | 23.9 | 63 | 64 | 302 | 5.89 | 0.48 |  | 6.37 | 0.23084 | 0.92465 | 46.4097 | 13.4436 | 12.7094 | 370.3811 | 244.5156 | 367.9263 | 1.2464 | 62.2536 | 0.20416 | 7.66 | 7.6 |  | 227 | 250 |  | 585.3125 |  | 10.6299 | 581.8184 | 60.9844 | 0.029 | 0.111 | 0.282 | 1.1305 | -300.8791 | 74.1071 | 1.1197 | 97.4101 | [8 empty] | SDS-DBAA* | mg/L | 7.9 | 7.6 | 7.75 | 3.871 | --- | -0.43182 | --- | -53.4653 | -0.36939 | 2198.0328 | SDS-DBAA* | mg/L | 7.3 | --- | -17.7 | --- | -44.5545 | -17.4759 | 141.7718 | SDS-DBAA* | mg/L | 6 | --- | 4.1373 | --- | -18.8119 | 4.1537 | -44.4491 | SDS-DBAA* | mg/L | 6.4 | --- | 4.4714 | --- | -26.7327 | 4.4887 | -42.5788 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 122.3 | 115.3 | 118.8 | 5.8923 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 14:20 | 77.3333 | 23.8 | 63 | 64 | 302 | 5.63 | 0.46 |  | 6.09 | 0.23084 | 0.92447 | 48.5895 | 12.8502 | 12.1843 | 370.2498 | 244.5018 | 367.9055 | 1.2458 | 62.2542 | 0.19572 | 7.74 | 7.72 |  |  | 252 | [6 empty] | 0.031 | 0.11 | 0.311 | 1.1034 | -254.7812 | 72.3214 | 1.0934 | 97.1647 | [8 empty] | SDS-BCAA* | mg/L | 9.7 | 12 | 10.85 | 21.1982 | --- | 34.0318 | --- | 41.3514 | 33.8549 | 67.9515 | SDS-BCAA* | mg/L | 9.7 | --- | 107.4778 | --- | 47.5676 | 106.6013 | 90.9007 | SDS-BCAA* | mg/L | 5.8 | --- | 30.702 | --- | 68.6486 | 30.482 | 80.9724 | SDS-BCAA* | mg/L | 5.5 | --- | 24.0714 | --- | 70.2703 | 23.9047 | 76.9919 | Qp/QT (HAA5), % | 61.2029 | 59.8191 | 53.341 | 52.6735 | Qp/QT (HAA5), % | 96.8936 | 94.7028 | 84.447 | 83.3902
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 14:40 | 77.6667 | 23.8 | 63 | 64 | 302 | 5.66 | 0.45 |  | 6.11 | 0.23084 | 0.92635 | 48.4272 | 12.9186 | 12.2493 | 370.6068 | 244.7291 | 368.2476 | 1.247 | 62.253 | 0.19677 | 8.13 | 7.95 |  | 229 | 248 |  | 568.4444 |  | 9.8425 | 565.2636 | 59.4879 | 0.033 | 0.11 | 0.35 | 1.1056 | -215.8984 | 70.5357 | 1.0956 | 96.9879 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 146.0451 | 168.8027 | 150.3906 | 145.9443 | SDS-THM4b, ug/L | 105.2506 | 141.2795 | 112.1302 | 105.091
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 15:00 | 78 | 23.8 | 63 | 64 | 302 | 5.4 | 0.56 |  | 5.96 | 0.23084 | 0.90604 | 49.6711 | 12.3252 | 11.6866 | 366.8193 | 242.3002 | 364.5928 | 1.2341 | 62.2659 | 0.18769 | 7.57 | 7.55 |  |  | 250 | 348 |  | #VALUE! |  |  |  | 0.035 | 0.11 | 0.382 | 0.8545 | -123.6911 | 68.75 | 0.84717 | 95.8686 | [8 empty] | SDS-CDBAA | mg/L | 6.1 | 8.8 | 7.45 | 36.2416 | --- | 9.1167 | --- | 6.875 | 9.104 | 18.1674 | SDS-CDBAA | mg/L | 2.3 | --- | 65.6333 | --- | 71.25 | 65.0656 | 96.4651 | SDS-CDBAA | mg/L | 2.1 | --- | 13.6686 | --- | 73.75 | 13.5664 | 84.5206 | SDS-CDBAA | mg/L | 2.8 | --- | 10.2286 | --- | 65 | 10.1619 | 72.446 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-10 | 15:30 | 78.5 | 23.9 | 63 | 64 | 302 | 5.2 | 0.54 |  | 5.74 | 0.23084 | 0.90592 | 51.6132 | 11.8687 | 11.2205 | 366.7257 | 242.2939 | 364.5832 | 1.2336 | 62.2664 | 0.1802 | 7.54 | 7.52 | 7.43 | 236 | 241 | 342 | 427.3333 | -24.9513 | 7.0866 | 425.6861 | 44.5601 | 0.037 | 0.11 | 0.411 | 0.83422 | -102.9738 | 66.9643 | 0.82736 | 95.5279 | [8 empty] | SDS-DCBAA | mg/L | 7.5 | 13 | 10.25 | 53.6585 | --- | 68.5833 | --- | 65.2542 | 68.1383 | 84.9571 | SDS-DCBAA | mg/L | 3.1 | --- | 296.4333 | --- | 89.4915 | 293.8038 | 98.9449 | SDS-DCBAA | mg/L | 1.8 | --- | 56.1137 | --- | 93.8983 | 55.6339 | 96.7646 | SDS-DCBAA | mg/L | 2.6 | --- | 41.0286 | --- | 91.1864 | 40.6835 | 93.6092 | SDS-TOXb, ug Cl- /L | 324.6695 | 356.5698 | 326.3018 | 323.7713 | SDS-TOXb, ug Cl- /L | 196.1831 | 246.686 | 198.7673 | 194.7611
[44 empty] | 1998-07-10 | 16:00 | 79 | 23.9 | 63 | 64 | 302 | 5.43 | 0.58 |  | 6.01 | 0.23084 | 0.90349 | 49.2496 | 12.3937 | 11.7168 | 366.3728 | 241.997 | 364.1365 | 1.2326 | 62.2674 | 0.18817 | 7.69 | 7.64 | 7.67 | 239 | 250 | 340 | 394.431 | -16.0091 | 5.9055 | 393.0337 | 39.191 | 0.036 | 0.111 | 0.455 | 0.82352 | -80.9928 | 67.8571 | 0.81644 | 95.5906 | [8 empty] | SDS-HAA5 | mg/L | 22.3 | 27 | 24.65 | 19.0669 | --- | 253.8924 | --- | 75.4237 | 252.1434 | 90.2238 | SDS-HAA5 | mg/L | 22.9 | --- | 882.9 | --- | 77.1685 | 875.1906 | 97.3834 | SDS-HAA5 | mg/L | 13.5 | --- | 183.6961 | --- | 86.5404 | 182.1925 | 92.5903 | SDS-HAA5 | mg/L | 12.4 | --- | 137.9714 | --- | 87.6371 | 136.8438 | 90.9386 | SDS-CDb, mg/L | 5.5308 | 5.58 | 5.4227 | 5.2916 | SDS-CDb, mg/L | 4.3388 | 4.4167 | 4.1676 | 3.96
[44 empty] | 1998-07-10 | 16:30 | 79.5 | 23.9 | 63 | 64 | 302 | 5.29 | 0.6 |  | 5.89 | 0.23084 | 0.89813 | 50.2733 | 12.0741 | 11.4147 | 365.3635 | 241.369 | 363.1915 | 1.2291 | 62.2709 | 0.18331 | 7.71 | 7.6 | 7.68 | 240 | 250 | 337 | 377.4333 | -11.998 | 5.5118 | 376.2297 | 36.2092 | 0.038 | 0.11 | 0.483 | 0.76443 | -58.2678 | 66.0714 | 0.75807 | 94.9873 | [8 empty] | SDS-HAA6 | mg/L | 32 | 39 | 35.5 | 19.7183 | --- | 287.9242 | --- | 70.1178 | 285.9983 | 87.5873 | SDS-HAA6 | mg/L | 32.6 | --- | 990.3778 | --- | 72.5589 | 981.7919 | 96.6795 | SDS-HAA6 | mg/L | 19.3 | --- | 214.398 | --- | 83.7542 | 212.6744 | 90.9251 | SDS-HAA6 | mg/L | 17.9 | --- | 162.0429 | --- | 84.9327 | 160.7484 | 88.8646 | TOCb, mg/L | 3.2295 | 3.7063 | 3.2396 | 3.219 | TOCb, mg/L | 1.7305 | 2.4854 | 1.7465 | 1.7139
[44 empty] | 1998-07-10 | 17:00 | 80 | 23.9 | 63 | 64 | 302 | 5.6 | 0.57 |  | 6.17 | 0.23084 | 0.90762 | 47.9465 | 12.7817 | 12.0836 | 367.176 | 242.4803 | 364.8637 | 1.2354 | 62.2646 | 0.19407 | 7.6 | 7.5 | 7.61 | 237 | 250 | 344 | 421.0175 | -22.3888 | 6.6929 | 419.3114 | 43.4788 | 0.04 | 0.11 | 0.5 | 0.81937 | -63.8737 | 64.2857 | 0.81214 | 95.0748 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.061508 | 0.074912 | 0.063993 | 0.06196 | UV254 b, cm-1 | 0.032063 | 0.053284 | 0.035998 | 0.032779
[44 empty] | 1998-07-10 | 17:30 | 80.5 | 23.9 | 63 | 64 | 302 | 5.45 | 0.58 |  | 6.03 | 0.23084 | 0.90381 | 49.0829 | 12.4393 | 11.76 | 366.4375 | 242.0342 | 364.1924 | 1.2328 | 62.2672 | 0.18886 | 7.58 | 7.52 | 7.52 | 235 | 250 | 336 | 432.5345 | -28.7305 | 7.4803 | 430.7521 | 45.4443 | 0.038 | 0.11 | 0.534 | 0.80734 | -51.1882 | 66.0714 | 0.8004 | 95.2524 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 173.8797 | 180 | 169.3318 | 169.4653 | Bromideb, ug/L | 170.3106 | 180 | 163.1106 | 163.322
[44 empty] | 1998-07-10 | 18:00 | 81 | 23.8 | 63 | 64 | 302 | 5.49 | 0.56 |  | 6.05 | 0.23084 | 0.90744 | 48.9174 | 12.5306 | 11.8814 | 367.1036 | 242.463 | 364.8377 | 1.2351 | 62.2649 | 0.19082 | 7.67 | 7.75 | 7.68 | 236 | 252 | 340 | 430.4643 | -26.6071 | 7.0866 | 428.6967 | 44.9494 | 0.039 | 0.11 | 0.552 | 0.82766 | -49.9385 | 65.1786 | 0.82049 | 95.2468 | [47 empty] | Alkb, mg/L CaCO3 | 56.3278 | 65.9819 | 53.5991 | 56.8396 | Alkb, mg/L CaCO3 | 54.1864 | 69.4703 | 49.8664 | 54.9966
[44 empty] | 1998-07-10 | 18:30 | 81.5 | 24 | 63 | 64 | 302 | 5.49 | 0.54 |  | 6.03 | 0.23084 | 0.91045 | 49.0829 | 12.5306 | 11.8113 | 367.6465 | 242.8217 | 365.3774 | 1.2369 | 62.2631 | 0.1897 | 7.65 | 7.63 | 7.59 | 237 | 250 | 337 | 426.8333 | -26.6568 | 6.6929 | 425.1079 | 44.2494 | 0.041 | 0.11 | 0.57 | 0.83383 | -46.2865 | 63.3929 | 0.82663 | 95.0401 | [47 empty] | T-Hdb, mg/L CaCO3 | 177.4151 | 184.438 | 175.1302 | 154.3345 | T-Hdb, mg/L CaCO3 | 165.9941 | 177.1124 | 162.3767 | 129.4539
[44 empty] | 1998-07-10 | 19:00 | 82 | 24 | 63 | 64 | 302 | 5.52 | 0.54 |  | 6.06 | 0.23084 | 0.91089 | 48.835 | 12.5991 | 11.8759 | 367.7377 | 242.8735 | 365.4554 | 1.2372 | 62.2628 | 0.19074 | 7.73 | 7.54 | 7.61 | 236 | 249 | 340 | 438 | -28.8235 | 7.0866 | 436.1539 | 45.8907 | 0.04 | 0.111 | 0.565 | 0.848 | -50.0885 | 64.2857 | 0.84062 | 95.2416 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 124.7594 | 139.991 | 115.1302 | 110.1365 | Ca-Hdb, mg/L CaCO3 | 117.6213 | 141.7351 | 102.3767 | 94.471
[44 empty] | 1998-07-10 | 19:30 | 82.5 | 23.9 | 63 | 64 | 302 | 5.63 | 0.55 |  | 6.18 | 0.23084 | 0.911 | 47.8673 | 12.8502 | 12.1484 | 367.7983 | 242.8829 | 365.4696 | 1.2375 | 62.2625 | 0.19512 | 7.69 | 7.64 | 7.6 | 241 | 250 | 339 | 387.0727 | -14.1807 | 5.1181 | 385.7112 | 37.518 | 0.042 | 0.111 | 0.588 | 0.82855 | -40.9091 | 62.5 | 0.82121 | 94.8856 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-07-11 | 10:30 | 97.5 | 23.9 | 63 | 65 | 302 | 5.15 | 0.51 |  | 5.66 | 0.23084 | 0.90989 | 52.3569 | 11.7546 | 11.1126 | 367.4222 | 242.7679 | 365.2965 | 1.2359 | 62.7641 | 0.17705 | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-07-11 | 11:00 | 98 | 23.9 | 63 | 65 | 302 | 5.15 | 0.51 |  | 5.66 | 0.23084 | 0.90989 | 52.3569 | 11.7546 | 11.1126 | 367.4222 | 242.7679 | 365.2965 | 1.2359 | 62.7641 | 0.17705 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-07-11 | 13:00 | 100 | 23.9 | 63 | 65 | 302 | 5.13 | 0.59 |  | 5.72 | 0.23084 | 0.89685 | 51.7972 | 11.709 | 11.0695 | 365.0786 | 241.2249 | 362.9747 | 1.228 | 62.772 | 0.17634 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-07-11 | 13:15 | 100.25 | 23.9 | 63 | 64 | 302 | 5.17 | 5.31 |  | 10.48 | 0.23084 | 0.49332 | 27.8168 | 11.8002 | 11.1558 | 305.0593 | 201.5581 | 303.2874 | 1.0262 | 62.4738 | 0.17857 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-07-11 | 13:45 | 100.75 | 23.9 | 63 | 64 | 302 | 5.18 | 5.24 |  | 10.42 | 0.23084 | 0.49712 | 27.9827 | 11.8231 | 11.1774 | 305.5338 | 201.8693 | 303.7557 | 1.0278 | 62.4722 | 0.17892 | 8.2 | 7.91 | 7.89 | 215 | 254 | 315 | 292.5534 | 7.1259 | 15.3543 | 291.8883 | 26.3417 | 0.028 | 0.11 | 0.427 | 0.19504 | 54.3236 | 75 | 0.19361 | 85.5376 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-07-11 | 14:15 | 101.25 | 23.9 | 63 | 64 | 302 | 5.18 | 5.32 |  | 10.5 | 0.23084 | 0.49333 | 27.7619 | 11.8231 | 11.1774 | 305.0622 | 201.5577 | 303.2869 | 1.0262 | 62.4738 | 0.17891 | 8.11 | 7.76 | 7.76 | 206 | 255 | 305 | 300.7368 | 1.3978 | 18.8976 | 299.9244 | 31.316 | 0.024 | 0.109 | 0.312 | 0.19768 | 36.6397 | 78.5714 | 0.19619 | 87.7673 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-07-11 | 14:45 | 101.75 | 23.9 | 63 | 64 | 302 | 5.07 | 5.27 |  | 10.34 | 0.23084 | 0.49033 | 28.207 | 11.572 | 10.94 | 304.6743 | 201.3267 | 302.9393 | 1.0248 | 62.4752 | 0.17511 | 8.15 | 7.89 | 7.76 | 203 | 256 | 302 | 303.0645 | -0.35249 | 20.0787 | 302.2246 | 32.8314 | 0.021 | 0.11 | 0.239 | 0.19955 | 16.5077 | 81.25 | 0.19805 | 89.3965 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-07-11 | 15:15 | 102.25 | 23.9 | 63 | 64 | 302 | 5.13 | 5.42 |  | 10.55 | 0.23084 | 0.48626 | 27.6256 | 11.709 | 11.0695 | 304.1783 | 200.9851 | 302.4254 | 1.0232 | 62.4768 | 0.17718 | 8.13 | 7.75 | 7.75 | 204 | 259 | 300 | 301.3247 | -0.44157 | 19.685 | 300.4981 | 32.1127 | 0.02 | 0.109 | 0.216 | 0.19908 | 7.8345 | 82.1429 | 0.19756 | 89.8763 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-07-11 | 15:45 | 102.75 | 23.7 | 63 | 64 | 302 | 5.18 | 5.38 |  | 10.56 | 0.23084 | 0.49053 | 27.5985 | 11.8231 | 11.2436 | 304.7142 | 201.3277 | 302.9409 | 1.025 | 62.475 | 0.17997 | 8.15 | 7.82 | 7.8 | 204 | 259 | 299 | 302.1413 | -1.0506 | 19.685 | 301.2996 | 32.2933 | 0.019 | 0.11 | 0.204 | 0.20154 | 1.2045 | 83.0357 | 0.19998 | 90.4989 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-07-11 | 16:15 | 103.25 | 23.7 | 63 | 64 | 302 | 5.18 | 5.36 |  | 10.54 | 0.23084 | 0.49146 | 27.6528 | 11.8231 | 11.2436 | 304.8297 | 201.404 | 303.0557 | 1.0254 | 62.4746 | 0.17997 | 8.19 | 7.85 | 7.82 | 203 | 259 | 303 | 303.2873 | -0.094823 | 20.0787 | 302.4272 | 32.8764 | 0.019 | 0.11 | 0.198 | 0.20188 | -1.958 | 83.0357 | 0.20031 | 90.5146 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-07-11 | 17:00 | 104 | 23.4 | 63 | 64 | 302 | 5.22 | 5.54 |  | 10.76 | 0.23084 | 0.48513 | 27.0669 | 11.9144 | 11.4314 | 304.0512 | 200.8805 | 302.2679 | 1.0228 | 62.4772 | 0.18297 | 8.08 | 7.78 | 7.77 | 207 | 252 | 301 | 298.2852 | 0.90193 | 18.5039 | 297.4963 | 30.4193 | 0.02 | 0.108 | 0.196 | 0.19869 | -1.3704 | 82.1429 | 0.19714 | 89.855 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-07-11 | 17:30 | 104.5 | 23.4 | 63 | 64 | 302 | 5.2 | 5.83 |  | 11.03 | 0.23084 | 0.47144 | 26.3799 | 11.8687 | 11.3876 | 302.3674 | 199.7727 | 300.6009 | 1.0171 | 62.4829 | 0.18225 | 8.08 | 7.78 | 7.75 | 202 | 256 | 304 | 300.3808 | 1.1905 | 20.4724 | 299.5338 | 32.5619 | 0.019 | 0.106 | 0.193 | 0.19495 | -1.0105 | 83.0357 | 0.19344 | 90.1776
[44 empty] | 1998-07-11 | 18:00 | 105 | 23.4 | 63 | 64 | 302 | 5.38 | 5.7 |  | 11.08 | 0.23084 | 0.48556 | 26.2563 | 12.2796 | 11.7818 | 304.1256 | 200.8929 | 302.2866 | 1.0231 | 62.4769 | 0.18858 | 7.97 | 7.65 | 7.66 | 199 | 250 | 300 | 305.9123 | -1.9708 | 21.6535 | 304.96 | 34.7455 | 0.02 | 0.109 | 0.193 | 0.19884 | -3.0234 | 82.1429 | 0.19724 | 89.8602
[44 empty] | 1998-07-12 | 11:00 | 122 | 23.4 | 63 | 64 | 302 | 5.31 | 5.43 |  | 10.74 | 0.23084 | 0.49441 | 27.1192 | 12.1198 | 11.6285 | 305.2144 | 201.6282 | 303.393 | 1.0268 | 62.4732 | 0.18614
[44 empty] | 1998-07-12 | 11:30 | 122.5 | 23.4 | 63 | 64 | 302 | 5.73 | 5.81 |  | 11.54 | 0.23084 | 0.49653 | 25.1698 | 13.0784 | 12.5482 | 305.5365 | 201.744 | 303.5672 | 1.0281 | 62.4719 | 0.20086 | 7.61 | 7.56 | 7.54 | 201 | 250 | 282 | 306.2702 | -8.6065 | 20.8661 | 305.2716 | 34.157 | 0.019 | 0.11 | 0.193 | 0.20372 | -5.5541 | 83.0357 | 0.20197 | 90.5925
[44 empty] | 1998-07-12 | 12:00 | 123 | 24 | 62 | 64 | 302 | 5.46 | 12.45 |  | 17.91 | 0.23084 | 0.30486 | 15.8621 | 12.4622 | 11.7468 | 283.3239 | 187.135 | 281.5849 | 0.95319 | 62.0468 | 0.18932 | 8.02 | 7.96 | 7.9 | 190 | 250 | 277 | 282.0675 | -1.8294 | 25.1969 | 281.2352 | 32.4409 | 0.016 | 0.11 | 0.155 | 0.1541 | 0.57987 | 85.7143 | 0.15285 | 89.5324
[44 empty] | 1998-07-12 | 12:15 | 123.25 | 24 | 62 | 64 | 302 | 5.33 | 11.66 |  | 16.99 | 0.23084 | 0.31371 | 16.7752 | 12.1654 | 11.4671 | 284.2675 | 187.7862 | 282.5647 | 0.9563 | 62.0437 | 0.18482 | 7.63 | 7.57 | 7.54 | 189 | 249 | 276 | 283.7127 | -2.7945 | 25.5906 | 282.8769 | 33.1865 | 0.016 | 0.11 | 0.152 | 0.15588 | -2.5548 | 85.7143 | 0.15465 | 89.654
[44 empty] | 1998-07-12 | 12:30 | 123.5 | 23.9 | 62 | 64 | 302 | 5.35 | 11.9 |  | 17.25 | 0.23084 | 0.31014 | 16.5072 | 12.2111 | 11.5442 | 283.8842 | 187.5287 | 282.1772 | 0.95502 | 62.045 | 0.18606 | 7.67 | 7.63 | 7.57 | 187 | 251 | 274 | 284.1218 | -3.6941 | 26.378 | 283.2616 | 33.9833 | 0.015 | 0.108 | 0.149 | 0.15561 | -4.4357 | 86.6071 | 0.15436 | 90.2827
[44 empty] | 1998-07-12 | 12:45 | 123.75 | 23.9 | 62 | 64 | 302 | 5.6 | 12.2 |  | 17.8 | 0.23084 | 0.31461 | 15.9663 | 12.7817 | 12.0836 | 284.3844 | 187.8054 | 282.5936 | 0.95684 | 62.0432 | 0.19476 | 7.66 | 7.66 | 7.6 | 185 | 250 | 272 | 285.6721 | -5.0265 | 27.1654 | 284.7387 | 35.0282 | 0.015 | 0.11 | 0.15 | 0.15652 | -4.3497 | 86.6071 | 0.15521 | 90.3358
[44 empty] | 1998-07-12 | 13:00 | 124 | 23.9 | 62 | 64 | 302 | 5.67 | 12.8 |  | 18.47 | 0.23084 | 0.30698 | 15.3508 | 12.9415 | 12.2347 | 283.5677 | 187.251 | 281.7594 | 0.95413 | 62.0459 | 0.19719 | 7.79 | 7.68 | 7.69 | 189 | 250 | 273 | 282.793 | -3.5872 | 25.5906 | 281.9125 | 32.9579 | 0.015 | 0.11 | 0.149 | 0.15497 | -4.0053 | 86.6071 | 0.15365 | 90.2378
[44 empty] | 1998-07-12 | 13:30 | 124.5 | 23.8 | 62 | 64 | 302 | 5.57 | 12.53 |  | 18.1 | 0.23084 | 0.30773 | 15.6851 | 12.7132 | 12.0545 | 283.6411 | 187.3209 | 281.8646 | 0.95432 | 62.0457 | 0.19428 | 7.69 | 7.56 | 7.53 | 188 | 251 | 273 | 283.3392 | -3.7872 | 25.9843 | 282.46 | 33.4419 | 0.014 | 0.11 | 0.148 | 0.15556 | -5.111 | 87.5 | 0.15426 | 90.9243
[44 empty] | 1998-07-12 | 14:00 | 125 | 23.8 | 62 | 64 | 302 | 5.38 | 11.93 |  | 17.31 | 0.23084 | 0.3108 | 16.4466 | 12.2796 | 11.6433 | 283.9573 | 187.5705 | 282.2402 | 0.95528 | 62.0447 | 0.18766 | 7.67 | 7.57 | 7.63 | 187 | 250 | 274 | 284.2146 | -3.728 | 26.378 | 283.3487 | 34.0036 | 0.016 | 0.112 | 0.15 | 0.15529 | -3.5284 | 85.7143 | 0.15405 | 89.6139
[44 empty] | 1998-07-12 | 14:30 | 125.5 | 23.9 | 62 | 64 | 302 | 5.53 | 14.76 |  | 20.29 | 0.23084 | 0.27255 | 13.8842 | 12.6219 | 11.9326 | 279.9037 | 184.8611 | 278.1633 | 0.94172 | 62.0583 | 0.19228 | 7.66 | 7.6 | 7.6 | 191 | 250 | 271 | 277.6037 | -2.4368 | 24.8031 | 276.8107 | 30.9998 | 0.016 | 0.11 | 0.15 | 0.14797 | 1.355 | 85.7143 | 0.14676 | 89.0978
[44 empty] | 1998-07-12 | 15:30 | 126.5 | 23.9 | 62 | 64 | 302 | 5.38 | 12.29 |  | 17.67 | 0.23084 | 0.30447 | 16.0911 | 12.2796 | 11.6089 | 283.2766 | 187.1209 | 281.5636 | 0.95299 | 62.047 | 0.1871 | 7.72 | 7.63 | 7.68 | 191 | 250 | 272 | 281.5785 | -3.5215 | 24.8031 | 280.7717 | 31.9732 | 0.023 | 0.113 | 0.155 | 0.15096 | 2.6064 | 79.4643 | 0.14982 | 84.6483
[44 empty] | 1998-07-12 | 16:30 | 127.5 | 24.1 | 62 | 64 | 302 | 5.33 | 12.23 |  | 17.56 | 0.23084 | 0.30353 | 16.1982 | 12.1654 | 11.4332 | 283.1722 | 187.0626 | 281.476 | 0.95261 | 62.0474 | 0.18427 | 7.77 | 7.76 | 7.68 | 189 | 249 | 267 | 282.3279 | -5.7408 | 25.5906 | 281.5043 | 32.8607 | 0.016 | 0.11 | 0.149 | 0.15384 | -3.247 | 85.7143 | 0.15262 | 89.5166
[44 empty] | 1998-07-12 | 17:30 | 128.5 | 24.1 | 62 | 64 | 302 | 5.32 | 12.13 |  | 17.45 | 0.23084 | 0.30487 | 16.3066 | 12.1426 | 11.4118 | 283.3152 | 187.1592 | 281.6213 | 0.95309 | 62.0469 | 0.18392 | 7.81 | 7.56 | 7.75 | 199 | 250 | 281 | 278.122 | 1.0242 | 21.6535 | 277.4251 | 28.2689 | 0.015 | 0.11 | 0.149 | 0.15454 | -3.7198 | 86.6071 | 0.15331 | 90.2161
[44 empty] | 1998-07-12 | 18:30 | 129.5 | 24.2 | 62 | 64 | 302 | 5.44 | 12.6 |  | 18.04 | 0.23084 | 0.30155 | 15.7406 | 12.4165 | 11.6348 | 282.9683 | 186.9044 | 281.2378 | 0.95199 | 62.048 | 0.18751 | 7.81 | 7.78 | 7.66 | 187 | 245 | 274 | 282.927 | -3.258 | 26.378 | 282.063 | 33.7028 | 0.017 | 0.111 | 0.153 | 0.15302 | -0.010375 | 84.8214 | 0.15179 | 88.8004
[44 empty] | 1998-07-12 | 19:30 | 130.5 | 24.2 | 62 | 64 | 302 | 5.78 | 13.2 |  | 18.98 | 0.23084 | 0.30453 | 14.9115 | 13.1925 | 12.3619 | 283.3122 | 187.0587 | 281.47 | 0.95332 | 62.0467 | 0.19924 | 7.82 | 7.71 | 7.77 | 193 | 248 | 274 | 280.7106 | -2.4491 | 24.0157 | 279.8713 | 31.0397 | 0.017 | 0.11 | 0.149 | 0.1536 | -3.0862 | 84.8214 | 0.15229 | 88.8372
[44 empty] | 1998-07-13 | 8:15 | 143.25 | 24.2 | 62 | 64 | 302 | 5.27 | 11.31 | X | 16.58 | 0.23084 | 0.31785 | 17.2147 | 12.0285 | 11.2712 | 284.7105 | 188.0918 | 283.0245 | 0.95776 | 62.0422 | 0.18167
[44 empty] | 1998-07-13 | 14:20 |  | 24.2 | 60 | 60 | 302 | 4.9 | 3.12 |  | 8.02 | 0.23084 | 0.61097 | 36.6559 | 11.184 | 10.4798 | 320.3704 | 211.7397 | 318.6078 | 1.0775 | 58.9225 | 0.17786
[44 empty] | 1998-07-13 | 15:00 |  | 24.2 | 60 | 60 | 302 | 4.9 | 2.92 |  | 7.82 | 0.23084 | 0.6266 | 37.6189 | 11.184 | 10.4798 | 322.5258 | 213.1642 | 320.7514 | 1.0847 | 58.9153 | 0.17788
[44 empty] | 1998-07-14 | 10:00 |  | 24.2 | 62 | 62 | 302 | 4.21 | 1.88 |  | 6.09 | 0.23084 | 0.6913 | 48.5895 | 9.6091 | 9.0041 | 331.6121 | 219.3419 | 330.047 | 1.1149 | 60.8851 | 0.14789
[44 empty] | 1998-07-14 | 10:30 |  | 24.2 | 62 | 62 | 302 | 4.27 | 1.82 |  | 6.09 | 0.23084 | 0.70115 | 48.5895 | 9.746 | 9.1324 | 333.0763 | 220.2953 | 331.4817 | 1.1198 | 60.8802 | 0.15001
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: Alison Gusses: NTR7450 membrane was used during quarters 1 and 2; NF200B membrane was used during quarters 3 and 4.
Note on R5: Gary Puetz: Consultant confirmed potential foulants were not measured during the study because they were not required under the ICR.
Note on X26: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on CY31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DL16: Gary Puetz: Consultant did not verify the parameter or explain why the mass balance for 90% recovery was high. No changes were made.
Note on DL20: Gary Puetz: Consultant did not verify the parameter or explain why the mass balance for 90% recovery was high. No changes were made.
Note on DL31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DN40: Gary Puetz: The contractor verfied the reported TCAA permeate concentration.
Note on DQ10: Alison Gusses: High mass balance closure errors for 90% recovery run may indicate membrane was not operated at steady-state. Consultant did not verify or explain the water quality parameters with high mass balance closure errors.
Note on DV31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on EF31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.

## NTR7450. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.71723 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.32 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 0.2 mg/L | plant | Sampling date | MM/DD/YY | 1998-09-15 | 1998-10-05 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 6.8 | [10 empty] | Feed flow rate during sample collection (mL/min) | 4.59 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.32 | [7 empty] | Feed flow rate during sample collection (mL/min) | 15.61 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI | Coagulation | 156 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 8:00 | 8:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 342.5 | 342.5 | 342.5 | 342.5 | SDS-THM4F, ug/L | 342.5 | 342.5 | 342.5 | 342.5 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.59 mg/L | plant | Operation time | hh.hh | 0 | 143 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 66.3 | 77 | 47.4 | 37.9 | SDS-THM4p, ug/L | 66.3 | 77 | 47.4 | 37.9 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 7.84 | 7.86 | 7.85 | 0.25478 | 1998-09-14 | 8:30 | 0 | 24 | [5 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-15 | 8:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 214.8 | 214.8 | 214.8 | 214.8 | SDS-HAA5F, ug/L | 214.8 | 214.8 | 214.8 | 214.8 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.2599 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-09-14 | 9:00 | 0.5 | 24 | 46.5 | 48 | 272 | 2.08 | 2.16 | 4.24 | 0.20821 | 0.49057 | 63.1509 | 4.7475 | 4.475 | 0 | 0 | 0 | 0 | 47.25 | 0.094708 | 1998-09-15 | 8:40 | 0.66667 | 24 | 42 | 44 | 263 | 5.46 | 2.77 |  | 8.23 | 0.20132 | 0.66343 | 30.9563 | 12.4622 | 11.7468 | 473.7605 | 131.9585 | 466.6645 | 3.3825 | 39.6175 | 0.29651 |  |  |  | 95 |  | 234 | 546.6101 | -133.5941 | 61.5385 | 541.9223 | 82.4698 | 0.01 | 0.215 | 0.207 | 0.60125 | -190.4602 | 95.2153 | 0.59512 | 98.3197 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 12.95 | 19 | 8.1 | 6.1 | SDS-HAA5p, ug/L | 12.95 | 19 | 8.1 | 6.1 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | highly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 144 | 146 | 145 | 1.3793 | 1998-09-14 | 10:00 | 1.5 | 24 | 76.5 | 77.5 | 272 | 3.96 | 1.15 | 5.11 | 0.20821 | 0.77495 | 52.229 | 9.0385 | 8.5196 | 0 | 0 | 0 | 0 | 77 | 0.11064 | 1998-09-15 | 9:00 | 1 | 24 | 42.5 | 44 | 263 | 5.3 | 2.51 |  | 7.81 | 0.20132 | 0.67862 | 32.6748 | 12.097 | 11.4026 | 483.853 | 134.83 | 476.8194 | 3.4551 | 39.7949 | 0.28653 |  |  |  | 130 | 268 | 294 | 494.0518 | -68.0448 | 47.3684 | 490.3836 | 73.4901 | 0.013 |  | 0.302 | 0.62286 | -106.2465 | 93.7799 | 0.61672 | 97.8921 | [8 empty] | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-17 | --- | --- | 1998-09-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-18 | 1998-09-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-19 | 1998-09-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-09-20 | 1998-09-20 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1580 | 1580 | 1580 | 1580 | SDS-TOXF, ug Cl- /L | 1580 | 1580 | 1580 | 1580 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 249 | 245 | 247 | 1.6194 | 1998-09-14 | 10:45 | 2.25 | 24 | 79 | 80 | 263 | 4.29 | 0.46 | 4.75 | 0.20132 | 0.90316 | 54.3684 | 9.7917 | 9.2296 | 0 | 0 | 0 | 0 | 79.5 | 0.1161 | 1998-09-15 | 9:20 | 1.3333 | 24 | 42.5 | 44 | 263 | 5.25 | 2.41 |  | 7.66 | 0.20132 | 0.68538 | 33.3342 | 11.9828 | 11.295 | 488.4946 | 136.1425 | 481.461 | 3.4884 | 39.7616 | 0.28407 |  |  |  | 137 |  | 341 | 486.6266 | -42.7057 | 44.5344 | 483.1369 | 71.6437 | 0.017 |  | 0.371 | 0.62726 | -69.072 | 91.866 | 0.62117 | 97.2632 | [8 empty] | Sampling time | hh:mm | 9:30 | 9:00 | --- | --- | 9:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 18:00 | 18:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:20 | 12:20 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 107.5 | 145 | 65 | 54 | SDS-TOXp, ug Cl- /L | 107.5 | 145 | 65 | 54 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 202 | 196 | 199 | 3.0151 | 1998-09-14 | 11:30 | 3 | 24 | 79.5 | 80 | 263 | 4.12 | 0.52 | 4.64 | 0.20132 | 0.88793 | 55.681 | 9.4037 | 8.8639 | 0 | 0 | 0 | 0 | 79.75 | 0.11115 | 1998-09-15 | 9:40 | 1.6667 | 24 | 42.5 | 44 | 263 | 5.15 | 2.22 |  | 7.37 | 0.20132 | 0.69878 | 34.6852 | 11.7546 | 11.0798 | 497.9598 | 138.8193 | 490.9272 | 3.5562 | 39.6938 | 0.27913 |  |  |  | 138 |  | 342 | 499.8604 | -46.158 | 44.1296 | 496.3174 | 72.1952 | 0.021 |  | 0.422 | 0.64513 | -52.8735 | 89.9522 | 0.63902 | 96.7137 | [8 empty] | Operation time | hh.hh | 25.5 | 49 | --- | --- | 25.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 82 | 82 | --- | --- | --- | --- | --- | Operation time | hh.hh | 103 | 103 | --- | --- | --- | --- | --- | Cumulative time | hr | 124.33 | 124.33 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.16 | 11.16 | 11.16 | 11.16 | SDS-CDF, mg/L | 11.16 | 11.16 | 11.16 | 11.16 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 164 | 164 | 164 | 0 | 1998-09-14 | 13:10 | 4.6667 | 24 | 40.5 | 41.5 | 263 | 5.3 | 3.3 | 8.6 | 0.20132 | 0.61628 | 29.5814 | 12.097 | 11.4026 | 0 | 0 | 0 | 0 | 41 | 0.27811 | 1998-09-15 | 10:00 | 2 | 24 | 42.5 | 43.5 | 263 | 5.15 | 2.23 |  | 7.38 | 0.20132 | 0.69783 | 34.6369 | 11.7546 | 11.0798 | 497.2752 | 138.6284 | 490.2523 | 3.5514 | 39.4486 | 0.28087 |  |  |  | 142 |  | 368 | 489.4888 | -33.0133 | 42.5101 | 486.0866 | 70.7871 | 0.021 |  | 0.465 | 0.64317 | -38.3162 | 89.9522 | 0.63708 | 96.7037 | [8 empty] | pH | --- | 7.95 | 7.8 | 7.875 | 1.9048 | 7.54 | --- | --- | --- | --- | --- | pH | --- | 7.79 | 7.59 | --- | --- | --- | --- | --- | pH | --- | 8.01 | 7.75 | --- | --- | --- | --- | --- | pH | --- | 7.92 | 7.83 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.295 | 2.48 | 1.6 | 1.37 | SDS-CDp, mg/L | 2.295 | 2.48 | 1.6 | 1.37 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 15 | 6.5 | 64.2145 | 283.3154 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.247 | 0.165 | 0.206 | 39.8058 | 1998-09-14 | 14:00 | 5.5 | 24 | 40.5 | 41.5 | 263 | 5.33 | 3.2 | 8.53 | 0.20132 | 0.62485 | 29.8324 | 12.1654 | 11.4671 | 0 | 0 | 0 | 0 | 41 | 0.27969 | 1998-09-15 | 11:00 | 3 | 24 | 42.5 | 44 | 263 | 5.01 | 2.46 |  | 7.47 | 0.20132 | 0.67068 | 34.2075 | 11.4351 | 10.7786 | 478.3478 | 133.4041 | 471.7768 | 3.4166 | 39.8334 | 0.27059 |  |  |  | 147 |  | 397 | 450.6585 | -13.516 | 40.4858 | 447.7663 | 67.1704 | 0.018 |  | 0.523 | 0.59799 | -14.338 | 91.3876 | 0.59246 | 96.9618 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 8.3 | 8.3 | 8.3 | 8.3 | TOCF, mg/L | 8.3 | 8.3 | 8.3 | 8.3 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 15 | 16.5 | 74.2145 | 283.3154 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-09-14 | 14:30 | 6 | 24 | 40.5 | 41.5 | 263 | 5.4 | 3.09 | 8.49 | 0.20132 | 0.63604 | 29.9776 | 12.3252 | 11.6177 | 0 | 0 | 0 | 0 | 41 | 0.28336 | 1998-09-15 | 12:00 | 4 | 24 | 42.5 | 44 | 263 | 4.98 | 2.32 |  | 7.3 | 0.20132 | 0.68219 | 35.0274 | 11.3666 | 10.7141 | 486.1465 | 135.5904 | 479.5086 | 3.4724 | 39.7776 | 0.26935 |  |  |  | 142 |  | 409 | 472.3879 | -15.4983 | 42.5101 | 469.2599 | 69.7396 | 0.019 |  | 0.563 | 0.61684 | -9.5639 | 90.9091 | 0.61118 | 96.8913 | [8 empty] | Alkalinity | mg/L as CaCO3 | 122 | 122 | 122 | 0 | 190 | 201.3103 | -5.9528 | 15.8621 | 200.5824 | 39.1771 | Alkalinity | mg/L as CaCO3 | 140 | 216 | 190 | 12.037 | 3.4483 | 189.6073 | 26.1632 | Alkalinity | mg/L as CaCO3 | 118 | 180 | 173.102 | 3.8322 | 18.6207 | 172.6041 | 31.6355 | Alkalinity | mg/L as CaCO3 | 110 | 168 | 161.4706 | 3.8866 | 24.1379 | 160.9818 | 31.6693 | TOCp, mg/L | 0.9 | 1.6 | 0.5 | 0.7 | TOCp, mg/L | 0.9 | 1.6 | 0.5 | 0.7 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 62.2145 | 283.3154 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 8.4 | 8.2 | 8.3 | 2.4096 | 1998-09-14 | 15:45 | 7.25 | 24 | 42.5 | 43.5 | 263 | 5.83 | 1.86 | 7.69 | 0.20132 | 0.75813 | 33.2003 | 13.3067 | 12.5428 | 0 | 0 | 0 | 0 | 43 | 0.29169 | 1998-09-15 | 14:00 | 6 | 24 | 42.5 | 43.5 | 263 | 4.96 | 2.12 |  | 7.08 | 0.20132 | 0.70056 | 36.1469 | 11.3209 | 10.6711 | 499.1517 | 139.2255 | 492.3638 | 3.5653 | 39.4347 | 0.2706 | [11 empty] | 0.02 | 0.208 | 0.608 | 0.65119 | -7.1034 | 90.4306 | 0.64524 | 96.9004 | [8 empty] | Total dissolved solids | mg/L | 147 | 146 | 146.5 | 0.68259 | 443 | 493.0517 | -11.2984 | 40.6883 | 489.8708 | 70.0942 | Total dissolved solids | mg/L | 165 | 694 | 985 | -41.9308 | 33.1984 | 978.56 | 83.1385 | Total dissolved solids | mg/L | 132 | 351 | 366.6939 | -4.4712 | 46.5587 | 364.5731 | 63.7933 | Total dissolved solids | mg/L | 125 | 291 | 304.4118 | -4.6089 | 49.3927 | 302.708 | 58.7061 | UV254 F, cm-1 | 0.209 | 0.209 | 0.209 | 0.209 | UV254 F, cm-1 | 0.209 | 0.209 | 0.209 | 0.209 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 3.6429 | 61.3573 | 283.3154 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.207 | 0.211 | 0.209 | 1.9139 | 1998-09-14 | 16:35 | 8.0833 | 24 | 42.5 | 43 | 263 | 5.71 | 1.49 | 7.2 | 0.20132 | 0.79306 | 35.5278 | 13.0328 | 12.2846 | 0 | 0 | 0 | 0 | 42.75 | 0.28736 | 1998-09-15 | 15:15 | 7.25 | 24 | 42.5 | 43.5 | 263 | 4.92 | 2.05 |  | 6.97 | 0.20132 | 0.70588 | 36.7331 | 11.2296 | 10.585 | 503.027 | 140.3221 | 496.2418 | 3.5931 | 39.4069 | 0.26861 | [27 empty] | Total hardness | mg/L as CaCO3 | 100 | 96 | 98 | 4.0816 | 436 | 446.2759 | -2.3568 | 50.7538 | 443.0791 | 77.8821 | Total hardness | mg/L as CaCO3 | 114 | 846 | 964 | -13.948 | 42.7136 | 957.3244 | 88.0918 | Total hardness | mg/L as CaCO3 | 92 | 328 | 310.3673 | 5.3758 | 53.7688 | 308.3941 | 70.168 | Total hardness | mg/L as CaCO3 | 80 | 248 | 255 | -2.8226 | 59.799 | 253.3381 | 68.4216 | UV254 p, cm-1 | 0.0185 | 0.032 | 0.012 | 0.009 | UV254 p, cm-1 | 0.0185 | 0.032 | 0.012 | 0.009 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.4643 | 2.5732 | 2.5187 | 4.323 | 1998-09-14 | 17:30 | 9 | 24 | 42 | 43.5 | 263 | 5.67 | 1.83 | 7.5 | 0.20132 | 0.756 | 34.0667 | 12.9415 | 12.1986 | 0 | 0 | 0 | 0 | 42.75 | 0.28535 | 1998-09-15 | 16:30 | 8.5 | 24 | 42.5 | 43.5 | 263 | 4.89 | 2.29 |  | 7.18 | 0.20132 | 0.68106 | 35.6295 | 11.1612 | 10.5205 | 485.3202 | 135.394 | 478.814 | 3.4667 | 39.5333 | 0.26612 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 84 | 82 | 83 | 2.4096 | 366 | 362.3103 | 1.0081 | 49.3902 | 359.7466 | 76.9282 | Calcium hardness | mg/L as CaCO3 | 94 | 700 | 794 | -13.4286 | 42.6829 | 788.5025 | 88.0787 | Calcium hardness | mg/L as CaCO3 | 72 | 272 | 259.7551 | 4.5018 | 56.0976 | 258.0585 | 72.0993 | Calcium hardness | mg/L as CaCO3 | 66 | 208 | 210.1176 | -1.0181 | 59.7561 | 208.749 | 68.3831 | BromideF, ug/L | 150 | 150 | 150 | 150 | BromideF, ug/L | 150 | 150 | 150 | 150 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 150 | 150 | 150 | 0 | 1998-09-15 | 6:35 | 22.0833 | 24 | 42 | 43.5 | 263 | 5.39 | 0.88 | 6.27 | 0.20132 | 0.85965 | 40.9458 | 12.3024 | 11.5962 | 0 | 0 | 0 | 0 | 42.75 | 0.27126 | 1998-09-16 | 8:30 | 24.5 | 24 | 42.5 | 43.5 | 263 | 4.91 | 1.68 |  | 6.59 | 0.20132 | 0.74507 | 38.909 | 11.2068 | 10.5635 | 533.7329 | 148.8918 | 526.5482 | 3.8125 | 39.1875 | 0.26956 |  |  |  | 130 | 246 | 456 | 588.9464 | -29.1549 | 47.3684 | 584.6623 | 77.7649 | 0.019 | 0.207 | 0.716 | 0.7643 | -6.7455 | 90.9091 | 0.75734 | 97.4912 | [8 empty] | Turbidity | ntu | 0.105 | 0.119 | 0.112 | 12.5 | 0.43 | 0.43614 | -1.4274 | 45.6311 | 0.43316 | 74.1437 | Turbidity | ntu | 0.098 | 0.429 | 1.178 | -174.5921 | 52.4272 | 1.1695 | 91.6205 | Turbidity | ntu | 0.095 | 0.393 | 0.32153 | 18.1856 | 53.8835 | 0.31948 | 70.2645 | Turbidity | ntu | 0.096 | 0.226 | 0.25776 | -14.0552 | 53.3981 | 0.25623 | 62.5334 | Bromidep, ug/L | 195 | 160 | 160 | 160 | Bromidep, ug/L | 195 | 160 | 160 | 160 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 12 | 12 | 12 | 0 | 1998-09-15 | 7:00 | 22.5 | 24 | 50 | 51.5 | 263 | 7.44 | 1.2 | 8.64 | 0.20132 | 0.86111 | 29.4398 | 16.9814 | 16.0066 | 0 | 0 | 0 | 0 | 50.75 | 0.3154 | 1998-09-16 | 9:30 | 25.5 | 24 | 42.5 | 43.5 | 263 | 4.91 | 2.17 |  | 7.08 | 0.20132 | 0.6935 | 36.1469 | 11.2068 | 10.5635 | 494.0406 | 137.8191 | 487.3903 | 3.529 | 39.471 | 0.26763 |  |  |  | 142 |  | 431 | 484.5806 | -12.4317 | 42.5101 | 481.3828 | 70.5016 | 0.018 |  | 0.669 | 0.64117 | 4.1599 | 91.3876 | 0.63535 | 97.1669 | [8 empty] | Ammonia | mg NH3-N / L | 0.09 | 0.11 | 0.1 | 20 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145 | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.5467 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.86 | 0.82 | 0.84 | 4.7619 | 1998-09-15 | 7:20 | 22.8333 | 24 | 60 | 61 | 272 | 8.9 | 1.73 | 10.63 | 0.20821 | 0.83725 | 24.588 | 20.3138 | 19.1477 | 0 | 0 | 0 | 0 | 60.5 | 0.31649 | 1998-09-16 | 10:30 | 26.5 | 24 | 42.5 | 43.5 | 263 | 4.86 | 2.03 |  | 6.89 | 0.20132 | 0.70537 | 37.1713 | 11.0927 | 10.4559 | 502.6152 | 140.2307 | 495.9187 | 3.5904 | 39.4096 | 0.26531 |  |  |  | 140 |  | 422 | 503.1675 | -19.234 | 43.3198 | 499.812 | 71.9895 | 0.019 |  | 0.656 | 0.66388 | -1.2007 | 90.9091 | 0.65792 | 97.1121 | [8 empty] | Total organic carbon | mg/L | 0.8 | 1 | 0.9 | 22.2222 | 26.1 | 26.4172 | -1.2155 | 89.1566 | 26.183 | 96.5627 | Total organic carbon | mg/L | 1.6 | 60.2 | 68.6 | -13.9535 | 80.7229 | 68.0738 | 97.6496 | Total organic carbon | mg/L | 0.5 | 86.9 | 16.4184 | 81.1066 | 93.9759 | 16.2745 | 96.9277 | Total organic carbon | mg/L | 0.7 | 12.2 | 11.8765 | 2.6519 | 91.5663 | 11.7703 | 94.0528 | Alkp, mg/L CaCO3 | 122 | 140 | 118 | 110 | Alkp, mg/L CaCO3 | 122 | 140 | 118 | 110
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.00233 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.14 | 11.18 | 11.16 | 0.35842 | 1998-09-15 | 7:40 | 23.1667 | 24 | 35 | 36 | 263 | 5.1 | 0.79 | 5.89 | 0.20132 | 0.86587 | 43.652 | 11.6405 | 10.9723 | 0 | 0 | 0 | 0 | 35.5 | 0.30908 | 1998-09-16 | 11:30 | 27.5 | 24 | 42.5 | 43.5 | 263 | 4.89 | 1.96 |  | 6.85 | 0.20132 | 0.71387 | 37.3942 | 11.1612 | 10.5205 | 508.9787 | 141.9942 | 502.1553 | 3.6357 | 39.3643 | 0.26726 |  |  |  | 143 |  | 424 | 506.4694 | -19.4503 | 42.1053 | 503.0904 | 71.5757 | 0.019 |  | 0.657 | 0.68303 | -3.962 | 90.9091 | 0.67686 | 97.1929 | [8 empty] | UV254 | cm-1 | 0.019 | 0.018 | 0.0185 | 5.4054 | 0.672 | 0.6754 | -0.50544 | 91.1483 | 0.66937 | 97.2362 | UV254 | cm-1 | 0.032 | 1.522 | 1.802 | -18.3968 | 84.689 | 1.7881 | 98.2104 | UV254 | cm-1 | 0.012 | 0.434 | 0.41404 | 4.5989 | 94.2584 | 0.41041 | 97.0761 | UV254 | cm-1 | 0.009 | 0.297 | 0.30312 | -2.0598 | 95.6938 | 0.30032 | 97.0032 | T-HdF, mg/L CaCO3 | 199 | 199 | 199 | 199 | T-HdF, mg/L CaCO3 | 199 | 199 | 199 | 199
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | 1998-09-15 | 8:00 | 23.5 | 24 | 42 | 43 | 263 | 5.93 | 1.45 | 7.38 | 0.20132 | 0.80352 | 34.6369 | 13.5349 | 12.7579 | 0 | 0 | 0 | 0 | 42.5 | 0.30019 | 1998-09-16 | 13:30 | 29.5 | 24 | 42.5 | 43.5 | 263 | 4.8 | 1.81 |  | 6.61 | 0.20132 | 0.72617 | 38.7882 | 10.9557 | 10.3268 | 518.401 | 144.6592 | 511.5799 | 3.7033 | 39.2967 | 0.26279 |  |  |  | 132 | 245 | 443 | 551.9724 | -24.5987 | 46.5587 | 548.1399 | 75.9186 | 0.018 | 0.205 | 0.677 | 0.71552 | -5.6897 | 91.3876 | 0.70915 | 97.4618 | [8 empty] | SUVA | L/(mg*m) | 2.375 | 1.8 | 2.0875 | 27.5449 | 2.5747 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 2.5282 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.4 | 0.49942 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.2857 | 2.4344 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 98 | 114 | 92 | 80 | T-Hdp, mg/L CaCO3 | 98 | 114 | 92 | 80
Process Train Name | Enhanced Coagulation/Lime Softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 7.85 | 7.88 | 7.865 | 0.38144 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-16 | 14:30 | 30.5 | 24 | 42.5 | 43.5 | 263 | 4.61 | 2 |  | 6.61 | 0.20132 | 0.69743 | 38.7882 | 10.5221 | 9.9181 | 496.6905 | 138.6744 | 490.415 | 3.5488 | 39.4512 | 0.2514 | 6 |  | 6 | 140 |  | 423 | 493.635 | -16.6986 | 43.3198 | 490.5357 | 71.4598 | 0.018 |  | 0.646 | 0.64926 | -0.50387 | 91.3876 | 0.64372 | 97.2038 | [8 empty] | Bromide | mg/L | 160 | 230 | 195 | 35.8974 | --- | 39.8276 | --- | -30 | 41.2519 | -372.7059 | Bromide | mg/L | 160 | --- | 60 | --- | -6.6667 | 60.7854 | -163.2213 | Bromide | mg/L | 160 | --- | 139.5918 | --- | -6.6667 | 139.7763 | -14.4687 | Bromide | mg/L | 160 | --- | 145.2941 | --- | -6.6667 | 145.4338 | -10.0157 | Ca-HdF, mg/L CaCO3 | 164 | 164 | 164 | 164 | Ca-HdF, mg/L CaCO3 | 164 | 164 | 164 | 164
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 72 | 72 | 72 | 0 | Changed NF200 membranes at 11:30 am on 9/14/98 | [8 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-16 | 15:30 | 31.5 | 24 | 42.5 | 43.5 | 263 | 4.84 | 1.93 |  | 6.77 | 0.20132 | 0.71492 | 37.8479 | 11.047 | 10.4129 | 509.7448 | 142.2278 | 502.9814 | 3.6414 | 39.3586 | 0.26456 | 7.18 | 6.69 | 6.93 | 140 | 248 | 429 | 515.3316 | -20.1239 | 43.3198 | 511.878 | 72.6497 | [16 empty] | SDS-Cl2 dose | mg/L | 3.5 | 3.5 | 3.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 83 | 94 | 72 | 66 | Ca-Hdp, mg/L CaCO3 | 83 | 94 | 72 | 66
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 1060 | 2100 | 1580 | 65.8228 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-16 | 16:30 | 32.5 | 24 | 42.5 | 43.5 | 263 | 4.8 | 2.12 |  | 6.92 | 0.20132 | 0.69364 | 37.0058 | 10.9557 | 10.3268 | 494.0808 | 137.8727 | 487.5796 | 3.5296 | 39.4704 | 0.26163 |  |  |  | 141 |  | 420 | 487 | -15.9524 | 42.915 | 483.8426 | 70.8583 | [16 empty] | SDS-Free Cl2 residual | mg/L | 1.16 | 1.25 | 1.205 | 7.4689 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.02 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.4 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.63 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 19 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 220 | 290 | 255 | 27.451 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-16 | 17:20 | 33.3333 | 24 | 42.5 | 43.5 | 263 | 4.8 | 2.04 |  | 6.84 | 0.20132 | 0.70175 | 37.4503 | 10.9557 | 10.3268 | 499.9298 | 139.5048 | 493.3517 | 3.5714 | 39.4286 | 0.26191 | [27 empty] | SDS-Cl2 demand | mg/L | 2.34 | 2.25 | 2.295 | 3.9216 | --- | 32.864 | --- | 79.4355 | 32.5834 | 92.9565 | SDS-Cl2 demand | mg/L | 2.48 | --- | 89.28 | --- | 77.7778 | 88.5983 | 97.2008 | SDS-Cl2 demand | mg/L | 1.6 | --- | 21.1102 | --- | 85.6631 | 20.9339 | 92.3569 | SDS-Cl2 demand | mg/L | 1.37 | --- | 15.7671 | --- | 87.724 | 15.6303 | 91.235 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | minus 10%, plus 25% | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 64 | 79 | 71.5 | 20.979 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 8:15 | 48.25 | 24 | 42.5 | 43.5 | 263 | 4.92 | 1.68 |  | 6.6 | 0.20132 | 0.74545 | 38.8485 | 11.2296 | 10.585 | 534.061 | 148.9792 | 526.8572 | 3.8148 | 39.1852 | 0.27013 | [27 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 97.9363 | 101.8832 | 91.6638 | 88.805 | Qp/QT (THM4), % | 110.9703 | 115.4426 | 103.8631 | 100.6238
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | >99% 2000 ppm MgSO4 @ 67 psi | [13 empty] | SDS-DBCM | mg/L | 14 | 18 | 16 | 25 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 9:00 | 49 | 24 | 42.5 | 43.5 | 263 | 4.89 | 2.05 |  | 6.94 | 0.20132 | 0.70461 | 36.8963 | 11.1612 | 10.5205 | 502.0728 | 140.0676 | 495.342 | 3.5864 | 39.4136 | 0.26692 | 7.73 | 7.67 | 7.39 | 138 | 249 | 440 | 507.0049 | -15.2284 | 44.1296 | 503.5744 | 72.5959 | 0.017 | 0.203 | 0.691 | 0.66699 | 3.4746 | 91.866 | 0.66095 | 97.4279 | [8 empty] | SDS-Chlorination pH | --- | 7.96 | 7.97 | 7.965 | 0.12555 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.93 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.98 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.03 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | NA | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NDP or< 50% 500 ppm CaCl2 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 10:00 | 50 | 24 | 42.5 | 43.5 | 263 | 4.78 | 1.92 |  | 6.7 | 0.20132 | 0.71343 | 38.2537 | 10.9101 | 10.2838 | 508.5853 | 141.9281 | 501.9214 | 3.6333 | 39.3667 | 0.26123 |  |  |  | 149 |  | 433 | 490.9792 | -13.3901 | 39.6761 | 487.8714 | 69.4592 | 0.021 |  | 0.666 | 0.67704 | -1.6579 | 89.9522 | 0.67108 | 96.8707 | [8 empty] | SDS-Incubation time | hours | 72 | 72 | 72 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 72 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 72 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 72 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 17.1156 | NA | 25.3308 | 29.464 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | unknown | [13 empty] | SDS-THM4 | mg/L | 298 | 387 | 342.5 | 25.9854 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 11:00 | 51 | 24 | 42.5 | 43.5 | 263 | 4.73 | 1.84 |  | 6.57 | 0.20132 | 0.71994 | 39.0304 | 10.796 | 10.1762 | 513.5153 | 143.3239 | 506.8575 | 3.6686 | 39.3314 | 0.25873 |  |  |  | 148 |  | 448 | 501.4946 | -11.9408 | 40.081 | 498.3158 | 70.3 | 0.02 |  | 0.667 | 0.69485 | -4.1759 | 90.4306 | 0.68878 | 97.0963 | [8 empty] | SDS-TOX | mg Cl- /L | 100 | 115 | 107.5 | 13.9535 | --- | 5185.0862 | --- | 93.1962 | 5138.4805 | 97.9079 | SDS-TOX | mg Cl- /L | 145 | --- | 14495 | --- | 90.8228 | 14382.3007 | 98.9918 | SDS-TOX | mg Cl- /L | 65 | --- | 3156.8367 | --- | 95.8861 | 3128.8973 | 97.9226 | SDS-TOX | mg Cl- /L | 54 | --- | 2298.1176 | --- | 96.5823 | 2276.8062 | 97.6283 | SDS-TOXb, ug Cl- /L | 137.8883 | NA | 191.2928 | 224.8359 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 15 | [13 empty] | SDS-MCAA* | mg/L | 11 | 8.9 | 9.95 | 21.1055 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 12:00 | 52 | 24 | 42.5 | 43.5 | 263 | 4.72 | 1.75 |  | 6.47 | 0.20132 | 0.72952 | 39.6491 | 10.7731 | 10.1547 | 520.9909 | 145.4144 | 514.2505 | 3.7221 | 39.2779 | 0.25854 |  |  |  | 145 |  | 455 | 522.1086 | -14.7491 | 41.2955 | 518.7246 | 72.0468 | 0.019 |  | 0.678 | 0.72146 | -6.4096 | 90.9091 | 0.71515 | 97.3432 | [8 empty] | SDS-CHCl3 | mg/L | 7.4 | 6.2 | 6.8 | 17.6471 | --- | 862.6621 | --- | 97.3333 | 854.8064 | 99.2045 | SDS-CHCl3 | mg/L | 12 | --- | 2442 | --- | 95.2941 | 2422.9157 | 99.5047 | SDS-CHCl3 | mg/L | 3.4 | --- | 516.8694 | --- | 98.6667 | 512.2294 | 99.3362 | SDS-CHCl3 | mg/L | 2.8 | --- | 373.6824 | --- | 98.902 | 370.1602 | 99.2436 | SDS-CDb, mg/L | 2.4779 | NA | 2.3969 | 2.466 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7.0 + 0.3 | [13 empty] | SDS-DCAA* | mg/L | 88 | 81 | 84.5 | 8.284 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 13:00 | 53 | 24 | 42.5 | 43.5 | 263 | 4.72 | 1.98 |  | 6.7 | 0.20132 | 0.70448 | 38.2537 | 10.7731 | 10.1547 | 501.8796 | 140.0802 | 495.3864 | 3.5855 | 39.4145 | 0.25764 | 7.7 | 7.51 | 7.45 | 143 | 248 | 430 | 494.9192 | -15.0975 | 42.1053 | 491.7613 | 70.9209 | 0.02 | 0.212 | 0.674 | 0.65955 | 2.1446 | 90.4306 | 0.65381 | 96.941 | [8 empty] | SDS-BDCM | mg/L | 18 | 15 | 16.5 | 18.1818 | --- | 206.1552 | --- | 76.9231 | 204.4144 | 91.9282 | SDS-BDCM | mg/L | 23 | --- | 508 | --- | 67.8322 | 504.191 | 95.4382 | SDS-BDCM | mg/L | 9 | --- | 136.551 | --- | 87.4126 | 135.3984 | 93.3529 | SDS-BDCM | mg/L | 7.1 | --- | 101.8059 | --- | 90.0699 | 100.9065 | 92.9638 | TOCb, mg/L | 1.0527 | NA | 1.1502 | 1.5508 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | < 105 psi | [13 empty] | SDS-TCAA* | mg/L | 120 | 110 | 115 | 8.6957 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 15:00 | 55 | 24 | 42.5 | 43.5 | 263 | 4.68 | 1.63 |  | 6.31 | 0.20132 | 0.74168 | 40.6799 | 10.6818 | 10.0687 | 530.7783 | 148.1627 | 523.9698 | 3.7921 | 39.2079 | 0.2568 |  |  |  | 130 |  | 429 | 582.9264 | -35.8803 | 47.3684 | 578.8965 | 77.5435 | [16 empty] | SDS-DBCM | mg/L | 29 | 27 | 28 | 7.1429 | --- | -13.3793 | --- | -75 | -12.9995 | 315.3929 | SDS-DBCM | mg/L | 32 | --- | -128 | --- | -100 | -126.7434 | 125.2479 | SDS-DBCM | mg/L | 21 | --- | 10.7959 | --- | -31.25 | 10.8881 | -92.8706 | SDS-DBCM | mg/L | 17 | --- | 15.5294 | --- | -6.25 | 15.5434 | -9.3713 | UV254 b, cm-1 | 0.022431 | NA | 0.028422 | 0.03139 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 3-10 (2-11 cleaning) | [13 empty] | SDS-MBAA* | mg/L | 2.1 | 1.9 | 2 | 10 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 16:00 | 56 | 24 | 42.5 | 43.5 | 263 | 4.69 | 1.89 |  | 6.58 | 0.20132 | 0.71277 | 38.9696 | 10.7047 | 10.0902 | 508.0301 | 141.8088 | 501.4994 | 3.6296 | 39.3704 | 0.25629 |  |  |  | 140 | 249 | 430 | 512.5185 | -19.1904 | 43.3198 | 509.197 | 72.5057 | [16 empty] | SDS-CHBr3 | mg/L | 16 | 14 | 15 | 13.3333 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 10 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 14 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 11 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 194.0713 | NA | 159.1664 | 158.8805 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 3 | [13 empty] | SDS-DBAA* | mg/L | 3.2 | 3.5 | 3.35 | 8.9552 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-17 | 17:00 | 57 | 24 | 42.5 | 43.5 | 263 | 4.67 | 1.82 |  | 6.49 | 0.20132 | 0.71957 | 39.5239 | 10.659 | 10.0472 | 513.1944 | 143.2583 | 506.6256 | 3.6665 | 39.3335 | 0.25544 |  |  |  | 141 |  | 423 | 518.989 | -22.6924 | 42.915 | 515.6331 | 72.655 | [16 empty] | SDS-THM4 | mg/L | 70.4 | 62.2 | 66.3 | 12.368 | --- | 1018.7138 | --- | 80.6423 | 1009.9719 | 93.4355 | SDS-THM4 | mg/L | 77 | --- | 2732 | --- | 77.5182 | 2711.1487 | 97.1599 | SDS-THM4 | mg/L | 47.4 | --- | 649.6449 | --- | 86.1606 | 644.2027 | 92.6421 | SDS-THM4 | mg/L | 37.9 | --- | 485.8412 | --- | 88.9343 | 481.5873 | 92.1302 | Alkb, mg/L CaCO3 | 122.4747 | NA | 120.2508 | 113.9183 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 5 | [13 empty] | SDS-BCAA* | mg/L | 23 | 21 | 22 | 9.0909 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 8:10 | 72.1667 | 24 | 42.5 | 43.5 | 263 | 4.67 | 1.36 |  | 6.03 | 0.20132 | 0.77446 | 42.6153 | 10.659 | 10.0472 | 559.1653 | 156.091 | 552.008 | 3.995 | 39.005 | 0.25759 |  |  |  | 143 |  | 498 | 604.1176 | -21.3088 | 42.1053 | 600.0237 | 76.1676 | 0.017 |  | 0.794 | 0.86829 | -9.3569 | 91.866 | 0.86074 | 98.0249 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 100.0844 | NA | 100.9197 | 93.3221 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 9:30 | 73.5 | 24 | 42.5 | 43.5 | 263 | 4.68 | 2.1 |  | 6.78 | 0.20132 | 0.69027 | 37.7906 | 10.6818 | 10.0687 | 491.6237 | 137.233 | 485.3174 | 3.5124 | 39.4876 | 0.25498 | 7.78 | 7.62 | 7.5 | 141 | 248 | 458 | 483.2286 | -5.5084 | 42.915 | 480.1836 | 70.6362 | 0.021 | 0.209 | 0.706 | 0.62797 | 11.0522 | 89.9522 | 0.62257 | 96.6269 | [8 empty] | SDS-DCAA* | mg/L | 3.5 | 3.2 | 3.35 | 8.9552 | --- | 283.1776 | --- | 96.0355 | 280.6091 | 98.8062 | SDS-DCAA* | mg/L | 5.8 | --- | 792.8 | --- | 93.1361 | 786.6192 | 99.2627 | SDS-DCAA* | mg/L | 1.8 | --- | 170.5755 | --- | 97.8698 | 169.0504 | 98.9352 | SDS-DCAA* | mg/L | 1.7 | --- | 123.4647 | --- | 97.9882 | 122.3084 | 98.6101 | Ca-Hdb, mg/L CaCO3 | 84.6716 | NA | 79.6693 | 76.9711 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hour | [13 empty] | SDS-CDBAA | mg/L | 6.5 | 4.3 | 5.4 | 40.7407 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 10:30 | 74.5 | 24 | 42.5 | 43.5 | 263 | 4.78 | 1.98 |  | 6.76 | 0.20132 | 0.7071 | 37.9053 | 10.9101 | 10.2838 | 503.8492 | 140.6064 | 497.2473 | 3.5994 | 39.4006 | 0.26101 |  |  |  | 146 |  | 444 | 490.8283 | -10.5469 | 40.8907 | 487.6947 | 70.0632 | 0.022 |  | 0.674 | 0.66044 | 2.0112 | 89.4737 | 0.65464 | 96.6394 | [8 empty] | SDS-TCAA* | mg/L | 1.9 | 1.6 | 1.75 | 17.1429 | --- | 392.2672 | --- | 98.4783 | 388.6828 | 99.5498 | SDS-TCAA* | mg/L | 4.2 | --- | 1112.2 | --- | 96.3478 | 1103.4982 | 99.6194 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 48 | 29 | 38.5 | 49.3506 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 11:30 | 75.5 | 24 | 42.5 | 43.5 | 263 | 4.69 | 1.91 |  | 6.6 | 0.20132 | 0.71061 | 38.8485 | 10.7047 | 10.0902 | 506.4084 | 141.3561 | 499.8985 | 3.618 | 39.382 | 0.25621 |  |  |  | 144 |  | 429 | 499.9162 | -16.5306 | 41.7004 | 496.7428 | 71.0112 | 0.021 |  | 0.661 | 0.67063 | -1.4574 | 89.9522 | 0.66484 | 96.8414 | [8 empty] | SDS-MBAA* | mg/L | 1.2 | 1.2 | 1.2 | 0 | --- | 3.9586 | --- | 40 | 3.9333 | 69.4913 | SDS-MBAA* | mg/L | 1.4 | --- | 7.4 | --- | 30 | 7.3529 | 80.9598 | SDS-MBAA* | mg/L | 1 | --- | 3.0408 | --- | 50 | 3.0224 | 66.9134 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 224.3 | 205.3 | 214.8 | 8.8454 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 13:50 | 77.8333 | 24 | 42.5 | 43.5 | 263 | 4.64 | 1.79 |  | 6.43 | 0.20132 | 0.72162 | 39.902 | 10.5906 | 9.9826 | 514.756 | 143.7062 | 508.2097 | 3.6778 | 39.3222 | 0.25387 | 7.7 | 7.55 | 7.38 | 144 | 243 | 450 | 513.9944 | -14.221 | 41.7004 | 510.7306 | 71.8051 | 0.016 | 0.205 | 0.681 | 0.70929 | -4.1543 | 92.3445 | 0.70317 | 97.7246 | [8 empty] | SDS-DBAA* | mg/L | 7 | 6.3 | 6.65 | 10.5263 | --- | -4.7293 | --- | -98.5075 | -4.6249 | 243.788 | SDS-DBAA* | mg/L | 7.6 | --- | -34.9 | --- | -126.8657 | -34.5662 | 121.9868 | SDS-DBAA* | mg/L | 5.3 | --- | 1.3204 | --- | -58.209 | 1.3564 | -290.7489 | SDS-DBAA* | mg/L | 4.4 | --- | 2.8559 | --- | -31.3433 | 2.8705 | -53.2809 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 247.3 | 226.3 | 236.8 | 8.8682 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 14:00 | 78 | 24 | 42.5 | 43.5 | 263 | 4.59 | 0.6 |  | 5.19 | 0.20132 | 0.88439 | 49.6744 | 10.4764 | 9.875 | 681.3033 | 190.2283 | 672.7328 | 4.8679 | 38.1321 | 0.25897 | [27 empty] | SDS-BCAA* | mg/L | 5.9 | 5.6 | 5.75 | 5.2174 | --- | 61.7845 | --- | 73.8636 | 61.2702 | 90.6153 | SDS-BCAA* | mg/L | 9.1 | --- | 138.1 | --- | 58.6364 | 137.0869 | 93.3619 | SDS-BCAA* | mg/L | 4 | --- | 40.7347 | --- | 81.8182 | 40.4027 | 90.0997 | SDS-BCAA* | mg/L | 3.3 | --- | 30.8 | --- | 85 | 30.5388 | 89.1941 | Qp/QT (HAA5), % | 79.6631 | 82.1246 | 77.7939 | 77.0484 | Qp/QT (HAA5), % | 93.0394 | 95.9142 | 90.8563 | 89.9856
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 14:20 | 78.3333 | 24 | 42.5 | 43.5 | 263 | 4.59 | 0.64 |  | 5.23 | 0.20132 | 0.87763 | 49.2868 | 10.4764 | 9.875 | 672.2628 | 187.7041 | 663.806 | 4.8033 | 38.1967 | 0.25853 |  |  |  | 147 |  |  | 964.1875 |  | 40.4858 | 957.0565 | 84.6404 | 0.018 |  | 0.704 | 1.5788 | -124.2654 | 91.3876 | 1.5652 | 98.85 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 122.4705 | 124.4591 | 112.9302 | 107.8106 | SDS-THM4b, ug/L | 85.5252 | 87.8478 | 74.383 | 68.4038
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 14:40 | 78.6667 | 24 | 42.5 | 43.5 | 263 | 4.59 | 0.6 |  | 5.19 | 0.20132 | 0.88439 | 49.6744 | 10.4764 | 9.875 | 681.3033 | 190.2283 | 672.7328 | 4.8679 | 38.1321 | 0.25897 |  |  |  | 144 |  |  | 1034.95 |  | 41.7004 | 1027.1754 | 85.981 | 0.09 |  | 0.753 | 1.1194 | -48.6521 | 56.9378 | 1.1104 | 91.8946 | [8 empty] | SDS-CDBAA | mg/L | 6.3 | 6 | 6.15 | 4.878 | --- | 3.5638 | --- | -13.8889 | 3.5875 | -71.4271 | SDS-CDBAA | mg/L | 9.8 | --- | -34.2 | --- | -81.4815 | -33.8544 | 128.9475 | SDS-CDBAA | mg/L | 5.1 | --- | 5.7122 | --- | 5.5556 | 5.7067 | 10.6316 | SDS-CDBAA | mg/L | 4.5 | --- | 5.8235 | --- | 16.6667 | 5.811 | 22.5601 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-18 | 15:00 | 79 | 24 | 42.5 | 43.5 | 263 | 4.32 | 0.56 |  | 4.88 | 0.20132 | 0.88525 | 52.8934 | 9.8602 | 9.2942 | 682.1097 | 190.5969 | 674.0362 | 4.8748 | 38.1252 | 0.24378 |  |  |  | 149 |  |  | 1003 |  | 39.6761 | 995.9862 | 85.04 | 0.02 |  | 0.806 | 1.667 | -106.8238 | 90.4306 | 1.6535 | 98.7904 | [8 empty] | SDS-DCBAA | mg/L | 5.1 | 4.7 | 4.9 | 8.1633 | --- | 120.7621 | --- | 87.2727 | 119.6986 | 95.9064 | SDS-DCBAA | mg/L | 11 | --- | 286 | --- | 71.4286 | 283.8403 | 96.1246 | SDS-DCBAA | mg/L | 2.9 | --- | 75.5531 | --- | 92.4675 | 74.8965 | 96.128 | SDS-DCBAA | mg/L | 2.6 | --- | 55.3941 | --- | 93.2468 | 54.8928 | 95.2635 | SDS-TOXb, ug Cl- /L | 406.9606 | 401.5117 | 401.4224 | 404.2415 | SDS-TOXb, ug Cl- /L | 209.995 | 203.6313 | 203.5269 | 206.8194
[44 empty] | 1998-09-18 | 15:20 | 79.3333 | 24 | 42.5 | 43.5 | 263 | 4.33 | 0.58 |  | 4.91 | 0.20132 | 0.88187 | 52.5642 | 9.883 | 9.3157 | 677.5758 | 189.3247 | 669.5372 | 4.8423 | 38.1577 | 0.24414 |  |  |  | 153 |  |  | 948.7586 |  | 38.0567 | 942.208 | 83.7615 | 0.21 |  | 0.837 | 0.20153 | 75.9218 | -0.47847 | 0.2016 | -4.1645 | [8 empty] | SDS-HAA5 | mg/L | 13.6 | 12.3 | 12.95 | 10.0386 | --- | 708.9845 | --- | 93.9711 | 702.5958 | 98.1568 | SDS-HAA5 | mg/L | 19 | --- | 1977 | --- | 91.1546 | 1961.6226 | 99.0314 | SDS-HAA5 | mg/L | 8.1 | --- | 429.9367 | --- | 96.2291 | 426.1248 | 98.0991 | SDS-HAA5 | mg/L | 6.1 | --- | 313.0118 | --- | 97.1601 | 310.0972 | 98.0329 | SDS-CDb, mg/L | 4.0979 | 4.0316 | 3.7229 | 3.617 | SDS-CDb, mg/L | 2.9121 | 2.8346 | 2.4741 | 2.3504
[44 empty] | 1998-09-18 | 15:40 | 79.6667 | 24 | 42.5 | 43.5 | 263 | 4.48 | 0.55 |  | 5.03 | 0.20132 | 0.89066 | 51.2863 | 10.2254 | 9.6384 | 689.7467 | 192.6449 | 681.279 | 4.9287 | 38.0713 | 0.25317 |  |  |  | 157 |  |  | 980.0909 |  | 36.4372 | 973.0806 | 83.8657 | 0.025 |  | 0.89 | 1.7078 | -91.8836 | 88.0383 | 1.6934 | 98.5237 | [8 empty] | SDS-HAA6 | mg/L | 19.5 | 17.9 | 18.7 | 8.5561 | --- | 770.769 | --- | 92.103 | 763.8659 | 97.5519 | SDS-HAA6 | mg/L | 28.1 | --- | 2115.1 | --- | 88.1334 | 2098.7095 | 98.6611 | SDS-HAA6 | mg/L | 12.1 | --- | 470.6714 | --- | 94.8902 | 466.5275 | 97.4064 | SDS-HAA6 | mg/L | 9.4 | --- | 343.8118 | --- | 96.0304 | 340.636 | 97.2405 | TOCb, mg/L | 2.4049 | 2.7977 | 2.2321 | 2.4443 | TOCb, mg/L | 1.4151 | 1.8737 | 1.2132 | 1.4611
[44 empty] | 1998-09-18 | 16:00 | 80 | 24 | 42.5 | 43.5 | 263 | 4.44 | 0.53 |  | 4.97 | 0.20132 | 0.89336 | 51.9175 | 10.1341 | 9.5523 | 693.4668 | 193.7055 | 685.0298 | 4.9554 | 38.0446 | 0.25108 |  |  |  | 149 |  |  | 1067.9811 |  | 39.6761 | 1060.224 | 85.9464 | 0.027 |  | 0.935 | 1.7337 | -85.4202 | 87.0813 | 1.7193 | 98.4296 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.057242 | 0.063639 | 0.055746 | 0.054903 | UV254 b, cm-1 | 0.03176 | 0.039232 | 0.030013 | 0.029029
[44 empty] | 1998-09-18 | 16:20 | 80.3333 | 24 | 42.5 | 43.5 | 263 | 4.44 | 0.5 |  | 4.94 | 0.20132 | 0.89879 | 52.2389 | 10.1341 | 9.5523 | 701.1635 | 195.8555 | 692.6329 | 5.0104 | 37.9896 | 0.25145 |  |  |  | 149 |  |  | 1117.24 |  | 39.6761 | 1109.067 | 86.5653 | 0.027 |  | 0.973 | 1.8252 | -87.5807 | 87.0813 | 1.81 | 98.5083 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 185.8484 | 158.2125 | 157.7794 | 157.7048 | Bromideb, ug/L | 191.8677 | 159.5914 | 159.0856 | 158.9986
[44 empty] | 1998-09-18 | 16:40 | 80.6667 | 24 | 42.5 | 43.5 | 263 | 4.4 | 0.51 |  | 4.91 | 0.20132 | 0.89613 | 52.5642 | 10.0428 | 9.4663 | 697.3206 | 194.8037 | 688.9135 | 4.9831 | 38.0169 | 0.249 |  |  |  | 150 |  |  | 1083.8627 |  | 39.2713 | 1076.051 | 86.0601 | 0.027 |  | 1.017 | 1.7792 | -74.9455 | 87.0813 | 1.7645 | 98.4699 | [47 empty] | Alkb, mg/L CaCO3 | 126.6775 | 140.8938 | 123.9956 | 118.0331 | Alkb, mg/L CaCO3 | 123.6009 | 140.2043 | 120.4688 | 113.505
[44 empty] | 1998-09-18 | 17:00 | 81 | 24 | 42.5 | 43.5 | 263 | 4.4 | 0.53 |  | 4.93 | 0.20132 | 0.89249 | 52.3469 | 10.0428 | 9.4663 | 692.201 | 193.3735 | 683.8556 | 4.9465 | 38.0535 | 0.24876 |  |  |  | 154 |  |  | 1019.0755 |  | 37.6518 | 1011.8391 | 84.7802 | 0.029 |  | 1.043 | 1.7033 | -63.3116 | 86.1244 | 1.6893 | 98.2833 | [47 empty] | T-Hdb, mg/L CaCO3 | 118.5403 | 129.1941 | 115.7605 | 107.3124 | T-Hdb, mg/L CaCO3 | 105.0302 | 117.4729 | 101.7837 | 91.9171
[44 empty] | 1998-09-18 | 17:20 | 81.3333 | 24 | 42.5 | 43.5 | 263 | 4.36 | 0.51 |  | 4.87 | 0.20132 | 0.89528 | 53.0041 | 9.9515 | 9.3802 | 696.0577 | 194.4726 | 687.7425 | 4.9743 | 38.0257 | 0.24668 |  |  |  | 160 |  |  | 990.7647 |  | 35.2227 | 983.8785 | 83.7378 | 0.029 |  | 1.067 | 1.7478 | -63.8073 | 86.1244 | 1.7336 | 98.3272 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 99.4729 | 106.5128 | 92.4296 | 88.4926 | Ca-Hdb, mg/L CaCO3 | 88.6381 | 96.8601 | 80.4122 | 75.8141
[44 empty] | 1998-09-18 | 17:40 | 81.6667 | 24 | 42.5 | 43.5 | 263 | 4.34 | 0.48 |  | 4.82 | 0.20132 | 0.90041 | 53.5643 | 9.9058 | 9.3372 | 703.3683 | 196.5261 | 695.0045 | 5.0266 | 37.9734 | 0.24589 |  |  |  | 157 |  |  | 1060.75 |  | 36.4372 | 1053.2932 | 85.0944 | 0.029 |  | 1.116 | 1.8365 | -64.5609 | 86.1244 | 1.8216 | 98.408 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-09-18 | 18:00 | 82 | 24 | 42.5 | 43.5 | 263 | 4.32 | 0.49 |  | 4.81 | 0.20132 | 0.89813 | 53.6778 | 9.8602 | 9.2942 | 700.0565 | 195.6116 | 691.7706 | 5.003 | 37.997 | 0.2446 | 7.73 | 7.7 |  | 157 | 248 |  | 1040.4694 |  | 36.4372 | 1033.2135 | 84.8047 | 0.029 | 0.208 | 1.148 | 1.7959 | -56.4407 | 86.1244 | 1.7814 | 98.3721 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-09-19 | 9:50 | 97.8333 | 24 | 42.5 | 43.5 | 263 | 4.07 | 0.36 |  | 4.43 | 0.20132 | 0.91874 | 58.3679 | 9.2896 | 8.7563 | 730.4268 | 204.2399 | 722.284 | 5.2212 | 37.7788 | 0.23178 | 7.67 | 7.55 |  | 166 | 251 |  | 1162.75 |  | 32.7935 | 1155.0375 | 85.6282 | 0.033 | 0.208 | 1.77 | 2.1988 | -24.2247 | 84.2105 | 2.182 | 98.4876 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-09-19 | 10:45 | 98.75 | 24 | 42.5 | 43.5 | 263 | 4.09 | 0.46 |  | 4.55 | 0.20132 | 0.8989 | 56.8022 | 9.3352 | 8.7993 | 700.8422 | 195.9566 | 692.9906 | 5.0096 | 37.9904 | 0.23162 |  |  | 7.49 | 165 |  | 762 | 976.087 | -28.0954 | 33.1984 | 969.7802 | 82.9858 | 0.034 |  | 1.797 | 1.765 | 1.782 | 83.7321 | 1.7515 | 98.0588 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-09-19 | 11:30 | 99.5 | 24 | 42.5 | 43.5 | 263 | 4.1 | 0.45 |  | 4.55 | 0.20132 | 0.9011 | 56.8022 | 9.358 | 8.8208 | 704.019 | 196.8394 | 696.1124 | 5.0323 | 37.9677 | 0.23232 |  |  |  | 163 |  |  | 1012.3333 |  | 34.0081 | 1005.7131 | 83.7926 | 0.035 |  | 1.767 | 1.7943 | -1.5469 | 83.2536 | 1.7806 | 98.0344 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-09-19 | 11:45 | 99.75 | 24 | 42.5 | 43.5 | 263 | 4.32 | 3.62 |  | 7.94 | 0.20132 | 0.54408 | 32.1234 | 9.8602 | 9.2942 | 406.2849 | 113.5252 | 401.476 | 2.9036 | 40.0964 | 0.23179 | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-09-19 | 12:00 | 100 | 24 | 42.5 | 43.5 | 263 | 4.32 | 3.62 |  | 7.94 | 0.20132 | 0.54408 | 32.1234 | 9.8602 | 9.2942 | 406.2849 | 113.5252 | 401.476 | 2.9036 | 40.0964 | 0.23179 |  |  |  | 159 |  | 617 | 352.0166 | 42.9471 | 35.6275 | 350.4313 | 54.6273 | 0.026 |  | 1.232 | 0.42739 | 65.3095 | 87.5598 | 0.42409 | 93.8692 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-09-19 | 12:20 | 100.3333 | 24 | 42.5 | 43.5 | 263 | 4.04 | 3.93 |  | 7.97 | 0.20132 | 0.5069 | 31.9987 | 9.2211 | 8.6918 | 389.0688 | 108.7994 | 384.7635 | 2.7812 | 40.2188 | 0.21611 |  |  |  | 147 |  | 536 | 349.799 | 34.739 | 40.4858 | 348.2414 | 57.7879 | 0.021 |  | 1.003 | 0.40226 | 59.8941 | 89.9522 | 0.39933 | 94.7412 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-09-19 | 12:40 | 100.6667 | 24 | 42.5 | 43.5 | 263 | 4.52 | 4.18 |  | 8.7 | 0.20132 | 0.51954 | 29.2299 | 10.3167 | 9.7244 | 394.8524 | 110.2692 | 389.9615 | 2.8214 | 40.1786 | 0.24203 |  |  |  | 140 |  | 463 | 362.7033 | 21.6623 | 43.3198 | 360.7896 | 61.1962 | 0.017 |  | 0.82 | 0.41662 | 49.193 | 91.866 | 0.41318 | 95.8856 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-09-19 | 13:00 | 101 | 24 | 42.5 | 43.5 | 263 | 4.62 | 4.72 |  | 9.34 | 0.20132 | 0.49465 | 27.1585 | 10.5449 | 9.9396 | 383.8663 | 107.1713 | 379.0057 | 2.7426 | 40.2574 | 0.2469 |  |  |  | 134 |  | 414 | 357.6059 | 13.6218 | 45.749 | 355.6419 | 62.3217 | 0.015 |  | 0.638 | 0.39889 | 37.4781 | 92.823 | 0.39552 | 96.2075 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-09-19 | 13:20 | 101.3333 | 24 | 42.5 | 43.5 | 263 | 4.66 | 4.66 |  | 9.32 | 0.20132 | 0.5 | 27.2189 | 10.6362 | 10.0256 | 386.1916 | 107.8084 | 381.259 | 2.7592 | 40.2408 | 0.24914 |  |  |  | 136 |  | 393 | 358 | 8.9059 | 44.9393 | 356.0332 | 61.8013 | 0.011 |  | 0.551 | 0.407 | 26.1343 | 94.7368 | 0.40349 | 97.2738 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-09-19 | 13:40 | 101.6667 | 24 | 42.5 | 43.5 | 263 | 4.68 | 4.64 |  | 9.32 | 0.20132 | 0.50215 | 27.2189 | 10.6818 | 10.0687 | 387.1326 | 108.0651 | 382.1667 | 2.7658 | 40.2342 | 0.25025 |  |  |  | 131 |  | 360 | 364 | -1.1111 | 46.9636 | 361.9269 | 63.8048 | 0.013 |  | 0.493 | 0.40669 | 17.5072 | 93.7799 | 0.40319 | 96.7757 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-09-19 | 14:00 | 102 | 24 | 42.5 | 43.5 | 263 | 3.9 | 3.83 |  | 7.73 | 0.20132 | 0.50453 | 33.0233 | 8.9015 | 8.3906 | 387.9905 | 108.5401 | 383.8466 | 2.7738 | 40.2262 | 0.20858 |  |  |  | 124 |  | 352 | 372.248 | -5.7523 | 49.7976 | 370.4074 | 66.5233 | 0.011 |  | 0.448 | 0.41062 | 8.344 | 94.7368 | 0.40766 | 97.3016
[44 empty] | 1998-09-19 | 14:20 | 102.3333 | 24 | 42.5 | 43.5 | 263 | 4.69 | 4.32 |  | 9.01 | 0.20132 | 0.52053 | 28.1898 | 10.7047 | 10.0902 | 395.3481 | 110.3553 | 390.2659 | 2.8245 | 40.1755 | 0.25115 |  |  |  | 125 |  | 341 | 379.4491 | -11.2754 | 49.3927 | 377.1803 | 66.8594 | 0.011 |  | 0.434 | 0.42396 | 2.3137 | 94.7368 | 0.42028 | 97.3827
[44 empty] | 1998-09-19 | 14:40 | 102.6667 | 24 | 42.5 | 43.5 | 263 | 4.72 | 4.56 |  | 9.28 | 0.20132 | 0.50862 | 27.3405 | 10.7731 | 10.1547 | 389.9953 | 108.852 | 384.9497 | 2.7862 | 40.2138 | 0.25252 |  |  |  | 125 |  | 338 | 373.2807 | -10.4381 | 49.3927 | 371.0528 | 66.3121 | 0.011 |  | 0.426 | 0.41395 | 2.8293 | 94.7368 | 0.41033 | 97.3192
[44 empty] | 1998-09-19 | 15:00 | 103 | 24 | 42.5 | 43.5 | 263 | 4.76 | 4.56 |  | 9.32 | 0.20132 | 0.51073 | 27.2189 | 10.8644 | 10.2408 | 390.9435 | 109.1045 | 385.8426 | 2.7929 | 40.2071 | 0.2547 | 7.86 |  | 7.59 | 126 |  | 336 | 373.307 | -11.1033 | 48.9879 | 371.069 | 66.0441 | 0.011 |  | 0.412 | 0.41568 | -0.89423 | 94.7368 | 0.41202 | 97.3302
[44 empty] | 1998-09-19 | 15:20 | 103.3333 | 24 | 42.5 | 43.5 | 263 | 4.76 | 4.56 |  | 9.32 | 0.20132 | 0.51073 | 27.2189 | 10.8644 | 10.2408 | 390.9435 | 109.1045 | 385.8426 | 2.7929 | 40.2071 | 0.2547
[44 empty] | 1998-09-20 | 9:15 | 121.25 | 24 | 42.5 | 43.5 | 263 | 4.76 | 4.56 |  | 9.32 | 0.20132 | 0.51073 | 27.2189 | 10.8644 | 10.2408 | 390.9435 | 109.1045 | 385.8426 | 2.7929 | 40.2071 | 0.2547 | 7.91 | 7.7 | 7.65 | 132 | 248 | 366 | 367.0439 | -0.28521 | 46.5587 | 364.9168 | 63.8274 | 0.012 | 0.206 | 0.478 | 0.41464 | 13.2552 | 94.2584 | 0.411 | 97.0803
[44 empty] | 1998-09-20 | 9:40 | 121.6667 | 24 | 41.5 | 43 | 263 | 4.84 | 13.26 |  | 18.1 | 0.20132 | 0.2674 | 13.5304 | 11.047 | 10.4129 | 305.9934 | 85.3776 | 301.9334 | 2.1859 | 40.0641 | 0.25991 |  |  |  | 126 |  | 304 | 291.1659 | 4.2217 | 48.9879 | 289.6461 | 56.4986 | 0.012 |  | 0.346 | 0.28091 | 18.8132 | 94.2584 | 0.27843 | 95.6902
[44 empty] | 1998-09-20 | 10:00 | 122 | 24 | 41.5 | 43 | 263 | 4.87 | 13.2 |  | 18.07 | 0.20132 | 0.26951 | 13.5545 | 11.1155 | 10.4774 | 306.572 | 85.5318 | 302.4789 | 2.1899 | 40.0601 | 0.26154 |  |  |  | 123 |  | 286 | 292.7485 | -2.3596 | 50.2024 | 291.1769 | 57.7576 | BMRL |  | 0.29 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-20 | 10:20 | 122.3333 | 24 | 42 | 43 | 263 | 4.89 | 12.15 |  | 17.04 | 0.20132 | 0.28697 | 14.4343 | 11.1612 | 10.5205 | 311.4412 | 86.8854 | 307.266 | 2.2247 | 40.2753 | 0.26121 |  |  |  | 119 |  | 283 | 298.516 | -5.4827 | 51.8219 | 296.8472 | 59.912 | BMRL |  | 0.278 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-20 | 10:40 | 122.6667 | 24 | 42 | 43 | 263 | 4.87 | 13.09 |  | 17.96 | 0.20132 | 0.27116 | 13.6437 | 11.1155 | 10.4774 | 307.0255 | 85.6584 | 302.9264 | 2.1932 | 40.3068 | 0.25994 | 7.98 | 7.78 | 7.74 | 118 | 248 | 276 | 294.9931 | -6.8816 | 52.2267 | 293.3544 | 59.7756 | BMRL | 0.206 | 0.278 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-20 | 11:00 | 123 | 24 | 42 | 43 | 263 | 4.87 | 13.03 |  | 17.9 | 0.20132 | 0.27207 | 13.6927 | 11.1155 | 10.4774 | 307.2758 | 85.7282 | 303.1734 | 2.195 | 40.305 | 0.25995 |  |  |  | 115 |  | 275 | 296.3354 | -7.7583 | 53.4413 | 294.6565 | 60.9715 | BMRL |  | 0.277 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-20 | 11:20 | 123.3333 | 24 | 42 | 43 | 263 | 4.84 | 12.23 |  | 17.07 | 0.20132 | 0.28354 | 14.4071 | 11.047 | 10.4129 | 310.4677 | 86.626 | 306.3484 | 2.2178 | 40.2822 | 0.2585 |  |  |  | 117 |  | 279 | 298.4473 | -6.9703 | 52.6316 | 296.7777 | 60.5765 | BMRL |  | 0.274 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-20 | 11:40 | 123.6667 | 24 | 42 | 43.5 | 263 | 4.87 | 12.15 |  | 17.02 | 0.20132 | 0.28613 | 14.4524 | 11.1155 | 10.4774 | 311.2024 | 86.8237 | 307.0475 | 2.223 | 40.527 | 0.25853 |  |  |  | 118 |  | 280 | 298.7062 | -6.6808 | 52.2267 | 297.0331 | 60.2738 | BMRL |  | 0.279 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-20 | 12:00 | 124 | 24 | 42 | 43.5 | 263 | 4.84 | 12.2 |  | 17.04 | 0.20132 | 0.28404 | 14.4343 | 11.047 | 10.4129 | 310.6082 | 86.6652 | 306.487 | 2.2188 | 40.5312 | 0.25691 |  |  |  | 117 |  | 276 | 298.5738 | -8.1789 | 52.6316 | 296.903 | 60.5932 | 0.009 |  | 0.281 | 0.28834 | -2.6136 | 95.6938 | 0.28577 | 96.8507
[44 empty] | 1998-09-20 | 12:20 | 124.3333 | 24 | 42 | 43.5 | 263 | 4.88 | 12.17 |  | 17.05 | 0.20132 | 0.28622 | 14.4252 | 11.1383 | 10.499 | 311.2267 | 86.828 | 307.063 | 2.2232 | 40.5268 | 0.25906 | 8.02 | 7.8 | 7.78 | 114 | 248 | 278 | 300.3311 | -8.0328 | 53.8462 | 298.6024 | 61.8221 | BMRL | 0.206 | 0.281 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-21 | 7:50 | 143.8333 | 24 | 42 | 43.5 | 263 | 4.88 | 9.28 | X | 14.16 | 0.20132 | 0.34463 | 17.5734 | 11.1383 | 10.499 | 328.6694 | 91.6943 | 324.2723 | 2.3478 | 40.4022 | 0.25986 | 7.92 | 7.77 | 7.71 | 123 | 250 | 294 | 312.2069 | -6.1928 | 50.2024 | 310.4515 | 60.3803 | BMRL | 0.204 | 0.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-09-22 | 15:45 |  | 24 | 40.5 | 41.5 | 263 | 5.3 | 7.2 |  | 12.5 | 0.20132 | 0.424 | 20.04 | 12.097 | 11.4026 | 355.8301 | 99.1553 | 350.6576 | 2.5409 | 38.4591 | 0.29649
[44 empty] | 1998-09-22 | 16:05 |  | 24 | 50 | 51 | 263 | 6.65 | 8.95 |  | 15.6 | 0.20132 | 0.42628 | 15.859 | 15.1783 | 14.307 | 356.9077 | 99.0792 | 350.3884 | 2.5457 | 47.9543 | 0.29835
[44 empty] | 1998-09-22 | 16:25 |  | 24 | 60 | 61 | 263 | 7.89 | 10.98 |  | 18.87 | 0.20132 | 0.41812 | 12.9375 | 18.0085 | 16.9747 | 354.1001 | 97.9558 | 346.4157 | 2.523 | 57.977 | 0.29278
[44 empty] | 1998-09-22 | 16:50 |  | 24 | 35 | 36 | 263 | 4.75 | 5.6 |  | 10.35 | 0.20132 | 0.45894 | 24.4106 | 10.8416 | 10.2193 | 369.1269 | 103.0188 | 364.3208 | 2.6371 | 32.8629 | 0.31097
[44 empty] | 1998-09-22 | 17:05 |  | 24 | 42 | 43 | 263 | 5.7 | 6.8 |  | 12.5 | 0.20132 | 0.456 | 20.04 | 13.0099 | 12.2631 | 368.1478 | 102.4728 | 362.3898 | 2.628 | 39.872 | 0.30756
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: Alison Gusses: NTR7450 membrane was used during quarters 1 and 2; NF200B membrane was used during quarters 3 and 4.
Note on R5: Gary Puetz: Contractor confirmed potential foulants were not measured during the study, because they were not required under the ICR.
Note on X26: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on X27: Gary Puetz: Consultant verified the concentrations of TOX and CHCl3. No changes were made.
Note on X28: Gary Puetz: Consultant verified the concentrations of TOX and CHCl3. No changes were made.
Note on CY31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DL31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DV31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on EF31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.

## NTR7450. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | FilmTec Corporation | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.50821 | [45 empty] | Recovery during sample collection (decimal) | 0.67 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | NF200B-400 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 0 mg/L | plant | Sampling date | MM/DD/YY | 1999-03-08 | 1999-03-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.02 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.8 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.48 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.78 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 200-400 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 22 |  |  | LSI | Coagulation | 135 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 12:00 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [6 empty] | SDS-THM4F, ug/L | 324.65 | 324.65 | 324.65 | 324.65 | SDS-THM4F, ug/L | 324.65 | 324.65 | 324.65 | 324.65 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 300 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.44 mg/L | plant | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 82.3 | 137.7 | 47.8 | 70.5 | SDS-THM4p, ug/L | 82.3 | 137.7 | 47.8 | 70.5 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | thin-film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 7.6 | 7.6 | 7.6 | 0 | 1999-03-16 | 8:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-17 | 10:00 | 0 | [7 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 112.9 | 112.9 | 112.9 | 112.9 | SDS-HAA5F, ug/L | 112.9 | 112.9 | 112.9 | 112.9 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | hydrophilic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.2599 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23.5 | 24 | 23.75 | 2.1053 | 1999-03-16 | 9:00 | 1 | 24 | 60 | 61 | 281 | 5.4 | 2.83 | 8.23 | 0.2151 | 0.65614 | 33.1434 | 12.3252 | 11.6177 | 0 | 0 | 0 | 0 | 63 | 0.18441 | 1999-03-17 | 10:15 | 0.25 | 23.5 | 60 | 61 | 272 | 5.75 | 3.52 |  | 9.27 | 0.20821 | 0.62028 | 28.342 | 13.1241 | 12.5549 | 518.7423 | 252.343 | 513.1107 | 2.6358 | 57.8642 | 0.21697 | 7.6 | 7.4 | 7.8 | 177 | 354 | 248 | 641.8168 | -158.7971 | 49.9293 | 636.9037 | 72.2093 | BMRL | 0.168 | 0.125 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 7.6 | 19.6 | 5.2 | 4.3 | SDS-HAA5p, ug/L | 7.6 | 19.6 | 5.2 | 4.3 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | highly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 218 | 216 | 217 | 0.92166 | 1999-03-16 | 9:45 | 1.75 | 24 | 65 | 66 | 272 | 6.2 | 2.84 | 9.04 | 0.20821 | 0.68584 | 29.0885 | 14.1512 | 13.3388 | 0 | 0 | 0 | 0 | 65.5 | 0.20365 | 1999-03-17 | 11:15 | 1.25 | 23.5 | 60 | 61 | 272 | 5.62 | 2.46 |  | 8.08 | 0.20821 | 0.69554 | 32.6634 | 12.8273 | 12.271 | 549.8616 | 267.5481 | 544.0285 | 2.794 | 57.706 | 0.21265 | 7.8 | 7.3 | 7.8 | 247 | 354 | 438 | 596.8049 | -36.2568 | 30.1273 | 593.1911 | 58.3608 | 0.014 | 0.169 | 0.323 | 0.52475 | -62.4607 | 91.7404 | 0.51947 | 97.305 | [8 empty] | Sampling date | MM/DD/YY | 1999-03-18 | 1999-03-19 | --- | --- | 1999-03-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-20 | 1999-03-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-21 | 1999-03-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-22 | 1999-03-22 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 892.5 | 892.5 | 892.5 | 892.5 | SDS-TOXF, ug Cl- /L | 892.5 | 892.5 | 892.5 | 892.5 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 354 | 353 | 353.5 | 0.28289 | 1999-03-16 | 10:15 | 2.25 | 24 | 65 | 66 | 272 | 6.22 | 2.62 | 8.84 | 0.20821 | 0.70362 | 29.7692 | 14.1968 | 13.3819 | 0 | 0 | 0 | 0 | 65.5 | 0.2043 | 1999-03-17 | 12:00 | 2 | 23.5 | 60 | 61 | 272 | 5.8 | 2.21 |  | 8.01 | 0.20821 | 0.72409 | 32.9576 | 13.2382 | 12.6641 | 562.8011 | 273.7491 | 556.6375 | 2.8597 | 57.6403 | 0.21971 | 7.7 | 7.3 | 7.8 | 284 | 354 | 483 | 535.8982 | -10.952 | 19.6605 | 533.2125 | 46.7379 | 0.017 | 0.168 | 0.419 | 0.56973 | -35.9729 | 89.9705 | 0.56383 | 96.9849 | [8 empty] | Sampling time | hh:mm | 9:00 | 8:30 | --- | --- | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:30 | 19:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:30 | 19:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:15 | 13:15 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 69.5 | 175 | 66 | 86 | SDS-TOXp, ug Cl- /L | 69.5 | 175 | 66 | 86 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 268 | 268 | 268 | 0 | 1999-03-16 | 11:00 | 3 | 24 | 65 | 66 | 272 | 6.58 | 2.2 | 8.78 | 0.20821 | 0.74943 | 29.9795 | 15.0185 | 14.1564 | 0 | 0 | 0 | 0 | 65.5 | 0.21613 | 1999-03-17 | 13:00 | 3 | 23.5 | 60 | 61 | 272 | 5.6 | 1.66 |  | 7.26 | 0.20821 | 0.77135 | 36.4656 | 12.7817 | 12.2274 | 585.2813 | 284.7934 | 579.0948 | 2.9739 | 57.5261 | 0.21255 | 7.7 | 7.3 | 7.8 | 315 | 354 | 551 | 483.3795 | 12.2723 | 10.8911 | 481.6462 | 34.5993 | 0.017 | 0.168 | 0.5 | 0.68396 | -36.7916 | 89.9705 | 0.67709 | 97.4893 | [8 empty] | Operation time | hh.hh | 23 | 46.5 | --- | --- | 23 | --- | --- | --- | --- | --- | Operation time | hh.hh | 81.5 | 81.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 105.5 | 105.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 123.25 | 123.25 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 9.55 | 9.55 | 9.55 | 9.55 | SDS-CDF, mg/L | 9.55 | 9.55 | 9.55 | 9.55 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 21.1 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 212 | 238 | 225 | 11.5556 | 1999-03-16 | 11:45 | 3.75 | 24 | 65 | 66 | 272 | 6.89 | 2.76 | 9.65 | 0.20821 | 0.71399 | 27.1865 | 15.7261 | 14.8233 | 0 | 0 | 0 | 0 | 63 | 0.23529 | 1999-03-17 | 14:00 | 4 | 23.5 | 60 | 61 | 272 | 5.55 | 2.29 |  | 7.84 | 0.20821 | 0.70791 | 33.6939 | 12.6676 | 12.1182 | 555.3045 | 270.2329 | 549.4878 | 2.8216 | 57.6784 | 0.2101 | 7.7 | 7.3 | 7.9 | 312 | 353 | 541 | 454.0786 | 16.0668 | 11.7397 | 452.6291 | 31.0694 | 0.017 | 0.169 | 0.507 | 0.5391 | -6.3306 | 89.9705 | 0.53377 | 96.8151 | [8 empty] | pH | --- | 7.9 | 8 | 7.95 | 1.2579 | 7.9 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 8 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 7.9 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.47 | 2.27 | 1.04 | 0.97 | SDS-CDp, mg/L | 1.47 | 2.27 | 1.04 | 0.97 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 71 | 1 | 0.7 | 15 | 6.5 | 64.2145 | 283.3154 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.218 | 0.218 | 0.218 | 0 | 1999-03-16 | 12:30 | 4.5 | 24 | 60 | 61 | 272 | 6.51 | 2.65 | 9.16 | 0.20821 | 0.7107 | 28.6943 | 14.8587 | 14.0058 | 0 | 0 | 0 | 0 | 61 | 0.2296 | 1999-03-17 | 15:00 | 5 | 23.5 | 61 | 61 | 272 | 5.7 | 1.71 |  | 7.41 | 0.20821 | 0.76923 | 35.7072 | 13.0099 | 12.4457 | 584.2986 | 284.2604 | 578.0111 | 2.9689 | 58.0311 | 0.21447 | 7.8 | 7.3 | 7.9 | 291 | 354 | 578 | 561.8333 | 2.797 | 17.6803 | 558.9956 | 47.9423 | 0.018 | 0.169 | 0.542 | 0.6745 | -24.4465 | 89.3805 | 0.66762 | 97.3039 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 7.75 | 7.75 | 7.75 | 7.75 | TOCF, mg/L | 7.75 | 7.75 | 7.75 | 7.75 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.284 | 2 | 0.9 | 15 | 16.5 | 74.2145 | 283.3154 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.1 | 0.19 | 0.145 | 62.069 | 1999-03-16 | 13:30 | 5.5 | 24 | 61 | 62 | 272 | 6.52 | 2.046 | 8.566 | 0.20821 | 0.76115 | 30.7534 | 14.8816 | 14.0273 | 0 | 0 | 0 | 0 | 61.5 | 0.22809 | 1999-03-17 | 16:00 | 6 | 23.5 | 60 | 61 | 272 | 5.71 | 2.62 |  | 8.33 | 0.20821 | 0.68547 | 31.6531 | 13.0328 | 12.4675 | 545.5234 | 265.3912 | 539.6427 | 2.7719 | 57.7281 | 0.21597 | 7.8 | 7.3 | 7.9 | 293 | 354 | 581 | 485.3531 | 16.4625 | 17.1146 | 483.3341 | 39.3794 | 0.018 | 0.17 | 0.551 | 0.49968 | 9.3144 | 89.3805 | 0.49462 | 96.3609 | [8 empty] | Alkalinity | mg/L as CaCO3 | NR | 112 | 112 | #VALUE! | 255 | 430.1818 | -68.6988 | 48.3871 | 427.039 | 73.7729 | Alkalinity | mg/L as CaCO3 | 184 | 292 | 484 | -65.7534 | 15.2074 | 481.1533 | 61.7586 | Alkalinity | mg/L as CaCO3 | 76 | 190 | 352.4706 | -85.5108 | 64.977 | 349.6118 | 78.2616 | Alkalinity | mg/L as CaCO3 | 68 | 186 | 280.8571 | -50.9985 | 68.6636 | 278.6527 | 75.5969 | TOCp, mg/L | 0.85 | 1.8 | BMRL | BMRL | TOCp, mg/L | 0.85 | 1.8 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 4.5 | 62.2145 | 283.3154 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 7.5 | 8 | 7.75 | 6.4516 | 1999-03-16 | 14:15 | 6.25 | 24 | 61 | 62 | 272 | 6.73 | 4.57 | 11.3 | 0.20821 | 0.59558 | 23.0708 | 15.3609 | 14.4791 | 0 | 0 | 0 | 0 | 61.5 | 0.23543 | 1999-03-17 | 17:00 | 7 | 23.5 | 60 | 61 | 272 | 5.7 | 2.5 |  | 8.2 | 0.20821 | 0.69512 | 32.1707 | 13.0099 | 12.4457 | 549.7207 | 267.4383 | 543.8052 | 2.7932 | 57.7068 | 0.21567 | 7.7 | 7.4 | 7.9 | 299 | 354 | 589 | 477.76 | 18.8862 | 15.4173 | 475.887 | 37.17 | 0.018 | 0.169 | 0.562 | 0.51492 | 8.3772 | 89.3805 | 0.50971 | 96.4686 | [8 empty] | Total dissolved solids | mg/L | 263 | 260 | 261.5 | 1.1472 | 570 | 540.2879 | 5.2127 | 26.0255 | 537.5341 | 51.3519 | Total dissolved solids | mg/L | 300 | 880 | 786.3636 | 10.6405 | 15.1344 | 781.7485 | 61.6245 | Total dissolved solids | mg/L | 245 | 456 | 457.7451 | -0.3827 | 30.6931 | 455.5452 | 46.2183 | Total dissolved solids | mg/L | 229 | 409 | 406.8571 | 0.52393 | 35.2192 | 405.0151 | 43.4589 | UV254 F, cm-1 | 0.1695 | 0.1695 | 0.1695 | 0.1695 | UV254 F, cm-1 | 0.1695 | 0.1695 | 0.1695 | 0.1695 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 400 | 4 | 0.3 | 15 | 3.6429 | 61.3573 | 283.3154 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.168 | 0.171 | 0.1695 | 1.7699 | 1999-03-16 | 15:00 | 7 | 24 | 61 | 62 | 272 | 6.3 | 2.7 | 9 | 0.20821 | 0.7 | 29.2222 | 14.3794 | 13.554 | 0 | 0 | 0 | 0 | 61.5 | 0.22039 | 1999-03-18 | 8:30 | 22.5 | 23.5 | 60 | 61 | 272 | 5.1 | 1.52 |  | 6.62 | 0.20821 | 0.77039 | 40.0876 | 11.6405 | 11.1356 | 584.4566 | 284.6659 | 578.8355 | 2.9698 | 57.5302 | 0.19356 | 7.9 | 7.3 | 7.7 |  | 353 | 880 |  | #VALUE! |  |  |  | 0.041 | 0.169 | 1.554 | 0.60065 | 61.348 | 75.8112 | 0.5954 | 93.1139 | [8 empty] | Total hardness | mg/L as CaCO3 | 156 | 154 | 155 | 1.2903 | 480 | 497.4242 | -3.6301 | 42.1642 | 494.0419 | 68.6261 | Total hardness | mg/L as CaCO3 | 244 | 772 | 462.1818 | 40.1319 | 8.9552 | 460.1115 | 46.9694 | Total hardness | mg/L as CaCO3 | 152 | 356 | 379.451 | -6.5874 | 43.2836 | 377.099 | 59.6923 | Total hardness | mg/L as CaCO3 | 146 | 318 | 320.2857 | -0.71878 | 45.5224 | 318.4807 | 54.1573 | UV254 p, cm-1 | 0.0115 | 0.036 | BMRL | BMRL | UV254 p, cm-1 | 0.0115 | 0.036 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.24 | 2.1375 | 2.1888 | 4.683 | 1999-03-16 | 15:45 | 7.75 | 24 | 61 | 62 | 272 | 6.4 | 2.7 | 9.1 | 0.20821 | 0.7033 | 28.8901 | 14.6077 | 13.7691 | 0 | 0 | 0 | 0 | 61.5 | 0.22389 | 1999-03-18 | 9:00 | 23 | 23.5 | 60 | 61 | 272 | 5.22 | 1.64 |  | 6.86 | 0.20821 | 0.76093 | 38.6501 | 11.9144 | 11.3976 | 579.8864 | 282.3748 | 574.1768 | 2.9466 | 57.5534 | 0.19804 | 7.8 | 7.3 | 7.9 |  | 353 | 787 |  | #VALUE! |  |  |  | 0.034 | 0.169 | 1.307 | 0.60079 | 54.0332 | 79.941 | 0.59535 | 94.2891 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 106 | 124 | 115 | 15.6522 | 400 | 448.3333 | -12.0833 | 48.8889 | 445.0408 | 74.1597 | Calcium hardness | mg/L as CaCO3 | 186 | 640 | 540.5455 | 15.5398 | 17.3333 | 537.1812 | 65.3748 | Calcium hardness | mg/L as CaCO3 | 94 | 306 | 350.8627 | -14.661 | 58.2222 | 348.2067 | 73.0045 | Calcium hardness | mg/L as CaCO3 | 88 | 266 | 283.7143 | -6.6595 | 60.8889 | 281.6873 | 68.7597 | BromideF, ug/L | 305 | 305 | 305 | 305 | BromideF, ug/L | 305 | 305 | 305 | 305 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 70 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 300 | 310 | 305 | 3.2787 | 1999-03-16 | 16:45 | 8.75 | 24 | 61 | 62 | 272 | 6.4 | 2.56 | 8.96 | 0.20821 | 0.71429 | 29.3571 | 14.6077 | 13.7691 | 0 | 0 | 0 | 0 | 61 | 0.22572 | 1999-03-18 | 10:00 | 24 | 23.5 | 60 | 61 | 272 | 5.45 | 1.76 |  | 7.21 | 0.20821 | 0.75589 | 36.7254 | 12.4393 | 11.8998 | 577.5916 | 281.1328 | 571.6515 | 2.9349 | 57.5651 | 0.20672 | 7.8 | 7.4 | 7.8 | 309 | 354 | 667 | 491.2983 | 26.3421 | 12.5884 | 489.472 | 36.8707 | 0.018 | 0.17 | 0.87 | 0.63863 | 26.5938 | 89.3805 | 0.63242 | 97.1538 | [8 empty] | Turbidity | ntu | 0.081 | 0.075 | 0.078 | 7.6923 | 0.233 | 0.50224 | -115.5547 | 64.2202 | 0.49805 | 84.339 | Turbidity | ntu | 0.101 | 0.357 | 1.1646 | -226.2287 | 53.6697 | 1.1545 | 91.252 | Turbidity | ntu | 0.064 | 0.225 | 0.36596 | -62.6492 | 70.6422 | 0.36284 | 82.3613 | Turbidity | ntu | 0.062 | 0.207 | 0.28486 | -37.6121 | 71.5596 | 0.28255 | 78.0569 | Bromidep, ug/L | 325 | 320 | 330 | 320 | Bromidep, ug/L | 325 | 320 | 330 | 320 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 16 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 10 | 11 | 10.5 | 9.5238 | 1999-03-16 | 17:30 | 9.5 | 24 | 60 | 61 | 272 | 6.4 | 2.73 | 9.13 | 0.20821 | 0.70099 | 28.7919 | 14.6077 | 13.7691 | 0 | 0 | 0 | 0 | 60.5 | 0.22759 | 1999-03-18 | 11:00 | 25 | 23.5 | 60 | 61 | 272 | 5.55 | 3.85 |  | 9.4 | 0.20821 | 0.59043 | 27.9362 | 12.6676 | 12.1182 | 507.2474 | 246.8464 | 501.934 | 2.5774 | 57.9226 | 0.20921 | 7.8 | 7.3 | 7.9 | 230 | 353 | 537 | 531.5325 | 1.0182 | 34.9364 | 528.4562 | 56.477 | 0.012 | 0.17 | 0.568 | 0.39655 | 30.1857 | 92.9204 | 0.39262 | 96.9436 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | 0.1 | NA | 0.18824 | #VALUE! | 31.0345 | 0.18732 | 46.6162 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217 | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 70.5467 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.95 | 0.95 | 0.95 | 0 | 1999-03-17 | 8:45 | 24.75 | 24 | 60 | 61 | 272 | 6.03 | 2 | 8.03 | 0.20821 | 0.75093 | 32.873 | 13.7632 | 12.9731 | 0 | 0 | 0 | 0 | 61 | 0.21267 | 1999-03-18 | 12:00 | 26 | 23.5 | 60 | 61 | 272 | 5.55 | 3.27 |  | 8.82 | 0.20821 | 0.62925 | 29.839 | 12.6676 | 12.1182 | 522.1822 | 254.1143 | 516.7124 | 2.6533 | 57.8467 | 0.20949 | 7.8 | 7.3 | 7.9 | 262 | 353 | 472 | 508.7982 | -7.7962 | 25.884 | 506.2803 | 48.25 | 0.01 | 0.169 | 0.384 | 0.44021 | -14.6383 | 94.1003 | 0.43582 | 97.7055 | [8 empty] | Total organic carbon | mg/L | 1 | 0.7 | 0.85 | 35.2941 | 21 | 21.7591 | -3.6147 | 89.0323 | 21.5526 | 96.0562 | Total organic carbon | mg/L | 1.8 | 62.1 | 55.8909 | 9.9985 | 76.7742 | 55.3776 | 96.7496 | Total organic carbon | mg/L | BMRL | 12.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 9.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 112 | 184 | 76 | 68 | Alkp, mg/L CaCO3 | 112 | 184 | 76 | 68
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.00233 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 9.05 | 10.05 | 9.55 | 10.4712 | 1999-03-17 | 9:45 | 25.75 | 24 | 61 | 62 | 272 | 6.3 | 2.8 | 9.1 | 0.20821 | 0.69231 | 28.8901 | 14.3794 | 13.554 | 0 | 0 | 0 | 0 | 66 | 0.20536 | 1999-03-18 | 13:00 | 27 | 23.5 | 60 | 61 | 272 | 5.77 | 3.18 |  | 8.95 | 0.20821 | 0.64469 | 29.3911 | 13.1697 | 12.5986 | 528.4741 | 257.0671 | 522.7167 | 2.6853 | 57.8147 | 0.21791 | 7.7 | 7.4 | 7.8 | 262 | 353 | 475 | 519.5236 | -9.3734 | 25.884 | 516.7921 | 49.3026 | 0.011 | 0.169 | 0.386 | 0.45709 | -18.4178 | 93.5103 | 0.45236 | 97.5683 | [8 empty] | UV254 | cm-1 | 0.013 | 0.01 | 0.0115 | 26.087 | 0.55 | 0.49029 | 10.8567 | 93.2153 | 0.48556 | 97.6316 | UV254 | cm-1 | 0.036 | 1.512 | 1.2496 | 17.3521 | 78.7611 | 1.2381 | 97.0924 | UV254 | cm-1 | BMRL | 0.352 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.242 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268 | T-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | 1999-03-17 | 9:25 | 25.4167 | 24 | 70 | 71 | 272 | 7.42 | NA | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 16.9358 | 15.9636 | #VALUE! | #VALUE! | #VALUE! | 0 | 60.5 | 0.26386 | 1999-03-18 | 14:00 | 28 | 23.5 | 60 | 61 | 272 | 5.7 | 2.52 |  | 8.22 | 0.20821 | 0.69343 | 32.09 | 13.0099 | 12.4457 | 548.9793 | 267.0776 | 543.0718 | 2.7895 | 57.7105 | 0.21566 | 7.8 | 7.3 | 7.9 | 275 | 354 | 502 | 531.0595 | -5.7887 | 22.2065 | 528.3765 | 47.9538 | 0.012 | 0.172 | 0.482 | 0.52575 | -9.0768 | 92.9204 | 0.52037 | 97.6939 | [8 empty] | SUVA | L/(mg*m) | 1.3 | 1.4286 | 1.3643 | 9.4241 | 2.619 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 2.4348 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.7717 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.5745 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 155 | 244 | 152 | 146 | T-Hdp, mg/L CaCO3 | 155 | 244 | 152 | 146
Process Train Name | Enhanced Coagulation/Lime Softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | 1999-03-17 | 9:40 | 25.6667 | 24 | 50 | 51 | 272 | 5.03 | NA | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 11.4807 | 10.8217 | #VALUE! | #VALUE! | #VALUE! | 0 | 56 | 0.19324 | 1999-03-18 | 15:30 | 29.5 | 23.5 | 60 | 61 | 272 | 5.51 | 2 |  | 7.51 | 0.20821 | 0.73369 | 35.2184 | 12.5763 | 12.0309 | 567.0693 | 275.9794 | 561.1726 | 2.8814 | 57.6186 | 0.2088 | 7.7 | 7.3 | 7.9 | 279 | 354 | 511 | 558.7475 | -9.3439 | 21.075 | 555.914 | 49.8124 | 0.013 | 0.17 | 0.491 | 0.60066 | -22.3335 | 92.3304 | 0.59471 | 97.814 | [8 empty] | Bromide | mg/L | 330 | 320 | 325 | 3.0769 | --- | 264.3939 | --- | -6.5574 | 264.9926 | -22.6449 | Bromide | mg/L | 320 | --- | 183.6364 | --- | -4.918 | 184.9303 | -73.0382 | Bromide | mg/L | 330 | --- | 280.9804 | --- | -8.1967 | 281.4873 | -17.2344 | Bromide | mg/L | 320 | --- | 298.5714 | --- | -4.918 | 298.7934 | -7.0974 | Ca-HdF, mg/L CaCO3 | 225 | 225 | 225 | 225 | Ca-HdF, mg/L CaCO3 | 225 | 225 | 225 | 225
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | 1999-03-17 | 9:55 | 25.9167 | 24 | 61 | 62 | 272 | 6.33 | NA | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 14.4479 | 13.6185 | #VALUE! | #VALUE! | #VALUE! | 0 | 31 | 0.43931 | 1999-03-18 | 16:45 | 30.75 | 23.5 | 60 | 61 | 272 | 5.2 | 1.05 |  | 6.25 | 0.20821 | 0.832 | 42.52 | 11.8687 | 11.354 | 616.7598 | 300.3418 | 610.7107 | 3.1339 | 57.3661 | 0.19792 | 7.7 | 7.4 | 7.9 | 281 | 353 | 515 | 712.5476 | -38.3588 | 20.5092 | 708.4225 | 60.3344 | 0.013 | 0.17 | 0.495 | 0.94455 | -90.8177 | 92.3304 | 0.93564 | 98.6106 | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 115 | 186 | 94 | 88 | Ca-Hdp, mg/L CaCO3 | 115 | 186 | 94 | 88
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 890 | 895 | 892.5 | 0.56022 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-18 | 18:00 | 32 | 23.5 | 60 | 61 | 272 | 5.8 | 3.43 |  | 9.23 | 0.20821 | 0.62839 | 28.4691 | 13.2382 | 12.6641 | 521.953 | 253.8804 | 516.2368 | 2.6521 | 57.8479 | 0.21892 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.98 | 1.08 | 1.03 | 9.7087 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.73 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.96 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.03 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 19 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 170 | 160 | 165 | 6.0606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 8:15 | 46.25 | 23.5 | 60 | 61 | 272 | 5.65 | 1.52 |  | 7.17 | 0.20821 | 0.78801 | 36.9358 | 12.8958 | 12.3365 | 593.7236 | 288.8735 | 587.3912 | 3.0168 | 57.4832 | 0.21461 | [27 empty] | SDS-Cl2 demand | mg/L | 1.52 | 1.42 | 1.47 | 6.8027 | --- | 25.9548 | --- | 84.6073 | 25.713 | 94.283 | SDS-Cl2 demand | mg/L | 2.27 | --- | 68.4518 | --- | 76.2304 | 67.8238 | 96.6531 | SDS-Cl2 demand | mg/L | 1.04 | --- | 17.7263 | --- | 89.1099 | 17.5537 | 94.0753 | SDS-Cl2 demand | mg/L | 0.97 | --- | 13.2271 | --- | 89.8429 | 13.1002 | 92.5955 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | minus 10%, plus 25% | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 100 | 100 | 100 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 8:30 | 46.5 | 23.5 | 60 | 61 | 272 | 5.5 | 2.89 |  | 8.39 | 0.20821 | 0.65554 | 31.4195 | 12.5535 | 12.009 | 532.7799 | 259.2966 | 527.2499 | 2.7072 | 57.7928 | 0.20779 | 7.7 | 7.3 | 7.8 | 274 | 353 | 576 | 504.7976 | 12.3615 | 22.4894 | 502.4641 | 45.4687 | 0.013 | 0.169 | 0.621 | 0.46734 | 24.7444 | 92.3304 | 0.46274 | 97.1907 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 104.2501 | 135.1431 | 91.2588 | 99.4098 | Qp/QT (THM4), % | 119.1046 | 154.3996 | 104.2622 | 113.5747
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | >99% 2000 ppm MgSO4 @ 67 psi | [13 empty] | SDS-DBCM | mg/L | 53 | 55 | 54 | 3.7037 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 9:30 | 47.5 | 23.5 | 60 | 61 | 272 | 5.37 | 2.53 |  | 7.9 | 0.20821 | 0.67975 | 33.4304 | 12.2567 | 11.7252 | 542.8779 | 264.2773 | 537.3776 | 2.7585 | 57.7415 | 0.20306 | 7.5 | 7.3 | 7.7 | 270 | 353 | 448 | 530.7312 | -18.4668 | 23.6209 | 528.1575 | 48.8789 | 0.012 | 0.169 | 0.543 | 0.5038 | 7.2194 | 92.9204 | 0.49894 | 97.5949 | [8 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NDP or< 50% 500 ppm CaCl2 | [13 empty] | SDS-CHBr3 | mg/L | 5.8 | 5.5 | 5.65 | 5.3097 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 10:30 | 48.5 | 23.5 | 60 | 61 | 272 | 5.43 | 2.2 |  | 7.63 | 0.20821 | 0.71166 | 34.6488 | 12.3937 | 11.8562 | 556.9215 | 271.0825 | 551.2152 | 2.8299 | 57.6701 | 0.20559 | 7.6 | 7.3 | 7.7 | 212 | 354 | 432 | 702.7477 | -62.6731 | 40.0283 | 697.8493 | 69.6209 | 0.01 | 0.17 | 0.536 | 0.56317 | -5.07 | 94.1003 | 0.55765 | 98.2068 | [8 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | 14.6143 | 4.941 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | unknown | [13 empty] | SDS-THM4 | mg/L | 328.8 | 320.5 | 324.65 | 2.5566 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 11:30 | 49.5 | 23.5 | 60 | 61 | 272 | 5.3 | 1.63 |  | 6.93 | 0.20821 | 0.76479 | 38.2496 | 12.097 | 11.5723 | 581.8302 | 283.2777 | 576.0128 | 2.9564 | 57.5436 | 0.20111 | 7.7 | 7.3 | 7.7 | 272 | 354 | 469 | 618.5 | -31.8763 | 23.0552 | 615.1242 | 55.7813 | 0.012 | 0.17 | 0.575 | 0.68162 | -18.542 | 92.9204 | 0.67509 | 98.2225 | [8 empty] | SDS-TOX | mg Cl- /L | 95 | 44 | 69.5 | 73.3813 | --- | 2563.4394 | --- | 92.2129 | 2538.8053 | 97.2625 | SDS-TOX | mg Cl- /L | 175 | --- | 6697.7273 | --- | 80.3922 | 6635.8333 | 97.3628 | SDS-TOX | mg Cl- /L | 66 | --- | 1686.5882 | --- | 92.605 | 1669.8306 | 96.0475 | SDS-TOX | mg Cl- /L | 86 | --- | 1238.1429 | --- | 90.3641 | 1226.2106 | 92.9865 | SDS-TOXb, ug Cl- /L | NA | NA | 138.246 | 90.76 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 15 | [13 empty] | SDS-MCAA* | mg/L | 6.3 | 5.4 | 5.85 | 15.3846 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 14:00 | 52 | 23.5 | 60 | 61 | 272 | 5.7 | 4.22 |  | 9.92 | 0.20821 | 0.5746 | 26.4194 | 13.0099 | 12.4457 | 501.4585 | 243.9588 | 496.0624 | 2.548 | 57.952 | 0.21476 | 7.7 | 7.3 | 7.8 | 203 | 354 | 399 | 556.782 | -39.5444 | 42.5743 | 553.0751 | 63.2961 | 0.01 | 0.17 | 0.501 | 0.38494 | 23.166 | 94.1003 | 0.38101 | 97.3754 | [8 empty] | SDS-CHCl3 | mg/L | 1.8 | 1.6 | 1.7 | 11.7647 | --- | 496.5485 | --- | 98.9697 | 491.6606 | 99.6542 | SDS-CHCl3 | mg/L | 6.7 | --- | 1445.7909 | --- | 95.9394 | 1432.1354 | 99.5322 | SDS-CHCl3 | mg/L | 0.6 | --- | 322.9529 | --- | 99.6364 | 319.6197 | 99.8123 | SDS-CHCl3 | mg/L | 1.4 | --- | 235.1143 | --- | 99.1515 | 232.6938 | 99.3984 | SDS-CDb, mg/L | NA | NA | 1.7839 | 1.0206 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7.0 + 0.3 | [13 empty] | SDS-DCAA* | mg/L | 43 | 50 | 46.5 | 15.0538 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 14:45 | 52.75 | 23.5 | 60 | 61 | 272 | 5.6 | 1.63 |  | 7.23 | 0.20821 | 0.77455 | 36.621 | 12.7817 | 12.2274 | 586.878 | 285.5703 | 580.6746 | 2.9821 | 57.5179 | 0.21258 | 7.7 | 7.3 | 7.7 | 237 | 354 | 441 | 753.7454 | -70.9173 | 32.9562 | 748.426 | 68.3335 | 0.01 | 0.17 | 0.451 | 0.71748 | -59.0855 | 94.1003 | 0.71019 | 98.5919 | [8 empty] | SDS-BDCM | mg/L | 7.6 | 6.6 | 7.1 | 14.0845 | --- | 288.6152 | --- | 92.9 | 285.8345 | 97.516 | SDS-BDCM | mg/L | 24 | --- | 714.9091 | --- | 76 | 708.3531 | 96.6119 | SDS-BDCM | mg/L | 3.2 | --- | 193.0039 | --- | 96.8 | 191.0413 | 98.325 | SDS-BDCM | mg/L | 6.1 | --- | 140.2429 | --- | 93.9 | 138.8536 | 95.6069 | TOCb, mg/L | NA | NA | #VALUE! | #VALUE! | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | < 105 psi | [13 empty] | SDS-TCAA* | mg/L | 43 | 47 | 45 | 8.8889 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 15:45 | 53.75 | 23.5 | 60 | 61 | 272 | 5.66 | 2.03 |  | 7.69 | 0.20821 | 0.73602 | 34.3706 | 12.9186 | 12.3584 | 568.255 | 276.4765 | 562.1835 | 2.8874 | 57.6126 | 0.21451 | 7.6 | 7.3 | 7.8 | 221 | 354 | 451 | 722.9335 | -60.2957 | 37.4823 | 717.7112 | 69.2077 | 0.01 | 0.17 | 0.521 | 0.61421 | -17.8914 | 94.1003 | 0.60793 | 98.3551 | [8 empty] | SDS-DBCM | mg/L | 31 | 26 | 28.5 | 17.5439 | --- | 105.7727 | --- | 47.2222 | 105.0095 | 72.8596 | SDS-DBCM | mg/L | 58 | --- | 21.6364 | --- | -7.4074 | 21.9814 | -163.8592 | SDS-DBCM | mg/L | 15 | --- | 91.4706 | --- | 72.2222 | 90.6798 | 83.4583 | SDS-DBCM | mg/L | 24 | --- | 66.8571 | --- | 55.5556 | 66.4133 | 63.8627 | UV254 b, cm-1 | NA | NA | #VALUE! | #VALUE! | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 3-10 (2-11 cleaning) | [13 empty] | SDS-MBAA* | mg/L | 8.6 | 2.5 | 5.55 | 109.9099 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 17:00 | 55 | 23.5 | 60 | 61 | 272 | 5.6 | 2.75 |  | 8.35 | 0.20821 | 0.67066 | 31.5749 | 12.7817 | 12.2274 | 539.136 | 262.3394 | 533.4373 | 2.7395 | 57.7605 | 0.21169 | 7.6 | 7.4 | 7.6 | 235 | 354 | 447 | 594.8091 | -33.0669 | 33.5219 | 591.1052 | 60.244 | 0.011 | 0.17 | 0.5 | 0.49226 | 1.5473 | 93.5103 | 0.48731 | 97.7427 | [8 empty] | SDS-CHBr3 | mg/L | 50 | 40 | 45 | 22.2222 | --- | -74.2424 | --- | -696.4602 | -73.0646 | 161.5893 | SDS-CHBr3 | mg/L | 49 | --- | -345.0909 | --- | -767.2566 | -341.3514 | 114.3547 | SDS-CHBr3 | mg/L | 29 | --- | -16.7843 | --- | -413.2743 | -16.3109 | 277.7954 | SDS-CHBr3 | mg/L | 39 | --- | -8.6429 | --- | -590.2655 | -8.1494 | 578.5606 | Bromideb, ug/L | NA | NA | 327.8147 | 319.9115 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 3 | [13 empty] | SDS-DBAA* | mg/L | 10 | 10 | 10 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-19 | 17:45 | 55.75 | 23.5 | 60 | 61 | 272 | 5.67 | 3.14 |  | 8.81 | 0.20821 | 0.64359 | 29.874 | 12.9415 | 12.3802 | 527.9781 | 256.8754 | 522.3268 | 2.6828 | 57.8172 | 0.21413 | 7.8 | 7.3 | 7.7 | 238 | 353 | 449 | 562.0621 | -25.1809 | 32.6733 | 558.6845 | 57.3999 | 0.012 | 0.17 | 0.487 | 0.4539 | 6.7961 | 92.9204 | 0.4493 | 97.3292 | [8 empty] | SDS-THM4 | mg/L | 90.4 | 74.2 | 82.3 | 19.6841 | --- | 816.6939 | --- | 74.6496 | 809.4399 | 89.8325 | SDS-THM4 | mg/L | 137.7 | --- | 1837.2455 | --- | 57.5851 | 1821.1185 | 92.4387 | SDS-THM4 | mg/L | 47.8 | --- | 590.6431 | --- | 85.2765 | 585.0299 | 91.8295 | SDS-THM4 | mg/L | 70.5 | --- | 433.5714 | --- | 78.2843 | 429.8112 | 83.5975 | Alkb, mg/L CaCO3 | NA | NA | 88.3251 | 68.8794 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 5 | [13 empty] | SDS-BCAA* | mg/L | 27 | 28 | 27.5 | 3.6364 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 10:00 | 72 | 23.5 | 60 | 61 | 272 | 5.66 | 2.3 |  | 7.96 | 0.20821 | 0.71106 | 33.1709 | 12.9186 | 12.3584 | 556.7817 | 270.8944 | 550.8327 | 2.8291 | 57.6709 | 0.21429 | 7.6 | 7.3 | 7.9 | 280 | 354 | 490 | 534.3739 | -9.0559 | 20.7921 | 531.7273 | 47.3414 | 0.015 | 0.172 | 0.692 | 0.5497 | 20.563 | 91.1504 | 0.54414 | 97.2434 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | NA | 162.1398 | 146.72 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | NR | 4.2 | 4.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 11:00 | 73 | 23.5 | 60 | 61 | 272 | 5.55 | 2.24 |  | 7.79 | 0.20821 | 0.71245 | 33.9166 | 12.6676 | 12.1182 | 557.3467 | 271.2267 | 551.5086 | 2.832 | 57.668 | 0.21014 | 7.5 | 7.3 | 7.7 | 289 | 353 | 508 | 513.3103 | -1.0453 | 18.2461 | 511.0218 | 43.4466 | 0.011 | 0.17 | 0.686 | 0.56221 | 18.0449 | 93.5103 | 0.55659 | 98.0237 | [8 empty] | SDS-DCAA* | mg/L | 1.1 | BMRL | 1.1 | #VALUE! | --- | 138.6758 | --- | 97.6344 | 137.3168 | 99.1989 | SDS-DCAA* | mg/L | 2.8 | --- | 400.0727 | --- | 93.9785 | 396.303 | 99.2935 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | NA | NA | 105.451 | 88.8086 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 1000 ppm-hour | [13 empty] | SDS-CDBAA | mg/L | 14 | 13 | 13.5 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 12:00 | 74 | 23.5 | 60 | 61 | 272 | 5.54 | 2.14 |  | 7.68 | 0.20821 | 0.72135 | 34.4167 | 12.6448 | 12.0964 | 561.3858 | 273.1976 | 555.516 | 2.8525 | 57.6475 | 0.20983 | 7.6 | 7.3 | 7.8 | 285 | 352 | 510 | 530.8318 | -4.0847 | 19.3777 | 528.3283 | 46.0563 | 0.011 | 0.169 | 0.659 | 0.57982 | 12.0148 | 93.5103 | 0.57403 | 98.0837 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.2 | --- | 399.3818 | --- | 97.3333 | 395.6035 | 99.6967 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 33 | 31 | 32 | 6.25 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 13:00 | 75 | 23.5 | 60 | 61 | 272 | 5.45 | 1.52 |  | 6.97 | 0.20821 | 0.78192 | 38.0244 | 12.4393 | 11.8998 | 590.4806 | 287.4063 | 584.408 | 3.0004 | 57.4996 | 0.20696 | 7.6 | 7.3 | 7.8 | 291 | 353 | 494 | 577.5954 | -16.9221 | 17.6803 | 574.7242 | 49.367 | 0.01 | 0.169 | 0.658 | 0.74139 | -12.6735 | 94.1003 | 0.73406 | 98.6377 | [8 empty] | SDS-MBAA* | mg/L | 1.3 | BMRL | 1.3 | #VALUE! | --- | 14.1788 | --- | 76.5766 | 14.0516 | 90.7484 | SDS-MBAA* | mg/L | 1.6 | --- | 37.5091 | --- | 71.1712 | 37.1684 | 95.6953 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 110.9 | 114.9 | 112.9 | 3.543 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 14:00 | 76 | 23.5 | 60 | 61 | 272 | 5.54 | 2.95 |  | 8.49 | 0.20821 | 0.65253 | 31.0377 | 12.6448 | 12.0964 | 531.5617 | 258.6837 | 526.0038 | 2.701 | 57.799 | 0.20928 | 7.6 | 7.3 | 7.8 | 287 | 354 | 492 | 478.3847 | 2.7673 | 18.8119 | 476.4357 | 39.761 | 0.011 | 0.169 | 0.636 | 0.46716 | 26.5475 | 93.5103 | 0.46251 | 97.6217 | [8 empty] | SDS-DBAA* | mg/L | 8.9 | 3.9 | 6.4 | 78.125 | --- | 17.3091 | --- | 36 | 17.2013 | 62.7936 | SDS-DBAA* | mg/L | 14 | --- | -22.3636 | --- | -40 | -22.0186 | 163.5827 | SDS-DBAA* | mg/L | 5.2 | --- | 14.6118 | --- | 48 | 14.5144 | 64.1736 | SDS-DBAA* | mg/L | 4.3 | --- | 12.4429 | --- | 57 | 12.3585 | 65.2062 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 137.9 | 142.9 | 140.4 | 3.5613 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 15:00 | 77 | 23.5 | 60 | 61 | 272 | 5.54 | 2.33 |  | 7.87 | 0.20821 | 0.70394 | 33.5616 | 12.6448 | 12.0964 | 553.527 | 269.3731 | 547.7395 | 2.8126 | 57.6874 | 0.20969 | 7.5 | 7.2 | 7.7 | 280 | 352 | 461 | 528.2597 | -14.5899 | 20.7921 | 525.7314 | 46.7409 | 0.012 | 0.17 | 0.601 | 0.54398 | 9.4867 | 92.9204 | 0.53857 | 97.7719 | [8 empty] | SDS-BCAA* | mg/L | 3.5 | 1.3 | 2.4 | 91.6667 | --- | 78.4606 | --- | 91.2727 | 77.7093 | 96.9116 | SDS-BCAA* | mg/L | 7.4 | --- | 190.1273 | --- | 73.0909 | 188.3934 | 96.072 | SDS-BCAA* | mg/L | 1.7 | --- | 52.2882 | --- | 93.8182 | 51.7651 | 96.7159 | SDS-BCAA* | mg/L | 1.2 | --- | 38.7714 | --- | 95.6364 | 38.3823 | 96.8736 | Qp/QT (HAA5), % | 55.9354 | 63.1297 | 54.689 | 54.2357 | Qp/QT (HAA5), % | 81.5764 | 92.0686 | 79.7586 | 79.0976
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 16:00 | 78 | 23.5 | 60 | 61 | 272 | 5.55 | 1.7 |  | 7.25 | 0.20821 | 0.76552 | 36.5172 | 12.6676 | 12.1182 | 582.3594 | 283.3989 | 576.2593 | 2.9591 | 57.5409 | 0.2106 | 7.6 | 7.3 | 7.7 | 292 | 353 | 491 | 554.2794 | -12.8879 | 17.3975 | 551.6036 | 47.0634 | 0.012 | 0.17 | 0.641 | 0.68369 | -6.6601 | 92.9204 | 0.67684 | 98.2271 | [8 empty] | SDS-TBAA | mg/L | 7.9 | 5.3 | 6.6 | 39.3939 | --- | -0.67273 | --- | -57.1429 | -0.60089 | 1198.3701 | SDS-TBAA | mg/L | 9.8 | --- | -41.1091 | --- | -133.3333 | -40.626 | 124.1225 | SDS-TBAA | mg/L | 6.3 | --- | 2.1824 | --- | -50 | 2.2249 | -183.1548 | SDS-TBAA | mg/L | 5.5 | --- | 3.6429 | --- | -30.9524 | 3.6621 | -50.1874 | SDS-THM4b, ug/L | 189.0905 | 206.629 | 173.2436 | 186.8099 | SDS-THM4b, ug/L | 126.9495 | 152.5278 | 103.8383 | 123.6234
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 16:45 | 78.75 | 23.5 | 60 | 61 | 272 | 5.18 | 0.41 |  | 5.59 | 0.20821 | 0.92665 | 47.6583 | 11.8231 | 11.3103 | 673.83 | 328.1457 | 667.2468 | 3.4239 | 57.0761 | 0.19816 | 7.6 | 7.3 | 7.8 | 296 | 353 | 608 | 1079.9634 | -77.6256 | 16.2659 | 1072.4985 | 72.4009 | 0.016 | 0.168 | 0.738 | 2.1088 | -185.7509 | 90.5605 | 2.0889 | 99.2341 | [8 empty] | SDS-CDBAA | mg/L | 4.6 | 2.6 | 3.6 | 55.5556 | --- | 33.6 | --- | 73.3333 | 33.3037 | 89.1904 | SDS-CDBAA | mg/L | 7.8 | --- | 59.6182 | --- | 42.2222 | 59.1265 | 86.8079 | SDS-CDBAA | mg/L | 3.1 | --- | 23.4922 | --- | 77.037 | 23.2813 | 86.6846 | SDS-CDBAA | mg/L | 2.2 | --- | 18.3429 | --- | 83.7037 | 18.1757 | 87.8959 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-20 | 17:30 | 79.5 | 23.5 | 60 | 61 | 272 | 5.2 | 0.64 |  | 5.84 | 0.20821 | 0.89041 | 45.5753 | 11.8687 | 11.354 | 650.7853 | 316.911 | 644.4024 | 3.3068 | 57.1932 | 0.19852 | 7.6 | 7.3 | 7.8 | 299 | 354 | 633 | 796.3125 | -25.7998 | 15.4173 | 791.5588 | 62.2264 | 0.022 | 0.169 | 0.85 | 1.3679 | -60.9338 | 87.0206 | 1.3551 | 98.3765 | [8 empty] | SDS-DCBAA | mg/L | 2.3 | 1.3 | 1.8 | 55.5556 | --- | 93.3152 | --- | 94.375 | 92.4112 | 98.0522 | SDS-DCBAA | mg/L | 4.4 | --- | 255.3091 | --- | 86.25 | 252.9282 | 98.2604 | SDS-DCBAA | mg/L | 1.5 | --- | 61.3039 | --- | 95.3125 | 60.6855 | 97.5282 | SDS-DCBAA | mg/L | 1.1 | --- | 45.2429 | --- | 96.5625 | 44.7857 | 97.5439 | SDS-TOXb, ug Cl- /L | 432.1515 | 439.5445 | 440.4958 | 455.0889 | SDS-TOXb, ug Cl- /L | 221.1258 | 231.9078 | 233.2953 | 254.5778
[44 empty] | 1999-03-20 | 18:15 | 80.25 | 23.5 | 60 | 61 | 272 | 5.25 | 0.86 |  | 6.11 | 0.20821 | 0.85925 | 43.5172 | 11.9828 | 11.4632 | 632.2235 | 307.8424 | 625.9624 | 3.2125 | 57.2875 | 0.2001 | 7.5 | 7.3 | 7.7 | 317 | 354 | 730 | 576.3198 | 21.0521 | 10.3253 | 573.8171 | 44.7559 | 0.024 | 0.17 | 0.93 | 1.0577 | -13.7341 | 85.8407 | 1.0478 | 97.7094 | [8 empty] | SDS-HAA5 | mg/L | 11.3 | 3.9 | 7.6 | 97.3684 | --- | 326.6909 | --- | 93.2684 | 323.5391 | 97.651 | SDS-HAA5 | mg/L | 19.6 | --- | 867.7818 | --- | 82.6395 | 859.7334 | 97.7202 | SDS-HAA5 | mg/L | 5.2 | --- | 216.3765 | --- | 95.3942 | 214.1928 | 97.5723 | SDS-HAA5 | mg/L | 4.3 | --- | 159.4429 | --- | 96.1913 | 157.8361 | 97.2757 | SDS-CDb, mg/L | 5.0304 | 4.9542 | 4.896 | 4.8966 | SDS-CDb, mg/L | 2.9586 | 2.8474 | 2.7625 | 2.7634
[44 empty] | 1999-03-20 | 19:00 | 81 | 23.5 | 60 | 61 | 272 | 5.29 | 0.69 |  | 5.98 | 0.20821 | 0.88462 | 44.4849 | 12.0741 | 11.5505 | 647.3308 | 315.1742 | 640.8708 | 3.2893 | 57.2107 | 0.20189 | 7.5 | 7.3 | 7.7 | 272 | 354 | 719 | 978.3333 | -36.0686 | 23.0552 | 971.4648 | 72.001 | 0.024 | 0.17 | 0.932 | 1.285 | -37.8755 | 85.8407 | 1.2727 | 98.1143 | [8 empty] | SDS-HAA6 | mg/L | 14.8 | 5.2 | 10 | 96 | --- | 405.1515 | --- | 92.8775 | 401.2484 | 97.5078 | SDS-HAA6 | mg/L | 27 | --- | 1057.9091 | --- | 80.7692 | 1048.1268 | 97.424 | SDS-HAA6 | mg/L | 6.9 | --- | 268.6647 | --- | 95.0855 | 265.9579 | 97.4056 | SDS-HAA6 | mg/L | 5.5 | --- | 198.2143 | --- | 96.0826 | 196.2184 | 97.197 | TOCb, mg/L | 3.8905 | 3.9938 | #VALUE! | #VALUE! | TOCb, mg/L | 2.1212 | 2.2719 | #VALUE! | #VALUE!
[44 empty] | 1999-03-20 | 19:30 | 81.5 | 23.5 | 60 | 61 | 272 | 5.31 | 0.54 |  | 5.85 | 0.20821 | 0.90769 | 45.4957 | 12.1198 | 11.5942 | 661.6994 | 322.1577 | 655.0709 | 3.3623 | 57.1377 | 0.20292 | 7.5 | 7.3 | 7.7 | 320 | 354 | 744 | 682.9167 | 8.2101 | 9.4767 | 679.3742 | 52.8978 | 0.025 | 0.169 | 0.951 | 1.5904 | -67.2362 | 85.2507 | 1.5751 | 98.4128 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.081122 | 0.085222 | #VALUE! | #VALUE! | UV254 b, cm-1 | 0.040609 | 0.046588 | #VALUE! | #VALUE!
[44 empty] | 1999-03-20 | 20:00 | 82 | 23.5 | 60 | 61 | 272 | 5.33 | 0.48 |  | 5.81 | 0.20821 | 0.91738 | 45.8158 | 12.1654 | 11.6378 | 667.9386 | 325.1828 | 661.2221 | 3.394 | 57.106 | 0.20379 | 7.5 | 7.3 | 7.7 | 325 | 354 | 762 | 669.9688 | 12.0776 | 8.0622 | 666.5888 | 51.2443 | 0.025 | 0.1 | 1.004 | 1.7741 | -76.6984 | 85.2507 | 1.7569 | 98.5771 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 316.1871 | 314.4695 | 318.6722 | 313.1354 | Bromideb, ug/L | 321.3153 | 318.8103 | 324.9396 | 316.8646
[44 empty] | 1999-03-20 | 20:30 | 82.5 | 23.5 | 60 | 61 | 272 | 5.31 | 0.88 |  | 6.19 | 0.20821 | 0.85784 | 42.9418 | 12.1198 | 11.5942 | 631.4598 | 307.4351 | 625.1342 | 3.2086 | 57.2914 | 0.20237 | 7.6 | 7.4 | 7.8 | 330 | 352 | 758 | 495.3011 | 34.6568 | 6.6478 | 493.6876 | 33.1561 | 0.025 | 0.171 | 1.083 | 1.0414 | 3.8388 | 85.2507 | 1.0315 | 97.5764 | [47 empty] | Alkb, mg/L CaCO3 | 158.2678 | 196.1672 | 139.8886 | 136.1888 | Alkb, mg/L CaCO3 | 131.3447 | 186.6174 | 104.5404 | 99.1446
[44 empty] | 1999-03-20 | 21:30 | 83.5 | 23.5 | 60 | 61 | 272 | 5.26 | 0.88 |  | 6.14 | 0.20821 | 0.85668 | 43.2997 | 12.0057 | 11.485 | 630.7453 | 307.1168 | 624.4869 | 3.205 | 57.295 | 0.20045 | 7.6 | 7.3 | 7.7 | 281 | 356 | 719 | 786.8523 | -9.437 | 20.5092 | 781.9611 | 64.0647 | 0.025 | 0.168 | 1.016 | 1.0332 | -1.6945 | 85.2507 | 1.0235 | 97.5573 | [47 empty] | T-Hdb, mg/L CaCO3 | 204.793 | 252.8489 | 204.5608 | 201.8324 | T-Hdb, mg/L CaCO3 | 175.8186 | 245.9035 | 175.48 | 171.5009
[44 empty] | 1999-03-20 | 22:00 | 84 | 23.5 | 60 | 61 | 272 | 5.31 | 0.77 |  | 6.08 | 0.20821 | 0.87336 | 43.7368 | 12.1198 | 11.5942 | 640.5726 | 311.8718 | 634.1556 | 3.2549 | 57.2451 | 0.20254 | 7.6 | 7.3 | 7.8 | 289 | 355 | 707 | 798.2987 | -12.9135 | 18.2461 | 793.3274 | 63.5712 | 0.026 | 0.169 | 1.008 | 1.1591 | -14.9892 | 84.6608 | 1.148 | 97.7353 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 163.471 | 200.3794 | 153.3575 | 150.6971 | Ca-Hdb, mg/L CaCO3 | 135.2659 | 189.0932 | 120.5162 | 116.6363
[44 empty] | 1999-03-21 | 10:00 | 96 | 23.5 | 60 | 61 | 272 | 4.97 | 0.1 |  | 5.07 | 0.20821 | 0.98028 | 52.6489 | 11.3438 | 10.8518 | 710.8426 | 346.31 | 704.1818 | 3.612 | 56.888 | 0.19076 | 7.7 | 7.3 |  | 341 | 354 |  | 974.75 |  | 3.5361 | 968.96 | 64.8076 | 0.026 | 0.169 |  | 7.3015 |  | 84.6608 | 7.235 | 99.6406 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-03-21 | 12:00 | 98 | 23.5 | 60 | 61 | 272 | 4.91 | 0.57 |  | 5.48 | 0.20821 | 0.89599 | 48.635 | 11.2068 | 10.7208 | 653.9355 | 318.6226 | 647.8826 | 3.3229 | 57.1771 | 0.1875 | 7.7 | 7.3 | 7.8 | 309 | 354 | 756 | 736.8246 | 2.5364 | 12.5884 | 732.9631 | 57.8424 | 0.026 | 0.169 | 1.093 | 1.4056 | -28.6015 | 84.6608 | 1.3932 | 98.1337 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-03-21 | 14:30 | 100.5 | 23.5 | 60 | 61 | 272 | 4.89 | 0.86 |  | 5.75 | 0.20821 | 0.85043 | 46.3043 | 11.1612 | 10.6771 | 626.8334 | 305.4291 | 621.0552 | 3.1852 | 57.3148 | 0.18629 | 7.7 | 7.3 | 7.8 | 289 | 353 | 701 | 720.25 | -2.7461 | 18.2461 | 716.3735 | 59.6579 | 0.025 | 0.17 | 1.003 | 0.99113 | 1.1831 | 85.2507 | 0.98245 | 97.4553 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-03-21 | 16:00 | 102 | 23.5 | 60 | 61 | 272 | 4.97 | 0.84 |  | 5.81 | 0.20821 | 0.85542 | 45.8158 | 11.3438 | 10.8518 | 629.7603 | 306.8081 | 623.8593 | 3.2 | 57.3 | 0.18939 | 7.7 | 7.3 | 7.8 | 298 | 355 | 688 | 681.875 | 0.89026 | 15.7001 | 678.3679 | 56.071 | 0.026 | 0.168 | 1.023 | 1.0185 | 0.43581 | 84.6608 | 1.0095 | 97.4244 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-03-21 | 16:30 | 102.5 | 23.5 | 61 | 62 | 272 | 5.2 | 4.05 |  | 9.25 | 0.20821 | 0.56216 | 28.4054 | 11.8687 | 11.354 | 496.7732 | 241.9122 | 491.9009 | 2.5242 | 58.9758 | 0.19252 | 7.6 | 7.4 | 7.7 | 281 | 356 | 558 | 446.5864 | 19.9666 | 20.5092 | 445.0036 | 36.8544 | 0.024 | 0.17 | 0.841 | 0.35631 | 57.632 | 85.8407 | 0.35314 | 93.2038 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-03-21 | 17:00 | 103 | 23.5 | 60 | 61 | 272 | 5.2 | 5.35 |  | 10.55 | 0.20821 | 0.49289 | 24.782 | 11.8687 | 11.354 | 473.1434 | 230.4053 | 468.5029 | 2.4042 | 58.0958 | 0.19544 | 7.7 | 7.4 | 7.8 | 251 | 355 | 561 | 453.1262 | 19.2288 | 28.9958 | 451.1941 | 44.3698 | 0.016 | 0.17 | 0.561 | 0.3187 | 43.1914 | 90.5605 | 0.3158 | 94.9335 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-03-21 | 17:30 | 103.5 | 23.5 | 60 | 61 | 272 | 5.36 | 4.96 |  | 10.32 | 0.20821 | 0.51938 | 25.3566 | 12.2339 | 11.7033 | 481.9601 | 234.6265 | 477.0862 | 2.449 | 58.051 | 0.2016 | 7.7 | 7.3 | 7.8 | 257 | 355 | 480 | 457.7823 | 4.6287 | 27.2984 | 455.804 | 43.6161 | 0.015 | 0.17 | 0.418 | 0.33646 | 19.5073 | 91.1504 | 0.33329 | 95.4994 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-03-21 | 18:15 | 104.25 | 23.5 | 60 | 61 | 272 | 5.4 | 4.95 |  | 10.35 | 0.20821 | 0.52174 | 25.2802 | 12.3252 | 11.7907 | 482.7699 | 235.0026 | 477.851 | 2.4531 | 58.0469 | 0.20312 | 7.7 | 7.3 | 7.8 | 258 | 354 | 463 | 457.6818 | 1.1486 | 27.0156 | 455.6997 | 43.3838 | 0.009 | 0.169 | 0.379 | 0.34459 | 9.0789 | 94.6903 | 0.34126 | 97.3627 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-03-21 | 19:00 | 105 | 23.5 | 60 | 61 | 272 | 5.25 | 4.3 |  | 9.55 | 0.20821 | 0.54974 | 27.4817 | 11.9828 | 11.4632 | 492.3807 | 239.7501 | 487.5045 | 2.5019 | 57.9981 | 0.19765 | 7.7 | 7.3 | 7.7 | 262 | 355 | 460 | 465.2151 | -1.1337 | 25.884 | 463.2539 | 43.4435 | 0.009 | 0.169 | 0.369 | 0.36546 | 0.95954 | 94.6903 | 0.36202 | 97.5139 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-03-21 | 19:30 | 105.5 | 23.5 | 60 | 61 | 272 | 5.5 | 7.4 |  | 12.9 | 0.20821 | 0.42636 | 20.0853 | 12.5535 | 12.009 | 452.5407 | 220.2452 | 447.8435 | 2.2995 | 58.2005 | 0.20634 | 7.7 | 7.3 | 7.7 | 231 | 355 | 339 | 444.5473 | -31.1349 | 34.6535 | 442.3883 | 47.7834 | BMRL | 0.17 | 0.317 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-03-21 | 20:30 | 106.5 | 23.5 | 60 | 61 | 272 | 5.67 | 6.73 |  | 12.4 | 0.20821 | 0.45726 | 20.9355 | 12.9415 | 12.3802 | 461.9646 | 224.7581 | 457.0199 | 2.3473 | 58.1527 | 0.21289 | 7.6 | 7.3 | 7.7 | 209 | 355 | 309 | 475.2407 | -53.7996 | 40.8769 | 472.4657 | 55.764 | BMRL | 0.17 | 0.254 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-03-21 | 21:00 | 107 | 23.5 | 60 | 61 | 272 | 5.73 | 6 |  | 11.73 | 0.20821 | 0.48849 | 22.1884 | 13.0784 | 12.5112 | 471.871 | 229.5513 | 466.7663 | 2.3977 | 58.1023 | 0.21533 | 7.6 | 7.3 | 7.7 | 213 | 355 | 326 | 487.6775 | -49.5943 | 39.7454 | 484.7843 | 56.0629 | BMRL | 0.17 | 0.306 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-03-21 | 21:45 | 107.75 | 23.5 | 60 | 61 | 272 | 5.66 | 5.94 |  | 11.6 | 0.20821 | 0.48793 | 22.4483 | 12.9186 | 12.3584 | 471.6698 | 229.4843 | 466.6302 | 2.3967 | 58.1033 | 0.2127 | 7.7 | 7.3 | 7.8 | 217 | 356 | 353 | 483.5657 | -36.9874 | 38.6139 | 480.7922 | 54.8662 | BMRL | 0.17 | 0.297 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-21 | 22:30 | 108.5 | 23.5 | 60 | 61 | 272 | 5.47 | 5.8 |  | 11.27 | 0.20821 | 0.48536 | 23.1349 | 12.485 | 11.9435 | 470.786 | 229.1382 | 465.9264 | 2.3922 | 58.1078 | 0.20554 | 7.6 | 7.3 | 7.8 | 221 | 355 | 328 | 478.4612 | -45.8723 | 37.4823 | 475.8724 | 53.559 | BMRL | 0.17 | 0.298 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 9:45 | 119.75 | 23.5 | 60 | 61 | 272 | 5.25 | 3.75 |  | 9 | 0.20821 | 0.58333 | 29.2222 | 11.9828 | 11.4632 | 504.493 | 245.6479 | 499.4969 | 2.5635 | 57.9365 | 0.19786 | 7.6 | 7.3 | 7.7 | 248 | 354 | 382 | 501.2 | -31.2042 | 29.8444 | 498.7564 | 50.2763 | BMRL | 0.17 | 0.317 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 10:00 | 120 | 23.5 | 60 | 61 | 272 | 5.49 | 11.4 |  | 16.89 | 0.20821 | 0.32504 | 15.1042 | 12.5306 | 11.9872 | 424.2917 | 206.5008 | 419.8959 | 2.1559 | 58.3441 | 0.20546 | 7.6 | 7.3 | 7.7 | 268 | 355 | 398 | 394.675 | 0.83543 | 24.1867 | 393.3966 | 31.8754 | 0.009 | 0.17 | 0.377 | 0.24679 | 34.5376 | 94.6903 | 0.24439 | 96.3174
[44 empty] | 1999-03-22 | 10:30 | 120.5 | 23.5 | 60 | 61 | 272 | 5.54 | 12.1 |  | 17.64 | 0.20821 | 0.31406 | 14.4195 | 12.6448 | 12.0964 | 421.4467 | 205.0964 | 417.0402 | 2.1415 | 58.3585 | 0.20728 | 7.6 | 7.4 | 7.6 | 210 | 356 | 421 | 419.2017 | 0.42716 | 40.5941 | 417.0712 | 49.6489 | BMRL | 0.17 | 0.262 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 11:15 | 121.25 | 23.5 | 60 | 61 | 272 | 5.5 | 13.15 |  | 18.65 | 0.20821 | 0.29491 | 13.5845 | 12.5535 | 12.009 | 416.5584 | 202.7332 | 412.2347 | 2.1166 | 58.3834 | 0.20569 | 7.7 | 7.3 | 7.8 | 227 | 355 | 392 | 406.4087 | -3.6757 | 35.785 | 404.5949 | 43.8945 | BMRL | 0.17 | 0.24 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 12:15 | 122.25 | 23.5 | 60 | 61 | 272 | 5.6 | 12.7 |  | 18.3 | 0.20821 | 0.30601 | 13.8634 | 12.7817 | 12.2274 | 419.3896 | 204.0718 | 414.9566 | 2.131 | 58.369 | 0.20948 | 7.7 | 7.3 | 7.7 | 214 | 355 | 402 | 415.0118 | -3.2368 | 39.4625 | 412.9426 | 48.1768 | BMRL | 0.169 | 0.227 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 13:15 | 123.25 | 23.5 | 60 | 61 | 272 | 5.6 | 11.73 |  | 17.33 | 0.20821 | 0.32314 | 14.6953 | 12.7817 | 12.2274 | 423.8112 | 206.2232 | 419.3314 | 2.1535 | 58.3465 | 0.20956 | 7.7 | 7.3 | 7.7 | 226 | 355 | 356 | 414.3696 | -16.3959 | 36.0679 | 412.4305 | 45.2029 | BMRL | 0.17 | 0.244 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 14:00 | 124 | 23.5 | 60 | 61 | 272 | 5.67 | 15.6 |  | 21.27 | 0.20821 | 0.26657 | 11.788 | 12.9415 | 12.3802 | 409.5597 | 199.2617 | 405.1759 | 2.0811 | 58.4189 | 0.21192 | 7.7 | 7.3 | 7.8 | 235 | 354 | 391 | 396.5702 | -1.4246 | 33.5219 | 394.8862 | 40.4892 | BMRL | 0.17 | 0.219 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 15:30 | 125.5 | 23.5 | 60 | 61 | 272 | 5.73 | 14.07 |  | 19.8 | 0.20821 | 0.28939 | 12.7374 | 13.0784 | 12.5112 | 415.2045 | 201.9847 | 410.7128 | 2.1097 | 58.3903 | 0.21427 | 7.6 | 7.3 | 7.7 | 212 | 354 | 401 | 411.1258 | -2.5251 | 40.0283 | 409.0284 | 48.1699 | BMRL | 0.17 | 0.231 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 16:15 | 126.25 | 23.5 | 60 | 61 | 272 | 5.67 | 13.87 |  | 19.54 | 0.20821 | 0.29017 | 12.9202 | 12.9415 | 12.3802 | 415.392 | 202.0993 | 410.9458 | 2.1107 | 58.3893 | 0.21203 | 7.6 | 7.3 | 7.7 | 223 | 354 | 387 | 406.8479 | -5.1286 | 36.9165 | 404.9317 | 44.929 | BMRL | 0.17 | 0.234 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 17:00 | 127 | 23.5 | 60 | 61 | 272 | 5.67 | 12.93 |  | 18.6 | 0.20821 | 0.30484 | 13.6237 | 12.9415 | 12.3802 | 419.1003 | 203.9035 | 414.6144 | 2.1295 | 58.3705 | 0.2121 | 7.7 | 7.3 | 7.8 | 198 | 354 | 312 | 421.6891 | -35.1568 | 43.9887 | 419.3576 | 52.7849 | BMRL | 0.17 | 0.241 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 18:00 | 128 | 23.5 | 60 | 61 | 272 | 5.6 | 12 |  | 17.6 | 0.20821 | 0.31818 | 14.4545 | 12.7817 | 12.2274 | 422.5219 | 205.5959 | 418.0558 | 2.1469 | 58.3531 | 0.20954 | 7.8 | 7.4 | 7.9 | 228 | 354 | 310 | 412.0667 | -32.9247 | 35.5021 | 410.1719 | 44.4135 | BMRL | 0.17 | 0.246 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-22 | 18:30 | 128.5 | 23.5 | 60 | 61 | 272 | 5.6 | 13.87 |  | 19.47 | 0.20821 | 0.28762 | 12.9702 | 12.7817 | 12.2274 | 414.7442 | 201.8113 | 410.3603 | 2.1074 | 58.3926 | 0.2094 | 7.7 | 7.4 | 7 | 221 | 355 | 302 | 406.9968 | -34.7671 | 37.4823 | 405.0821 | 45.4432 | BMRL | 0.17 | 0.236 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 9:30 | 119.5 | 23.5 | 60 | 61 | 272 | 5.55 | 11.1 | X | 16.65 | 0.20821 | 0.33333 | 15.3363 | 12.6676 | 12.1182 | 426.4792 | 207.5415 | 422.012 | 2.167 | 58.333 | 0.20774
[44 empty] | 1999-03-23 | 12:00 |  | 23.5 | 60 | 61 | 272 | 5.77 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 13.1697 | 12.5986 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 12:30 |  | 23.5 | 70 | 71 | 272 | 6.63 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 15.1326 | 14.4763 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 13:30 |  | 23.5 | 51 | 52 | 272 | 4.86 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 11.0927 | 10.6116 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 13:15 |  | 23.5 | 60 | 61 | 272 | 5.77 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 13.1697 | 12.5986 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 14:30 |  | 23.5 | 60 | 61 | 272 | 6.3 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 14.3794 | 13.7558 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 15:00 |  | 23.5 | 70 | 71 | 272 | 7.4 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 16.8901 | 16.1576 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 15:15 |  | 23.5 | 50 | 51 | 272 | 5.05 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 11.5264 | 11.0265 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-23 | 15:30 |  | 23.5 | 60 | 61 | 272 | 6.4 | NA |  | #VALUE! | 0.20821 | #VALUE! | #VALUE! | 14.6077 | 13.9741 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: Alison Gusses: NTR7450 membrane was used during quarters 1 and 2; NF200B membrane was used during quarters 3 and 4.
Note on R5: Gary Puetz: Contractor confirmed potential foulants were not measured during the study because they were not required under the ICR.
Note on X11: Gary Puetz: Consultant verified the water quality parameter, but did not explain why the mass balance error was high. No changes were made.
Note on X26: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on X36: Gary Puetz: The consultant did verify the difference in MBAA concentrations. No changes were made.
Note on CY16: Gary Puetz: Consultant verified the water quality parameter, but did not explain why the mass balance error was high. No changes were made.
Note on CY31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DL16: Gary Puetz: Consultant verified the water quality parameter, but did not explain why the mass balance error was high. No changes were made.
Note on DL31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on DV16: Gary Puetz: Consultant verified the water quality parameter, but did not explain why the mass balance error was high. No changes were made.
Note on DV31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.
Note on EF16: Gary Puetz: Consultant verified the water quality parameter, but did not explain why the mass balance error was high. No changes were made.
Note on EF31: Gary Puetz: SDS incubation times reflect the seasonal variations of the full scale distribution system.

## SR40. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.76389 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.88 | [7 empty] | Recovery during sample collection (decimal) | 0.56 | [7 empty] | Recovery during sample collection (decimal) | 0.33 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 3.3 mg/L | plant | Sampling date | MM/DD/YY | 1998-03-18 | 1998-03-25 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.1 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.51 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.41 | [7 empty] | Feed flow rate during sample collection (mL/min) | 17 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24 |  |  | LSI | Coagulation | 123 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 9:00 | 10:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 123.8 | 123.8 | 123.8 | 123.8 | SDS-THM4F, ug/L | 123.8 | 123.8 | 123.8 | 123.8 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 210 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.54 mg/L | plant | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 19.25 | 23.3 | 15.6 | 13 | SDS-THM4p, ug/L | 19.25 | 23.3 | 15.6 | 13 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 6.9 | 7.8 | 7.35 | 12.2449 | 1998-03-17 | 8:00 | 0 | 22 | 62 | 61 | 263 | 6.2 | 5.1 | 11.3 | 0.18158 | 0.54867 | 22.2743 | 14.1512 | 15.013 | 0 | 0 | 0 | 0 | 61.5 | 0.24411 | 1998-03-18 | 7:00 | 0 | 22 | 62 | 60 | 263 | 6.67 | 3.6 |  | 10.27 | 0.18158 | 0.64946 | 24.6086 | 15.2239 | 16.1511 | 429.2353 | 99.3707 | 420.8696 | 3.2568 | 57.7432 | 0.2797 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 90.75 | 90.75 | 90.75 | 90.75 | SDS-HAA5F, ug/L | 90.75 | 90.75 | 90.75 | 90.75 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23301 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 23 | 23 | 0 | 1998-03-17 | 9:00 | 1 | 22 | 62 | 61 | 263 | 6.4 | 1.63 | 8.03 | 0.18158 | 0.79701 | 31.7522 | 14.6077 | 15.4973 | 0 | 0 | 0 | 0 | 61.5 | 0.25199 | 1998-03-18 | 8:00 | 1 | 22 | 62 | 60 | 263 | 6.55 | 3.43 |  | 9.98 | 0.18158 | 0.65631 | 25.3527 | 14.95 | 15.8605 | 433.7453 | 100.4509 | 425.4446 | 3.2914 | 57.7086 | 0.27484 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 4.85 | 5.2 | 3.9 | 3.7 | SDS-HAA5p, ug/L | 4.85 | 5.2 | 3.9 | 3.7 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 40 | 46 | 43 | 13.9535 | 1998-03-17 | 10:00 | 2 | 22 | 62.5 | 62 | 263 | 6.4 | 3.75 | 10.15 | 0.18158 | 0.63054 | 24.9113 | 14.6077 | 15.4973 | 0 | 0 | 0 | 0 | 62.25 | 0.24895 | 1998-03-18 | 9:00 | 2 | 22 | 62 | 61 | 263 | 6.13 | 2.55 |  | 8.68 | 0.18158 | 0.70622 | 29.2995 | 13.9914 | 14.8435 | 469.9062 | 108.9623 | 461.4934 | 3.5674 | 57.9326 | 0.25622 | 6.67 |  |  | 72 | 205 | 220 | 558.7608 | -153.9822 | 66.5116 | 553.0881 | 86.9822 | [16 empty] | Sampling date | MM/DD/YY | 1998-03-19 | 1998-03-19 | --- | --- | 1998-03-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-21 | 1998-03-21 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-22 | 1998-03-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-03-22 | 1998-03-22 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 540 | 540 | 540 | 540 | SDS-TOXF, ug Cl- /L | 540 | 540 | 540 | 540 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 213 | 217 | 215 | 1.8605 | 1998-03-17 | 11:00 | 3 | 22 | 62 | 62 | 263 | 6.5 | 3 | 9.5 | 0.18158 | 0.68421 | 26.6842 | 14.8359 | 15.7394 | 0 | 0 | 0 | 0 | 62 | 0.25386 | 1998-03-18 | 9:30 | 2.5 | 22 | 62.5 | 61.5 | 263 | 6.11 | 2.44 |  | 8.55 | 0.18158 | 0.71462 | 29.7602 | 13.9457 | 14.795 | 476.6161 | 110.5248 | 468.1111 | 3.6184 | 58.3816 | 0.25342 |  |  |  | 85.8 |  | 288 | 538.5295 | -86.9894 | 60.093 | 533.2706 | 83.9106 | BMRL |  | 0.303 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 8:00 | 18:00 | --- | --- | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:15 | 15:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:15 | 12:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 22:00 | 22:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 60 | 38 | 46 | 47 | SDS-TOXp, ug Cl- /L | 60 | 38 | 46 | 47 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 134 | 148 | 141 | 9.9291 | 1998-03-17 | 13:30 | 5.5 | 22 | 60 | 59 | 263 | 6.2 | 1.35 | 7.55 | 0.18158 | 0.82119 | 33.8344 | 14.1512 | 15.013 | 0 | 0 | 0 | 0 | 59.5 | 0.25232 | 1998-03-18 | 10:30 | 3.5 | 22 | 62.5 | 61.5 | 263 | 6.1 | 3.3 |  | 9.4 | 0.18158 | 0.64894 | 26.9787 | 13.9229 | 14.7708 | 428.6683 | 99.409 | 421.0315 | 3.2544 | 58.7456 | 0.25144 | 6.7 | 6.9 | 6.9 | 97.1 |  | 356 | 432.9364 | -21.6113 | 54.8372 | 429.0417 | 77.3682 |  | 0.128 | [14 empty] | Operation time | hh.hh | 25 | 35 | --- | --- | 25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80 | 80 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101 | 101 | --- | --- | --- | --- | --- | Cumulative time | hr | 111 | 111 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 6.095 | 6.095 | 6.095 | 6.095 | SDS-CDF, mg/L | 6.095 | 6.095 | 6.095 | 6.095 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 100 | 108 | 104 | 7.6923 | 1998-03-17 | 14:30 | 6.5 | 22 | 60 | 58 | 263 | 6 | 2.1 | 8.1 | 0.18158 | 0.74074 | 31.4691 | 13.6947 | 14.5287 | 0 | 0 | 0 | 0 | 59 | 0.24625 | 1998-03-18 | 13:00 | 6 | 22 | 62 | 61 | 263 | 6 | 2.83 |  | 8.83 | 0.18158 | 0.6795 | 28.7848 | 13.6947 | 14.5287 | 449.675 | 104.3116 | 441.796 | 3.4142 | 58.0858 | 0.25012 |  |  |  | 97 |  | 390 | 465.1767 | -19.2761 | 54.8837 | 460.9769 | 78.9577 | BMRL |  | 0.357 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.4 | 7.4 | 7.4 | 0 | 7.45 | --- | --- | --- | --- | --- | pH | --- | 7.2 | 7.6 | --- | --- | --- | --- | --- | pH | --- | 7.5 | 7.8 | --- | --- | --- | --- | --- | pH | --- | 7.6 | 7.6 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.355 | 1.44 | 1.34 | 1.31 | SDS-CDp, mg/L | 1.355 | 1.44 | 1.34 | 1.31 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 4.55 | 68.925 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.15 | 0.13 | 0.14 | 14.2857 | 1998-03-17 | 15:30 | 7.5 | 22 | 60 | 58 | 263 | 6.1 | 2.67 | 8.77 | 0.18158 | 0.69555 | 28.9886 | 13.9229 | 14.7708 | 0 | 0 | 0 | 0 | 59 | 0.25035 | 1998-03-18 | 14:30 | 7.5 | 22 | 62 | 61 | 263 | 5.9 | 2.51 |  | 8.41 | 0.18158 | 0.70155 | 30.2723 | 13.4664 | 14.2865 | 466.1335 | 108.1618 | 458.103 | 3.5396 | 57.9604 | 0.24649 | 6.65 |  |  | 99.4 |  | 404 | 486.7291 | -20.4775 | 53.7674 | 482.3845 | 79.394 | BMRL |  | 0.378 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 22 | 22 | 22 | 0 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 22 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 22 | 22 | --- | --- | --- | --- | --- | Temperature | oC | 22 | 22 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.3 | 6.3 | 6.3 | 6.3 | TOCF, mg/L | 6.3 | 6.3 | 6.3 | 6.3 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 11.55 | 75.925 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.09 | 0.07 | 0.08 | 25 | 1998-03-17 | 16:00 | 8 | 22 | 60 | 58 | 263 | 6.2 | 2.08 | 8.28 | 0.18158 | 0.74879 | 30.7633 | 14.1512 | 15.013 | 0 | 0 | 0 | 0 | 59 | 0.25446 | 1998-03-18 | 15:30 | 8.5 | 22 | 62 | 61 | 263 | 5.85 | 2.45 |  | 8.3 | 0.18158 | 0.70482 | 30.6867 | 13.3523 | 14.1655 | 468.6631 | 108.765 | 460.6577 | 3.559 | 57.941 | 0.24448 |  |  |  | 100 |  | 411 | 489.5918 | -19.1221 | 53.4884 | 485.2589 | 79.3924 | BMRL |  | 0.387 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 30 | 32 | 31 | 6.4516 | 54 | 71 | -31.4815 | 27.907 | 70.5688 | 56.0713 | Alkalinity | mg/L as CaCO3 | 38 | 56 | 79.6667 | -42.2619 | 11.6279 | 79.2826 | 52.0702 | Alkalinity | mg/L as CaCO3 | 25 | 50 | 65.9091 | -31.8182 | 41.8605 | 65.4993 | 61.8316 | Alkalinity | mg/L as CaCO3 | 24 | 46 | 52.3582 | -13.8222 | 44.186 | 52.0558 | 53.8956 | TOCp, mg/L | 0.5 | BMRL | BMRL | BMRL | TOCp, mg/L | 0.5 | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 3.15 | 67.525 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6.4 | 6.2 | 6.3 | 3.1746 | 1998-03-17 | 16:30 | 8.5 | 22 | 72 | 70 | 263 | 7.625 | 4.4 | 12.025 | 0.18158 | 0.6341 | 20.8711 | 17.4037 | 18.4635 | 0 | 0 | 0 | 0 | 71 | 0.26005 | 1998-03-19 | 7:00 | 24 | 22 | 60 | 59 | 263 | 5.6 | 4.34 |  | 9.94 | 0.18158 | 0.56338 | 25.4588 | 12.7817 | 13.5601 | 378.8788 | 87.994 | 372.685 | 2.8779 | 56.6221 | 0.23948 |  | 7 |  | 104 | 209 | 431 | 358.2258 | 16.885 | 51.6279 | 355.5192 | 70.747 | [16 empty] | Total dissolved solids | mg/L | 103 | 103 | 103 | 0 | 409.5 | 476.3333 | -16.3207 | 52.093 | 472.309 | 78.1922 | Total dissolved solids | mg/L | 119 | 730 | 919 | -25.8904 | 44.6512 | 911.6254 | 86.9464 | Total dissolved solids | mg/L | 99 | 352 | 362.6364 | -3.0217 | 53.9535 | 359.9952 | 72.4996 | Total dissolved solids | mg/L | 87 | 269 | 278.0448 | -3.3624 | 59.5349 | 276.0072 | 68.4791 | UV254 F, cm-1 | 0.123 | 0.123 | 0.123 | 0.123 | UV254 F, cm-1 | 0.123 | 0.123 | 0.123 | 0.123 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 2.55 | 66.925 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.121 | 0.125 | 0.123 | 3.252 | 1998-03-17 | 16:45 | 8.75 | 22 | 52 | 50 | 263 | 5.25 | 2.82 | 8.07 | 0.18158 | 0.65056 | 31.5898 | 11.9828 | 12.7126 | 0 | 0 | 0 | 0 | 51 | 0.24927 | 1998-03-19 | 8:00 | 25 | 22 | 60.5 | 59.5 | 263 | 5.6 | 2.87 |  | 8.47 | 0.18158 | 0.66116 | 30.0508 | 12.7817 | 13.5601 | 436.6408 | 101.4091 | 429.5028 | 3.3166 | 56.6834 | 0.23923 | [27 empty] | Total hardness | mg/L as CaCO3 | 58 | 56 | 57 | 3.5088 | 352 | 337 | 4.2614 | 59.5745 | 333.9817 | 82.9332 | Total hardness | mg/L as CaCO3 | 52 | 844 | 793.6667 | 5.9637 | 63.1206 | 786.8298 | 93.3912 | Total hardness | mg/L as CaCO3 | 61 | 304 | 242.8182 | 20.1256 | 56.7376 | 240.9967 | 74.6884 | Total hardness | mg/L as CaCO3 | 38 | 194 | 191.7313 | 1.1694 | 73.0496 | 190.0917 | 80.0097 | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 1.8906 | 2.0161 | 1.9534 | 6.425 | 1998-03-17 | 17:00 | 9 | 22 | 40 | 38 | 263 | 3.95 | 2.17 | 6.12 | 0.18158 | 0.64542 | 41.9739 | 9.0157 | 9.5647 | 0 | 0 | 0 | 0 | 39 | 0.24525 | 1998-03-19 | 9:00 | 26 | 22 | 60.5 | 59.5 | 263 | 5.6 | 2.26 |  | 7.86 | 0.18158 | 0.71247 | 32.4606 | 12.7817 | 13.5601 | 474.6123 | 110.2279 | 466.8535 | 3.605 | 56.395 | 0.24045 |  |  |  | 101 |  |  | 497.4779 |  | 53.0233 | 493.2568 | 79.5239 | BMRL |  | 0.377 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 28 | 28 | 28 | 0 | 265 | 281.3333 | -6.1635 | 73.0769 | 278.6025 | 89.9498 | Calcium hardness | mg/L as CaCO3 | 38 | 600 | 588 | 2 | 63.4615 | 582.93 | 93.4812 | Calcium hardness | mg/L as CaCO3 | NA | 212 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Calcium hardness | mg/L as CaCO3 | 22 | 146 | 144.3881 | 1.1041 | 78.8462 | 143.0827 | 84.6243 | BromideF, ug/L | 110 | 110 | 110 | 110 | BromideF, ug/L | 110 | 110 | 110 | 110 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 110 | 110 | 110 | 0 | 1998-03-17 | 17:30 | 9.5 | 22 | 61 | 59 | 263 | 6.33 | 5.07 | 11.4 | 0.18158 | 0.55526 | 22.0702 | 14.4479 | 15.3278 | 0 | 0 | 0 | 0 | 60 | 0.25546 | 1998-03-19 | 10:00 | 27 | 22 | 62 | 60.5 | 263 | 5.69 | 2.66 |  | 8.35 | 0.18158 | 0.68144 | 30.497 | 12.9871 | 13.778 | 450.9389 | 104.7017 | 443.448 | 3.4249 | 57.8251 | 0.23827 |  |  |  | 102 |  | 405 | 456.718 | -12.7699 | 52.5581 | 452.8809 | 77.4775 | [16 empty] | Turbidity | ntu | 0.05 | 0.05 | 0.05 | 0 | 0.185 | 0.35 | -89.1892 | 64.2857 | 0.34677 | 85.5811 | Turbidity | ntu | 0.05 | 0.39 | 0.8 | -105.1282 | 64.2857 | 0.79309 | 93.6955 | Turbidity | ntu | 0.05 | 0.15 | 0.25455 | -69.697 | 64.2857 | 0.2525 | 80.1977 | Turbidity | ntu | 0.05 | 0.13 | 0.18433 | -41.791 | 64.2857 | 0.1829 | 72.662 | Bromidep, ug/L | 99 | 110 | 96 | 100 | Bromidep, ug/L | 99 | 110 | 96 | 100 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 7 | 7 | 7 | 0 | 1998-03-18 | 7:00 | 23 | 22 | 62 | 60 | 263 | 6.67 | 3.6 | 10.27 | 0.18158 | 0.64946 | 24.6086 | 15.2239 | 16.1511 | 0 | 0 | 0 | 0 | 61 | 0.26477 | 1998-03-19 | 11:30 | 28.5 | 22 | 61 | 60 | 263 | 5.65 | 2.22 |  | 7.87 | 0.18158 | 0.71792 | 32.418 | 12.8958 | 13.6812 | 479.0618 | 111.2447 | 471.1601 | 3.6387 | 56.8613 | 0.24061 | 6.67 | 6.95 | 6.84 | 102 |  | 415 | 502.5901 | -21.106 | 52.5581 | 498.2872 | 79.5299 | BMRL | 0.126 | 0.39 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.08 | 0.08 | 0.08 | 0 | NA | 0.08 | #VALUE! | 0 | 0.08 | 0 | Ammonia | mg NH3-N / L | 0.07 | NA | 0.15333 | #VALUE! | 12.5 | 0.15257 | 54.118 | Ammonia | mg NH3-N / L | 0.08 | NA | 0.08 | #VALUE! | 0 | 0.08 | 0 | Ammonia | mg NH3-N / L | 0.08 | NA | 0.08 | #VALUE! | 0 | 0.08 | 0 | AlkF, mg/L CaCO3 | 43 | 43 | 43 | 43 | AlkF, mg/L CaCO3 | 43 | 43 | 43 | 43
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.89 | 0.92 | 0.905 | 3.3149 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-19 | 13:00 | 30 | 22 | 60.5 | 59.5 | 263 | 5.65 | 2.29 |  | 7.94 | 0.18158 | 0.71159 | 32.1234 | 12.8958 | 13.6812 | 473.9302 | 110.0531 | 466.113 | 3.5997 | 56.4003 | 0.24257 | 6.63 |  |  | 104 |  | 416 | 488.8646 | -17.5155 | 51.6279 | 484.7306 | 78.5448 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | 0.5 | 0.5 | #VALUE! | 19.35 | 19.8333 | -2.4978 | 92.0635 | 19.6249 | 97.4522 | Total organic carbon | mg/L | BMRL | 45.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 14.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 9.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 31 | 38 | 25 | 24 | Alkp, mg/L CaCO3 | 31 | 38 | 25 | 24
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 6.11 | 6.08 | 6.095 | 0.49221 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-19 | 14:30 | 31.5 | 22 | 60.5 | 59.5 | 263 | 5.6 | 1.99 |  | 7.59 | 0.18158 | 0.73781 | 33.6509 | 12.7817 | 13.5601 | 495.914 | 115.1752 | 487.807 | 3.7669 | 56.2331 | 0.24114 |  |  |  | 103 |  | 430 | 530.1759 | -23.2967 | 52.093 | 525.628 | 80.4044 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.38 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | BMRL | 0.974 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.295 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.19 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 141 | 141 | 141 | 141 | T-HdF, mg/L CaCO3 | 141 | 141 | 141 | 141
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-19 | 15:30 | 32.5 | 22 | 61 | 60 | 263 | 5.8 | 2.52 |  | 8.32 | 0.18158 | 0.69712 | 30.6106 | 13.2382 | 14.0444 | 462.6721 | 107.3907 | 454.837 | 3.5136 | 56.9864 | 0.24645 | [27 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.9638 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.1549 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.0068 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.0652 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 57 | 52 | 61 | 38 | T-Hdp, mg/L CaCO3 | 57 | 52 | 61 | 38
Process Train Name | Enhanced Coagulation/Lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8 | 7.9 | 7.95 | 1.2579 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-19 | 17:30 | 34.5 | 22 | 60.5 | 60 | 263 | 5.67 | 2.73 |  | 8.4 | 0.18158 | 0.675 | 30.3095 | 12.9415 | 13.7296 | 446.3036 | 103.6316 | 438.9159 | 3.3898 | 56.8602 | 0.24146 | [27 empty] | Bromide | mg/L | 99 | 99 | 99 | 0 | --- | 135.6667 | --- | 10 | 135.2714 | 26.8138 | Bromide | mg/L | 110 | --- | 110 | --- | 0 | 110 | 0 | Bromide | mg/L | 96 | --- | 127.8182 | --- | 12.7273 | 127.4994 | 24.7055 | Bromide | mg/L | 100 | --- | 114.9254 | --- | 9.0909 | 114.7662 | 12.8663 | Ca-HdF, mg/L CaCO3 | 104 | 104 | 104 | 104 | Ca-HdF, mg/L CaCO3 | 104 | 104 | 104 | 104
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-20 | 8:10 | 49.1667 | 22 | 60.5 | 59.5 | 263 | 5.68 | 2.58 |  | 8.26 | 0.18158 | 0.68765 | 30.8402 | 12.9643 | 13.7538 | 455.4926 | 105.7622 | 447.9395 | 3.4595 | 56.5405 | 0.24326 | 6.7 |  |  | 100 |  | 401 | 468.1783 | -16.7527 | 53.4884 | 464.2025 | 78.4577 | BMRL |  | 0.36 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 28 | 38 | NA | 22 | Ca-Hdp, mg/L CaCO3 | 28 | 38 | NA | 22
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 560 | 520 | 540 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-20 | 10:00 | 51 | 22 | 60 | 59 | 263 | 5.63 | 2.53 |  | 8.16 | 0.18158 | 0.68995 | 31.2304 | 12.8502 | 13.6327 | 457.1796 | 106.1697 | 449.6656 | 3.4725 | 56.0275 | 0.24332 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.16 | 1.13 | 1.145 | 2.6201 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.56 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.16 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.19 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 74 | 81 | 77.5 | 9.0323 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-20 | 11:10 | 52.1667 | 22 | 60 | 59 | 263 | 5.6 | 2.5 |  | 8.1 | 0.18158 | 0.69136 | 31.4691 | 12.7817 | 13.5601 | 458.2182 | 106.4204 | 450.7275 | 3.4805 | 56.0195 | 0.24206 | 6.8 | 6.7 | 6.8 | 99 | 206 | 398 | 474.84 | -19.3065 | 53.9535 | 470.8387 | 78.9737 | BMRL | 0.123 | 0.356 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 1.34 | 1.37 | 1.355 | 2.214 | --- | 17.155 | --- | 77.7687 | 16.9847 | 92.0222 | SDS-Cl2 demand | mg/L | 1.44 | --- | 40.2317 | --- | 76.3741 | 39.8741 | 96.3886 | SDS-Cl2 demand | mg/L | 1.34 | --- | 12.1468 | --- | 78.0148 | 12.0386 | 88.8691 | SDS-Cl2 demand | mg/L | 1.31 | --- | 8.4518 | --- | 78.507 | 8.3756 | 84.3594 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 35 | 33 | 34 | 5.8824 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-20 | 13:20 | 54.3333 | 22 | 59.5 | 58 | 263 | 5.55 | 2.65 |  | 8.2 | 0.18158 | 0.67683 | 31.0732 | 12.6676 | 13.439 | 447.5561 | 103.9597 | 440.3053 | 3.3997 | 55.3503 | 0.2428 | [27 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 49.5457 | 51.5423 | 47.8743 | 46.7509 | Qp/QT (THM4), % | 83.979 | 87.3632 | 81.146 | 79.2419
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 12 | 12 | 12 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-20 | 15:20 | 56.3333 | 22 | 59.5 | 58 | 263 | 5.53 | 2.6 |  | 8.13 | 0.18158 | 0.6802 | 31.3493 | 12.6219 | 13.3906 | 449.9689 | 104.5264 | 442.7054 | 3.4181 | 55.3319 | 0.24201 | 6.7 |  |  | 111 |  | 395 | 436.2 | -10.4304 | 48.3721 | 432.7811 | 74.3519 | BMRL |  | 0.352 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | 0.6 | 0.6 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-20 | 16:50 | 57.8333 | 22 | 59.5 | 58 | 263 | 5.55 | 2.2 |  | 7.75 | 0.18158 | 0.71613 | 32.9355 | 12.6676 | 13.439 | 477.549 | 110.9265 | 469.8123 | 3.6275 | 55.1225 | 0.2438 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 48.1903 | 46.6556 | 49.1712 | 50.0533 | SDS-HAA5b, ug/L | 18.6121 | 16.0108 | 20.2747 | 21.7699
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 121 | 126.6 | 123.8 | 4.5234 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 11:00 | 76 | 22 | 59.5 | 58 | 263 | 5.6 | 2.5 |  | 8.1 | 0.18158 | 0.69136 | 31.4691 | 12.7817 | 13.5601 | 458.2182 | 106.4204 | 450.7275 | 3.4805 | 55.2695 | 0.24535 | 6.8 | 6.8 | 6.8 | 108 | 207 | 399 | 454.68 | -13.9549 | 49.7674 | 450.9891 | 76.0526 | BMRL | 0.124 | 0.358 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | 52 | 68 | 60 | 26.6667 | --- | 1660 | --- | 88.8889 | 1642.7529 | 96.3476 | SDS-TOX | mg Cl- /L | 38 | --- | 4221.3333 | --- | 92.963 | 4182.7703 | 99.0915 | SDS-TOX | mg Cl- /L | 46 | --- | 1168.7273 | --- | 91.4815 | 1157.4795 | 96.0258 | SDS-TOX | mg Cl- /L | 47 | --- | 782.8209 | --- | 91.2963 | 774.9731 | 93.9353 | SDS-TOXb, ug Cl- /L | 302.1808 | 281.2577 | 303.5009 | 309.5181 | SDS-TOXb, ug Cl- /L | 136.901 | 101.4368 | 139.1386 | 149.3375
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 5.4 | 5.1 | 5.25 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 12:00 | 77 | 22 | 59.5 | 58 | 263 | 5.6 | 2.6 |  | 8.2 | 0.18158 | 0.68293 | 31.0732 | 12.7817 | 13.5601 | 451.9828 | 104.9723 | 444.594 | 3.4332 | 55.3168 | 0.24514 | 6.7 | 6.9 |  | 106 |  | 394 | 449.7692 | -14.1546 | 50.6977 | 446.1093 | 76.239 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 3.4 | 3.1 | 3.25 | 9.2308 | --- | 250.75 | --- | 95.8065 | 248.0821 | 98.6899 | SDS-CHCl3 | mg/L | 2.4 | --- | 628.2333 | --- | 96.9032 | 622.4642 | 99.6144 | SDS-CHCl3 | mg/L | 2.6 | --- | 172.8273 | --- | 96.6452 | 171.1219 | 98.4806 | SDS-CHCl3 | mg/L | 2.2 | --- | 114.5881 | --- | 97.1613 | 113.3894 | 98.0598 | SDS-CDb, mg/L | 3.7465 | 3.6957 | 3.8186 | 3.858 | SDS-CDb, mg/L | 2.1144 | 2.0282 | 2.2365 | 2.3033
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 35 | 36 | 35.5 | 2.8169 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 13:00 | 78 | 22 | 59.5 | 58 | 263 | 5.6 | 2.6 |  | 8.2 | 0.18158 | 0.68293 | 31.0732 | 12.7817 | 13.5601 | 451.9828 | 104.9723 | 444.594 | 3.4332 | 55.3168 | 0.24514 | [27 empty] | SDS-BDCM | mg/L | 4.6 | 4.1 | 4.35 | 11.4943 | --- | 103.1833 | --- | 87.2059 | 102.118 | 95.7402 | SDS-BDCM | mg/L | 4.3 | --- | 251.8 | --- | 87.3529 | 249.5185 | 98.2767 | SDS-BDCM | mg/L | 3.4 | --- | 72.9455 | --- | 90 | 72.2487 | 95.294 | SDS-BDCM | mg/L | 2.9 | --- | 49.3179 | --- | 91.4706 | 48.8228 | 94.0602 | TOCb, mg/L | 3.4264 | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | 1.4292 | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 48 | 42 | 45 | 13.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 13:15 | 78.25 | 22 | 60 | 58 | 263 | 5.25 | 1.14 |  | 6.39 | 0.18158 | 0.8216 | 40.1581 | 11.9828 | 12.7126 | 581.9977 | 135.3091 | 573.0809 | 4.4223 | 54.5777 | 0.23293 |  |  |  | 112 |  |  | 689.3421 |  | 47.907 | 683.5797 | 83.6157 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 7.6 | 6.9 | 7.25 | 9.6552 | --- | 23.0833 | --- | 39.5833 | 22.9127 | 68.3581 | SDS-DBCM | mg/L | 9 | --- | 34 | --- | 25 | 33.7695 | 73.3488 | SDS-DBCM | mg/L | 5.4 | --- | 20.4 | --- | 55 | 20.2497 | 73.333 | SDS-DBCM | mg/L | 4.7 | --- | 15.5955 | --- | 60.8333 | 15.4793 | 69.6369 | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | 2 | 1.8 | 1.9 | 10.5263 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 13:30 | 78.5 | 22 | 60 | 58 | 263 | 5.25 | 0.86 |  | 6.11 | 0.18158 | 0.85925 | 42.0442 | 11.9828 | 12.7126 | 631.3876 | 146.7918 | 621.7141 | 4.7976 | 54.2024 | 0.23454 | 6.7 |  |  | 118 |  |  | 807.1512 |  | 45.1163 | 800.2728 | 85.255 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 4.5 | 4.3 | 4.4 | 4.5455 | --- | -8.2667 | --- | -633.3333 | -8.1301 | 154.1197 | SDS-CHBr3 | mg/L | 7.6 | --- | -50.7333 | --- | -1166.6667 | -50.1956 | 115.1408 | SDS-CHBr3 | mg/L | 4.2 | --- | -3.9818 | --- | -600 | -3.8999 | 207.6964 | SDS-CHBr3 | mg/L | 3.2 | --- | -0.6806 | --- | -433.3333 | -0.63921 | 600.6188 | Bromideb, ug/L | 104.55 | 110 | 103.2976 | 105.3249 | Bromideb, ug/L | 100.7623 | 110 | 98.6396 | 102.0758
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 2.9 | 3.3 | 3.1 | 12.9032 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 13:45 | 78.75 | 22 | 60 | 58 | 263 | 5.18 | 0.83 |  | 6.01 | 0.18158 | 0.8619 | 42.7604 | 11.8231 | 12.5431 | 635.1027 | 147.6863 | 625.5026 | 4.8262 | 54.1738 | 0.23153 |  |  |  | 113 |  |  | 851.5783 |  | 47.4419 | 844.3049 | 86.6162 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 20.1 | 18.4 | 19.25 | 8.8312 | --- | 367.75 | --- | 84.4507 | 363.9934 | 94.7114 | SDS-THM4 | mg/L | 23.3 | --- | 860.8 | --- | 81.1793 | 853.0797 | 97.2687 | SDS-THM4 | mg/L | 15.6 | --- | 261.5091 | --- | 87.399 | 259.0455 | 93.9779 | SDS-THM4 | mg/L | 13 | --- | 178.3731 | --- | 89.4992 | 176.6094 | 92.6391 | Alkb, mg/L CaCO3 | 37.0545 | 40.4229 | 34.3826 | 34.1173 | Alkb, mg/L CaCO3 | 32.9225 | 38.6318 | 28.3937 | 27.944
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 14 | 14 | 14 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 14:00 | 79 | 22 | 60 | 58 | 263 | 5.18 | 0.8 |  | 5.98 | 0.18158 | 0.86622 | 42.9799 | 11.8231 | 12.5431 | 641.3899 | 149.1483 | 631.6948 | 4.8739 | 54.1261 | 0.23174 |  |  | 6.75 | 112 |  |  | 881.925 |  | 47.907 | 874.3428 | 87.1904 |  | 0.124 | [14 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 99.3816 | 95.1274 | 102.7006 | 92.8466 | T-Hdb, mg/L CaCO3 | 70.4577 | 63.2468 | 76.0832 | 59.3809
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 14:15 | 79.25 | 22 | 60 | 58 | 263 | 5.2 | 0.77 |  | 5.97 | 0.18158 | 0.87102 | 43.0536 | 11.8687 | 12.5915 | 648.542 | 150.8024 | 638.7007 | 4.9282 | 54.0718 | 0.23287 |  |  |  | 112 | 208 |  | 910.5844 |  | 47.907 | 902.6897 | 87.5926 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | 1.3 | 1.5 | 1.4 | 14.2857 | --- | 115.0667 | --- | 96.0563 | 113.8414 | 98.7702 | SDS-DCAA* | mg/L | 1.1 | --- | 287.7667 | --- | 96.9014 | 285.1241 | 99.6142 | SDS-DCAA* | mg/L | 1.1 | --- | 79.2818 | --- | 96.9014 | 78.4986 | 98.5987 | SDS-DCAA* | mg/L | 1 | --- | 52.4925 | --- | 97.1831 | 51.9433 | 98.0748 | Ca-Hdb, mg/L CaCO3 | 66.3453 | 69.9821 | #VALUE! | 65.6643 | Ca-Hdb, mg/L CaCO3 | 40.176 | 46.3403 | #VALUE! | 39.0217
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 6.3 | 5.8 | 6.05 | 8.2645 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 14:45 | 79.75 | 22 | 60 | 58 | 263 | 5.22 | 0.71 |  | 5.93 | 0.18158 | 0.88027 | 43.3508 | 11.9144 | 12.64 | 662.7558 | 154.0983 | 652.66 | 5.0361 | 53.9639 | 0.23423 | 6.7 |  |  | 112 |  |  | 972.2676 |  | 47.907 | 963.7303 | 88.3785 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | 1.3 | 1.4 | 1.35 | 7.4074 | --- | 146.85 | --- | 97 | 145.2816 | 99.0708 | SDS-TCAA* | mg/L | 1.3 | --- | 365.4667 | --- | 97.1111 | 362.1097 | 99.641 | SDS-TCAA* | mg/L | 1.2 | --- | 100.7455 | --- | 97.3333 | 99.7482 | 98.797 | SDS-TCAA* | mg/L | 1.2 | --- | 66.5731 | --- | 97.3333 | 65.8759 | 98.1784
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 25 | 20 | 22.5 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-21 | 15:15 | 80.25 | 22 | 60 | 58 | 263 | 5.13 | 0.71 |  | 5.84 | 0.18158 | 0.87842 | 44.0342 | 11.709 | 12.422 | 659.7644 | 153.4439 | 649.8883 | 5.0138 | 53.9862 | 0.2301 |  |  |  | 113 |  |  | 951.9859 |  | 47.4419 | 943.8034 | 88.0272 | BMRL |  | 0.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 93.3 | 88.2 | 90.75 | 5.6198 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-22 | 9:15 | 98.25 | 22 | 60 | 58 | 263 | 4.6 | 0.6 |  | 5.2 | 0.18158 | 0.88462 | 49.5769 | 10.4993 | 11.1387 | 668.8499 | 155.8022 | 659.8764 | 5.0856 | 53.9144 | 0.2066 | [27 empty] | SDS-DBAA* | mg/L | 2.2 | 2 | 2.1 | 9.5238 | --- | 5.4333 | --- | 32.2581 | 5.3974 | 61.0924 | SDS-DBAA* | mg/L | 2.8 | --- | 5.3 | --- | 9.6774 | 5.277 | 46.9391 | SDS-DBAA* | mg/L | 1.6 | --- | 5.0091 | --- | 48.3871 | 4.9749 | 67.8388 | SDS-DBAA* | mg/L | 1.5 | --- | 3.8881 | --- | 51.6129 | 3.8626 | 61.166 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 107.3 | 102.2 | 104.75 | 4.8687 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-22 | 9:30 | 98.5 | 22 | 60 | 58 | 263 | 4.65 | 0.8 |  | 5.45 | 0.18158 | 0.85321 | 47.2569 | 10.6134 | 11.2597 | 622.2742 | 144.9313 | 613.8345 | 4.7312 | 54.2688 | 0.20748 | 6.8 |  | 6.9 | 120 | 209 | 930 | 767.1875 | 17.5067 | 44.186 | 761.4662 | 84.2409 | BMRL |  | 1.408 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | 1.7 | 1.7 | 1.7 | 0 | --- | 42.7 | --- | 87.8571 | 42.258 | 95.9771 | SDS-BCAA* | mg/L | 1.9 | --- | 102.7333 | --- | 86.4286 | 101.8038 | 98.1337 | SDS-BCAA* | mg/L | 1.4 | --- | 30.0364 | --- | 90 | 29.7495 | 95.294 | SDS-BCAA* | mg/L | 1.1 | --- | 20.3537 | --- | 92.1429 | 20.1484 | 94.5405 | Qp/QT (HAA5), % | 42.7823 | 42.9573 | 42.3143 | 42.2171 | Qp/QT (HAA5), % | 74.2142 | 74.5178 | 73.4024 | 73.2338
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-22 | 9:45 | 98.75 | 22 | 60 | 58 | 263 | 4.61 | 0.9 |  | 5.51 | 0.18158 | 0.83666 | 46.7314 | 10.5221 | 11.1629 | 600.1803 | 139.8021 | 592.1105 | 4.5634 | 54.4366 | 0.20506 | [27 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.7 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 79.0711 | 80.6279 | 78.0159 | 77.0234 | SDS-THM4b, ug/L | 46.2091 | 48.9096 | 44.3786 | 42.657
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-22 | 10:00 | 99 | 22 | 60 | 58 | 263 | 4.6 | 0.95 |  | 5.55 | 0.18158 | 0.82883 | 46.3874 | 10.4993 | 11.1387 | 590.2719 | 137.4982 | 582.3526 | 4.4881 | 54.5119 | 0.20433 | [27 empty] | SDS-CDBAA | mg/L | 2.3 | 2.3 | 2.3 | 0 | --- | 14.8 | --- | 61.9835 | 14.6653 | 84.3167 | SDS-CDBAA | mg/L | 2.5 | --- | 32.0833 | --- | 58.6777 | 31.8106 | 92.141 | SDS-CDBAA | mg/L | 2 | --- | 11.2045 | --- | 66.9421 | 11.1123 | 82.002 | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-03-22 | 10:15 | 99.25 | 22 | 60 | 58.5 | 263 | 4.68 | 4.3 |  | 8.98 | 0.18158 | 0.52116 | 28.2873 | 10.6818 | 11.3324 | 358.2069 | 83.4211 | 353.3171 | 2.7234 | 56.5266 | 0.20048 | 6.87 | 6.72 |  | 120 |  | 870 | 318.3953 | 63.4028 | 44.186 | 316.6302 | 62.1009 | BMRL | 0.125 |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.7 | 1.8 | 1.75 | 5.7143 | --- | 70.9167 | --- | 92.2222 | 70.1711 | 97.5061 | SDS-DCBAA | mg/L | 1.9 | --- | 173.5667 | --- | 91.5556 | 171.9842 | 98.8952 | SDS-DCBAA | mg/L | 1.5 | --- | 49.2273 | --- | 93.3333 | 48.7491 | 96.923 | SDS-DCBAA | mg/L | 1.5 | --- | 32.8433 | --- | 93.3333 | 32.509 | 95.3859 | SDS-TOXb, ug Cl- /L | 334.6449 | 324.3542 | 330.9672 | 331.8696 | SDS-TOXb, ug Cl- /L | 183.7718 | 165.9205 | 177.3921 | 178.9575
[44 empty] | 1998-03-22 | 10:30 | 99.5 | 22 | 60 | 58.5 | 263 | 4.83 | 4.5 |  | 9.33 | 0.18158 | 0.51768 | 27.1886 | 11.0242 | 11.6956 | 356.6556 | 83.0228 | 351.6303 | 2.7112 | 56.5388 | 0.20686 |  |  |  | 112 |  | 712 | 325.5533 | 54.2762 | 47.907 | 323.5924 | 65.3886 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 4.8 | 4.9 | 4.85 | 2.0619 | --- | 291.1833 | --- | 94.6556 | 288.0968 | 98.3165 | SDS-HAA5 | mg/L | 5.2 | --- | 718.1167 | --- | 94.27 | 711.5448 | 99.2692 | SDS-HAA5 | mg/L | 3.9 | --- | 201.2864 | --- | 95.7025 | 199.3089 | 98.0432 | SDS-HAA5 | mg/L | 3.7 | --- | 133.6254 | --- | 95.9229 | 132.2397 | 97.202 | SDS-CDb, mg/L | 4.0671 | 4.0953 | 4.083 | 4.0749 | SDS-CDb, mg/L | 2.5772 | 2.6262 | 2.6047 | 2.5908
[44 empty] | 1998-03-22 | 10:45 | 99.75 | 22 | 60 | 58.5 | 263 | 4.94 | 5.13 |  | 10.07 | 0.18158 | 0.49057 | 25.1172 | 11.2753 | 11.962 | 344.7771 | 80.2315 | 339.8081 | 2.6206 | 56.6294 | 0.21123 |  |  |  | 105 |  | 616 | 320.9259 | 47.9016 | 51.1628 | 318.898 | 67.0741 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 6.5 | 6.6 | 6.55 | 1.5267 | --- | 333.8833 | --- | 93.747 | 330.3549 | 98.0173 | SDS-HAA6 | mg/L | 7.1 | --- | 820.85 | --- | 93.222 | 813.3486 | 99.1271 | SDS-HAA6 | mg/L | 5.3 | --- | 231.3227 | --- | 94.9403 | 229.0584 | 97.6862 | SDS-HAA6 | mg/L | 4.8 | --- | 153.9791 | --- | 95.4177 | 152.388 | 96.8501 | TOCb, mg/L | 3.8186 | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | 1.9956 | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-03-22 | 11:15 | 100.25 | 22 | 60 | 58.5 | 263 | 5.14 | 5.01 |  | 10.15 | 0.18158 | 0.5064 | 24.9113 | 11.7318 | 12.4462 | 351.6699 | 81.7868 | 346.3953 | 2.6725 | 56.5775 | 0.21999 | 6.8 |  |  | 99 |  | 523 | 334.01 | 36.1358 | 53.9535 | 331.7135 | 70.155 | BMRL |  | 0.547 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-03-22 | 11:45 | 100.75 | 22 | 60 | 58.5 | 263 | 5.1 | 4.88 |  | 9.98 | 0.18158 | 0.51102 | 25.3527 | 11.6405 | 12.3494 | 353.7121 | 82.2715 | 348.4485 | 2.6881 | 56.5619 | 0.21833 |  |  |  | 97 |  | 428 | 338.3197 | 20.9533 | 54.8837 | 335.9799 | 71.1292 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 105.2939 | 110 | 104.076 | 105.7783 | Bromideb, ug/L | 101.8364 | 110 | 99.7237 | 102.6766
[44 empty] | 1998-03-22 | 12:15 | 101.25 | 22 | 60 | 58.5 | 263 | 5.1 | 4.9 |  | 10 | 0.18158 | 0.51 | 25.3 | 11.6405 | 12.3494 | 353.2563 | 82.1655 | 347.9994 | 2.6846 | 56.5654 | 0.21832 |  |  |  | 97 | 208 | 420 | 337.8163 | 19.5675 | 54.8837 | 335.4814 | 71.0863 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 37.8661 | 40.8521 | 35.3834 | 34.9787 | Alkb, mg/L CaCO3 | 34.0943 | 39.2741 | 29.7876 | 29.0856
[44 empty] | 1998-03-22 | 19:30 | 108.5 | 22 | 60 | 58.5 | 263 | 5.35 | 3.47 |  | 8.82 | 0.18158 | 0.60658 | 28.8186 | 12.2111 | 12.9547 | 402.3163 | 93.507 | 396.0345 | 3.0567 | 56.1933 | 0.23054 |  |  |  | 98 |  | 356 | 395.389 | -11.0643 | 54.4186 | 392.3643 | 75.0232 | BMRL |  | 0.302 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 105.0629 | 102.768 | 107.1485 | 97.5164 | T-Hdb, mg/L CaCO3 | 78.6601 | 74.6791 | 82.2781 | 65.5692
[44 empty] | 1998-03-22 | 20:00 | 109 | 22 | 59.5 | 58 | 263 | 5.38 | 15.8 |  | 21.18 | 0.18158 | 0.25401 | 11.4174 | 12.2796 | 13.0274 | 267.0742 | 62.0682 | 262.8806 | 2.0291 | 56.7209 | 0.22968 | 6.75 |  |  | 99 |  | 341 | 254.4987 | 25.3669 | 53.9535 | 252.9083 | 60.8554 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 71.4854 | 75.6482 | #VALUE! | 69.382 | Ca-Hdb, mg/L CaCO3 | 47.5972 | 54.8182 | #VALUE! | 43.9483
[44 empty] | 1998-03-22 | 20:30 | 109.5 | 22 | 60.5 | 59 | 263 | 5.5 | 14.4 |  | 19.9 | 0.18158 | 0.27638 | 12.2161 | 12.5535 | 13.318 | 272.9027 | 63.4001 | 268.5215 | 2.0731 | 57.6769 | 0.23091 | 6.6 |  |  | 87 |  | 267 | 263.8889 | 1.1652 | 59.5349 | 262.0393 | 66.7989 | BMRL | 0.127 | 0.195 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-03-22 | 21:00 | 110 | 22 | 60.5 | 59 | 263 | 5.55 | 14.2 |  | 19.75 | 0.18158 | 0.28101 | 12.3165 | 12.6676 | 13.439 | 274.1431 | 63.6788 | 269.7018 | 2.0824 | 57.6676 | 0.23304 | 6.61 |  |  | 82 | 208 | 255 | 266.9824 | -4.699 | 61.8605 | 265.0306 | 69.0602 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-03-22 | 21:30 | 110.5 | 22 | 60.5 | 59 | 263 | 5.45 | 13.83 |  | 19.28 | 0.18158 | 0.28268 | 12.6411 | 12.4393 | 13.1969 | 274.5835 | 63.8001 | 270.2155 | 2.086 | 57.664 | 0.22886 | 6.69 |  |  | 81 |  | 252 | 267.8055 | -6.272 | 62.3256 | 265.87 | 69.534 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-03-22 | 22:00 | 111 | 22 | 60.5 | 59 | 263 | 5.5 | 13.7 |  | 19.2 | 0.18158 | 0.28646 | 12.6979 | 12.5535 | 13.318 | 275.6089 | 64.0288 | 271.1842 | 2.0937 | 57.6563 | 0.23099 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-03-23 | 7:00 | 120 | 22 | 60.5 | 59 | 263 | 5.58 | 11 |  | 16.58 | 0.18158 | 0.33655 | 14.8625 | 12.7361 | 13.5117 | 289.9067 | 67.3344 | 285.1845 | 2.2021 | 57.5479 | 0.23479 |  |  |  | 83 | 208 | 265 | 281.96 | -6.4 | 61.3953 | 279.8494 | 70.3412 | [55 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-03-23 | 7:30 | 120.5 | 22 | 60.5 | 59 | 263 | 5.58 | 10.9 |  | 16.48 | 0.18158 | 0.33859 | 14.9587 | 12.7361 | 13.5117 | 290.5209 | 67.477 | 285.7887 | 2.2068 | 57.5432 | 0.23481 | 6.6 | 6.75 |  | 84 |  |  | 282.0624 |  | 60.9302 | 279.9613 | 69.9958 | BMRL | 0.126 | 0.184 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-03-23 | 8:00 | 121 | 22 | 60.5 | 59 | 263 | 5.55 | 11 |  | 16.55 | 0.18158 | 0.33535 | 14.8912 | 12.6676 | 13.439 | 289.5435 | 67.256 | 284.8527 | 2.1994 | 57.5506 | 0.23352 |  |  |  | 84 |  |  | 281.0955 |  | 60.9302 | 279.0158 | 69.8942 | BMRL |  | 0.183 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-03-23 | 8:30 | 121.5 | 22 | 61 | 60 | 263 | 5.56 | 11 |  | 16.56 | 0.18158 | 0.33575 | 14.8816 | 12.6904 | 13.4632 | 289.6647 | 67.2822 | 284.9633 | 2.2003 | 58.2997 | 0.23093 | 6.61 |  |  | 84 |  |  | 281.2145 |  | 60.9302 | 279.1299 | 69.9065 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-03-23 | 9:00 | 122 | 22 | 61 | 60 | 263 | 5.6 | 11 | X | 16.6 | 0.18158 | 0.33735 | 14.8434 | 12.7817 | 13.5601 | 290.1487 | 67.3865 | 285.4054 | 2.2039 | 58.2961 | 0.23261 | [11 empty] | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-03-23 | 13:30 |  | 22 | 30 | 28.5 | 263 | 3.09 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 7.0528 | 7.4823 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-03-23 | 13:50 |  | 22 | 46 | 44 | 263 | 4.62 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 10.5449 | 11.1871 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-03-23 | 14:15 |  | 22 | 60 | 58.5 | 263 | 6.25 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 14.2653 | 15.134 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-03-23 | 14:35 |  | 22 | 75 | 74 | 263 | 8.07 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 18.4193 | 19.5411 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on E19: Gary Puetz: The consultant stated that the cost of an 8X40 TFC-SR membrane element was not available from the manufacturer.
Note on R5: Gary Puetz: Consultant confirmed potential foulants were not measured during the study, because they were not required under the ICR.
Note on X11: Gary Puetz: The consultant did verify the alkalinity, but did not explain the large mass balance error. No changes were made.
Note on X26: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on CY16: Gary Puetz: The consultant did verify the alkalinity, but did not explain the large mass balance error. No changes were made.
Note on CY18: Gary Puetz: The consultant did verify the permeate total hardness, but did not explain why it decreased with increasing recovery %. No changes were made. This may be indicate that the membrane was not allowed to stabilize long enough prior to operation with test water.
Note on CY31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DL16: Gary Puetz: The consultant did verify the alkalinity, but did not explain the large mass balance error. No changes were made.
Note on DL18: Gary Puetz: The consultant did verify the permeate total hardness, but did not explain why it decreased with increasing recovery %. No changes were made.
Note on DL31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DV16: Gary Puetz: The consultant did verify the alkalinity, but did not explain the large mass balance error. No changes were made.
Note on DV18: Gary Puetz: The consultant did verify the permeate total hardness, but did not explain why it decreased with increasing recovery %. No changes were made.
Note on DV31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on EF16: Gary Puetz: The consultant did verify the alkalinity, but did not explain the large mass balance error. No changes were made.
Note on EF18: Gary Puetz: The consultant did verify the permeate total hardness, but did not explain why it decreased with increasing recovery %. No changes were made.
Note on EF31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.

## SR40. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.72913 | [45 empty] | Recovery during sample collection (decimal) | 0.71 | [10 empty] | Recovery during sample collection (decimal) | 0.88 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.32 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 4.6 mg/L | plant | Sampling date | MM/DD/YY | 1998-06-24 | 1998-07-06 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 11.21 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.52 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.5 | [7 empty] | Feed flow rate during sample collection (mL/min) | 20.96 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24 |  |  | LSI | Coagulation | 127 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 9:30 | 10:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 246 | [10 empty] | Influent flow rate during sample collection (mL/min) | 246 | [7 empty] | Influent flow rate during sample collection (mL/min) | 246 | [7 empty] | Influent flow rate during sample collection (mL/min) | 246 | [6 empty] | SDS-THM4F, ug/L | 216 | 216 | 216 | 216 | SDS-THM4F, ug/L | 216 | 216 | 216 | 216 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 210 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.53 mg/L | plant | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 30.1 | 37.6 | 24.6 | 19.4 | SDS-THM4p, ug/L | 30.1 | 37.6 | 24.6 | 19.4 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 6.68 | 7.7 | 7.19 | 14.1864 | 1998-06-23 | 9:00 | 0 | 24 | [5 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-24 | 9:30 | 0 | 24 | 60 | 62 | 246 | 8.8 | 7.2 |  | 16 | 0.16984 | 0.55 | 14.375 | 20.0855 | 20.0855 | 426.8524 | 112.5753 | 415.6099 | 3.0866 | 57.9134 | 0.34682 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 100.3 | 100.3 | 100.3 | 100.3 | SDS-HAA5F, ug/L | 100.3 | 100.3 | 100.3 | 100.3 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23301 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-06-23 | 9:45 | 0.75 | 24 | 57 | 58 | 265 | 7.9 | 2.12 | 10.02 | 0.18296 | 0.78842 | 25.4471 | 18.0313 | 18.0313 | 0 | 0 | 0 | 0 | 57.5 | 0.31359 | 1998-06-24 | 10:30 | 1 | 24 | 60 | 60 | 246 | 8.23 | 4.85 |  | 13.08 | 0.16984 | 0.6292 | 17.8073 | 18.7845 | 18.7845 | 472.9708 | 124.9589 | 461.328 | 3.4219 | 56.5781 | 0.33201 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 5.75 | 7.3 | 3.8 | 3 | SDS-HAA5p, ug/L | 5.75 | 7.3 | 3.8 | 3 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 58 | 62 | 60 | 6.6667 | 1998-06-23 | 10:30 | 1.5 | 24 | 57 | 58 | 265 | 8.17 | 1.95 | 10.12 | 0.18296 | 0.80731 | 25.1858 | 18.6476 | 18.6476 | 0 | 0 | 0 | 0 | 57.5 | 0.32431 | 1998-06-24 | 11:00 | 1.5 | 24 | 60 | 60 | 246 | 8.27 | 3.68 |  | 11.95 | 0.16984 | 0.69205 | 19.5858 | 18.8758 | 18.8758 | 517.5574 | 136.7217 | 504.7545 | 3.7443 | 56.2557 | 0.33554 | 6.8 | 6.62 | 6.94 | 117 | 250 | 430 | 561.8777 | -30.6692 | 53.937 | 554.3998 | 78.8961 | BMRL | 0.122 | 0.301 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-06-25 | 1998-06-26 | --- | --- | 1998-06-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-27 | 1998-06-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-28 | 1998-06-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-29 | 1998-06-29 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 545 | 545 | 545 | 545 | SDS-TOXF, ug Cl- /L | 545 | 545 | 545 | 545 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 255 | 253 | 254 | 0.7874 | 1998-06-23 | 11:00 | 2 | 24 | 57 | 58 | 265 | 8.3 | 2.08 | 10.38 | 0.18296 | 0.79961 | 24.5299 | 18.9443 | 18.9443 | 0 | 0 | 0 | 0 | 57.5 | 0.32947 | 1998-06-24 | 11:45 | 2.25 | 24.2 | 60 | 61 | 246 | 8.63 | 3.63 |  | 12.26 | 0.16984 | 0.70392 | 19.0653 | 19.6975 | 19.5814 | 527.1581 | 139.1027 | 513.5446 | 3.8125 | 56.6875 | 0.34543 | 6.96 | 6.62 | 6.95 | 135 | 252 | 446 | 536.9118 | -20.3838 | 46.8504 | 529.8621 | 74.5217 | BMRL | 0.12 | 0.333 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 8:00 | 8:30 | --- | --- | 8:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:30 | 16:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 21:00 | 21:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 190 | 204 | 197 | 7.1066 | 1998-06-23 | 11:30 | 2.5 | 24 | 58 | 58 | 265 | 8.25 | 2.33 | 10.58 | 0.18296 | 0.77977 | 24.0473 | 18.8302 | 18.8302 | 0 | 0 | 0 | 0 | 58 | 0.32466 | 1998-06-24 | 13:00 | 3.5 | 24.2 | 60 | 61 | 246 | 8.34 | 3.53 |  | 11.87 | 0.16984 | 0.70261 | 19.7245 | 19.0356 | 18.9234 | 525.9287 | 138.9031 | 512.8076 | 3.8047 | 56.6953 | 0.33377 | 6.94 | 6.6 | 6.9 | 131 | 251 | 467 | 544.6006 | -16.6168 | 48.4252 | 537.5895 | 75.632 | BMRL | 0.119 | 0.354 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 22.5 | 47 | --- | --- | 22.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 79 | 79 | --- | --- | --- | --- | --- | Operation time | hh.hh | 107.5 | 107.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 123.5 | 123.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 7.575 | 7.575 | 7.575 | 7.575 | SDS-CDF, mg/L | 7.575 | 7.575 | 7.575 | 7.575 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 128 | 146 | 137 | 13.1387 | 1998-06-23 | 12:20 | 3.3333 | 24 | 57 | 58 | 265 | 8.38 | 4.5 | 12.88 | 0.18296 | 0.65062 | 19.5745 | 19.1269 | 19.1269 | 0 | 0 | 0 | 0 | 57.5 | 0.33264 | 1998-06-24 | 13:45 | 4.25 | 24.4 | 60 | 61 | 246 | 8.67 | 3.57 |  | 12.24 | 0.16984 | 0.70833 | 19.098 | 19.7888 | 19.5562 | 530.7663 | 140.0374 | 516.9954 | 3.8384 | 56.6616 | 0.34514 | 7.02 | 6.69 | 6.98 | 138 | 246 | 470 | 535.7143 | -13.9818 | 45.6693 | 528.7058 | 73.8985 | BMRL | 0.123 | 0.356 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.52 | 7.29 | 7.405 | 3.106 | 7.22 | --- | --- | --- | --- | --- | pH | --- | 7.49 | 7.67 | --- | --- | --- | --- | --- | pH | --- | 7.78 | 7.87 | --- | --- | --- | --- | --- | pH | --- | 7.78 | 7.45 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.06 | 2.5 | 2.22 | 2.12 | SDS-CDp, mg/L | 2.06 | 2.5 | 2.22 | 2.12 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 4.55 | 68.925 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.206 | 0.19 | 0.198 | 8.0808 | 1998-06-23 | 12:45 | 3.75 | 24 | 57 | 58 | 265 | 8.47 | 4.28 | 12.75 | 0.18296 | 0.66431 | 19.7843 | 19.3323 | 19.3323 | 0 | 0 | 0 | 0 | 57.5 | 0.33621 | 1998-06-24 | 15:00 | 5.5 | 24.4 | 60 | 61 | 246 | 8.3 | 3.48 |  | 11.78 | 0.16984 | 0.70458 | 19.8829 | 18.9443 | 18.7216 | 527.4889 | 139.3324 | 514.3925 | 3.8161 | 56.6839 | 0.33028 | 6.88 | 6.59 | 6.91 | 129 | 248 | 469 | 552.1322 | -17.7254 | 49.2126 | 544.994 | 76.33 | BMRL | 0.12 | 0.361 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 5.8 | 5.8 | 5.8 | 5.8 | TOCF, mg/L | 5.8 | 5.8 | 5.8 | 5.8 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 11.55 | 75.925 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.19 | BMRL | 0.19 | #VALUE! | 1998-06-23 | 13:30 | 4.5 | 24 | 58 | 58 | 265 | 8.5 | 3.53 | 12.03 | 0.18296 | 0.70657 | 21.0283 | 19.4008 | 19.4008 | 0 | 0 | 0 | 0 | 58 | 0.3345 | 1998-06-24 | 16:00 | 6.5 | 24.4 | 60 | 61 | 246 | 8.15 | 3.4 |  | 11.55 | 0.16984 | 0.70563 | 20.2987 | 18.6019 | 18.3833 | 528.2364 | 139.5946 | 515.3607 | 3.822 | 56.678 | 0.32435 | 6.74 | 6.67 | 6.75 | 133 | 246 | 455 | 544.0441 | -19.5701 | 47.6378 | 537.2352 | 75.2436 | BMRL | 0.12 | 0.358 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 52 | 58 | 55 | 10.9091 | 68 | 72.2414 | -6.2373 | 8.3333 | 71.9625 | 23.5713 | Alkalinity | mg/L as CaCO3 | 50 | 72 | 133.3333 | -85.1852 | 16.6667 | 132.2125 | 62.1821 | Alkalinity | mg/L as CaCO3 | 50 | 66 | 70.4082 | -6.679 | 16.6667 | 70.1226 | 28.6963 | Alkalinity | mg/L as CaCO3 | 42 | 66 | 68.4706 | -3.7433 | 30 | 68.1097 | 38.3348 | TOCp, mg/L | 0.6 | 0.7 | BMRL | BMRL | TOCp, mg/L | 0.6 | 0.7 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 3.15 | 67.525 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 5.8 | 5.8 | 5.8 | 0 | 1998-06-23 | 15:00 | 6 | 24 | 42 | 43 | 265 | 6.1 | 2.64 | 8.74 | 0.18296 | 0.69794 | 29.3204 | 13.9229 | 13.9229 | 0 | 0 | 0 | 0 | 42.5 | 0.3276 | 1998-06-24 | 17:00 | 7.5 | 24.4 | 60 | 61 | 246 | 8.3 | 3.31 |  | 11.61 | 0.16984 | 0.7149 | 20.1886 | 18.9443 | 18.7216 | 535.9385 | 141.5643 | 522.6324 | 3.8772 | 56.6228 | 0.33064 | 6.81 | 6.57 | 6.79 | 130 | 249 | 471 | 564.9366 | -19.9441 | 48.8189 | 557.5992 | 76.6858 | BMRL | 0.121 | 0.375 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 135 | 137 | 136 | 1.4706 | 480 | 542.8966 | -13.1034 | 46.4567 | 536.3142 | 74.6417 | Total dissolved solids | mg/L | 144 | 744 | 1060.6667 | -42.5627 | 43.3071 | 1048.3371 | 86.264 | Total dissolved solids | mg/L | 130 | 351 | 383.0612 | -9.1343 | 48.8189 | 379.5199 | 65.7462 | Total dissolved solids | mg/L | 116 | 296 | 318.9412 | -7.7504 | 54.3307 | 316.1746 | 63.3114 | UV254 F, cm-1 | 0.112 | 0.112 | 0.112 | 0.112 | UV254 F, cm-1 | 0.112 | 0.112 | 0.112 | 0.112 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 2.55 | 66.925 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.113 | 0.111 | 0.112 | 1.7857 | 1998-06-23 | 15:45 | 6.75 | 24 | 65 | 66 | 265 | 9.78 | 4.69 | 14.47 | 0.18296 | 0.67588 | 17.3138 | 22.3223 | 22.3223 | 0 | 0 | 0 | 0 | 65.5 | 0.3408 | 1998-06-25 | 8:00 | 22.5 | 24.4 | 60 | 62 | 246 | 8.96 | 3.13 |  | 12.09 | 0.16984 | 0.74111 | 19.3474 | 20.4507 | 20.2103 | 559.1637 | 147.3971 | 544.166 | 4.0427 | 56.9573 | 0.35483 | [27 empty] | Total hardness | mg/L as CaCO3 | 102 | 86 | 94 | 17.0213 | 457 | 449.1724 | 1.7128 | 52.2843 | 443.4268 | 78.8015 | Total hardness | mg/L as CaCO3 | 122 | 804 | 747 | 7.0896 | 38.0711 | 738.5935 | 83.4821 | Total hardness | mg/L as CaCO3 | 74 | 274 | 325.0204 | -18.6206 | 62.4365 | 321.5077 | 76.9834 | Total hardness | mg/L as CaCO3 | 52 | 212 | 265.2353 | -25.111 | 73.6041 | 262.3284 | 80.1775 | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 1.9483 | 1.9138 | 1.931 | 1.7857 | 1998-06-23 | 16:15 | 7.25 | 24 | 50 | 51 | 265 | 7.44 | 3.26 | 10.7 | 0.18296 | 0.69533 | 23.7664 | 16.9814 | 16.9814 | 0 | 0 | 0 | 0 | 50.5 | 0.33627 | 1998-06-25 | 9:00 | 23.5 | 24.5 | 60 | 62 | 246 | 8.12 | 3.26 |  | 11.38 | 0.16984 | 0.71353 | 20.6169 | 18.5335 | 18.2616 | 534.684 | 141.3116 | 521.6995 | 3.8688 | 57.1312 | 0.31964 | 6.81 | 7.57 | 6.92 | 172 | 250 | 470 | 458.2454 | 2.501 | 32.2835 | 453.5212 | 62.0745 | BMRL | 0.113 | 0.37 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 62 | 64 | 63 | 3.1746 | 314 | 318.1724 | -1.3288 | 54.0146 | 314.0445 | 79.9391 | Calcium hardness | mg/L as CaCO3 | 56 | 568 | 731 | -28.6972 | 59.1241 | 721.921 | 92.2429 | Calcium hardness | mg/L as CaCO3 | 46 | 206 | 231.7143 | -12.4827 | 66.4234 | 229.1154 | 79.9228 | Calcium hardness | mg/L as CaCO3 | 40 | 160 | 182.6471 | -14.1544 | 70.8029 | 180.7024 | 77.8642 | BromideF, ug/L | 180 | 180 | 180 | 180 | BromideF, ug/L | 180 | 180 | 180 | 180 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 180 | 180 | 180 | 0 | 1998-06-24 | 8:30 | 23.5 | 24 | 60 | 60 | 246 | 9.11 | 1.64 | 10.75 | 0.16984 | 0.84744 | 21.8837 | 20.7931 | 20.7931 | 0 | 0 | 0 | 0 | 60 | 0.34655 | 1998-06-25 | 10:00 | 24.5 | 24.5 | 60 | 62 | 246 | 8.17 | 3.45 |  | 11.62 | 0.16984 | 0.7031 | 20.1704 | 18.6476 | 18.374 | 526.2123 | 139.0511 | 513.3541 | 3.8073 | 57.1927 | 0.32127 | 6.86 | 6.71 |  | 139 | 250 |  | 526.3333 |  | 45.2756 | 519.9014 | 73.2642 | BMRL | 0.116 | 0.351 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.051 | 0.066 | 0.0585 | 25.641 | 0.156 | 0.53953 | -245.8554 | 70.4545 | 0.53175 | 88.9986 | Turbidity | ntu | 0.069 | 0.224 | 1.144 | -410.7143 | 65.1515 | 1.1295 | 93.8913 | Turbidity | ntu | 0.052 | 0.158 | 0.34996 | -121.4932 | 73.7374 | 0.34579 | 84.962 | Turbidity | ntu | 0.064 | 0.198 | 0.26106 | -31.8479 | 67.6768 | 0.25837 | 75.2296 | Bromidep, ug/L | 170 | 180 | 170 | 160 | Bromidep, ug/L | 170 | 180 | 170 | 160 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 9 | 8 | 8.5 | 11.7647 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 11:00 | 25.5 | 24.5 | 61 | 62 | 246 | 8.07 | 3.26 |  | 11.33 | 0.16984 | 0.71227 | 20.7123 | 18.4193 | 18.1491 | 533.6066 | 141.0487 | 520.7287 | 3.8612 | 57.6388 | 0.31488 | 6.97 | 6.59 | 6.95 | 139 | 249 | 457 | 538.6779 | -17.8726 | 45.2756 | 532.1222 | 73.8782 | BMRL | 0.115 | 0.359 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.17 | 0.32 | 0.245 | 61.2245 | NA | 0.055345 | #VALUE! | -28.9474 | 0.058413 | -319.428 | Ammonia | mg NH3-N / L | 0.22 | NA | -0.03 | #VALUE! | -15.7895 | -0.026637 | 925.9065 | Ammonia | mg NH3-N / L | 0.22 | NA | 0.15878 | #VALUE! | -15.7895 | 0.15963 | -37.8167 | Ammonia | mg NH3-N / L | 0.25 | NA | 0.16176 | #VALUE! | -31.5789 | 0.16297 | -53.4047 | AlkF, mg/L CaCO3 | 60 | 60 | 60 | 60 | AlkF, mg/L CaCO3 | 60 | 60 | 60 | 60
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.06 | 0.79 | 0.925 | 29.1892 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 12:00 | 26.5 | 24.7 | 61 | 62 | 246 | 7.73 | 3.3 |  | 11.03 | 0.16984 | 0.70082 | 21.3028 | 17.6433 | 17.282 | 524.1155 | 138.6855 | 512.0043 | 3.7937 | 57.7063 | 0.29948 | [27 empty] | Total organic carbon | mg/L | BMRL | 0.6 | 0.6 | #VALUE! | 19.3 | 18.531 | 3.9843 | 89.6552 | 18.241 | 96.7107 | Total organic carbon | mg/L | 0.7 | 42.3 | 43.2 | -2.1277 | 87.931 | 42.6284 | 98.3579 | Total organic carbon | mg/L | BMRL | 11.9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 8.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 55 | 50 | 50 | 42 | Alkp, mg/L CaCO3 | 55 | 50 | 50 | 42
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 7.94 | 7.21 | 7.575 | 9.637 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 13:00 | 27.5 | 24.7 | 61 | 62 | 246 | 7.93 | 3.19 |  | 11.12 | 0.16984 | 0.71313 | 21.1223 | 18.0998 | 17.7291 | 534.226 | 141.2735 | 521.5589 | 3.8662 | 57.6338 | 0.30762 | 7.04 | 6.76 | 7.03 | 139 | 248 | 472 | 539.8777 | -14.3809 | 45.2756 | 533.4164 | 73.9416 | BMRL | 0.115 | 0.362 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.375 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | BMRL | 0.778 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.219 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.158 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 197 | 197 | 197 | 197 | T-HdF, mg/L CaCO3 | 197 | 197 | 197 | 197
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 14:00 | 28.5 | 24.7 | 61 | 62 | 246 | 7.64 | 3.04 |  | 10.68 | 0.16984 | 0.71536 | 22.0337 | 17.4379 | 17.0808 | 535.8807 | 141.838 | 523.643 | 3.8792 | 57.6208 | 0.29643 | 6.97 | 6.72 | 6.94 | 136 | 244 | 466 | 550.5526 | -18.1443 | 46.4567 | 544.1153 | 75.0053 | BMRL | 0.113 | 0.371 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 1.943 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.8392 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.8403 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 1.9036 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 94 | 122 | 74 | 52 | T-Hdp, mg/L CaCO3 | 94 | 122 | 74 | 52
Process Train Name | Enhanced Coagulation/Lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 15:00 | 29.5 | 24.7 | 61 | 62 | 246 | 7.7 | 3.32 |  | 11.02 | 0.16984 | 0.69873 | 21.323 | 17.5748 | 17.2149 | 522.4431 | 138.2557 | 510.4177 | 3.7817 | 57.7183 | 0.29826 | 7.02 | 6.79 | 6.97 | 188 | 248 | 458 | 407.0723 | 11.1196 | 25.9843 | 403.6437 | 53.4243 | BMRL | 0.113 | 0.355 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 170 | 170 | 170 | 0 | --- | 204.4828 | --- | 5.5556 | 203.9249 | 16.636 | Bromide | mg/L | 180 | --- | 180 | --- | 0 | 180 | 0 | Bromide | mg/L | 170 | --- | 190.4082 | --- | 5.5556 | 190.1226 | 10.584 | Bromide | mg/L | 160 | --- | 189.4118 | --- | 11.1111 | 189.0108 | 15.3488 | Ca-HdF, mg/L CaCO3 | 137 | 137 | 137 | 137 | Ca-HdF, mg/L CaCO3 | 137 | 137 | 137 | 137
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 16:00 | 30.5 | 24.7 | 61 | 62 | 246 | 7.73 | 3.27 |  | 11 | 0.16984 | 0.70273 | 21.3636 | 17.6433 | 17.282 | 525.6401 | 139.0889 | 513.4936 | 3.8048 | 57.6952 | 0.29954 | 7.1 | 6.69 | 7.04 | 139 | 247 | 465 | 525.8502 | -13.0861 | 45.2756 | 519.7722 | 73.2575 | BMRL | 0.11 | 0.347 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 3 | 3 | 3 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 63 | 56 | 46 | 40 | Ca-Hdp, mg/L CaCO3 | 63 | 56 | 46 | 40
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 550 | 540 | 545 | 1.8349 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-25 | 18:30 | 33 | 24.7 | 61 | 62 | 246 | 7.63 | 3.2 |  | 10.83 | 0.16984 | 0.70452 | 21.7147 | 17.4151 | 17.0584 | 527.0188 | 139.4967 | 514.9993 | 3.8151 | 57.6849 | 0.29572 | [27 empty] | SDS-Free Cl2 residual | mg/L | 1.05 | 0.83 | 0.94 | 23.4043 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.78 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.88 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 140 | 130 | 135 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 8:30 | 47 | 24.7 | 60 | 62 | 246 | 7.75 | 2.48 |  | 10.23 | 0.16984 | 0.75758 | 23.0469 | 17.689 | 17.3267 | 573.528 | 151.7511 | 560.2403 | 4.1513 | 56.8487 | 0.30479 | [27 empty] | SDS-Cl2 demand | mg/L | 1.95 | 2.17 | 2.06 | 10.6796 | --- | 21.0772 | --- | 72.8053 | 20.7696 | 90.0817 | SDS-Cl2 demand | mg/L | 2.5 | --- | 44.7917 | --- | 66.9967 | 44.2228 | 94.3468 | SDS-Cl2 demand | mg/L | 2.22 | --- | 13.1486 | --- | 70.6931 | 12.9956 | 82.9173 | SDS-Cl2 demand | mg/L | 2.12 | --- | 10.1421 | --- | 72.0132 | 10.0327 | 78.8691 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 55 | 59 | 57 | 7.0175 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 9:30 | 48 | 25.4 | 60 | 62 | 246 | 7.54 | 2.67 |  | 10.21 | 0.16984 | 0.73849 | 23.094 | 17.2096 | 16.512 | 555.7572 | 147.1443 | 543.233 | 4.0235 | 56.9765 | 0.2898 | 6.83 | 6.62 | 6.89 | 138 | 253 | 511 | 581.5805 | -13.8122 | 45.6693 | 574.7826 | 75.9909 | BMRL | 0.134 | 0.409 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 77.461 | 80.7175 | 75.2351 | 73.2452 | Qp/QT (THM4), % | 96.8263 | 100.8969 | 94.0439 | 91.5565
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 22 | 22 | 22 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 10:30 | 49 | 25.4 | 60 | 62 | 246 | 7.31 | 2.8 |  | 10.11 | 0.16984 | 0.72305 | 23.3323 | 16.6847 | 16.0083 | 542.1261 | 143.6371 | 530.2848 | 3.9257 | 57.0743 | 0.28048 | 6.81 | 6.57 | 6.85 | 138 | 252 | 487 | 556.8429 | -14.3414 | 45.6693 | 550.6198 | 74.9373 | BMRL | 0.114 | 0.398 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | 2.1 | 1.9 | 2 | 10 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 11:30 | 50 | 25.4 | 60 | 62 | 246 | 7.45 | 3.05 |  | 10.5 | 0.16984 | 0.70952 | 22.4286 | 17.0042 | 16.3149 | 530.9537 | 140.6163 | 519.1325 | 3.8443 | 57.1557 | 0.28545 | 6.75 | 6.54 | 6.69 | 138 | 253 | 460 | 537.3443 | -16.814 | 45.6693 | 531.2973 | 74.0258 | BMRL | 0.114 | 0.384 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 27.0606 | 25.2327 | 27.6981 | 29.0325 | SDS-HAA5b, ug/L | 8.7508 | NA | 9.5476 | 11.2156
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 219.1 | 212.9 | 216 | 2.8704 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 13:30 | 52 | 25.4 | 60 | 62 | 246 | 7.31 | 2.9 |  | 10.21 | 0.16984 | 0.71596 | 23.094 | 16.6847 | 16.0083 | 536.1691 | 142.0588 | 524.4579 | 3.8825 | 57.1175 | 0.28027 |  |  |  | 142 | 251 | 461 | 536.3172 | -16.3378 | 44.0945 | 530.4586 | 73.2307 | BMRL | 0.116 | 0.371 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | NA | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 5.1 | 5.6 | 5.35 | 9.3458 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 15:00 | 53.5 | 25.4 | 60 | 62 | 246 | 7.53 | 2.85 |  | 10.38 | 0.16984 | 0.72543 | 22.6994 | 17.1868 | 16.4901 | 544.3158 | 144.1195 | 532.0659 | 3.9407 | 57.0593 | 0.289 |  |  |  | 147 | 249 | 471 | 536.7053 | -13.9502 | 42.126 | 530.7409 | 72.3029 | BMRL | 0.115 | 0.374 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 6.3 | 2.9 | 4.6 | 73.913 | --- | 454.2552 | --- | 96.5926 | 446.9811 | 98.9709 | SDS-CHCl3 | mg/L | 3.7 | --- | 1097.8667 | --- | 97.2593 | 1083.1497 | 99.6584 | SDS-CHCl3 | mg/L | 4.2 | --- | 271.1388 | --- | 96.8889 | 267.4033 | 98.4293 | SDS-CHCl3 | mg/L | 2.2 | --- | 197.4941 | --- | 98.3704 | 194.8318 | 98.8708 | SDS-CDb, mg/L | 3.303 | 3.4786 | 3.5462 | 3.5795 | SDS-CDb, mg/L | 2.235 | NA | 2.5389 | 2.5806
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 43 | 38 | 40.5 | 12.3457 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 16:00 | 54.5 | 25.4 | 60 | 62 | 246 | 7.33 | 2.99 |  | 10.32 | 0.16984 | 0.71027 | 22.8372 | 16.7303 | 16.0521 | 531.4869 | 140.8096 | 519.846 | 3.8486 | 57.1514 | 0.28087 |  |  |  | 141 | 250 | 466 | 531.0201 | -13.9528 | 44.4882 | 525.2094 | 73.1536 | BMRL | 0.115 | 0.366 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 6 | 5.4 | 5.7 | 10.5263 | --- | 182.5966 | --- | 90 | 179.7349 | 96.8287 | SDS-BDCM | mg/L | 6.9 | --- | 424.4 | --- | 87.8947 | 418.7845 | 98.3524 | SDS-BDCM | mg/L | 4.3 | --- | 111.851 | --- | 92.4561 | 110.346 | 96.1032 | SDS-BDCM | mg/L | 3.9 | --- | 81.9882 | --- | 93.1579 | 80.9237 | 95.1806 | TOCb, mg/L | 1.772 | 1.6834 | #VALUE! | #VALUE! | TOCb, mg/L | 0.76503 | NA | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 48 | 47 | 47.5 | 2.1053 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 17:00 | 55.5 | 25.4 | 60 | 62 | 246 | 7.6 | 2.89 |  | 10.49 | 0.16984 | 0.7245 | 22.4509 | 17.3466 | 16.6434 | 543.5641 | 143.8894 | 531.2164 | 3.935 | 57.065 | 0.29166 |  |  |  | 140 | 248 | 470 | 553.7924 | -17.8282 | 44.8819 | 547.4005 | 74.4246 | BMRL | 0.116 | 0.37 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 11 | 11 | 11 | 0 | --- | 48.931 | --- | 50 | 48.3174 | 77.2339 | SDS-DBCM | mg/L | 14 | --- | 80.6667 | --- | 36.3636 | 79.77 | 82.4495 | SDS-DBCM | mg/L | 8.5 | --- | 36.051 | --- | 61.3636 | 35.6655 | 76.1674 | SDS-DBCM | mg/L | 7.3 | --- | 28.9176 | --- | 66.8182 | 28.6229 | 74.496 | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | NA | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | 2.1 | 1.7 | 1.9 | 21.0526 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 21:00 | 59.5 | 25.4 | 60 | 62 | 246 | 7.8 | 2.34 |  | 10.14 | 0.16984 | 0.76923 | 23.2604 | 17.8031 | 17.0814 | 584.8892 | 154.7333 | 571.2501 | 4.2334 | 56.7666 | 0.30091 | [27 empty] | SDS-CHBr3 | mg/L | 7.6 | 10 | 8.8 | 27.2727 | --- | -14.6483 | --- | -340 | -14.269 | 161.6724 | SDS-CHBr3 | mg/L | 13 | --- | -78.6667 | --- | -550 | -77.4337 | 116.7886 | SDS-CHBr3 | mg/L | 7.6 | --- | -3.8286 | --- | -280 | -3.6686 | 307.1612 | SDS-CHBr3 | mg/L | 6 | --- | 0.11765 | --- | -200 | 0.19784 | -2932.779 | Bromideb, ug/L | 172.2539 | 180 | 172.4765 | 165.351 | Bromideb, ug/L | 170.3174 | NA | 170.5956 | 161.6887
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 5.1 | 5 | 5.05 | 1.9802 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 22:00 | 60.5 | 25.4 | 60 | 62 | 246 | 7.55 | 3.4 |  | 10.95 | 0.16984 | 0.6895 | 21.4658 | 17.2325 | 16.5339 | 515.1601 | 136.3915 | 503.5353 | 3.7296 | 57.2704 | 0.2887 | [27 empty] | SDS-THM4 | mg/L | 30.9 | 29.3 | 30.1 | 5.3156 | --- | 671.1345 | --- | 86.0648 | 660.7644 | 95.4447 | SDS-THM4 | mg/L | 37.6 | --- | 1524.2667 | --- | 82.5926 | 1504.2704 | 97.5004 | SDS-THM4 | mg/L | 24.6 | --- | 415.2122 | --- | 88.6111 | 409.7461 | 93.9963 | SDS-THM4 | mg/L | 19.4 | --- | 308.5176 | --- | 91.0185 | 304.5762 | 93.6305 | Alkb, mg/L CaCO3 | 56.1269 | 51.9283 | 52.4765 | 46.8159 | Alkb, mg/L CaCO3 | 55.1587 | NA | 50.5956 | 43.5198
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 19 | 18 | 18.5 | 5.4054 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-26 | 23:00 | 61.5 | 25.4 | 60 | 62 | 246 | 7.09 | 2.62 |  | 9.71 | 0.16984 | 0.73018 | 24.3347 | 16.1825 | 15.5265 | 548.1026 | 145.3189 | 536.4939 | 3.9698 | 57.0302 | 0.27225 | 7.26 | 6.8 | 7.01 | 148 | 254 | 496 | 540.8473 | -9.0418 | 41.7323 | 535.1862 | 72.3461 | BMRL | 0.112 | 0.396 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 117.2152 | 136.4619 | 104.4608 | 90.7945 | T-Hdb, mg/L CaCO3 | 97.269 | NA | 81.326 | 64.2431
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 0:00 | 62.5 | 25.4 | 60 | 62 | 246 | 6.87 | 2.72 |  | 9.59 | 0.16984 | 0.71637 | 24.6517 | 15.6804 | 15.0448 | 536.2163 | 142.2637 | 525.2145 | 3.8845 | 57.1155 | 0.26341 | 7.06 | 7.03 | 6.98 | 139 | 257 | 464 | 544.4596 | -17.3404 | 45.2756 | 538.798 | 74.2018 | BMRL | 0.113 | 0.377 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | 2.2 | 1.6 | 1.9 | 31.5789 | --- | 135.0034 | --- | 95.3086 | 132.8502 | 98.5698 | SDS-DCAA* | mg/L | 1.6 | --- | 325.7667 | --- | 96.0494 | 321.4065 | 99.5022 | SDS-DCAA* | mg/L | 1.3 | --- | 81.3 | --- | 96.7901 | 80.1805 | 98.3787 | SDS-DCAA* | mg/L | 1 | --- | 59.0882 | --- | 97.5309 | 58.2963 | 98.2846 | Ca-Hdb, mg/L CaCO3 | 79.6789 | 71.6188 | 68.5361 | 65.9522 | Ca-Hdb, mg/L CaCO3 | 65.3486 | NA | 51.4201 | 48.1902
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 7.4 | 8.6 | 8 | 15 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 1:00 | 63.5 | 25.4 | 60 | 62 | 246 | 6.97 | 2.74 |  | 9.71 | 0.16984 | 0.71782 | 24.3347 | 15.9087 | 15.2638 | 537.4877 | 142.5572 | 526.298 | 3.8934 | 57.1066 | 0.26729 | 7.02 | 6.78 | 6.94 | 138 | 258 | 462 | 549.0803 | -18.8485 | 45.6693 | 543.2567 | 74.5976 | BMRL | 0.113 | 0.38 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | 1.3 | 1 | 1.15 | 26.087 | --- | 160.9776 | --- | 97.5789 | 158.3921 | 99.274 | SDS-TCAA* | mg/L | 1.1 | --- | 387.7667 | --- | 97.6842 | 382.5658 | 99.7125 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 27 | 32 | 29.5 | 16.9492 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 2:00 | 64.5 | 25.4 | 60 | 62 | 246 | 7.05 | 2.8 |  | 9.85 | 0.16984 | 0.71574 | 23.9746 | 16.0912 | 15.4389 | 535.8073 | 142.0765 | 524.5235 | 3.8809 | 57.1191 | 0.27029 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | 1 | --- | 8.5 | --- | 47.3684 | 8.3991 | 88.094 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 103.3 | 97.3 | 100.3 | 5.9821 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 14:15 | 76.75 | 25.4 | 60 | 62 | 246 | 6.97 | 1.17 |  | 8.14 | 0.16984 | 0.85627 | 29.2211 | 15.9087 | 15.2638 | 684.93 | 181.6631 | 670.6708 | 4.9614 | 56.0386 | 0.27238 | 7.01 | 7.56 |  | 161 | 251 |  | 808.0256 |  | 36.6142 | 798.8594 | 79.8463 | BMRL | 0.114 | 0.383 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | 2.7 | 2.7 | 2.7 | 0 | --- | 10.8034 | --- | 46.5347 | 10.6724 | 74.701 | SDS-DBAA* | mg/L | 3.6 | --- | 15.6833 | --- | 28.7129 | 15.5208 | 76.8053 | SDS-DBAA* | mg/L | 2.5 | --- | 7.7041 | --- | 50.495 | 7.6313 | 67.24 | SDS-DBAA* | mg/L | 2 | --- | 6.4853 | --- | 60.396 | 6.4241 | 68.8675 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 122.3 | 115.3 | 118.8 | 5.8923 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 14:30 | 77 | 25.4 | 60 | 62 | 246 | 6.8 | 1.14 |  | 7.94 | 0.16984 | 0.85642 | 29.9824 | 15.5206 | 14.8915 | 684.925 | 181.7567 | 671.0162 | 4.9621 | 56.0379 | 0.26574 | 7.05 | 6.65 |  | 140 | 257 |  | 934 |  | 44.8819 | 923.026 | 84.8325 | BMRL | 0.11 | 0.411 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | 2 | 2 | 2 | 0 | --- | 58.8966 | --- | 89.1892 | 57.9761 | 96.5503 | SDS-BCAA* | mg/L | 2.3 | --- | 137.3 | --- | 87.5676 | 135.4842 | 98.3024 | SDS-BCAA* | mg/L | 1.8 | --- | 35.8816 | --- | 90.2703 | 35.4047 | 94.9159 | SDS-BCAA* | mg/L | 1.6 | --- | 26.4529 | --- | 91.3514 | 26.1141 | 93.873 | Qp/QT (HAA5), % | 48.9688 | 49.7849 | 47.9793 | 47.5848 | Qp/QT (HAA5), % | 77.5251 | 78.8172 | 75.9585 | 75.334
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 14:45 | 77.25 | 25.4 | 60 | 62 | 246 | 6.99 | 1.09 |  | 8.08 | 0.16984 | 0.8651 | 29.4455 | 15.9543 | 15.3075 | 697.1587 | 184.8951 | 682.6029 | 5.0499 | 55.9501 | 0.27359 | 6.97 | 6.62 |  | 141 | 258 |  | 978.6514 |  | 44.4882 | 966.7506 | 85.4151 | BMRL | 0.113 | 0.452 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 124.967 | 127.1837 | 124.1677 | 122.4483 | SDS-THM4b, ug/L | 71.8808 | 75.3901 | 70.6153 | 67.8933
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 15:00 | 77.5 | 25.4 | 60 | 62 | 246 | 6.7 | 1.13 |  | 7.83 | 0.16984 | 0.85568 | 30.4176 | 15.2924 | 14.6725 | 683.7941 | 181.5123 | 670.1141 | 4.9544 | 56.0456 | 0.2618 | 7.15 | 6.75 |  | 146 | 256 |  | 894.354 |  | 42.5197 | 884.163 | 83.4872 | BMRL | 0.113 | 0.474 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CDBAA | mg/L | 2.2 | 2 | 2.1 | 9.5238 | --- | 22.4448 | --- | 73.75 | 22.1157 | 90.5045 | SDS-CDBAA | mg/L | 2.3 | --- | 49.8 | --- | 71.25 | 49.1611 | 95.3215 | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-06-27 | 15:30 | 78 | 25.4 | 60 | 62 | 246 | 6.69 | 0.99 |  | 7.68 | 0.16984 | 0.87109 | 31.0312 | 15.2696 | 14.6506 | 705.2732 | 187.2197 | 691.1846 | 5.1101 | 55.8899 | 0.26213 | 6.97 | 6.63 | 6.97 | 148 | 258 | 558 | 970.303 | -73.8894 | 41.7323 | 959.1217 | 84.5692 | BMRL | 0.112 | 0.505 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.9 | 1.5 | 1.7 | 23.5294 | --- | 97.5621 | --- | 94.2373 | 96.0113 | 98.2294 | SDS-DCBAA | mg/L | 1.8 | --- | 232.6333 | --- | 93.8983 | 229.5285 | 99.2158 | SDS-DCBAA | mg/L | 1.1 | --- | 59.0592 | --- | 96.2712 | 58.2481 | 98.1115 | SDS-DCBAA | mg/L | 1.2 | --- | 42.8176 | --- | 95.9322 | 42.2503 | 97.1598 | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-27 | 16:00 | 78.5 | 25.4 | 60 | 62 | 246 | 6.63 | 0.97 |  | 7.6 | 0.16984 | 0.87237 | 31.3684 | 15.1326 | 14.5192 | 707.0276 | 187.7199 | 693.0316 | 5.1231 | 55.8769 | 0.25984 | 7.06 | 6.72 | 6.93 | 164 | 258 | 608 | 869.1546 | -42.9531 | 35.4331 | 859.6523 | 80.9225 | BMRL | 0.107 | 0.547 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 6.2 | 5.3 | 5.75 | 15.6522 | --- | 331.7845 | --- | 94.2672 | 326.5102 | 98.239 | SDS-HAA5 | mg/L | 7.3 | --- | 782.3 | --- | 92.7218 | 771.8759 | 99.0543 | SDS-HAA5 | mg/L | 3.8 | --- | 200.7388 | --- | 96.2114 | 197.9828 | 98.0806 | SDS-HAA5 | mg/L | 3 | --- | 146.0882 | --- | 97.009 | 144.1376 | 97.9187 | SDS-CDb, mg/L | 4.8744 | 5.0484 | 5.0057 | 4.9792 | SDS-CDb, mg/L | 3.2995 | 3.575 | 3.5074 | 3.4655
[44 empty] | 1998-06-27 | 16:30 | 79 | 25.4 | 60 | 62 | 246 | 6.47 | 0.96 |  | 7.43 | 0.16984 | 0.87079 | 32.109 | 14.7674 | 14.1688 | 704.5373 | 187.1506 | 690.9296 | 5.1058 | 55.8942 | 0.25349 | 7.08 | 6.7 | 6.97 | 148 | 258 | 610 | 968.3958 | -58.7534 | 41.7323 | 957.6073 | 84.5448 | BMRL | 0.111 | 0.584 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 8.2 | 7.3 | 7.75 | 11.6129 | --- | 390.681 | --- | 93.4764 | 384.4863 | 97.9843 | SDS-HAA6 | mg/L | 9.6 | --- | 919.6 | --- | 91.9192 | 907.3601 | 98.942 | SDS-HAA6 | mg/L | 5.6 | --- | 236.6204 | --- | 95.2862 | 233.3875 | 97.6006 | SDS-HAA6 | mg/L | 4.6 | --- | 172.5412 | --- | 96.1279 | 170.2517 | 97.2981 | TOCb, mg/L | 3.2536 | 3.261 | #VALUE! | #VALUE! | TOCb, mg/L | 1.7687 | 1.7803 | #VALUE! | #VALUE!
[44 empty] | 1998-06-27 | 17:15 | 79.75 | 25.4 | 60 | 62 | 246 | 6.74 | 0.94 |  | 7.68 | 0.16984 | 0.8776 | 31.0312 | 15.3837 | 14.7601 | 714.8361 | 189.7291 | 700.449 | 5.1791 | 55.8209 | 0.26442 | 7.07 | 6.78 | 6.88 | 151 | 258 | 637 | 992.5319 | -55.8135 | 40.5512 | 981.0036 | 84.6076 | BMRL | 0.112 | 0.638 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-27 | 17:45 | 80.25 | 25.4 | 60 | 62 | 246 | 6.51 | 0.97 |  | 7.48 | 0.16984 | 0.87032 | 31.8877 | 14.8587 | 14.2564 | 703.9141 | 186.9621 | 690.2338 | 5.1011 | 55.8989 | 0.25504 | [27 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 175.1031 | 180 | 175.2021 | 170.483 | Bromideb, ug/L | 172.2475 | 180 | 172.4041 | 164.9332
[44 empty] | 1998-06-27 | 18:00 | 80.5 | 25.4 | 60 | 62 | 246 | 6.53 | 0.97 |  | 7.5 | 0.16984 | 0.87067 | 31.8 | 14.9044 | 14.3002 | 704.4376 | 187.0897 | 690.7047 | 5.1048 | 55.8952 | 0.25584 | 6.97 | 6.72 | 6.82 | 159 | 257 | 660 | 893.5361 | -35.3843 | 37.4016 | 883.7871 | 82.0092 | BMRL | 0.11 | 0.66 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 57.5516 | 55.0215 | 55.2021 | 51.4347 | Alkb, mg/L CaCO3 | 56.1237 | 52.1183 | 52.4041 | 46.4399
[44 empty] | 1998-06-27 | 18:45 | 81.25 | 25.4 | 60 | 62 | 246 | 6.52 | 0.97 |  | 7.49 | 0.16984 | 0.87049 | 31.8438 | 14.8816 | 14.2783 | 704.1761 | 187.026 | 690.4695 | 5.103 | 55.897 | 0.25544 | 6.91 | 6.67 | 6.97 | 164 | 258 | 672 | 858.9485 | -27.8197 | 35.4331 | 849.739 | 80.7 | BMRL | 0.12 | 0.696 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 146.5621 | 159.6613 | 137.9855 | 128.0021 | T-Hdb, mg/L CaCO3 | 117.1491 | 137.8871 | 103.571 | 87.7657
[44 empty] | 1998-06-27 | 19:30 | 82 | 25.4 | 60 | 62 | 246 | 6.6 | 0.98 |  | 7.58 | 0.16984 | 0.87071 | 31.4538 | 15.0641 | 14.4535 | 704.6002 | 187.0927 | 690.7159 | 5.1057 | 55.8943 | 0.25859 | 6.97 | 6.68 | 6.93 | 149 | 256 | 674 | 961.1429 | -42.6028 | 41.3386 | 950.2483 | 84.3199 | BMRL | 0.112 | 0.712 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 100.7631 | 96.6742 | 93.3389 | 90.8428 | Ca-Hdb, mg/L CaCO3 | 79.6314 | 73.1581 | 67.8777 | 63.926
[44 empty] | 1998-06-28 | 10:00 | 96.5 | 25.4 | 60 | 62 | 246 | 6.74 | 0.83 |  | 7.57 | 0.16984 | 0.89036 | 31.4967 | 15.3837 | 14.7601 | 734.1923 | 194.8665 | 719.4156 | 5.3194 | 55.6806 | 0.26508 | 7.35 | 6.97 | 7.01 | 158 | 257 | 788 | 1033.5663 | -31.1632 | 37.7953 | 1021.5717 | 84.5336 | BMRL | 0.112 | 0.89 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-06-28 | 11:00 | 97.5 | 25.4 | 60 | 62 | 246 | 6.62 | 0.82 |  | 7.44 | 0.16984 | 0.88978 | 32.0645 | 15.1098 | 14.4973 | 733.1179 | 194.6531 | 718.6275 | 5.3122 | 55.6878 | 0.26033 | 7 | 6.71 | 6.89 | 155 | 258 | 782 | 1053.2439 | -34.6859 | 38.9764 | 1041.1578 | 85.1127 | BMRL | 0.111 | 0.897 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-06-28 | 16:00 | 102.5 | 25.4 | 60 | 61 | 246 | 6.83 | 8.13 |  | 14.96 | 0.16984 | 0.45655 | 15.4439 | 15.5891 | 14.9572 | 382.1895 | 101.4113 | 374.394 | 2.7688 | 57.7312 | 0.25908 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-06-28 | 17:00 | 103.5 | 25.4 | 60 | 61 | 246 | 6.83 | 8.13 |  | 14.96 | 0.16984 | 0.45655 | 15.4439 | 15.5891 | 14.9572 | 382.1895 | 101.4113 | 374.394 | 2.7688 | 57.7312 | 0.25908 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-06-28 | 18:00 | 104.5 | 25.4 | 60 | 61 | 246 | 6.83 | 6.53 |  | 13.36 | 0.16984 | 0.51123 | 17.4132 | 15.5891 | 14.9572 | 406.7755 | 107.935 | 398.4784 | 2.9469 | 57.5531 | 0.25988 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-06-28 | 19:00 | 105.5 | 25.4 | 60 | 61 | 246 | 6.92 | 6.77 |  | 13.69 | 0.16984 | 0.50548 | 16.9693 | 15.7945 | 15.1543 | 404.0664 | 107.1865 | 395.7151 | 2.927 | 57.573 | 0.26322 | 7.37 | 6.93 | 7 | 181 | 256 | 363 | 328.6174 | 9.4718 | 28.7402 | 326.5412 | 44.5705 | BMRL | 0.108 | 0.212 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-06-28 | 20:00 | 106.5 | 25.4 | 60 | 61 | 246 | 7 | 6.74 |  | 13.74 | 0.16984 | 0.50946 | 16.9039 | 15.9771 | 15.3294 | 405.9778 | 107.6671 | 397.4893 | 2.9407 | 57.5593 | 0.26632 | 7.3 | 6.89 | 6.99 | 130 | 255 | 369 | 382.7834 | -3.7353 | 48.8189 | 379.1869 | 65.7161 | BMRL | 0.116 | 0.226 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-06-28 | 21:00 | 107.5 | 25.4 | 60 | 61 | 246 | 6.85 | 6.93 |  | 13.78 | 0.16984 | 0.4971 | 16.852 | 15.6348 | 15.001 | 400.1286 | 106.1648 | 391.9431 | 2.8987 | 57.6013 | 0.26043 | 7.27 | 6.87 | 6.91 | 132 | 260 | 371 | 374.5916 | -0.96809 | 48.0315 | 371.2141 | 64.441 | BMRL | 0.114 | 0.227 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-06-28 | 22:00 | 108.5 | 25.4 | 60 | 61 | 246 | 7.08 | 6.8 |  | 13.88 | 0.16984 | 0.51009 | 16.7233 | 16.1597 | 15.5046 | 406.2977 | 107.7254 | 397.7046 | 2.9428 | 57.5572 | 0.26938 | 7.15 | 6.79 | 6.89 | 133 | 261 | 371 | 379.9824 | -2.4211 | 47.6378 | 376.4282 | 64.6679 | BMRL | 0.112 | 0.221 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-06-28 | 23:00 | 109.5 | 25.4 | 60 | 61 | 246 | 6.93 | 6.88 |  | 13.81 | 0.16984 | 0.50181 | 16.8132 | 15.8174 | 15.1762 | 402.344 | 106.7263 | 394.0162 | 2.9145 | 57.5855 | 0.26354 | 7.1 | 6.78 | 6.87 | 134 | 255 | 373 | 374.8721 | -0.5019 | 47.2441 | 371.4793 | 63.928 | BMRL | 0.111 | 0.22 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-06-29 | 0:00 | 110.5 | 25.4 | 60 | 61 | 246 | 7.14 | 6.74 |  | 13.88 | 0.16984 | 0.51441 | 16.7233 | 16.2967 | 15.636 | 408.3893 | 108.26 | 399.6782 | 2.9577 | 57.5423 | 0.27173 | 7.09 | 6.81 | 6.93 | 136 | 253 | 371 | 379.003 | -2.1571 | 46.4567 | 375.4765 | 63.7794 | BMRL | 0.114 | 0.223 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-06-29 | 8:00 | 118.5 | 25.4 | 60 | 61 | 246 | 6.5 | 5.67 |  | 12.17 | 0.16984 | 0.5341 | 19.2136 | 14.8359 | 14.2345 | 417.926 | 111.0061 | 409.8164 | 3.0287 | 57.4713 | 0.24768 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-06-29 | 8:30 | 119 | 25.4 | 60 | 60 | 246 | 6.5 | 10.75 |  | 17.25 | 0.16984 | 0.37681 | 13.2609 | 14.8359 | 14.2345 | 351.1809 | 93.2778 | 344.3664 | 2.545 | 57.455 | 0.24775
[44 empty] | 1998-06-29 | 9:00 | 119.5 | 25.4 | 60 | 60 | 246 | 6.5 | 10.75 |  | 17.25 | 0.16984 | 0.37681 | 13.2609 | 14.8359 | 14.2345 | 351.1809 | 93.2778 | 344.3664 | 2.545 | 57.455 | 0.24775
[44 empty] | 1998-06-29 | 10:30 | 121 | 23.4 | 59 | 60 | 246 | 6.6 | 14.67 |  | 21.27 | 0.16984 | 0.3103 | 10.5656 | 15.0641 | 15.3337 | 328.9743 | 87.3526 | 322.4917 | 2.3838 | 57.1162 | 0.26846
[44 empty] | 1998-06-29 | 11:30 | 122 | 23.4 | 59 | 60 | 246 | 6.56 | 15.3 |  | 21.86 | 0.16984 | 0.30009 | 10.2534 | 14.9728 | 15.2408 | 325.8074 | 86.5223 | 319.4265 | 2.3609 | 57.1391 | 0.26673 | 7.08 | 6.88 | 6.91 | 125 | 253 | 299 | 309.3098 | -3.4481 | 50.7874 | 306.8523 | 59.2638 | BMRL | 0.113 | 0.158 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-29 | 12:00 | 122.5 | 23.7 | 59 | 60 | 246 | 6.56 | 16.33 |  | 22.89 | 0.16984 | 0.28659 | 9.7471 | 14.9728 | 15.1062 | 321.7148 | 85.4355 | 315.414 | 2.3313 | 57.1687 | 0.26424 | 7.14 | 6.91 | 6.96 | 119 | 254 | 307 | 308.2315 | -0.40113 | 53.1496 | 305.7084 | 61.074 | BMRL | 0.115 | 0.156 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-29 | 13:00 | 123.5 | 23.7 | 59 | 60 | 246 | 6.68 | 14.73 |  | 21.41 | 0.16984 | 0.312 | 10.49 | 15.2467 | 15.3825 | 329.5182 | 87.4756 | 322.9457 | 2.3876 | 57.1124 | 0.26934 | 7.19 | 6.99 | 7 | 118 | 254 | 316 | 315.6755 | 0.10269 | 53.5433 | 312.9916 | 62.2993 | BMRL | 0.107 | 0.159 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-29 | 14:00 | 124.5 | 23.7 | 59 | 60 | 246 | 6.51 | 14.33 |  | 20.84 | 0.16984 | 0.31238 | 10.8042 | 14.8587 | 14.9911 | 329.6179 | 87.5477 | 323.2119 | 2.3887 | 57.1113 | 0.26249 | 7.13 | 6.9 | 6.93 | 125 | 257 | 305 | 312.6036 | -2.493 | 50.7874 | 310.1213 | 59.6932 | BMRL | 0.113 | 0.161 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-29 | 15:00 | 125.5 | 24.5 | 59 | 60 | 246 | 6.61 | 14 |  | 20.61 | 0.16984 | 0.32072 | 10.936 | 15.087 | 14.8656 | 332.2695 | 88.2249 | 325.7121 | 2.4077 | 57.0923 | 0.26038 | 7.08 | 6.89 | 6.94 | 119 | 258 | 308 | 317.7393 | -3.1621 | 53.1496 | 315.0692 | 62.2305 | BMRL | 0.112 | 0.163 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-29 | 16:30 | 127 | 24.5 | 59 | 60 | 246 | 6.61 | 14.36 |  | 20.97 | 0.16984 | 0.31521 | 10.731 | 15.087 | 14.8656 | 330.521 | 87.7607 | 323.9981 | 2.395 | 57.105 | 0.26032 | 7.15 | 6.85 | 6.92 | 122 | 256 | 305 | 314.7604 | -3.2001 | 51.9685 | 312.1707 | 60.9188 | BMRL | 0.111 | 0.161 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-30 | 14:30 | 149 | 24.5 | 59 | 60 | 246 | 9.38 | 2.37 | X | 11.75 | 0.16984 | 0.7983 | 19.9362 | 21.4093 | 21.0953 | 616.7131 | 162.355 | 599.3884 | 4.457 | 55.043 | 0.38325
[44 empty] | 1998-06-30 | 15:00 |  | 24.5 | 43 | 44 | 246 | 6.89 | 1.25 |  | 8.14 | 0.16984 | 0.84644 | 29.2211 | 15.7261 | 15.4953 | 671.7491 | 178.211 | 657.926 | 4.8663 | 38.6337 | 0.40108
[44 empty] | 1998-06-30 | 15:15 |  | 24.5 | 65 | 67 | 246 | 10.5 | 2.45 |  | 12.95 | 0.16984 | 0.81081 | 17.9961 | 23.9657 | 23.6141 | 632.003 | 165.7993 | 612.1041 | 4.5625 | 61.4375 | 0.38436
[44 empty] | 1998-06-30 | 15:45 |  | 24.5 | 50 | 51 | 246 | 8 | 1.52 |  | 9.52 | 0.16984 | 0.84034 | 24.8403 | 18.2596 | 17.9917 | 665.2024 | 175.8715 | 649.2892 | 4.8137 | 45.6863 | 0.39381
[44 empty] | 1998-06-30 | 16:00 |  | 24.5 | 61 | 62 | 246 | 9.98 | 2.03 |  | 12.01 | 0.16984 | 0.83097 | 19.4829 | 22.7788 | 22.4446 | 655.6904 | 172.2934 | 636.0794 | 4.7359 | 56.7641 | 0.3954
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on E19: Gary Puetz: The consultant stated that the cost of an 8X40 TFC-SR membrane element was not available from the manufacturer.
Note on R5: Gary Puetz: Consultant confirmed potential foulants were not measured during the study, because they were not required under the ICR.
Note on X26: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on CY31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DL31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DQ10: Alison Gusses: All water quality parameters were verified for the 90% recovery run; however, no explanation was given for the high mass balance closure errors, which may suggest that the membrane was not operating at steady-state
Note on DV31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on EF31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.

## SR40. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.70554 | [45 empty] | Recovery during sample collection (decimal) | 0.7 | [10 empty] | Recovery during sample collection (decimal) | 0.92 | [7 empty] | Recovery during sample collection (decimal) | 0.53 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 0.2 mg/L | plant | Sampling date | MM/DD/YY | 1998-09-15 | 1998-10-05 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.48 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.07 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.68 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.49 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24 |  |  | LSI | Coagulation | 156 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 8:00 | 8:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 263 | [10 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [7 empty] | Influent flow rate during sample collection (mL/min) | 263 | [6 empty] | SDS-THM4F, ug/L | 342.5 | 342.5 | 342.5 | 342.5 | SDS-THM4F, ug/L | 342.5 | 342.5 | 342.5 | 342.5 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 210 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.59 mg/L | plant | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 46.8 | 79.6 | 60.5 | 55.6 | SDS-THM4p, ug/L | 46.8 | 79.6 | 60.5 | 55.6 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 7.84 | 7.86 | 7.85 | 0.25478 | 1998-09-28 | 8:45 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-09-29 | 9:30 | 0 | 23.5 | 43.5 | 44.5 | 263 | 6.34 | 3.35 |  | 9.69 | 0.18158 | 0.65428 | 26.1414 | 14.4707 | 14.6862 | 461.6132 | 133.6003 | 453.7059 | 3.2406 | 40.7594 | 0.36031 | 6.05 | 6.23 | 6.19 | 133 | 247 | 363 | 462.7493 | -27.4791 | 46.1538 | 458.7747 | 71.0097 | BMRL | 0.207 | 0.44 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 214.8 | 214.8 | 214.8 | 214.8 | SDS-HAA5F, ug/L | 214.8 | 214.8 | 214.8 | 214.8 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23301 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-09-28 | 9:30 | 0.75 | 23.5 | 64 | 65.5 | 211 | 10.07 | 4.4 | 14.47 | 0.14568 | 0.69592 | 13.5819 | 22.9842 | 23.3265 | 0 | 0 | 0 | 0 | 64.75 | 0.36025 | 1998-09-29 | 10:30 | 1 | 23.5 | 43.5 | 44.5 | 263 | 6.22 | 3.12 |  | 9.34 | 0.18158 | 0.66595 | 27.1585 | 14.1968 | 14.4082 | 468.8228 | 135.732 | 460.9451 | 3.2915 | 40.7085 | 0.35394 |  |  |  | 136 |  | 396 | 468.2885 | -18.2547 | 44.9393 | 464.3591 | 70.7123 | BMRL |  | 0.53 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 6 | 12.3 | 10.5 | 8.7 | SDS-HAA5p, ug/L | 6 | 12.3 | 10.5 | 8.7 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 144 | 146 | 145 | 1.3793 | 1998-09-28 | 10:00 | 1.25 | 23.5 | 53 | 54.5 | 272 | 7.4 | 25.3 | 32.7 | 0.18779 | 0.2263 | 7.318 | 16.8901 | 17.1416 | 0 | 0 | 0 | 0 | 53.75 | 0.31891 | 1998-09-29 | 11:30 | 2 | 23.5 | 43.5 | 44.5 | 263 | 6.11 | 2.95 |  | 9.06 | 0.18158 | 0.67439 | 28.0287 | 13.9457 | 14.1534 | 474.1662 | 137.3208 | 466.3406 | 3.3293 | 40.6707 | 0.348 |  |  |  | 130 |  | 401 | 489.3288 | -22.0271 | 47.3684 | 485.1549 | 73.2044 | BMRL |  | 0.584 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-09-30 | 1998-10-01 | --- | --- | 1998-09-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-02 | 1998-10-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-03 | 1998-10-03 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-10-04 | 1998-10-04 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 1580 | 1580 | 1580 | 1580 | SDS-TOXF, ug Cl- /L | 1580 | 1580 | 1580 | 1580 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 249 | 245 | 247 | 1.6194 | 1998-09-28 | 10:30 | 1.75 | 23.5 | 56.5 | 58 | 263 | 8.4 | 3.84 | 12.24 | 0.18158 | 0.68627 | 20.4869 | 19.1726 | 19.458 | 0 | 0 | 0 | 0 | 57.25 | 0.33988 | 1998-09-29 | 13:00 | 3.5 | 23.5 | 43.5 | 44.5 | 263 | 6.11 | 2.83 |  | 8.94 | 0.18158 | 0.68345 | 28.4183 | 13.9457 | 14.1534 | 480.0929 | 139.0372 | 472.1695 | 3.3709 | 40.6291 | 0.34836 | 7.84 | 7.61 | 7.45 | 136 | 251 | 413 | 486.6502 | -17.833 | 44.9393 | 482.577 | 71.818 | BMRL | 0.206 | 0.615 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 8:30 | 9:30 | --- | --- | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:40 | 17:40 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 52.5 | 93 | 81 | 58 | SDS-TOXp, ug Cl- /L | 52.5 | 93 | 81 | 58 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 202 | 196 | 199 | 3.0151 | 1998-09-28 | 11:30 | 2.75 | 23.5 | 56.5 | 58 | 263 | 8.84 | 2.4 | 11.24 | 0.18158 | 0.78648 | 22.3986 | 20.1768 | 20.4772 | 0 | 0 | 0 | 0 | 57.25 | 0.35768 | 1998-09-29 | 15:10 | 5.6667 | 23.5 | 41 | 42.5 | 263 | 5.97 | 2.83 |  | 8.8 | 0.18158 | 0.67841 | 28.8864 | 13.6262 | 13.8291 | 476.7075 | 138.1102 | 469.0215 | 3.3475 | 38.4025 | 0.36011 |  |  |  | 128 |  | 373 | 498.0353 | -33.5215 | 48.1781 | 493.8355 | 74.0804 | BMRL |  | 0.516 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 23 | 48 | --- | --- | 23 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80.17 | 80.17 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101.5 | 101.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 122.5 | 122.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 11.16 | 11.16 | 11.16 | 11.16 | SDS-CDF, mg/L | 11.16 | 11.16 | 11.16 | 11.16 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 164 | 164 | 164 | 0 | 1998-09-28 | 12:30 | 3.75 | 23.5 | 50 | 51 | 263 | 7.91 | 1.25 | 9.16 | 0.18158 | 0.86354 | 27.7118 | 18.0542 | 18.323 | 0 | 0 | 0 | 0 | 50.5 | 0.36283 | 1998-09-29 | 16:10 | 6.6667 | 23.5 | 42.5 | 43.5 | 263 | 6.09 | 2.7 |  | 8.79 | 0.18158 | 0.69283 | 28.9204 | 13.9001 | 14.1071 | 486.3871 | 140.8678 | 478.3863 | 3.4152 | 39.5848 | 0.35638 | 7.9 | 7.78 | 7.66 | 137 | 248 | 396 | 495.1111 | -25.0281 | 44.5344 | 490.9649 | 72.0958 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.89 | 8 | 7.945 | 1.3845 | 7.59 | --- | --- | --- | --- | --- | pH | --- | 8.01 | 7.48 | --- | --- | --- | --- | --- | pH | --- | 7.98 | 7.68 | --- | --- | --- | --- | --- | pH | --- | 7.98 | 7.76 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.94 | 1.5 | 1.27 | 1.2 | SDS-CDp, mg/L | 0.94 | 1.5 | 1.27 | 1.2 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 4.55 | 68.925 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.247 | 0.165 | 0.206 | 39.8058 | 1998-09-28 | 13:30 | 4.75 | 23.5 | 51 | 52.5 | 263 | 8.27 | 3.75 | 12.02 | 0.18158 | 0.68802 | 20.8802 | 18.8758 | 19.1569 | 0 | 0 | 0 | 0 | 51.75 | 0.37018 | 1998-09-29 | 17:10 | 7.6667 | 23.5 | 42.5 | 44 | 263 | 6.09 | 2.62 |  | 8.71 | 0.18158 | 0.6992 | 29.1952 | 13.9001 | 14.1071 | 490.7557 | 142.133 | 482.683 | 3.4459 | 39.8041 | 0.35441 |  |  |  | 138 |  | 418 | 500.3626 | -19.704 | 44.1296 | 496.1672 | 72.1868 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 8.3 | 8.3 | 8.3 | 8.3 | TOCF, mg/L | 8.3 | 8.3 | 8.3 | 8.3 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 11.55 | 75.925 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-09-28 | 14:30 | 5.75 | 23.5 | 46 | 47 | 263 | 7.35 | 2.4 | 9.75 | 0.18158 | 0.75385 | 25.9744 | 16.776 | 17.0258 | 0 | 0 | 0 | 0 | 46.5 | 0.36615 | 1998-09-30 | 8:30 | 23 | 23.5 | 42.5 | 44 | 263 | 6 | 2.09 |  | 8.09 | 0.18158 | 0.74166 | 31.5093 | 13.6947 | 13.8986 | 521.9823 | 151.2145 | 513.5237 | 3.6654 | 39.5846 | 0.35111 |  |  |  | 142 |  | 453 | 548.4354 | -21.0674 | 42.5101 | 543.7993 | 73.8874 | 0.01 | 0.209 | 0.776 | 0.78029 | -0.55308 | 95.2153 | 0.77151 | 98.7038 | [8 empty] | Alkalinity | mg/L as CaCO3 | 132 | 132 | 132 | 0 | 180 | 175.3333 | 2.5926 | 8.9655 | 174.8443 | 24.5043 | Alkalinity | mg/L as CaCO3 | 144 | 190 | 156.5 | 17.6316 | 0.68966 | 156.3892 | 7.922 | Alkalinity | mg/L as CaCO3 | 122 | 170 | 170.9362 | -0.55069 | 15.8621 | 170.4096 | 28.4078 | Alkalinity | mg/L as CaCO3 | 110 | 164 | 160 | 2.439 | 24.1379 | 159.4442 | 31.0103 | TOCp, mg/L | 0.55 | 1.1 | 0.7 | 0.7 | TOCp, mg/L | 0.55 | 1.1 | 0.7 | 0.7 | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 3.15 | 67.525 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 8.4 | 8.2 | 8.3 | 2.4096 | 1998-09-28 | 15:30 | 6.75 | 23.5 | 43 | 44 | 263 | 6.87 | 1.75 | 8.62 | 0.18158 | 0.79698 | 29.5104 | 15.6804 | 15.9139 | 0 | 0 | 0 | 0 | 43.5 | 0.36584 | 1998-09-30 | 10:30 | 25 | 23.5 | 42.5 | 44 | 263 | 5.97 | 1.74 |  | 7.71 | 0.18158 | 0.77432 | 33.1115 | 13.6262 | 13.8291 | 548.8716 | 159.0173 | 540.022 | 3.8543 | 39.3957 | 0.35103 | [27 empty] | Total dissolved solids | mg/L | 138 | 138 | 138 | 0 | 440 | 501.3333 | -13.9394 | 44.1296 | 497.2331 | 72.2464 | Total dissolved solids | mg/L | 157 | 753 | 1282 | -70.2523 | 36.4372 | 1272.0239 | 87.6575 | Total dissolved solids | mg/L | 132 | 354 | 376.6809 | -6.407 | 46.5587 | 374.0478 | 64.7104 | Total dissolved solids | mg/L | 127 | 286 | 298.4286 | -4.3457 | 48.583 | 296.523 | 57.1703 | UV254 F, cm-1 | 0.209 | 0.209 | 0.209 | 0.209 | UV254 F, cm-1 | 0.209 | 0.209 | 0.209 | 0.209 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 2.55 | 66.925 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.207 | 0.211 | 0.209 | 1.9139 | 1998-09-28 | 15:50 | 7.0833 | 23.5 | 50 | 51.5 | 263 | 8.05 | 2.13 | 10.18 | 0.18158 | 0.79077 | 24.835 | 18.3737 | 18.6473 | 0 | 0 | 0 | 0 | 50.75 | 0.36743 | 1998-09-30 | 11:30 | 26 | 23.5 | 42.5 | 44 | 263 | 6 | 2.8 |  | 8.8 | 0.18158 | 0.68182 | 28.8864 | 13.6947 | 13.8986 | 478.961 | 138.7515 | 471.1995 | 3.3633 | 39.8867 | 0.34845 | [27 empty] | Total hardness | mg/L as CaCO3 | 90 | 90 | 90 | 0 | 472 | 453.3333 | 3.9548 | 54.7739 | 449.2331 | 79.9659 | Total hardness | mg/L as CaCO3 | 106 | 1000 | 1268.5 | -26.85 | 46.7337 | 1258.1913 | 91.5752 | Total hardness | mg/L as CaCO3 | 86 | 336 | 326.4255 | 2.8495 | 56.7839 | 323.8383 | 73.4435 | Total hardness | mg/L as CaCO3 | 80 | 268 | 250 | 6.7164 | 59.799 | 248.1103 | 67.7563 | UV254 p, cm-1 | 0.0095 | 0.022 | 0.014 | 0.013 | UV254 p, cm-1 | 0.0095 | 0.022 | 0.014 | 0.013 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.4643 | 2.5732 | 2.5187 | 4.323 | 1998-09-28 | 16:10 | 7.4167 | 23.5 | 60 | 61.5 | 309 | 9.87 | 2.8 | 12.67 | 0.21334 | 0.77901 | 23.3883 | 22.5277 | 22.8632 | 0 | 0 | 0 | 0 | 60.75 | 0.37635 | 1998-09-30 | 13:00 | 27.5 | 23.5 | 42.5 | 44 | 263 | 5.89 | 2.09 |  | 7.98 | 0.18158 | 0.7381 | 31.9574 | 13.4436 | 13.6438 | 519.1359 | 150.4357 | 510.8787 | 3.6457 | 39.6043 | 0.3445 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 76 | 76 | 76 | 0 | 384 | 369.3333 | 3.8194 | 53.6585 | 366.023 | 79.2363 | Calcium hardness | mg/L as CaCO3 | 84 | 830 | 1084 | -30.6024 | 48.7805 | 1075.1323 | 92.187 | Calcium hardness | mg/L as CaCO3 | 72 | 288 | 267.7447 | 7.0331 | 56.0976 | 265.6382 | 72.8955 | Calcium hardness | mg/L as CaCO3 | 68 | 210 | 205.1429 | 2.3129 | 58.5366 | 203.6184 | 66.6042 | BromideF, ug/L | 150 | 150 | 150 | 150 | BromideF, ug/L | 150 | 150 | 150 | 150 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 150 | 150 | 150 | 0 | 1998-09-28 | 16:30 | 7.75 | 23.5 | 31 | 32 | 245 | 5 | 1.05 | 6.05 | 0.16915 | 0.82645 | 39.4959 | 11.4122 | 11.5822 | 0 | 0 | 0 | 0 | 31.5 | 0.36769 | 1998-09-30 | 14:15 | 28.75 | 23.5 | 42.5 | 44 | 263 | 6 | 2.98 |  | 8.98 | 0.18158 | 0.66815 | 28.2873 | 13.6947 | 13.8986 | 470.1115 | 136.1879 | 462.4935 | 3.3011 | 39.9489 | 0.34791 | 6.26 | 6.23 | 6.25 | 142 | 248 | 437 | 458.4094 | -4.8992 | 42.5101 | 454.8002 | 68.7775 | 0.009 | 0.208 | 0.686 | 0.61168 | 10.8332 | 95.6938 | 0.60481 | 98.5119 | [8 empty] | Turbidity | ntu | 0.08 | 0.073 | 0.0765 | 9.1503 | 0.396 | 0.50817 | -28.3249 | 62.8641 | 0.5033 | 84.8002 | Turbidity | ntu | 0.059 | 0.463 | 1.8965 | -309.6112 | 71.3592 | 1.8802 | 96.862 | Turbidity | ntu | 0.081 | 0.382 | 0.34696 | 9.1734 | 60.6796 | 0.3441 | 76.46 | Turbidity | ntu | 0.096 | 0.286 | 0.25314 | 11.4885 | 53.3981 | 0.2514 | 61.8132 | Bromidep, ug/L | 160 | 160 | 160 | 160 | Bromidep, ug/L | 160 | 160 | 160 | 160 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 12 | 12 | 12 | 0 | 1998-09-28 | 17:15 | 8.5 | 23.5 | 41.5 | 42.5 | 263 | 7.1 | 1.47 | 8.57 | 0.18158 | 0.82847 | 29.6884 | 16.2054 | 16.4467 | 0 | 0 | 0 | 0 | 42 | 0.39159 | 1998-09-30 | 15:10 | 29.6667 | 23.5 | 42.5 | 44 | 263 | 5.97 | 2.88 |  | 8.85 | 0.18158 | 0.67458 | 28.7175 | 13.6262 | 13.8291 | 474.2159 | 137.3883 | 466.57 | 3.33 | 39.92 | 0.34642 |  |  |  | 143 | 248 | 428 | 462.5833 | -8.0802 | 42.1053 | 458.9561 | 68.8423 | 0.009 | 0.209 | 0.687 | 0.62358 | 9.231 | 95.6938 | 0.61661 | 98.5404 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145 | AlkF, mg/L CaCO3 | 145 | 145 | 145 | 145
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.86 | 0.82 | 0.84 | 4.7619 | 1998-09-29 | 8:30 | 23.75 | 23.5 | 44 | 44.5 | 263 | 6.73 | 3.64 | 10.37 | 0.18158 | 0.64899 | 24.3616 | 15.3609 | 15.5896 | 0 | 0 | 0 | 0 | 44.25 | 0.35231 | 1998-09-30 | 16:10 | 30.6667 | 23.5 | 42.5 | 44 | 263 | 5.94 | 2.82 |  | 8.76 | 0.18158 | 0.67808 | 29.0228 | 13.5577 | 13.7596 | 476.479 | 138.0554 | 468.8355 | 3.346 | 39.904 | 0.34482 | 7.15 | 7.09 | 7.04 | 137 | 249 | 416 | 478.7021 | -15.0726 | 44.5344 | 474.8434 | 71.1484 | [16 empty] | Total organic carbon | mg/L | 0.5 | 0.6 | 0.55 | 18.1818 | 26.2 | 26.3833 | -0.69975 | 93.3735 | 26.0918 | 97.8921 | Total organic carbon | mg/L | 1.1 | 71.6 | 91.1 | -27.2346 | 86.747 | 90.3019 | 98.7819 | Total organic carbon | mg/L | 0.7 | 16.1 | 16.8702 | -4.7839 | 91.5663 | 16.6962 | 95.8074 | Total organic carbon | mg/L | 0.7 | 10.4 | 11.5571 | -11.1264 | 91.5663 | 11.4365 | 93.8792 | Alkp, mg/L CaCO3 | 132 | 144 | 122 | 110 | Alkp, mg/L CaCO3 | 132 | 144 | 122 | 110
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 11.14 | 11.18 | 11.16 | 0.35842 | 1998-09-29 | 8:45 | 24 | 23.5 | 44 | 44.5 | 263 | 6.73 | 3.64 | 10.37 | 0.18158 | 0.64899 | 24.3616 | 15.3609 | 15.5896 | 0 | 0 | 0 | 0 | 44.25 | 0.35231 | 1998-09-30 | 17:00 | 31.5 | 23.5 | 42.5 | 44 | 263 | 5.97 | 2.8 |  | 8.77 | 0.18158 | 0.68073 | 28.9886 | 13.6262 | 13.8291 | 478.2289 | 138.5509 | 470.5183 | 3.3582 | 39.8918 | 0.34667 |  |  |  | 141 | 250 | 412 | 473.0071 | -14.8076 | 42.915 | 469.2389 | 69.9513 | [16 empty] | UV254 | cm-1 | 0.009 | 0.01 | 0.0095 | 10.5263 | 0.692 | 0.6745 | 2.5289 | 95.4545 | 0.667 | 98.5757 | UV254 | cm-1 | 0.022 | 1.764 | 2.3595 | -33.7585 | 89.4737 | 2.3388 | 99.0593 | UV254 | cm-1 | 0.014 | 0.439 | 0.42889 | 2.3021 | 93.3014 | 0.42443 | 96.7014 | UV254 | cm-1 | 0.013 | 0.291 | 0.293 | -0.68729 | 93.7799 | 0.28989 | 95.5155 | T-HdF, mg/L CaCO3 | 199 | 199 | 199 | 199 | T-HdF, mg/L CaCO3 | 199 | 199 | 199 | 199
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 8:15 | 46.75 | 23.5 | 42.5 | 44 | 263 | 5.91 | 2.5 |  | 8.41 | 0.18158 | 0.70273 | 30.2723 | 13.4893 | 13.6901 | 493.1193 | 142.8886 | 485.2491 | 3.463 | 39.787 | 0.34408 | 7.82 | 7.65 | 7.5 | 139 | 248 | 440 | 502.312 | -14.1618 | 43.7247 | 498.2299 | 72.1012 | [16 empty] | SUVA | L/(mg*m) | 1.8 | 1.6667 | 1.7333 | 7.6923 | 2.6412 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 2.4637 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 2.7267 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8571 | 2.7981 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 90 | 106 | 86 | 80 | T-Hdp, mg/L CaCO3 | 90 | 106 | 86 | 80
Process Train Name | Enhanced Coagulation/Lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 7.85 | 7.88 | 7.865 | 0.38144 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 9:30 | 48 | 23.5 | 42.5 | 44 | 263 | 5.86 | 2.44 |  | 8.3 | 0.18158 | 0.70602 | 30.6867 | 13.3751 | 13.5743 | 495.4019 | 143.5699 | 487.5626 | 3.4791 | 39.7709 | 0.34131 | 7.86 | 7.65 | 7.47 | 139 | 249 | 432 | 506.377 | -17.2169 | 43.7247 | 502.2842 | 72.3264 | [16 empty] | Bromide | mg/L | 160 | 160 | 160 | 0 | --- | 126.6667 | --- | -6.6667 | 127.0428 | -25.9418 | Bromide | mg/L | 160 | --- | 35 | --- | -6.6667 | 36.1085 | -343.1095 | Bromide | mg/L | 160 | --- | 138.7234 | --- | -6.6667 | 138.9524 | -15.1474 | Bromide | mg/L | 160 | --- | 145.7143 | --- | -6.6667 | 145.8731 | -9.6844 | Ca-HdF, mg/L CaCO3 | 164 | 164 | 164 | 164 | Ca-HdF, mg/L CaCO3 | 164 | 164 | 164 | 164
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 72 | 72 | 72 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 11:30 | 50 | 23.5 | 42.5 | 44 | 263 | 5.8 | 2.41 |  | 8.21 | 0.18158 | 0.70646 | 31.0341 | 13.2382 | 13.4353 | 495.6727 | 143.6722 | 487.91 | 3.4812 | 39.7688 | 0.33784 | 7.82 | 7.68 | 7.55 | 139 | 249 | 433 | 506.917 | -17.0709 | 43.7247 | 502.8601 | 72.3581 | 0.009 | 0.206 | 0.673 | 0.69033 | -2.5747 | 95.6938 | 0.68282 | 98.6819 | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 76 | 84 | 72 | 68 | Ca-Hdp, mg/L CaCO3 | 76 | 84 | 72 | 68
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 1060 | 2100 | 1580 | 65.8228 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 13:00 | 51.5 | 23.5 | 42.5 | 44 | 263 | 5.81 | 2.38 |  | 8.19 | 0.18158 | 0.7094 | 31.1123 | 13.261 | 13.4585 | 497.7683 | 144.2756 | 489.9592 | 3.4959 | 39.7541 | 0.33854 | 7.97 | 7.77 | 7.64 | 137 | 248 | 442 | 515.5294 | -16.6356 | 44.5344 | 511.3483 | 73.2081 | 0.009 | 0.208 | 0.679 | 0.69724 | -2.6856 | 95.6938 | 0.68963 | 98.695 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.6 | 1.52 | 1.56 | 5.1282 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.23 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.3 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 220 | 290 | 255 | 27.451 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 14:45 | 53.25 | 23.5 | 42.5 | 44 | 263 | 5.8 | 2.33 |  | 8.13 | 0.18158 | 0.71341 | 31.3493 | 13.2382 | 13.4353 | 500.6324 | 145.1097 | 492.792 | 3.516 | 39.734 | 0.33813 | 7.94 | 7.79 | 7.61 | 133 | 248 | 440 | 530.7768 | -20.6311 | 46.1538 | 526.3907 | 74.7336 | 0.009 | 0.208 | 0.686 | 0.70685 | -3.04 | 95.6938 | 0.69916 | 98.7127 | [8 empty] | SDS-Cl2 demand | mg/L | 0.9 | 0.98 | 0.94 | 8.5106 | --- | 35.0067 | --- | 91.5771 | 34.6222 | 97.285 | SDS-Cl2 demand | mg/L | 1.5 | --- | 122.25 | --- | 86.5591 | 121.1792 | 98.7622 | SDS-Cl2 demand | mg/L | 1.27 | --- | 22.3126 | --- | 88.6201 | 22.0861 | 94.2498 | SDS-Cl2 demand | mg/L | 1.2 | --- | 15.4286 | --- | 89.2473 | 15.2704 | 92.1417 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 64 | 79 | 71.5 | 20.979 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 15:45 | 54.25 | 23.5 | 42.5 | 44 | 263 | 5.77 | 2.31 |  | 8.08 | 0.18158 | 0.71411 | 31.5495 | 13.1697 | 13.3658 | 501.1212 | 145.2635 | 493.3139 | 3.5195 | 39.7305 | 0.33641 | 7.97 | 7.82 | 7.63 | 130 | 246 | 460 | 539.2468 | -17.2276 | 47.3684 | 534.7575 | 75.6899 | 0.009 | 0.209 | 0.687 | 0.70857 | -3.1393 | 95.6938 | 0.70089 | 98.7159 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 91.4778 | 102.8908 | 95.922 | 94.2837 | Qp/QT (THM4), % | 103.6524 | 116.5843 | 108.6879 | 106.8316
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 14 | 18 | 16 | 25 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-01 | 17:00 | 55.5 | 23.5 | 42.5 | 44 | 263 | 5.8 | 2.31 |  | 8.11 | 0.18158 | 0.71517 | 31.4291 | 13.2382 | 13.4353 | 501.9034 | 145.4781 | 494.043 | 3.525 | 39.725 | 0.33821 | 7.95 | 7.84 | 7.63 | 138 | 248 | 428 | 520.6797 | -21.6541 | 44.1296 | 516.46 | 73.2796 | 0.01 | 0.205 | 0.695 | 0.70865 | -1.9646 | 95.2153 | 0.70095 | 98.5734 | [8 empty] | SDS-Chlorination pH | --- | 7.98 | 7.97 | 7.975 | 0.12539 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 7.97 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.04 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.08 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | NA | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 8:00 | 70.5 | 23.5 | 42.5 | 44 | 263 | 5.57 | 1.81 |  | 7.38 | 0.18158 | 0.75474 | 34.6369 | 12.7132 | 12.9025 | 532.1433 | 154.3412 | 524.142 | 3.738 | 39.512 | 0.32655 | 7.96 | 7.8 | 7.59 | 144 | 248 | 497 | 563.9669 | -13.4742 | 41.7004 | 559.5197 | 74.2636 | 0.013 | 0.205 | 0.795 | 0.81216 | -2.1585 | 93.7799 | 0.8037 | 98.3825 | [8 empty] | SDS-Incubation time | hours | 72 | 72 | 72 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 72 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 72 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 72 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 23.7943 | NA | 18.8314 | 20.4812 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 298 | 387 | 342.5 | 25.9854 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 9:00 | 71.5 | 23.5 | 42.5 | 44 | 263 | 5.54 | 1.9 |  | 7.44 | 0.18158 | 0.74462 | 34.3495 | 12.6448 | 12.833 | 524.0128 | 151.9956 | 516.1764 | 3.681 | 39.569 | 0.32432 | 8.05 | 7.9 |  | 138 | 249 | 470 | 564.8211 | -20.1747 | 44.1296 | 560.3256 | 75.3715 | 0.01 | 0.205 | 0.76 | 0.78924 | -3.8476 | 95.2153 | 0.78103 | 98.7196 | [8 empty] | SDS-TOX | mg Cl- /L | 50 | 55 | 52.5 | 9.5238 | --- | 5144.1667 | --- | 96.6772 | 5086.7063 | 98.9679 | SDS-TOX | mg Cl- /L | 93 | --- | 18680.5 | --- | 94.1139 | 18515.672 | 99.4977 | SDS-TOX | mg Cl- /L | 81 | --- | 3270.3617 | --- | 94.8734 | 3236.0403 | 97.4969 | SDS-TOX | mg Cl- /L | 58 | --- | 2232.2857 | --- | 96.3291 | 2208.1164 | 97.3733 | SDS-TOXb, ug Cl- /L | 182.6759 | NA | 142.1294 | 145.0017 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 11 | 8.9 | 9.95 | 21.1055 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 10:30 | 73 | 23.5 | 42.5 | 44 | 263 | 5.49 | 1.8 |  | 7.29 | 0.18158 | 0.75309 | 35.0768 | 12.5306 | 12.7172 | 530.7438 | 153.9693 | 522.8788 | 3.7284 | 39.5216 | 0.32178 | 8.02 | 7.9 | 7.63 | 141 | 249 | 471 | 570.3 | -21.0828 | 42.915 | 565.8193 | 75.0804 | 0.01 | 0.208 | 0.781 | 0.81595 | -4.475 | 95.2153 | 0.80754 | 98.7617 | [8 empty] | SDS-CHCl3 | mg/L | 2.6 | 2.9 | 2.75 | 10.9091 | --- | 843.5833 | --- | 98.9216 | 834.0944 | 99.6703 | SDS-CHCl3 | mg/L | 6.6 | --- | 3111.6 | --- | 97.4118 | 3084.0659 | 99.786 | SDS-CHCl3 | mg/L | 5.5 | --- | 536.3511 | --- | 97.8431 | 530.6385 | 98.9635 | SDS-CHCl3 | mg/L | 3.6 | --- | 362.7429 | --- | 98.5882 | 358.7506 | 98.9965 | SDS-CDb, mg/L | 1.811 | NA | 1.6733 | 1.7693 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 88 | 81 | 84.5 | 8.284 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 12:30 | 75 | 23.5 | 42.5 | 44 | 263 | 5.43 | 1.67 |  | 7.1 | 0.18158 | 0.76479 | 36.0423 | 12.3937 | 12.5782 | 540.3468 | 156.781 | 532.4275 | 3.7961 | 39.4539 | 0.31881 | 8.03 | 7.85 | 7.7 | 135 | 246 | 504 | 611.1677 | -21.2634 | 45.3441 | 606.2521 | 77.732 | 0.013 | 0.206 | 0.804 | 0.84629 | -5.2604 | 93.7799 | 0.83769 | 98.4481 | [8 empty] | SDS-BDCM | mg/L | 8.8 | 9.3 | 9.05 | 5.5249 | --- | 217.2167 | --- | 87.3427 | 214.8675 | 95.7881 | SDS-BDCM | mg/L | 18 | --- | 686.75 | --- | 74.8252 | 680.8197 | 97.3561 | SDS-BDCM | mg/L | 13 | --- | 137.4681 | --- | 81.8182 | 136.1287 | 90.4502 | SDS-BDCM | mg/L | 11 | --- | 97.4286 | --- | 84.6154 | 96.4678 | 88.5972 | TOCb, mg/L | 1.2105 | NA | 1.0099 | 1.1344 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 120 | 110 | 115 | 8.6957 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 13:30 | 76 | 23.5 | 42.5 | 44 | 263 | 5.43 | 1.63 |  | 7.06 | 0.18158 | 0.76912 | 36.2521 | 12.3937 | 12.5782 | 544.0073 | 157.8431 | 536.0344 | 3.8218 | 39.4282 | 0.31902 | 8.06 | 7.9 | 7.72 | 144 | 248 | 475 | 590.1227 | -24.2364 | 41.7004 | 585.5173 | 75.4064 | 0.012 | 0.206 | 0.817 | 0.86526 | -5.9074 | 94.2584 | 0.85646 | 98.5989 | [8 empty] | SDS-DBCM | mg/L | 19 | 21 | 20 | 10 | --- | 6.6667 | --- | -25 | 6.8171 | -193.3784 | SDS-DBCM | mg/L | 34 | --- | -191 | --- | -112.5 | -189.0048 | 117.989 | SDS-DBCM | mg/L | 25 | --- | 5.8511 | --- | -56.25 | 6.0571 | -312.7367 | SDS-DBCM | mg/L | 24 | --- | 12.5714 | --- | -50 | 12.6985 | -88.9992 | UV254 b, cm-1 | 0.026502 | NA | 0.021952 | 0.024204 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | 2.1 | 1.9 | 2 | 10 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 14:30 | 77 | 23.5 | 43 | 44 | 263 | 5.43 | 1.61 |  | 7.04 | 0.18158 | 0.77131 | 36.358 | 12.3937 | 12.5782 | 545.872 | 158.3842 | 537.8718 | 3.8349 | 39.6651 | 0.31711 | 8.06 | 7.92 | 7.65 | 144 | 248 |  | 594.3851 |  | 41.7004 | 589.7357 | 75.5823 | 0.011 | 0.209 | 0.835 | 0.87679 | -5.0046 | 94.7368 | 0.86785 | 98.7325 | [8 empty] | SDS-CHBr3 | mg/L | 14 | 16 | 15 | 13.3333 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 21 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 17 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 17 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 159.1478 | NA | 159.5922 | 159.4284 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 3.2 | 3.5 | 3.35 | 8.9552 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 16:00 | 78.5 | 23.5 | 43 | 44 | 263 | 5.29 | 0.59 |  | 5.88 | 0.18158 | 0.89966 | 43.7279 | 12.0741 | 12.2539 | 683.3093 | 198.3379 | 673.5545 | 4.8009 | 38.6991 | 0.31665 |  |  |  | 147 |  |  | 1143.6102 |  | 40.4858 | 1133.5872 | 87.0323 | 0.012 |  | 0.92 | 1.9753 | -114.7089 | 94.2584 | 1.9556 | 99.3864 | [8 empty] | SDS-THM4 | mg/L | 44.4 | 49.2 | 46.8 | 10.2564 | --- | 1032.4667 | --- | 86.3358 | 1021.3432 | 95.4178 | SDS-THM4 | mg/L | 79.6 | --- | 3365.85 | --- | 76.7591 | 3336.7086 | 97.6144 | SDS-THM4 | mg/L | 60.5 | --- | 660.5 | --- | 82.3358 | 654.0433 | 90.7498 | SDS-THM4 | mg/L | 55.6 | --- | 465.4571 | --- | 83.7664 | 460.9012 | 87.9367 | Alkb, mg/L CaCO3 | 133.1079 | NA | 122.9379 | 112.0007 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 23 | 21 | 22 | 9.0909 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 16:20 | 78.8333 | 23.5 | 43 | 44 | 263 | 5.26 | 0.57 |  | 5.83 | 0.18158 | 0.90223 | 44.1115 | 12.0057 | 12.1844 | 686.7334 | 199.3483 | 676.9857 | 4.8251 | 38.6749 | 0.31505 |  |  |  | 150 |  |  | 1142.1228 |  | 39.2713 | 1132.2016 | 86.7515 | 0.012 |  | 0.98 | 2.0269 | -106.8296 | 94.2584 | 2.0068 | 99.402 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 99.2891 | NA | 90.6082 | 86.8024 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 16:40 | 79.1667 | 23.5 | 43 | 44 | 263 | 5.17 | 0.56 |  | 5.73 | 0.18158 | 0.90227 | 44.8988 | 11.8002 | 11.9759 | 686.6622 | 199.377 | 677.0833 | 4.825 | 38.675 | 0.30966 |  |  |  | 155 |  |  | 1096.3571 |  | 37.247 | 1087.1046 | 85.7419 | 0.013 |  | 1.03 | 2.0185 | -95.9709 | 93.7799 | 1.9988 | 99.3496 | [8 empty] | SDS-DCAA* | mg/L | 1.4 | 1.4 | 1.4 | 0 | --- | 278.4 | --- | 98.3432 | 275.274 | 99.4914 | SDS-DCAA* | mg/L | 2.7 | --- | 1025.2 | --- | 96.8047 | 1016.1328 | 99.7343 | SDS-DCAA* | mg/L | 3.4 | --- | 175.9532 | --- | 95.9763 | 174.0963 | 98.0471 | SDS-DCAA* | mg/L | 2 | --- | 119.8571 | --- | 97.6331 | 118.547 | 98.3129 | Ca-Hdb, mg/L CaCO3 | 83.4995 | NA | 75.7518 | 73.4876 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 6.5 | 4.3 | 5.4 | 40.7407 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 17:00 | 79.5 | 23.5 | 43 | 44 | 263 | 5.15 | 0.56 |  | 5.71 | 0.18158 | 0.90193 | 45.0595 | 11.7546 | 11.9296 | 686.1714 | 199.2454 | 676.6365 | 4.8216 | 38.6784 | 0.30843 |  |  |  | 143 |  |  | 1203.4286 |  | 42.1053 | 1193.046 | 88.0139 | 0.014 |  | 1.086 | 2.0023 | -84.3742 | 93.3014 | 1.9828 | 99.2939 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.1 | --- | 1424.85 | --- | 99.0435 | 1412.2246 | 99.9221 | SDS-TCAA* | mg/L | 1 | --- | 243.5532 | --- | 99.1304 | 240.943 | 99.585 | SDS-TCAA* | mg/L | 1.2 | --- | 163.7714 | --- | 98.9565 | 161.9643 | 99.2591
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 48 | 29 | 38.5 | 49.3506 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 17:20 | 79.8333 | 23.5 | 43 | 44 | 263 | 5.1 | 0.55 |  | 5.65 | 0.18158 | 0.90265 | 45.5487 | 11.6405 | 11.8138 | 687.0892 | 199.5394 | 677.6348 | 4.8282 | 38.6718 | 0.30549 |  |  |  | 151 | 248 |  | 1137.1818 |  | 38.8664 | 1127.62 | 86.609 | 0.014 |  | 1.132 | 2.0172 | -78.1963 | 93.3014 | 1.9978 | 99.2992 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | 1.1 | --- | 12.35 | --- | 45 | 12.2502 | 91.0206 | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 224.3 | 205.3 | 214.8 | 8.8454 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-02 | 17:40 | 80.1667 | 23.5 | 43 | 44 | 263 | 5.05 | 0.52 |  | 5.57 | 0.18158 | 0.90664 | 46.2172 | 11.5264 | 11.698 | 692.4702 | 201.1298 | 683.0358 | 4.8662 | 38.6338 | 0.30279 | 7.88 | 7.65 |  | 148 | 248 |  | 1208.4423 |  | 40.081 | 1198.2613 | 87.6488 | 0.013 | 0.208 | 1.176 | 2.1125 | -79.6311 | 93.7799 | 2.0923 | 99.3787 | [8 empty] | SDS-DBAA* | mg/L | 4.6 | 4.6 | 4.6 | 0 | --- | 0.43333 | --- | -37.3134 | 0.48035 | -857.6253 | SDS-DBAA* | mg/L | 7.4 | --- | -43.225 | --- | -120.8955 | -42.7761 | 117.2994 | SDS-DBAA* | mg/L | 6.1 | --- | 0.24894 | --- | -82.0896 | 0.3119 | -1855.7504 | SDS-DBAA* | mg/L | 5.5 | --- | 2.4286 | --- | -64.1791 | 2.4627 | -123.3309 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 247.3 | 226.3 | 236.8 | 8.8682 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-03 | 9:45 | 96.25 | 23.5 | 42.5 | 43.5 | 263 | 4.56 | 0.38 |  | 4.94 | 0.18158 | 0.92308 | 52.2389 | 10.408 | 10.5629 | 715.1246 | 207.9896 | 706.3317 | 5.0274 | 37.9726 | 0.27817 | 7.91 | 7.76 | 7.41 | 156 | 248 | 877 | 1339 | -52.6796 | 36.8421 | 1328.7443 | 88.2596 | 0.021 | 0.208 | 2.022 | 2.465 | -21.909 | 89.9522 | 2.4438 | 99.1407 | [8 empty] | SDS-BCAA* | mg/L | 3.1 | 3.6 | 3.35 | 14.9254 | --- | 65.5167 | --- | 84.7727 | 64.8151 | 94.8315 | SDS-BCAA* | mg/L | 5.6 | --- | 210.6 | --- | 74.5455 | 208.7821 | 97.3178 | SDS-BCAA* | mg/L | 4.5 | --- | 41.734 | --- | 79.5455 | 41.3334 | 89.1129 | SDS-BCAA* | mg/L | 4 | --- | 29.7143 | --- | 81.8182 | 29.4284 | 86.4077 | Qp/QT (HAA5), % | 77.0115 | 79.4074 | 78.7078 | 78.0204 | Qp/QT (HAA5), % | 89.9425 | 92.7407 | 91.9236 | 91.1208
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-03 | 11:00 | 97.5 | 23.5 | 42.5 | 44 | 263 | 4.53 | 0.38 |  | 4.91 | 0.18158 | 0.92261 | 52.5642 | 10.3395 | 10.4934 | 714.3895 | 207.7929 | 705.6637 | 5.0223 | 38.2277 | 0.2745 | 7.96 | 7.83 |  | 156 | 249 |  | 1331.8158 |  | 36.8421 | 1321.6895 | 88.1969 | 0.021 | 0.207 | 2.049 | 2.4502 | -19.5782 | 89.9522 | 2.4292 | 99.1355 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 114.777 | 133.7379 | 120.5441 | 118.6595 | SDS-THM4b, ug/L | 76.5399 | 98.6846 | 83.2753 | 81.0744
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-03 | 12:00 | 98.5 | 23.5 | 42.5 | 44 | 263 | 4.49 | 0.37 |  | 4.86 | 0.18158 | 0.92387 | 53.1152 | 10.2482 | 10.4008 | 716.1813 | 208.337 | 707.5112 | 5.0351 | 38.2149 | 0.27217 |  |  |  | 159 |  |  | 1314.8919 |  | 35.6275 | 1305.0251 | 87.8163 | 0.021 |  | 2.077 | 2.4904 | -19.904 | 89.9522 | 2.4693 | 99.1496 | [8 empty] | SDS-CDBAA | mg/L | 2.9 | 3.1 | 3 | 6.6667 | --- | 11 | --- | 44.4444 | 10.9097 | 72.5016 | SDS-CDBAA | mg/L | 4.6 | --- | 14.6 | --- | 14.8148 | 14.5113 | 68.3006 | SDS-CDBAA | mg/L | 3.9 | --- | 7.0915 | --- | 27.7778 | 7.0571 | 44.7369 | SDS-CDBAA | mg/L | 3.6 | --- | 6.1714 | --- | 33.3333 | 6.1428 | 41.3952 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-10-03 | 12:30 | 99 | 23.5 | 42.5 | 44 | 263 | 4.64 | 3.98 |  | 8.62 | 0.18158 | 0.53828 | 29.5104 | 10.5906 | 10.7482 | 399.5219 | 116.173 | 394.5229 | 2.8085 | 40.4415 | 0.26577 |  |  |  | 150 |  | 708 | 360.0854 | 49.1405 | 39.2713 | 358.2322 | 58.1277 | 0.018 |  | 1.552 | 0.43167 | 72.186 | 91.3876 | 0.42802 | 95.7946 | [8 empty] | SDS-DCBAA | mg/L | 1.8 | 1.9 | 1.85 | 5.4054 | --- | 124.0167 | --- | 95.1948 | 122.638 | 98.4915 | SDS-DCBAA | mg/L | 3.1 | --- | 445.6 | --- | 91.9481 | 441.6761 | 99.2981 | SDS-DCBAA | mg/L | 2.5 | --- | 79.0957 | --- | 93.5065 | 78.2715 | 96.806 | SDS-DCBAA | mg/L | 2.4 | --- | 53.9714 | --- | 93.7662 | 53.3982 | 95.5055 | SDS-TOXb, ug Cl- /L | 403.6494 | 399.2119 | 400.1703 | 392.5298 | SDS-TOXb, ug Cl- /L | 206.1279 | 200.9452 | 202.0646 | 193.1412
[44 empty] | 1998-10-03 | 13:00 | 99.5 | 23.5 | 42.5 | 44 | 263 | 5.23 | 4.41 |  | 9.64 | 0.18158 | 0.54253 | 26.2822 | 11.9372 | 12.1149 | 401.6453 | 116.6012 | 395.977 | 2.8221 | 40.4279 | 0.29967 |  |  |  | 144 |  | 516 | 369.1519 | 28.4589 | 41.7004 | 366.9132 | 60.7537 | 0.016 |  | 0.933 | 0.43789 | 53.0668 | 92.3445 | 0.43369 | 96.3107 | [8 empty] | SDS-HAA5 | mg/L | 6 | 6 | 6 | 0 | --- | 702 | --- | 97.2067 | 694.1455 | 99.1356 | SDS-HAA5 | mg/L | 12.3 | --- | 2543.55 | --- | 94.2737 | 2521.1037 | 99.5121 | SDS-HAA5 | mg/L | 10.5 | --- | 445.1809 | --- | 95.1117 | 440.5032 | 97.6164 | SDS-HAA5 | mg/L | 8.7 | --- | 303.1286 | --- | 95.9497 | 299.8557 | 97.0986 | SDS-CDb, mg/L | 3.2894 | 3.4892 | 3.3758 | 3.3892 | SDS-CDb, mg/L | 1.9679 | 2.2012 | 2.0688 | 2.0844
[44 empty] | 1998-10-03 | 13:20 | 99.8333 | 23.5 | 42.5 | 44 | 263 | 5.39 | 4.93 |  | 10.32 | 0.18158 | 0.52229 | 24.4845 | 12.3024 | 12.4856 | 392.5178 | 113.9012 | 386.8077 | 2.7576 | 40.4924 | 0.30834 |  |  |  | 139 |  | 437 | 365.0771 | 16.4583 | 43.7247 | 362.7604 | 61.6827 | 0.014 |  | 0.724 | 0.42219 | 41.6858 | 93.3014 | 0.41801 | 96.6508 | [8 empty] | SDS-HAA6 | mg/L | 9.1 | 9.6 | 9.35 | 5.3476 | --- | 767.5167 | --- | 96.0515 | 758.9606 | 98.7681 | SDS-HAA6 | mg/L | 17.9 | --- | 2754.15 | --- | 92.4409 | 2729.8858 | 99.3443 | SDS-HAA6 | mg/L | 15 | --- | 486.9149 | --- | 93.6655 | 481.8365 | 96.8869 | SDS-HAA6 | mg/L | 12.7 | --- | 332.8429 | --- | 94.6368 | 329.2842 | 96.1431 | TOCb, mg/L | 2.3316 | 2.5827 | 2.3182 | 2.3705 | TOCb, mg/L | 1.3295 | 1.6227 | 1.3138 | 1.3748
[44 empty] | 1998-10-03 | 13:40 | 100.1667 | 23.5 | 42.5 | 44 | 263 | 5.47 | 5.4 |  | 10.87 | 0.18158 | 0.50322 | 23.195 | 12.485 | 12.6709 | 384.2727 | 111.484 | 378.5991 | 2.6995 | 40.5505 | 0.31247 |  |  |  | 137 |  | 400 | 358.4259 | 10.3935 | 44.5344 | 356.1233 | 61.5302 | 0.013 |  | 0.584 | 0.40754 | 30.2156 | 93.7799 | 0.40344 | 96.7777 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.055362 | 0.060508 | 0.05552 | 0.05608 | UV254 b, cm-1 | 0.029565 | 0.035575 | 0.029749 | 0.030403
[44 empty] | 1998-10-03 | 14:00 | 100.5 | 23.5 | 42.5 | 44 | 263 | 5.52 | 5.34 |  | 10.86 | 0.18158 | 0.50829 | 23.2173 | 12.5991 | 12.7867 | 386.4477 | 112.0995 | 380.6895 | 2.7147 | 40.5353 | 0.31545 |  |  |  | 134 |  | 368 | 363.809 | 1.1389 | 45.749 | 361.3973 | 62.9217 | 0.012 |  | 0.508 | 0.41264 | 18.7716 | 94.2584 | 0.40844 | 97.062 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 157.7011 | 157.9407 | 157.8708 | 157.802 | Bromideb, ug/L | 158.9943 | 159.2741 | 159.1924 | 159.1121
[44 empty] | 1998-10-03 | 14:20 | 100.8333 | 23.5 | 42.5 | 44 | 263 | 5.55 | 6.09 |  | 11.64 | 0.18158 | 0.4768 | 21.5945 | 12.6676 | 12.8562 | 373.397 | 108.3049 | 367.8029 | 2.623 | 40.627 | 0.31644 |  |  |  | 130 |  | 349 | 353.6256 | -1.3254 | 47.3684 | 351.2661 | 62.991 | 0.011 |  | 0.456 | 0.38944 | 14.5958 | 94.7368 | 0.38545 | 97.1462 | [47 empty] | Alkb, mg/L CaCO3 | 134.9885 | 144.2059 | 126.8972 | 117.6929 | Alkb, mg/L CaCO3 | 133.3075 | 144.0726 | 123.8576 | 113.1077
[44 empty] | 1998-10-03 | 14:40 | 101.1667 | 23.5 | 42.5 | 44 | 263 | 5.58 | 6.05 |  | 11.63 | 0.18158 | 0.47979 | 21.6139 | 12.7361 | 12.9257 | 374.6055 | 108.6464 | 368.9627 | 2.6314 | 40.6186 | 0.31822 |  |  |  | 131 |  | 343 | 353.9884 | -3.2036 | 46.9636 | 351.6229 | 62.7442 | 0.011 |  | 0.42 | 0.39162 | 6.7576 | 94.7368 | 0.38758 | 97.1619 | [47 empty] | T-Hdb, mg/L CaCO3 | 115.0575 | 125.1511 | 110.0602 | 106.1557 | T-Hdb, mg/L CaCO3 | 100.9626 | 112.7511 | 95.1263 | 90.5662
[44 empty] | 1998-10-03 | 15:00 | 101.5 | 23.5 | 42.5 | 44 | 263 | 5.66 | 6 |  | 11.66 | 0.18158 | 0.48542 | 21.5557 | 12.9186 | 13.111 | 376.9067 | 109.2897 | 371.1473 | 2.6474 | 40.6026 | 0.32291 | 8.1 | 7.91 | 7.85 | 129 | 248 | 323 | 358.3133 | -10.9329 | 47.7733 | 355.8458 | 63.7483 | 0.011 | 0.205 | 0.409 | 0.39578 | 3.2323 | 94.7368 | 0.39164 | 97.1913 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 96.2299 | 100.4741 | 91.5888 | 89.1004 | Ca-Hdb, mg/L CaCO3 | 84.8506 | 89.8074 | 79.4302 | 76.524
[44 empty] | 1998-10-04 | 9:10 | 119.6667 | 23.5 | 42.5 | 44 | 263 | 5.57 | 4.12 |  | 9.69 | 0.18158 | 0.57482 | 26.1414 | 12.7132 | 12.9025 | 417.3006 | 121.0326 | 411.026 | 2.9313 | 40.3187 | 0.32001 | 7.91 | 7.88 | 7.7 | 133 | 247 | 356 | 401.1214 | -12.6745 | 46.1538 | 398.2821 | 66.6066 | 0.014 | 0.206 | 0.454 | 0.47263 | -4.1032 | 93.3014 | 0.46777 | 97.0071 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-10-04 | 9:40 | 120.1667 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.52 |  | 20.35 | 0.18158 | 0.28649 | 11.9238 | 13.3067 | 13.5048 | 310.089 | 89.8727 | 305.2074 | 2.1778 | 41.5722 | 0.32485 |  |  |  | 133 |  | 291 | 292.7727 | -0.60918 | 46.1538 | 291.0019 | 54.2958 | 0.014 |  | 0.305 | 0.2873 | 5.8048 | 93.3014 | 0.28427 | 95.075 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-10-04 | 10:00 | 120.5 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.4 |  | 20.23 | 0.18158 | 0.28819 | 12.0005 | 13.3067 | 13.5048 | 310.5595 | 90.0091 | 305.6705 | 2.1811 | 41.5689 | 0.32488 |  |  |  | 123 |  | 283 | 297.2028 | -5.0186 | 50.2024 | 295.272 | 58.3435 | 0.013 |  | 0.287 | 0.28835 | -0.47135 | 93.7799 | 0.2853 | 95.4434 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-10-04 | 10:20 | 120.8333 | 23.5 | 43 | 44.5 | 263 | 5.84 | 14.33 |  | 20.17 | 0.18158 | 0.28954 | 12.0392 | 13.3295 | 13.528 | 310.9361 | 90.1158 | 306.0327 | 2.1837 | 41.5663 | 0.32545 |  |  |  | 124 |  | 278 | 297.127 | -6.8802 | 49.7976 | 295.2048 | 57.9953 | 0.013 |  | 0.283 | 0.28888 | -2.0767 | 93.7799 | 0.28581 | 95.4516 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-10-04 | 10:40 | 121.1667 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.27 |  | 20.1 | 0.18158 | 0.29005 | 12.0846 | 13.3067 | 13.5048 | 311.0772 | 90.1592 | 306.1801 | 2.1847 | 41.5653 | 0.32491 |  |  |  | 124 |  | 271 | 297.2516 | -9.6869 | 49.7976 | 295.3313 | 58.0133 | 0.013 |  | 0.284 | 0.28908 | -1.7872 | 93.7799 | 0.28602 | 95.4548 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-10-04 | 11:00 | 121.5 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.23 |  | 20.06 | 0.18158 | 0.29063 | 12.1107 | 13.3067 | 13.5048 | 311.2382 | 90.2058 | 306.3385 | 2.1858 | 41.5642 | 0.32491 | 8.14 | 7.99 | 7.9 | 123 | 248 | 278 | 297.8025 | -7.1232 | 50.2024 | 295.8651 | 58.427 | 0.013 | 0.205 | 0.281 | 0.2893 | -2.954 | 93.7799 | 0.28624 | 95.4583 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-10-04 | 11:20 | 121.8333 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.2 |  | 20.03 | 0.18158 | 0.29106 | 12.1303 | 13.3067 | 13.5048 | 311.3595 | 90.241 | 306.4579 | 2.1867 | 41.5633 | 0.32492 |  |  |  | 122 |  | 277 | 298.3204 | -7.6969 | 50.6073 | 296.3661 | 58.8347 | 0.013 |  | 0.283 | 0.28947 | -2.2864 | 93.7799 | 0.28641 | 95.461 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-10-04 | 11:40 | 122.1667 | 23.5 | 43 | 44.5 | 263 | 5.86 | 14.27 |  | 20.13 | 0.18158 | 0.29111 | 12.0651 | 13.3751 | 13.5743 | 311.3746 | 90.2379 | 306.4474 | 2.1867 | 41.5633 | 0.32659 |  |  |  | 124 |  | 280 | 297.5102 | -6.2536 | 49.7976 | 295.5771 | 58.0482 | 0.013 |  | 0.281 | 0.28949 | -3.0205 | 93.7799 | 0.28641 | 95.461 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-10-04 | 12:00 | 122.5 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.07 |  | 19.9 | 0.18158 | 0.29296 | 12.2161 | 13.3067 | 13.5048 | 311.8904 | 90.3949 | 306.9804 | 2.1904 | 41.5596 | 0.32495 | 8.1 | 7.94 | 7.93 | 122 | 248 | 274 | 298.7946 | -9.0491 | 50.6073 | 296.8351 | 58.8997 | 0.013 | 0.207 | 0.282 | 0.29021 | -2.9127 | 93.7799 | 0.28714 | 95.4726 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-10-04 | 12:20 | 122.8333 | 23.5 | 43 | 44.5 | 263 | 5.83 | 14.13 |  | 19.96 | 0.18158 | 0.29208 | 12.1764 | 13.3067 | 13.5048 | 311.6443 | 90.3235 | 306.7382 | 2.1887 | 41.5613 | 0.32494 |  |  |  | 124 |  | 279 | 297.7495 | -6.7202 | 49.7976 | 295.8237 | 58.0831 | 0.013 |  | 0.284 | 0.28987 | -2.0666 | 93.7799 | 0.2868 | 95.4672 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-10-04 | 13:00 | 123.5 | 23.5 | 43 | 44.5 | 263 | 5.87 | 14.07 |  | 19.94 | 0.18158 | 0.29438 | 12.1896 | 13.398 | 13.5974 | 312.2913 | 90.501 | 307.3411 | 2.1932 | 41.5568 | 0.3272 |  |  |  | 124 |  | 280 | 298.3156 | -6.5413 | 49.7976 | 296.3703 | 58.1604 | 0.013 |  | 0.283 | 0.29077 | -2.746 | 93.7799 | 0.28767 | 95.481 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-10-05 | 8:30 | 143 | 23.5 | 43.5 | 45 | 263 | 5.66 | 12.51 | X | 18.17 | 0.18158 | 0.3115 | 13.4744 | 12.9186 | 13.111 | 317.1455 | 91.9611 | 312.2993 | 2.2276 | 42.0224 | 0.312 | 8.04 | 7.83 | 7.84 | 124 | 248 | 287 | 302.6499 | -5.4529 | 49.7976 | 300.7275 | 58.7667 | 0.011 | 0.205 | 0.289 | 0.29858 | -3.3158 | 94.7368 | 0.29549 | 96.2773 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-10-06 | 16:00 |  | 23.5 | 51.5 | 52.5 | 263 | 8.35 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 19.0584 | 19.3422 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-06 | 16:30 |  | 23.5 | 60.5 | 61 | 263 | 10.2 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 23.281 | 23.6276 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-06 | 17:00 |  | 23.5 | 29.5 | 30 | 263 | 5 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 11.4122 | 11.5822 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-06 | 17:20 |  | 23.5 | 39.5 | 40.5 | 263 | 6.57 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 14.9957 | 15.2189 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-10-06 | 17:45 |  | 23.5 | 49.5 | 51 | 263 | 8.47 | NA |  | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 19.3323 | 19.6202 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on E19: Gary Puetz: The consultant stated that the cost of an 8X40 TFC-SR membrane element was not available from the manufacturer.
Note on R5: Gary Puetz: Consultant confirmed potential foulants were not measured during the study, because they were not required under the ICR.
Note on X26: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on X27: Gary Puetz: The consultant did verify the concentrations of TOX and CHCl3, but did not explain why the 2nd feed samples are high relative to the 1st sample. No changes were made.
Note on X28: Gary Puetz: The consultant did verify the concentrations of TOX and CHCl3, but did not explain why the 2nd feed samples are high relative to the 1st sample. No changes were made.
Note on CY22: Gary Puetz: The consultant did verify the permeate concentrations of TOC, UV, THM, HAA, and TOX, but did not explain why they dipped at the 70% recovery. No changes were made. This trend may indicate membrane was not completely stabilized prior to operation with test water.
Note on CY23: Gary Puetz: The consultant did verify the permeate concentrations of TOC, UV, THM, HAA, and TOX, but did not explain why they dipped at the 70% recovery. No changes were made. This trend may indicate membrane was not completely stabilized prior to operation with test water.
Note on CY31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on CY32: Gary Puetz: The consultant did verify the permeate concentrations of TOC, UV, THM, HAA, and TOX, but did not explain why they dipped at the 70% recovery. No changes were made. This trend may indicate membrane was not completely stabilized prior to operation with test water.
Note on CY37: Gary Puetz: The consultant did verify the permeate concentrations of TOC, UV, THM, HAA, and TOX, but did not explain why they dipped at the 70% recovery. No changes were made. This trend may indicate membrane was not completely stabilized prior to operation with test water.
Note on CY47: Gary Puetz: The consultant did verify the permeate concentrations of TOC, UV, THM, HAA, and TOX, but did not explain why they dipped at the 70% recovery. No changes were made. This trend may indicate membrane was not completely stabilized prior to operation with test water.
Note on CY48: Gary Puetz: The consultant did verify the permeate concentrations of TOC, UV, THM, HAA, and TOX, but did not explain why they dipped at the 70% recovery. No changes were made. This trend may indicate membrane was not completely stabilized prior to operation with test water.
Note on DL31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DQ10: Gary Puetz: The consultant did verify the water quality parameters including TDS, but did not explain the large mass balance error for the 90% recovery run. No changes were made.
Note on DV31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on EF31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.

## SR40. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Lee County Utilities | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.72985 | [45 empty] | Recovery during sample collection (decimal) | 0.73 | [10 empty] | Recovery during sample collection (decimal) | 0.85 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.33 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | FL 536-4048 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | PAC | 0 mg/L | plant | Sampling date | MM/DD/YY | 1999-03-08 | 1999-03-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.75 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.59 | [7 empty] | Feed flow rate during sample collection (mL/min) | 11.71 | [7 empty] | Feed flow rate during sample collection (mL/min) | 18.58 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24 |  |  | LSI | Coagulation | 135 mg/L aluminum sulfate (Al2(SO4)3 14H2O) | plant | Sampling time | hh:mm | 12:00 | 9:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [7 empty] | Influent flow rate during sample collection (mL/min) | 279 | [6 empty] | SDS-THM4F, ug/L | 324.65 | 324.65 | 324.65 | 324.65 | SDS-THM4F, ug/L | 324.65 | 324.65 | 324.65 | 324.65 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 210 |  |  | Dissolved iron (mg/L) | Coagulation | Organic Polymer LC 214 PWG, 0.44 mg/L | plant | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 38.2 | 57.6 | 24.7 | 17.8 | SDS-THM4p, ug/L | 38.2 | 57.6 | 24.7 | 17.8 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) | Cartridge filtration | 5 micron filter | bench | pH | --- | 7.6 | 7.6 | 7.6 | 0 | 1999-03-08 | 12:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-09 | 10:30 | 0 | 23.1 | 57 | 58 | 272 | 6.33 | 2.97 |  | 9.3 | 0.18779 | 0.68065 | 28.2473 | 14.4479 | 14.8374 | 706.8758 | 187.6981 | 694.7935 | 5.1314 | 52.3686 | 0.28333 |  |  |  | 137 | 353 | 298 | 814.9293 | -173.4662 | 61.2447 | 807.0409 | 83.0244 | BMRL | 0.168 | 0.156 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 112.9 | 112.9 | 112.9 | 112.9 | SDS-HAA5F, ug/L | 112.9 | 112.9 | 112.9 | 112.9 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23301 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23.5 | 24 | 23.75 | 2.1053 | 1999-03-08 | 12:30 | 0.5 | 23.6 | 50 | 51 | 272 | 5.05 | 2.45 | 7.5 | 0.18779 | 0.67333 | 35.2667 | 11.5264 | 11.6634 | 0 | 0 | 0 | 0 | 50.5 | 0.23096 | 1999-03-09 | 11:00 | 0.5 | 23.1 | 55 | 56 | 272 | 6.11 | 2.2 |  | 8.31 | 0.18779 | 0.73526 | 31.7316 | 13.9457 | 14.3217 | 768.3202 | 204.1376 | 755.6469 | 5.5785 | 49.9215 | 0.28688 |  |  |  | 162 | 353 | 473 | 885.3477 | -87.1771 | 54.1726 | 877.2234 | 81.5326 | BMRL | 0.171 | 0.306 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 4.2 | 6.1 | 2.5 | 1.9 | SDS-HAA5p, ug/L | 4.2 | 6.1 | 2.5 | 1.9 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 218 | 216 | 217 | 0.92166 | 1999-03-08 | 13:30 | 1.5 | 23.6 | 60 | 61 | 272 | 6.74 | 2.88 | 9.62 | 0.18779 | 0.70062 | 27.2744 | 15.3837 | 15.5667 | 0 | 0 | 0 | 0 | 60.5 | 0.2573 | 1999-03-09 | 11:30 | 1 | 23.1 | 56 | 55 | 272 | 5.75 | 2.51 |  | 8.26 | 0.18779 | 0.69613 | 31.9298 | 13.1241 | 13.4779 | 722.8833 | 192.2562 | 711.666 | 5.2502 | 50.2498 | 0.26822 |  |  |  | 169 | 353 | 564 | 776.1594 | -37.6169 | 52.1924 | 769.7418 | 78.0446 | BMRL | 0.17 | 0.378 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1999-03-10 | 1999-03-11 | --- | --- | 1999-03-10 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-12 | 1999-03-12 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-13 | 1999-03-13 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-14 | 1999-03-14 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 892.5 | 892.5 | 892.5 | 892.5 | SDS-TOXF, ug Cl- /L | 892.5 | 892.5 | 892.5 | 892.5 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 354 | 353 | 353.5 | 0.28289 | 1999-03-08 | 14:00 | 2 | 23.6 | 60 | 61 | 272 | 7.07 | 2.17 | 9.24 | 0.18779 | 0.76515 | 28.4372 | 16.1369 | 16.3288 | 0 | 0 | 0 | 0 | 60.5 | 0.2699 | 1999-03-09 | 12:30 | 2 | 23.2 | 54 | 54 | 272 | 5.38 | 1.2 |  | 6.58 | 0.18779 | 0.81763 | 40.3374 | 12.2796 | 12.5734 | 883.646 | 235.2518 | 870.8211 | 6.4198 | 47.5802 | 0.26426 |  |  |  | 181 | 353 | 723 | 1126.875 | -55.861 | 48.7977 | 1117.5206 | 83.8034 | BMRL | 0.171 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 10:30 | 10:00 | --- | --- | 10:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:20 | 16:20 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:30 | 17:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:45 | 15:45 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 51.5 | 66 | 36 | 27 | SDS-TOXp, ug Cl- /L | 51.5 | 66 | 36 | 27 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 268 | 268 | 268 | 0 | 1999-03-08 | 14:30 | 2.5 | 23.6 | 60 | 61 | 272 | 7.07 | 3.87 | 10.94 | 0.18779 | 0.64625 | 23.8629 | 16.1369 | 16.3288 | 0 | 0 | 0 | 0 | 60.5 | 0.2699 | 1999-03-09 | 14:00 | 3.5 | 23.3 | 54 | 54 | 272 | 5.23 | 1.27 |  | 6.5 | 0.18779 | 0.80462 | 40.8462 | 11.9372 | 12.1868 | 862.8588 | 229.8125 | 850.6866 | 6.2696 | 47.7304 | 0.25532 |  |  |  | 212 | 353 | 783 | 936.2126 | -19.5674 | 40.0283 | 929.25 | 77.1859 | BMRL | 0.171 | 0.654 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 24 | 47.5 | --- | --- | 24 | --- | --- | --- | --- | --- | Operation time | hh.hh | 77.83 | 77.83 | --- | --- | --- | --- | --- | Operation time | hh.hh | 103 | 103 | --- | --- | --- | --- | --- | Cumulative time | hr | 125.25 | 125.25 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 9.55 | 9.55 | 9.55 | 9.55 | SDS-CDF, mg/L | 9.55 | 9.55 | 9.55 | 9.55 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 212 | 238 | 225 | 11.5556 | 1999-03-08 | 14:45 | 2.75 | 23.6 | 60 | 61 | 272 | 7.2 | 3.55 | 10.75 | 0.18779 | 0.66977 | 24.3023 | 16.4336 | 16.6291 | 0 | 0 | 0 | 0 | 60.5 | 0.27486 | 1999-03-09 | 14:45 | 4.25 | 23.3 | 54 | 55 | 272 | 5.88 | 2.23 |  | 8.11 | 0.18779 | 0.72503 | 32.5388 | 13.4208 | 13.7014 | 755.7822 | 200.9338 | 743.7877 | 5.4885 | 49.0115 | 0.27955 |  |  |  | 210 | 354 | 791 | 731.8767 | 7.4745 | 40.5941 | 726.2358 | 71.0838 | BMRL | 0.17 | 0.662 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 8 | 8.1 | 8.05 | 1.2422 | 8.3 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.4 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8.3 | --- | --- | --- | --- | --- | pH | --- | 7.8 | 8.2 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.97 | 1.26 | 0.85 | 0.85 | SDS-CDp, mg/L | 0.97 | 1.26 | 0.85 | 0.85 | Labor Rate + Fringe ($/work-hour) | 28
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 4.55 | 68.925 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.218 | 0.218 | 0.218 | 0 | 1999-03-08 | 15:00 | 3 | 23.6 | 55 | 56 | 272 | 6.2 | 2.72 | 8.92 | 0.18779 | 0.69507 | 29.4933 | 14.1512 | 14.3195 | 0 | 0 | 0 | 0 | 55.5 | 0.25801 | 1999-03-10 | 9:15 | 22.75 | 22.9 | 53 | 54 | 272 | 4.56 | 0.8 |  | 5.36 | 0.18779 | 0.85075 | 49.7463 | 10.408 | 10.7519 | 939.5163 | 250.6901 | 927.9684 | 6.8305 | 46.6695 | 0.23038 | [27 empty] | Temperature | oC | 23.5 | 23.5 | 23.5 | 0 | 23.5 | --- | --- | --- | --- | --- | Temperature | oC | 23.4 | 23.4 | --- | --- | --- | --- | --- | Temperature | oC | 23.5 | 23.5 | --- | --- | --- | --- | --- | Temperature | oC | 23.5 | 23.5 | --- | --- | --- | --- | --- | TOCF, mg/L | 7.75 | 7.75 | 7.75 | 7.75 | TOCF, mg/L | 7.75 | 7.75 | 7.75 | 7.75 | Labor Overhead Factor (% of labor) | NA
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 11.55 | 75.925 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | 0.1 | 0.19 | 0.145 | 62.069 | 1999-03-08 | 15:30 | 3.5 | 23.6 | 55 | 56 | 272 | 6.45 | 2.38 | 8.83 | 0.18779 | 0.73046 | 29.8041 | 14.7218 | 14.8969 | 0 | 0 | 0 | 0 | 55.5 | 0.26841 | 1999-03-10 | 9:45 | 23.25 | 22.9 | 54 | 54 | 272 | 5 | 11 |  | 16 | 0.18779 | 0.3125 | 16 | 11.4122 | 11.7894 | 458.6243 | 122.2265 | 452.4405 | 3.3331 | 50.6669 | 0.23268 | [27 empty] | Alkalinity | mg/L as CaCO3 | 84 | 102 | 93 | 19.3548 | 326 | 552.2593 | -69.4047 | 57.1429 | 547.483 | 83.0132 | Alkalinity | mg/L as CaCO3 | 216 | 344 | 222.6667 | 35.2713 | 0.46083 | 222.6084 | 2.9686 | Alkalinity | mg/L as CaCO3 | 72 | 246 | 367.9184 | -49.5603 | 66.8203 | 364.7738 | 80.2617 | Alkalinity | mg/L as CaCO3 | 66 | 208 | 291.3731 | -40.0832 | 69.5853 | 288.8967 | 77.1545 | TOCp, mg/L | 0.6 | 0.7 | 0.6 | BMRL | TOCp, mg/L | 0.6 | 0.7 | 0.6 | BMRL | Electric Rate ($/kW-h) | 0.05
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 3.15 | 67.525 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 7.5 | 8 | 7.75 | 6.4516 | 1999-03-08 | 15:45 | 3.75 | 23.6 | 55 | 56 | 272 | 6.37 | 2.61 | 8.98 | 0.18779 | 0.70935 | 29.2895 | 14.5392 | 14.7121 | 0 | 0 | 0 | 0 | 55.5 | 0.26508 | 1999-03-10 | 10:00 | 23.5 | 23 | 54 | 54 | 272 | 5.71 | 4.07 |  | 9.78 | 0.18779 | 0.58384 | 26.8119 | 13.0328 | 13.4238 | 618.6015 | 164.5398 | 609.0695 | 4.493 | 49.507 | 0.27115 |  |  |  | 176 | 352 | 570 | 602.5233 | -5.7058 | 50.2122 | 598.0464 | 70.5708 | BMRL | 0.169 | 0.485 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 202 | 192 | 197 | 5.0761 | 710 | 776.6296 | -9.3845 | 44.2716 | 770.6016 | 74.4356 | Total dissolved solids | mg/L | 264 | 1250 | 860.6667 | 31.1467 | 25.3182 | 855.4552 | 69.1392 | Total dissolved solids | mg/L | 187 | 636 | 526.7959 | 17.1705 | 47.1004 | 523.1851 | 64.2574 | Total dissolved solids | mg/L | 180 | 449 | 438.9552 | 2.2371 | 49.0806 | 436.1098 | 58.726 | UV254 F, cm-1 | 0.1695 | 0.1695 | 0.1695 | 0.1695 | UV254 F, cm-1 | 0.1695 | 0.1695 | 0.1695 | 0.1695 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 2.55 | 66.925 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.168 | 0.171 | 0.1695 | 1.7699 | 1999-03-08 | 16:00 | 4 | 23.6 | 55 | 56 | 272 | 6.47 | 2.56 | 9.03 | 0.18779 | 0.7165 | 29.1218 | 14.7674 | 14.9431 | 0 | 0 | 0 | 0 | 55.5 | 0.26924 | 1999-03-10 | 10:30 | 24 | 23 | 54 | 54 | 272 | 5.74 | 2.69 |  | 8.43 | 0.18779 | 0.6809 | 31.2657 | 13.1012 | 13.4943 | 706.7254 | 187.964 | 695.7781 | 5.1329 | 48.8671 | 0.27614 |  |  |  | 214 | 353 | 624 | 651.1691 | -4.354 | 39.4625 | 646.5564 | 66.9016 | BMRL | 0.17 | 0.474 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 126 | 130 | 128 | 3.125 | 808 | 646.5185 | 19.9853 | 52.2388 | 641.126 | 80.0351 | Total hardness | mg/L as CaCO3 | 232 | 958 | 472 | 50.7307 | 13.4328 | 469.9038 | 50.6282 | Total hardness | mg/L as CaCO3 | 104 | 684 | 438.6939 | 35.8635 | 61.194 | 435.1372 | 76.0995 | Total hardness | mg/L as CaCO3 | 102 | 470 | 349.7612 | 25.5827 | 61.9403 | 347.0388 | 70.6085 | UV254 p, cm-1 | #DIV/0! | 0.013 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.013 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.24 | 2.1375 | 2.1888 | 4.683 | 1999-03-08 | 16:30 | 4.5 | 23.6 | 55 | 56 | 272 | 6.57 | 2.55 | 9.12 | 0.18779 | 0.72039 | 28.8246 | 14.9957 | 15.174 | 0 | 0 | 0 | 0 | 55.5 | 0.27341 | 1999-03-10 | 11:00 | 24.5 | 23 | 53 | 54 | 272 | 5.7 | 2 |  | 7.7 | 0.18779 | 0.74026 | 34.3247 | 13.0099 | 13.4002 | 774.1244 | 205.9125 | 762.217 | 5.6226 | 47.8774 | 0.27989 |  |  |  | 189 | 353 | 590 | 822.325 | -39.3771 | 46.5347 | 815.6891 | 76.8294 | BMRL | 0.17 | 0.479 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 86 | 74 | 80 | 15 | 682 | 617.037 | 9.5254 | 64.4444 | 611.452 | 86.9164 | Calcium hardness | mg/L as CaCO3 | 186 | 832 | 446 | 46.3942 | 17.3333 | 443.7291 | 58.0825 | Calcium hardness | mg/L as CaCO3 | 68 | 488 | 388.4082 | 20.4082 | 69.7778 | 385.0033 | 82.3378 | Calcium hardness | mg/L as CaCO3 | 62 | 386 | 305.2836 | 20.911 | 72.4444 | 302.6103 | 79.5116 | BromideF, ug/L | 305 | 305 | 305 | 305 | BromideF, ug/L | 305 | 305 | 305 | 305 | Current Process Water Rate ($/1000 gal) | 0.8
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 300 | 310 | 305 | 3.2787 | 1999-03-08 | 17:15 | 5.25 | 23.6 | 55 | 56 | 272 | 6.53 | 2.24 | 8.77 | 0.18779 | 0.74458 | 30.0148 | 14.9044 | 15.0816 | 0 | 0 | 0 | 0 | 55.5 | 0.27174 | 1999-03-10 | 12:00 | 25.5 | 23.3 | 53 | 54 | 272 | 5.73 | 2.27 |  | 8 | 0.18779 | 0.71625 | 33 | 13.0784 | 13.3518 | 745.3836 | 198.2512 | 733.8576 | 5.4137 | 48.0863 | 0.27766 |  |  |  | 191 | 353 | 588 | 763.6872 | -29.8788 | 45.9689 | 757.6551 | 74.7906 | BMRL | 0.17 | 0.482 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.108 | 0.106 | 0.107 | 1.8692 | 0.336 | 0.51811 | -54.1997 | 50.9174 | 0.51384 | 79.1762 | Turbidity | ntu | 0.137 | 0.396 | 0.677 | -70.9596 | 37.156 | 0.67228 | 79.6217 | Turbidity | ntu | 0.087 | 0.291 | 0.35435 | -21.7687 | 60.0917 | 0.35151 | 75.2494 | Turbidity | ntu | 0.069 | 0.241 | 0.29139 | -20.9079 | 68.3486 | 0.28894 | 76.12 | Bromidep, ug/L | 220 | 280 | 210 | 180 | Bromidep, ug/L | 220 | 280 | 210 | 180 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 10 | 11 | 10.5 | 9.5238 | 1999-03-08 | 18:00 | 6 | 23.6 | 55 | 56 | 272 | 6.58 | 2.33 | 8.91 | 0.18779 | 0.7385 | 29.5275 | 15.0185 | 15.1971 | 0 | 0 | 0 | 0 | 55.5 | 0.27382 | 1999-03-10 | 13:30 | 27 | 23.3 | 53 | 55 | 272 | 5.32 | 1.2 |  | 6.52 | 0.18779 | 0.81595 | 40.7178 | 12.1426 | 12.3965 | 880.8555 | 234.5476 | 868.2145 | 6.3999 | 47.6001 | 0.26043 |  |  |  | 205 | 353 | 688 | 1011.85 | -47.0712 | 42.0085 | 1003.9595 | 79.5808 | BMRL | 0.168 | 0.634 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.06 | 0.15 | 0.105 | 85.7143 | NA | 0.25315 | #VALUE! | 27.5862 | 0.25161 | 58.2683 | Ammonia | mg NH3-N / L | 0.11 | NA | 0.34333 | #VALUE! | 24.1379 | 0.3413 | 67.7698 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217 | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.95 | 0.95 | 0.95 | 0 | 1999-03-09 | 9:00 | 21 | 23.6 | 55 | 56 | 272 | 6.51 | 2.1 | 8.61 | 0.18779 | 0.7561 | 30.5912 | 14.8587 | 15.0355 | 0 | 0 | 0 | 0 | 55.5 | 0.27091 | 1999-03-10 | 14:30 | 28 | 23.5 | 53 | 54 | 272 | 5.02 | 1.25 |  | 6.27 | 0.18779 | 0.80064 | 42.3812 | 11.4579 | 11.6285 | 856.5007 | 228.2508 | 844.9058 | 6.2245 | 47.2755 | 0.24597 |  |  |  | 187 | 352 | 733 | 1022.164 | -39.4494 | 47.1004 | 1014.4572 | 81.5665 | BMRL | 0.17 | 0.673 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | 0.7 | 0.5 | 0.6 | 33.3333 | 25.3 | 27.0815 | -7.0414 | 92.2581 | 26.8061 | 97.7617 | Total organic carbon | mg/L | 0.7 | 87.1 | 47.7 | 45.2354 | 90.9677 | 47.2895 | 98.5198 | Total organic carbon | mg/L | 0.6 | 16.6 | 15.1918 | 8.4829 | 92.2581 | 15.0368 | 96.0098 | Total organic carbon | mg/L | BMRL | 9 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 93 | 216 | 72 | 66 | Alkp, mg/L CaCO3 | 93 | 216 | 72 | 66
Plant Name | North (Olga) Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 9.05 | 10.05 | 9.55 | 10.4712 | 1999-03-09 | 9:15 | 21.25 | 23.6 | 65 | 66 | 272 | 7.9 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 18.0313 | 18.2458 | #VALUE! | #VALUE! | #VALUE! | 0 | 65.5 | 0.27856 | 1999-03-10 | 15:30 | 29 | 23.4 | 53 | 54 | 272 | 5.48 | 1.4 |  | 6.88 | 0.18779 | 0.79651 | 38.5349 | 12.5078 | 12.7316 | 850.8146 | 226.4488 | 838.2355 | 6.1808 | 47.3192 | 0.26906 |  |  |  | 192 | 353 | 790 | 985.6571 | -24.7667 | 45.686 | 977.6622 | 80.3613 | BMRL | 0.168 | 0.707 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.61 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.013 | 2.034 | 1.0563 | 48.0662 | 92.3304 | 1.0472 | 98.7586 | UV254 | cm-1 | BMRL | 0.449 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.239 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268 | T-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268
Treatment Plant Category | SOFT | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | 1999-03-09 | 9:30 | 21.5 | 23.6 | 45 | 46 | 272 | 5.35 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 12.2111 | 12.3563 | #VALUE! | #VALUE! | #VALUE! | 0 | 45.5 | 0.27157 | 1999-03-10 | 16:30 | 30 | 23.4 | 53 | 54 | 272 | 5.47 | 4.42 |  | 9.89 | 0.18779 | 0.55308 | 26.5025 | 12.485 | 12.7084 | 594.9913 | 158.3644 | 586.2106 | 4.3224 | 49.1776 | 0.25842 |  |  |  | 170 | 353 | 634 | 580.5916 | 8.424 | 51.9095 | 576.4631 | 70.5098 | BMRL | 0.168 | 0.492 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 2.4111 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8571 | 2.3352 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.7048 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 2.6556 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 128 | 232 | 104 | 102 | T-Hdp, mg/L CaCO3 | 128 | 232 | 104 | 102
Process Train Name | Enhanced Coagulation/Lime softening | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | 1999-03-09 | 9:45 | 21.75 | 23.6 | 55 | 56 | 272 | 6.7 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 15.2924 | 15.4743 | #VALUE! | #VALUE! | #VALUE! | 0 | 55.5 | 0.27882 | 1999-03-10 | 18:00 | 31.5 | 23.4 | 53 | 54 | 272 | 5.56 | 1.75 |  | 7.31 | 0.18779 | 0.7606 | 36.2093 | 12.6904 | 12.9175 | 800.1508 | 212.9175 | 788.1471 | 5.8123 | 47.6877 | 0.27088 |  |  |  | 181 | 352 | 679 | 901.5571 | -32.7772 | 48.7977 | 894.1926 | 79.7583 | BMRL | 0.17 | 0.551 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 230 | 210 | 220 | 9.0909 | --- | 534.8148 | --- | 27.8689 | 531.5408 | 58.6109 | Bromide | mg/L | 280 | --- | 446.6667 | --- | 8.1967 | 445.2109 | 37.1085 | Bromide | mg/L | 210 | --- | 403.8776 | --- | 31.1475 | 401.8173 | 47.7374 | Bromide | mg/L | 180 | --- | 366.5672 | --- | 40.9836 | 364.5171 | 50.6196 | Ca-HdF, mg/L CaCO3 | 225 | 225 | 225 | 225 | Ca-HdF, mg/L CaCO3 | 225 | 225 | 225 | 225
ICR Treatment Plant Identification Number | 1095 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | 1999-03-09 | 10:00 | 22 | 23.6 | 55 | 56 | 272 | 6.57 | 2.2 | 8.77 | 0.18779 | 0.74914 | 30.0148 | 14.9957 | 15.174 | 0 | 0 | 0 | 0 | 55.5 | 0.27341 | 1999-03-10 | 18:45 | 32.25 | 23.4 | 53 | 54 | 272 | 5.75 | 1.98 |  | 7.73 | 0.18779 | 0.74386 | 34.1876 | 13.1241 | 13.3589 | 778.671 | 207.0933 | 766.588 | 5.6554 | 47.8446 | 0.27921 |  |  |  | 192 | 352 | 671 | 822.5025 | -22.5786 | 45.686 | 815.8382 | 76.4659 | BMRL | 0.17 | 0.594 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 1.75 | 1.75 | 1.75 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.25 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.75 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 80 | 186 | 68 | 62 | Ca-Hdp, mg/L CaCO3 | 80 | 186 | 68 | 62
PWSID Number of Plant (if assigned) | FL 536-4048 | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 890 | 895 | 892.5 | 0.56022 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 9:00 | 46.5 | 23 | 52 | 53 | 272 | 4.23 | 0.51 |  | 4.74 | 0.18779 | 0.89241 | 56.384 | 9.6547 | 9.9444 | 1021.8838 | 272.9147 | 1010.2362 | 7.4315 | 45.0685 | 0.22065 | [27 empty] | SDS-Free Cl2 residual | mg/L | 0.72 | 0.84 | 0.78 | 15.3846 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.99 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 26 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 170 | 160 | 165 | 6.0606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 9:30 | 47 | 23 | 55 | 56 | 272 | 4.72 | 2 |  | 6.72 | 0.18779 | 0.70238 | 39.4762 | 10.7731 | 11.0963 | 728.9376 | 194.4163 | 719.6621 | 5.2988 | 50.2012 | 0.22104 |  |  |  | 267 | 353 | 1326 | 557.64 | 57.9457 | 24.4696 | 555.1183 | 51.9021 | 0.011 | 0.167 | 2.153 | 0.54356 | 74.7534 | 93.5103 | 0.53894 | 97.959 | [8 empty] | SDS-Cl2 demand | mg/L | 1.03 | 0.91 | 0.97 | 12.3711 | --- | 32.7478 | --- | 89.8429 | 32.4173 | 97.0078 | SDS-Cl2 demand | mg/L | 1.26 | --- | 56.5267 | --- | 86.8063 | 56.0439 | 97.7518 | SDS-Cl2 demand | mg/L | 0.85 | --- | 18.6051 | --- | 91.0995 | 18.4164 | 95.3846 | SDS-Cl2 demand | mg/L | 0.85 | --- | 13.8351 | --- | 91.0995 | 13.6924 | 93.7922 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 100 | 100 | 100 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 10:00 | 47.5 | 23 | 55 | 56 | 272 | 4.9 | 1.62 |  | 6.52 | 0.18779 | 0.75153 | 40.7178 | 11.184 | 11.5195 | 787.6381 | 209.9686 | 777.2315 | 5.7247 | 49.7753 | 0.23143 |  |  |  | 248 | 353 | 968 | 672.6049 | 30.516 | 29.8444 | 668.7804 | 62.9176 | 0.009 | 0.169 | 1.752 | 0.65496 | 62.6163 | 94.6903 | 0.64914 | 98.6136 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 88.2004 | 94.6078 | 84.2307 | 82.3366 | Qp/QT (THM4), % | 100.768 | 108.0884 | 96.2327 | 94.0688
State Approved Plant Capacity (MGD) | 5 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 53 | 55 | 54 | 3.7037 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 11:00 | 48.5 | 23 | 55 | 56 | 272 | 5.73 | 2.63 |  | 8.36 | 0.18779 | 0.68541 | 31.5359 | 13.0784 | 13.4708 | 711.4217 | 189.2183 | 700.4209 | 5.167 | 50.333 | 0.26763 |  |  |  | 228 | 353 | 830 | 626.9278 | 24.4665 | 35.5021 | 622.7258 | 63.3868 | BMRL | 0.17 | 1.15 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | 5.8 | 5.5 | 5.65 | 5.3097 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 12:00 | 49.5 | 23.1 | 55 | 56 | 272 | 5.65 | 2.02 |  | 7.67 | 0.18779 | 0.73664 | 34.4628 | 12.8958 | 13.2435 | 769.5965 | 204.7363 | 757.8632 | 5.5899 | 49.9101 | 0.26535 | 7 | 7 | 7.3 | 231 | 353 | 424 | 696.1361 | -64.1831 | 34.6535 | 691.3052 | 66.5849 | BMRL | 0.168 | 0.905 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 48 | 48 | 48 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 48 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 17.0262 | 11.8589 | 19.9093 | 21.5063 | SDS-HAA5b, ug/L | NA | NA | 6.6591 | 8.4837
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 328.8 | 320.5 | 324.65 | 2.5566 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 12:45 | 50.25 | 23.3 | 55 | 56 | 272 | 5.69 | 4.85 |  | 10.54 | 0.18779 | 0.53985 | 24.8065 | 12.9871 | 13.2586 | 585.5051 | 155.7452 | 576.5149 | 4.2526 | 51.2474 | 0.25872 | 7.2 | 7.1 | 7.3 | 188 | 352 | 621 | 547.6639 | 11.8094 | 46.8175 | 543.902 | 65.4349 | BMRL | 0.169 | 0.725 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | 49 | 54 | 51.5 | 9.7087 | --- | 3166.3148 | --- | 94.2297 | 3133.9213 | 98.3567 | SDS-TOX | mg Cl- /L | 66 | --- | 5576 | --- | 92.605 | 5527.8736 | 98.8061 | SDS-TOX | mg Cl- /L | 36 | --- | 1783.9592 | --- | 95.9664 | 1765.3845 | 97.9608 | SDS-TOX | mg Cl- /L | 27 | --- | 1318.791 | --- | 96.9748 | 1304.5966 | 97.9304 | SDS-TOXb, ug Cl- /L | 150.7348 | 110.5669 | 171.064 | 179.8763 | SDS-TOXb, ug Cl- /L | NA | NA | 68.2669 | 78.3349
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 6.3 | 5.4 | 5.85 | 15.3846 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 14:00 | 51.5 | 23.3 | 55 | 56 | 272 | 6.46 | 4.22 |  | 10.68 | 0.18779 | 0.60487 | 24.4682 | 14.7446 | 15.0529 | 636.1514 | 168.8578 | 625.0532 | 4.6174 | 50.8826 | 0.29584 | 7.1 | 7.1 | 7.4 | 201 | 351 | 426 | 586.9479 | -37.7812 | 43.14 | 582.3647 | 65.4855 | BMRL | 0.171 | 0.429 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 0.9 | 1.9 | 1.4 | 71.4286 | --- | 607.3259 | --- | 99.1515 | 601.0244 | 99.7671 | SDS-CHCl3 | mg/L | 1.7 | --- | 1090.3667 | --- | 98.9697 | 1080.8578 | 99.8427 | SDS-CHCl3 | mg/L | 1.7 | --- | 334.9653 | --- | 98.9697 | 331.4239 | 99.4871 | SDS-CHCl3 | mg/L | 1.2 | --- | 245.6776 | --- | 99.2727 | 242.9912 | 99.5062 | SDS-CDb, mg/L | 1.9824 | 1.707 | 2.2219 | 2.3867 | SDS-CDb, mg/L | NA | NA | 1.1778 | 1.366
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 43 | 50 | 46.5 | 15.0538 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 15:00 | 52.5 | 23.3 | 54 | 54 | 272 | 5.7 | 1.77 |  | 7.47 | 0.18779 | 0.76305 | 35.4123 | 13.0099 | 13.2819 | 803.5641 | 213.7433 | 791.2039 | 5.8364 | 48.1636 | 0.27577 | 7.1 | 7 | 7.3 | 218 | 353 | 610 | 789.8559 | -29.4846 | 38.331 | 783.8641 | 72.1891 | BMRL | 0.17 | 0.497 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 2.9 | 3.7 | 3.3 | 24.2424 | --- | 361.4481 | --- | 96.7 | 357.7235 | 99.0775 | SDS-BDCM | mg/L | 5.9 | --- | 633.2333 | --- | 94.1 | 627.754 | 99.0601 | SDS-BDCM | mg/L | 3 | --- | 200.9592 | --- | 97 | 198.8556 | 98.4914 | SDS-BDCM | mg/L | 2.4 | --- | 148.0716 | --- | 97.6 | 146.471 | 98.3615 | TOCb, mg/L | 1.4437 | 1.0802 | 1.7275 | #VALUE! | TOCb, mg/L | NA | NA | 0.86936 | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 43 | 47 | 45 | 8.8889 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 16:30 | 54 | 23 | 53 | 54 | 272 | 5.7 | 3.25 |  | 8.95 | 0.18779 | 0.63687 | 29.3911 | 13.0099 | 13.4002 | 663.8092 | 176.5693 | 653.5987 | 4.8213 | 48.6787 | 0.27528 | 7 | 7.1 | 7.3 | 210 | 354 | 608 | 605.1769 | 0.46432 | 40.5941 | 601.0363 | 65.0603 | BMRL | 0.171 | 0.481 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 12 | 13 | 12.5 | 8 | --- | 166.2037 | --- | 76.8519 | 164.6052 | 92.4061 | SDS-DBCM | mg/L | 21 | --- | 241 | --- | 61.1111 | 239.0784 | 91.2163 | SDS-DBCM | mg/L | 8 | --- | 101.8776 | --- | 85.1852 | 100.88 | 92.0698 | SDS-DBCM | mg/L | 6.1 | --- | 77.5925 | --- | 88.7037 | 76.807 | 92.058 | UV254 b, cm-1 | #DIV/0! | 0.021439 | #VALUE! | #VALUE! | UV254 b, cm-1 | NA | NA | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | 8.6 | 2.5 | 5.55 | 109.9099 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-11 | 17:30 | 55 | 23.3 | 53 | 54 | 272 | 5.68 | 2.8 |  | 8.48 | 0.18779 | 0.66981 | 31.0755 | 12.9643 | 13.2353 | 695.3674 | 184.9738 | 684.7092 | 5.0506 | 48.4494 | 0.27318 | 7.1 | 7.2 | 7.3 | 203 | 353 | 601 | 658.8 | -9.6173 | 42.5743 | 654.0409 | 68.9622 | BMRL | 0.169 | 0.489 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 21 | 21 | 21 | 0 | --- | -35.8519 | --- | -271.6814 | -35.2606 | 159.5566 | SDS-CHBr3 | mg/L | 29 | --- | -126.6667 | --- | -413.2743 | -125.307 | 123.1432 | SDS-CHBr3 | mg/L | 12 | --- | -0.95918 | --- | -112.3894 | -0.82147 | 1560.791 | SDS-CHBr3 | mg/L | 8.1 | --- | 4.4433 | --- | -43.3628 | 4.4835 | -80.6639 | Bromideb, ug/L | 230.0297 | 281.3481 | 224.9808 | 202.0792 | Bromideb, ug/L | NA | NA | 213.5789 | 187.414
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 10 | 10 | 10 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 9:00 | 70.5 | 23 | 52 | 53 | 272 | 5.04 | 0.67 |  | 5.71 | 0.18779 | 0.88266 | 46.6357 | 11.5035 | 11.8486 | 1002.7013 | 267.1974 | 989.0728 | 7.2869 | 45.2131 | 0.26206 | 7.2 | 7.2 | 7.4 | 261 | 354 | 801 | 1049.3209 | -31.0014 | 26.1669 | 1042.0173 | 74.9524 | BMRL | 0.17 | 0.96 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 36.8 | 39.6 | 38.2 | 7.3298 | --- | 1099.1259 | --- | 88.2335 | 1088.0925 | 96.4893 | SDS-THM4 | mg/L | 57.6 | --- | 1837.9333 | --- | 82.2578 | 1822.3832 | 96.8393 | SDS-THM4 | mg/L | 24.7 | --- | 636.8429 | --- | 92.3918 | 630.3379 | 96.0815 | SDS-THM4 | mg/L | 17.8 | --- | 475.7851 | --- | 94.5172 | 470.7527 | 96.2188 | Alkb, mg/L CaCO3 | 107.6315 | 216.0539 | 94.8655 | 92.6717 | Alkb, mg/L CaCO3 | NA | NA | 77.4626 | 74.9562
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 27 | 28 | 27.5 | 3.6364 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 11:00 | 72.5 | 23.4 | 54 | 56 | 272 | 5.24 | 1.77 |  | 7.01 | 0.18779 | 0.7475 | 37.8017 | 11.96 | 12.174 | 782.8072 | 208.4859 | 771.743 | 5.6879 | 49.3121 | 0.24688 | 7.3 | 7.2 | 7.5 | 191 | 353 | 836 | 834.5734 | 0.17064 | 45.9689 | 828.3743 | 76.9428 | BMRL | 0.17 | 0.809 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 144.5195 | 233.9412 | 129.8616 | 131.3212 | T-Hdb, mg/L CaCO3 | NA | NA | 110.1784 | 111.8459
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | NR | 4.2 | 4.2 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 12:00 | 73.5 | 23.3 | 55 | 56 | 272 | 5.5 | 3.14 |  | 8.64 | 0.18779 | 0.63657 | 30.4815 | 12.5535 | 12.8159 | 663.421 | 176.5633 | 653.5764 | 4.8194 | 50.6806 | 0.25288 | 7.2 | 7.2 | 7.4 | 243 | 353 | 656 | 547.051 | 16.6081 | 31.2588 | 543.9769 | 55.329 | BMRL | 0.17 | 0.605 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 97.1094 | 188.103 | 92.7578 | 90.7913 | Ca-Hdb, mg/L CaCO3 | NA | NA | 73.9147 | 71.6679
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 14 | 13 | 13.5 | 7.4074 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 13:00 | 74.5 | 23.3 | 55 | 56 | 272 | 5.7 | 2.36 |  | 8.06 | 0.18779 | 0.7072 | 32.7469 | 13.0099 | 13.2819 | 735.0588 | 195.5213 | 723.7523 | 5.3388 | 50.1612 | 0.26479 | 7.2 | 7.2 | 7.3 | 174 | 353 | 676 | 787.0381 | -16.4258 | 50.7779 | 780.6148 | 77.7099 | BMRL | 0.168 | 0.556 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 33 | 31 | 32 | 6.25 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 13:45 | 75.25 | 23 | 54 | 56 | 272 | 5.5 | 0.3 |  | 5.8 | 0.18779 | 0.94828 | 45.8966 | 12.5535 | 12.9301 | 1162.4508 | 309.3754 | 1145.2011 | 8.4445 | 46.5555 | 0.27773 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 110.9 | 114.9 | 112.9 | 3.543 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 14:30 | 76 | 23 | 54 | 56 | 272 | 5.45 | 0.75 |  | 6.2 | 0.18779 | 0.87903 | 42.871 | 12.4393 | 12.8125 | 995.9257 | 265.0928 | 981.2821 | 7.2351 | 47.7649 | 0.26824 | 7.4 | 7.1 | 7.5 | 195 | 354 | 670 | 1505.2667 | -124.6667 | 44.8373 | 1492.1399 | 86.9315 | BMRL | 0.167 | 0.71 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | 4.3 | 4.1 | 4.2 | 4.7619 | --- | 25.6815 | --- | 58 | 25.4581 | 83.5023 | SDS-DBAA* | mg/L | 6.1 | --- | 32.1 | --- | 39 | 31.8729 | 80.8615 | SDS-DBAA* | mg/L | 2.5 | --- | 17.8061 | --- | 75 | 17.6435 | 85.8305 | SDS-DBAA* | mg/L | 1.9 | --- | 13.9896 | --- | 81 | 13.8567 | 86.2882 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 137.9 | 142.9 | 140.4 | 3.5613 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 15:00 | 76.5 | 23 | 54 | 56 | 272 | 5.25 | 1.09 |  | 6.34 | 0.18779 | 0.82808 | 41.9022 | 11.9828 | 12.3423 | 900.7274 | 239.8852 | 887.9722 | 6.5446 | 48.4554 | 0.25472 | 7.3 | 7.1 | 7.4 | 199 | 353 | 788 | 1097.6514 | -39.2959 | 43.7058 | 1088.9787 | 81.726 | BMRL | 0.168 | 0.837 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | 1.4 | 1.5 | 1.45 | 6.8966 | --- | 97.9315 | --- | 94.7273 | 96.9281 | 98.504 | SDS-BCAA* | mg/L | 2.4 | --- | 169.7333 | --- | 91.2727 | 168.2718 | 98.5737 | SDS-BCAA* | mg/L | 1 | --- | 55.0816 | --- | 96.3636 | 54.5069 | 98.1654 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 54.1858 | 55.1498 | 53.3514 | 53.0631 | Qp/QT (HAA5), % | 79.0248 | 80.4307 | 77.808 | 77.3874
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 15:45 | 77.25 | 23 | 54 | 56 | 272 | 5.33 | 0.65 |  | 5.98 | 0.18779 | 0.8913 | 44.4849 | 12.1654 | 12.5304 | 1021.6202 | 272.0219 | 1006.9314 | 7.4225 | 47.5775 | 0.26337 | 7.3 | 7.1 | 7.6 | 202 | 355 | 856 | 1595.8 | -86.4252 | 42.8571 | 1582.1438 | 87.2325 | BMRL | 0.168 | 0.875 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TBAA | mg/L | NR | NR | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-THM4b, ug/L | 169.4347 | 177.3724 | 164.6223 | 161.826 | SDS-THM4b, ug/L | 98.2833 | 109.8598 | 91.265 | 87.1868
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 16:20 | 77.8333 | 23 | 54 | 56 | 272 | 5.33 | 0.48 |  | 5.81 | 0.18779 | 0.91738 | 45.8158 | 12.1654 | 12.5304 | 1081.4248 | 287.9458 | 1065.8761 | 7.857 | 47.143 | 0.2658 | 7.4 | 7.2 | 7.6 | 210 | 354 | 880 | 1946.9479 | -121.2441 | 40.5941 | 1929.9297 | 89.1188 | 0.013 | 0.167 | 0.92 | 1.9073 | -107.3154 | 92.3304 | 1.8887 | 99.3117 | [8 empty] | SDS-CDBAA | mg/L | 2.5 | 2.3 | 2.4 | 8.3333 | --- | 43.5111 | --- | 82.2222 | 43.0836 | 94.4294 | SDS-CDBAA | mg/L | 3.8 | --- | 68.4667 | --- | 71.8519 | 67.9018 | 94.4037 | SDS-CDBAA | mg/L | 2.2 | --- | 25.2612 | --- | 83.7037 | 25.0162 | 91.2057 | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-12 | 16:40 | 78.1667 | 23 | 54 | 56 | 272 | 5.35 | 1.38 |  | 6.73 | 0.18779 | 0.79495 | 39.416 | 12.2111 | 12.5774 | 848.3172 | 225.8649 | 836.0741 | 6.1633 | 48.8367 | 0.25754 | 7.6 | 7.1 | 7.6 | 202 | 354 | 895 | 940.837 | -5.1214 | 42.8571 | 933.5708 | 78.3626 | BMRL | 0.167 | 0.93 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | 1.5 | 1.4 | 1.45 | 6.8966 | --- | 114.5981 | --- | 95.4688 | 113.4214 | 98.7216 | SDS-DCBAA | mg/L | 2.2 | --- | 200.8667 | --- | 93.125 | 199.1314 | 98.8952 | SDS-DCBAA | mg/L | 1.5 | --- | 63.7449 | --- | 95.3125 | 63.0835 | 97.6222 | SDS-DCBAA | mg/L | 1.2 | --- | 47.1701 | --- | 96.25 | 46.665 | 97.4285 | SDS-TOXb, ug Cl- /L | 436.7971 | 436.6868 | 435.5448 | 433.2392 | SDS-TOXb, ug Cl- /L | 227.9011 | 227.7402 | 226.0747 | 222.7122
[44 empty] | 1999-03-12 | 17:10 | 78.6667 | 23 | 54 | 56 | 272 | 5.35 | 0.72 |  | 6.07 | 0.18779 | 0.88138 | 43.8105 | 12.2111 | 12.5774 | 1000.6083 | 266.4125 | 986.1673 | 7.2698 | 47.7302 | 0.26351 | 7.4 | 7.1 | 7.5 | 203 | 354 | 890 | 1471.7986 | -65.3706 | 42.5743 | 1459.3205 | 86.0894 | BMRL | 0.167 | 0.923 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 4.3 | 4.1 | 4.2 | 4.7619 | --- | 406.7926 | --- | 96.2799 | 402.6057 | 98.9568 | SDS-HAA5 | mg/L | 6.1 | --- | 718.1 | --- | 94.597 | 711.8811 | 99.1431 | SDS-HAA5 | mg/L | 2.5 | --- | 227.8061 | --- | 97.7857 | 225.4119 | 98.8909 | SDS-HAA5 | mg/L | 1.9 | --- | 167.5716 | --- | 98.3171 | 165.7512 | 98.8537 | SDS-CDb, mg/L | 4.9009 | 4.9781 | 4.9084 | 4.9335 | SDS-CDb, mg/L | 2.7697 | 2.8823 | 2.7807 | 2.8173
[44 empty] | 1999-03-13 | 9:15 | 94.75 | 23 | 54 | 56 | 272 | 3.72 | 0.54 |  | 4.26 | 0.18779 | 0.87324 | 62.8498 | 8.4907 | 8.7454 | 981.1208 | 262.3937 | 971.2912 | 7.1381 | 47.8619 | 0.18272 | 7.6 | 7.2 | 7.5 | 276 | 354 | 1263 | 887.3889 | 29.7396 | 21.9236 | 883.2081 | 68.7503 | 0.014 | 0.168 | 2.408 | 1.2407 | 48.475 | 91.7404 | 1.2323 | 98.8639 | [8 empty] | SDS-HAA6 | mg/L | 5.7 | 5.6 | 5.65 | 1.7699 | --- | 504.7241 | --- | 95.9758 | 499.5338 | 98.8689 | SDS-HAA6 | mg/L | 8.5 | --- | 887.8333 | --- | 93.9459 | 880.1529 | 99.0343 | SDS-HAA6 | mg/L | 3.5 | --- | 282.8878 | --- | 97.5071 | 279.9188 | 98.7496 | SDS-HAA6 | mg/L | 1.9 | --- | 208.6164 | --- | 98.6467 | 206.345 | 99.0792 | TOCb, mg/L | 3.8757 | 3.8619 | 3.9354 | #VALUE! | TOCb, mg/L | 2.0997 | 2.0796 | 2.1867 | #VALUE!
[44 empty] | 1999-03-13 | 12:45 | 98.25 | 23 | 54 | 55 | 272 | 3.66 | 0.61 |  | 4.27 | 0.18779 | 0.85714 | 62.7002 | 8.3538 | 8.6044 | 949.9332 | 254.0945 | 940.5701 | 6.9116 | 47.5884 | 0.18081 | 7.6 | 7.2 | 7.8 | 231 | 355 | 1300 | 1088.5 | 16.2692 | 34.6535 | 1082.7308 | 78.6651 | 0.011 | 0.167 | 2.54 | 1.1205 | 55.8858 | 93.5103 | 1.113 | 99.0117 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.083191 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.043626 | #VALUE! | #VALUE!
[44 empty] | 1999-03-13 | 13:45 | 99.25 | 23 | 54 | 55 | 272 | 4.4 | 0.42 |  | 4.82 | 0.18779 | 0.91286 | 55.4315 | 10.0428 | 10.344 | 1068.5504 | 285.2452 | 1055.8793 | 7.7697 | 46.7303 | 0.22136 | 7.6 | 7.2 | 7.8 | 226 | 353 | 1224 | 1689.2143 | -38.0077 | 36.0679 | 1677.3795 | 86.5266 | 0.012 | 0.168 | 2.416 | 1.8195 | 24.6896 | 92.9204 | 1.8049 | 99.3351 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 258.942 | 291.2125 | 254.3161 | 238.6712 | Bromideb, ug/L | 237.8289 | 284.8923 | 231.0824 | 208.2658
[44 empty] | 1999-03-13 | 15:00 | 100.5 | 23 | 54 | 55 | 272 | 5.2 | 1.95 |  | 7.15 | 0.18779 | 0.72727 | 37.042 | 11.8687 | 12.2248 | 757.8617 | 201.8644 | 747.2323 | 5.5068 | 48.9932 | 0.24952 | 7.5 | 7.3 | 7.7 | 192 | 354 | 892 | 784.1667 | 12.0889 | 45.686 | 778.5063 | 75.3374 | BMRL | 0.166 | 1.26 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 149.8096 | 216.4485 | 139.6404 | 136.8748 | Alkb, mg/L CaCO3 | 119.0092 | 216.1957 | 104.1784 | 100.145
[44 empty] | 1999-03-13 | 16:00 | 101.5 | 23 | 55 | 56 | 281 | 7.45 | 5.85 |  | 13.3 | 0.19401 | 0.56015 | 20.1278 | 17.0042 | 17.5144 | 600.9609 | 159.1851 | 589.2483 | 4.3592 | 51.1408 | 0.34247 | 7.6 | 7.3 | 7.6 | 159 | 354 | 525 | 601.1966 | -14.5136 | 55.0212 | 595.3347 | 73.2923 | BMRL | 0.167 | 0.361 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 192.1398 | 248.1461 | 180.5036 | 179.9153 | T-Hdb, mg/L CaCO3 | 157.3652 | 239.0449 | 140.3949 | 139.5369
[44 empty] | 1999-03-13 | 16:30 | 102 | 23 | 55 | 56 | 281 | 6.15 | 7.93 |  | 14.08 | 0.19401 | 0.43679 | 18.9574 | 14.037 | 14.4582 | 520.3789 | 138.3211 | 512.0172 | 3.7788 | 51.7212 | 0.27954 | 7.6 | 7.3 | 7.6 | 161 | 353 | 517 | 502.7907 | 2.7484 | 54.4554 | 499.0504 | 67.7387 | BMRL | 0.167 | 0.358 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 146.4305 | 203.4916 | 141.2382 | 138.5072 | Ca-Hdb, mg/L CaCO3 | 110.414 | 193.632 | 102.8415 | 98.8586
[44 empty] | 1999-03-13 | 17:00 | 102.5 | 23 | 55 | 56 | 281 | 6 | 5.28 |  | 11.28 | 0.19401 | 0.53191 | 23.9113 | 13.6947 | 14.1055 | 579.9558 | 154.2189 | 570.8653 | 4.2119 | 51.2881 | 0.27503 | 7.6 | 7.3 | 7.5 | 166 | 353 | 526 | 566.5682 | -7.7126 | 53.041 | 562.2917 | 70.478 | BMRL | 0.168 | 0.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-03-13 | 17:30 | 103 | 23 | 55 | 56 | 281 | 6.05 | 7.29 |  | 13.34 | 0.19401 | 0.45352 | 20.0645 | 13.8088 | 14.2231 | 529.9379 | 140.8996 | 521.5618 | 3.8485 | 51.6515 | 0.27537 | 7.7 | 7.3 | 7.6 | 159 | 353 | 492 | 514.9163 | -4.6578 | 55.0212 | 511.0848 | 68.8897 | BMRL | 0.1687 | 0.317 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-03-13 | 18:00 | 103.5 | 23 | 55 | 56 | 281 | 6.05 | 4.59 |  | 10.64 | 0.19401 | 0.56861 | 25.4098 | 13.8088 | 14.2231 | 606.7915 | 161.3334 | 597.2007 | 4.4066 | 51.0934 | 0.27837 | 7.7 | 7.3 | 7.6 | 162 | 354 | 517 | 605.9129 | -17.1978 | 54.1726 | 601.1341 | 73.0509 | BMRL | 0.168 | 0.338 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-03-14 | 11:00 | 120.5 | 23 | 55 | 56 | 281 | 5.45 | 2.54 |  | 7.99 | 0.19401 | 0.6821 | 34.169 | 12.4393 | 12.8125 | 707.6442 | 188.4493 | 697.5744 | 5.1416 | 50.3584 | 0.25443 | 7.7 | 7.3 | 7.8 | 187 | 353 | 655 | 710.7539 | -8.5121 | 47.1004 | 705.6748 | 73.5005 | BMRL | 0.174 | 0.52 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-03-14 | 12:00 | 121.5 | 23 | 55 | 56 | 281 | 5.75 | 7.43 |  | 13.18 | 0.19401 | 0.43627 | 20.3202 | 13.1241 | 13.5178 | 519.9904 | 138.3655 | 512.1813 | 3.7772 | 51.7228 | 0.26135 | 7.7 | 7.3 | 7.7 | 162 | 353 | 541 | 501.6999 | 7.2644 | 54.1726 | 498.2243 | 67.4845 | BMRL | 0.166 | 0.385 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-03-14 | 13:00 | 122.5 | 23 | 55 | 56 | 281 | 5.9 | 6.9 |  | 12.8 | 0.19401 | 0.46094 | 20.9531 | 13.4664 | 13.8704 | 534.2579 | 142.1051 | 526.0241 | 3.8804 | 51.6196 | 0.2687 | 7.6 | 7.3 | 7.7 | 158 | 354 | 490 | 520.6667 | -6.2585 | 55.3041 | 516.8593 | 69.4308 | BMRL | 0.168 | 0.312 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-03-14 | 13:30 | 123 | 23 | 55 | 56 | 281 | 5.83 | 6.46 |  | 12.29 | 0.19401 | 0.47437 | 21.8641 | 13.3067 | 13.7059 | 542.3195 | 144.2763 | 534.0612 | 3.9391 | 51.5609 | 0.26582 | 7.6 | 7.3 | 7.7 | 156 | 354 | 486 | 531.7392 | -9.4114 | 55.8699 | 527.8414 | 70.4457 | BMRL | 0.168 | 0.314 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-03-14 | 14:15 | 123.75 | 23 | 55 | 56 | 281 | 6.02 | 12.55 |  | 18.57 | 0.19401 | 0.32418 | 14.1319 | 13.7403 | 14.1525 | 463.8982 | 123.3509 | 456.6025 | 3.369 | 52.131 | 0.27148 | 7.7 | 7.3 | 7.7 | 149 | 353 | 440 | 451.5948 | -2.6352 | 57.8501 | 448.3535 | 66.7673 | BMRL | 0.165 | 0.255 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-03-14 | 14:45 | 124.25 | 23 | 55 | 56 | 281 | 6.05 | 13.1 |  | 19.15 | 0.19401 | 0.31593 | 13.6736 | 13.8088 | 14.2231 | 460.2436 | 122.3693 | 452.969 | 3.3424 | 52.1576 | 0.27269 | 7.8 | 7.3 | 7.6 | 149 | 353 | 372 | 447.9447 | -20.4152 | 57.8501 | 444.7265 | 66.4963 | BMRL | 0.168 | 0.116 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-03-14 | 15:15 | 124.75 | 23 | 55 | 56 | 281 | 6.1 | 14.8 |  | 20.9 | 0.19401 | 0.29187 | 12.445 | 13.9229 | 14.3406 | 449.9031 | 119.604 | 442.7329 | 3.2671 | 52.2329 | 0.27455 | 7.1 | 7 | 7.4 | 147 | 353 | 420 | 438.6115 | -4.4313 | 58.4158 | 435.4463 | 66.2415 | BMRL | 0.168 | 0.237 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-03-14 | 15:45 | 125.25 | 23 | 55 | 56 | 281 | 6.11 | 14.29 |  | 20.4 | 0.19401 | 0.29951 | 12.7745 | 13.9457 | 14.3641 | 453.1407 | 120.4615 | 445.907 | 3.2906 | 52.2094 | 0.27513 | 7.4 | 7.1 | 7.5 | 149 | 353 | 423 | 440.9384 | -4.2408 | 57.8501 | 437.7645 | 65.9634 | BMRL | 0.168 | 0.238 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-03-14 | 16:45 | 126.25 | 23 | 55 | 56 | 281 | 6.06 | 13.26 |  | 19.32 | 0.19401 | 0.31366 | 13.5445 | 13.8316 | 14.2466 | 459.2519 | 122.1024 | 451.9809 | 3.3351 | 52.1649 | 0.27311 | 7.4 | 7.1 | 7.6 | 150 | 354 | 428 | 446.5023 | -4.323 | 57.5672 | 443.3051 | 66.1633 | BMRL | 0.167 | 0.239 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-03-14 | 17:45 | 127.25 | 23 | 55 | 56 | 281 | 6.19 | 13.94 |  | 20.13 | 0.19401 | 0.3075 | 12.9593 | 14.1283 | 14.5522 | 456.5848 | 121.3511 | 449.2001 | 3.3154 | 52.1846 | 0.27886 | 7.4 | 7.1 | 7.5 | 148 | 354 | 435 | 444.7514 | -2.2417 | 58.133 | 441.4829 | 66.4766 | BMRL | 0.163 | 0.243 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-15 | 9:00 | 142.5 | 23 | 55 | 56 | 272 | 5.93 | 8.53 | X | 14.46 | 0.18779 | 0.4101 | 17.8105 | 13.5349 | 13.941 | 505.7823 | 134.4498 | 497.6867 | 3.6728 | 51.8272 | 0.26899 | 7.5 | 7.2 | 7.6 | 171 | 354 | 466 | 480.3728 | -3.0843 | 51.6266 | 477.0004 | 64.151 | BMRL | 0.165 | 0.284 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-15 | 11:00 |  | 23 | 55 | 56 | 272 | 6.95 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 15.863 | 16.3389 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-15 | 11:15 |  | 23 | 65 | 66 | 272 | 8.2 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 18.7161 | 19.2775 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-15 | 11:30 |  | 23 | 45 | 46 | 272 | 5.8 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 13.2382 | 13.6353 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-15 | 11:45 |  | 23 | 55 | 56 | 272 | 7 | NA |  | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 15.9771 | 16.4564 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on E19: Gary Puetz: The consultant stated that the cost of an 8X40 TFC-SR membrane element was not available from the manufacturer.
Note on R5: Gary Puetz: Consultant confirmed potential foulants were not measured during the study, because they were not required under the ICR.
Note on X26: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on X36: Gary Puetz: The consultant did not address the difference in MBAA concentrations between the 1st and 2nd feed samples.
Note on BO7: Gary Puetz: All operational data was verified by the consultant, who hypothesized that the erratic behavior of the MTCw and flux may be due to experimental variability.
Note on BV7: Gary Puetz: All operational data was verified by the consultant, who hypothesized that the erratic behavior of the MTCw and flux may be due to experimental variability.
Note on BX7: Gary Puetz: OK. The consultant stated that they had problems with the pH instrument and no pH data is available during the early portion of this run.
Note on CY31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DG10: Alison Gusses: The consultant did not address why Alkalinity, total hardness and calcium hardness had large mass balance errors.
Note on DL31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on DQ10: Alison Gusses: The consultant did not address why Alkalinity, total hardness and calcium hardness had large mass balance errors.
Note on DV31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on EA10: Alison Gusses: The consultant did not address why Alkalinity, total hardness and calcium hardness had large mass balance errors.
Note on EF31: Gary Puetz: OK. SDS incubation times reflect the seasonal variations of the full-scale distribution system.
Note on EK10: Alison Gusses: The consultant did not address why Alkalinity, total hardness and calcium hardness had large mass balance errors.