## Sheet1. 1st Quarter
|  | Study title: GAC adorption test using RSSCT |  | Study title: GAC adorption test using RSSCT, quarter 1 |  |  |  | Study title: GAC adorption test using RSSCT |  |  | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [26 empty] | Study title: GAC adorption test using RSSCT | [11 empty] | Study title: GAC adorption test using RSSCT | [9 empty] | Study title: GAC adorption test using RSSCT | [8 empty] | Study title: GAC adorption test using RSSCT
|  | Client: City Odessa, TX |  | Client: City of Odessa, TX |  |  |  | Client: City of Odessa, TX |  |  | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [26 empty] | Client: City of Odessa, TX | [11 empty] | Client: City of Odessa, TX | [10 empty] | Client: City of Odessa, TX | [7 empty] | Client: City of Odessa, TX
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run | [33 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run | [33 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Odessa | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.8 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-05-05 | [5 empty] | 20-min. EBCT Start Date | 1998-05-05 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0680002 | Carbon trade name | Calgon F-400 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | Ferric chloride FeCl3 coagulant is added at a 10 mg/L dose | Bench-scale | 10-min. EBCT Start Time | 9:00 | [5 empty] | 20-min. EBCT Start Time | 9:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.52 | 4 | 4.75 | Rapid MIX | 5.3 mg/L organic polymer (20% DADMAC) | Bench-scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 21.6 | 6 | 3.35 | Flocculation | 2-stage | Bench-scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-05-05 | 14:05 | 5.0833 | 285.3444 | 8.1 | 23 | 0.4 | BMRL | #VALUE! | 1.4 | 1.14 | 0.26 | 17 | 8.3 | 15 | BMRL | BMRL | BMRL | BMRL | 4 | 4 | BMRL | BMRL | BMRL | BMRL | 1.1 | BMRL | NA | NA | NA | 1.1 | 1.1 | C1-20 | N | 1998-05-05 | 14:05 | 5.0833 | 142.6722 | 8.2 | 23 | 0.55 | BMRL |  | 1.4 | 1.06 | 0.34 | 17 | 8.2 | 15 | BMRL | BMRL | BMRL | BMRL | 2.3 | 2.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Sedimentation | tube settler | Bench-scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-05-05 | 19:25 | 10.4167 | 584.7222 | 8 | 23 | 0.65 | BMRL |  | 1.4 | 1.03 | 0.37 | 17 | 8.3 | 15 | BMRL | BMRL | BMRL | BMRL | 5.9 | 5.9 | BMRL | BMRL | BMRL | 1.7 | 2 | BMRL | NA | NA | NA | 3.7 | 3.7 | C2-20 | N | 1998-05-06 | 23:05 | 38.0833 | 1068.8722 | 8 | 23 | 0.8 | BMRL |  | 1.4 | 0.73 | 0.67 | 17 | 8 | 15 | BMRL | BMRL | BMRL | BMRL | 9.2 | 9.2 | BMRL | BMRL | BMRL | BMRL | 2.3 | BMRL | NA | NA | NA | 2.3 | 2.3 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Cartridge filtration | 0.45 um exclusion size and on-line 0.2 um | Bench-scale | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-22 | --- | --- |  | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-22 | --- | --- |  | C3-10 | N | 1998-05-05 | 23:33 | 14.55 | 816.74 | 8 | 23 | 0.65 | BMRL |  | 1.4 | 1.01 | 0.39 | 17 | 8.3 | 15 | BMRL | BMRL | BMRL | BMRL | 8.7 | 8.7 | BMRL | BMRL | BMRL | 1.2 | 2.1 | BMRL | NA | NA | NA | 3.3 | 3.3 | C3-20 | N | 1998-05-07 | 17:07 | 56.1167 | 1575.0078 | 8.1 | 23 | 0.9 | BMRL |  | 1.4 | 0.97 | 0.43 | 17 | 8.1 | 15 | BMRL | BMRL | BMRL | BMRL | 13 | 13 | BMRL | BMRL | BMRL | BMRL | 3.3 | BMRL | NA | NA | NA | 3.3 | 3.3 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 14:05 | 13:55 | --- | --- |  | Sampling time | hh:mm | 14:05 | 13:55 | --- | --- |  | C4-10 | N | 1998-05-06 | 15:37 | 30.6167 | 1718.6156 | 8 | 23 | 0.85 | BMRL | #VALUE! | 1.4 | 0.87 | 0.53 | 17 | 8.3 | 15 | BMRL | BMRL | BMRL | BMRL | 18 | 18 | BMRL | BMRL | BMRL | 3 | 4 | BMRL | NA | NA | NA | 7 | 7 | C4-20 | N | 1998-05-07 | 23:11 | 62.1833 | 1745.2789 | 8.1 | 23 | 0.85 | BMRL |  | 1.4 | 0.97 | 0.43 | 17 | 8.1 | 15 | BMRL | BMRL | BMRL | BMRL | 14 | 14 | BMRL | BMRL | BMRL | BMRL | 3.7 | BMRL | NA | NA | NA | 3.7 | 3.7 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 5.0833 | 412.9167 | --- | --- |  | Operation time | hh.hh | 5.0833 | 412.9167 | --- | --- |  | C5-10 | N | 1998-05-07 | 11:56 | 50.9333 | 2859.0578 | 8 | 23 | 1.3 | 0.0105 | 0.80769 | 1.6 | 0.81 | 0.79 | 17 | 8.3 | 15 | 28 | BMRL | BMRL | 1.8 | 39 | 40.8 | BMRL | BMRL | BMRL | 2.8 | 7.4 | BMRL | NA | NA | NA | 10.2 | 10.2 | C5-20 | N | 1998-05-08 | 13:40 | 76.6667 | 2151.7778 | 8 | 23 | 1.05 | BMRL |  | 1.4 | 0.95 | 0.45 | 17 | 8 | 15 | BMRL | BMRL | BMRL | BMRL | 16 | 16 | BMRL | BMRL | BMRL | BMRL | 4.5 | BMRL | NA | NA | NA | 4.5 | 4.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6859
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 285.3444 | 23178.3889 | --- | --- |  | Bed volumes | (20 minutes) | 142.6722 | 11589.1944 | --- | --- |  | C6-10 | N | 1998-05-07 | 17:07 | 56.1167 | 3150.0156 | 8.1 | 23 | 1.7 | 0.013 | 0.76471 | 1.8 | 0.83 | 0.97 | 17 | 8.2 | 15 | 53 | BMRL | BMRL | 3 | 50 | 53 | BMRL | BMRL | BMRL | 3.2 | 9.6 | BMRL | NA | NA | NA | 12.8 | 12.8 | C6-20 | N | 1998-05-09 | 12:20 | 99.3333 | 2787.9556 | 8.1 | 23 | 1.15 | BMRL |  | 1.4 | 0.83 | 0.57 | 17 | 8.1 | 15 | 34 | BMRL | BMRL | BMRL | 23 | 23 | BMRL | BMRL | BMRL | 1.1 | 5.6 | BMRL | NA | NA | NA | 6.7 | 6.7 | 1998 Producers Price Index (PPI base year 1967 = 100) | 130.5
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 125 | 130 | 127.5 | 3.9216 |  | Alkalinity | mg/L as CaCO3 | 125 | 130 | 127.5 | 3.9216 |  | C7-10 | N | 1998-05-07 | 23:11 | 62.1833 | 3490.5578 | 8.1 | 23 | 1.45 | 0.0135 | 0.93103 | 1.8 | 0.8 | 1 | 17 | 8.2 | 15 | 49 | BMRL | BMRL | 2.6 | 45 | 47.6 | BMRL | BMRL | BMRL | 1.8 | 9.3 | BMRL | NA | NA | NA | 11.1 | 11.1 | C7-20 | N | 1998-05-09 | 18:15 | 105.25 | 2954.0167 | 8 | 23 | 1.3 | 0.009 | 0.69231 | 1.4 | 0.74 | 0.66 | 17 | 8 | 15 | 30 | BMRL | BMRL | BMRL | 32 | 32 | BMRL | BMRL | BMRL | BMRL | 4.2 | BMRL | NA | NA | NA | 4.2 | 4.2 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2823.8793 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 448 | 450 | 449 | 0.44543 |  | Total hardness | mg/L as CaCO3 | 448 | 450 | 449 | 0.44543 |  | C8-10 | N | 1998-05-08 | 17:48 | 80.8 | 4535.5733 | 8.1 | 23 | 2.15 | 0.018 | 0.83721 | 2.2 | 0.87 | 1.33 | 17 | 8.3 | 15 | 75 | BMRL | BMRL | 5.3 | 65 | 70.3 | BMRL | BMRL | BMRL | 2.6 | 14 | 1.1 | NA | NA | NA | 16.6 | 17.7 | C8-20 | N | 1998-05-11 | 0:10 | 135.1667 | 3793.6778 | 8 | 23 | 1.55 | 0.011 | 0.70968 | 1.6 | 0.76 | 0.84 | 17 | 8 | 15 | 43 | BMRL | BMRL | 1.3 | 42 | 43.3 | BMRL | BMRL | BMRL | 2.2 | 9 | BMRL | NA | NA | NA | 11.2 | 11.2 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 5647.7585 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 250 | 250 | 250 | 0 |  | Calcium hardness | mg/L as CaCO3 | 250 | 250 | 250 | 0 |  | C9-10 | N | 1998-05-09 | 12:20 | 99.3333 | 5575.9111 | 8 | 23 | 2.4 | 0.022 | 0.91667 | 2.4 | 0.81 | 1.59 | 17 | 8.3 | 15 | 74 | BMRL | BMRL | 6 | 75 | 81 | BMRL | BMRL | BMRL | 3 | 15 | 1.2 | NA | NA | NA | 18 | 19.2 | C9-20 | N | 1998-05-13 | 5:56 | 188.9333 | 5302.7289 | 8.1 | 23 | 2.15 | 0.018 | 0.83721 | 2.2 | 0.92 | 1.28 | 17 | 8.1 | 15 | 68 | BMRL | BMRL | 4.2 | 77 | 81.2 | BMRL | BMRL | BMRL | BMRL | 10 | BMRL | NA | NA | NA | 10 | 10 | Electric Rate ($/kW-h) | 0.075
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7342.0861 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.2 | 0.2 | 0.2 | 0 |  | Ammonia | mg NH3-N / L | 0.2 | 0.2 | 0.2 | 0 |  | C10-10 | N | 1998-05-09 | 18:15 | 105.25 | 5908.0333 | 8 | 23 | 2.2 | 0.0255 | 1.1591 | 2.4 | 0.84 | 1.56 | 17 | 8.2 | 15 | 83 | BMRL | BMRL | 7.5 | 73 | 80.5 | BMRL | BMRL | BMRL | 3 | 17 | 1.5 | NA | NA | NA | 20 | 21.5 | C10-20 | N | 1998-05-14 | 11:31 | 218.5167 | 6133.0344 | 8.1 | 23 | 2 | 0.022 | 1.1 | 2.2 | 0.75 | 1.45 | 17 | 8.1 | 15 | 75 | BMRL | BMRL | 3.7 | 70 | 73.7 | BMRL | BMRL | BMRL | 2.8 | 16 | 1.2 | NA | NA | NA | 18.8 | 20 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 1370 | 1410 | 1390 | 2.8777 |  | Bromide | mg/L | 1370 | 1410 | 1390 | 2.8777 |  | C11-10 | N | 1998-05-09 | 23:48 | 110.8 | 6219.5733 | 8 | 23 | 2.5 | 0.029 | 1.16 | 2.4 | 0.81 | 1.59 | 17 | 8.2 | 15 | 79 | BMRL | BMRL | 7.9 | 77 | 84.9 | BMRL | BMRL | BMRL | 3.3 | 17 | 1.4 | NA | NA | NA | 20.3 | 21.7 | C11-20 | N | 1998-05-14 | 15:50 | 222.8333 | 6254.1889 | 8.1 | 23 | 2.5 | 0.022 | 0.88 | 2.5 | 0.9 | 1.6 | 17 | 8.1 | 15 | 75 | BMRL | BMRL | 4.5 | 68 | 72.5 | BMRL | BMRL | BMRL | 3.1 | 16 | 1.4 | NA | NA | NA | 19.1 | 20.5 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-05-11 | 0:10 | 135.1667 | 7587.3556 | 8 | 23 | 2.7 | 0.0365 | 1.3519 | 2.8 | 0.95 | 1.85 | 17 | 8.3 | 15 | 94 | BMRL | 1 | 11 | 91 | 103 | BMRL | BMRL | BMRL | 3.8 | 20 | 2.1 | NA | NA | NA | 23.8 | 25.9 | C12-20 | N | 1998-05-16 | 13:10 | 268.1667 | 7526.5444 | 8 | 23 | 2.5 | 0.024 | 0.96 | 2.5 | 0.83 | 1.67 | 17 | 8 | 15 | 72 | BMRL | BMRL | 4.7 | 71 | 75.7 | BMRL | BMRL | BMRL | 3.2 | 17 | 1.4 | NA | NA | NA | 20.2 | 21.6 | Current Process Water Rate ($/1000 gal)** | 0.15 to 0.20
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 9.8747e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [6 empty] | C13-10 | N | 1998-05-13 | 14:44 | 197.7333 | 11099.4311 | 8 | 23 | 3.25 | 0.032 | 0.98462 | 3.4 | 1.17 | 2.23 | 17 | 8.3 | 15 | 135 | BMRL | 2.2 | 19 | 100 | 121.2 | BMRL | BMRL | BMRL | 5 | 23 | 3.2 | NA | NA | NA | 28 | 31.2 | C13-20 | N | 1998-05-19 | 10:52 | 337.8667 | 9482.7911 | 8.1 | 23 | 3 | 0.031 | 1.0333 | 3 | 0.95 | 2.05 | 17 | 8.1 | 15 | 95 | BMRL | BMRL | 11 | 97 | 108 | BMRL | BMRL | BMRL | 4.5 | 21 | 2.3 | NA | NA | NA | 25.5 | 27.8 | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | C14-10 | N | 1998-05-15 | 12:05 | 243.0833 | 13645.0778 | 8 | 23 | 3.5 | 0.044 | 1.2571 | 2.8 | 0.97 | 1.83 | 17 | 8.2 | 15 | 150 | BMRL | 2.4 | 21 | 110 | 133.4 | BMRL | BMRL | BMRL | 5.2 | 25 | 3.4 | NA | NA | NA | 30.2 | 33.6 | C14-20 | N | 1998-05-21 | 11:53 | 386.8833 | 10858.5256 | 8.2 | 23 | 3.3 | 0.034 | 1.0303 | 3.4 | 1.11 | 2.29 | 17 | 8.2 | 15 | NR | BMRL | BMRL | 14 | 97 | 111 | BMRL | BMRL | BMRL | 5.2 | 23 | 3.1 | NA | NA | NA | 28.2 | 31.3
|  |  |  | Scaling factor, SF | 9.3556 | 140 | 0.106 |  |  |  | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-17 | 1998-05-22 | --- | --- | Sampling date | MM/DD/YY | 1998-05-05 | 1998-05-17 | 1998-05-22 | --- | --- | C15-10 | N | 1998-05-17 | 10:03 | 289.05 | 16225.34 | 8.1 | 23 | 3.55 | 0.041 | 1.1549 | 3.8 | 1.13 | 2.67 | 17 | 8.3 | 15 | 150 | BMRL | 3.1 | 24 | 120 | 147.1 | BMRL | BMRL | BMRL | 5 | 26 | 4 | NA | NA | NA | 31 | 35 | C15-20 | N | 1998-05-22 | 13:55 | 412.9167 | 11589.1944 | 8.1 | 23 | 3.4 | 0.0355 | 1.0441 | 3.4 | 0.96 | 2.44 | 17 | 8.1 | 15 | NR | BMRL | BMRL | 13 | 95 | 108 | BMRL | BMRL | BMRL | 4.7 | 24 | 3 | NA | NA | NA | 28.7 | 31.7
Plant Name | Odessa Utilities Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3942 | 170 | 0.088 |  |  |  | Sampling time | hh:mm | 14:05 | 10:03 | 13:55 | --- | --- | Sampling time | hh:mm | 14:05 | 10:03 | 13:55 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Treatment Plant Category | Conventional filtration |  |  | RSSCT flow rate, QSC (mL/min) | 11.7115 | 200 | 0.075 |  |  |  | Operation time | hh.hh | 5.0833 | 289.05 | 412.9167 | --- | --- | Operation time | hh.hh | 5.0833 | 289.05 | 412.9167 | --- | --- | ** Temperature, and SDS temperature are target values (controlled laboratory room-temperature and incubator) | [33 empty] | ** Temperature, and SDS temperature are target values (controlled laboratory room-temperature and incubator)
Process Train Name | Plants 1 and 2 |  |  | Estimated total influent volume required, VSCT (L) | 275.7297 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 285.3444 | 16225.34 | 23178.3889 | --- | --- | Bed volumes | (20 minute) | 142.6722 | 8112.67 | 11589.1944 | --- | ---
ICR Treatment Plant Identification Number | 702 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.9 | 8 | 7.9 | 7.9333 | 0.72775 | pH | --- | 7.9 | 8 | 7.9 | 7.9333 | 0.72775
PWSID Number of Plant (if assigned) | TX0680002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.36 | 0.38 | 0.4 | 0.38 | 5.2632 | Turbidity | ntu | 0.36 | 0.38 | 0.4 | 0.38 | 5.2632
Historical Minimum Water Temperature (oC) | 7 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 23 | 23 | 23 | 23 | 0 | Temperature | oC | 23 | 23 | 23 | 23 | 0
Historical Average Water Temperature (oC) | 19 |  |  | Estimated full-scale run time, tLCT (days) | 50.9867 | [5 empty] | Total organic carbon | mg/L | 4.85 | 4.65 | 4.85 | 4.7833 | 2.414 | Total organic carbon | mg/L | 4.85 | 4.65 | 4.85 | 4.7833 | 2.414 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 40 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0689 | [5 empty] | UV254 | cm-1 | 0.066 | 0.0665 | 0.067 | 0.0665 | 0.75188 | UV254 | cm-1 | 0.066 | 0.0665 | 0.067 | 0.0665 | 0.75188 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 5.4499 | [5 empty] | SUVA | L/(mg*m) | 1.3608 | 1.4301 | 1.3814 | 1.3908 | 2.5579 | SUVA | L/(mg*m) | 1.3608 | 1.4301 | 1.3814 | 1.3908 | 2.5579 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.1725 | [5 empty] | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 5 | 0 | SDS-Cl2 dose | mg/L | 5 | 5 | 5 | 5 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 91.9099 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.38 | 1.34 | 1.35 | 1.3567 | 1.5344 | SDS-Free Cl2 residual | mg/L | 1.38 | 1.34 | 1.35 | 1.3567 | 1.5344
|  |  |  | Mass GAC required, mSC (g) | 6.2591 | [5 empty] | SDS-Cl2 demand | mg/L | 3.62 | 3.66 | 3.65 | 3.6433 | 0.57136 | SDS-Cl2 demand | mg/L | 3.62 | 3.66 | 3.65 | 3.6433 | 0.57136
[11 empty] | SDS-Chlorination temp. | oC | 17 | 17 | 17 | 17 | 0 | SDS-Chlorination temp. | oC | 17 | 17 | 17 | 17 | 0
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.3 | 8.3 | 8.3 | 8.3 | 0 | SDS-Chlorination pH | --- | 8.3 | 8.3 | 8.3 | 8.3 | 0
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 15 | 15 | 15 | 15 | 0 | SDS-Incubation time | hours | 15 | 15 | 15 | 15 | 0
|  |  |  | Estimated full-scale run time, tLCT (days) | 101.9734 | [5 empty] | SDS-TOX | mg Cl- /L | 225 | 220 | 205 | 216.6667 | 4.8038 | SDS-TOX | mg Cl- /L | 225 | 220 | 205 | 216.6667 | 4.8038
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1378 | [5 empty] | SDS-CHCl3 | mg/L | 1.6 | 1.5 | 1.1 | 1.4 | 18.8982 | SDS-CHCl3 | mg/L | 1.6 | 1.5 | 1.1 | 1.4 | 18.8982
|  |  |  | Estimated RSSCT run time, tSCT (days) | 10.8998 | [5 empty] | SDS-BDCM | mg/L | 7.4 | 7.3 | 6.4 | 7.0333 | 7.8307 | SDS-BDCM | mg/L | 7.4 | 7.3 | 6.4 | 7.0333 | 7.8307
|  |  |  | RSSCT bed length, lSC (cm) | 26.345 | [5 empty] | SDS-DBCM | mg/L | 37 | 36 | 43 | 38.6667 | 9.7912 | SDS-DBCM | mg/L | 37 | 36 | 43 | 38.6667 | 9.7912
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 183.8198 | [5 empty] | SDS-CHBr3 | mg/L | 160 | 180 | 140 | 160 | 12.5 | SDS-CHBr3 | mg/L | 160 | 180 | 140 | 160 | 12.5
|  |  |  | Mass GAC required, mSC (g) | 12.5182 | [5 empty] | SDS-THM4 | mg/L | 206 | 224.8 | 190.5 | 207.1 | 8.2938 | SDS-THM4 | mg/L | 206 | 224.8 | 190.5 | 207.1 | 8.2938
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | 2.1 | 2.1 | 1.1 | 1.7667 | 32.6802 | SDS-DCAA* | mg/L | 2.1 | 2.1 | 1.1 | 1.7667 | 32.6802 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 5.4 | 4.5 | 7.6 | 5.8333 | 27.3391 | SDS-MBAA* | mg/L | 5.4 | 4.5 | 7.6 | 5.8333 | 27.3391
[11 empty] | SDS-DBAA* | mg/L | 31 | 31 | 33 | 31.6667 | 3.6464 | SDS-DBAA* | mg/L | 31 | 31 | 33 | 31.6667 | 3.6464
[11 empty] | SDS-BCAA* | mg/L | 6.2 | 6.1 | 6.8 | 6.3667 | 5.9465 | SDS-BCAA* | mg/L | 6.2 | 6.1 | 6.8 | 6.3667 | 5.9465
[11 empty] | SDS-TBAA | mg/L | NR | NR | NA | NA |  | SDS-TBAA | mg/L | NR | NR | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | 8.9 | 9.2 | NA | NA |  | SDS-CDBAA | mg/L | 8.9 | 9.2 | NA | 9.05 | 2.344
[11 empty] | SDS-DCBAA | mg/L | 3.3 | 3.9 | NA | NA |  | SDS-DCBAA | mg/L | 3.3 | 3.9 | NA | 3.6 | 11.7851
[11 empty] | SDS-HAA5 | mg/L | 38.5 | 37.6 | 41.7 | 39.2667 | 5.4877 | SDS-HAA5 | mg/L | 38.5 | 37.6 | 41.7 | 39.2667 | 5.4877
[11 empty] | SDS-HAA6 | mg/L | 44.7 | 43.7 | 48.5 | 45.6333 | 5.5496 | SDS-HAA6 | mg/L | 44.7 | 43.7 | 48.5 | 45.6333 | 5.5496
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
** Temperature, and SDS temperature are target values (controlled laboratory room-temperature and incubator)
Note on N10: Reviewer M.H. (8/26/99): Per consultant: A 0.2-m in-line filter was incorporated for all RSSCT studies to minimize headloss formation and to render sample collection reasonable. High and frequent headloss formation were experienced in a previous study, eventhough the carbon fines were minimized with the rinsing process. No head-loss problems were experienced following this change.
Note on Q28: Reviewer M.H. (8/26/99): Per consultant: Temperature, and SDS temperature are target values (controlled laboratory room-temperature)
Note on Q35: Reviewer M.H. (8/26/99): Per consultant: Temperature, and SDS temperature are target values (controlled laboratory room-temperature)
Note on Y28: Reviewer M.H. (8/26/99): Per consultant: Temperature, and SDS temperature are target values (controlled laboratory room-temperature)
Note on Y35: Reviewer M.H. (8/26/99): Per consultant: Temperature, and SDS temperature are target values (controlled laboratory room-temperature)
Note on AG33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.
Note on AN8: Reviewer M.H. (8/26/99): Per consultant: Temperature, and SDS temperature are target values (controlled laboratory room-temperature)
Note on AU8: Reviewer M.H. (8/26/99): Per consultant: Temperature, and SDS temperature are target values (controlled laboratory room-temperature)
Note on BP33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.
Note on CK40: Reviewer M.H. (8/26/99): Per consultant: Bromoform results were verified (C5-20 and C5-20b), and no changes were made.

## Sheet2. 2nd Quarter
|  | Study title: GAC adorption test using RSSCT |  | Study title: GAC adorption test using RSSCT |  |  |  | Study title: GAC adorption test using RSSCT |  |  | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [26 empty] | Study title: GAC adorption test using RSSCT | [11 empty] | Study title: GAC adorption test using RSSCT | [9 empty] | Study title: GAC adorption test using RSSCT | [8 empty] | Study title: GAC adorption test using RSSCT
|  | Client: City Odessa, TX |  | Client: City of Odessa, TX |  |  |  | Client: City of Odessa, TX |  |  | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [26 empty] | Client: City of Odessa, TX | [11 empty] | Client: City of Odessa, TX | [10 empty] | Client: City of Odessa, TX | [7 empty] | Client: City of Odessa, TX
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run | [33 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run | [33 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Odessa | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.7 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-09-16 | [5 empty] | 20-min. EBCT Start Date | 1998-09-16 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0680002 | Carbon trade name | Calgon F-400 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Removal of Fe and Mn | Addition of KMnO4 at 0.3 mg/L | Bench-scale | 10-min. EBCT Start Time | 10:00 | [5 empty] | 20-min. EBCT Start Time | 10:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.595 | 4 | 4.75 | Coagulation | Alum coagulant is added at a 13 mg/L dose | Bench-scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 27.3 | 6 | 3.35 | Rapid MIX | 0.5 mg/L organic polymer | Bench-scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-09-16 | 16:10 | 6.1667 | 346.1556 | 8.2 | 22 | 0.7 | BMRL | BMRL | 1.6 | 0.76 | 0.84 | 22 | 8.2 | 24 | BMRL | BMRL | BMRL | BMRL | 9 | 9 | BMRL | BMRL | BMRL | BMRL | 1.6 | BMRL | BMRL | BMRL | BMRL | 1.6 | 1.6 | C1-20 | N | 1998-09-16 | 16:10 | 6.1667 | 173.0778 | 8.4 | 22 | 0.5 | BMRL | BMRL | 1.8 | 0.93 | 0.87 | 22 | 8.4 | 23.7 | 35 | BMRL | BMRL | BMRL | 5.9 | 5.9 | BMRL | BMRL | BMRL | BMRL | 1.2 | BMRL | BMRL | BMRL | BMRL | 1.2 | 1.2 | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Flocculation | 5, 10 and 20 rpm for 10-min period each | Bench-scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-09-17 | 11:40 | 25.6667 | 1440.7556 | 8.2 | 22 | 0.95 | BMRL | BMRL | 1.6 | 0.69 | 0.91 | 22 | 8.2 | 24 | BMRL | BMRL | BMRL | BMRL | 17 | 17 | BMRL | BMRL | BMRL | BMRL | 3.2 | BMRL | BMRL | BMRL | BMRL | 3.2 | 3.2 | C2-20 | N | 1998-09-19 | 17:58 | 79.9667 | 2244.3978 | 8 | 23 | 1.2 | BMRL | BMRL | 1.8 | 0.88 | 0.92 | 23 | 8.1 | 23.7 | 57 | BMRL | BMRL | BMRL | 23 | 23 | BMRL | BMRL | BMRL | BMRL | 4.2 | BMRL | 4.3 | BMRL | BMRL | 4.2 | 4.2 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Sedimentation | in a drum for at least 1 hour | Bench-scale | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-24 | --- | --- |  | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-24 | --- | --- |  | C3-10 | N | 1998-09-17 | 16:35 | 30.5833 | 1716.7444 | 8.1 | 23 | 1.65 | BMRL | BMRL | 1.8 | 0.8 | 1 | 22 | 8.1 | 24 | 42 | BMRL | BMRL | 1.2 | 23 | 24.2 | BMRL | BMRL | BMRL | BMRL | 3.9 | BMRL | BMRL | BMRL | BMRL | 3.9 | 3.9 | C3-20 | N | 1998-09-20 | 13:30 | 99.5 | 2792.6333 | 8.2 | 24 | 1.35 | BMRL | BMRL | 2 | 0.96 | 1.04 | 23 | 8.3 | 23.7 | 34 | BMRL | BMRL | 1.2 | 29 | 30.2 | BMRL | BMRL | BMRL | BMRL | 5.2 | BMRL | 5.2 | BMRL | BMRL | 5.2 | 5.2 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 | Cartridge filtration | 0.45 um exclusion size and on-line 0.2 um | Bench-scale | Sampling time | hh:mm | 16:10 | 13:35 | --- | --- |  | Sampling time | hh:mm | 16:10 | 13:35 | --- | --- |  | C4-10 | N | 1998-09-17 | 21:35 | 35.5833 | 1997.4111 | 8.1 | 23 | 1.9 | BMRL | BMRL | 1.8 | 0.7 | 1.1 | 22 | 8.1 | 24 | 32 | BMRL | BMRL | 1.4 | 26 | 27.4 | BMRL | BMRL | BMRL | BMRL | 4.7 | BMRL | BMRL | BMRL | BMRL | 4.7 | 4.7 | C4-20 | N | 1998-09-20 | 17:37 | 103.6167 | 2908.1744 | 8 | 24 | 1.2 | BMRL | BMRL | 2.2 | 1.06 | 1.14 | 22 | 8.1 | 23.8 | 60 | BMRL | BMRL | 1.7 | 32 | 33.7 | BMRL | BMRL | BMRL | 1.3 | 6.6 | BMRL | NR | 2 | BMRL | 7.9 | 7.9 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 6.1667 | 195.5833 | --- | --- |  | Operation time | hh.hh | 6.1667 | 195.5833 | --- | --- |  | C5-10 | N | 1998-09-18 | 13:14 | 51.2333 | 2875.8978 | 8.1 | 23 | 2.1 | 0.0095 | 0.45238 | 1.8 | 0.68 | 1.12 | 23 | 8.1 | 24 | 76 | BMRL | BMRL | 2 | 36 | 38 | BMRL | BMRL | BMRL | 1 | 6.7 | BMRL | 5.3 | BMRL | BMRL | 7.7 | 7.7 | C5-20 | N | 1998-09-21 | 11:15 | 121.25 | 3403.0833 | 8 | 23 | 1.4 | 0.009 | 0.64286 | 2.2 | 1.11 | 1.09 | 23 | 8.1 | 23.7 | 39 | BMRL | BMRL | 1.2 | 30 | 31.2 | BMRL | BMRL | BMRL | BMRL | 5.6 | BMRL | 6.1 | BMRL | BMRL | 5.6 | 5.6 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6859
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 346.1556 | 10978.7444 | --- | --- |  | Bed volumes | (20 minutes) | 173.0778 | 5489.3722 | --- | --- |  | C6-10 | N | 1998-09-18 | 17:26 | 55.4333 | 3111.6578 | 8.2 | 23 | 1.75 | 0.01 | 0.57143 | 2 | 0.74 | 1.26 | 22 | 8.3 | 24 | 53 | BMRL | BMRL | 2.7 | 44 | 46.7 | BMRL | BMRL | BMRL | 1.3 | 7.7 | BMRL | 6.6 | BMRL | BMRL | 9 | 9 | C6-20 | N | 1998-09-21 | 15:30 | 125.5 | 3522.3667 | 8.1 | 23 | 1.3 | 0.0095 | 0.73077 | 2.4 | 1.14 | 1.26 | 22 | 8.2 | 23.8 | 53 | BMRL | BMRL | 2.1 | 34 | 36.1 | BMRL | BMRL | BMRL | 1.4 | 7.3 | BMRL | 6.7 | BMRL | BMRL | 8.7 | 8.7 | 1998 Producers Price Index (PPI base year 1967 = 100) | 130.5
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 125 | 125 | 125 | 0 |  | Alkalinity | mg/L as CaCO3 | 125 | 125 | 125 | 0 |  | C7-10 | N | 1998-09-18 | 22:30 | 60.5 | 3396.0667 | 8.2 | 21 | 1.6 | 0.011 | 0.6875 | 2 | 0.69 | 1.31 | 22 | 8.2 | 24 | 86 | BMRL | BMRL | 3 | 48 | 51 | BMRL | BMRL | BMRL | 1.4 | 8.6 | BMRL | 7.3 | BMRL | BMRL | 10 | 10 | C7-20 | N | 1998-09-23 | 11:06 | 169.1 | 4746.0733 | 8.1 | 23 | 1.45 | 0.01 | 0.68966 | 2.4 | 1.08 | 1.32 | 22 | 8.2 | 23.7 | 76 | BMRL | BMRL | 2.2 | 46 | 48.2 | BMRL | BMRL | BMRL | BMRL | 8 | BMRL | 9 | BMRL | BMRL | 8 | 8 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2902.2346 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 591 | 583 | 587 | 1.3629 |  | Total hardness | mg/L as CaCO3 | 591 | 583 | 587 | 1.3629 |  | C8-10 | N | 1998-09-19 | 22:30 | 84.5 | 4743.2667 | 8.2 | 23 | 2.2 | 0.017 | 0.77273 | 2.2 | 0.53 | 1.67 | 22 | 8.1 | 23.7 | 82 | BMRL | BMRL | 3.8 | 78 | 81.8 | BMRL | BMRL | BMRL | BMRL | 12 | BMRL | 11 | BMRL | BMRL | 12 | 12 | C8-20 | N | 1998-09-24 | 13:35 | 195.5833 | 5489.3722 | 8 | 22 | 1.75 | 0.012 | 0.68571 | 2.4 | 0.97 | 1.43 | 22 | 8.1 | 23.7 | 77 | BMRL | BMRL | 3 | 56 | 59 | BMRL | BMRL | BMRL | BMRL | 9.6 | BMRL | 11 | BMRL | BMRL | 9.6 | 9.6 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 5804.4692 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 300 | 300 | 300 | 0 |  | Calcium hardness | mg/L as CaCO3 | 300 | 300 | 300 | 0 |  | C9-10 | N | 1998-09-20 | 13:30 | 99.5 | 5585.2667 | 8 | 24 | 2.3 | 0.019 | 0.82609 | 2.2 | 0.52 | 1.68 | 23 | 8.1 | 23.7 | 115 | BMRL | BMRL | 3.9 | 81 | 84.9 | BMRL | BMRL | BMRL | BMRL | 13 | BMRL | 11 | BMRL | BMRL | 13 | 13 | C9-20 | N | 1998-09-24 | 17:15 | 199.25 | 5592.2833 | 8.1 | 22 | 1.95 | 0.013 | 0.66667 | 2.8 | 1.11 | 1.69 | 22 | 8.2 | 23.8 | 75 | BMRL | BMRL | 4.2 | 63 | 67.2 | BMRL | BMRL | BMRL | 2.1 | 12 | BMRL | 11 | BMRL | BMRL | 14.1 | 14.1 | Electric Rate ($/kW-h) | 0.075
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7545.81 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-09-20 | 17:37 | 103.6167 | 5816.3489 | 8.1 | 24 | 2.5 | 0.019 | 0.76 | 2.4 | 0.62 | 1.78 | 23 | 8 | 23.73 | 125 | BMRL | BMRL | 4.9 | 86 | 90.9 | BMRL | BMRL | BMRL | BMRL | 14 | BMRL | 14 | BMRL | BMRL | 14 | 14 | C10-20 | N | 1998-09-26 | 14:05 | 244.0833 | 6850.6056 | 8.3 | 23 | 2.1 | 0.016 | 0.7619 | 2.8 | 0.96 | 1.84 | 23 | 8.3 | 23.7 | 97 | BMRL | BMRL | 5.3 | 83 | 88.3 | BMRL | BMRL | BMRL | BMRL | 13 | BMRL | 15 | BMRL | BMRL | 13 | 13 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 1770 | 1850 | 1810 | 4.4199 |  | Bromide | mg/L | 1770 | 1850 | 1810 | 4.4199 |  | C11-10 | N | 1998-09-21 | 11:15 | 121.25 | 6806.1667 | 8 | 23 | 2.55 | 0.02 | 0.78431 | 2.4 | 0.58 | 1.82 | 23 | 8 | 23.7 | 125 | BMRL | BMRL | 4.5 | 93 | 97.5 | BMRL | BMRL | BMRL | BMRL | 14 | BMRL | 13 | BMRL | BMRL | 14 | 14 | C11-20 | N | 1998-09-27 | 14:43 | 268.7167 | 7541.9811 | 8.2 | 23 | 2.4 | 0.018 | 0.75 | 3 | 1.05 | 1.95 | 23 | 8.2 | 23.7 | 115 | BMRL | BMRL | 5.5 | 88 | 93.5 | BMRL | BMRL | BMRL | BMRL | 14 | BMRL | 13 | BMRL | BMRL | 14 | 14 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-09-21 | 15:30 | 125.5 | 7044.7333 | 8 | 23 | 2.65 | 0.021 | 0.79245 | 2.6 | 0.66 | 1.94 | 22 | 8 | 23.75 | 115 | BMRL | BMRL | 5.5 | 92 | 97.5 | BMRL | BMRL | BMRL | BMRL | 15 | BMRL | 16 | 2 | BMRL | 15 | 15 | C12-20 | N | 1998-09-29 | 13:50 | 315.8333 | 8864.3889 | 8.1 | 22 | 2.75 | 0.021 | 0.76364 | 3.2 | 1.09 | 2.11 | 22 | 8.2 | 23.7 | 110 | BMRL | BMRL | 8.2 | 120 | 128.2 | BMRL | BMRL | BMRL | 3 | 19 | 1 | NR | 2.9 | BMRL | 22 | 23 | Current Process Water Rate ($/1000 gal)** | 0.15 to 0.20
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 8.6262e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [6 empty] | C13-10 | N | 1998-09-22 | 11:43 | 145.7167 | 8179.5622 | 8.1 | 23 | 2.7 | 0.022 | 0.81481 | 2.6 | 0.62 | 1.98 | 22 | 8.1 | 23.7 | 140 | BMRL | BMRL | 6.1 | 100 | 106.1 | BMRL | BMRL | BMRL | BMRL | 16 | BMRL | 17 | 2 | BMRL | 16 | 16 | C13-20 | N | 1998-10-01 | 13:38 | 363.6333 | 10205.9756 | 8.2 | 22 | 2.8 | 0.024 | 0.85714 | 3.4 | 1.08 | 2.32 | 23 | 8.2 | 23.7 | 125 | BMRL | 1 | 9.6 | 110 | 120.6 | BMRL | BMRL | BMRL | 3.2 | 21 | 1.3 | NR | 3.3 | BMRL | 24.2 | 25.5 | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | C14-10 | N | 1998-09-23 | 11:06 | 169.1 | 9492.1467 | 8.1 | 23 | 3 | 0.0245 | 0.81667 | 2.8 | 0.6 | 2.2 | 22 | 8.1 | 23.8 | 105 | BMRL | BMRL | 7.4 | 120 | 127.4 | BMRL | BMRL | BMRL | BMRL | 18 | BMRL | 20 | 2.4 | BMRL | 18 | 18 | C14-20 | N | 1998-10-03 | 20:20 | 418.3333 | 11741.2222 | 8.3 | 23 | 2.7 | 0.025 | 0.92593 | 3.6 | 0.96 | 2.64 | 22 | 8.2 | 23.7 | 145 | BMRL | 1.2 | 13 | 120 | 134.2 | BMRL | BMRL | BMRL | 3.3 | 22 | 1.6 | NR | 3.8 | BMRL | 25.3 | 26.9
|  |  |  | Scaling factor, SF | 9.3556 | 140 | 0.106 |  |  |  | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-24 | 1998-10-05 | --- | --- | Sampling date | MM/DD/YY | 1998-09-16 | 1998-09-24 | 1998-10-05 | --- | --- | C15-10 | N | 1998-09-24 | 13:35 | 195.5833 | 10978.7444 | 8.1 | 22 | 3.25 | 0.028 | 0.86154 | 2.8 | 0.52 | 2.28 | 22 | 8.1 | 23.7 | 140 | BMRL | BMRL | 8.2 | 120 | 128.2 | BMRL | BMRL | BMRL | BMRL | 19 | BMRL | 21 | 2.7 | BMRL | 19 | 19 | C15-20 | N | 1998-10-05 | 15:30 | 461.5 | 12952.7667 | 8.1 | 22 | 3 | 0.026 | 0.86667 | 3.8 | 1.15 | 2.65 | 23 | 8.2 | 23.7 | 195 | BMRL | 1.3 | 13 | 120 | 134.3 | BMRL | BMRL | BMRL | 3.7 | 23 | 1.8 | NR | 3.8 | BMRL | 26.7 | 28.5
Plant Name | Odessa Utilities Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3909 | 170 | 0.088 |  |  |  | Sampling time | hh:mm | 16:10 | 13:35 | 15:30 | --- | --- | Sampling time | hh:mm | 16:10 | 13:35 | 15:30 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Treatment Plant Category | Conventional filtration |  |  | RSSCT flow rate, QSC (mL/min) | 11.7064 | 200 | 0.075 |  |  |  | Operation time | hh.hh | 6.1667 | 195.5833 | 461.5 | --- | --- | Operation time | hh.hh | 6.1667 | 195.5833 | 461.5 | --- | --- | ** Temperature, and SDS temperature are measured values | [33 empty] | ** Temperature, and SDS temperature are measured values
Process Train Name | Plants 1 and 2 |  |  | Estimated total influent volume required, VSCT (L) | 283.2576 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 346.1556 | 10978.7444 | 25905.5333 | --- | --- | Bed volumes | (20 minute) | 173.0778 | 5489.3722 | 12952.7667 | --- | ---
ICR Treatment Plant Identification Number | 702 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.8 | 7.9 | 8.2 | 7.9667 | 2.613 | pH | --- | 7.8 | 7.9 | 8.2 | 7.9667 | 2.613
PWSID Number of Plant (if assigned) | TX0680002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.3 | 0.2 | 0.4 | 0.3 | 33.3333 | Turbidity | ntu | 0.3 | 0.2 | 0.4 | 0.3 | 33.3333
Historical Minimum Water Temperature (oC) | 7 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 22 | 24 | 23 | 23 | 4.3478 | Temperature | oC | 22 | 24 | 23 | 23 | 4.3478
Historical Average Water Temperature (oC) | 19 |  |  | Estimated full-scale run time, tLCT (days) | 52.4015 | [5 empty] | Total organic carbon | mg/L | 4.3 | 4.2 | 4.25 | 4.25 | 1.1765 | Total organic carbon | mg/L | 4.3 | 4.2 | 4.25 | 4.25 | 1.1765 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 40 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0689 | [5 empty] | UV254 | cm-1 | 0.05 | 0.05 | 0.051 | 0.050333 | 1.1471 | UV254 | cm-1 | 0.05 | 0.05 | 0.051 | 0.050333 | 1.1471 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 5.6011 | [5 empty] | SUVA | L/(mg*m) | 1.1628 | 1.1905 | 1.2 | 1.1844 | 1.632 | SUVA | L/(mg*m) | 1.1628 | 1.1905 | 1.2 | 1.1844 | 1.632 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.1668 | [5 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 4 | 0 | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 4 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 94.4192 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.62 | 0.6 | 0.63 | 0.615 | 3.4493 | SDS-Free Cl2 residual | mg/L | 0.62 | 0.6 | 0.63 | 0.61667 | 2.4771
|  |  |  | Mass GAC required, mSC (g) | 6.2564 | [5 empty] | SDS-Cl2 demand | mg/L | 3.38 | 3.4 | 3.37 | 3.385 | 0.62668 | SDS-Cl2 demand | mg/L | 3.38 | 3.4 | 3.37 | 3.3833 | 0.45149
[11 empty] | SDS-Chlorination temp. | oC | 23 | 22 | 23 | 22.5 | 3.1427 | SDS-Chlorination temp. | oC | 23 | 22 | 23 | 22.6667 | 2.5471
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8 | 8.3 | 8.1 | 8.2 | 1.7247 | SDS-Chlorination pH | --- | 8 | 8.3 | 8.1 | 8.1333 | 1.8781
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 23.8 | 23.8 | 23.8 | 23.8 | 0 | SDS-Incubation time | hours | 23.8 | 23.8 | 23.8 | 23.8 | 0
|  |  |  | Estimated full-scale run time, tLCT (days) | 104.8029 | [5 empty] | SDS-TOX | mg Cl- /L | 200 | 225 | 290 | 238.3333 | 19.4928 | SDS-TOX | mg Cl- /L | 200 | 225 | 290 | 238.3333 | 19.4928
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1378 | [5 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
|  |  |  | Estimated RSSCT run time, tSCT (days) | 11.2022 | [5 empty] | SDS-BDCM | mg/L | 2.7 | 3.5 | 2.8 | 3 | 14.5297 | SDS-BDCM | mg/L | 2.7 | 3.5 | 2.8 | 3 | 14.5297
|  |  |  | RSSCT bed length, lSC (cm) | 26.3335 | [5 empty] | SDS-DBCM | mg/L | 21 | 23 | 22 | 22 | 4.5455 | SDS-DBCM | mg/L | 21 | 23 | 22 | 22 | 4.5455
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 188.8384 | [5 empty] | SDS-CHBr3 | mg/L | 170 | 190 | 190 | 183.3333 | 6.2984 | SDS-CHBr3 | mg/L | 170 | 190 | 190 | 183.3333 | 6.2984
|  |  |  | Mass GAC required, mSC (g) | 12.5128 | [5 empty] | SDS-THM4 | mg/L | 193.7 | 216.5 | 214.8 | 208.3333 | 6.0966 | SDS-THM4 | mg/L | 193.7 | 216.5 | 214.8 | 208.3333 | 6.0966
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-DCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 4.4 | 4.1 | 4.2 | 4.2333 | 3.6083 | SDS-MBAA* | mg/L | 4.4 | 4.1 | 4.2 | 4.2333 | 3.6083
[11 empty] | SDS-DBAA* | mg/L | 29 | 29 | 29 | 29 | 0 | SDS-DBAA* | mg/L | 29 | 29 | 29 | 29 | 0
[11 empty] | SDS-BCAA* | mg/L | 3.1 | 3.2 | 3.1 | 3.1333 | 1.8426 | SDS-BCAA* | mg/L | 3.1 | 3.2 | 3.1 | 3.1333 | 1.8426
[11 empty] | SDS-TBAA | mg/L | 28 | 26 | 26 | 26.6667 | 4.3301 | SDS-TBAA | mg/L | 28 | 26 | 26 | 26.6667 | 4.3301
[11 empty] | SDS-CDBAA | mg/L | 6.5 | 5.7 | 6.2 | 6.1333 | 6.5893 | SDS-CDBAA | mg/L | 6.5 | 5.7 | 6.2 | 6.1333 | 6.5893
[11 empty] | SDS-DCBAA | mg/L | 1.2 | 1.2 | 1.1 | 1.1667 | 4.9487 | SDS-DCBAA | mg/L | 1.2 | 1.2 | 1.1 | 1.1667 | 4.9487
[11 empty] | SDS-HAA5 | mg/L | 33.4 | 33.1 | 33.2 | 33.2333 | 0.45964 | SDS-HAA5 | mg/L | 33.4 | 33.1 | 33.2 | 33.2333 | 0.45964
[11 empty] | SDS-HAA6 | mg/L | 36.5 | 36.3 | 36.3 | 36.3667 | 0.31752 | SDS-HAA6 | mg/L | 36.5 | 36.3 | 36.3 | 36.3667 | 0.31752
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
** Temperature, and SDS temperature are measured values
Note on N11: Reviewer M.H. (8/26/99): Per consultant: A 0.2-m in-line filter was incorporated for all RSSCT studies to minimize headloss formation and to render sample collection reasonable. High and frequent headloss formation were experienced in a previous study, eventhough the carbon fines were minimized with the rinsing process. No head-loss problems were experienced following this change.
Note on AG33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.
Note on BP33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.

## Sheet3. 3rd Quarter
|  | Study title: GAC adorption test using RSSCT |  | Study title: GAC adorption test using RSSCT |  |  |  | Study title: GAC adorption test using RSSCT |  |  | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [26 empty] | Study title: GAC adorption test using RSSCT | [11 empty] | Study title: GAC adorption test using RSSCT | [9 empty] | Study title: GAC adorption test using RSSCT | [8 empty] | Study title: GAC adorption test using RSSCT
|  | Client: City Odessa, TX |  | Client: City of Odessa, TX |  |  |  | Client: City of Odessa, TX |  |  | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [26 empty] | Client: City of Odessa, TX | [11 empty] | Client: City of Odessa, TX | [10 empty] | Client: City of Odessa, TX | [7 empty] | Client: City of Odessa, TX
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run | [33 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run | [33 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Odessa | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 3.7 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-12-01 | [5 empty] | 20-min. EBCT Start Date | 1998-12-01 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0680002 | Carbon trade name | Calgon F-400 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | Alum coagulant is added at a 13 mg/L dose | Bench-scale | 10-min. EBCT Start Time | 9:00 | [5 empty] | 20-min. EBCT Start Time | 9:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.446 | 4 | 4.75 | Rapid MIX | 0.5 mg/L organic polymer | Bench-scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 15.4 | 6 | 3.35 | Flocculation | 5, 10 and 20 rpm for 10-min period each | Bench-scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-12-01 | 14:18 | 5.3 | 297.5067 | 7.8 | 22 | 0.8 | BMRL | BMRL | 5 | 0.95 | 4.05 | 22 | 8.1 | 23.9 | BMRL | BMRL | BMRL | BMRL | 5.4 | 5.4 | BMRL | BMRL | BMRL | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | 1.1 | 1.1 | C1-20 | N | 1998-12-01 | 14:18 | 5.3 | 148.7533 | 8.1 | 23 | 1.15 | BMRL | BMRL | 5 | 1.23 | 3.77 | 23 | 8.2 | 24 | BMRL | BMRL | BMRL | BMRL | 4.3 | 4.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Sedimentation | in a drum for at least 1 hour | Bench-scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-12-02 | 13:48 | 28.8 | 1616.64 | 7.9 | 22 | 1.05 | BMRL | BMRL | 5 | 0.89 | 4.11 | 22 | 8.1 | 23.9 | BMRL | BMRL | BMRL | BMRL | 12 | 12 | BMRL | BMRL | BMRL | BMRL | 2.7 | BMRL | BMRL | BMRL | BMRL | 2.7 | 2.7 | C2-20 | N | 1998-12-03 | 16:33 | 55.55 | 1559.1033 | 7.7 | 22 | 1.6 | BMRL | BMRL | 5 | 1.23 | 3.77 | 22 | 8 | 24 | 46 | BMRL | BMRL | BMRL | 10 | 10 | BMRL | BMRL | BMRL | BMRL | 2.3 | BMRL | BMRL | BMRL | BMRL | 2.3 | 2.3 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Cartridge filtration | 0.45 um exclusion size and on-line 0.2 um | Bench-scale | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-17 | --- | --- |  | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-17 | --- | --- |  | C3-10 | N | 1998-12-02 | 23:43 | 38.7167 | 2173.2956 | 7.9 | 23 | 1 | BMRL | BMRL | 5.2 | 0.97 | 4.23 | 22 | 8.1 | 23.93 | 24 | BMRL | BMRL | 1 | 16 | 17 | BMRL | BMRL | BMRL | BMRL | 3.4 | BMRL | BMRL | BMRL | BMRL | 3.4 | 3.4 | C3-20 | N | 1998-12-03 | 20:00 | 59 | 1655.9333 | 7.8 | 23 | NA | BMRL | BMRL | 5 | 1.21 | 3.79 | 22 | 8 | 23.9 | BMRL | BMRL | BMRL | BMRL | 7.3 | 7.3 | BMRL | BMRL | BMRL | BMRL | 2.3 | BMRL | BMRL | BMRL | BMRL | 2.3 | 2.3 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 14:18 | 13:05 | --- | --- |  | Sampling time | hh:mm | 14:18 | 13:05 | --- | --- |  | C4-10 | N | 1998-12-03 | 16:33 | 55.55 | 3118.2067 | 7.8 | 22 | 1.2 | 0.008 | 0.66667 | 5.2 | 0.87 | 4.33 | 22 | 8.2 | 24 | 39 | BMRL | BMRL | 1.4 | 25 | 26.4 | BMRL | 2.5 | BMRL | BMRL | 5.5 | BMRL | 5.5 | BMRL | BMRL | 8 | 8 | C4-20 | N | 1998-12-04 | 18:21 | 81.35 | 2283.2233 | 7.7 | 23 | 1.95 | BMRL | BMRL | 5.2 | 1.1 | 4.1 | 22 | 8.1 | 24 | BMRL | BMRL | BMRL | 1.1 | 15 | 16.1 | BMRL | BMRL | BMRL | BMRL | 3.5 | BMRL | BMRL | BMRL | BMRL | 3.5 | 3.5 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 5.3 | 388.0833 | --- | --- |  | Operation time | hh.hh | 5.3 | 388.0833 | --- | --- |  | C5-10 | N | 1998-12-03 | 20:00 | 59 | 3311.8667 | 7.8 | 23 | 1.3 | 0.011 | 0.84615 | 5.4 | 0.95 | 4.45 | 23 | 8.1 | 24 | 30 | BMRL | BMRL | 1.9 | 26 | 27.9 | BMRL | BMRL | BMRL | BMRL | 5.4 | BMRL | 4.8 | BMRL | BMRL | 5.4 | 5.4 | C5-20 | N | 1998-12-05 | 19:40 | 106.6667 | 2993.7778 | 7.9 | 22 | 1.45 | BMRL | BMRL | 5.4 | 1.06 | 4.34 | 23 | 8.1 | 24 | 45 | BMRL | BMRL | 1.5 | 19 | 20.5 | BMRL | BMRL | BMRL | BMRL | 4.5 | BMRL | 4.4 | BMRL | BMRL | 4.5 | 4.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6859
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 297.5067 | 21784.4111 | --- | --- |  | Bed volumes | (20 minutes) | 148.7533 | 10892.2056 | --- | --- |  | C6-10 | N | 1998-12-04 | 3:45 | 66.75 | 3746.9 | 7.9 | 23 | 1.45 | 0.011 | 0.75862 | 5.4 | 0.9 | 4.5 | 22 | 8.1 | 24 | 35 | BMRL | BMRL | 2.1 | 31 | 33.1 | BMRL | 2.9 | BMRL | BMRL | 6.1 | BMRL | 5.9 | BMRL | BMRL | 9 | 9 | C6-20 | N | 1998-12-06 | 23:40 | 134.6667 | 3779.6444 | 8.1 | 22 | 1.3 | 0.0095 | 0.73077 | 5.4 | 0.92 | 4.48 | 23 | 8 | 24 | 41 | BMRL | BMRL | 1.1 | 27 | 28.1 | BMRL | 3.5 | BMRL | BMRL | 6.2 | BMRL | 5.4 | BMRL | BMRL | 9.7 | 9.7 | 1998 Producers Price Index (PPI base year 1967 = 100) | 130.5
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 130 | 135 | 132.5 | 3.7736 |  | Alkalinity | mg/L as CaCO3 | 130 | 135 | 132.5 | 3.7736 |  | C7-10 | N | 1998-12-04 | 13:09 | 76.15 | 4274.5533 | 7.7 | 22 | 1.65 | 0.012 | 0.72727 | 5.6 | 1.04 | 4.56 | 22 | 8 | 24 | 36 | BMRL | BMRL | 2.7 | 29 | 31.7 | BMRL | 2.8 | BMRL | 1 | 6.9 | BMRL | 6.7 | BMRL | BMRL | 10.7 | 10.7 | C7-20 | N | 1998-12-08 | 15:31 | 174.5167 | 4898.1011 | 8.1 | 23 | 1.8 | 0.0145 | 0.80556 | 5.6 | 0.69 | 4.91 | 22 | 8 | 24 | 54 | BMRL | BMRL | 1.5 | 35 | 36.5 | BMRL | 2.9 | BMRL | 1.3 | 7.9 | BMRL | 7.9 | BMRL | BMRL | 12.1 | 12.1 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3960.933 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 464 | 454 | 459 | 2.1786 |  | Total hardness | mg/L as CaCO3 | 464 | 454 | 459 | 2.1786 |  | C8-10 | N | 1998-12-04 | 18:21 | 81.35 | 4566.4467 | 8.1 | 22 | 1.85 | 0.014 | 0.75676 | 8.2 | 1.04 | 7.16 | 23 | 8.2 | 23.9 | 79 | BMRL | BMRL | 4.2 | 33 | 37.2 | BMRL | BMRL | BMRL | 1 | 8.9 | 1.1 | 7.1 | 2.2 | BMRL | 9.9 | 11 | C8-20 | N | 1998-12-09 | 11:50 | 194.8333 | 5468.3222 | 8 | 22 | 1.85 | 0.015 | 0.81081 | 5.6 | 0.65 | 4.95 | 22 | 8 | 24 | 65 | BMRL | BMRL | 1.5 | 39 | 40.5 | BMRL | 3 | BMRL | 1.4 | 8.7 | BMRL | 7.9 | BMRL | BMRL | 13.1 | 13.1 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 7921.8659 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 232 | 228 | 230 | 1.7391 |  | Calcium hardness | mg/L as CaCO3 | 232 | 228 | 230 | 1.7391 |  | C9-10 | N | 1998-12-05 | 12:34 | 99.5667 | 5589.0089 | 8 | 23 | 2.25 | 0.0185 | 0.82222 | 5.8 | 0.91 | 4.89 | 23 | 8.1 | 24 | 59 | BMRL | BMRL | 3.1 | 43 | 46.1 | BMRL | 2.9 | BMRL | 1.7 | 9.1 | BMRL | 9.3 | 2.1 | BMRL | 13.7 | 13.7 | C9-20 | N | 1998-12-10 | 13:07 | 220.1167 | 6177.9411 | 8.1 | 22 | 2.15 | 0.018 | 0.83721 | 5.8 | 0.71 | 5.09 | 23 | 8 | 24 | 62 | BMRL | BMRL | 2.4 | 44 | 46.4 | BMRL | 2.9 | BMRL | 1.2 | 9 | BMRL | 8.9 | BMRL | BMRL | 13.1 | 13.1 | Electric Rate ($/kW-h) | 0.075
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 10298.4257 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.8 | 0.8 | 0.8 | 0 |  | Ammonia | mg NH3-N / L | 0.8 | 0.8 | 0.8 | 0 |  | C10-10 | N | 1998-12-05 | 16:55 | 103.9167 | 5833.1889 | 8.1 | 22 | 2.05 | 0.0185 | 0.90244 | 8.2 | 0.96 | 7.24 | 22 | 8.2 | 23.9 | 66 | BMRL | BMRL | 5.4 | 46 | 51.4 | BMRL | BMRL | BMRL | 1.5 | 10 | BMRL | 8.6 | 2.3 | BMRL | 11.5 | 11.5 | C10-20 | N | 1998-12-10 | 17:42 | 224.7 | 6306.58 | 8.1 | 23 | 2.25 | 0.017 | 0.75556 | 6 | 0.96 | 5.04 | 22 | 8 | 24 | 71 | BMRL | BMRL | 4.2 | 43 | 47.2 | BMRL | BMRL | BMRL | 1.6 | 10 | BMRL | 10 | 2.4 | BMRL | 11.6 | 11.6 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 1180 | 1140 | 1160 | 3.4483 |  | Bromide | mg/L | 1180 | 1140 | 1160 | 3.4483 |  | C11-10 | N | 1998-12-06 | 12:22 | 123.3667 | 6924.9822 | 8 | 23 | 2.55 | 0.021 | 0.82353 | 3.5 | 1.39 | 2.11 | 23 | 8.1 | 23.9 | NR | BMRL | 1 | 8.7 | 47 | 56.7 | BMRL | BMRL | BMRL | 2.6 | 11 | 1.7 | 9.8 | 2.6 | BMRL | 13.6 | 15.3 | C11-20 | N | 1998-12-12 | 13:30 | 268.5 | 7535.9 | 8.1 | 23 | 2.2 | 0.021 | 0.95455 | 6.2 | 1 | 5.2 | 22 | 8 | 24 | 79 | BMRL | BMRL | 5.4 | 45 | 50.4 | BMRL | BMRL | BMRL | 1.7 | 11 | 1.3 | 11 | 2.7 | BMRL | 12.7 | 14 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-12-06 | 23:40 | 134.6667 | 7559.2889 | 8 | 23 | 2.6 | 0.02 | 0.76923 | 3.3 | 1.37 | 1.93 | 22 | 8.1 | 23.9 | 82 | BMRL | 1.1 | 9.7 | 59 | 69.8 | BMRL | BMRL | BMRL | 2.6 | 11 | 2 | 11 | 2.6 | BMRL | 13.6 | 15.6 | C12-20 | N | 1998-12-12 | 18:05 | 273.0833 | 7664.5389 | 8.2 | 22 | 2.3 | 0.021 | 0.91304 | 6.2 | 0.98 | 5.22 | 23 | 8 | 24 | 76 | BMRL | BMRL | 6.1 | 48 | 54.1 | BMRL | BMRL | BMRL | 1.7 | 11 | 1.2 | 11 | 2.5 | BMRL | 12.7 | 13.9 | Current Process Water Rate ($/1000 gal)** | 0.15 to 0.20
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1508e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [6 empty] | C13-10 | N | 1998-12-08 | 13:30 | 172.5 | 9683 | 8 | 22 | 2.9 | 0.024 | 0.82759 | 8.6 | 0.66 | 7.94 | 22 | 8 | 24 | 93 | BMRL | 1.2 | 7.8 | 69 | 78 | BMRL | BMRL | BMRL | 1.9 | 13 | 1.2 | 11 | 3 | BMRL | 14.9 | 16.1 | C13-20 | N | 1998-12-14 | 13:13 | 316.2167 | 8875.1478 | 8.1 | 23 | 2.5 | 0.024 | 0.96 | 6.8 | 1.3 | 5.5 | 22 | 8.2 | 24 | 94 | BMRL | BMRL | 8.4 | 65 | 73.4 | BMRL | BMRL | BMRL | 2 | 13 | 1.5 | 14 | 3 | BMRL | 15 | 16.5 | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | C14-10 | N | 1998-12-09 | 11:50 | 194.8333 | 10936.6444 | 8 | 22 | 2.95 | 0.0255 | 0.86441 | 9 | 0.63 | 8.37 | 23 | 8.1 | 23.9 | 91 | BMRL | 1.4 | 7.6 | 68 | 77 | BMRL | BMRL | BMRL | 2.6 | 17 | 4.1 | 9.8 | 2.3 | 1 | 19.6 | 23.7 | C14-20 | N | 1998-12-16 | 13:20 | 364.3333 | 10225.6222 | 8.1 | 22 | 2.65 | 0.025 | 0.9434 | 6.8 | 1.24 | 5.56 | 23 | 8.1 | 24 | 96 | BMRL | 1 | 9.3 | 58 | 68.3 | BMRL | BMRL | BMRL | 2.6 | 13 | 1.7 | 14 | 3.4 | BMRL | 15.6 | 17.3
|  |  |  | Scaling factor, SF | 9.3556 | 140 | 0.106 |  |  |  | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-10 | 1998-12-17 | --- | --- | Sampling date | MM/DD/YY | 1998-12-01 | 1998-12-10 | 1998-12-17 | --- | --- | C15-10 | N | 1998-12-10 | 13:07 | 220.1167 | 12355.8822 | 88 | 22 | 3.1 | 0.028 | 0.90323 | 3.7 | 1.4 | 2.3 | 22 | 8 | 24 | 100 | BMRL | 1.6 | 14 | 68 | 83.6 | BMRL | 3.1 | BMRL | 3.6 | 14 | 2.9 | 14 | 3.4 | 1.2 | 20.7 | 23.6 | C15-20 | N | 1998-12-17 | 13:05 | 388.0833 | 10892.2056 | 8.1 | 22 | 2.9 | 0.026 | 0.89655 | 7 | 1.3 | 5.7 | 23 | 8 | 24 | 94 | BMRL | 1.3 | 11 | 61 | 73.3 | BMRL | BMRL | BMRL | 2.4 | 14 | 1.8 | 15 | 3.8 | BMRL | 16.4 | 18.2
Plant Name | Odessa Utilities Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.391 | 170 | 0.088 |  |  |  | Sampling time | hh:mm | 14:18 | 13:07 | 13:05 | --- | --- | Sampling time | hh:mm | 14:18 | 13:07 | 13:05 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Treatment Plant Category | Conventional filtration |  |  | RSSCT flow rate, QSC (mL/min) | 11.7065 | 200 | 0.075 |  |  |  | Operation time | hh.hh | 5.3 | 220.1167 | 388.0833 | --- | --- | Operation time | hh.hh | 5.3 | 220.1167 | 388.0833 | --- | --- | ** Temperature, and SDS temperature are measured values | [33 empty] | ** Temperature, and SDS temperature are measured values
Process Train Name | Plants 1 and 2 |  |  | Estimated total influent volume required, VSCT (L) | 386.5903 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 297.5067 | 12355.8822 | 21784.4111 | --- | --- | Bed volumes | (20 minute) | 148.7533 | 6177.9411 | 10892.2056 | --- | ---
ICR Treatment Plant Identification Number | 702 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.9 | 8 | 8 | 7.9667 | 0.72471 | pH | --- | 7.9 | 8 | 8 | 7.9667 | 0.72471
PWSID Number of Plant (if assigned) | TX0680002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.2 | 0.2 | 0.2 | 0.2 | 0 | Turbidity | ntu | 0.2 | 0.2 | 0.2 | 0.2 | 0
Historical Minimum Water Temperature (oC) | 7 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 23 | 23 | 23 | 23 | 0 | Temperature | oC | 23 | 23 | 23 | 23 | 0
Historical Average Water Temperature (oC) | 19 |  |  | Estimated full-scale run time, tLCT (days) | 71.5168 | [5 empty] | Total organic carbon | mg/L | 3.9 | 4.05 | 3.95 | 3.9667 | 1.9255 | Total organic carbon | mg/L | 3.9 | 4.05 | 3.95 | 3.9667 | 1.9255 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 40 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0689 | [5 empty] | UV254 | cm-1 | 0.051 | 0.051 | 0.0515 | 0.051167 | 0.56419 | UV254 | cm-1 | 0.051 | 0.051 | 0.0515 | 0.051167 | 0.56419 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 7.6443 | [5 empty] | SUVA | L/(mg*m) | 1.3077 | 1.2593 | 1.3038 | 1.2902 | 2.0856 | SUVA | L/(mg*m) | 1.3077 | 1.2593 | 1.3038 | 1.2902 | 2.0856 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.1669 | [5 empty] | SDS-Cl2 dose | mg/L | 9.7 | 9.7 | 9.7 | 9.7 | 0 | SDS-Cl2 dose | mg/L | 9.7 | 9.7 | 9.7 | 9.7 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 128.8634 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.78 | 0.64 | 0.64 | 0.68667 | 11.7712 | SDS-Free Cl2 residual | mg/L | 0.78 | 0.64 | 0.64 | 0.68667 | 11.7712
|  |  |  | Mass GAC required, mSC (g) | 6.2565 | [5 empty] | SDS-Cl2 demand | mg/L | 8.92 | 9.06 | 9.06 | 9.0133 | 0.89677 | SDS-Cl2 demand | mg/L | 8.92 | 9.06 | 9.06 | 9.0133 | 0.89677
[11 empty] | SDS-Chlorination temp. | oC | 23 | 23 | 22 | 22.6667 | 2.5471 | SDS-Chlorination temp. | oC | 23 | 23 | 22 | 22.6667 | 2.5471
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8 | 8 | 8 | 8 | 0 | SDS-Chlorination pH | --- | 8 | 8 | 8 | 8 | 0
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 24 | 0 | SDS-Incubation time | hours | 24 | 24 | 24 | 24 | 0
|  |  |  | Estimated full-scale run time, tLCT (days) | 143.0337 | [5 empty] | SDS-TOX | mg Cl- /L | 175 | 185 | 165 | 175 | 5.7143 | SDS-TOX | mg Cl- /L | 175 | 185 | 165 | 175 | 5.7143
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1378 | [5 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
|  |  |  | Estimated RSSCT run time, tSCT (days) | 15.2886 | [5 empty] | SDS-BDCM | mg/L | 3.5 | 3.2 | 2.6 | 3.1 | 14.7825 | SDS-BDCM | mg/L | 3.5 | 3.2 | 2.6 | 3.1 | 14.7825
|  |  |  | RSSCT bed length, lSC (cm) | 26.3338 | [5 empty] | SDS-DBCM | mg/L | 22 | 21 | 19 | 20.6667 | 7.3913 | SDS-DBCM | mg/L | 22 | 21 | 19 | 20.6667 | 7.3913
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 257.7268 | [5 empty] | SDS-CHBr3 | mg/L | 110 | 110 | 110 | 110 | 0 | SDS-CHBr3 | mg/L | 110 | 110 | 110 | 110 | 0
|  |  |  | Mass GAC required, mSC (g) | 12.5129 | [5 empty] | SDS-THM4 | mg/L | 135.5 | 134.2 | 131.6 | 133.7667 | 1.4845 | SDS-THM4 | mg/L | 135.5 | 134.2 | 131.6 | 133.7667 | 1.4845
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | 5 | 4.3 | 4.6 | 4.6333 | 7.5796 | SDS-DCAA* | mg/L | 5 | 4.3 | 4.6 | 4.6333 | 7.5796 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 4.8 | 4.6 | 4.6 | 4.6667 | 2.4744 | SDS-MBAA* | mg/L | 4.8 | 4.6 | 4.6 | 4.6667 | 2.4744
[11 empty] | SDS-DBAA* | mg/L | 37 | 35 | 34 | 35.3333 | 4.3232 | SDS-DBAA* | mg/L | 37 | 35 | 34 | 35.3333 | 4.3232
[11 empty] | SDS-BCAA* | mg/L | 10 | 9.3 | 9.7 | 9.6667 | 3.633 | SDS-BCAA* | mg/L | 10 | 9.3 | 9.7 | 9.6667 | 3.633
[11 empty] | SDS-TBAA | mg/L | 13 | 13 | 13 | 13 | 0 | SDS-TBAA | mg/L | 13 | 13 | 13 | 13 | 0
[11 empty] | SDS-CDBAA | mg/L | 3.9 | 3.8 | 3.6 | 3.7667 | 4.0554 | SDS-CDBAA | mg/L | 3.9 | 3.8 | 3.6 | 3.7667 | 4.0554
[11 empty] | SDS-DCBAA | mg/L | 1.7 | 1.5 | 1.6 | 1.6 | 6.25 | SDS-DCBAA | mg/L | 1.7 | 1.5 | 1.6 | 1.6 | 6.25
[11 empty] | SDS-HAA5 | mg/L | 46.8 | 43.9 | 43.2 | 44.6333 | 4.2765 | SDS-HAA5 | mg/L | 46.8 | 43.9 | 43.2 | 44.6333 | 4.2765
[11 empty] | SDS-HAA6 | mg/L | 56.8 | 53.2 | 52.9 | 54.3 | 3.9968 | SDS-HAA6 | mg/L | 56.8 | 53.2 | 52.9 | 54.3 | 3.9968
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
** Temperature, and SDS temperature are measured values
Note on N10: Reviewer M.H. (8/26/99): Per consultant: A 0.2-m in-line filter was incorporated for all RSSCT studies to minimize headloss formation and to render sample collection reasonable. High and frequent headloss formation were experienced in a previous study, eventhough the carbon fines were minimized with the rinsing process. No head-loss problems were experienced following this change.
Note on AG33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.
Note on AR8: Reviewer M.H. (8/26/99): Per consultant: The chlorine dose for the 10-min column was checked. The variation in dose may have been due to the impact of ammonia. A small test was conducted at the time of the testing to verify this assumption. Chlorine dose and ammonia were compared for 4 effluent samples (C1-20, C4-20, C5-10, and C4-10). However, the ammonia-N in those samples was always less than 0.1 mg/L NH3-N. This was only experienced in Quarter 3.
Note on BP33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.

## Sheet4. 4th Quarter
|  | Study title: GAC adorption test using RSSCT |  | Study title: GAC adorption test using RSSCT |  |  |  | Study title: GAC adorption test using RSSCT |  |  | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [6 empty] | Study title: GAC adorption test using RSSCT | [26 empty] | Study title: GAC adorption test using RSSCT | [11 empty] | Study title: GAC adorption test using RSSCT | [9 empty] | Study title: GAC adorption test using RSSCT | [8 empty] | Study title: GAC adorption test using RSSCT
|  | Client: City Odessa, TX |  | Client: City of Odessa, TX |  |  |  | Client: City of Odessa, TX |  |  | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [6 empty] | Client: City of Odessa, TX | [26 empty] | Client: City of Odessa, TX | [11 empty] | Client: City of Odessa, TX | [10 empty] | Client: City of Odessa, TX | [7 empty] | Client: City of Odessa, TX
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run | [33 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run | [33 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Odessa | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1999-02-16 | [5 empty] | 20-min. EBCT Start Date | 1999-02-16 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX0680002 | Carbon trade name | Calgon F-400 | Inner diameter of the RSSCT column, DSC (mm) | 11 | mesh size | (mm) | Coagulation | Alum coagulant is added at a 13 mg/L dose | Bench-scale | 10-min. EBCT Start Time | 10:00 | [5 empty] | 20-min. EBCT Start Time | 10:00 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous coal based | Minimum RSSCT Reynolds number, ReSC, min | 0.422 | 4 | 4.75 | Rapid MIX | 0.3 mg/L organic polymer | Bench-scale | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 30
|  | Original GAC mesh size, upper (US standard mesh) | 12 | Full-scale operating temperature, ToC (oC) | 13.2 | 6 | 3.35 | Flocculation | 5, 10 and 20 rpm for 10-min period each | Bench-scale | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1999-02-16 | 15:35 | 5.5833 | 313.4111 | 8.3 | 22 | 0.8 | BMRL | BMRL | 1.8 | 1.28 | 0.52 | 13 | 8.3 | 23.88 | BMRL | BMRL | BMRL | BMRL | 6 | 6 | BMRL | BMRL | BMRL | BMRL | 1 | BMRL | BMRL | BMRL | BMRL | 1 | 1 | C1-20 | N | 1999-02-16 | 15:35 | 5.5833 | 156.7056 | 8.3 | 22 | 0.7 | BMRL | BMRL | 1.8 | 1.39 | 0.41 | 14 | 8.4 | 24 | 59 | BMRL | BMRL | BMRL | 3.3 | 3.3 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | 0 | Overhead & Profit Factor (% of construction costs) | 5
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 40 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Sedimentation | in a drum for at least 1 hour | Bench-scale | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1999-02-16 | 21:18 | 11.3 | 634.3067 | 8.1 | 22 | 1 | BMRL | BMRL | 1.8 | 1.28 | 0.52 | 13 | 8.3 | 23.9 | BMRL | BMRL | BMRL | 0.6 | 11 | 11.6 | BMRL | BMRL | BMRL | BMRL | 1.9 | BMRL | BMRL | BMRL | BMRL | 1.9 | 1.9 | C2-20 | N | 1999-02-17 | 12:55 | 26.9167 | 755.4611 | 8.2 | 22 | 1.25 | BMRL | BMRL | 1.8 | 1.32 | 0.48 | 13 | 8.4 | 24 | 33 | BMRL | BMRL | BMRL | 8.5 | 8.5 | BMRL | BMRL | BMRL | BMRL | 1.7 | BMRL | BMRL | BMRL | BMRL | 1.7 | 1.7 | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.0525 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.5 | 10 | 2 | Cartridge filtration | 0.45 um exclusion size and on-line 0.2 um | Bench-scale | Sampling date | MM/DD/YY | 1999-02-16 | 1999-03-04 | --- | --- |  | Sampling date | MM/DD/YY | 1999-02-16 | 1999-03-04 | --- | --- |  | C3-10 | N | 1999-02-17 | 12:55 | 26.9167 | 1510.9222 | 8.1 | 22 | 1.3 | BMRL | BMRL | 1.8 | 1.11 | 0.69 | 13 | 8.3 | 24 | 37 | BMRL | BMRL | 1.3 | 27 | 28.3 | BMRL | BMRL | BMRL | BMRL | 4.9 | BMRL | 5.4 | BMRL | BMRL | 4.9 | 4.9 | C3-20 | N | 1999-02-17 | 16:40 | 30.6667 | 860.7111 | 8 | 22 | 1.05 | BMRL | BMRL | 1.8 | 1.34 | 0.46 | 13 | 8.3 | 24 | 31 | BMRL | BMRL | 0.5 | 9.9 | 10.4 | BMRL | BMRL | BMRL | BMRL | 1.9 | BMRL | BMRL | BMRL | BMRL | 1.9 | 1.9 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 15:35 | 12:00 | --- | --- |  | Sampling time | hh:mm | 15:35 | 12:00 | --- | --- |  | C4-10 | N | 1999-02-17 | 22:12 | 36.2 | 2032.0267 | 8.1 | 23 | 1.65 | 0.01 | 0.60606 | 2 | 1.07 | 0.93 | 13 | 8.3 | 24 | 72 | BMRL | BMRL | 2.2 | 41 | 43.2 | BMRL | BMRL | BMRL | 1.3 | 7.3 | BMRL | 7.8 | BMRL | BMRL | 8.6 | 8.6 | C4-20 | N | 1999-02-18 | 17:38 | 55.6333 | 1561.4422 | 8.2 | 23 | 1.1 | BMRL | BMRL | 2 | 1.34 | 0.66 | 13 | 8.4 | 24 | 25 | BMRL | BMRL | 0.9 | 16 | 16.9 | BMRL | BMRL | BMRL | BMRL | 3.2 | BMRL | BMRL | BMRL | BMRL | 3.2 | 3.2 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 5.5833 | 386 | --- | --- |  | Operation time | hh.hh | 5.5833 | 386 | --- | --- |  | C5-10 | N | 1999-02-18 | 17:38 | 55.6333 | 3122.8844 | 8.1 | 22 | 2.3 | 0.016 | 0.69565 | 2 | 0.83 | 1.17 | 14 | 8.3 | 24 | 100 | BMRL | BMRL | 3.6 | 65 | 68.6 | BMRL | BMRL | BMRL | 2 | 12 | BMRL | 13 | 2.4 | BMRL | 14 | 14 | C5-20 | N | 1999-02-19 | 14:05 | 76.0833 | 2135.4056 | 8.1 | 22 | 1.15 | BMRL | BMRL | 2 | 1.29 | 0.71 | 14 | 8.3 | 24 | 44 | BMRL | BMRL | 1.2 | 22 | 23.2 | BMRL | BMRL | BMRL | BMRL | 4.5 | BMRL | 5.2 | BMRL | BMRL | 4.5 | 4.5 | 1998 ENR Construction Cost Index (CCI base year 1913) | 6859
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 313.4111 | 21667.4667 | --- | --- |  | Bed volumes | (20 minutes) | 156.7056 | 10833.7333 | --- | --- |  | C6-10 | N | 1999-02-18 | 22:39 | 60.65 | 3404.4867 | 8.1 | 23 | 2.4 | 0.019 | 0.79167 | 2.4 | 0.96 | 1.44 | 13 | 8.2 | 23.95 | 100 | BMRL | BMRL | 5.4 | 64 | 69.4 | BMRL | BMRL | BMRL | 1.9 | 14 | 1.2 | 14 | 2.6 | BMRL | 15.9 | 17.1 | C6-20 | N | 1999-02-19 | 18:00 | 80 | 2245.3333 | 8.1 | 22 | 1.25 | BMRL | BMRL | 2 | 1.35 | 0.65 | 13 | 8.2 | 24 | 52 | BMRL | BMRL | 1.1 | 21 | 22.1 | BMRL | BMRL | BMRL | BMRL | 5 | BMRL | 6 | BMRL | BMRL | 5 | 5 | 1998 Producers Price Index (PPI base year 1967 = 100) | 130.5
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 125 | 125 | 125 | 0 |  | Alkalinity | mg/L as CaCO3 | 125 | 125 | 125 | 0 |  | C7-10 | N | 1999-02-19 | 3:39 | 65.65 | 3685.1533 | 8.2 | 22 | 2.75 | 0.02 | 0.72727 | 2.4 | 1 | 1.4 | 13 | 8.3 | 23.9 | 90 | BMRL | BMRL | 5.6 | 71 | 76.6 | BMRL | BMRL | BMRL | 1.8 | 15 | 1.2 | 16 | 2.7 | BMRL | 16.8 | 18 | C7-20 | N | 1999-02-20 | 21:48 | 107.8 | 3025.5867 | 8.1 | 23 | 1.5 | BMRL | BMRL | 2 | 1.2 | 0.8 | 13 | 8.2 | 24 | 71 | BMRL | BMRL | 1.7 | 34 | 35.7 | BMRL | BMRL | BMRL | BMRL | 6.6 | BMRL | 7.5 | BMRL | BMRL | 6.6 | 6.6 | Labor Rate + Fringe ($/work-hour) | 19
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 2677.927 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 506 | 504 | 505 | 0.39604 |  | Total hardness | mg/L as CaCO3 | 506 | 504 | 505 | 0.39604 |  | C8-10 | N | 1999-02-19 | 14:05 | 76.0833 | 4270.8111 | 8 | 22 | 2.9 | 0.022 | 0.75862 | 2.4 | 0.95 | 1.45 | 13 | 8.2 | 23.9 | 120 | BMRL | BMRL | 6 | 79 | 85 | BMRL | BMRL | BMRL | 1.4 | 15 | 1.1 | 15 | 2.5 | BMRL | 16.4 | 17.5 | C8-20 | N | 1999-02-21 | 17:15 | 127.25 | 3571.4833 | 8.2 | 23 | 1.85 | 0.01 | 0.54054 | 2.2 | 1.22 | 0.98 | 13 | 8.3 | 24 | 63 | BMRL | BMRL | 2.5 | 42 | 44.5 | BMRL | BMRL | BMRL | BMRL | 8.2 | BMRL | 8.5 | BMRL | BMRL | 8.2 | 8.2 | Labor Overhead Factor (% of labor) | 10
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 5355.8539 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 245 | 244 | 244.5 | 0.409 |  | Calcium hardness | mg/L as CaCO3 | 245 | 244 | 244.5 | 0.409 |  | C9-10 | N | 1999-02-19 | 18:00 | 80 | 4490.6667 | 8.1 | 23 | 3 | 0.023 | 0.76667 | 2.4 | 0.88 | 1.52 | 13 | 8.2 | 24 | 145 | BMRL | 0.6 | 6.8 | 85 | 92.4 | BMRL | BMRL | BMRL | 1.9 | 16 | 1.2 | 16 | 2.6 | BMRL | 17.9 | 19.1 | C9-20 | N | 1999-02-21 | 20:50 | 130.8333 | 3672.0556 | 8.2 | 22 | 1.8 | 0.011 | 0.61111 | 2.2 | 1.2 | 1 | 13 | 8.3 | 24 | 57 | BMRL | BMRL | 2.6 | 45 | 47.6 | BMRL | BMRL | BMRL | BMRL | 8.9 | BMRL | 9.3 | BMRL | BMRL | 8.9 | 8.9 | Electric Rate ($/kW-h) | 0.075
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 6962.6101 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1999-02-19 | 23:00 | 85 | 4771.3333 | 8.1 | 22 | 2.95 | 0.025 | 0.84746 | 2.4 | 0.83 | 1.57 | 14 | 8.3 | 24 | 99 | BMRL | BMRL | 6.7 | 93 | 99.7 | BMRL | BMRL | BMRL | 1.9 | 17 | 1.2 | 16 | 2.6 | BMRL | 18.9 | 20.1 | C10-20 | N | 1999-02-22 | 19:33 | 153.55 | 4309.6367 | 8.1 | 22 | 2.2 | 0.014 | 0.63636 | 2.4 | 1.21 | 1.19 | 14 | 8.2 | 24.1 | 63 | BMRL | BMRL | 3.8 | 50 | 53.8 | BMRL | BMRL | BMRL | 1.2 | 11 | BMRL | 11 | 2 | BMRL | 12.2 | 12.2 | Fuel Oil Rate ($/gal) | 0.89
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 1500 | 1400 | 1450 | 6.8966 |  | Bromide | mg/L | 1500 | 1400 | 1450 | 6.8966 |  | C11-10 | N | 1999-02-20 | 16:48 | 102.8 | 5770.5067 | 8.1 | 23 | 3.1 | 0.025 | 0.80645 | 2.4 | 0.76 | 1.64 | 14 | 8.2 | 24 | 100 | BMRL | BMRL | 6.6 | 96 | 102.6 | BMRL | BMRL | BMRL | 2.1 | 17 | 1.1 | 16 | 2.6 | BMRL | 19.1 | 20.2 | C11-20 | N | 1999-02-24 | 21:33 | 203.55 | 5712.97 | 8.2 | 23 | 2.5 | 0.02 | 0.8 | 2.4 | 0.99 | 1.41 | 14 | 8.2 | 24.1 | 91 | BMRL | BMRL | 5.1 | 71 | 76.1 | BMRL | BMRL | BMRL | 1.7 | 14 | 1 | 14 | 2.3 | BMRL | 15.7 | 16.7 | Natural Gas Rate ($/ft3) | 0.0055
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1999-02-20 | 21:48 | 107.8 | 6051.1733 | 8.2 | 22 | 3.15 | 0.0265 | 0.84127 | 2.4 | 0.83 | 1.57 | 13 | 8.3 | 23.9 | 135 | BMRL | 0.6 | 7.2 | 82 | 89.8 | BMRL | BMRL | BMRL | 2 | 17 | 1.3 | 15 | 2.7 | BMRL | 19 | 20.3 | C12-20 | N | 1999-02-27 | 22:47 | 276.7833 | 7768.3856 | 8.2 | 22 | 3.15 | 0.0245 | 0.77778 | 2.8 | 1.02 | 1.78 | 14 | 8.3 | 23.96 | 175 | BMRL | 0.5 | 7.5 | 79 | 87 | BMRL | BMRL | BMRL | 2.2 | 16 | 1.4 | 16 | 2.8 | BMRL | 18.2 | 19.6 | Current Process Water Rate ($/1000 gal)** | 0.15 to 0.20
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.217e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [6 empty] | C13-10 | N | 1999-02-21 | 17:15 | 127.25 | 7142.9667 | 8.2 | 22 | 3.55 | 0.029 | 0.8169 | 2.8 | 0.92 | 1.88 | 14 | 8.2 | 23.9 | 200 | BMRL | 0.7 | 9.6 | 97 | 107.3 | BMRL | BMRL | BMRL | 2.3 | 18 | 1.7 | 19 | 3.3 | BMRL | 20.3 | 22 | C13-20 | N | 1999-02-28 | 22:00 | 300 | 8420 | 8.2 | 22 | 3.2 | 0.026 | 0.8125 | 2.8 | 1 | 1.8 | 13 | 8.3 | 24 | 195 | BMRL | 0.5 | 7.9 | 79 | 87.4 | BMRL | BMRL | BMRL | 2.5 | 17 | 1.6 | 16 | 3 | BMRL | 19.5 | 21.1 | Modifications to Existing Plant (% of construction costs) | 5
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | C14-10 | N | 1999-02-21 | 20:50 | 130.8333 | 7344.1111 | 8.2 | 23 | 3.55 | 0.03 | 0.84507 | 2.8 | 0.88 | 1.92 | 13 | 8.3 | 23.9 | 190 | BMRL | 1.2 | 11 | 99 | 111.2 | BMRL | BMRL | BMRL | 2.4 | 19 | 1.9 | 19 | 3.5 | BMRL | 21.4 | 23.3 | C14-20 | N | 1999-03-02 | 13:11 | 339.1833 | 9519.7456 | 8.1 | 22 | 3.65 | 0.028 | 0.76712 | 3 | 0.95 | 2.05 | 14 | 8.3 | 24 | 185 | BMRL | 0.7 | 10 | 93 | 103.7 | BMRL | BMRL | BMRL | 2.4 | 18 | 1.8 | 19 | 3.6 | BMRL | 20.4 | 22.2
|  |  |  | Scaling factor, SF | 9.3556 | 140 | 0.106 |  |  |  | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-22 | 1999-03-04 | --- | --- | Sampling date | MM/DD/YY | 1999-02-16 | 1999-02-22 | 1999-03-04 | --- | --- | C15-10 | N | 1999-02-22 | 13:15 | 147.25 | 8265.6333 | 8 | 23 | 3.8 | 0.033 | 0.86842 | 3 | 0.89 | 2.11 | 13 | 8.3 | 23.9 | 225 | BMRL | 0.9 | 12 | 99 | 111.9 | BMRL | BMRL | BMRL | 3.3 | 20 | 2.1 | 20 | 3.9 | BMRL | 23.3 | 25.4 | C15-20 | N | 1999-03-03 | 14:09 | 364.15 | 10220.4767 | 8.1 | 22 | 3.95 | 0.029 | 0.73418 | 3 | 0.98 | 2.02 | 14 | 8.3 | 24 | 235 | BMRL | 0.8 | 11 | 89 | 100.8 | BMRL | BMRL | BMRL | 2.5 | 18 | 2.1 | 18 | 3.7 | BMRL | 20.5 | 22.6
Plant Name | Odessa Utilities Water Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3955 | 170 | 0.088 |  |  |  | Sampling time | hh:mm | 15:35 | 13:15 | 12:00 | --- | --- | Sampling time | hh:mm | 15:35 | 13:15 | 12:00 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
Treatment Plant Category | Conventional filtration |  |  | RSSCT flow rate, QSC (mL/min) | 11.7136 | 200 | 0.075 |  |  |  | Operation time | hh.hh | 5.5833 | 147.25 | 386 | --- | --- | Operation time | hh.hh | 5.5833 | 147.25 | 386 | --- | --- | ** Temperature, and SDS temperature are measured values | [33 empty] | ** Temperature, and SDS temperature are measured values
Process Train Name | Plants 1 and 2 |  |  | Estimated total influent volume required, VSCT (L) | 261.5249 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 313.4111 | 8265.6333 | 21667.4667 | --- | --- | Bed volumes | (20 minute) | 156.7056 | 4132.8167 | 10833.7333 | --- | ---
ICR Treatment Plant Identification Number | 702 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8 | 7.9 | 8.1 | 8 | 1.25 | pH | --- | 8 | 7.9 | 8.1 | 8 | 1.25
PWSID Number of Plant (if assigned) | TX0680002 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.2 | 0.2 | 0.2 | 0.2 | 0 | Turbidity | ntu | 0.2 | 0.2 | 0.2 | 0.2 | 0
Historical Minimum Water Temperature (oC) | 7 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 22 | 23 | 22 | 22.3333 | 2.5852 | Temperature | oC | 22 | 23 | 22 | 22.3333 | 2.5852
Historical Average Water Temperature (oC) | 19 |  |  | Estimated full-scale run time, tLCT (days) | 48.3515 | [5 empty] | Total organic carbon | mg/L | 5.05 | 4.95 | 4.9 | 4.9667 | 1.5378 | Total organic carbon | mg/L | 5.05 | 4.95 | 4.9 | 4.9667 | 1.5378 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 40 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.0689 | [5 empty] | UV254 | cm-1 | 0.062 | 0.061 | 0.061 | 0.061333 | 0.94133 | UV254 | cm-1 | 0.062 | 0.061 | 0.061 | 0.061333 | 0.94133 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 5.1682 | [5 empty] | SUVA | L/(mg*m) | 1.2277 | 1.2323 | 1.2449 | 1.235 | 0.71991 | SUVA | L/(mg*m) | 1.2277 | 1.2323 | 1.2449 | 1.235 | 0.71991 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 13.1748 | [5 empty] | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 4 | 0 | SDS-Cl2 dose | mg/L | 4 | 4 | 4 | 4 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 87.175 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.73 | 0.76 | 0.76 | 0.75 | 2.3094 | SDS-Free Cl2 residual | mg/L | 0.73 | 0.76 | 0.76 | 0.75 | 2.3094
|  |  |  | Mass GAC required, mSC (g) | 6.2602 | [5 empty] | SDS-Cl2 demand | mg/L | 3.27 | 3.24 | 3.24 | 3.25 | 0.53294 | SDS-Cl2 demand | mg/L | 3.27 | 3.24 | 3.24 | 3.25 | 0.53294
[11 empty] | SDS-Chlorination temp. | oC | 14 | 14 | 14 | 14 | 0 | SDS-Chlorination temp. | oC | 14 | 14 | 14 | 14 | 0
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.2 | 8.1 | 8.2 | 8.1667 | 0.70696 | SDS-Chlorination pH | --- | 8.2 | 8.1 | 8.2 | 8.1667 | 0.70696
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 24.1 | 24.06 | 24 | 24.0533 | 0.20925 | SDS-Incubation time | hours | 24.1 | 24.06 | 24 | 24.0533 | 0.20925
|  |  |  | Estimated full-scale run time, tLCT (days) | 96.7029 | [5 empty] | SDS-TOX | mg Cl- /L | 370 | 365 | 370 | 368.3333 | 0.78373 | SDS-TOX | mg Cl- /L | 370 | 365 | 370 | 368.3333 | 0.78373
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 2.1378 | [5 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
|  |  |  | Estimated RSSCT run time, tSCT (days) | 10.3364 | [5 empty] | SDS-BDCM | mg/L | 3 | 3.4 | 3 | 3.1333 | 7.3704 | SDS-BDCM | mg/L | 3 | 3.4 | 3 | 3.1333 | 7.3704
|  |  |  | RSSCT bed length, lSC (cm) | 26.3496 | [5 empty] | SDS-DBCM | mg/L | 28 | 30 | 28 | 28.6667 | 4.028 | SDS-DBCM | mg/L | 28 | 30 | 28 | 28.6667 | 4.028
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 174.3499 | [5 empty] | SDS-CHBr3 | mg/L | 160 | 150 | 170 | 160 | 6.25 | SDS-CHBr3 | mg/L | 160 | 150 | 170 | 160 | 6.25
|  |  |  | Mass GAC required, mSC (g) | 12.5204 | [5 empty] | SDS-THM4 | mg/L | 191 | 183.4 | 201 | 191.8 | 4.6023 | SDS-THM4 | mg/L | 191 | 183.4 | 201 | 191.8 | 4.6023
[11 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-MCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-DCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [33 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-TCAA* | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 5.1 | 4.2 | 3.8 | 4.3667 | 15.2481 | SDS-MBAA* | mg/L | 5.1 | 4.2 | 3.8 | 4.3667 | 15.2481
[11 empty] | SDS-DBAA* | mg/L | 28 | 28 | 30 | 28.6667 | 4.028 | SDS-DBAA* | mg/L | 28 | 28 | 30 | 28.6667 | 4.028
[11 empty] | SDS-BCAA* | mg/L | 4.7 | 5.1 | 4.7 | 4.8333 | 4.7781 | SDS-BCAA* | mg/L | 4.7 | 5.1 | 4.7 | 4.8333 | 4.7781
[11 empty] | SDS-TBAA | mg/L | 30 | 29 | 35 | 31.3333 | 10.2592 | SDS-TBAA | mg/L | 30 | 29 | 35 | 31.3333 | 10.2592
[11 empty] | SDS-CDBAA | mg/L | 7.5 | 8.1 | 7.9 | 7.8333 | 3.9001 | SDS-CDBAA | mg/L | 7.5 | 8.1 | 7.9 | 7.8333 | 3.9001
[11 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | BMRL | BMRL |  | SDS-DCBAA | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 33.1 | 32.2 | 33.8 | 33.0333 | 2.4281 | SDS-HAA5 | mg/L | 33.1 | 32.2 | 33.8 | 33.0333 | 2.4281
[11 empty] | SDS-HAA6 | mg/L | 37.8 | 37.3 | 38.5 | 37.8667 | 1.5918 | SDS-HAA6 | mg/L | 37.8 | 37.3 | 38.5 | 37.8667 | 1.5918
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
** Temperature, and SDS temperature are measured values
Note on N10: Reviewer M.H. (8/26/99): Per consultant: A 0.2-m in-line filter was incorporated for all RSSCT studies to minimize headloss formation and to render sample collection reasonable. High and frequent headloss formation were experienced in a previous study, eventhough the carbon fines were minimized with the rinsing process. No head-loss problems were experienced following this change.
Note on AG33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.
Note on BP33: Reviewer M.H. (8/26/99): Consultant indicated that duplicate samples for all quarters were actually taken sequentially and not mixed. Therefore, all duplicate samples were moved from Group D to Group C.