## Sheet1. 1st Pilot Study
FIELD-SET 1: RESULTS FROM 1st PILOT-SCALE STUDY (FILE: gacpilot.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Pilot-Scale GAC Design Parameters |  |  |  | Field 1-3: Pretreatment Used Prior To GAC1 |  |  | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors1 | [14 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [15 empty] | Field 1-4: Influent Water Quality For The 10- And 20-Minute, Pilot-Scale GAC Contactors (continued) | [9 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-5: Effluent Water Quality For The 10-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor1 | [16 empty] | Field 1-6: Effluent Water Quality For The 20-Minute, Pilot-Scale GAC Contactor (continued) | [18 empty] | Field 1-7: GAC Cost Parameters
|  | Input Design Parameters |  | US Standard Mesh Sizes |  |  |  |  | Group A, 15 influent samples per run | [40 empty] | Group B, 15 effluent samples per run | [35 empty] | Group C, 15 effluent samples per run
PWS Name | City of Columbus, DPU | Carbon manufacturer | Calgon | US standard | Opening | Process | Description | Scale | Sample | Was sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | OH2500411 | Carbon trade name | F300 | mesh size | (mm) | Coagulation | 59.2 mg/L Aluminum Sulfate | Full-Scale | ID | duplicated? | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 5
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminous | 4 | 4.75 | Flocculation | 2-Stage | Full-Scale |  | Y/N | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Pilot GAC influent TOC (mg/L) | 2.3 | 6 | 3.35 | Sedimentation | Conventional | Full-Scale | START | --- | 1998-02-16 | 9:00 | 0 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-02-16 | 9:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | START | --- | 1998-02-16 | 9:00 | 0 | 0 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | Overhead & Profit Factor (% of construction costs) | 20
Official ICR Contact Person |  | Inner diameter of the pilot GAC column, D (mm) | 75 | 8 | 2.36 | Coagulation | 227 mg/L CaO | Full-Scale | A1 | N | 1998-02-17 | 14:00 | 29 | 87 | 174 | 7.61 | 0.06 | 70 | 11 | 134 | 64 | 0.07 | 30 | 1.91 | 0.032 | 1.6754 | 3.7 | 3.2 | 2.4 | 11 | NA | 48 | 135 | 24.8 | 10.7 | 4.5 | BMRL | 40 | BMRL | 12.1 | 8.1 | 1.3 | 1 | 4.4 | NA | NA | NA | 22.5 | 26.9 | B1 | N | 1998-02-17 | 14:00 | 29 | 174 | 8.11 | 0.11 | 11 | BMRL | BMRL | BMRL | #VALUE! | 2 | 0.2 | 1.8 | 11 | NA | 48 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1.7 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | C1 | N | 1998-02-17 | 14:00 | 29 | 87 | 9.22 | 0.06 | 7 | 0.06 | BMRL | BMRL | #VALUE! | 1.2 | 0.7 | 0.5 | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Special Sitework Factor (% of construction costs) | 5
Mailing Address |  | Manufacturer reported dry bed density, r (kg/m3) | 500 | 10 | 2 | Flocculation | 2-Stage | Full-Scale | Avg-A2 | Y | 1998-03-02 | 9:30 | 336.5 | 1009.5 | 2019 | 9.09 | 0.06 | 53 | 10 | 118 | NA | 0.07 | BMRL | 2.505 | 0.0505 | 2.016 | 3 | 0.35 | 2.65 | 11 | 9.11 | 48 | 181.5 | 52.5 | 8.5 | 1.4 | BMRL | 62.4 | 2.6 | 21.2 | 10.4 | BMRL | BMRL | 3.2 | NA | NA | NA | 34.2 | 37.4 | B2 | N | 1998-02-24 | 15:55 | 198.9167 | 1193.5 | 7.32 | 0.053 | 11 | 0.06 | 0.56 | BMRL | #VALUE! | 3 | 1 | 2 | 9 | 8.4 | 48 | 26.2 | 2.7 | 2.2 | 1.6 | BMRL | 6.5 | BMRL | 1 | BMRL | BMRL | BMRL | B | NA | NA | NA | 1 | 1 | Avg-C2 | Y | 1998-03-02 | 9:30 | 336.5 | 1009.5 | 7.1 | 0.044 | 10 | 0.06 | BMRL | BMRL | #VALUE! | 3 | 1.55 | 1.45 | 11 | 7.38 | 48 | BMRL | BMRL | B | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Construction Contingencies (% of construction costs) | 15
|  | Pilot GAC mesh size, upper (US standard mesh) | 8 | 12 | 1.68 | Sedimentation | Conventional | Full-Scale | A3 | N | 1998-03-09 | 9:30 | 504.5 | 1513.5 | 3027 | 6.69 | 0.046 | 56 | 11 | 114 | 82 | 0.05 | BMRL | 2.37 | 0.046 | 1.9409 | 3.5 | 0.6 | 2.9 | 11 | 7.13 | 49 | 192 | 26.3 | 7.1 | 1.1 | BMRL | 34.5 | 2.2 | 14 | 18.1 | BMRL | BMRL | 3.2 | NA | NA | NA | 34.3 | 37.5 | Avg-B3 | Y | 1998-03-02 | 16:30 | 343.5 | 2061 | 7.37 | 0.066 | 10 | 0.06 | 0.785 | 0.0125 | 1.5924 | 3 | 1.3 | 1.7 | 11 | 7.7 | 48 | 57 | 6.85 | 4.1 | 1.9 | BMRL | 12.85 | BMRL | 3.7 | 3 | BMRL | BMRL | 1.55 | NA | NA | NA | 6.7 | 8.25 | C3 | N | 1998-03-09 | 9:30 | 504.5 | 1513.5 | 6.85 | 0.163 | 11 | BMRL | BMRL | BMRL | #VALUE! | 2.5 | 1.6 | 0.9 | 11 | 7.48 | 49 | BMRL | BMRL | B | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | Engineering Fee Factor (% of construction costs) | 20
Phone Number |  | Pilot GAC mesh size, lower (US standard mesh) | 30 | 16 | 1.18 | Recarbonation | CO2 tp pH = 9.4 | Full-Scale | A4 | N | 1998-03-19 | 11:00 | 746 | 2238 | 4476 | 7.4 | 0.061 | 50 | 10 | 110 | 88 | 0.06 | 21 | 2.6 | 0.049 | 1.8846 | 3.5 | 1 | 2.5 | 9.5 | 8.5 | 49 | 112 | 49.7 | 9.1 | 1.4 | BMRL | 60.2 | 2.2 | 15.7 | 13.5 | 1 | BMRL | 2.7 | NA | NA | NA | 32.4 | 35.1 | B4 | N | 1998-03-04 | 14:45 | 389.75 | 2338.5 | 7.71 | 0.068 | 10.5 | 0.06 | 0.81 | 0.013001 | 1.6051 | 2.5 | NR | #VALUE! | 11 | 7.23 | 48 | 46 | 8.9 | 5.1 | 2.2 | BMRL | 16.2 | BMRL | 4.4 | 2.3 | BMRL | BMRL | 1.8 | NA | NA | NA | 6.7 | 8.5 | C4 | N | 1998-03-19 | 11:00 | 746 | 2238 | 7.33 | 0.06 | 10 | 0.06 | BMRL | BMRL | #VALUE! | 2.5 | 1.1 | 1.4 | 9.5 | 8.57 | 49 | BMRL | 4.6 | 1.4 | 1.5 | BMRL | 7.5 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Flow rate, Q (L/hr) | 21.6 | 20 | 0.85 | Recarbonation | CO2 to pH = 7.0-8.0 | Pilot-Scale | A5 | N | 1998-03-26 | 13:00 | 916 | 2748 | 5496 | 7.44 | 0.058 | 55 | 9.5 | 110 | 96 | 0.12 | NA | 2.54 | 0.05 | 1.9685 | 3.5 | 0.7 | 2.8 | 11.5 | 8.56 | 46 | 196 | 47.9 | 7.7 | BMRL | BMRL | 55.6 | 3.2 | 19 | 14.4 | BMRL | BMRL | 2.2 | NA | NA | NA | 36.6 | 38.8 | B5 | N | 1998-03-09 | 9:30 | 504.5 | 3027 | 6.7 | 0.072 | 11 | BMRL | 0.9 | 0.011 | 1.2222 | 3 | 0.6 | 2.4 | 11 | 7.39 | 49 | 93 | 4.1 | 3.1 | 1.6 | BMRL | 8.8 | BMRL | 2.7 | 1.9 | BMRL | BMRL | 1.6 | NA | NA | NA | 4.6 | 6.2 | C5 | N | 1998-03-26 | 13:00 | 916 | 2748 | 7.52 | 0.073 | 9.5 | 0.11 | 0.53 | BMRL | #VALUE! | 3 | 1.1 | 1.9 | 11.58 | 8.59 | 46 | BMRL | 2.9 | 2.4 | 2.1 | BMRL | 7.4 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1.1 | NA | NA | NA | 1.7 | 2.8 | 1998 Producers Price Index (PPI base year 1967 = 100) | 130.9
E-Mail Address (optional) |  |  |  | 30 | 0.6 | Filtration | 20 in Anthracite over 10 in Sand Granular Media | Pilot-Scale | A6 | N | 1998-04-01 | 10:00 | 1057 | 3171 | 6342 | 8.58 | 0.051 | 50 | 15 | 110 | 86 | 0.06 | BMRL | 2.53 | 0.05 | 1.9763 | 3.5 | 0.9 | 2.6 | 16 | 8.52 | 48 | 219 | 58.6 | 9.9 | 1.3 | BMRL | 69.8 | 3.3 | 22.8 | 14.3 | BMRL | BMRL | 3 | NA | NA | NA | 40.4 | 43.4 | B6 | N | 1998-03-19 | 11:00 | 746 | 4476 | 7.24 | 0.063 | 10 | 0.06 | 1.3 | 0.02 | 1.5385 | 3 | 0.2 | 2.8 | 9.5 | 7.45 | 49 | 99 | 15.6 | 6.8 | 2.3 | BMRL | 24.7 | BMRL | 6.4 | 4.1 | BMRL | BMRL | 2.6 | NA | NA | NA | 10.5 | 13.1 | C6 | N | 1998-04-01 | 10:00 | 1057 | 3171 | 7.36 | 0.113 | 15 | BMRL | BMRL | BMRL | #VALUE! | 2.5 | 1.8 | 0.7 | 16 | 8.56 | 48 | 32 | 3 | 2.9 | 2.9 | BMRL | 8.8 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1.2 | NA | NA | NA | 1.7 | 2.9 | Labor Rate + Fringe ($/work-hour) | 40
|  | Estimated Run Length |  | 40 | 0.425 |  |  |  | Avg-A7 | Y | 1998-04-07 | 10:00 | 1201 | 3603 | 7206 | 7.21 | 0.0715 | 51.5 | 15.5 | 112 | 80 | BMRL | BMRL | 2.505 | 0.046 | 1.8363 | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | B7 | N | 1998-03-21 | 11:00 | 794 | 4764 | 7.74 | 0.063 | 9.5 | 0.06 | 1.35 | 0.022 | 1.6296 | 3 | 1.2 | 1.8 | 8.5 | 8.57 | 45 | 85 | 18.4 | 6.5 | 2.1 | BMRL | 27 | BMRL | 7.3 | 4.2 | BMRL | BMRL | 2.9 | NA | NA | NA | 11.5 | 14.4 | Avg-C7 | Y | 1998-04-07 | 10:00 | 1201 | 3603 | 7.56 | 0.0395 | 15.5 | BMRL | 0.615 | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Labor Overhead Factor (% of labor) | 20
Technical ICR Contact Person |  | Bed volumes to 50% TOC breakthrough, BV50 | 7348.7512 | 50 | 0.3 |  |  |  | A8 | N | 1998-04-20 | 13:00 | 1516 | 4548 | 9096 | 7.1 | 0.12 | 43 | 15.5 | 106 | 76 | BMRL | BMRL | 2.41 | 0.037 | 1.5353 | 3.5 | 1.1 | 2.4 | 15.5 | 8.41 | 48 | 173 | 41.8 | 10.4 | 2 | BMRL | 54.2 | 3.2 | 16.8 | 12.6 | BMRL | BMRL | 2.8 | NA | NA | NA | 32.6 | 35.4 | B8 | N | 1998-03-23 | 11:00 | 842 | 5052 | 7.67 | 0.076 | 9 | 0.12 | 1.44 | 0.023 | 1.5972 | 3.1 | 1 | 2.1 | 9 | 8.57 | 45 | 77 | 14.6 | 6.9 | 2.8 | BMRL | 24.3 | BMRL | 6.4 | 4 | BMRL | BMRL | 2.7 | NA | NA | NA | 10.4 | 13.1 | C8 | N | 1998-04-20 | 13:00 | 1516 | 4548 | 6.87 | 0.24 | 15.5 | BMRL | 0.55 | BMRL | #VALUE! | 2.8 | 1.8 | 1 | 15.5 | 8.06 | 48 | BMRL | 1.5 | 1.8 | 2.7 | BMRL | 6 | BMRL | 1.4 | BMRL | BMRL | BMRL | 1 | NA | NA | NA | 1.4 | 2.4 | Electric Rate ($/kW-h) | 0.045
Mailing Address |  | Estimated run length, BVT (= 2 x BV50) | 14697.5025 | 60 | 0.25 |  |  |  | A9 | N | 1998-04-27 | 13:00 | 1684 | 5052 | 10104 | 7.01 | 0.114 | 47 | 16 | 96 | 78 | BMRL | BMRL | 2.44 | 0.036 | 1.4754 | 3.5 | 1.1 | 2.4 | 16 | 8.3 | 48 | 168 | 36.2 | 8.7 | BMRL | BMRL | 44.9 | 3.1 | 18.3 | 14.8 | BMRL | BMRL | 3.2 | NA | NA | NA | 36.2 | 39.4 | B9 | N | 1998-03-26 | 13:00 | 916 | 5496 | 7.63 | 0.062 | 9.5 | 0.12 | 1.52 | 0.024 | 1.5789 | 3 | 0.7 | 2.3 | 11.5 | 8.61 | 46 | 92 | 20.8 | 6.7 | 1.6 | BMRL | 29.1 | BMRL | 8.6 | 5.7 | BMRL | BMRL | 2 | NA | NA | NA | 14.3 | 16.3 | C9 | N | 1998-04-27 | 13:00 | 1684 | 5052 | 7.13 | 0.051 | 16 | BMRL | 0.56 | BMRL | #VALUE! | 2 | 1.4 | 0.6 | 16 | 8.3 | 48 | 26 | 1.1 | 2 | 1.5 | BMRL | 4.6 | BMRL | 1.7 | BMRL | BMRL | BMRL | 1.4 | NA | NA | NA | 1.7 | 3.1 | Fuel Oil Rate ($/gal) | NA
|  |  |  | 70 | 0.21 |  |  |  | A10 | N | 1998-05-04 | 9:30 | 1848.5 | 5545.5 | 11091 | 6.97 | 0.085 | 59 | 17 | 116 | 92 | BMRL | BMRL | 2.27 | 0.042 | 1.8502 | 3 | 1.1 | 1.9 | 18.5 | 7.37 | 48.5 | 185 | 35.2 | 10.6 | 1 | BMRL | 46.8 | 2.4 | 15.9 | 14.8 | BMRL | BMRL | BMRL | NA | NA | NA | 33.1 | 33.1 | B10 | N | 1998-03-28 | 13:00 | 964 | 5784 | 7.62 | 0.079 | 11.5 | 0.07 | 1.36 | 0.02 | 1.4706 | 2.9 | 1 | 1.9 | 14 | 8.43 | 46 | 85 | 20.6 | 6.9 | 1.9 | BMRL | 29.4 | BMRL | 9.7 | 7.4 | BMRL | BMRL | 2.3 | NA | NA | NA | 17.1 | 19.4 | C10 | N | 1998-05-04 | 9:30 | 1848.5 | 5545.5 | 7.07 | 0.031 | 17 | BMRL | 0.58 | BMRL | #VALUE! | 1.5 | 0.9 | 0.6 | 18.5 | 8.1 | 48.5 | 30 | 1.4 | 3 | 3 | BMRL | 7.4 | BMRL | 1.4 | BMRL | BMRL | 1 | 1.7 | NA | NA | NA | 2.4 | 4.1 | Natural Gas Rate ($/ft3) | 0.0036
Phone Number |  | General Pilot Design Parameters |  | 80 | 0.18 |  |  |  | A11 | N | 1998-05-11 | 9:30 | 2016.5 | 6049.5 | 12099 | 6.94 | 0.1 | 52 | 20 | 108 | 76 | BMRL | BMRL | 2.25 | 0.04 | 1.7778 | 3 | 0.9 | 2.1 | 20 | 7.85 | 47.5 | 178 | 43 | 12.4 | 1.5 | BMRL | 56.9 | 2.7 | 18.4 | 13.6 | 1.2 | BMRL | 4 | NA | NA | NA | 35.9 | 39.9 | B11 | N | 1998-03-30 | 12:30 | 1011.5 | 6069 | 7.39 | 0.071 | 14 | NA | 1.41 | 0.02 | 1.4184 | 2.5 | 0.8 | 1.7 | 15 | 7.78 | 46 | 95 | 22.6 | 8.3 | 2.4 | BMRL | 33.3 | BMRL | 8.6 | 5.5 | BMRL | BMRL | 2.4 | NA | NA | NA | 14.1 | 16.5 | C11 | N | 1998-05-11 | 9:30 | 2016.5 | 6049.5 | 7.2 | 0.103 | 20 | BMRL | 0.71 | BMRL | #VALUE! | 1.5 | 0.9 | 0.6 | 20 | NA | 47.5 | 70 | 3.1 | 4.2 | 4.3 | BMRL | 11.6 | BMRL | 2 | BMRL | BMRL | 1.1 | 2 | NA | NA | NA | 3.1 | 5.1 | Current Process Water Rate ($/1000 gal) | 0.203
FAX Number |  | Carbon particle diameter, d (mm) | 1.48 | [5 empty] | A12 | N | 1998-05-18 | 9:30 | 2184.5 | 6553.5 | 13107 | 7.75 | 0.075 | 32 | 24.4 | 106 | 64 | BMRL | BMRL | 2.82 | 0.05 | 1.773 | 3 | 0.6 | 2.4 | 25 | 7.4 | 48 | NR | 72.7 | 13.2 | 1 | BMRL | 86.9 | 6.7 | 30.5 | 18.1 | 1 | BMRL | 4.7 | NA | NA | NA | 56.3 | 61 | B12 | N | 1998-04-01 | 10:00 | 1057 | 6342 | 7.5 | 0.073 | 15 | BMRL | 1.53 | 0.022 | 1.4379 | 3 | 1.3 | 1.7 | 16 | 8.48 | 48 | 117 | 23.4 | 8.3 | 2.2 | BMRL | 33.9 | BMRL | 10.1 | 6.6 | BMRL | BMRL | 2.8 | NA | NA | NA | 16.7 | 19.5 | C12 | N | 1998-05-18 | 9:30 | 2184.5 | 6553.5 | 7.25 | 0.069 | 24.4 | BMRL | 0.94 | 0.01 | 1.0638 | 2 | 0.5 | 1.5 | 25 | 7.35 | 48 | 131 | 9.6 | 6.6 | 3.7 | BMRL | 19.9 | 2.6 | 5.3 | 1.9 | BMRL | 1.2 | 3.2 | NA | NA | NA | 11 | 14.2 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Column cross-sectional area, A (m2) | 0.0044179 | [5 empty] | A13 | N | 1998-05-27 | 10:00 | 2401 | 7203 | 14406 | 7.01 | 0.127 | 50 | 23 | 116 | 108 | BMRL | 28 | 2.6 | 0.047 | 1.8077 | 3 | 0.5 | 2.5 | 26 | 8.23 | 48 | 230 | 60.3 | 17.3 | 3.4 | BMRL | 81 | 3.7 | 28 | 15.2 | BMRL | BMRL | 6.6 | NA | NA | NA | 46.9 | 53.5 | Avg-B13 | Y | 1998-04-04 | 12:00 | 1131 | 6786 | 7.66 | 0.058 | 17 | BMRL | 1.395 | NA | #VALUE! | 2 | 0.7 | 1.3 | 15 | 8.465 | 45 | 80.5 | 21.85 | 7.7 | 2.3 | BMRL | 31.85 | BMRL | 8.1 | 4.45 | BMRL | BMRL | 2.5 | NA | NA | NA | 12.55 | 15.05 | C13 | N | 1998-05-27 | 10:00 | 2401 | 7203 | 7.03 | 0.067 | 23 | BMRL | 0.61 | BMRL | #VALUE! | 2 | 0.9 | 1.1 | 26 | 8.18 | 48 | 47 | 6.2 | 7.5 | 7.2 | 1.3 | 22.2 | BMRL | 3.2 | BMRL | BMRL | 1.7 | 3.2 | NA | NA | NA | 4.9 | 8.1
|  | Hydraulic loading rate1, v (m/hr) | 4.8892 |  |  | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | A14 | N | 1998-06-01 | 12:00 | 2523 | 7569 | 15138 | 7.35 | 0.132 | 50 | 24 | 118 | 104 | BMRL | 30 | 2.48 | 0.048 | 1.9355 | 3 | 0.6 | 2.4 | 24.7 | 8.42 | 47.5 | 209 | 59.3 | 17 | 5.3 | BMRL | 81.6 | 2.1 | 24.6 | 11.3 | BMRL | BMRL | 6.6 | NA | NA | NA | 38 | 44.6 | B14 | N | 1998-04-07 | 10:00 | 1201 | 7206 | 7.41 | 0.053 | 15.5 | BMRL | 1.51 | 0.022 | 1.457 | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | C14 | N | 1998-06-01 | 12:00 | 2523 | 7569 | 7.11 | 0.077 | 24 | BMRL | 1.13 | 0.015 | 1.3274 | 2 | 0.9 | 1.1 | 24.6 | 8.32 | 47.5 | 68 | 9.8 | 9.4 | 7.7 | 1.5 | 28.4 | BMRL | 4.9 | 1.5 | BMRL | 2.1 | 4.3 | NA | NA | NA | 8.5 | 12.8
Plant Name | Dublin Road Water Plant | 1: If v is not in the range from 5 to 15 m/hr (2 to 6 gpm/ft2) then either Q or D must be adjusted. |  |  |  | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Avg-A15 | Y | 1998-06-08 | 10:00 | 2689 | 8067 | 16134 | 6.53 | 0.0895 | 53.5 | 22 | 114 | 89 | BMRL | 30.5 | 2.38 | 0.0425 | 1.7857 | 3 | 1 | 2 | 23 | 7.715 | 49 | 211.5 | 39.45 | 15.3 | 4.7 | BMRL | 59.45 | 2.8 | 21.25 | 14.65 | BMRL | BMRL | 6.45 | NA | NA | NA | 38.7 | 45.15 | Avg-B15 | Y | 1998-04-20 | 13:00 | 1516 | 9096 | 6.79 | 0.1305 | 15.5 | BMRL | 1.39 | 0.014 | 1.0072 | 2.5 | 1.2 | 1.3 | 15.5 | 7.915 | 48 | 78 | 14.95 | 6.8 | 2.65 | BMRL | 24.4 | BMRL | 6.75 | 4.7 | BMRL | BMRL | 2.35 | NA | NA | NA | 11.45 | 13.8 | Avg-C15 | Y | 1998-06-08 | 10:00 | 2689 | 8067 | 6.65 | 0.1105 | 22 | BMRL | 0.975 | 0.0115 | 1.1795 | 2 | 1.25 | 0.75 | 23 | 7.925 | 49 | 63.5 | 6.45 | 7.35 | 7.25 | 1.15 | 22.2 | BMRL | 4 | 1.4 | BMRL | 1.9 | 3.6 | NA | NA | NA | 7.3 | 10.9
Treatment Plant Category | CS/SOFT |  |  |  |  | is to list the pretreatment processes used in this particular pilot GAC run. |  |  | A16 | N | 1998-06-15 | 10:00 | 2857 | 8571 | 17142 | 6.66 | 0.083 | 55 | 23.6 | 120 | 92 | BMRL | BMRL | 2.37 | 0.039 | 1.6456 | 3 | 0.5 | 2.5 | 24 | 8.12 | 48 | 189 | 27.6 | 13.5 | 4.4 | BMRL | 45.5 | 2.4 | 17.1 | 11.4 | BMRL | BMRL | 5.8 | NA | NA | NA | 30.9 | 36.7 | B16 | N | 1998-04-22 | 11:30 | 1562.5 | 9375 | 7.15 | 0.086 | 15.5 | BMRL | 1.39 | 0.019 | 1.3669 | 2 | 1 | 1 | NA | NA | NA | 68 | 14.8 | 6.9 | 1.8 | BMRL | 23.5 | 2.2 | 8.3 | 4.7 | BMRL | BMRL | 2.6 | NA | NA | NA | 15.2 | 17.8 | C16 | N | 1998-06-15 | 10:00 | 2857 | 8571 | 6.72 | 0.078 | 23.6 | BMRL | 1.24 | 0.009 | 0.72581 | 2 | 1.1 | 0.9 | 24 | 7.94 | 48 | 74 | 9.6 | 9.1 | 7.8 | 1.1 | 27.6 | BMRL | 5.8 | 1.9 | BMRL | 2.4 | 4.8 | NA | NA | NA | 10.1 | 14.9
Process Train Name | Coagulation/Sedimentation/Softening | 10-Minute EBCT Run | [6 empty] | A17 | N | 1998-06-22 | 10:00 | 3025 | 9075 | 18150 | 7.21 | 0.072 | 45 | 23.5 | 112 | 96 | BMRL | BMRL | 1.81 | 0.04 | 2.2099 | 3 | 1 | 2 | 25 | 8.15 | 48 | 188 | 53.3 | 12.1 | 2.9 | BMRL | 68.3 | 3 | 24.4 | 13.9 | BMRL | BMRL | 4.8 | NA | NA | NA | 41.3 | 46.1 | B17 | N | 1998-04-27 | 13:00 | 1684 | 10104 | 7.02 | 0.085 | 16 | BMRL | 1.48 | 0.015 | 1.0135 | 2.5 | 1.3 | 1.2 | 16 | 8.3 | 48 | 75 | 14.6 | 6.9 | 1.4 | BMRL | 22.9 | BMRL | 8.3 | 4.8 | BMRL | BMRL | 2.8 | NA | NA | NA | 13.1 | 15.9 | C17 | N | 1998-06-22 | 10:00 | 3025 | 9075 | 7.19 | 0.063 | 23.5 | BMRL | 1.15 | 0.019 | 1.6522 | 2 | 1.1 | 0.9 | 25 | 8.22 | 48 | 67 | 14.6 | 8.2 | 5 | BMRL | 27.8 | BMRL | 8.2 | 3.2 | BMRL | 1.2 | 4.2 | NA | NA | NA | 12.6 | 16.8
ICR Treatment Plant Identification Number | 528 | Empty bed contact time, EBCT (min) | 10 | [5 empty] | A18 | N | 1998-06-29 | 9:30 | 3192.5 | 9577.5 | 19155 | 7.25 | 0.24 | 57 | 27 | 122 | 110 | BMRL | BMRL | 2.32 | 0.043 | 1.8534 | 3 | 0.7 | 2.3 | 26 | 8.06 | 48 | 221 | 69.3 | 14.8 | 2.7 | BMRL | 86.8 | 3.7 | 26.5 | 12.4 | BMRL | BMRL | 5.6 | NA | NA | NA | 42.6 | 48.2 | B18 | N | 1998-05-04 | 9:30 | 1848.5 | 11091 | 6.95 | 0.05 | 17 | BMRL | 1.37 | 0.012 | 0.87591 | 2 | 1.2 | 0.8 | 18.5 | 8.06 | 48.5 | NR | 15 | 8.2 | 2.6 | BMRL | 25.8 | BMRL | 7.2 | 4.6 | BMRL | BMRL | B | NA | NA | NA | 11.8 | 11.8 | C18 | N | 1998-06-29 | 9:30 | 3192.5 | 9577.5 | 7.46 | 0.135 | 27 | BMRL | 1.49 | 0.019 | 1.2752 | 2 | 1 | 1 | 26 | 7.93 | 48 | 84 | 16.6 | 9.5 | 5.5 | BMRL | 31.6 | BMRL | 8.1 | 2.9 | BMRL | 1.5 | 4.6 | NA | NA | NA | 12.5 | 17.1
PWSID Number of Plant (if assigned) | Not assigned | Estimated run time, t (days) | 102.066 | [5 empty] | A19 | N | 1998-07-06 | 10:00 | 3361 | 10083 | 20166 | 6.76 | 0.066 | 50 | 26 | 110 | 98 | BMRL | BMRL | 1.85 | 0.041 | 2.2162 | 3 | 0.7 | 2.3 | 26 | 7.86 | 47.5 | 187 | 55.4 | 15.1 | 3.3 | BMRL | 73.8 | 3.5 | 23 | 12.6 | BMRL | BMRL | 5.8 | NA | NA | NA | 39.1 | 44.9 | B19 | N | 1998-05-27 | 10:00 | 2401 | 14406 | 6.96 | 0.079 | 23 | BMRL | 1.67 | 0.024 | 1.4371 | 2 | 0.5 | 1.5 | 26 | 8.2 | 48 | 133 | 15.9 | 7.6 | 3 | BMRL | 26.5 | BMRL | 12 | 5.6 | BMRL | 1 | 4.9 | NA | NA | NA | 18.6 | 23.5 | C19 | N | 1998-07-06 | 10:00 | 3361 | 10083 | 7.21 | 0.079 | 26 | BMRL | 0.92 | 0.016 | 1.7391 | 2 | 1 | 1 | 26 | 8.05 | 47.5 | 56 | 12.5 | 9 | 6.4 | BMRL | 27.9 | BMRL | 5.8 | 1.9 | BMRL | 1.6 | 4.1 | NA | NA | NA | 9.3 | 13.4
Historical Minimum Water Temperature (oC) | 1.7 | Pilot column bed length, l (m) | 0.81487 | [5 empty] | A20 | N | 1998-07-13 | 10:00 | 3529 | 10587 | 21174 | 6.96 | 0.13 | 47 | 25.3 | 114 | 102 | BMRL | BMRL | 2.34 | 0.045 | 1.9231 | 3 | 0.6 | 2.4 | 26.5 | 6.89 | 48 | 214 | 44.8 | 12.4 | 2 | BMRL | 59.2 | 4.1 | 25.1 | 23.8 | BMRL | BMRL | 5.5 | NA | NA | NA | 53 | 58.5 | B20 | N | 1998-06-08 | 10:00 | 2689 | 16134 | 6.55 | 0.174 | 22 | BMRL | 1.62 | 0.023 | 1.4198 | 2 | 0.8 | 1.2 | 23 | 7.73 | 49 | 115 | 19.4 | 11.8 | 6.2 | BMRL | 37.4 | 2 | 11.2 | 5.9 | BMRL | 1.6 | 5.8 | NA | NA | NA | 20.7 | 26.5 | C20 | N | 1998-07-13 | 10:00 | 3529 | 10587 | 7.25 | 0.137 | 25.2 | BMRL | 1.12 | 0.01 | 0.89286 | 2 | 1 | 1 | 26.5 | 7.13 | 48 | 49 | 7.9 | 6.5 | 4.5 | BMRL | 18.9 | BMRL | 5.3 | 2.6 | BMRL | 1.4 | 4 | NA | NA | NA | 9.3 | 13.3
Historical Average Water Temperature (oC) | 12.8 | Mass GAC required, m (kg) | 1.8 | [5 empty] | A21 | N | 1998-07-20 | 9:30 | 3696.5 | 11089.5 | 22179 | 6.6 | 0.15 | 50 | 25.7 | 116 | 106 | BMRL | 22 | 2.35 | 0.05 | 2.1277 | 3 | 0.6 | 2.4 | 26.6 | 6.91 | 47.5 | 195 | 37.1 | 15.7 | 4.3 | BMRL | 57.1 | 3.7 | 22 | 19.2 | BMRL | BMRL | 6.7 | NA | NA | NA | 44.9 | 51.6 | B21 | N | 1998-06-22 | 10:00 | 3025 | 18150 | 7.39 | 0.112 | 23.5 | BMRL | 1.68 | 0.033 | 1.9643 | 2 | 0.7 | 1.3 | 25 | 8 | 48 | 106 | 30.4 | 10.4 | 3.8 | BMRL | 44.6 | 2.7 | 13.9 | 6.4 | BMRL | BMRL | 4.3 | NA | NA | NA | 23 | 27.3 | C21 | N | 1998-07-20 | 9:30 | 3696.5 | 11089.5 | 6.57 | 0.146 | 25.7 | BMRL | 1.06 | 0.015 | 1.4151 | 1.5 | 0.6 | 0.9 | 26.6 | 7.26 | 47.5 | 50 | 7 | 8.1 | 7.3 | 1.2 | 23.6 | BMRL | 4.7 | 2.1 | BMRL | 2.1 | 4.6 | NA | NA | NA | 8.9 | 13.5
State Approved Plant Capacity (MGD) | 65 | [7 empty] | A22 | N | 1998-07-27 | 9:00 | 3864 | 11592 | 23184 | 7.68 | 0.104 | 51 | 26.5 | 120 | 96 | BMRL | 24 | 2.59 | 0.053 | 2.0463 | 3 | 0.5 | 2.5 | 26.3 | 7.24 | 48 | 233 | 51.3 | 16.4 | 3.3 | BMRL | 71 | 4.6 | 23.8 | 19.7 | BMRL | BMRL | 5.4 | NA | NA | NA | 48.1 | 53.5 | B22 | N | 1998-07-06 | 10:00 | 3361 | 20166 | 7.5 | 0.06 | 26 | BMRL | 1.64 | 0.03 | 1.8293 | 2 | 0.6 | 1.4 | 26 | 7.9 | 47.5 | 105 | 27.3 | 13.6 | 5.8 | BMRL | 46.7 | 2 | 12.7 | 5 | BMRL | 1.2 | 5.4 | NA | NA | NA | 20.9 | 26.3 | C22 | N | 1998-07-27 | 9:00 | 3864 | 11592 | 7.84 | 0.077 | 25 | BMRL | 1.24 | 0.017 | 1.371 | 1.5 | 0.5 | 1 | 26.1 | 7.46 | 48 | 72 | 11.5 | 9.4 | 6.4 | BMRL | 27.3 | BMRL | 6.3 | 3 | BMRL | 1.5 | 4.3 | NA | NA | NA | 10.8 | 15.1
|  | 20-Minute EBCT Run | [6 empty] | A23 | N | 1998-08-10 | 9:00 | 4200 | 12600 | 25200 | 6.45 | 0.06 | 55 | 26.5 | 120 | 94 | BMRL | 24 | 2.88 | 0.053 | 1.8403 | 3 | 0.4 | 2.6 | 25 | 7.55 | 48 | 218 | 40.5 | 15.9 | 3.4 | BMRL | 59.8 | 3.5 | 25.2 | 22.6 | BMRL | BMRL | 7 | NA | NA | NA | 51.3 | 58.3 | B23 | N | 1998-07-20 | 9:30 | 3696.5 | 22179 | 6.54 | 0.081 | 25.7 | BMRL | 1.71 | 0.027 | 1.5789 | 2 | 0.5 | 1.5 | 26.6 | 7.23 | 47.5 | 113 | 18.8 | 12.7 | 6.4 | BMRL | 37.9 | 2.6 | 11.8 | 7.6 | BMRL | 1.4 | 6.1 | NA | NA | NA | 23.4 | 29.5 | C23 | N | 1998-08-10 | 9:00 | 4200 | 12600 | 7 | 0.053 | 26.3 | BMRL | 1.47 | 0.014 | 0.95238 | 1.5 | 0.5 | 1 | 25 | 6.97 | 48 | 66 | 7.8 | 8.3 | 6.6 | BMRL | 22.7 | BMRL | 5.6 | 2.5 | BMRL | 1.8 | 4.7 | NA | NA | NA | 9.9 | 14.6
|  | Empty bed contact time, EBCT (min) | 20 | [5 empty] | A24 | N | 1998-08-26 | 15:00 | 4590 | 13770 | 27540 | 6.92 | 0.112 | 58 | 26.1 | 118 | 84 | BMRL | 33 | 3.04 | 0.059 | 1.9408 | 3 | 0.5 | 2.5 | 27 | 7.45 | 49 | 274 | 72.6 | 22.7 | 6.4 | BMRL | 101.7 | 4.5 | 28.2 | 20.8 | BMRL | 1.1 | 8.1 | NA | NA | NA | 54.6 | 62.7 | B24 | N | 1998-08-10 | 9:00 | 4200 | 25200 | 6.45 | 0.053 | 26.2 | BMRL | 2.11 | 0.03 | 1.4218 | 2 | 0.4 | 1.6 | 25.1 | 7.36 | 48 | 137 | 22.2 | 13.5 | 5.5 | BMRL | 41.2 | 2.1 | 13.1 | 9.1 | BMRL | 1 | 5.7 | NA | NA | NA | 25.3 | 31 | C24 | N | 1998-08-26 | 15:00 | 4590 | 13770 | 7.59 | 0.069 | 26.2 | BMRL | 1.88 | 0.025 | 1.3298 | 1.5 | 0.5 | 1 | 27 | 7.5 | 49 | 116 | 10.9 | 9.7 | 7.9 | BMRL | 28.5 | BMRL | 9.1 | 5 | BMRL | 2.7 | 7 | NA | NA | NA | 16.8 | 23.8
|  | Estimated run time, t (days) | 204.132 | [5 empty] | A26 | N | 1998-09-22 | 9:00 | 5232 | 15696 | 31392 | 6.96 | 0.063 | 54 | 25.7 | 122 | 86 | BMRL | 37 | 3.21 | 0.057 | 1.7757 | 3 | 0.3 | 2.7 | 24.9 | 7.89 | 47.5 | 286 | 62.2 | 22.7 | 6.5 | BMRL | 91.4 | 4.1 | 27.6 | 18.3 | BMRL | 1.2 | 8.6 | NA | NA | NA | 51.2 | 59.8 | [36 empty] | C26 | N | 1998-09-22 | 9:00 | 5232 | 15696 | 7.35 | 0.111 | 25.6 | BMRL | 2.19 | 0.022 | 1.0046 | 2 | 0.5 | 1.5 | 24.9 | 8.04 | 47.5 | 111 | 22 | 16.1 | 10.9 | BMRL | 49 | 2.4 | 12.1 | 5.4 | BMRL | 3.1 | 7.9 | NA | NA | NA | 23 | 30.9
|  | Pilot column bed length, l (m) | 1.6297 | [5 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
|  | Mass GAC required, m (kg) | 3.6 | [5 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[9 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [40 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [35 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
[9 empty] | Group D, 3 duplicate influent samples per run | [40 empty] | Group D, 3 duplicate effluent samples per run | [35 empty] | Group D, 3 duplicate effluent samples per run
[9 empty] | Sample | Sample | Sampling | Sampling | Operation | Bed | Bed | pH | Turbidity | Alkalinity | Temp. | Total | Calcium | Ammonia | Bromide | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Turbidity | Temp. | Ammonia | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
[9 empty] | ID | Type | date | time | time | volumes | volumes |  |  |  |  | Hardness | Hardness | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [7 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
[11 empty] | MM/DD/YY | hh:mm | hh.hh | ( 20 minute) | ( 10 minute) | --- | ntu | mg/L as CaCO3 | oC | mg/L as CaCO3 | mg/L as CaCO3 | mg NH3-N / L | mg/L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | ntu | oC | mg NH3-N / L | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
[9 empty] | A2 | Primary | 1998-03-02 | 9:30 | 336.5 | 1009.5 | 2019 | 9.09 | 0.06 | 53 | 10 | 118 | NA | 0.05 | BMRL | 2.6 | 0.049 | 1.8846 | 3 | 0.7 | 2.3 | 11 | 9.3 | 48 | 175 | 53.3 | 8.4 | 1.4 | BMRL | 63.1 | 2.6 | 21.2 | 10.4 | BMRL | BMRL | 3.2 | NA | NA | NA | 34.2 | 37.4 | B3 | Primary | 1998-03-02 | 16:00 | 343 | 2058 | 7.37 | 0.066 | 10 | 0.07 | 0.8 | 0.013 | 1.625 | 3 | 1.5 | 1.5 | 11 | 7.8 | 48 | 55 | 6.9 | 4.2 | 1.9 | BMRL | 13 | BMRL | 3.8 | 3.2 | BMRL | BMRL | 1.6 | NA | NA | NA | 7 | 8.6 | C2 | Primary | 1998-03-02 |  | 327 | 981 | 7.1 | 0.044 | 10 | 0.06 | BMRL | BMRL | #VALUE! | 3 | 1.1 | 1.9 | 11 | 7.3 | 48 | BMRL | BMRL | BMRL | BMRL | BMRL | 0 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | D-A2 | Duplicate | 1998-03-02 | 9:30 | 336.5 | 1009.5 | 2019 | 9.09 | 0.06 | 53 | 10 | 118 | NA | 0.09 | BMRL | 2.41 | 0.052 | 2.1577 | 3 | 0 | 3 | 11 | 8.92 | 48 | 188 | 51.7 | 8.6 | 1.4 | BMRL | 61.7 | NA | NA | NA | NA | NA | NA | NA | NA | NA | 0 | 0 | D-B3 | Duplicate | 1998-03-02 | 16:00 | 343 | 2058 | 7.37 | 0.066 | 10 | 0.05 | 0.77 | 0.012 | 1.5584 | 3 | 1.1 | 1.9 | 11 | 7.6 | 48 | 59 | 6.8 | 4 | 1.9 | BMRL | 12.7 | BMRL | 3.6 | 2.8 | BMRL | BMRL | 1.5 | NA | NA | NA | 6.4 | 7.9 | D-C2 | Duplicate | 1998-03-02 |  | 327 | 981 | 7.1 | 0.044 | 10 | 0.06 | BMRL | BMRL | #VALUE! | 3 | 2 | 1 | 11 | 7.46 | 48 | BMRL | 1.1 | BMRL | BMRL | BMRL | 1.1 | BMRL | BMRL | BMRL | BMRL | BMRL | BMRL | NA | NA | NA | 0 | 0
[9 empty] | Avg-A2 | Average | --- | --- | --- | --- | --- | 9.09 | 0.06 | 53 | 10 | 118 | #DIV/0! | 0.07 | #DIV/0! | 2.505 | 0.0505 | 2.0211 | 3 | 0.35 | 2.65 | 11 | 9.11 | 48 | 181.5 | 52.5 | 8.5 | 1.4 | #DIV/0! | 62.4 | 2.6 | 21.2 | 10.4 | #DIV/0! | #DIV/0! | 3.2 | #DIV/0! | #DIV/0! | #DIV/0! | 17.1 | 18.7 | Avg-B3 | Average | --- | --- | --- | --- | 7.37 | 0.066 | 10 | 0.06 | 0.785 | 0.0125 | 1.5917 | 3 | 1.3 | 1.7 | 11 | 7.7 | 48 | 57 | 6.85 | 4.1 | 1.9 | #DIV/0! | 12.85 | #DIV/0! | 3.7 | 3 | #DIV/0! | #DIV/0! | 1.55 | #DIV/0! | #DIV/0! | #DIV/0! | 6.7 | 8.25 | Avg-C2 | Average | --- | --- | --- | --- | 7.1 | 0.044 | 10 | 0.06 | #DIV/0! | #DIV/0! | #VALUE! | 3 | 1.55 | 1.45 | 11 | 7.38 | 48 | #DIV/0! | 1.1 | #DIV/0! | #DIV/0! | #DIV/0! | 0.55 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0
[9 empty] | RPD-A2 | RPD | --- | --- | --- | --- | --- | 0 | 0 | 0 | 0 | 0 | #VALUE! | 57.1429 | #VALUE! | 7.5848 | 5.9406 | 13.5102 | 0 | 200 | 26.4151 | 0 | 4.1712 | 0 | 7.1625 | 3.0476 | 2.3529 | 0 | #VALUE! | 2.2436 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | 200 | RPD-B3 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 33.3333 | 3.8217 | 8 | 4.1815 | 0 | 30.7692 | 23.5294 | 0 | 2.5974 | 0 | 7.0175 | 1.4599 | 4.878 | 0 | #VALUE! | 2.3346 | #VALUE! | 5.4054 | 13.3333 | #VALUE! | #VALUE! | 6.4516 | #VALUE! | #VALUE! | #VALUE! | 8.9552 | 8.4848 | RPD-C2 | RPD | --- | --- | --- | --- | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 58.0645 | 62.069 | 0 | 2.168 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 200 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #DIV/0! | #DIV/0!
[9 empty] | A7 | Primary | 1998-04-07 | 12:00 | 1203 | 3609 | 7218 | 7.2 | 0.071 | 52 | 15.5 | 112 | 80 | BMRL | BMRL | 2.55 | 0.046 | 1.8039 | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | B13 | Primary | 1998-04-04 | 12:00 | 1131 | 6786 | 7.66 | 0.057 | 17 | BMRL | 1.39 | NA | #VALUE! | 2 | 0.7 | 1.3 | 15 | 8.6 | 45 | 76 | 21.8 | 7.7 | 2.4 | BMRL | 31.9 | BMRL | 8.6 | 4.5 | BMRL | BMRL | 2.6 | NA | NA | NA | 13.1 | 15.7 | C7 | Primary | 1998-04-07 | 12:00 | 1203 | 3609 | 7.55 | 0.04 | 15.5 | BMRL | 0.57 | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[9 empty] | D-A7 | Duplicate | 1998-04-07 | 12:00 | 1203 | 3609 | 7218 | 7.22 | 0.072 | 51 | 15.5 | 112 | 80 | BMRL | BMRL | 2.46 | 0.047 | 1.9106 | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | D-B13 | Duplicate | 1998-04-04 | 12:00 | 1131 | 6786 | 7.66 | 0.059 | 17 | BMRL | 1.4 | NA | #VALUE! | 2 | 0.7 | 1.3 | 15 | 8.33 | 45 | 85 | 21.9 | 7.7 | 2.2 | BMRL | 31.8 | BMRL | 7.6 | 4.4 | BMRL | BMRL | 2.4 | NA | NA | NA | 12 | 14.4 | D-C7 | Duplicate | 1998-04-07 | 12:00 | 1203 | 3609 | 7.57 | 0.039 | 15.5 | BMRL | 0.66 | BMRL | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR
[9 empty] | Avg-A7 | Average | --- | --- | --- | --- | --- | 7.21 | 0.0715 | 51.5 | 15.5 | 112 | 80 | #DIV/0! | #DIV/0! | 2.505 | 0.0465 | 1.8572 | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Avg-B13 | Average | --- | --- | --- | --- | 7.66 | 0.058 | 17 | #DIV/0! | 1.395 | #DIV/0! | #VALUE! | 2 | 0.7 | 1.3 | 15 | 8.465 | 45 | 80.5 | 21.85 | 7.7 | 2.3 | #DIV/0! | 31.85 | #DIV/0! | 8.1 | 4.45 | #DIV/0! | #DIV/0! | 2.5 | #DIV/0! | #DIV/0! | #DIV/0! | 12.55 | 15.05 | Avg-C7 | Average | --- | --- | --- | --- | 7.56 | 0.0395 | 15.5 | #DIV/0! | 0.615 | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[9 empty] | RPD-A7 | RPD | --- | --- | --- | --- | --- | 0.27739 | 1.3986 | 1.9417 | 0 | 0 | 0 | #VALUE! | #VALUE! | 3.5928 | 2.1505 | 5.7422 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | RPD-B13 | RPD | --- | --- | --- | --- | 0 | 3.4483 | 0 | #VALUE! | 0.71685 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 | 3.1896 | 0 | 11.1801 | 0.45767 | 0 | 8.6957 | #VALUE! | 0.31397 | #VALUE! | 12.3457 | 2.2472 | #VALUE! | #VALUE! | 8 | #VALUE! | #VALUE! | #VALUE! | 8.7649 | 8.6379 | RPD-C7 | RPD | --- | --- | --- | --- | 0.26455 | 2.5316 | 0 | #VALUE! | 14.6341 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | A15 | Primary | 1998-06-08 | 1:00 | 2680 | 8040 | 16080 | 6.53 | 0.086 | 54 | 22 | 114 | 88 | 0 | 31 | 2.36 | 0.044 | 1.8644 | 3 | 1 | 2 | 23 | 7.72 | 49 | 217 | 40 | 15.4 | 4.7 | BMRL | 60.1 | 3 | 21.2 | 14.7 | BMRL | BMRL | 6.5 | NA | NA | NA | 38.9 | 45.4 | B15 | Primary | 1998-04-20 | 1:00 | 1504 | 9024 | 6.77 | 0.144 | 15.5 | BMRL | 1.34 | 0.014 | 1.0448 | 2.5 | 1.2 | 1.3 | 15.5 | 7.94 | 48 | 78 | 17.5 | 7.4 | 3.6 | BMRL | 28.5 | BMRL | 6.8 | 4.8 | BMRL | BMRL | 2.4 | NA | NA | NA | 11.6 | 14 | C15 | Primary | 1998-06-08 | 1:00 | 2680 | 8040 | 6.67 | 0.111 | 22 | BMRL | 0.91 | 0.012 | 1.3187 | 2 | 1.3 | 0.7 | 23 | 7.93 | 49 | 62 | 6.5 | 7.4 | 7.3 | 1.1 | 22.3 | BMRL | 4.1 | 1.5 | BMRL | 1.9 | 3.6 | NA | NA | NA | 7.5 | 11.1
[9 empty] | D-A15 | Duplicate | 1998-06-08 | 1:00 | 2680 | 8040 | 16080 | 6.53 | 0.093 | 53 | 22 | 114 | 90 | 0 | 30 | 2.4 | 0.041 | 1.7083 | 3 | 1 | 2 | 23 | 7.71 | 49 | 206 | 38.9 | 15.2 | 4.7 | BMRL | 58.8 | 2.6 | 21.3 | 14.6 | BMRL | 1 | 6.4 | NA | NA | NA | 39.5 | 45.9 | D-B15 | Duplicate | 1998-04-20 | 1:00 | 1504 | 9024 | 6.81 | 0.117 | 15.5 | BMRL | 1.44 | 0.014 | 0.97222 | 2.5 | 1.2 | 1.3 | 15.5 | 7.89 | 48 | 78 | 12.4 | 6.2 | 1.7 | BMRL | 20.3 | BMRL | 6.7 | 4.6 | BMRL | BMRL | 2.3 | NA | NA | NA | 11.3 | 13.6 | D-C15 | Duplicate | 1998-06-08 | 1:00 | 2680 | 8040 | 6.63 | 0.11 | 22 | BMRL | 1.04 | 0.011 | 1.0577 | 2 | 1.2 | 0.8 | 23 | 7.92 | 49 | 65 | 6.4 | 7.3 | 7.2 | 1.2 | 22.1 | BMRL | 3.9 | 1.3 | BMRL | 1.9 | 3.6 | NA | NA | NA | 7.1 | 10.7
[9 empty] | Avg-A15 | Average | --- | --- | --- | --- | --- | 6.53 | 0.0895 | 53.5 | 22 | 114 | 89 | 0 | 30.5 | 2.38 | 0.0425 | 1.7864 | 3 | 1 | 2 | 23 | 7.715 | 49 | 211.5 | 39.45 | 15.3 | 4.7 | #DIV/0! | 59.45 | 2.8 | 21.25 | 14.65 | #DIV/0! | 1 | 6.45 | #DIV/0! | #DIV/0! | #DIV/0! | 39.2 | 45.65 | Avg-B15 | Average | --- | --- | --- | --- | 6.79 | 0.1305 | 15.5 | #DIV/0! | 1.39 | 0.014 | 1.0085 | 2.5 | 1.2 | 1.3 | 15.5 | 7.915 | 48 | 78 | 14.95 | 6.8 | 2.65 | #DIV/0! | 24.4 | #DIV/0! | 6.75 | 4.7 | #DIV/0! | #DIV/0! | 2.35 | #DIV/0! | #DIV/0! | #DIV/0! | 11.45 | 13.8 | Avg-C15 | Average | --- | --- | --- | --- | 6.65 | 0.1105 | 22 | #DIV/0! | 0.975 | 0.0115 | 1.1882 | 2 | 1.25 | 0.75 | 23 | 7.925 | 49 | 63.5 | 6.45 | 7.35 | 7.25 | 1.15 | 22.2 | #DIV/0! | 4 | 1.4 | #DIV/0! | 1.9 | 3.6 | #DIV/0! | #DIV/0! | #DIV/0! | 7.3 | 10.9
[9 empty] | RPD-A15 | RPD | --- | --- | --- | --- | --- | 0 | 7.8212 | 1.8692 | 0 | 0 | 2.2472 | #DIV/0! | 3.2787 | 1.6807 | 7.0588 | 8.7369 | 0 | 0 | 0 | 0 | 0.12962 | 0 | 5.2009 | 2.7883 | 1.3072 | 0 | #VALUE! | 2.1867 | 14.2857 | 0.47059 | 0.68259 | #VALUE! | #VALUE! | 1.5504 | #VALUE! | #VALUE! | #VALUE! | 1.5306 | 1.0953 | RPD-B15 | RPD | --- | --- | --- | --- | 0.5891 | 20.6897 | 0 | #VALUE! | 7.1942 | 0 | 7.1942 | 0 | 0 | 0 | 0 | 0.63171 | 0 | 0 | 34.1137 | 17.6471 | 71.6981 | #VALUE! | 33.6066 | #VALUE! | 1.4815 | 4.2553 | #VALUE! | #VALUE! | 4.2553 | #VALUE! | #VALUE! | #VALUE! | 2.6201 | 2.8986 | RPD-C15 | RPD | --- | --- | --- | --- | 0.6015 | 0.90498 | 0 | #VALUE! | 13.3333 | 8.6957 | 21.9653 | 0 | 8 | 13.3333 | 0 | 0.12618 | 0 | 4.7244 | 1.5504 | 1.3605 | 1.3793 | 8.6957 | 0.9009 | #VALUE! | 5 | 14.2857 | #VALUE! | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 5.4795 | 3.6697
[9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [9 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [18 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [16 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [9 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [18 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [16 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on AC25: Reviewer D.S. (11/8/99): Per Consultant: "Data verified."
Note on AC27: Reviewer D.S. (11/8/99): Per Consultant: "Data verified."
Note on BX53: Reviewer M.H. (11/13/99): Per Consultant: "Entries in cells BX50 and BZ50 verified."
Note on BZ53: Reviewer M.H. (11/13/99): Per Consultant: "Entries in cells BX50 and BZ50 verified."
Note on DH20: Reviewer M.H. (11/13/99): Per consultant, "Numbers in spreadsheet are correct as reported."