## 7450. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.26687 | [45 empty] | Recovery during sample collection (decimal) | 0.67 | [10 empty] | Recovery during sample collection (decimal) | 0.88 | [7 empty] | Recovery during sample collection (decimal) | 0.52 | [7 empty] | Recovery during sample collection (decimal) | 0.32 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-05-19 | 1998-05-27 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.04 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.39 | [7 empty] | Feed flow rate during sample collection (mL/min) | 8.85 | [7 empty] | Feed flow rate during sample collection (mL/min) | 14.33 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 7:30 | 12:45 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 481 | [10 empty] | Influent flow rate during sample collection (mL/min) | 481 | [7 empty] | Influent flow rate during sample collection (mL/min) | 481 | [7 empty] | Influent flow rate during sample collection (mL/min) | 481 | [6 empty] | SDS-THM4F, ug/L | 190.6 | 190.6 | 190.6 | 190.6 | SDS-THM4F, ug/L | 190.6 | 190.6 | 190.6 | 190.6 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 33.45 | 42 | 27.5 | 24.2 | SDS-THM4p, ug/L | 33.45 | 42 | 27.5 | 24.2 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.54 | 8.42 | 8.48 | 1.4151 | 1998-05-26 | 14:15 | 0 | 24 | 78 | 79 | 481 | 3.94 | 2.11 | 6.05 | 0.36767 | 0.65124 | 78.5041 | 8.9928 | 9.1538 | 0 | 0 | 0 | 0 | 78.5 | 0.11661 | 1998-05-27 | 12:45 | 0 | 24 | 80 | 80 | 481 | 4.92 | 1.35 |  | 6.27 | 0.36767 | 0.78469 | 75.7145 | 11.2296 | 11.4306 | 341.5696 | 249.7248 | 340.6301 | 0.91375 | 79.0862 | 0.14453 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 90.85 | 90.85 | 90.85 | 90.85 | SDS-HAA5F, ug/L | 90.85 | 90.85 | 90.85 | 90.85 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24.5 | 24.25 | 2.0619 | 1998-05-26 | 14:35 | 0.33333 | 24 | 78 | 78 | 481 | 4.24 | 1.96 | 6.2 | 0.36767 | 0.68387 | 76.5806 | 9.6776 | 9.8507 | 0 | 0 | 0 | 0 | 78 | 0.12629 | 1998-05-27 | 13:15 | 0.5 | 24 | 80 | 80 | 481 | 5.09 | 2.48 |  | 7.57 | 0.36767 | 0.67239 | 62.5403 | 11.6177 | 11.8255 | 328.9982 | 240.5107 | 328.0618 | 0.88019 | 79.1198 | 0.14946 | 8.26 | 8.16 | 8.26 |  | 269 | 260 |  | #VALUE! |  |  |  | 0.024 | 0.182 | 0.28 | 0.51544 | -84.0855 | 87.027 | 0.51284 | 95.3202 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 7.15 | 13.2 | 5 | 4.1 | SDS-HAA5p, ug/L | 7.15 | 13.2 | 5 | 4.1 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 222 | 236 | 229 | 6.1135 | 1998-05-26 | 15:05 | 0.83333 | 24 | 79 | 79 | 481 | 4.15 | 1.87 | 6.02 | 0.36767 | 0.68937 | 78.9003 | 9.4722 | 9.6416 | 0 | 0 | 0 | 0 | 79 | 0.12205 | 1998-05-27 | 13:45 | 1 | 24 | 80 | 80 | 481 | 5.13 | 2.25 |  | 7.38 | 0.36767 | 0.69512 | 64.1762 | 11.709 | 11.9185 | 331.4768 | 242.3172 | 330.5259 | 0.88684 | 79.1132 | 0.15065 | 8.24 | 8.14 | 8.23 | 238 | 269 | 289 | 341.32 | -18.1038 | 11.6883 | 340.769 | 30.158 | 0.029 | 0.191 | 0.346 | 0.54068 | -56.2659 | 84.3243 | 0.53795 | 94.6092 | [8 empty] | Sampling date | MM/DD/YY | 1998-05-28 | 1998-05-29 | --- | --- | 1998-05-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-30 | 1998-05-30 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-31 | 1998-05-31 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-06-01 | 1998-06-01 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 537.5 | 537.5 | 537.5 | 537.5 | SDS-TOXF, ug Cl- /L | 537.5 | 537.5 | 537.5 | 537.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 271 | 268 | 269.5 | 1.1132 | 1998-05-26 | 15:35 | 1.3333 | 24 | 79 | 79 | 481 | 4.38 | 1.84 | 6.22 | 0.36767 | 0.70418 | 76.3312 | 9.9971 | 10.176 | 0 | 0 | 0 | 0 | 79 | 0.12881 | 1998-05-27 | 14:15 | 1.5 | 24 | 80 | 80 | 481 | 5.33 | 2.15 |  | 7.48 | 0.36767 | 0.71257 | 63.3048 | 12.1654 | 12.3831 | 333.4253 | 243.714 | 332.4312 | 0.89214 | 79.1079 | 0.15653 | 8.25 | 8.17 | 8.25 |  | 268 | 283 |  | #VALUE! |  |  |  | 0.031 | 0.187 | 0.384 | 0.56678 | -47.5981 | 83.2432 | 0.56381 | 94.5017 | [8 empty] | Sampling time | hh:mm | 10:30 | 8:00 | --- | --- | 10:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 21:00 | 21:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:30 | 20:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 79 | 105 | 67 | 49 | SDS-TOXp, ug Cl- /L | 79 | 105 | 67 | 49 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 252 | 330 | 291 | 26.8041 | 1998-05-26 | 16:00 | 1.75 | 24 | 79 | 79 | 481 | 4.5 | 1.9 | 6.4 | 0.36767 | 0.70312 | 74.1562 | 10.271 | 10.4548 | 0 | 0 | 0 | 0 | 79 | 0.13234 | 1998-05-27 | 14:45 | 2 | 24 | 80 | 80 | 481 | 5 | 2.01 |  | 7.01 | 0.36767 | 0.71327 | 67.6163 | 11.4122 | 11.6164 | 333.4629 | 243.7869 | 332.5307 | 0.8921 | 79.1079 | 0.14684 | 8.29 | 8.19 | 8.29 | 239 | 270 | 297 | 345.3706 | -16.2864 | 11.3173 | 344.8178 | 30.688 | 0.034 | 0.185 | 0.442 | 0.56062 | -26.8375 | 81.6216 | 0.55788 | 93.9056 | [8 empty] | Operation time | hh.hh | 21.75 | 43.25 | --- | --- | 21.75 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80.25 | 80.25 | --- | --- | --- | --- | --- | Operation time | hh.hh | 103.75 | 103.75 | --- | --- | --- | --- | --- | Cumulative time | hr | 119.25 | 119.25 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 5.345 | 5.345 | 5.345 | 5.345 | SDS-CDF, mg/L | 5.345 | 5.345 | 5.345 | 5.345 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 236 | 260 | 248 | 9.6774 | 1998-05-26 | 16:30 | 2.25 | 24 | 78 | 79 | 481 | 4.53 | 1.89 | 6.42 | 0.36767 | 0.70561 | 73.9221 | 10.3395 | 10.5245 | 0 | 0 | 0 | 0 | 78.5 | 0.13407 | 1998-05-27 | 15:15 | 2.5 | 24 | 80 | 80 | 481 | 5 | 1.88 |  | 6.88 | 0.36767 | 0.72674 | 68.9128 | 11.4122 | 11.6164 | 334.9651 | 244.8851 | 334.0287 | 0.89612 | 79.1039 | 0.14685 | 8.27 | 8.16 | 8.27 | 237 | 269 | 300 | 355.9362 | -18.6454 | 12.0594 | 355.318 | 33.2992 | 0.034 | 0.193 | 0.474 | 0.5866 | -23.7544 | 81.6216 | 0.58372 | 94.1753 | [8 empty] | pH | --- | 8.22 | 8.26 | 8.24 | 0.48544 | 8.42 | --- | --- | --- | --- | --- | pH | --- | 8.36 | 8.45 | --- | --- | --- | --- | --- | pH | --- | 8.32 | 8.41 | --- | --- | --- | --- | --- | pH | --- | 8.5 | 8.37 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.55 | 1.15 | 0.5 | 0.57 | SDS-CDp, mg/L | 0.55 | 1.15 | 0.5 | 0.57 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 15.1667 | 62.5992 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.112 | 0.142 | 0.127 | 23.622 | 1998-05-26 | 17:00 | 2.75 | 24 | 79 | 80 | 481 | 4.6 | 1.92 | 6.52 | 0.36767 | 0.70552 | 72.773 | 10.4993 | 10.6871 | 0 | 0 | 0 | 0 | 79.5 | 0.13443 | 1998-05-27 | 16:15 | 3.5 | 24 | 80 | 80 | 481 | 5.09 | 1.73 |  | 6.82 | 0.36767 | 0.74633 | 69.5279 | 11.6177 | 11.8255 | 337.1846 | 246.4952 | 336.2249 | 0.90209 | 79.0979 | 0.14951 | 8.31 | 8.19 | 8.3 | 241 | 269 | 300 | 353.3526 | -17.7842 | 10.5751 | 352.7581 | 31.6812 | 0.035 | 0.185 | 0.534 | 0.62633 | -17.2902 | 81.0811 | 0.6232 | 94.3838 | [8 empty] | Temperature | oC | 24.5 | 24.5 | 24.5 | 0 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | Temperature | oC | 24.5 | 24.5 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.1 | 6.1 | 6.1 | 6.1 | TOCF, mg/L | 6.1 | 6.1 | 6.1 | 6.1 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 38.5 | 85.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | 0.05 | 0.05 | #VALUE! | 1998-05-27 | 8:00 | 17.75 | 24 | 80 | 81 | 481 | 3.79 | 1.35 | 5.14 | 0.36767 | 0.73735 | 92.5798 | 8.6505 | 8.8053 | 0 | 0 | 0 | 0 | 80.5 | 0.10938 | 1998-05-27 | 16:45 | 4 | 24 | 80 | 80 | 481 | 5.11 | 3.45 |  | 8.56 | 0.36767 | 0.59696 | 55.1916 | 11.6633 | 11.872 | 321.049 | 234.6969 | 320.1316 | 0.85893 | 79.1411 | 0.15001 | [27 empty] | Alkalinity | mg/L as CaCO3 | 175 | 180 | 177.5 | 2.8169 | 236 | 333.5606 | -41.3392 | 22.4891 | 332.7954 | 46.6639 | Alkalinity | mg/L as CaCO3 | 226 | 248 | 251 | -1.2097 | 1.31 | 250.8767 | 9.9159 | Alkalinity | mg/L as CaCO3 | 188 | 238 | 273.4167 | -14.881 | 17.9039 | 273.0081 | 31.1376 | Alkalinity | mg/L as CaCO3 | 186 | 227 | 249.2353 | -9.7953 | 18.7773 | 248.9339 | 25.2814 | TOCp, mg/L | 0.95 | 1.3 | 0.8 | 0.7 | TOCp, mg/L | 0.95 | 1.3 | 0.8 | 0.7 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 57.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6 | 6.2 | 6.1 | 3.2787 | 1998-05-27 | 9:00 | 18.75 | 24 | 80 | 81 | 481 | 4.89 | 1.4 | 6.29 | 0.36767 | 0.77742 | 75.4706 | 11.1612 | 11.3609 | 0 | 0 | 0 | 0 | 80.5 | 0.14113 | 1998-05-27 | 17:05 | 4.3333 | 24 | 80 | 80 | 481 | 4.87 | 2.75 |  | 7.62 | 0.36767 | 0.63911 | 62.1234 | 11.1155 | 11.3144 | 325.4189 | 237.9236 | 324.533 | 0.87052 | 79.1295 | 0.14299 | 8.31 | 8.2 | 8.3 | 239 | 266 | 285 | 323.5127 | -13.5132 | 11.3173 | 323.0849 | 26.0256 | 0.033 | 0.191 | 0.486 | 0.45418 | 6.5477 | 82.1622 | 0.45205 | 92.6999 | [8 empty] | Total dissolved solids | mg/L | 244 | 227 | 235.5 | 7.2187 | 279 | 338.5303 | -21.337 | 12.616 | 338.0251 | 30.3306 | Total dissolved solids | mg/L | 247 | 416 | 434.5 | -4.4471 | 8.3488 | 433.5755 | 43.0318 | Total dissolved solids | mg/L | 228 | 280 | 314.4583 | -12.3065 | 15.3989 | 314.0447 | 27.3989 | Total dissolved solids | mg/L | 226 | 272 | 289.9706 | -6.6068 | 16.141 | 289.6657 | 21.979 | UV254 F, cm-1 | 0.185 | 0.185 | 0.185 | 0.185 | UV254 F, cm-1 | 0.185 | 0.185 | 0.185 | 0.185 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 8.5 | 55.9325 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.185 | 0.185 | 0.185 | 0 | 1998-05-27 | 9:30 | 19.25 | 24 | 80 | 81 | 481 | 4.86 | 1.07 | 5.93 | 0.36767 | 0.81956 | 80.113 | 11.0927 | 11.2912 | 0 | 0 | 0 | 0 | 80.5 | 0.14026 | 1998-05-28 | 8:00 | 19.25 | 24 | 80 | 80 | 481 | 4.86 | 1.59 |  | 6.45 | 0.36767 | 0.75349 | 73.5736 | 11.0927 | 11.2912 | 337.9679 | 247.1 | 337.0498 | 0.90409 | 79.0959 | 0.14275 | [27 empty] | Total hardness | mg/L as CaCO3 | 196 | 224 | 210 | 13.3333 | 300 | 455.4545 | -51.8182 | 27.8351 | 454.2511 | 53.7701 | Total hardness | mg/L as CaCO3 | 260 | 359 | 518.3333 | -44.3825 | 10.6529 | 517.0596 | 49.7157 | Total hardness | mg/L as CaCO3 | 244 | 304 | 341.9167 | -12.4726 | 16.1512 | 341.4483 | 28.5397 | Total hardness | mg/L as CaCO3 | 222 | 282 | 323.4706 | -14.7059 | 23.7113 | 322.9869 | 31.2666 | UV254 p, cm-1 | 0.02 | 0.027 | 0.014 | 0.011 | UV254 p, cm-1 | 0.02 | 0.027 | 0.014 | 0.011 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.0833 | 2.9839 | 3.0336 | 3.2787 | 1998-05-27 | 10:00 | 19.75 | 24 | 80 | 81 | 481 | 5 | 3.15 | 8.15 | 0.36767 | 0.6135 | 58.0184 | 11.4122 | 11.6164 | 0 | 0 | 0 | 0 | 80.5 | 0.1443 | 1998-05-28 | 8:30 | 19.75 | 24 | 80 | 80 | 481 | 4.8 | 2.99 |  | 7.79 | 0.36767 | 0.61617 | 60.7458 | 10.9557 | 11.1518 | 323.007 | 236.1696 | 322.1405 | 0.86404 | 79.136 | 0.14092 | [27 empty] | Calcium hardness | mg/L as CaCO3 | 180 | 176 | 178 | 2.2472 | 271 | 390.1212 | -43.9562 | 28.2258 | 389.0812 | 54.2512 | Calcium hardness | mg/L as CaCO3 | 238 | 305 | 321.3333 | -5.3552 | 4.0323 | 320.9225 | 25.8388 | Calcium hardness | mg/L as CaCO3 | 204 | 273 | 295.6667 | -8.3028 | 17.7419 | 295.2282 | 30.9009 | Calcium hardness | mg/L as CaCO3 | 196 | 260 | 272.4706 | -4.7964 | 20.9677 | 272.1061 | 27.9693 | BromideF, ug/L | 62 | 62 | 62 | 62 | BromideF, ug/L | 62 | 62 | 62 | 62 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 63 | 61 | 62 | 3.2258 | 1998-05-27 | 10:20 | 20.0833 | 24 | 80 | 81 | 481 | 4.87 | 2.53 | 7.4 | 0.36767 | 0.65811 | 64 | 11.1155 | 11.3144 | 0 | 0 | 0 | 0 | 80.5 | 0.14055 | 1998-05-28 | 9:15 | 20.5 | 24 | 79 | 80 | 481 | 4.73 | 2.51 |  | 7.24 | 0.36767 | 0.65331 | 65.4365 | 10.796 | 10.9891 | 326.9119 | 239.0341 | 326.0477 | 0.87446 | 78.6255 | 0.13977 | 8.3 | 8.24 | 8.3 | 239 | 268 | 296 | 326.9761 | -10.4649 | 11.3173 | 326.5435 | 26.8091 | 0.022 | 0.191 | 0.558 | 0.49217 | 11.798 | 88.1081 | 0.48986 | 95.5089 | [8 empty] | Turbidity | ntu | 0.141 | 0.105 | 0.123 | 29.2683 | 0.196 | 0.13512 | 31.0606 | 3.1496 | 0.13506 | 8.9306 | Turbidity | ntu | 0.169 | 0.409 | -0.181 | 144.2543 | -33.0709 | -0.17927 | 194.2689 | Turbidity | ntu | 0.105 | 0.205 | 0.15083 | 26.4228 | 17.3228 | 0.15061 | 30.2854 | Turbidity | ntu | 0.152 | 0.19 | 0.11524 | 39.3498 | -19.685 | 0.11541 | -31.7037 | Bromidep, ug/L | 60.5 | 63 | 58 | 56 | Bromidep, ug/L | 60.5 | 63 | 58 | 56 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 8 | 7 | 7.5 | 13.3333 | 1998-05-27 | 10:35 | 20.3333 | 24 | 60 | 60 | 481 | 3.5 | 1.5 | 5 | 0.36767 | 0.7 | 95.2 | 7.9886 | 8.1315 | 0 | 0 | 0 | 0 | 60 | 0.13553 | 1998-05-28 | 10:15 | 21.5 | 24 | 80 | 80 | 481 | 5.46 | 2.42 |  | 7.88 | 0.36767 | 0.69289 | 60.0406 | 12.4622 | 12.6851 | 331.2711 | 242.1216 | 330.2591 | 0.88644 | 79.1136 | 0.16034 | 8.3 | 8.2 | 8.3 | 235 | 269 | 298 | 347.3388 | -16.5567 | 12.8015 | 346.7012 | 32.2183 | 0.022 | 0.183 | 0.519 | 0.55276 | -6.5049 | 88.1081 | 0.54975 | 95.9982 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.09 | NA | -0.24333 | #VALUE! | -80 | -0.24169 | 137.2378 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 229 | 229 | 229 | 229 | AlkF, mg/L CaCO3 | 229 | 229 | 229 | 229
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.71 | 2.6 | 2.155 | 41.2993 | 1998-05-27 | 11:00 | 20.75 | 24 | 70 | 71 | 481 | 4.24 | 1.98 | 6.22 | 0.36767 | 0.68167 | 76.3312 | 9.6776 | 9.8507 | 0 | 0 | 0 | 0 | 70.5 | 0.13973 | 1998-05-28 | 10:30 | 21.75 | 24 | 80 | 80 | 481 | 4.6 | 2.32 |  | 6.92 | 0.36767 | 0.66474 | 68.5087 | 10.4993 | 10.6871 | 328.1201 | 239.9351 | 327.2767 | 0.87763 | 79.1224 | 0.13507 | [27 empty] | Total organic carbon | mg/L | 1 | 0.9 | 0.95 | 10.5263 | 16.2 | 16.5561 | -2.1979 | 84.4262 | 16.4795 | 94.2353 | Total organic carbon | mg/L | 1.3 | 38.8 | 41.3 | -6.4433 | 78.6885 | 41.1028 | 96.8372 | Total organic carbon | mg/L | 0.8 | 12 | 11.8417 | 1.3194 | 86.8852 | 11.7888 | 93.2139 | Total organic carbon | mg/L | 0.7 | 8.8 | 8.6412 | 1.8048 | 88.5246 | 8.6033 | 91.8636 | Alkp, mg/L CaCO3 | 177.5 | 226 | 188 | 186 | Alkp, mg/L CaCO3 | 177.5 | 226 | 188 | 186
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 6.29 | 4.4 | 5.345 | 35.3601 | 1998-05-27 | 11:20 | 21.0833 | 24 | 90 | 91 | 481 | 5.89 | 3 | 8.89 | 0.36767 | 0.66254 | 53.1057 | 13.4436 | 13.6842 | 0 | 0 | 0 | 0 | 90.5 | 0.15121 | 1998-05-28 | 11:15 | 22.5 | 24 | 79 | 80 | 481 | 4.6 | 2.32 |  | 6.92 | 0.36767 | 0.66474 | 68.5087 | 10.4993 | 10.6871 | 328.1201 | 239.9351 | 327.2767 | 0.87763 | 78.6224 | 0.13593 | 8.31 | 8.26 | 8.3 | 236 | 268 | 297 | 335.9224 | -13.1052 | 12.4304 | 335.4446 | 29.6456 | 0.023 | 0.188 | 0.521 | 0.50621 | 2.8394 | 87.5676 | 0.5039 | 95.4356 | [8 empty] | UV254 | cm-1 | 0.022 | 0.018 | 0.02 | 20 | 0.521 | 0.52 | 0.19194 | 89.1892 | 0.51755 | 96.1356 | UV254 | cm-1 | 0.027 | 1.242 | 1.3437 | -8.1857 | 85.4054 | 1.3372 | 97.9808 | UV254 | cm-1 | 0.014 | 0.376 | 0.37025 | 1.5293 | 92.4324 | 0.36855 | 96.2013 | UV254 | cm-1 | 0.011 | 0.269 | 0.26688 | 0.78723 | 94.0541 | 0.26566 | 95.8594 | T-HdF, mg/L CaCO3 | 291 | 291 | 291 | 291 | T-HdF, mg/L CaCO3 | 291 | 291 | 291 | 291
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | 1998-05-27 | 11:50 | 21.5833 | 24 | 80 | 80 | 481 | 5.5 | 2.3 | 7.8 | 0.36767 | 0.70513 | 60.6667 | 12.5535 | 12.7781 | 0 | 0 | 0 | 0 | 80 | 0.15973 | 1998-05-28 | 13:30 | 24.75 | 24 | 80 | 80 | 481 | 4.55 | 2.18 |  | 6.73 | 0.36767 | 0.67608 | 70.471 | 10.3851 | 10.571 | 329.3362 | 240.8312 | 328.499 | 0.88086 | 79.1191 | 0.13361 | 8.34 | 8.24 | 8.35 | 246 | 269 | 326 | 318.5482 | 2.2858 | 8.7199 | 318.205 | 22.6914 | 0.021 | 0.185 | 0.526 | 0.52729 | -0.24593 | 88.6486 | 0.5249 | 95.9992 | [8 empty] | SUVA | L/(mg*m) | 2.2 | 2 | 2.1 | 9.5238 | 3.216 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.0769 | 3.201 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.75 | 3.1333 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.5714 | 3.0568 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 210 | 260 | 244 | 222 | T-Hdp, mg/L CaCO3 | 210 | 260 | 244 | 222
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.48 | 8.58 | 8.53 | 1.1723 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 14:45 | 26 | 24 | 80 | 80 | 481 | 4.6 | 2.13 |  | 6.73 | 0.36767 | 0.68351 | 70.471 | 10.4993 | 10.6871 | 330.1474 | 241.4176 | 329.2989 | 0.88306 | 79.1169 | 0.13508 | 8.49 | 8.43 | 8.51 | 238 | 269 | 334 | 337.5282 | -1.0563 | 11.6883 | 337.0523 | 29.3878 | 0.021 | 0.188 | 0.536 | 0.53918 | -0.59299 | 88.6486 | 0.5367 | 96.0872 | [8 empty] | Bromide | mg/L | 61 | 60 | 60.5 | 1.6529 | --- | 65.0455 | --- | 2.4194 | 65.0232 | 6.9562 | Bromide | mg/L | 63 | --- | 54.6667 | --- | -1.6129 | 54.7078 | -15.1573 | Bromide | mg/L | 58 | --- | 66.3333 | --- | 6.4516 | 66.2935 | 12.5102 | Bromide | mg/L | 56 | --- | 64.8235 | --- | 9.6774 | 64.7815 | 13.5555 | Ca-HdF, mg/L CaCO3 | 248 | 248 | 248 | 248 | Ca-HdF, mg/L CaCO3 | 248 | 248 | 248 | 248
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 25 | 24 | 24.5 | 4.0816 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 15:45 | 27 | 24 | 80 | 80 | 481 | 4.67 | 2.14 |  | 6.81 | 0.36767 | 0.68576 | 69.6314 | 10.659 | 10.8498 | 330.4002 | 241.5929 | 329.5379 | 0.88376 | 79.1162 | 0.13714 | 8.13 | 8.07 | 8.13 | 239 | 269 | 304 | 336.0584 | -10.5455 | 11.3173 | 335.5872 | 28.7816 | 0.021 | 0.186 | 0.543 | 0.54289 | 0.020654 | 88.6486 | 0.54035 | 96.1137 | [8 empty] | SDS-Cl2 dose | mg/L | 2 | 2 | 2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 178 | 238 | 204 | 196 | Ca-Hdp, mg/L CaCO3 | 178 | 238 | 204 | 196
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 575 | 500 | 537.5 | 13.9535 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 16:30 | 27.75 | 24 | 80 | 80 | 481 | 4.52 | 2.12 |  | 6.64 | 0.36767 | 0.68072 | 71.4398 | 10.3167 | 10.5013 | 329.8361 | 241.2008 | 329.0031 | 0.88219 | 79.1178 | 0.13273 | 8.11 | 8.02 | 8.11 | 239 | 269 | 295 | 334.5283 | -13.3994 | 11.3173 | 334.0795 | 28.4601 | 0.021 | 0.187 | 0.55 | 0.53466 | 2.789 | 88.6486 | 0.53225 | 96.0545 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.48 | 1.42 | 1.45 | 4.1379 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.85 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.5 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.43 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 170 | 160 | 165 | 6.0606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 20:15 | 31.5 | 24 | 80 | 80 | 481 | 4.8 | 2.2 |  | 7 | 0.36767 | 0.68571 | 67.7143 | 10.9557 | 11.1518 | 330.4105 | 241.5827 | 329.5241 | 0.88385 | 79.1162 | 0.14095 | [27 empty] | SDS-Cl2 demand | mg/L | 0.52 | 0.58 | 0.55 | 10.9091 | --- | 15.0803 | --- | 89.71 | 15.0091 | 96.3355 | SDS-Cl2 demand | mg/L | 1.15 | --- | 36.1083 | --- | 78.4846 | 35.936 | 96.7999 | SDS-Cl2 demand | mg/L | 0.5 | --- | 10.5938 | --- | 90.6455 | 10.5455 | 95.2586 | SDS-Cl2 demand | mg/L | 0.57 | --- | 7.5921 | --- | 89.3358 | 7.5586 | 92.4589 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 24 | 20 | 22 | 18.1818 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 20:45 | 32 | 24 | 80 | 80 | 481 | 4.71 | 2 |  | 6.71 | 0.36767 | 0.70194 | 70.6841 | 10.7503 | 10.9427 | 332.1761 | 242.886 | 331.3017 | 0.88853 | 79.1115 | 0.13832 | [27 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 75.4693 | 79.8116 | 72.7161 | 71.274 | Qp/QT (THM4), % | 98.3773 | 104.0377 | 94.7885 | 92.9087
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 3.4 | 3.8 | 3.6 | 11.1111 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 21:15 | 32.5 | 24 | 80 | 80 | 481 | 4.53 | 2.78 |  | 7.31 | 0.36767 | 0.6197 | 64.8003 | 10.3395 | 10.5245 | 323.3475 | 236.4545 | 322.5291 | 0.86484 | 79.1352 | 0.13299 | [27 empty] | SDS-Chlorination pH | --- | 8.34 | 8.73 | 8.535 | 4.5694 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.5 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.37 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.34 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | NA | 36 | 36
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-28 | 21:45 | 33 | 24 | 80 | 80 | 481 | 5 | 2.63 |  | 7.63 | 0.36767 | 0.65531 | 62.0406 | 11.4122 | 11.6164 | 327.1535 | 239.1743 | 326.2389 | 0.87522 | 79.1248 | 0.14681 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 27.6822 | 28.8763 | 28.4232 | 29.0198 | SDS-HAA5b, ug/L | 8.5082 | NA | 9.4741 | 10.2517
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 197.4 | 183.8 | 190.6 | 7.1354 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 8:00 | 43.25 | 24 | 80 | 80 | 481 | 4.5 | 1.85 |  | 6.35 | 0.36767 | 0.70866 | 74.748 | 10.271 | 10.4548 | 332.8925 | 243.4386 | 332.0556 | 0.89035 | 79.1096 | 0.13216 | 8.32 | 8.27 | 8.35 | 246 | 270 | 308 | 326.6622 | -6.0591 | 8.7199 | 326.2848 | 24.6058 | 0.017 | 0.191 | 0.597 | 0.59365 | 0.56137 | 90.8108 | 0.59095 | 97.1233 | [8 empty] | SDS-TOX | mg Cl- /L | 74 | 84 | 79 | 12.6582 | --- | 1468.3939 | --- | 85.3023 | 1461.5816 | 94.5949 | SDS-TOX | mg Cl- /L | 105 | --- | 3709.1667 | --- | 80.4651 | 3691.3961 | 97.1555 | SDS-TOX | mg Cl- /L | 67 | --- | 1047.2083 | --- | 87.5349 | 1042.5192 | 93.5733 | SDS-TOX | mg Cl- /L | 49 | --- | 767.3824 | --- | 90.8837 | 763.958 | 93.586 | SDS-TOXb, ug Cl- /L | 191.4733 | 192.3149 | 195.3706 | 189.3263 | SDS-TOXb, ug Cl- /L | 86.4399 | NA | 91.5202 | 83.6412
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 6.2 | 4.5 | 5.35 | 31.7757 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 9:00 | 44.25 | 24 | 80 | 80 | 481 | 4.48 | 2.64 |  | 7.12 | 0.36767 | 0.62921 | 66.5562 | 10.2254 | 10.4083 | 324.3374 | 237.1851 | 323.5257 | 0.86746 | 79.1325 | 0.13153 | 8.37 | 8.27 | 8.37 | 250 | 269 | 304 | 302.5909 | 0.46352 | 7.2356 | 302.346 | 17.3133 | 0.017 | 0.19 | 0.557 | 0.47009 | 15.6031 | 90.8108 | 0.46798 | 96.3674 | [8 empty] | SDS-CHCl3 | mg/L | 8 | 8 | 8 | 0 | --- | 483.7576 | --- | 95.1515 | 481.4249 | 98.3383 | SDS-CHCl3 | mg/L | 15 | --- | 1265 | --- | 90.9091 | 1258.8368 | 98.8084 | SDS-CHCl3 | mg/L | 5.3 | --- | 338.0083 | --- | 96.7879 | 336.4167 | 98.4246 | SDS-CHCl3 | mg/L | 4.2 | --- | 240.6706 | --- | 97.4545 | 239.5434 | 98.2467 | SDS-CDb, mg/L | 1.7262 | 1.9969 | 1.8219 | 1.9417 | SDS-CDb, mg/L | 0.62781 | NA | 0.7525 | 0.90861
|  | Standard testing pH | 7 | [13 empty] | SDS-DCAA* | mg/L | 51 | 44 | 47.5 | 14.7368 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 9:30 | 44.75 | 24 | 80 | 80 | 481 | 5.2 | 2.26 |  | 7.46 | 0.36767 | 0.69705 | 63.4772 | 11.8687 | 12.0811 | 331.6967 | 242.4683 | 330.7321 | 0.88746 | 79.1125 | 0.15271 | 8.37 | 8.26 | 8.34 | 239 | 269 | 309 | 339.677 | -9.9278 | 11.3173 | 339.1328 | 29.5261 | 0.02 | 0.184 | 0.539 | 0.56465 | -4.7581 | 89.1892 | 0.5617 | 96.4394 | [8 empty] | SDS-BDCM | mg/L | 9.6 | 9.7 | 9.65 | 1.0363 | --- | 47.0742 | --- | 56.1364 | 46.8907 | 79.4202 | SDS-BDCM | mg/L | 13 | --- | 88 | --- | 40.9091 | 87.6302 | 85.1649 | SDS-BDCM | mg/L | 7.6 | --- | 37.6 | --- | 65.4545 | 37.4565 | 79.7098 | SDS-BDCM | mg/L | 6.6 | --- | 29.2471 | --- | 70 | 29.1391 | 77.35 | TOCb, mg/L | 2.2133 | 2.269 | 2.246 | 2.2512 | TOCb, mg/L | 1.0336 | NA | 1.0762 | 1.0829
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 40 | 35 | 37.5 | 13.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 10:00 | 45.25 | 24 | 80 | 80 | 481 | 4.46 | 2.72 |  | 7.18 | 0.36767 | 0.62117 | 65.9916 | 10.1797 | 10.3619 | 323.4939 | 236.571 | 322.688 | 0.8652 | 79.1348 | 0.13094 | 8.37 | 8.28 | 8.37 | 245 | 269 | 298 | 309.6728 | -3.917 | 9.0909 | 309.373 | 20.8076 | 0.017 | 0.19 | 0.518 | 0.46047 | 11.1061 | 90.8108 | 0.45841 | 96.2916 | [8 empty] | SDS-DBCM | mg/L | 11 | 12 | 11.5 | 8.6957 | --- | -12.4394 | --- | -219.4444 | -12.322 | 193.3289 | SDS-DBCM | mg/L | 11 | --- | -50.6667 | --- | -205.5556 | -50.3626 | 121.8416 | SDS-DBCM | mg/L | 10 | --- | -3.3333 | --- | -177.7778 | -3.2695 | 405.8525 | SDS-DBCM | mg/L | 9.1 | --- | 1.0118 | --- | -152.7778 | 1.0503 | -766.4033 | UV254 b, cm-1 | 0.060476 | 0.058898 | 0.060655 | 0.060983 | UV254 b, cm-1 | 0.022677 | NA | 0.022912 | 0.023339
|  | Acceptable range of operating pH values | 2-11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 10:45 | 46 | 24 | 80 | 80 | 481 | 4.6 | 2.3 |  | 6.9 | 0.36767 | 0.66667 | 68.7101 | 10.4993 | 10.6871 | 328.3271 | 240.0865 | 327.4832 | 0.87819 | 79.1218 | 0.13507 | 8.37 | 8.3 | 8.36 | 241 | 269 | 293 | 326.5 | -11.4334 | 10.5751 | 326.0912 | 26.0943 | 0.016 | 0.193 | 0.514 | 0.523 | -1.751 | 91.3514 | 0.52058 | 96.9265 | [8 empty] | SDS-CHBr3 | mg/L | 3.8 | 4.8 | 4.3 | 23.2558 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 60.868 | 62.7981 | 59.0914 | 57.7236 | Bromideb, ug/L | 60.5243 | NA | 58.2085 | 56.4255
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 1 | BMRL | 1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 11:30 | 46.75 | 24 | 80 | 80 | 481 | 4.43 | 2.28 |  | 6.71 | 0.36767 | 0.66021 | 70.6841 | 10.1112 | 10.2922 | 327.6158 | 239.5894 | 326.8051 | 0.87621 | 79.1238 | 0.13008 | 8.35 | 8.28 | 8.35 | 246 | 269 | 301 | 315.1601 | -4.7043 | 8.7199 | 314.8416 | 21.8655 | 0.016 | 0.192 | 0.524 | 0.51336 | 2.0298 | 91.3514 | 0.51107 | 96.8693 | [8 empty] | SDS-THM4 | mg/L | 32.4 | 34.5 | 33.45 | 6.278 | --- | 509.6621 | --- | 82.4502 | 507.3272 | 93.4066 | SDS-THM4 | mg/L | 42 | --- | 1280.3333 | --- | 77.9643 | 1274.2277 | 96.7039 | SDS-THM4 | mg/L | 27.5 | --- | 367.2917 | --- | 85.5719 | 365.6662 | 92.4795 | SDS-THM4 | mg/L | 24.2 | --- | 268.9059 | --- | 87.3033 | 267.7394 | 90.9614 | Alkb, mg/L CaCO3 | 190.1333 | 226.6057 | 199.1864 | 198.3522 | Alkb, mg/L CaCO3 | 178.3357 | NA | 190.1367 | 189.0493
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 8.1 | 7.3 | 7.7 | 10.3896 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 13:00 | 48.25 | 24 | 80 | 80 | 481 | 4.38 | 2.15 |  | 6.53 | 0.36767 | 0.67075 | 72.66 | 9.9971 | 10.176 | 328.7423 | 240.4199 | 327.938 | 0.8792 | 79.1208 | 0.12861 | 8.34 | 8.32 | 8.38 | 244 | 269 | 309 | 321.4488 | -4.0287 | 9.462 | 321.0962 | 24.0103 | 0.015 | 0.174 | 0.536 | 0.53133 | 0.87209 | 91.8919 | 0.52897 | 97.1643 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 229.8699 | 266.2584 | 256.8234 | 241.8209 | T-Hdb, mg/L CaCO3 | 211.3143 | NA | 246.4494 | 226.893
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 16:30 | 51.75 | 24 | 80 | 80 | 481 | 4.6 | 2.06 |  | 6.66 | 0.36767 | 0.69069 | 71.2222 | 10.4993 | 10.6871 | 330.9302 | 241.99 | 330.0796 | 0.88515 | 79.1149 | 0.13508 | 8.35 | 8.29 | 8.34 | 243 | 269 | 367 | 328.6748 | 10.4428 | 9.833 | 328.2651 | 25.9745 | 0.021 | 0.193 | 0.558 | 0.55121 | 1.2162 | 88.6486 | 0.54868 | 96.1726 | [8 empty] | SDS-DCAA* | mg/L | 3.6 | 3.3 | 3.45 | 8.6957 | --- | 136.9348 | --- | 92.7368 | 136.2804 | 97.4685 | SDS-DCAA* | mg/L | 7 | --- | 344.5 | --- | 85.2632 | 342.8359 | 97.9582 | SDS-DCAA* | mg/L | 2.3 | --- | 96.4667 | --- | 95.1579 | 96.0162 | 97.6046 | SDS-DCAA* | mg/L | 1.8 | --- | 69.0059 | --- | 96.2105 | 68.6855 | 97.3794 | Ca-Hdb, mg/L CaCO3 | 195.1715 | 240.0188 | 216.0049 | 210.9375 | Ca-Hdb, mg/L CaCO3 | 179.1359 | NA | 206.2931 | 199.6875
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 17:00 | 52.25 | 24 | 80 | 80 | 481 | 4.5 | 2.74 |  | 7.24 | 0.36767 | 0.62155 | 65.4365 | 10.271 | 10.4548 | 323.5373 | 236.5973 | 322.7239 | 0.86533 | 79.1347 | 0.13211 | [27 empty] | SDS-TCAA* | mg/L | 1.4 | BMRL | 1.4 | #VALUE! | --- | 110.7939 | --- | 96.2667 | 110.2576 | 98.7302 | SDS-TCAA* | mg/L | 2.7 | --- | 292.7 | --- | 92.8 | 291.2701 | 99.073 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 7.3 | 7.6 | 7.45 | 4.0268 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-29 | 17:45 | 53 | 24 | 80 | 80 | 481 | 4.57 | 2.71 |  | 7.28 | 0.36767 | 0.62775 | 65.0714 | 10.4308 | 10.6174 | 324.1928 | 237.0673 | 323.365 | 0.86712 | 79.1329 | 0.13417 | [27 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 98.2 | 83.5 | 90.85 | 16.1805 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-30 | 16:30 | 75.75 | 24 | 80 | 80 | 481 | 4.41 | 1.66 |  | 6.07 | 0.36767 | 0.72652 | 78.2422 | 10.0656 | 10.2457 | 334.8668 | 244.8948 | 334.0419 | 0.8956 | 79.1044 | 0.12952 | 8.29 | 8.19 | 8.32 | 249 | 269 | 295 | 323.9608 | -9.8172 | 7.6067 | 323.6172 | 23.0572 | 0.019 | 0.191 | 0.623 | 0.626 | -0.48154 | 89.7297 | 0.62322 | 96.9513 | [8 empty] | SDS-DBAA* | mg/L | 2.8 | 3.2 | 3 | 13.3333 | --- | -3.0606 | --- | -200 | -3.0309 | 198.9808 | SDS-DBAA* | mg/L | 3.5 | --- | -17.3333 | --- | -250 | -17.2306 | 120.3127 | SDS-DBAA* | mg/L | 2.7 | --- | -0.84167 | --- | -170 | -0.82472 | 427.3822 | SDS-DBAA* | mg/L | 2.3 | --- | 0.38824 | --- | -130 | 0.39735 | -478.8374 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 106.3 | 90.8 | 98.55 | 15.7281 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-30 | 17:00 | 76.25 | 24 | 80 | 80 | 481 | 4.44 | 2.05 |  | 6.49 | 0.36767 | 0.68413 | 73.114 | 10.1341 | 10.3154 | 330.1969 | 241.4755 | 329.3779 | 0.88312 | 79.1169 | 0.13038 | 8.33 | 8.29 | 8.31 | 251 | 269 | 307 | 309.5683 | -0.83658 | 6.8646 | 309.298 | 18.8485 | 0.019 | 0.191 | 0.627 | 0.54453 | 13.1528 | 89.7297 | 0.54211 | 96.4952 | [8 empty] | SDS-BCAA* | mg/L | 3.3 | 3 | 3.15 | 9.5238 | --- | 16.9379 | --- | 59.0909 | 16.8703 | 81.3281 | SDS-BCAA* | mg/L | 4.7 | --- | 29.7 | --- | 38.961 | 29.5767 | 84.1091 | SDS-BCAA* | mg/L | 2.2 | --- | 13.6583 | --- | 71.4286 | 13.6035 | 83.8277 | SDS-BCAA* | mg/L | 2 | --- | 10.3824 | --- | 74.026 | 10.3424 | 80.6621 | Qp/QT (HAA5), % | 44.0263 | 47.4565 | 42.9237 | 42.4784 | Qp/QT (HAA5), % | 76.2843 | 82.2279 | 74.3739 | 73.6023
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-30 | 17:30 | 76.75 | 24 | 80 | 80 | 481 | 4.6 | 2.08 |  | 6.68 | 0.36767 | 0.68862 | 71.006 | 10.4993 | 10.6871 | 330.7045 | 241.8249 | 329.8545 | 0.88455 | 79.1155 | 0.13508 | [27 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 121.4127 | 120.0796 | 120.5914 | 119.916 | SDS-THM4b, ug/L | 70.7191 | 68.4093 | 69.2962 | 68.1258
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-30 | 18:00 | 77.25 | 24 | 80 | 80 | 481 | 5.33 | 0.31 |  | 5.64 | 0.36767 | 0.94504 | 84.2837 | 12.1654 | 12.3831 | 361.3913 | 264.1555 | 360.3138 | 0.96697 | 79.033 | 0.15668 | 8.32 | 8.32 |  | 251 | 269 |  | 587.5806 |  | 6.8646 | 585.7158 | 57.1465 | 0.018 | 0.19 | 0.626 | 3.0563 | -388.2304 | 90.2703 | 3.0395 | 99.4078 | [8 empty] | SDS-CDBAA | mg/L | 2.2 | BMRL | 2.2 | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | 2.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-30 | 18:30 | 77.75 | 24 | 80 | 81 | 481 | 4.5 | 0.34 |  | 4.84 | 0.36767 | 0.92975 | 98.3802 | 10.271 | 10.4548 | 359.2568 | 262.7184 | 358.3536 | 0.96087 | 79.5391 | 0.13144 | 8.33 | 8.29 | 8.4 | 251 | 269 |  | 514.3529 |  | 6.8646 | 513.121 | 51.0837 | 0.025 | 0.19 | 0.677 | 2.3026 | -240.1251 | 86.4865 | 2.292 | 98.9092 | [8 empty] | SDS-DCBAA | mg/L | 2.2 | 1.6 | 1.9 | 31.5789 | --- | 18.7182 | --- | 74.4966 | 18.6357 | 89.8045 | SDS-DCBAA | mg/L | 2.9 | --- | 40.8167 | --- | 61.0738 | 40.6297 | 92.8624 | SDS-DCBAA | mg/L | 1.6 | --- | 13.7875 | --- | 78.5235 | 13.7292 | 88.346 | SDS-DCBAA | mg/L | 1.4 | --- | 10.2971 | --- | 81.2081 | 10.2546 | 86.3477 | SDS-TOXb, ug Cl- /L | 335.6395 | 332.2505 | 335.544 | 329.9931 | SDS-TOXb, ug Cl- /L | 187.7363 | 181.8641 | 187.5708 | 177.9527
[44 empty] | 1998-05-30 | 18:45 | 78 | 24 | 80 | 80 | 481 | 4.75 | 0.52 |  | 5.27 | 0.36767 | 0.90133 | 90.2713 | 10.8416 | 11.0356 | 355.6794 | 260.0656 | 354.7352 | 0.95142 | 79.0486 | 0.13961 | [27 empty] | SDS-HAA5 | mg/L | 7.8 | 6.5 | 7.15 | 18.1818 | --- | 260.7864 | --- | 92.1299 | 259.5428 | 97.2452 | SDS-HAA5 | mg/L | 13.2 | --- | 660.2833 | --- | 85.4706 | 657.0928 | 97.9912 | SDS-HAA5 | mg/L | 5 | --- | 183.8542 | --- | 94.4964 | 182.9986 | 97.2677 | SDS-HAA5 | mg/L | 4.1 | --- | 131.6735 | --- | 95.4871 | 131.0654 | 96.8718 | SDS-CDb, mg/L | 3.2339 | 3.3542 | 3.2653 | 3.3167 | SDS-CDb, mg/L | 1.6872 | 1.8955 | 1.7416 | 1.8305
[44 empty] | 1998-05-30 | 19:00 | 78.25 | 24 | 80 | 80 | 481 | 4.8 | 0.54 |  | 5.34 | 0.36767 | 0.89888 | 89.0749 | 10.9557 | 11.1518 | 355.379 | 259.8386 | 354.4255 | 0.95064 | 79.0494 | 0.14107 | 8.31 | 8.28 | 8.35 | 255 | 269 |  | 398.3889 |  | 5.3803 | 397.6734 | 35.877 | 0.025 | 0.191 | 0.81 | 1.6072 | -98.4225 | 86.4865 | 1.5993 | 98.4368 | [8 empty] | SDS-HAA6 | mg/L | 11.1 | 9.5 | 10.3 | 15.534 | --- | 277.7242 | --- | 89.5485 | 276.413 | 96.2737 | SDS-HAA6 | mg/L | 17.9 | --- | 689.9833 | --- | 81.8366 | 686.6696 | 97.3932 | SDS-HAA6 | mg/L | 7.2 | --- | 197.5125 | --- | 92.6941 | 196.6021 | 96.3378 | SDS-HAA6 | mg/L | 6.1 | --- | 142.0559 | --- | 93.8102 | 141.4078 | 95.6862 | TOCb, mg/L | 3.8326 | 3.8221 | 3.825 | 3.8062 | TOCb, mg/L | 2.1714 | 2.1531 | 2.1582 | 2.1255
[44 empty] | 1998-05-30 | 19:15 | 78.5 | 24 | 80 | 80 | 481 | 4.75 | 0.51 |  | 5.26 | 0.36767 | 0.90304 | 90.4449 | 10.8416 | 11.0356 | 355.8958 | 260.2238 | 354.951 | 0.952 | 79.048 | 0.13961 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.11236 | 0.11002 | 0.1116 | 0.11109 | UV254 b, cm-1 | 0.059131 | 0.05508 | 0.057821 | 0.056932
[44 empty] | 1998-05-30 | 19:30 | 78.75 | 24 | 80 | 80 | 481 | 4.6 | 0.48 |  | 5.08 | 0.36767 | 0.90551 | 93.685 | 10.4993 | 10.6871 | 356.1817 | 260.455 | 355.2662 | 0.95269 | 79.0473 | 0.1352 | 8.33 | 8.29 |  | 256 | 268 |  | 398.875 |  | 5.0093 | 398.1918 | 35.7094 | 0.025 | 0.193 | 0.894 | 1.7183 | -92.2073 | 86.4865 | 1.7102 | 98.5382 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 61.3396 | 62.4746 | 60.2831 | 59.4513 | Bromideb, ug/L | 60.8557 | 62.8223 | 59.025 | 57.5839
[44 empty] | 1998-05-30 | 19:45 | 79 | 24 | 80 | 80 | 481 | 5 | 0.82 |  | 5.82 | 0.36767 | 0.85911 | 81.646 | 11.4122 | 11.6164 | 350.4705 | 256.2208 | 349.4908 | 0.9376 | 79.0624 | 0.14693 | [66 empty] | Alkb, mg/L CaCO3 | 206.3265 | 227.5763 | 211.4013 | 210.7343 | Alkb, mg/L CaCO3 | 189.7136 | 226.5332 | 198.5067 | 197.351
[44 empty] | 1998-05-30 | 20:00 | 79.25 | 24 | 80 | 80 | 481 | 4.67 | 0.83 |  | 5.5 | 0.36767 | 0.84909 | 86.4545 | 10.659 | 10.8498 | 349.1949 | 255.3358 | 348.2836 | 0.93403 | 79.066 | 0.13722 | 8.29 | 8.31 | 8.34 | 259 | 270 |  | 328.5783 |  | 3.8961 | 328.2405 | 21.0945 | 0.028 | 0.201 | 0.935 | 1.0684 | -14.2633 | 84.8649 | 1.0633 | 97.3667 | [47 empty] | T-Hdb, mg/L CaCO3 | 255.3387 | 276.2885 | 270.8259 | 261.6899 | T-Hdb, mg/L CaCO3 | 229.2097 | 265.5093 | 256.0443 | 240.2144
[44 empty] | 1998-05-30 | 20:30 | 79.75 | 24 | 80 | 80 | 481 | 5.6 | 0.81 |  | 6.41 | 0.36767 | 0.87363 | 74.039 | 12.7817 | 13.0104 | 352.3601 | 257.5149 | 351.2559 | 0.94293 | 79.0571 | 0.16457 | [66 empty] | Ca-Hdb, mg/L CaCO3 | 217.1816 | 243.2543 | 229.1136 | 225.9112 | Ca-Hdb, mg/L CaCO3 | 194.601 | 239.7772 | 215.2755 | 209.7268
[44 empty] | 1998-05-30 | 21:00 | 80.25 | 24 | 80 | 80 | 481 | 4.77 | 0.78 |  | 5.55 | 0.36767 | 0.85946 | 85.6667 | 10.8873 | 11.0821 | 350.4766 | 256.2585 | 349.5422 | 0.93751 | 79.0625 | 0.14017 | 8.28 | 8.27 | 8.3 | 256 | 270 | 378 | 352.0577 | 6.863 | 5.0093 | 351.5814 | 27.1861 | 0.025 | 0.187 | 0.979 | 1.1635 | -18.8418 | 86.4865 | 1.1578 | 97.8408 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-05-30 | 22:00 | 81.25 | 24 | 80 | 80 | 481 | 4.83 | 0.78 |  | 5.61 | 0.36767 | 0.86096 | 84.7398 | 11.0242 | 11.2215 | 350.6706 | 256.3917 | 349.7239 | 0.93806 | 79.0619 | 0.14193 | 8.29 | 8.27 | 8.29 | 256 | 269 | 411 | 353.0962 | 14.0885 | 5.0093 | 352.6087 | 27.3983 | 0.023 | 0.185 | 1.017 | 1.1882 | -16.8293 | 87.5676 | 1.1823 | 98.0546 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-05-30 | 23:00 | 82.25 | 24 | 80 | 80 | 481 | 4.9 | 0.78 |  | 5.68 | 0.36767 | 0.86268 | 83.6831 | 11.184 | 11.3841 | 350.8923 | 256.5437 | 349.9312 | 0.93868 | 79.0613 | 0.14399 | 8.3 | 8.27 | 8.31 | 254 | 269 | 319 | 366.8718 | -15.0068 | 5.7514 | 366.2969 | 30.6573 | 0.024 | 0.193 | 1.056 | 1.1964 | -13.2964 | 87.027 | 1.1904 | 97.9839 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-05-30 | 23:30 | 82.75 | 24 | 80 | 80 | 481 | 5 | 0.79 |  | 5.79 | 0.36767 | 0.86356 | 82.0743 | 11.4122 | 11.6164 | 351.017 | 256.6203 | 350.0357 | 0.93906 | 79.0609 | 0.14693 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-05-30 | 24:00 | 83.25 | 24 | 80 | 80 | 481 | 4.99 | 0.75 |  | 5.74 | 0.36767 | 0.86934 | 82.7979 | 11.3894 | 11.5932 | 351.7274 | 257.1412 | 350.7462 | 0.94096 | 79.059 | 0.14664 | 8.25 | 8.24 | 8.29 | 260 | 269 | 442 | 332.7067 | 24.727 | 3.525 | 332.3295 | 21.7644 | 0.026 | 0.191 | 1.083 | 1.2429 | -14.7627 | 85.9459 | 1.2366 | 97.8974 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-05-31 | 0:30 | 83.75 | 24 | 80 | 80 | 481 | 4.93 | 0.81 |  | 5.74 | 0.36767 | 0.85889 | 82.7979 | 11.2525 | 11.4538 | 350.4321 | 256.2028 | 349.4663 | 0.93746 | 79.0625 | 0.14487 | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-05-31 | 16:00 | 99.25 | 24 | 80 | 81 | 481 | 4.38 | 0.44 |  | 4.82 | 0.36767 | 0.90871 | 98.7925 | 9.9971 | 10.176 | 356.5484 | 260.7554 | 355.6761 | 0.95357 | 79.5464 | 0.12793 | [66 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-05-31 | 16:30 | 99.75 | 24 | 80 | 81 | 481 | 4.33 | 0.43 |  | 4.76 | 0.36767 | 0.90966 | 100.0504 | 9.883 | 10.0598 | 356.66 | 260.8444 | 355.7974 | 0.95384 | 79.5462 | 0.12647 | 8.22 | 8.33 | 8.33 | 261 | 269 | 528 | 355.093 | 32.7475 | 3.154 | 354.6695 | 26.4104 | 0.03 | 0.185 | 1.57 | 1.7458 | -11.1983 | 83.7838 | 1.7381 | 98.274 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-05-31 | 17:45 | 101 | 24 | 80 | 81 | 481 | 4.4 | 0.44 |  | 4.84 | 0.36767 | 0.90909 | 98.3802 | 10.0428 | 10.2225 | 356.5997 | 260.79 | 355.7233 | 0.95371 | 79.5463 | 0.12851 | 8.2 | 8.33 | 8.33 | 261 | 269 | 327 | 354.5 | -8.4098 | 3.154 | 354.0723 | 26.2863 | 0.028 | 0.19 | 1.58 | 1.755 | -11.0759 | 84.8649 | 1.7471 | 98.3973 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-05-31 | 18:45 | 102 | 24 | 78 | 79 | 481 | 4.57 | 9.3 |  | 13.87 | 0.36767 | 0.32949 | 33.6792 | 10.4308 | 10.6174 | 295.6822 | 216.2189 | 294.9273 | 0.79086 | 77.7091 | 0.13663 | [66 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-05-31 | 19:30 | 102.75 | 24 | 80 | 80 | 481 | 4.5 | 3.3 |  | 7.8 | 0.36767 | 0.57692 | 60.6667 | 10.271 | 10.4548 | 318.9459 | 233.2397 | 318.144 | 0.85305 | 79.1469 | 0.13209 | [66 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-05-31 | 19:45 | 103 | 24 | 80 | 80 | 481 | 4.54 | 4.02 |  | 8.56 | 0.36767 | 0.53037 | 55.1916 | 10.3623 | 10.5477 | 314.2964 | 229.8345 | 313.4992 | 0.84063 | 79.1594 | 0.13325 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-05-31 | 20:00 | 103.25 | 24 | 80 | 80 | 481 | 4.53 | 4.59 |  | 9.12 | 0.36767 | 0.49671 | 51.7412 | 10.3395 | 10.5245 | 311.0144 | 227.4357 | 310.2273 | 0.83185 | 79.1681 | 0.13294
[44 empty] | 1998-05-31 | 20:30 | 103.75 | 24 | 80 | 80 | 481 | 4.5 | 4.3 |  | 8.8 | 0.36767 | 0.51136 | 53.6591 | 10.271 | 10.4548 | 312.4319 | 228.4762 | 311.6465 | 0.83563 | 79.1644 | 0.13206 | 8.32 | 8.35 | 8.36 | 246 | 263 | 280 | 294.093 | -5.0332 | 8.7199 | 293.8681 | 16.289 | 0.01 | 0.184 | 0.429 | 0.36814 | 14.1866 | 94.5946 | 0.36646 | 97.2712
[44 empty] | 1998-05-31 | 21:10 | 104.4167 | 24 | 80 | 80 | 481 | 4.6 | 4.66 |  | 9.26 | 0.36767 | 0.49676 | 50.9438 | 10.4993 | 10.6871 | 311.0244 | 227.434 | 310.225 | 0.83191 | 79.1681 | 0.13499 | 8.25 | 8.31 | 8.32 | 238 | 267 | 378 | 300.5944 | 20.4777 | 11.6883 | 300.2951 | 20.7446 | 0.013 | 0.188 | 0.394 | 0.35479 | 9.9529 | 92.973 | 0.35315 | 96.3189
[44 empty] | 1998-05-31 | 22:00 | 105.25 | 24 | 80 | 80 | 481 | 4.63 | 4.46 |  | 9.09 | 0.36767 | 0.50935 | 51.9153 | 10.5677 | 10.7568 | 312.246 | 228.3235 | 311.4382 | 0.83519 | 79.1648 | 0.13588 | 8.29 | 8.27 | 8.31 | 234 | 265 | 290 | 306.3531 | -5.639 | 13.1725 | 306.0049 | 23.5306 | 0.013 | 0.188 | 0.38 | 0.36356 | 4.3274 | 92.973 | 0.36187 | 96.4075
[44 empty] | 1998-05-31 | 22:30 | 105.75 | 24 | 80 | 80 | 481 | 4.67 | 4.4 |  | 9.07 | 0.36767 | 0.51488 | 52.032 | 10.659 | 10.8498 | 312.7881 | 228.7147 | 311.9718 | 0.83665 | 79.1633 | 0.13706 | 8.3 | 8.28 | 8.31 | 233 | 266 | 286 | 308.2398 | -7.7761 | 13.5436 | 307.8745 | 24.3198 | 0.013 | 0.19 | 0.381 | 0.36755 | 3.529 | 92.973 | 0.36583 | 96.4465
[44 empty] | 1998-05-31 | 23:00 | 106.25 | 24 | 80 | 80 | 481 | 4.5 | 5.2 |  | 9.7 | 0.36767 | 0.46392 | 48.5876 | 10.271 | 10.4548 | 307.8812 | 225.1483 | 307.1072 | 0.82346 | 79.1765 | 0.13204 | 8.3 | 8.29 | 8.31 | 231 | 267 | 286 | 302.8173 | -5.8802 | 14.2857 | 302.4814 | 23.6317 | 0.013 | 0.189 | 0.371 | 0.33385 | 10.0145 | 92.973 | 0.33235 | 96.0884
[44 empty] | 1998-06-01 | 8:00 | 115.25 | 24 | 80 | 80 | 481 | 4.5 | 3.22 |  | 7.72 | 0.36767 | 0.5829 | 61.3057 | 10.271 | 10.4548 | 319.5534 | 233.684 | 318.7501 | 0.85468 | 79.1453 | 0.1321
[44 empty] | 1998-06-01 | 8:40 | 115.9167 | 24 | 80 | 80 | 481 | 4.5 | 4.12 |  | 8.62 | 0.36767 | 0.52204 | 54.8005 | 10.271 | 10.4548 | 313.4747 | 229.2387 | 312.6866 | 0.83842 | 79.1616 | 0.13207 | 8.22 | 8.3 | 8.27 | 231 | 264 | 281 | 311.551 | -10.8722 | 14.2857 | 311.1742 | 25.765 | 0.014 | 0.187 | 0.408 | 0.37177 | 8.8794 | 92.4324 | 0.3701 | 96.2172
[44 empty] | 1998-06-01 | 9:15 | 116.5 | 24 | 80 | 80 | 481 | 4.44 | 4.09 |  | 8.53 | 0.36767 | 0.52052 | 55.3892 | 10.1341 | 10.3154 | 313.3206 | 229.1338 | 312.5435 | 0.83798 | 79.162 | 0.13031 | 8.3 | 8.32 | 8.33 | 228 | 268 | 289 | 314.5513 | -8.8413 | 15.3989 | 314.1519 | 27.4236 | 0.012 | 0.187 | 0.391 | 0.3728 | 4.6536 | 93.5135 | 0.37114 | 96.7667
[44 empty] | 1998-06-01 | 10:45 | 118 | 24 | 78 | 79 | 481 | 4.44 | 10.4 |  | 14.84 | 0.36767 | 0.29919 | 31.4124 | 10.1341 | 10.3154 | 293.0591 | 214.3164 | 292.3323 | 0.78379 | 77.7162 | 0.13273
[44 empty] | 1998-06-01 | 11:15 | 118.5 | 24 | 79 | 79 | 481 | 4.5 | 10.35 |  | 14.85 | 0.36767 | 0.30303 | 31.3906 | 10.271 | 10.4548 | 293.3906 | 214.5516 | 292.653 | 0.7847 | 78.2153 | 0.13367
[44 empty] | 1998-06-01 | 11:45 | 119 | 24 | 79 | 80 | 481 | 4.57 | 9.6 |  | 14.17 | 0.36767 | 0.32251 | 32.945 | 10.4308 | 10.6174 | 295.0753 | 215.7751 | 294.3219 | 0.78924 | 78.7108 | 0.13489
[44 empty] | 1998-06-01 | 12:00 | 119.25 | 24.6 | 79 | 80 | 481 | 4.5 | 10.1 |  | 14.6 | 0.36767 | 0.30822 | 31.9452 | 10.271 | 10.271 | 293.8366 | 214.8778 | 293.0979 | 0.7859 | 78.7141 | 0.13048
[44 empty] | 1998-06-01 | 13:00 | 120.25 | 24 | 79 | 80 | 481 | 4.6 | 10.16 |  | 14.76 | 0.36767 | 0.31165 | 31.5881 | 10.4993 | 10.6871 | 294.1367 | 215.085 | 293.3807 | 0.78674 | 78.7133 | 0.13577 | 8.39 | 8.32 | 8.37 | 235 | 264 | 281 | 285.1201 | -1.4662 | 12.8015 | 284.8804 | 17.5092 | 0.013 | 0.186 | 0.269 | 0.26287 | 2.2773 | 92.973 | 0.26168 | 95.0321
[44 empty] | 1998-06-01 | 15:15 | 122.5 | 24 | 79 | 80 | 481 | 4.4 | 10.22 |  | 14.62 | 0.36767 | 0.30096 | 31.9001 | 10.0428 | 10.2225 | 293.2089 | 214.4308 | 292.4882 | 0.78418 | 78.7158 | 0.12987 | 8.33 | 8.34 | 8.35 | 231 | 262 | 275 | 286.0753 | -4.0274 | 14.2857 | 285.8234 | 19.1809 | 0.011 | 0.185 | 0.269 | 0.25991 | 3.3785 | 94.0541 | 0.25877 | 95.7492
[44 empty] | 1998-06-01 | 15:50 | 123.0833 | 24.5 | 79 | 80 | 481 | 4.42 | 9.79 |  | 14.21 | 0.36767 | 0.31105 | 32.8494 | 10.0884 | 10.1183 | 294.0771 | 215.0633 | 293.3511 | 0.78651 | 78.7135 | 0.12855 | 8.31 | 8.33 | 8.34 | 227 | 262 | 275 | 288.6879 | -4.9774 | 15.7699 | 288.4045 | 21.2911 | 0.012 | 0.185 | 0.268 | 0.26311 | 1.826 | 93.5135 | 0.26195 | 95.419
[44 empty] | 1998-06-01 | 16:20 | 123.5833 | 24 | 79 | 80 | 481 | 4.44 | 11.73 |  | 16.17 | 0.36767 | 0.27458 | 28.7464 | 10.1341 | 10.3154 | 290.967 | 212.7864 | 290.2454 | 0.7782 | 78.7218 | 0.13104 | 8.31 | 8.34 | 8.34 | 226 | 262 | 270 | 285.9655 | -5.9131 | 16.141 | 285.6887 | 20.8929 | 0.01 | 0.185 | 0.259 | 0.25124 | 2.996 | 94.5946 | 0.25013 | 96.002
[44 empty] | 1998-06-02 | 12:00 | 143.25 | 24 | 79 | 80 | 481 | 4.93 | 9.17 |  | 14.1 | 0.36767 | 0.34965 | 33.1135 | 11.2525 | 11.4538 | 297.4672 | 217.4799 | 296.6474 | 0.79577 | 78.7042 | 0.14553
[44 empty] | 1998-06-02 | 20:00 | 151.25 | 24 | 79 | 80 | 481 | 4.48 | 7.5 |  | 11.98 | 0.36767 | 0.37396 | 39.1503 | 10.2254 | 10.4083 | 299.606 | 219.0993 | 298.8562 | 0.80132 | 78.6987 | 0.13226 | 8.3 | 8.2 | 8.19 | 226 | 264 | 293 | 295.484 | -0.84778 | 16.141 | 295.1604 | 23.4315 | BMRL | 0.188 | 0.293 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-06-02 | 21:00 | 152.25 | 24 | 79 | 80 | 481 | 4.56 | 9.67 | X | 14.23 | 0.36767 | 0.32045 | 32.8018 | 10.408 | 10.5942 | 294.8959 | 215.6451 | 294.1446 | 0.78875 | 78.7112 | 0.1346 | 8.31 | 8.25 | 8.3 | 228 | 263 | 279 | 289.0698 | -3.6092 | 15.3989 | 288.7803 | 21.0473 | 0.01 | 0.19 | 0.276 | 0.26752 | 3.0713 | 94.5946 | 0.2663 | 96.2449
[44 empty] | 1998-06-03 | 14:30 |  | 24 | 61 | 60 | 382 | 3.2 | 2.66 |  | 5.86 | 0.292 | 0.54608 | 64.1877 | 7.3038 | 7.4345 | 315.8081 | 231.0064 | 315.0977 | 0.84447 | 59.6555 | 0.12462
[44 empty] | 1998-06-03 | 15:15 |  | 24 | 80 | 80 | 382 | 4.13 | 2.26 |  | 6.39 | 0.292 | 0.64632 | 58.7809 | 9.4265 | 9.5952 | 326.2177 | 238.4632 | 325.269 | 0.8728 | 79.1272 | 0.12126
[44 empty] | 1998-06-03 | 15:30 |  | 24 | 70 | 69 | 382 | 3.56 | 1.6 |  | 5.16 | 0.292 | 0.68992 | 73.031 | 8.1255 | 8.2709 | 330.8327 | 241.9347 | 330.0043 | 0.88484 | 68.6152 | 0.12054
[44 empty] | 1998-06-03 | 15:45 |  | 24 | 91 | 90 | 382 | 4.76 | 2.8 |  | 7.56 | 0.292 | 0.62963 | 49.5291 | 10.8644 | 11.0588 | 324.5349 | 237.1265 | 323.4457 | 0.86864 | 89.6314 | 0.12338
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on U3: C. Rice: Cartridge filtration was the only membrane pretreatment employed.
Note on X13: C. Rice: Total hardness values verified by consultant.
Note on BV7: C. Rice 7/12/99: Consultant verified MTCw values but gave no explanation as to why these values are low relative to the other three quarters.
Note on CY18: C. Rice: Consultant verified all total hardness vlaues due to the consistently high mass balance closure error.
Note on DL18: C. Rice: Consultant verified all total hardness vlaues due to the consistently high mass balance closure error.
Note on DV18: C. Rice: Consultant verified all total hardness vlaues due to the consistently high mass balance closure error.
Note on EF18: C. Rice: Consultant verified all total hardness vlaues due to the consistently high mass balance closure error.

## 7450. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.13935 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.92 | [7 empty] | Recovery during sample collection (decimal) | 0.48 | [7 empty] | Recovery during sample collection (decimal) | 0.32 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-07-24 | 1998-07-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 10.38 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.15 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.08 | [7 empty] | Feed flow rate during sample collection (mL/min) | 20.21 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:30 | 9:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 321 | [10 empty] | Influent flow rate during sample collection (mL/min) | 321 | [7 empty] | Influent flow rate during sample collection (mL/min) | 321 | [7 empty] | Influent flow rate during sample collection (mL/min) | 321 | [6 empty] | SDS-THM4F, ug/L | 202.15 | 202.15 | 202.15 | 202.15 | SDS-THM4F, ug/L | 202.15 | 202.15 | 202.15 | 202.15 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 71.75 | 62 | 78.4 | 53.9 | SDS-THM4p, ug/L | 71.75 | 62 | 78.4 | 53.9 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.71 | 8 | 7.855 | 3.6919 | 1998-07-15 | 8:30 | 0 | 24 | 62 | 35.5 | 340 | 7.32 | 3.6 | 10.92 | 0.25989 | 0.67033 | 30.1355 | 16.7075 | 17.0065 | 0 | 0 | 0 | 0 | 48.75 | 0.34885 | 1998-07-16 | 9:30 | 0 | 24 | 58 | 60 | 321 | 7.25 | 3.4 |  | 10.65 | 0.24537 | 0.68075 | 29.1408 | 16.5477 | 16.8438 | 316.6316 | 271.6348 | 315.6153 | 0.44489 | 58.5551 | 0.28766 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-07-15 | 9:15 | 0.75 | 24 | 62 | 35.5 | 340 | 7.32 | 3.6 | 10.92 | 0.25989 | 0.67033 | 30.1355 | 16.7075 | 17.0065 | 0 | 0 | 0 | 0 | 48.75 | 0.34885 | 1998-07-16 | 10:40 | 1.1667 | 24 | 58 | 60 | 321 | 7.25 | 3.4 |  | 10.65 | 0.24537 | 0.68075 | 29.1408 | 16.5477 | 16.8438 | 316.6316 | 271.6348 | 315.6153 | 0.44489 | 58.5551 | 0.28766 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 14.85 | 16.7 | 12.5 | 9 | SDS-HAA5p, ug/L | 14.85 | 16.7 | 12.5 | 9 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 334 | 326 | 330 | 2.4242 | 1998-07-15 | 10:20 | 1.8333 | 24 | 63 | 35.5 | 340 | 7.57 | 3.37 | 10.94 | 0.25989 | 0.69196 | 30.0786 | 17.2781 | 17.5873 | 0 | 0 | 0 | 0 | 49.25 | 0.3571 | 1998-07-16 | 11:00 | 1.5 | 24 | 59 | 60 | 321 | 7.29 | 3.14 |  | 10.43 | 0.24537 | 0.69895 | 29.7766 | 16.639 | 16.9368 | 317.5444 | 272.413 | 316.5194 | 0.44619 | 59.0538 | 0.2868 | 7.59 | 7.46 | 7.62 | 256 | 283 | 277 | 355.6497 | -28.3934 | 10.4895 | 354.5181 | 27.7893 | 0.037 | 0.2 | 0.3 | 0.59006 | -96.6852 | 81.8182 | 0.58378 | 93.6619 | [8 empty] | Sampling date | MM/DD/YY | 1998-07-17 | 1998-07-18 | --- | --- | 1998-07-17 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-19 | 1998-07-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-20 | 1998-07-20 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-21 | 1998-07-21 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 472.5 | 472.5 | 472.5 | 472.5 | SDS-TOXF, ug Cl- /L | 472.5 | 472.5 | 472.5 | 472.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 288 | 284 | 286 | 1.3986 | 1998-07-15 | 10:50 | 2.3333 | 24 | 63 | 35.5 | 340 | 7.83 | 3.3 | 11.13 | 0.25989 | 0.7035 | 29.5481 | 17.8716 | 18.1913 | 0 | 0 | 0 | 0 | 49.25 | 0.36937 | 1998-07-16 | 11:30 | 2 | 24 | 58 | 60 | 321 | 6.86 | 2.97 |  | 9.83 | 0.24537 | 0.69786 | 31.6551 | 15.6576 | 15.9378 | 317.4491 | 272.3843 | 316.4861 | 0.44583 | 58.5542 | 0.27219 | 7.55 | 7.45 | 7.55 | 273 | 284 | 293 | 316.0269 | -7.859 | 4.5455 | 315.5672 | 13.4891 | 0.047 | 0.202 | 0.394 | 0.56498 | -43.3955 | 76.9042 | 0.55944 | 91.5988 | [8 empty] | Sampling time | hh:mm | 8:30 | 10:30 | --- | --- | 8:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:00 | 19:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 10:30 | 10:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 140 | 180 | 100 | 84 | SDS-TOXp, ug Cl- /L | 140 | 180 | 100 | 84 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 322 | 278 | 300 | 14.6667 | 1998-07-15 | 11:15 | 2.75 | 24 | 46 | 31.5 | 340 | 5.15 | 2.08 | 7.23 | 0.25989 | 0.71231 | 46.0263 | 11.7546 | 11.9649 | 0 | 0 | 0 | 0 | 38.75 | 0.30877 | 1998-07-16 | 12:00 | 2.5 | 24 | 58 | 60 | 321 | 7.31 | 2.89 |  | 10.2 | 0.24537 | 0.71667 | 30.4706 | 16.6847 | 16.9832 | 318.4369 | 273.1761 | 317.4062 | 0.44745 | 58.5525 | 0.29005 | 7.45 | 7.43 | 7.57 | 273 | 282 | 296 | 318.8824 | -7.7305 | 4.5455 | 318.3599 | 14.248 | 0.05 | 0.203 | 0.438 | 0.59176 | -35.1061 | 75.43 | 0.5856 | 91.4617 | [8 empty] | Operation time | hh.hh | 23 | 49 | --- | --- | 23 | --- | --- | --- | --- | --- | Operation time | hh.hh | 81.5 | 81.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 103 | 103 | --- | --- | --- | --- | --- | Cumulative time | hr | 122.5 | 122.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 4.575 | 4.575 | 4.575 | 4.575 | SDS-CDF, mg/L | 4.575 | 4.575 | 4.575 | 4.575 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 272 | 264 | 268 | 2.9851 | 1998-07-15 | 11:30 | 3 | 24 | 72 | 39 | 340 | 9.13 | 4.03 | 13.16 | 0.25989 | 0.69377 | 24.8359 | 20.8387 | 21.2116 | 0 | 0 | 0 | 0 | 55.5 | 0.38219 | 1998-07-16 | 13:15 | 3.75 | 24 | 58 | 60 | 321 | 7.25 | 6.47 |  | 13.72 | 0.24537 | 0.52843 | 22.3965 | 16.5477 | 16.8438 | 309.2209 | 265.2773 | 308.2284 | 0.43447 | 58.5655 | 0.28761 | 7.6 | 7.51 | 7.64 | 271 | 280 | 297 | 302.8083 | -1.9557 | 5.2448 | 302.4491 | 10.3982 | 0.052 | 0.203 | 0.468 | 0.37326 | 20.2427 | 74.4472 | 0.36964 | 85.9321 | [8 empty] | pH | --- | 8.09 | 8.18 | 8.135 | 1.1063 | 8 | --- | --- | --- | --- | --- | pH | --- | 8.16 | 8.44 | --- | --- | --- | --- | --- | pH | --- | 8.14 | 8.35 | --- | --- | --- | --- | --- | pH | --- | 8.03 | 8.34 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.5 | 1.43 | 0.97 | 0.82 | SDS-CDp, mg/L | 1.5 | 1.43 | 0.97 | 0.82 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 15.1667 | 62.5992 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.195 | 0.195 | 0.195 | 0 | 1998-07-15 | 11:45 | 3.25 | 24 | 60 | 34.5 | 340 | 7.6 | 3.08 | 10.68 | 0.25989 | 0.71161 | 30.8352 | 17.3466 | 17.657 | 0 | 0 | 0 | 0 | 47.25 | 0.37369 | 1998-07-16 | 15:00 | 5.5 | 24 | 58 | 60 | 321 | 7.44 | 3.37 |  | 10.81 | 0.24537 | 0.68825 | 28.6947 | 16.9814 | 17.2853 | 317.0235 | 271.9477 | 315.9788 | 0.44553 | 58.5545 | 0.2952 | 7.51 | 7.47 | 7.62 | 270 | 281 | 294 | 321.3234 | -9.2937 | 5.5944 | 320.7287 | 15.8167 | 0.043 | 0.195 | 0.497 | 0.55784 | -12.2411 | 78.8698 | 0.55187 | 92.2083 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.65 | 6.65 | 6.65 | 6.65 | TOCF, mg/L | 6.65 | 6.65 | 6.65 | 6.65 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 38.5 | 85.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | 0.07 | 0.07 | #VALUE! | 1998-07-15 | 13:30 | 5 | 24 | 60 | 34.5 | 340 | 7.33 | 2.93 | 10.26 | 0.25989 | 0.71442 | 32.1384 | 16.7303 | 17.0297 | 0 | 0 | 0 | 0 | 47.25 | 0.36042 | 1998-07-16 | 16:00 | 6.5 | 24 | 59 | 60 | 321 | 7.25 | 3.23 |  | 10.48 | 0.24537 | 0.69179 | 29.6298 | 16.5477 | 16.8438 | 317.1827 | 272.1076 | 316.1646 | 0.44566 | 59.0543 | 0.28523 | 7.46 | 7.43 | 7.53 | 271 | 279 | 299 | 319.6687 | -6.9126 | 5.2448 | 319.1191 | 15.0787 | 0.053 | 0.206 | 0.507 | 0.54131 | -6.7672 | 73.9558 | 0.5358 | 90.1082 | [8 empty] | Alkalinity | mg/L as CaCO3 | 220 | 296 | 258 | 29.4574 | 369 | 490.2581 | -32.8613 | 21.8182 | 487.667 | 47.095 | Alkalinity | mg/L as CaCO3 | 354 | 398 | 54 | 86.4322 | -7.2727 | 57.0738 | -520.2492 | Alkalinity | mg/L as CaCO3 | 268 | 366 | 387.2308 | -5.8008 | 18.7879 | 386.0648 | 30.5816 | Alkalinity | mg/L as CaCO3 | 214 | 344 | 384.5882 | -11.7989 | 35.1515 | 382.8698 | 44.1063 | TOCp, mg/L | 2.05 | 2.5 | 1.2 | 1.4 | TOCp, mg/L | 2.05 | 2.5 | 1.2 | 1.4 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 57.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6.5 | 6.8 | 6.65 | 4.5113 | 1998-07-15 | 15:00 | 6.5 | 24 | 60 | 34.5 | 340 | 7.38 | 2.83 | 10.21 | 0.25989 | 0.72282 | 32.3007 | 16.8445 | 17.1459 | 0 | 0 | 0 | 0 | 47.25 | 0.36288 | 1998-07-16 | 16:45 | 7.25 | 24 | 59 | 60 | 321 | 7.14 | 3.29 |  | 10.43 | 0.24537 | 0.68456 | 29.7766 | 16.2967 | 16.5883 | 316.8114 | 271.8026 | 315.8102 | 0.44508 | 59.0549 | 0.2809 | [27 empty] | Total dissolved solids | mg/L | 253 | 266 | 259.5 | 5.0096 | 281 | 344.9839 | -22.7701 | 9.2657 | 344.0302 | 24.5706 | Total dissolved solids | mg/L | 273 | 318 | 435.5 | -36.9497 | 4.5455 | 433.835 | 37.0729 | Total dissolved solids | mg/L | 261 | 292 | 309.0769 | -5.8483 | 8.7413 | 308.6068 | 15.4263 | Total dissolved solids | mg/L | 246 | 285 | 304.8235 | -6.9556 | 13.986 | 304.231 | 19.1404 | UV254 F, cm-1 | 0.2035 | 0.2035 | 0.2035 | 0.2035 | UV254 F, cm-1 | 0.2035 | 0.2035 | 0.2035 | 0.2035 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 8.5 | 55.9325 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.192 | 0.215 | 0.2035 | 11.3022 | 1998-07-15 | 16:00 | 7.5 | 24 | 60 | 35.5 | 340 | 7.62 | 3.24 | 10.86 | 0.25989 | 0.70166 | 30.3076 | 17.3922 | 17.7035 | 0 | 0 | 0 | 0 | 47.75 | 0.37075 | 1998-07-17 | 8:30 | 23 | 24 | 59 | 60 | 321 | 7.26 | 3.02 |  | 10.28 | 0.24537 | 0.70623 | 30.2257 | 16.5706 | 16.8671 | 317.9067 | 272.7275 | 316.8849 | 0.44668 | 59.0533 | 0.28562 | [27 empty] | Total hardness | mg/L as CaCO3 | 294 | 286 | 290 | 2.7586 | 328 | 322.2581 | 1.7506 | 3.3333 | 321.8982 | 9.9094 | Total hardness | mg/L as CaCO3 | 332 | 400 | -68 | 117 | -10.6667 | -63.9016 | 619.5492 | Total hardness | mg/L as CaCO3 | 278 | 340 | 320.3077 | 5.7919 | 7.3333 | 319.8939 | 13.0962 | Total hardness | mg/L as CaCO3 | 268 | 300 | 315.0588 | -5.0196 | 10.6667 | 314.5848 | 14.8083 | UV254 p, cm-1 | 0.0475 | 0.07 | 0.029 | 0.028 | UV254 p, cm-1 | 0.0475 | 0.07 | 0.029 | 0.028 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.9538 | 3.1618 | 3.0578 | 6.7996 | 1998-07-15 | 16:30 | 8 | 24 | 60 | 36 | 340 | 7.6 | 3.68 | 11.28 | 0.25989 | 0.67376 | 29.1418 | 17.3466 | 17.657 | 0 | 0 | 0 | 0 | 48 | 0.36785 | 1998-07-17 | 9:30 | 24 | 24 | 59 | 60 | 321 | 7.13 | 2.81 |  | 9.94 | 0.24537 | 0.7173 | 31.2938 | 16.2738 | 16.565 | 318.4512 | 273.2107 | 317.4463 | 0.44738 | 59.0526 | 0.28051 | 7.63 | 7.58 | 7.61 | 272 | 282 | 302 | 321.5231 | -6.4646 | 4.8951 | 320.9731 | 15.2577 | 0.052 | 0.22 | 0.574 | 0.58791 | -2.4235 | 74.4472 | 0.58196 | 91.0647 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 240 | 254 | 247 | 5.668 | 305 | 314.7419 | -3.1941 | 7.8358 | 313.9862 | 21.3341 | Calcium hardness | mg/L as CaCO3 | 314 | 354 | -261 | 173.7288 | -17.1642 | -255.1085 | 223.0849 | Calcium hardness | mg/L as CaCO3 | 236 | 302 | 297.5385 | 1.4773 | 11.9403 | 296.9366 | 20.5218 | Calcium hardness | mg/L as CaCO3 | 226 | 268 | 287.7647 | -7.3749 | 15.6716 | 287.1425 | 21.2934 | BromideF, ug/L | 84.5 | 84.5 | 84.5 | 84.5 | BromideF, ug/L | 84.5 | 84.5 | 84.5 | 84.5 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 86 | 83 | 84.5 | 3.5503 | 1998-07-15 | 17:00 | 8.5 | 24 | 60 | 36 | 340 | 7.5 | 3.67 | 11.17 | 0.25989 | 0.67144 | 29.4387 | 17.1183 | 17.4247 | 0 | 0 | 0 | 0 | 48 | 0.36301 | 1998-07-17 | 10:30 | 25 | 24 | 58 | 60 | 321 | 7.18 | 3.11 |  | 10.29 | 0.24537 | 0.69776 | 30.1953 | 16.388 | 16.6812 | 317.4747 | 272.3668 | 316.4658 | 0.44603 | 58.554 | 0.28489 | 7.84 | 7.63 | 7.81 | 277 | 283 | 304 | 306.7781 | -0.91386 | 3.1469 | 306.4451 | 9.6086 | 0.05 | 0.213 | 0.567 | 0.55788 | 1.608 | 75.43 | 0.5522 | 90.9454 | [8 empty] | Turbidity | ntu | 0.084 | 0.089 | 0.0865 | 5.7803 | 0.213 | 0.4365 | -104.9296 | 55.641 | 0.4326 | 80.0044 | Turbidity | ntu | 0.119 | 0.488 | 1.069 | -119.0574 | 38.9744 | 1.0593 | 88.7658 | Turbidity | ntu | 0.08 | 0.214 | 0.30115 | -40.7261 | 58.9744 | 0.29899 | 73.2433 | Turbidity | ntu | 0.07 | 0.197 | 0.25382 | -28.8444 | 64.1026 | 0.25197 | 72.2191 | Bromidep, ug/L | 80 | 85 | 81 | 76 | Bromidep, ug/L | 80 | 85 | 81 | 76 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 5 | 6 | 5.5 | 18.1818 | 1998-07-16 | 9:20 | 24.8333 | 24 | 59 | 34.5 | 340 | 7.19 | 2.8 | 9.99 | 0.25989 | 0.71972 | 33.034 | 16.4108 | 16.7044 | 0 | 0 | 0 | 0 | 46.75 | 0.35731 | 1998-07-17 | 11:30 | 26 | 24 | 58 | 60 | 321 | 7.22 | 3.12 |  | 10.34 | 0.24537 | 0.69826 | 30.0445 | 16.4793 | 16.7741 | 317.5033 | 272.3864 | 316.4885 | 0.4461 | 58.5539 | 0.28647 | 7.9 | 7.74 | 7.86 | 271 | 284 | 298 | 320.7115 | -7.6213 | 5.2448 | 320.1525 | 15.3528 | 0.049 | 0.213 | 0.55 | 0.56103 | -2.0052 | 75.9214 | 0.55527 | 91.1755 | [8 empty] | Ammonia | mg NH3-N / L | 0.13 | BMRL | 0.13 | #VALUE! | NA | -0.063548 | #VALUE! | -85.7143 | -0.061389 | 311.7638 | Ammonia | mg NH3-N / L | 0.06 | NA | 0.185 | #VALUE! | 14.2857 | 0.18372 | 67.3415 | Ammonia | mg NH3-N / L | 0.06 | NA | 0.079231 | #VALUE! | 14.2857 | 0.079043 | 24.0917 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 330 | 330 | 330 | 330 | AlkF, mg/L CaCO3 | 330 | 330 | 330 | 330
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.15 | 0.7 | 0.925 | 48.6486 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 13:00 | 27.5 | 24 | 58 | 60 | 321 | 7 | 2.95 |  | 9.95 | 0.24537 | 0.70352 | 31.2613 | 15.9771 | 16.263 | 317.7457 | 272.6215 | 316.7617 | 0.44632 | 58.5537 | 0.27775 | 7.88 | 7.77 | 7.8 |  | 283 | 303 |  | #VALUE! |  |  |  | 0.047 | 0.221 | 0.57 | 0.57486 | -0.85192 | 76.9042 | 0.5691 | 91.7414 | [8 empty] | Total organic carbon | mg/L | 1.9 | 2.2 | 2.05 | 14.6341 | 14.9 | 16.8887 | -13.347 | 69.1729 | 16.7232 | 87.7416 | Total organic carbon | mg/L | 2.5 | 21.6 | 54.375 | -151.7361 | 62.406 | 53.8435 | 95.3569 | Total organic carbon | mg/L | 1.2 | 10.1 | 11.6808 | -15.6512 | 81.9549 | 11.5783 | 89.6358 | Total organic carbon | mg/L | 1.4 | 8 | 9.1206 | -14.0074 | 78.9474 | 9.0428 | 84.5181 | Alkp, mg/L CaCO3 | 258 | 354 | 268 | 214 | Alkp, mg/L CaCO3 | 258 | 354 | 268 | 214
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.85 | 5.3 | 4.575 | 31.694 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 14:00 | 28.5 | 24 | 58 | 60 | 321 | 7.2 | 3.54 |  | 10.74 | 0.24537 | 0.67039 | 28.8883 | 16.4336 | 16.7277 | 316.1118 | 271.195 | 315.1043 | 0.44413 | 58.5559 | 0.28567 | 7.79 | 7.75 | 7.78 |  | 284 | 312 |  | #VALUE! |  |  |  | 0.047 | 0.22 | 0.531 | 0.52181 | 1.7316 | 76.9042 | 0.51648 | 90.8999 | [8 empty] | UV254 | cm-1 | 0.047 | 0.048 | 0.0475 | 2.1053 | 0.552 | 0.55073 | 0.23083 | 76.6585 | 0.54511 | 91.2862 | UV254 | cm-1 | 0.07 | 1.519 | 1.7388 | -14.4668 | 65.602 | 1.7217 | 95.9341 | UV254 | cm-1 | 0.029 | 0.371 | 0.36458 | 1.7313 | 85.7494 | 0.3613 | 91.9733 | UV254 | cm-1 | 0.028 | 0.289 | 0.28609 | 1.0075 | 86.2408 | 0.28349 | 90.1231 | T-HdF, mg/L CaCO3 | 300 | 300 | 300 | 300 | T-HdF, mg/L CaCO3 | 300 | 300 | 300 | 300
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 15:00 | 29.5 | 24 | 58 | 60 | 321 | 7.3 | 3.58 |  | 10.88 | 0.24537 | 0.67096 | 28.5037 | 16.6619 | 16.96 | 316.1489 | 271.2146 | 315.1271 | 0.44423 | 58.5558 | 0.28964 | 7.85 | 7.53 | 7.81 |  | 282 | 305 |  | #VALUE! |  |  |  | 0.046 | 0.217 | 0.519 | 0.52466 | -1.0904 | 77.3956 | 0.51922 | 91.1405 | [8 empty] | SUVA | L/(mg*m) | 2.4737 | 2.1818 | 2.3278 | 12.5385 | 3.7047 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.8 | 7.0324 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.4167 | 3.6733 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2 | 3.6125 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 290 | 332 | 278 | 268 | T-Hdp, mg/L CaCO3 | 290 | 332 | 278 | 268
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 9 | 8.78 | 8.89 | 2.4747 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-17 | 16:00 | 30.5 | 24 | 58 | 60 | 321 | 7.2 | 3.44 |  | 10.64 | 0.24537 | 0.67669 | 29.1692 | 16.4336 | 16.7277 | 316.4249 | 271.4637 | 315.4164 | 0.44457 | 58.5554 | 0.28567 | 7.8 | 7.5 | 7.79 | 273 | 282 | 297 | 313.2093 | -5.4577 | 4.5455 | 312.7584 | 12.7122 | 0.045 | 0.216 | 0.509 | 0.53524 | -5.156 | 77.887 | 0.52975 | 91.5054 | [8 empty] | Bromide | mg/L | 80 | NR | 80 | #VALUE! | --- | 94.5161 | --- | 5.3254 | 94.3542 | 15.2131 | Bromide | mg/L | 85 | --- | 78.75 | --- | -0.59172 | 78.814 | -7.8488 | Bromide | mg/L | 81 | --- | 87.7308 | --- | 4.142 | 87.6649 | 7.6027 | Bromide | mg/L | 76 | --- | 88.5 | --- | 10.0592 | 88.3741 | 14.0019 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 9:30 | 48 | 24 | 58 | 60 | 321 | 7.23 | 3.15 |  | 10.38 | 0.24537 | 0.69653 | 29.9249 | 16.5021 | 16.7974 | 317.4178 | 272.3118 | 316.4018 | 0.44598 | 58.554 | 0.28687 | [27 empty] | SDS-Cl2 dose | mg/L | 3 | 2 | 2.5 | 40 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 247 | 314 | 236 | 226 | Ca-Hdp, mg/L CaCO3 | 247 | 314 | 236 | 226
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 415 | 530 | 472.5 | 24.3386 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 10:30 | 49 | 24 | 58 | 60 | 321 | 7.1 | 3.27 |  | 10.37 | 0.24537 | 0.68467 | 29.9547 | 16.2054 | 16.4953 | 316.8128 | 271.8088 | 315.8174 | 0.44506 | 58.5549 | 0.28171 | 7.69 | 7.55 | 7.67 | 275 | 284 | 305 | 309.8838 | -1.6012 | 3.8462 | 309.498 | 11.1464 | 0.045 | 0.218 | 0.538 | 0.54764 | -1.7925 | 77.887 | 0.54208 | 91.6987 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.28 | 0.72 | 1 | 56 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.57 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.03 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.18 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 150 | 200 | 175 | 28.5714 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 11:30 | 50 | 24 | 58 | 60 | 321 | 7.09 | 3.2 |  | 10.29 | 0.24537 | 0.68902 | 30.1953 | 16.1825 | 16.4721 | 317.0289 | 271.9954 | 316.0343 | 0.44536 | 58.5546 | 0.28131 | 7.67 | 7.61 | 7.7 | 276 | 285 | 305 | 308.1562 | -1.0348 | 3.4965 | 307.8011 | 10.3317 | 0.044 | 0.211 | 0.545 | 0.55689 | -2.1821 | 78.3784 | 0.55123 | 92.0178 | [8 empty] | SDS-Cl2 demand | mg/L | 1.72 | 1.28 | 1.5 | 29.3333 | --- | 11.4194 | --- | 67.2131 | 11.3087 | 86.7359 | SDS-Cl2 demand | mg/L | 1.43 | --- | 40.7425 | --- | 68.7432 | 40.3397 | 96.4551 | SDS-Cl2 demand | mg/L | 0.97 | --- | 7.9027 | --- | 78.7978 | 7.8349 | 87.6195 | SDS-Cl2 demand | mg/L | 0.82 | --- | 6.3421 | --- | 82.0765 | 6.2864 | 86.956 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 19 | 27 | 23 | 34.7826 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 12:30 | 51 | 24 | 58 | 60 | 321 | 7.07 | 3.07 |  | 10.14 | 0.24537 | 0.69724 | 30.6568 | 16.1369 | 16.4256 | 317.4379 | 272.3487 | 316.4448 | 0.44593 | 58.5541 | 0.28052 | 7.84 | 7.52 | 7.96 | 269 | 285 | 300 | 325.1498 | -8.3833 | 5.9441 | 324.5315 | 17.1113 | 0.045 | 0.212 | 0.538 | 0.56851 | -5.6719 | 77.887 | 0.56275 | 92.0035 | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 99.8083 | 92.8648 | 105.1717 | 87.7909 | Qp/QT (THM4), % | 127.4156 | 118.5516 | 134.2626 | 112.0742
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 3.8 | 4.5 | 4.15 | 16.8675 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 13:30 | 52 | 24 | 58 | 60 | 321 | 7.05 | 3.03 |  | 10.08 | 0.24537 | 0.6994 | 30.8452 | 16.0912 | 16.3792 | 317.5444 | 272.4426 | 316.5539 | 0.44607 | 58.5539 | 0.27973 | 7.83 | 7.6 | 7.87 | 270 | 284 | 294 | 323.2277 | -9.9414 | 5.5944 | 322.6432 | 16.3162 | 0.044 | 0.211 | 0.536 | 0.57461 | -7.2041 | 78.3784 | 0.56879 | 92.2642 | [8 empty] | SDS-Chlorination pH | --- | 8.66 | 8.76 | 8.71 | 1.1481 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.87 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.91 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.4 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | NA | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 14:30 | 53 | 24 | 58 | 60 | 321 | 7.11 | 3.05 |  | 10.16 | 0.24537 | 0.6998 | 30.5945 | 16.2282 | 16.5186 | 317.5701 | 272.4573 | 316.5709 | 0.44613 | 58.5539 | 0.28211 | 7.71 | 7.52 | 7.7 | 266 | 286 | 315 | 332.623 | -5.5946 | 6.993 | 331.8851 | 19.8518 | 0.045 | 0.212 | 0.556 | 0.57299 | -3.0552 | 77.887 | 0.56714 | 92.0654 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 14.9328 | 19.6504 | NA | 14.9886 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 172.8 | 231.5 | 202.15 | 29.0378 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 15:30 | 54 | 24 | 58 | 60 | 321 | 7.13 | 3.38 |  | 10.51 | 0.24537 | 0.6784 | 29.5423 | 16.2738 | 16.565 | 316.5035 | 271.5397 | 315.5048 | 0.44464 | 58.5554 | 0.2829 | 7.81 | 7.61 | 7.82 | 271 | 285 | 301 | 317.642 | -5.5289 | 5.2448 | 317.124 | 14.5445 | 0.045 | 0.212 | 0.537 | 0.53785 | -0.1584 | 77.887 | 0.53238 | 91.5473 | [8 empty] | SDS-TOX | mg Cl- /L | 150 | 130 | 140 | 14.2857 | --- | 1212.5806 | --- | 70.3704 | 1200.6149 | 88.3393 | SDS-TOX | mg Cl- /L | 180 | --- | 3836.25 | --- | 61.9048 | 3798.7877 | 95.2616 | SDS-TOX | mg Cl- /L | 100 | --- | 816.3462 | --- | 78.836 | 809.3407 | 87.6443 | SDS-TOX | mg Cl- /L | 84 | --- | 655.3235 | --- | 82.2222 | 649.5683 | 87.0683 | SDS-TOXb, ug Cl- /L | 140.6375 | 200.8705 | NA | 131.4324 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 3.5 | 3.3 | 3.4 | 5.8824 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-18 | 16:30 | 55 | 24 | 58 | 60 | 321 | 7.12 | 3.58 |  | 10.7 | 0.24537 | 0.66542 | 29 | 16.251 | 16.5418 | 315.858 | 270.9871 | 314.8627 | 0.44373 | 58.5563 | 0.28249 | 7.71 | 7.6 |  | 270 | 285 | 306 | 317.8212 | -3.8631 | 5.5944 | 317.2909 | 14.9046 | 0.042 | 0.211 | 0.533 | 0.5247 | 1.5581 | 79.3612 | 0.51934 | 91.9128 | [8 empty] | SDS-CHCl3 | mg/L | 40 | 32 | 36 | 22.2222 | --- | 484.3871 | --- | 79.4286 | 479.3849 | 92.4904 | SDS-CHCl3 | mg/L | 25 | --- | 1900 | --- | 85.7143 | 1880.7886 | 98.6708 | SDS-CHCl3 | mg/L | 44 | --- | 295.9231 | --- | 74.8571 | 293.4594 | 85.0064 | SDS-CHCl3 | mg/L | 18 | --- | 248.8824 | --- | 89.7143 | 246.5566 | 92.6994 | SDS-CDb, mg/L | 1.5059 | 1.6544 | NA | 1.2785 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7 | [13 empty] | SDS-DCAA* | mg/L | 34 | 45 | 39.5 | 27.8481 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 14:30 | 77 | 24 | 60 | 61 | 321 | 6.64 | 0.61 |  | 7.25 | 0.24537 | 0.91586 | 43.2759 | 15.1554 | 15.4266 | 328.7119 | 282.0762 | 327.7472 | 0.46153 | 60.0385 | 0.25695 | [27 empty] | SDS-BDCM | mg/L | 22 | 19 | 20.5 | 14.6341 | --- | 28.5645 | --- | 10.8696 | 28.4745 | 28.0059 | SDS-BDCM | mg/L | 18 | --- | 80.5 | --- | 21.7391 | 79.8596 | 77.4604 | SDS-BDCM | mg/L | 21 | --- | 24.8462 | --- | 8.6957 | 24.8085 | 15.3517 | SDS-BDCM | mg/L | 16 | --- | 26.2941 | --- | 30.4348 | 26.1904 | 38.909 | TOCb, mg/L | 2.0588 | 2.7961 | NA | 2.041 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 8.3 | 22 | 15.15 | 90.429 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 15:15 | 77.75 | 24 | 60 | 61 | 321 | 6.55 | 0.73 |  | 7.28 | 0.24537 | 0.89973 | 43.0934 | 14.95 | 15.2175 | 327.8374 | 281.3372 | 326.8886 | 0.46026 | 60.0397 | 0.25346 | [27 empty] | SDS-DBCM | mg/L | 13 | 13 | 13 | 0 | --- | -15.5484 | --- | -213.253 | -15.2299 | 185.3584 | SDS-DBCM | mg/L | 15 | --- | -120.625 | --- | -261.4458 | -119.2354 | 112.5802 | SDS-DBCM | mg/L | 12 | --- | -3.0962 | --- | -189.1566 | -2.9485 | 506.9836 | SDS-DBCM | mg/L | 15 | --- | -0.95588 | --- | -261.4458 | -0.79515 | 1986.4355 | UV254 b, cm-1 | 0.047799 | 0.079526 | NA | 0.049427 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2-11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 16:00 | 78.5 | 24 | 60 | 61 | 321 | 6.5 | 0.6 |  | 7.1 | 0.24537 | 0.91549 | 44.2113 | 14.8359 | 15.1014 | 328.6734 | 282.0609 | 327.7295 | 0.4614 | 60.0386 | 0.25153 | 8.03 | 7.75 | 7.78 | 274 | 282 | 310 | 416 | -34.1935 | 4.1958 | 414.5623 | 33.9062 | 0.053 | 0.199 | 0.984 | 1.8339 | -86.3736 | 73.9558 | 1.8159 | 97.0813 | [8 empty] | SDS-CHBr3 | mg/L | 1.9 | 2.6 | 2.25 | 31.1111 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.4 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.9 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 80.0086 | 84.9643 | NA | 77.0378 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 16:45 | 79.25 | 24 | 60 | 61 | 321 | 6.5 | 0.59 |  | 7.09 | 0.24537 | 0.91678 | 44.275 | 14.8359 | 15.1014 | 328.7425 | 282.1203 | 327.7985 | 0.4615 | 60.0385 | 0.25153 | 8.97 | 7.67 |  | 284 | 294 | 320 | 308.0339 | 3.7394 | 0.6993 | 307.7906 | 7.7295 | 0.056 | 0.204 | 1.073 | 1.8285 | -70.4101 | 72.4816 | 1.8106 | 96.907 | [8 empty] | SDS-THM4 | mg/L | 76.9 | 66.6 | 71.75 | 14.3554 | --- | 492.3952 | --- | 64.5066 | 487.7024 | 85.2882 | SDS-THM4 | mg/L | 62 | --- | 1813.875 | --- | 69.3297 | 1795.9251 | 96.5477 | SDS-THM4 | mg/L | 78.4 | --- | 316.3808 | --- | 61.2169 | 314.0535 | 75.0361 | SDS-THM4 | mg/L | 53.9 | --- | 271.9147 | --- | 73.3366 | 269.7185 | 80.0162 | Alkb, mg/L CaCO3 | 258.138 | 352.2875 | NA | 228.1626 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 5 | 6.7 | 5.85 | 29.0598 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 17:30 | 80 | 24 | 60 | 61 | 321 | 6.73 | 0.62 |  | 7.35 | 0.24537 | 0.91565 | 42.6735 | 15.3609 | 15.6357 | 328.7124 | 282.0651 | 327.7344 | 0.46158 | 60.0384 | 0.26043 | 7.85 | 7.56 | 7.56 |  | 298 | 321 |  | #VALUE! |  |  |  | 0.055 | 0.202 | 1.104 | 1.8154 | -64.4424 | 72.973 | 1.797 | 96.9393 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 290.0192 | 329.7167 | NA | 271.9069 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 19:00 | 81.5 | 24 | 60 | 61 | 321 | 6.86 | 0.66 |  | 7.52 | 0.24537 | 0.91223 | 41.6862 | 15.6576 | 15.9378 | 328.5469 | 281.9066 | 327.5501 | 0.46142 | 60.0386 | 0.26546 | 7.86 | 7.55 | 7.69 |  | 298 | 320 |  | #VALUE! |  |  |  | 0.055 | 0.204 | 1.188 | 1.747 | -47.0539 | 72.973 | 1.7289 | 96.8188 | [8 empty] | SDS-DCAA* | mg/L | 8.4 | 8.3 | 8.35 | 1.1976 | --- | 108.8339 | --- | 78.8608 | 107.7129 | 92.2479 | SDS-DCAA* | mg/L | 10 | --- | 378.75 | --- | 74.6835 | 374.9717 | 97.3331 | SDS-DCAA* | mg/L | 6.3 | --- | 70.1462 | --- | 84.0506 | 69.5218 | 90.9381 | SDS-DCAA* | mg/L | 4.1 | --- | 56.1588 | --- | 89.6203 | 55.6344 | 92.6305 | Ca-Hdb, mg/L CaCO3 | 247.0403 | 310.7178 | NA | 231.1278 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 19:45 | 82.25 | 24 | 60 | 61 | 321 | 6.83 | 0.65 |  | 7.48 | 0.24537 | 0.9131 | 41.9144 | 15.5891 | 15.8681 | 328.5894 | 281.9468 | 327.5969 | 0.46146 | 60.0385 | 0.2643 | 7.88 | 7.6 | 7.73 | 283 | 295 | 320 | 317.5231 | 0.77404 | 1.049 | 317.1558 | 10.7694 | 0.058 | 0.204 | 1.256 | 1.7324 | -37.9275 | 71.4988 | 1.7146 | 96.6172 | [8 empty] | SDS-TCAA* | mg/L | 3.9 | 3.8 | 3.85 | 2.5974 | --- | 40.3016 | --- | 74.5875 | 39.895 | 90.3497 | SDS-TCAA* | mg/L | 4.5 | --- | 137.625 | --- | 70.297 | 136.261 | 96.6975 | SDS-TCAA* | mg/L | 2.7 | --- | 26.6423 | --- | 82.1782 | 26.4082 | 89.7759 | SDS-TCAA* | mg/L | 1.9 | --- | 21.3853 | --- | 87.4587 | 21.189 | 91.0331
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 1.2 | 3.9 | 2.55 | 105.8824 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 20:30 | 83 | 24 | 60 | 61 | 321 | 6.86 | 0.7 |  | 7.56 | 0.24537 | 0.90741 | 41.4603 | 15.6576 | 15.9378 | 328.2885 | 281.6848 | 327.2925 | 0.46106 | 60.0389 | 0.26546 |  |  |  |  | 288 | 321 |  | #VALUE! | [19 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 45.8 | 70.3 | 58.05 | 42.205 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-19 | 23:30 | 86 | 24 | 59 | 60 | 321 | 6.89 | 0.76 |  | 7.65 | 0.24537 | 0.90065 | 40.9608 | 15.7261 | 16.0075 | 327.9315 | 281.3748 | 326.9322 | 0.46057 | 59.0394 | 0.27113 | [27 empty] | SDS-DBAA* | mg/L | 2.6 | 2.7 | 2.65 | 3.7736 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 2.2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 3.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 50.8 | 77 | 63.9 | 41.0016 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 9:00 | 95.5 | 24 | 59 | 60 | 321 | 6.31 | 0.41 |  | 6.72 | 0.24537 | 0.93899 | 46.7679 | 14.4022 | 14.6599 | 329.9105 | 283.1469 | 328.9913 | 0.46304 | 59.037 | 0.24832 | 8.16 | 7.82 | 8.03 | 285 | 298 | 320 | 301.3902 | 5.8155 | 0.34965 | 301.2291 | 5.3876 | 0.066 | 0.204 | 1.727 | 2.3197 | -34.3172 | 67.5676 | 2.2975 | 97.1273 | [8 empty] | SDS-BCAA* | mg/L | 5.2 | 4.4 | 4.8 | 16.6667 | --- | 8.1871 | --- | 17.9487 | 8.1493 | 41.0993 | SDS-BCAA* | mg/L | 5 | --- | 15.625 | --- | 14.5299 | 15.5161 | 67.7755 | SDS-BCAA* | mg/L | 4.3 | --- | 7.2808 | --- | 26.4957 | 7.2516 | 40.7029 | SDS-BCAA* | mg/L | 3.2 | --- | 7.0971 | --- | 45.2991 | 7.0578 | 54.6601 | Qp/QT (HAA5), % | 9.375 | 9.7944 | 8.8913 | 8.2569 | Qp/QT (HAA5), % | 71.875 | 75.0907 | 68.1668 | 63.3028
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 9:45 | 96.25 | 24 | 59 | 60 | 321 | 6.34 | 0.63 |  | 6.97 | 0.24537 | 0.90961 | 45.0545 | 14.4707 | 14.7296 | 328.3374 | 281.793 | 327.4181 | 0.46085 | 59.0392 | 0.24949 | 8.12 | 7.84 | 7.97 | 284 | 295 | 317 | 306.127 | 3.43 | 0.6993 | 305.9085 | 7.1618 | 0.063 | 0.201 | 1.765 | 1.6174 | 8.3614 | 69.0418 | 1.6021 | 96.0676 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 189.925 | 188.4231 | 191.147 | 189.9092 | SDS-THM4b, ug/L | 108.425 | 96.9104 | 117.7935 | 108.3037
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 10:15 | 96.75 | 24 | 59 | 60 | 321 | 6.29 | 0.61 |  | 6.9 | 0.24537 | 0.91159 | 45.5217 | 14.3566 | 14.6135 | 328.4367 | 281.8845 | 327.5245 | 0.46096 | 59.039 | 0.24752 | 8.06 | 7.79 | 7.83 |  | 296 | 320 |  | #VALUE! |  |  |  | 0.061 | 0.201 | 1.723 | 1.6729 | 2.9086 | 70.0246 | 1.6571 | 96.3189 | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-20 | 12:15 | 98.75 | 24 | 60 | 60 | 321 | 6.25 | 0.58 |  | 6.83 | 0.24537 | 0.91508 | 45.9985 | 14.2653 | 14.5205 | 328.6179 | 282.0451 | 327.7111 | 0.46119 | 59.5388 | 0.24388 | 8.01 | 7.71 | 7.88 | 277 | 287 | 311 | 382.9828 | -23.1456 | 3.1469 | 381.951 | 27.4776 | 0.061 | 0.203 | 1.721 | 1.7391 | -1.0494 | 70.0246 | 1.7227 | 96.4591 | [8 empty] | SDS-DCBAA | mg/L | 2.6 | 2 | 2.3 | 26.087 | --- | 3.1065 | --- | 9.8039 | 3.0975 | 25.7455 | SDS-DCBAA | mg/L | 2.3 | --- | 5.425 | --- | 9.8039 | 5.393 | 57.352 | SDS-DCBAA | mg/L | 2.2 | --- | 2.8731 | --- | 13.7255 | 2.8665 | 23.2512 | SDS-DCBAA | mg/L | 1.8 | --- | 2.9029 | --- | 29.4118 | 2.8918 | 37.7557 | SDS-TOXb, ug Cl- /L | 441.3281 | 443.8513 | 439.3798 | 440.422 | SDS-TOXb, ug Cl- /L | 233.5156 | 252.8597 | 218.5785 | 226.5688
[44 empty] | 1998-07-20 | 13:15 | 99.75 | 24 | 60 | 60 | 321 | 6.2 | 0.49 |  | 6.69 | 0.24537 | 0.92676 | 46.9821 | 14.1512 | 14.4044 | 329.2371 | 282.5829 | 328.336 | 0.46204 | 59.538 | 0.24194 | [27 empty] | SDS-HAA5 | mg/L | 14.9 | 14.8 | 14.85 | 0.6734 | --- | 154.2048 | --- | 74.4186 | 152.6502 | 90.2719 | SDS-HAA5 | mg/L | 16.7 | --- | 533.575 | --- | 71.2317 | 528.279 | 96.8388 | SDS-HAA5 | mg/L | 12.5 | --- | 100.0962 | --- | 78.4668 | 99.2395 | 87.4042 | SDS-HAA5 | mg/L | 9 | --- | 81.1324 | --- | 84.4961 | 80.4057 | 88.8068 | SDS-CDb, mg/L | 4.2867 | 4.267 | 4.2545 | 4.265 | SDS-CDb, mg/L | 2.3648 | 2.2134 | 2.1176 | 2.198
[44 empty] | 1998-07-20 | 14:00 | 100.5 | 24 | 59 | 60 | 321 | 7.17 | 5.87 |  | 13.04 | 0.24537 | 0.54985 | 23.6166 | 16.3651 | 16.658 | 310.2363 | 266.158 | 309.2517 | 0.43586 | 59.0641 | 0.28203 | [27 empty] | SDS-HAA6 | mg/L | 20.1 | 19.2 | 19.65 | 4.5802 | --- | 162.3919 | --- | 69.2488 | 160.7995 | 87.7798 | SDS-HAA6 | mg/L | 21.7 | --- | 549.2 | --- | 66.0407 | 543.7952 | 96.0095 | SDS-HAA6 | mg/L | 16.8 | --- | 107.3769 | --- | 73.7089 | 106.4911 | 84.224 | SDS-HAA6 | mg/L | 12.2 | --- | 88.2294 | --- | 80.9077 | 87.4635 | 86.0513 | TOCb, mg/L | 6.2188 | 6.2435 | 6.1654 | 6.2165 | TOCb, mg/L | 3.3438 | 3.5337 | 2.9349 | 3.3266
[44 empty] | 1998-07-20 | 14:20 | 100.8333 | 24 | 60 | 60 | 321 | 6.46 | 7.2 |  | 13.66 | 0.24537 | 0.47291 | 22.4993 | 14.7446 | 15.0084 | 306.5582 | 263.0869 | 305.6833 | 0.43034 | 59.5697 | 0.25195 | [27 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.18887 | 0.19042 | 0.18798 | 0.18901 | UV254 b, cm-1 | 0.091375 | 0.10325 | 0.084549 | 0.092404
[44 empty] | 1998-07-20 | 15:15 | 101.75 | 24 | 60 | 60 | 321 | 6.2 | 7.14 |  | 13.34 | 0.24537 | 0.46477 | 23.063 | 14.1512 | 14.4044 | 306.1638 | 262.7792 | 305.3258 | 0.42966 | 59.5703 | 0.2418 | 7.8 | 7.63 | 7.82 | 256 | 283 | 295 | 312.0504 | -5.7798 | 10.4895 | 311.5091 | 17.8194 | 0.027 | 0.2 | 0.404 | 0.35676 | 11.6923 | 86.7322 | 0.35358 | 92.3638 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 84.0781 | 84.549 | 84.1888 | 83.7982 | Bromideb, ug/L | 81.2656 | 84.8755 | 82.1142 | 79.1193
[44 empty] | 1998-07-20 | 16:00 | 102.5 | 24 | 60 | 60 | 321 | 6.22 | 7.02 |  | 13.24 | 0.24537 | 0.46979 | 23.2447 | 14.1968 | 14.4508 | 306.3983 | 262.9781 | 305.557 | 0.43 | 59.57 | 0.24259 | 7.94 | 7.69 | 7.73 | 278 | 298 | 304 | 293.0883 | 3.5894 | 2.7972 | 292.9421 | 5.1007 | 0.026 | 0.2 | 0.375 | 0.36077 | 3.7941 | 87.2236 | 0.35753 | 92.7279 | [47 empty] | Alkb, mg/L CaCO3 | 323.25 | 332.3507 | 324.4874 | 320.422 | Alkb, mg/L CaCO3 | 278.25 | 348.0218 | 287.7366 | 256.5688
[44 empty] | 1998-07-20 | 16:30 | 103 | 24 | 59 | 60 | 321 | 6.24 | 6.95 |  | 13.19 | 0.24537 | 0.47309 | 23.3366 | 14.2425 | 14.4973 | 306.553 | 263.1085 | 305.7084 | 0.43022 | 59.0698 | 0.24543 | 7.86 | 7.67 | 7.73 | 274 | 297 | 305 | 296.7741 | 2.697 | 4.1958 | 296.5527 | 7.605 | 0.026 | 0.202 | 0.363 | 0.36287 | 0.036665 | 87.2236 | 0.35959 | 92.7696 | [47 empty] | T-Hdb, mg/L CaCO3 | 299.0625 | 303.1342 | 298.0439 | 297.3578 | T-Hdb, mg/L CaCO3 | 292.8125 | 324.029 | 285.0033 | 279.7431
[44 empty] | 1998-07-20 | 17:00 | 103.5 | 24 | 59 | 60 | 321 | 6.22 | 6.91 |  | 13.13 | 0.24537 | 0.47372 | 23.4478 | 14.1968 | 14.4508 | 306.5815 | 263.1353 | 305.7397 | 0.43025 | 59.0697 | 0.24464 | 7.79 | 7.64 | 7.72 | 276 | 303 | 310 | 295.0014 | 4.8382 | 3.4965 | 294.8174 | 6.3827 | 0.026 | 0.2 | 0.363 | 0.36328 | -0.075947 | 87.2236 | 0.36001 | 92.7779 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 266.0312 | 272.5054 | 265.1548 | 264.5321 | Ca-Hdb, mg/L CaCO3 | 252.9062 | 302.5417 | 246.1866 | 241.4128
[44 empty] | 1998-07-20 | 17:30 | 104 | 24 | 59 | 60 | 321 | 6.3 | 6.92 |  | 13.22 | 0.24537 | 0.47655 | 23.2814 | 14.3794 | 14.6367 | 306.718 | 263.243 | 305.8648 | 0.43048 | 59.0695 | 0.24779 | 7.79 | 7.65 | 7.7 | 259 | 287 | 298 | 310.5809 | -4.2218 | 9.4406 | 310.0748 | 16.4718 | 0.026 | 0.201 | 0.361 | 0.3651 | -1.1349 | 87.2236 | 0.36177 | 92.8131 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-07-20 | 18:00 | 104.5 | 24 | 59 | 60 | 321 | 6.12 | 6.93 |  | 13.05 | 0.24537 | 0.46897 | 23.5977 | 13.9686 | 14.2185 | 306.3541 | 262.952 | 305.5266 | 0.42988 | 59.0701 | 0.24071 | 7.81 | 7.68 | 7.72 | 273 | 298 | 306 | 297.4805 | 2.7841 | 4.5455 | 297.2472 | 8.1572 | 0.025 | 0.201 | 0.361 | 0.36114 | -0.037774 | 87.715 | 0.35793 | 93.0154 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-07-21 | 8:15 | 118.75 | 24 | 59 | 60 | 321 | 6.52 | 6.27 |  | 12.79 | 0.24537 | 0.50977 | 24.0977 | 14.8816 | 15.1478 | 308.2893 | 264.5653 | 307.4012 | 0.4328 | 59.0672 | 0.25645 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-07-21 | 9:00 | 119.5 | 24 | 59 | 60 | 321 | 6.4 | 11.9 |  | 18.3 | 0.24537 | 0.34973 | 16.541 | 14.6077 | 14.869 | 300.9211 | 258.2561 | 300.0704 | 0.4224 | 59.0776 | 0.25169 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-07-21 | 9:30 | 120 | 24 | 59 | 60 | 321 | 6.64 | 13.51 |  | 20.15 | 0.24537 | 0.32953 | 14.9305 | 15.1554 | 15.4266 | 300.0267 | 257.4607 | 299.1462 | 0.42126 | 59.0787 | 0.26112 | 7.51 | 7.45 | 7.44 | 258 | 297 | 288 | 299.7617 | -4.0839 | 9.7902 | 299.3297 | 13.8074 | 0.025 | 0.22 | 0.306 | 0.29123 | 4.8266 | 87.715 | 0.28848 | 91.3338 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-07-21 | 10:00 | 120.5 | 24 | 58 | 59 | 321 | 6.53 | 14.34 |  | 20.87 | 0.24537 | 0.31289 | 14.3809 | 14.9044 | 15.1711 | 299.2814 | 256.8338 | 298.4179 | 0.42016 | 58.0798 | 0.26121 | 7.88 | 7.79 | 7.81 | 256 | 296 | 288 | 299.6611 | -4.049 | 10.4895 | 299.217 | 14.4434 | 0.024 | 0.221 | 0.282 | 0.28524 | -1.1485 | 88.2064 | 0.28258 | 91.5069 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-07-21 | 10:30 | 121 | 24 | 58 | 60 | 321 | 6.45 | 14.73 |  | 21.18 | 0.24537 | 0.30453 | 14.1558 | 14.7218 | 14.9852 | 298.9077 | 256.5224 | 298.056 | 0.41959 | 58.5804 | 0.25581 | 7.75 | 7.67 | 7.74 | 265 | 295 | 287 | 295.1955 | -2.8556 | 7.3427 | 294.8922 | 10.1366 | 0.024 | 0.217 | 0.287 | 0.2821 | 1.7074 | 88.2064 | 0.27951 | 91.4134 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-07-21 | 11:00 | 121.5 | 24 | 58 | 60 | 321 | 6.56 | 14.4 |  | 20.96 | 0.24537 | 0.31298 | 14.3149 | 14.9728 | 15.2408 | 299.2864 | 256.8347 | 298.4189 | 0.42018 | 58.5798 | 0.26017 | 7.88 | 7.69 | 7.83 | 257 | 288 | 287 | 299.2111 | -4.2547 | 10.1399 | 298.7798 | 13.9835 | 0.021 | 0.199 | 0.283 | 0.28664 | -1.2858 | 89.6806 | 0.28392 | 92.6037 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-07-21 | 12:00 | 122.5 | 24 | 58 | 60 | 321 | 6.7 | 14.29 |  | 20.99 | 0.24537 | 0.3192 | 14.293 | 15.2924 | 15.566 | 299.5685 | 257.0605 | 298.6813 | 0.42064 | 58.5794 | 0.26573 | 7.88 | 7.72 | 7.82 | 265 | 289 | 293 | 295.846 | -0.97135 | 7.3427 | 295.5241 | 10.3288 | 0.021 | 0.208 | 0.28 | 0.28907 | -3.2382 | 89.6806 | 0.28627 | 92.6642 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-07-21 | 13:30 | 124 | 24 | 58 | 60 | 321 | 6.33 | 13.83 |  | 20.16 | 0.24537 | 0.31399 | 14.9226 | 14.4479 | 14.7064 | 299.3226 | 256.8924 | 298.4859 | 0.42012 | 58.5799 | 0.25105 | 7.84 | 7.78 | 7.81 | 258 | 289 | 288 | 298.8156 | -3.7554 | 9.7902 | 298.4132 | 13.5427 | 0.019 | 0.208 | 0.282 | 0.28795 | -2.1084 | 90.6634 | 0.28529 | 93.3402 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-07-21 | 14:30 | 125 | 24 | 58 | 60 | 321 | 6.29 | 13.6 |  | 19.89 | 0.24537 | 0.31624 | 15.1388 | 14.3566 | 14.6135 | 299.4211 | 256.9815 | 298.5895 | 0.42024 | 58.5798 | 0.24946 | 7.73 | 7.64 | 7.73 | 252 | 282 | 288 | 301.725 | -4.7656 | 11.8881 | 301.2378 | 16.3452 | 0.022 | 0.2 | 0.285 | 0.28744 | -0.85746 | 89.1892 | 0.28484 | 92.2764 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-07-21 | 16:00 | 126.5 | 24 | 58 | 60 | 321 | 6.43 | 13.54 |  | 19.97 | 0.24537 | 0.32198 | 15.0741 | 14.6761 | 14.9387 | 299.6819 | 257.1892 | 298.8308 | 0.42067 | 58.5793 | 0.25502 | 7.81 | 7.71 | 7.85 | 255 | 286 | 289 | 300.7216 | -4.0559 | 10.8392 | 300.2636 | 15.0746 | 0.02 | 0.201 | 0.287 | 0.29064 | -1.269 | 90.172 | 0.28793 | 93.0539 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-07-21 | 16:45 | 127.25 | 24 | 58 | 60 | 321 | 6.48 | 13.57 |  | 20.05 | 0.24537 | 0.32319 | 15.01 | 14.7903 | 15.0549 | 299.7378 | 257.2313 | 298.8797 | 0.42077 | 58.5792 | 0.257
[44 empty] | 1998-07-22 | 8:00 | 118.5 | 24 | 58 | 60 | 321 | 6.48 | 13.57 | X | 20.05 | 0.24537 | 0.32319 | 15.01 | 14.7903 | 15.0549 | 299.7378 | 257.2313 | 298.8797 | 0.42077 | 58.5792 | 0.257
[44 empty] | 1998-07-22 | 14:30 |  | 24 | 62 | 62 | 330 | 6.5 | 7.85 |  | 14.35 | 0.25225 | 0.45296 | 21.9965 | 14.8359 | 15.1014 | 305.6234 | 262.3009 | 304.7701 | 0.42896 | 61.571 | 0.24527
[44 empty] | 1998-07-22 | 14:45 |  | 24 | 64 | 65 | 330 | 6.58 | 3.31 |  | 9.89 | 0.25225 | 0.66532 | 32.367 | 15.0185 | 15.2872 | 315.7882 | 271.0153 | 314.8955 | 0.44327 | 64.0567 | 0.23865
[44 empty] | 1998-07-22 | 15:00 |  | 24 | 46 | 46 | 330 | 4.75 | 1.95 |  | 6.7 | 0.25225 | 0.70896 | 48.2537 | 10.8416 | 11.0356 | 317.7887 | 272.9499 | 317.1433 | 0.44516 | 45.5548 | 0.24225
[44 empty] | 1998-07-22 | 15:30 |  | 24 | 76 | 76 | 330 | 8 | 4.3 |  | 12.3 | 0.25225 | 0.65041 | 25.8293 | 18.2596 | 18.5863 | 315.1739 | 270.319 | 314.0865 | 0.44311 | 75.5569 | 0.24599
[44 empty] | 1998-07-22 | 16:00 |  | 24 | 62 | 62 | 330 | 6.5 | 3.1 |  | 9.6 | 0.25225 | 0.67708 | 33.375 | 14.8359 | 15.1014 | 316.3638 | 271.5188 | 315.4805 | 0.44403 | 61.556 | 0.24533
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on U3: C. Rice: Cartridge filtration was the only membrane pretreatment employed.
Note on AA27: C. Rice 7/12/99: Consultant verified value.
Note on AA32: C. Rice 7/12/99: Consultant verified value.
Note on AA42: C. Rice 7/12/99: Consultant verified value.
Note on AA43: C. Rice 7/12/99: Consultant verified value.
Note on CY16: C. Rice: Alkalinity values verified by consultant.
Note on CY17: C. Rice: TDS values verified by consultant.
Note on CY25: C. Rice: Bromide values verified by consultant.
Note on CY33: C. Rice 7/12/99: Consultant verified (but did not explain) the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on CY37: C. Rice 7/12/99: Consultant verified (but did not explain) the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on DL33: C. Rice 7/12/99: Consultant verified the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on DL37: C. Rice 7/12/99: Consultant verified the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on DQ10: C. Rice: Consultant verified all water quality parameters for the 90% recovery run due to high mass balance closure errors. No explanation was given for the high mass balance errors which may suggest that the system was not operating at steady-state.
Note on DV33: C. Rice 7/12/99: Consultant verified the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on DV37: C. Rice 7/12/99: Consultant verified the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on EF33: C. Rice 7/12/99: Consultant verified the decrease in THM4 and CHCl3 concentrations with increasing recovery.
Note on EF37: C. Rice 7/12/99: Consultant verified the decrease in THM4 and CHCl3 concentrations with increasing recovery.

## 7450. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.22652 | [45 empty] | Recovery during sample collection (decimal) | 0.72 | [10 empty] | Recovery during sample collection (decimal) | 0.87 | [7 empty] | Recovery during sample collection (decimal) | 0.52 | [7 empty] | Recovery during sample collection (decimal) | 0.31 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-12-05 | 1998-12-19 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.62 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.76 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.65 | [7 empty] | Feed flow rate during sample collection (mL/min) | 15.05 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 12:00 | 13:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [6 empty] | SDS-THM4F, ug/L | 235.75 | 235.75 | 235.75 | 235.75 | SDS-THM4F, ug/L | 235.75 | 235.75 | 235.75 | 235.75 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 74.85 | 88 | 56.3 | 41 | SDS-THM4p, ug/L | 74.85 | 88 | 56.3 | 41 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.23 | 7.91 | 7.57 | 8.9828 | 1998-12-14 | 9:40 | 0 | 23 | 61 | 60 | 272 | 6.4 | 27.3 | 33.7 | 0.20791 | 0.18991 | 7.0712 | 14.6077 | 15.3151 | 0 | 0 | 0 | 0 | 60.5 | 0.25314 | 1998-12-15 | 8:30 | 0 | 23 | 64 | 62 | 272 | 7.27 | 3.35 |  | 10.62 | 0.20791 | 0.68456 | 24.6121 | 16.5934 | 17.397 | 395.0522 | 303.6761 | 392.6099 | 0.90155 | 62.0985 | 0.28015 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 66.3 | 66.3 | 66.3 | 66.3 | SDS-HAA5F, ug/L | 66.3 | 66.3 | 66.3 | 66.3 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 23 | 23 | 0 | 1998-12-14 | 10:00 | 0.33333 | 23 | 52 | 50 | 272 | 5.3 | 11.5 | 16.8 | 0.20791 | 0.31548 | 15.1905 | 12.097 | 12.6828 | 0 | 0 | 0 | 0 | 51 | 0.24868 | 1998-12-15 | 9:00 | 0.5 | 23 | 64 | 62 | 272 | 7.27 | 3.35 |  | 10.62 | 0.20791 | 0.68456 | 24.6121 | 16.5934 | 17.397 | 395.0522 | 303.6761 | 392.6099 | 0.90155 | 62.0985 | 0.28015 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 8.7 | 12.6 | 6.5 | 5.1 | SDS-HAA5p, ug/L | 8.7 | 12.6 | 6.5 | 5.1 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 448 | 438 | 443 | 2.2573 | 1998-12-14 | 10:15 | 0.58333 | 23 | 56 | 54 | 263 | 5.8 | 3.7 | 9.5 | 0.20103 | 0.61053 | 26.6842 | 13.2382 | 13.8793 | 0 | 0 | 0 | 0 | 55 | 0.25235 | 1998-12-15 | 9:20 | 0.83333 | 23 | 44 | 42 | 272 | 4.85 | 2.55 |  | 7.4 | 0.20791 | 0.65541 | 35.7568 | 11.0699 | 11.606 | 391.4243 | 301.5192 | 389.8213 | 0.89104 | 42.109 | 0.27562 | [27 empty] | Sampling date | MM/DD/YY | 1998-12-16 | 1998-12-17 | --- | --- | 1998-12-16 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-18 | 1998-12-18 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-19 | 1998-12-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-20 | 1998-12-20 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 660 | 660 | 660 | 660 | SDS-TOXF, ug Cl- /L | 660 | 660 | 660 | 660 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 331 | 334 | 332.5 | 0.90226 | 1998-12-14 | 11:00 | 1.3333 | 23 | 56 | 54 | 254 | 5.65 | 2.1 | 7.75 | 0.19415 | 0.72903 | 31.7742 | 12.8958 | 13.5204 | 0 | 0 | 0 | 0 | 55 | 0.24582 | 1998-12-15 | 9:45 | 1.25 | 23 | 56 | 55 | 272 | 6.33 | 3.13 |  | 9.46 | 0.20791 | 0.66913 | 27.7526 | 14.4479 | 15.1476 | 393.1887 | 302.4912 | 391.078 | 0.89642 | 54.6036 | 0.27741 | [27 empty] | Sampling time | hh:mm | 9:30 | 9:00 | --- | --- | 9:30 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 9:00 | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 15:00 | 15:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 16:00 | 16:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 114.5 | 125 | 83 | 65 | SDS-TOXp, ug Cl- /L | 114.5 | 125 | 83 | 65 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 272 | 300 | 286 | 9.7902 | 1998-12-14 | 11:30 | 1.8333 | 23 | 56 | 54 | 254 | 5.9 | 2.33 | 8.23 | 0.19415 | 0.71689 | 29.8627 | 13.4664 | 14.1186 | 0 | 0 | 0 | 0 | 55 | 0.2567 | 1998-12-15 | 11:00 | 2.5 | 23 | 56 | 54 | 272 | 6.34 | 2.83 |  | 9.17 | 0.20791 | 0.69138 | 28.6619 | 14.4707 | 15.1715 | 395.592 | 304.3375 | 393.4649 | 0.90191 | 54.0981 | 0.28044 | 7.6 | 7.77 | 7.91 | 271 | 325 | 296 | 470.2774 | -58.8775 | 18.4962 | 467.9549 | 42.0884 | 0.029 | 0.198 | 0.281 | 0.58633 | -108.6579 | 85.5721 | 0.57983 | 94.9986 | [8 empty] | Operation time | hh.hh | 1.0417 | 48.5 | --- | --- | 1.0417 | --- | --- | --- | --- | --- | Operation time | hh.hh | 106.5 | 106.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 126.5 | 126.5 | --- | --- | --- | --- | --- | Cumulative time | hr | 151.5 | 151.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 5.595 | 5.595 | 5.595 | 5.595 | SDS-CDF, mg/L | 5.595 | 5.595 | 5.595 | 5.595 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 260 | 260 | 260 | 0 | 1998-12-14 | 12:10 | 2.5 | 23 | 56 | 54 | 254 | 6 | 1.6 | 7.6 | 0.19415 | 0.78947 | 32.4211 | 13.6947 | 14.3579 | 0 | 0 | 0 | 0 | 55 | 0.26105 | 1998-12-15 | 11:30 | 3 | 23 | 56 | 54 | 272 | 6.34 | 2.8 |  | 9.14 | 0.20791 | 0.69365 | 28.7593 | 14.4707 | 15.1715 | 395.8385 | 304.5272 | 393.7102 | 0.90247 | 54.0975 | 0.28045 | 7.77 | 7.81 | 7.95 | 290 | 319 | 324 | 428.7321 | -32.3247 | 12.782 | 427.1153 | 32.1026 | 0.038 | 0.204 | 0.34 | 0.57008 | -67.6702 | 81.0945 | 0.56388 | 93.2609 | [8 empty] | pH | --- | 8.05 | 8.12 | 8.085 | 0.8658 | 8.24 | --- | --- | --- | --- | --- | pH | --- | 8.04 | 8.32 | --- | --- | --- | --- | --- | pH | --- | 8 | 7.99 | --- | --- | --- | --- | --- | pH | --- | 7.89 | 7.89 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.37 | 1.9 | 1.53 | 1.47 | SDS-CDp, mg/L | 1.37 | 1.9 | 1.53 | 1.47 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 15.1667 | 62.5992 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.3 | 0.25 | 0.275 | 18.1818 | 1998-12-14 | 13:30 | 3.8333 | 23 | 56 | 54 | 254 | 6.05 | 2.4 | 8.45 | 0.19415 | 0.71598 | 29.0592 | 13.8088 | 14.4776 | 0 | 0 | 0 | 0 | 55 | 0.26323 | 1998-12-15 | 12:00 | 3.5 | 23 | 56 | 54 | 272 | 6.34 | 2.78 |  | 9.12 | 0.20791 | 0.69518 | 28.8246 | 14.4707 | 15.1715 | 396.0039 | 304.6544 | 393.8747 | 0.90285 | 54.0972 | 0.28045 | 7.41 | 7.63 | 7.62 | 300 | 331 | 373 | 406.6187 | -9.0131 | 9.7744 | 405.3761 | 25.9947 | 0.033 | 0.206 | 0.419 | 0.58414 | -39.4121 | 83.5821 | 0.57771 | 94.2878 | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.75 | 6.75 | 6.75 | 6.75 | TOCF, mg/L | 6.75 | 6.75 | 6.75 | 6.75 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 38.5 | 85.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-12-14 | 14:30 | 4.8333 | 23 | 55 | 54 | 254 | 6.2 | 2.35 | 8.55 | 0.19415 | 0.72515 | 28.7076 | 14.1512 | 14.8365 | 0 | 0 | 0 | 0 | 54.5 | 0.27223 | 1998-12-15 | 12:30 | 4 | 23 | 56 | 54 | 272 | 6.23 | 2.72 |  | 8.95 | 0.20791 | 0.69609 | 29.3911 | 14.2196 | 14.9083 | 396.0793 | 304.7415 | 393.9872 | 0.90292 | 54.0971 | 0.27558 | 7.59 | 7.7 | 7.87 | 308 | 328 | 341 | 388.6158 | -13.9636 | 7.3684 | 387.6926 | 20.5556 | 0.043 | 0.193 | 0.431 | 0.56289 | -30.6009 | 78.607 | 0.55694 | 92.2792 | [8 empty] | Alkalinity | mg/L as CaCO3 | 370 | 358 | 364 | 3.2967 | 511 | 646.1429 | -26.4467 | 17.833 | 643.2974 | 43.4165 | Alkalinity | mg/L as CaCO3 | 432 | 562 | 516.6154 | 8.0756 | 2.4831 | 515.8359 | 16.2524 | Alkalinity | mg/L as CaCO3 | 336 | 496 | 558.9167 | -12.6848 | 24.1535 | 556.8604 | 39.6617 | Alkalinity | mg/L as CaCO3 | 318 | 484 | 499.1594 | -3.1321 | 28.2167 | 497.6057 | 36.094 | TOCp, mg/L | 1.3 | 1.7 | 1 | 0.7 | TOCp, mg/L | 1.3 | 1.7 | 1 | 0.7 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 57.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6.4 | 7.1 | 6.75 | 10.3704 | 1998-12-14 | 15:30 | 5.8333 | 23 | 56 | 54 | 254 | 6.2 | 2.25 | 8.45 | 0.19415 | 0.73373 | 29.0592 | 14.1512 | 14.8365 | 0 | 0 | 0 | 0 | 55 | 0.26975 | 1998-12-15 | 13:30 | 5 | 23 | 56 | 54 | 272 | 6.17 | 2.65 |  | 8.82 | 0.20791 | 0.69955 | 29.839 | 14.0827 | 14.7647 | 396.4425 | 305.0368 | 394.3691 | 0.90369 | 54.0963 | 0.27293 | 7.62 | 7.77 | 7.91 | 309 | 332 | 347 | 387.2151 | -11.5894 | 7.0677 | 386.328 | 20.0161 | 0.045 | 0.199 | 0.506 | 0.56422 | -11.505 | 77.6119 | 0.55833 | 91.9402 | [8 empty] | Total dissolved solids | mg/L | 306 | 309 | 307.5 | 0.97561 | 375 | 396.7857 | -5.8095 | 7.5188 | 395.8852 | 22.326 | Total dissolved solids | mg/L | 325 | 388 | 382.6923 | 1.368 | 2.2556 | 382.1609 | 14.9573 | Total dissolved solids | mg/L | 287 | 362 | 381.7917 | -5.4673 | 13.6842 | 380.9173 | 24.6556 | Total dissolved solids | mg/L | 278 | 339 | 356.9855 | -5.3055 | 16.391 | 356.3081 | 21.9776 | UV254 F, cm-1 | 0.201 | 0.201 | 0.201 | 0.201 | UV254 F, cm-1 | 0.201 | 0.201 | 0.201 | 0.201 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 8.5 | 55.9325 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.201 | 0.201 | 0.201 | 0 | 1998-12-14 | 16:00 | 6.3333 | 23 | 55 | 54 | 254 | 6.2 | 2.8 | 9 | 0.19415 | 0.68889 | 27.2222 | 14.1512 | 14.8365 | 0 | 0 | 0 | 0 | 54.5 | 0.27223 | 1998-12-15 | 14:30 | 6 | 23 | 56 | 54 | 272 | 6.11 | 2.65 |  | 8.76 | 0.20791 | 0.69749 | 30.0502 | 13.9457 | 14.6211 | 396.2052 | 304.8701 | 394.1535 | 0.90309 | 54.0969 | 0.27028 | 7.64 | 7.79 | 7.94 | 310 | 332 | 348 | 384.3774 | -10.4533 | 6.7669 | 383.542 | 19.1744 | 0.042 | 0.202 | 0.505 | 0.5676 | -12.396 | 79.1045 | 0.5617 | 92.5227 | [8 empty] | Total hardness | mg/L as CaCO3 | 230 | 240 | 235 | 4.2553 | 320 | 417.1429 | -30.3571 | 17.8322 | 415.3059 | 43.4152 | Total hardness | mg/L as CaCO3 | 282 | 360 | 312.7692 | 13.1197 | 1.3986 | 312.4858 | 9.7559 | Total hardness | mg/L as CaCO3 | 214 | 312 | 364 | -16.6667 | 25.1748 | 362.6164 | 40.9845 | Total hardness | mg/L as CaCO3 | 214 | 300 | 318.3478 | -6.1159 | 25.1748 | 317.4529 | 32.5884 | UV254 p, cm-1 | 0.0285 | 0.035 | 0.014 | 0.011 | UV254 p, cm-1 | 0.0285 | 0.035 | 0.014 | 0.011 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | [9 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.1406 | 2.831 | 2.9858 | 10.3704 | 1998-12-14 | 16:30 | 6.8333 | 23 | 64 | 63 | 272 | 7.53 | 2.77 | 10.3 | 0.20791 | 0.73107 | 25.4078 | 17.1868 | 18.0192 | 0 | 0 | 0 | 0 | 63.5 | 0.28377 | 1998-12-15 | 15:30 | 7 | 23 | 55 | 54 | 272 | 6 | 2.51 |  | 8.51 | 0.20791 | 0.70505 | 30.9624 | 13.6947 | 14.3579 | 397.0056 | 305.5151 | 394.9875 | 0.90481 | 53.5952 | 0.2679 | 7.86 | 8.11 | 8.1 | 309 | 330 | 352 | 388.6753 | -10.4191 | 7.0677 | 387.7965 | 20.319 | 0.041 | 0.198 | 0.55 | 0.58347 | -6.0855 | 79.602 | 0.57749 | 92.9003 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 222 | 232 | 227 | 4.4053 | 298 | 344.8571 | -15.7239 | 12.6923 | 343.6685 | 33.948 | Calcium hardness | mg/L as CaCO3 | 254 | 334 | 300.1538 | 10.1336 | 2.3077 | 299.7287 | 15.2567 | Calcium hardness | mg/L as CaCO3 | 210 | 286 | 314.1667 | -9.8485 | 19.2308 | 313.2058 | 32.9514 | Calcium hardness | mg/L as CaCO3 | 202 | 270 | 286.058 | -5.9474 | 22.3077 | 285.3371 | 29.2065 | BromideF, ug/L | 190 | 190 | 190 | 190 | BromideF, ug/L | 190 | 190 | 190 | 190 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 190 | 190 | 190 | 0 | 1998-12-14 | 17:00 | 7.3333 | 23 | 45 | 43 | 272 | 5.1 | 2.2 | 7.3 | 0.20791 | 0.69863 | 36.2603 | 11.6405 | 12.2042 | 0 | 0 | 0 | 0 | 44 | 0.27737 | 1998-12-15 | 16:30 | 8 | 23 | 54 | 53 | 272 | 5.94 | 2.44 |  | 8.38 | 0.20791 | 0.70883 | 31.4582 | 13.5577 | 14.2143 | 397.4053 | 305.8386 | 395.4056 | 0.90567 | 52.5943 | 0.27026 | 7.69 | 7.9 | 8 | 309 | 332 | 346 | 389.709 | -12.6327 | 7.0677 | 388.8277 | 20.5304 | 0.043 | 0.202 | 0.55 | 0.58564 | -6.4799 | 78.607 | 0.57971 | 92.5826 | [8 empty] | Turbidity | ntu | 0.19 | 0.18 | 0.185 | 5.4054 | 0.285 | 0.50643 | -77.6942 | 32.7273 | 0.50319 | 63.2343 | Turbidity | ntu | 0.22 | 1.3 | 0.64308 | 50.5325 | 20 | 0.63918 | 65.5809 | Turbidity | ntu | 0.15 | 0.27 | 0.41042 | -52.0062 | 45.4545 | 0.40801 | 63.2366 | Turbidity | ntu | 0.12 | 0.262 | 0.34464 | -31.5411 | 56.3636 | 0.34271 | 64.9851 | Bromidep, ug/L | 215 | 190 | 180 | 180 | Bromidep, ug/L | 215 | 190 | 180 | 180 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 6.5 | 6.5 | 6.5 | 0 | 1998-12-14 | 17:20 | 7.6667 | 23 | 56 | 54 | 272 | 6.4 | 2.6 | 9 | 0.20791 | 0.71111 | 29.2222 | 14.6077 | 15.3151 | 0 | 0 | 0 | 0 | 55 | 0.27846 | 1998-12-16 | 8:45 | 24.25 | 23 | 55 | 54 | 272 | 5.55 | 2.11 |  | 7.66 | 0.20791 | 0.72454 | 34.5091 | 12.6676 | 13.2811 | 399.0422 | 307.202 | 397.1683 | 0.90903 | 53.591 | 0.24782 | 7.82 | 8.06 | 8.09 | 309 | 333 | 360 | 394.3128 | -9.5313 | 7.0677 | 393.4424 | 21.4625 | 0.054 | 0.204 | 0.611 | 0.58766 | 3.8202 | 73.1343 | 0.58221 | 90.7251 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 443 | 443 | 443 | 443 | AlkF, mg/L CaCO3 | 443 | 443 | 443 | 443
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI |  |  |  | SDS-Free Cl2 residual | mg/L | 0.75 | 1.06 | 0.905 | 34.2541 | 1998-12-14 | 17:45 | 8.0833 | 23 | 56 | 54 | 272 | 6.33 | 3.3 | 9.63 | 0.20791 | 0.65732 | 27.2451 | 14.4479 | 15.1476 | 0 | 0 | 0 | 0 | 55 | 0.27541 | 1998-12-16 | 9:45 | 25.25 | 23 | 55 | 54 | 272 | 5.6 | 2.13 |  | 7.73 | 0.20791 | 0.72445 | 34.1876 | 12.7817 | 13.4007 | 399.0435 | 307.1897 | 397.1524 | 0.90908 | 53.5909 | 0.25006 | 7.63 | 7.86 | 7.93 | 309 | 332 | 354 | 394.284 | -11.3797 | 7.0677 | 393.4061 | 21.4552 | 0.053 | 0.205 | 0.603 | 0.59011 | 2.138 | 73.6318 | 0.58458 | 90.9336 | [8 empty] | Total organic carbon | mg/L | 1.4 | 1.2 | 1.3 | 15.3846 | 16.6 | 20.7643 | -25.0861 | 80.7407 | 20.568 | 93.6795 | Total organic carbon | mg/L | 1.7 | 49.5 | 40.5462 | 18.0886 | 74.8148 | 40.1883 | 95.7699 | Total organic carbon | mg/L | 1 | 11.9 | 12.9792 | -9.0686 | 85.1852 | 12.8687 | 92.2292 | Total organic carbon | mg/L | 0.7 | 8 | 9.4681 | -18.3514 | 89.6296 | 9.3929 | 92.5476 | Alkp, mg/L CaCO3 | 364 | 432 | 336 | 318 | Alkp, mg/L CaCO3 | 364 | 432 | 336 | 318
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Cl2 demand | mg/L | 5.75 | 5.44 | 5.595 | 5.5407 | 1998-12-15 | 8:30 | 22.8333 | 23 | 64 | 62 | 272 | 7.27 | 3.35 | 10.62 | 0.20791 | 0.68456 | 24.6121 | 16.5934 | 17.397 | 0 | 0 | 0 | 0 | 63 | 0.27614 | 1998-12-16 | 10:45 | 26.25 | 23 | 55 | 54 | 272 | 5.6 | 2.07 |  | 7.67 | 0.20791 | 0.73012 | 34.4628 | 12.7817 | 13.4007 | 399.6692 | 307.6714 | 397.7752 | 0.91051 | 53.5895 | 0.25006 | 7.75 | 7.8 | 8.02 | 308 | 333 | 355 | 398.7802 | -12.3324 | 7.3684 | 397.8457 | 22.583 | 0.031 | 0.204 | 0.663 | 0.6609 | 0.31623 | 84.5771 | 0.65442 | 95.263 | [8 empty] | UV254 | cm-1 | 0.029 | 0.028 | 0.0285 | 3.5088 | 0.65 | 0.64457 | 0.83516 | 85.8209 | 0.63836 | 95.5354 | UV254 | cm-1 | 0.035 | 1.693 | 1.3119 | 22.509 | 82.5871 | 1.3002 | 97.308 | UV254 | cm-1 | 0.014 | 0.453 | 0.40358 | 10.9088 | 93.0348 | 0.39999 | 96.4999 | UV254 | cm-1 | 0.011 | 0.284 | 0.28636 | -0.8318 | 94.5274 | 0.284 | 96.1268 | T-HdF, mg/L CaCO3 | 286 | 286 | 286 | 286 | T-HdF, mg/L CaCO3 | 286 | 286 | 286 | 286
Treatment Plant Category | Conventional Filtration | [12 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-16 | 12:00 | 27.5 | 23 | 55 | 53 | 272 | 5.55 | 2.04 |  | 7.59 | 0.20791 | 0.73123 | 34.8366 | 12.6676 | 13.2811 | 399.7801 | 307.77 | 397.9027 | 0.91071 | 53.0893 | 0.25016 | 7.9 | 8.03 | 8.2 | 311 | 333 | 354 | 390.9926 | -10.4499 | 6.4662 | 390.1765 | 20.2925 | 0.031 | 0.202 | 0.662 | 0.6635 | -0.22659 | 84.5771 | 0.65705 | 95.2819 | [8 empty] | SUVA | L/(mg*m) | 2.0714 | 2.3333 | 2.2024 | 11.8919 | 3.9157 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 2.0588 | 3.4202 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.4 | 3.8067 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.5714 | 3.55 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 235 | 282 | 214 | 214 | T-Hdp, mg/L CaCO3 | 235 | 282 | 214 | 214
Process Train Name | Lime softening and conventional filtration | Additional Information | [11 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination pH | --- | 8.74 | 8.58 | 8.66 | 1.8476 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-16 | 13:00 | 28.5 | 23 | 54 | 53 | 272 | 5.555 | 2.04 |  | 7.595 | 0.20791 | 0.7314 | 34.813 | 12.679 | 13.293 | 399.8009 | 307.7847 | 397.9216 | 0.91077 | 52.5892 | 0.25277 | 7.87 | 7.97 | 8.05 | 309 | 332 | 354 | 396.4914 | -12.0032 | 7.0677 | 395.598 | 21.8904 | 0.03 | 0.202 | 0.658 | 0.66664 | -1.313 | 85.0746 | 0.66014 | 95.4555 | [8 empty] | Bromide | mg/L | 240 | 190 | 215 | 23.2558 | --- | 125.7143 | --- | -13.1579 | 126.6148 | -69.8064 | Bromide | mg/L | 190 | --- | 190 | --- | 0 | 190 | 0 | Bromide | mg/L | 180 | --- | 200.8333 | --- | 5.2632 | 200.6412 | 10.2876 | Bromide | mg/L | 180 | --- | 194.4928 | --- | 5.2632 | 194.3685 | 7.3924 | Ca-HdF, mg/L CaCO3 | 260 | 260 | 260 | 260 | Ca-HdF, mg/L CaCO3 | 260 | 260 | 260 | 260
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-16 | 14:00 | 29.5 | 23 | 54 | 53 | 272 | 5.55 | 2.01 |  | 7.56 | 0.20791 | 0.73413 | 34.9788 | 12.6676 | 13.2811 | 400.1014 | 308.0173 | 398.2225 | 0.91145 | 52.5886 | 0.25255 | 8.12 | 8.06 | 8.1 | 308 | 332 | 353 | 400.1493 | -13.3567 | 7.3684 | 399.2091 | 22.8475 | 0.03 | 0.201 | 0.659 | 0.67316 | -2.1493 | 85.0746 | 0.6666 | 95.4996 | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 227 | 254 | 210 | 202 | Ca-Hdp, mg/L CaCO3 | 227 | 254 | 210 | 202
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 700 | 620 | 660 | 12.1212 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-16 | 15:00 | 30.5 | 23 | 54 | 53 | 272 | 5.6 | 2.4 |  | 8 | 0.20791 | 0.7 | 33 | 12.7817 | 13.4007 | 396.3663 | 305.1287 | 394.4879 | 0.90298 | 52.597 | 0.25478 | 7.88 | 7.98 | 7.86 | 308 | 331 | 354 | 389.6667 | -10.0753 | 7.3684 | 388.826 | 20.7872 | 0.03 | 0.199 | 0.633 | 0.6 | 5.2133 | 85.0746 | 0.59413 | 94.9506 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.16 | 1.1 | 1.13 | 5.3097 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.1 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.97 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.03 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 160 | 130 | 145 | 20.6897 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-16 | 16:00 | 31.5 | 23 | 54 | 52 | 272 | 5.55 | 2.3 |  | 7.85 | 0.20791 | 0.70701 | 33.6497 | 12.6676 | 13.2811 | 397.1187 | 305.7211 | 395.2538 | 0.90465 | 52.0953 | 0.25494 | 7.89 | 8.03 | 8.2 | 308 | 331 | 354 | 391.6196 | -10.627 | 7.3684 | 390.7665 | 21.1805 | 0.032 | 0.202 | 0.619 | 0.6088 | 1.6471 | 84.0796 | 0.60292 | 94.6925 | [8 empty] | SDS-Cl2 demand | mg/L | 1.34 | 1.4 | 1.37 | 4.3796 | --- | 16.4593 | --- | 75.5139 | 16.3071 | 91.5988 | SDS-Cl2 demand | mg/L | 1.9 | --- | 30.3231 | --- | 66.0411 | 30.0613 | 93.6796 | SDS-Cl2 demand | mg/L | 1.53 | --- | 9.9987 | --- | 72.6542 | 9.9206 | 84.5776 | SDS-Cl2 demand | mg/L | 1.47 | --- | 7.4483 | --- | 73.7265 | 7.397 | 80.1271 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 67 | 64 | 65.5 | 4.5802 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 8:45 | 48.25 | 22 | 54 | 52 | 272 | 5.25 | 2 |  | 7.25 | 0.20791 | 0.72414 | 36.5172 | 11.9828 | 12.9401 | 398.9285 | 307.1939 | 397.1579 | 0.90849 | 52.0915 | 0.24841 | 7.61 | 7.82 | 7.93 | 306 | 331 | 355 | 402.0625 | -13.257 | 7.9699 | 401.1354 | 23.7165 | 0.029 | 0.202 | 0.649 | 0.6525 | -0.53929 | 85.5721 | 0.64648 | 95.5142 | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 101.7713 | 110.8291 | 91.251 | 84.0822 | Qp/QT (THM4), % | 124.1454 | 135.1946 | 111.3123 | 102.5674
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 24 | 23 | 23.5 | 4.2553 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 10:00 | 49.5 | 22 | 54 | 52 | 272 | 5.3 | 2.02 |  | 7.32 | 0.20791 | 0.72404 | 36.1585 | 12.097 | 13.0633 | 398.9296 | 307.1815 | 397.1419 | 0.90854 | 52.0915 | 0.25078 | 7.73 | 7.81 | 7.89 | 306 | 332 | 357 | 402.0297 | -12.6134 | 7.9699 | 401.0941 | 23.7087 | 0.03 | 0.204 | 0.664 | 0.64966 | 2.1591 | 85.0746 | 0.64363 | 95.3389 | [8 empty] | SDS-Chlorination pH | --- | 8.66 | 8.45 | 8.555 | 2.4547 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.41 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.45 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.44 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | NA | NA | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | 1.8 | 1.7 | 1.75 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 11:00 | 50.5 | 23 | 54 | 52 | 272 | 5.35 | 2 |  | 7.35 | 0.20791 | 0.72789 | 36.0068 | 12.2111 | 12.8025 | 399.3652 | 307.5037 | 397.5584 | 0.90958 | 52.0904 | 0.24577 | 7.78 | 7.87 | 8.26 | 309 | 332 | 361 | 395.3625 | -9.5187 | 7.0677 | 394.5132 | 21.6756 | 0.031 | 0.205 | 0.662 | 0.65575 | 0.94411 | 84.5771 | 0.64961 | 95.2279 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | NA | NA | 11.7319 | 14.8417 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 252.8 | 218.7 | 235.75 | 14.4645 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 12:00 | 51.5 | 23 | 54 | 52 | 272 | 5.25 | 2.02 |  | 7.27 | 0.20791 | 0.72215 | 36.414 | 11.9828 | 12.5632 | 398.7094 | 307.0252 | 396.9397 | 0.90799 | 52.092 | 0.24117 | 8.02 | 8.1 | 8.12 | 308 | 332 | 359 | 396.1757 | -10.3554 | 7.3684 | 395.3248 | 22.0894 | 0.03 | 0.206 | 0.664 | 0.64543 | 2.7966 | 85.0746 | 0.63949 | 95.3088 | [8 empty] | SDS-TOX | mg Cl- /L | 99 | 130 | 114.5 | 27.0742 | --- | 2062.7143 | --- | 82.6515 | 2043.066 | 94.3957 | SDS-TOX | mg Cl- /L | 125 | --- | 4240.3846 | --- | 81.0606 | 4202.4747 | 97.0256 | SDS-TOX | mg Cl- /L | 83 | --- | 1285.0833 | --- | 87.4242 | 1273.995 | 93.4851 | SDS-TOX | mg Cl- /L | 65 | --- | 927.3188 | --- | 90.1515 | 919.9233 | 92.9342 | SDS-TOXb, ug Cl- /L | NA | NA | 133.4815 | 159.7112 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | 3.6 | 4 | 3.8 | 10.5263 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 14:00 | 53.5 | 23 | 54 | 52 | 272 | 5.29 | 1.94 |  | 7.23 | 0.20791 | 0.73167 | 36.621 | 12.0741 | 12.6589 | 399.769 | 307.8305 | 397.9809 | 0.91044 | 52.0896 | 0.24302 | 7.76 | 8.16 | 8.22 | 310 | 332 | 362 | 393.8531 | -8.7992 | 6.7669 | 393.0377 | 21.1272 | 0.029 | 0.205 | 0.666 | 0.67001 | -0.60215 | 85.5721 | 0.66378 | 95.6311 | [8 empty] | SDS-CHCl3 | mg/L | 7 | 5.7 | 6.35 | 20.4724 | --- | 501.5286 | --- | 95.6207 | 496.5345 | 98.7211 | SDS-CHCl3 | mg/L | 12 | --- | 1035.0769 | --- | 91.7241 | 1025.6526 | 98.83 | SDS-CHCl3 | mg/L | 3.8 | --- | 297.9667 | --- | 97.3793 | 295.2532 | 98.713 | SDS-CHCl3 | mg/L | 2.8 | --- | 208.887 | --- | 98.069 | 207.1195 | 98.6481 | SDS-CDb, mg/L | NA | NA | 1.8856 | 2.1266 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7 | [13 empty] | SDS-DCAA* | mg/L | 33 | 33 | 33 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 15:00 | 54.5 | 23 | 54 | 52 | 272 | 5.3 | 1.92 |  | 7.22 | 0.20791 | 0.73407 | 36.6731 | 12.097 | 12.6828 | 400.0366 | 308.0339 | 398.2439 | 0.91106 | 52.0889 | 0.24348 | 7.78 | 8.03 | 8.1 | 307 | 331 | 372 | 402.8906 | -8.3039 | 7.6692 | 401.9564 | 23.6236 | 0.029 | 0.208 | 0.679 | 0.67579 | 0.47251 | 85.5721 | 0.66949 | 95.6683 | [8 empty] | SDS-BDCM | mg/L | 17 | 13 | 15 | 26.6667 | --- | 195.3571 | --- | 77.0992 | 193.5382 | 92.2496 | SDS-BDCM | mg/L | 22 | --- | 356.6154 | --- | 66.4122 | 353.533 | 93.7771 | SDS-BDCM | mg/L | 9.5 | --- | 126.1667 | --- | 85.4962 | 125.0905 | 92.4055 | SDS-BDCM | mg/L | 7.2 | --- | 91.6928 | --- | 89.0076 | 90.9681 | 92.0851 | TOCb, mg/L | NA | NA | 1.5031 | 1.663 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 21 | 29 | 25 | 32 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-17 | 16:00 | 55.5 | 23 | 54 | 52 | 272 | 5.3 | 2.04 |  | 7.34 | 0.20791 | 0.72207 | 36.0572 | 12.097 | 12.6828 | 398.7126 | 307.0144 | 396.9258 | 0.90805 | 52.092 | 0.24347 | 7.86 | 7.99 | 8.07 | 307 | 331 | 364 | 398.75 | -9.5467 | 7.6692 | 397.8561 | 22.8364 | 0.028 | 0.21 | 0.629 | 0.65046 | -3.4119 | 86.0697 | 0.6444 | 95.6548 | [8 empty] | SDS-DBCM | mg/L | 31 | 27 | 29 | 13.7931 | --- | 9.3571 | --- | -23.4043 | 9.5552 | -203.4982 | SDS-DBCM | mg/L | 35 | --- | -53.4615 | --- | -48.9362 | -52.6467 | 166.481 | SDS-DBCM | mg/L | 22 | --- | 25.125 | --- | 6.383 | 25.0962 | 12.3372 | SDS-DBCM | mg/L | 16 | --- | 26.8696 | --- | 31.9149 | 26.7763 | 40.2458 | UV254 b, cm-1 | NA | NA | 0.030361 | 0.041244 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2-11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 9:30 | 73 | 23 | 54 | 52 | 272 | 5.3 | 1.92 |  | 7.22 | 0.20791 | 0.73407 | 36.6731 | 12.097 | 12.6828 | 400.0366 | 308.0339 | 398.2439 | 0.91106 | 52.0889 | 0.24348 | 7.69 | 8.01 | 8.13 | 309 | 331 | 370 | 397.3698 | -7.3972 | 7.0677 | 396.5088 | 22.0698 | 0.025 | 0.207 | 0.737 | 0.68683 | 6.8069 | 87.5622 | 0.68039 | 96.3256 | [8 empty] | SDS-CHBr3 | mg/L | 26 | 23 | 24.5 | 12.2449 | --- | -56.75 | --- | -1300 | -55.9306 | 143.8043 | SDS-CHBr3 | mg/L | 19 | --- | -113.6923 | --- | -985.7143 | -112.47 | 116.8934 | SDS-CHBr3 | mg/L | 21 | --- | -19.1042 | --- | -1100 | -18.7342 | 212.0942 | SDS-CHBr3 | mg/L | 15 | --- | -4.2029 | --- | -757.1429 | -4.0382 | 471.4518 | Bromideb, ug/L | NA | NA | 180.8749 | 181.5918 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 4.6 | 4.4 | 4.5 | 4.4444 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 10:30 | 74 | 23 | 54 | 52 | 272 | 5.3 | 2.04 |  | 7.34 | 0.20791 | 0.72207 | 36.0572 | 12.097 | 12.6828 | 398.7126 | 307.0144 | 396.9258 | 0.90805 | 52.092 | 0.24347 | 7.77 | 7.98 | 8.09 | 309 | 331 | 372 | 393.5539 | -5.7941 | 7.0677 | 392.7301 | 21.32 | 0.025 | 0.203 | 0.702 | 0.65825 | 6.2315 | 87.5622 | 0.65209 | 96.1661 | [8 empty] | SDS-THM4 | mg/L | 81 | 68.7 | 74.85 | 16.4329 | --- | 649.4929 | --- | 68.2503 | 643.6974 | 88.3719 | SDS-THM4 | mg/L | 88 | --- | 1224.5385 | --- | 62.6723 | 1214.0689 | 92.7516 | SDS-THM4 | mg/L | 56.3 | --- | 430.1542 | --- | 76.1188 | 426.7056 | 86.8059 | SDS-THM4 | mg/L | 41 | --- | 323.2464 | --- | 82.6087 | 320.8258 | 87.2205 | Alkb, mg/L CaCO3 | NA | NA | 345.3614 | 337.8973 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 14 | 14 | 14 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 11:30 | 75 | 23 | 54 | 52 | 272 | 5.2 | 1.96 |  | 7.16 | 0.20791 | 0.72626 | 36.9888 | 11.8687 | 12.4435 | 399.1503 | 307.378 | 397.3958 | 0.90895 | 52.091 | 0.23888 | 7.8 | 8.06 | 8.13 | 309 | 331 | 370 | 394.8469 | -6.7154 | 7.0677 | 394.0263 | 21.5788 | 0.024 | 0.203 | 0.692 | 0.67059 | 3.0937 | 88.0597 | 0.66441 | 96.3878 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | NA | NA | 220.2992 | 225.4608 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 13:30 | 77 | 23 | 54 | 52 | 272 | 5.2 | 1.82 |  | 7.02 | 0.20791 | 0.74074 | 37.7464 | 11.8687 | 12.4435 | 400.7524 | 308.6117 | 398.9909 | 0.9126 | 52.0874 | 0.2389 | 8.01 | 8.1 | 8.18 | 306 | 331 | 370 | 408.2143 | -10.3282 | 7.9699 | 407.2372 | 24.8595 | 0.024 | 0.205 | 0.697 | 0.70671 | -1.3937 | 88.0597 | 0.70019 | 96.5724 | [8 empty] | SDS-DCAA* | mg/L | 2.2 | 2 | 2.1 | 9.5238 | --- | 112.4571 | --- | 93.6364 | 111.3442 | 98.114 | SDS-DCAA* | mg/L | 3.4 | --- | 231.0923 | --- | 89.697 | 228.9949 | 98.5153 | SDS-DCAA* | mg/L | 1.4 | --- | 67.2333 | --- | 95.7576 | 66.6261 | 97.8987 | SDS-DCAA* | mg/L | 1.1 | --- | 47.3319 | --- | 96.6667 | 46.9354 | 97.6564 | Ca-Hdb, mg/L CaCO3 | NA | NA | 214.3745 | 211.2323 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 3.2 | 3.5 | 3.35 | 8.9552 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 14:30 | 78 | 23 | 54 | 52 | 272 | 5.25 | 2.34 |  | 7.59 | 0.20791 | 0.6917 | 34.8366 | 11.9828 | 12.5632 | 395.3899 | 304.4691 | 393.635 | 0.90043 | 52.0996 | 0.24114 | 7.99 | 8.13 | 8.14 | 305 | 331 | 368 | 394.1987 | -7.1192 | 8.2707 | 393.3379 | 22.4585 | 0.023 | 0.203 | 0.695 | 0.60036 | 13.6174 | 88.5572 | 0.59479 | 96.1331 | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | 1.9 | --- | 179.5923 | --- | 92.4 | 177.9554 | 98.9323 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 9 | 11 | 10 | 20 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 16:30 | 80 | 23 | 54 | 52 | 272 | 5.18 | 1.04 |  | 6.22 | 0.20791 | 0.8328 | 42.7299 | 11.8231 | 12.3957 | 411.2377 | 316.6917 | 409.4371 | 0.93646 | 52.0635 | 0.23809 | 8.15 | 8.1 |  | 318 | 331 |  | 404.7212 |  | 4.3609 | 403.8954 | 21.2667 | 0.003 | 0.204 | 0.626 | 1.1872 | -89.6473 | 98.5075 | 1.1759 | 99.7449 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 62.2 | 70.4 | 66.3 | 12.368 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 17:00 | 80.5 | 23 | 54 | 52 | 272 | 5.2 | 0.72 |  | 5.92 | 0.20791 | 0.87838 | 44.9459 | 11.8687 | 12.4435 | 416.6438 | 320.8493 | 414.8124 | 0.94879 | 52.0512 | 0.23906 | 8.07 | 8.17 |  | 314 | 331 |  | 466.1111 |  | 5.5639 | 464.6571 | 32.4233 | 0.059 | 0.202 | 0.683 | 1.2266 | -79.5835 | 70.6468 | 1.2154 | 95.1456 | [8 empty] | SDS-DBAA* | mg/L | 6.8 | 6.4 | 6.6 | 6.0606 | --- | -0.9 | --- | -46.6667 | -0.82436 | 900.6208 | SDS-DBAA* | mg/L | 7.3 | --- | -14.2385 | --- | -62.2222 | -14.0401 | 151.9941 | SDS-DBAA* | mg/L | 5.1 | --- | 3.85 | --- | -13.3333 | 3.8615 | -32.072 | SDS-DBAA* | mg/L | 4 | --- | 4.7246 | --- | 11.1111 | 4.7184 | 15.2259 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 76.2 | 84.4 | 80.3 | 10.2117 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 17:30 | 81 | 23 | 54 | 52 | 272 | 5.2 | 0.75 |  | 5.95 | 0.20791 | 0.87395 | 44.7143 | 11.8687 | 12.4435 | 416.1128 | 320.4405 | 414.2838 | 0.94758 | 52.0524 | 0.23906 | 8.1 | 8.21 |  | 315 | 331 |  | 453.8333 |  | 5.2632 | 452.5063 | 30.3877 | 0.032 | 0.202 | 0.731 | 1.3727 | -87.7884 | 84.0796 | 1.3599 | 97.6469 | [8 empty] | SDS-BCAA* | mg/L | 4 | 3.7 | 3.85 | 7.7922 | --- | 40.1 | --- | 72.5 | 39.7344 | 90.3107 | SDS-BCAA* | mg/L | 5.5 | --- | 70.8846 | --- | 60.7143 | 70.2823 | 92.1744 | SDS-BCAA* | mg/L | 2.8 | --- | 26.1333 | --- | 80 | 25.9181 | 89.1967 | SDS-BCAA* | mg/L | 2 | --- | 19.3913 | --- | 85.7143 | 19.2422 | 89.6062 | Qp/QT (HAA5), % | 21.3542 | 22.905 | 20.5686 | 20.098 | Qp/QT (HAA5), % | 68.2292 | 73.1844 | 65.7191 | 64.2157
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 18:00 | 81.5 | 23 | 54 | 52 | 272 | 5.25 | 0.7 |  | 5.95 | 0.20791 | 0.88235 | 44.7143 | 11.9828 | 12.5632 | 417.1367 | 321.2151 | 415.2853 | 0.94996 | 52.05 | 0.24137 | 8.05 | 8.18 |  | 317 | 332 |  | 448.75 |  | 4.6617 | 447.4785 | 29.1586 | 0.029 | 0.204 | 0.787 | 1.491 | -89.4536 | 85.5721 | 1.4769 | 98.0364 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 201.3911 | 201.9078 | 198.8397 | 196.6091 | SDS-THM4b, ug/L | 125.9693 | 127.6201 | 117.8171 | 110.69
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 18:20 | 81.8333 | 23 | 54 | 52 | 272 | 5.25 | 0.63 |  | 5.88 | 0.20791 | 0.89286 | 45.2585 | 11.9828 | 12.5632 | 418.4046 | 322.1914 | 416.5476 | 0.95285 | 52.0472 | 0.24138 | 7.94 | 8.25 |  | 316 | 331 |  | 470 |  | 4.9624 | 468.5138 | 32.5527 | 0.032 | 0.206 | 0.833 | 1.6093 | -93.1973 | 84.0796 | 1.5941 | 97.9926 | [8 empty] | SDS-CDBAA | mg/L | 3.9 | 3.9 | 3.9 | 0 | --- | 1.9357 | --- | -16.4179 | 1.9555 | -99.435 | SDS-CDBAA | mg/L | 5.3 | --- | -9.7 | --- | -58.209 | -9.5618 | 155.4288 | SDS-CDBAA | mg/L | 3.2 | --- | 3.5125 | --- | 4.4776 | 3.5096 | 8.822 | SDS-CDBAA | mg/L | 2.5 | --- | 3.7319 | --- | 25.3731 | 3.7213 | 32.8195 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 18:40 | 106.1667 | 23 | 54 | 52 | 272 | 5.25 | 0.63 |  | 5.88 | 0.20791 | 0.89286 | 45.2585 | 11.9828 | 12.5632 | 418.4046 | 322.1914 | 416.5476 | 0.95285 | 52.0472 | 0.24138 | 7.97 | 8.15 | 8.22 | 321 | 330 | 363 | 428.3333 | -17.9982 | 3.4586 | 427.2975 | 24.8767 | 0.028 | 0.204 | 0.846 | 1.6427 | -94.1686 | 86.0697 | 1.6271 | 98.2791 | [8 empty] | SDS-DCBAA | mg/L | 2.8 | 2.9 | 2.85 | 3.5088 | --- | 28.3857 | --- | 71.5 | 28.1282 | 89.8678 | SDS-DCBAA | mg/L | 4.5 | --- | 46.8077 | --- | 55 | 46.418 | 90.3055 | SDS-DCBAA | mg/L | 2.2 | --- | 18.45 | --- | 78 | 18.3001 | 87.9782 | SDS-DCBAA | mg/L | 1.9 | --- | 13.6391 | --- | 81 | 13.5385 | 85.9659 | SDS-TOXb, ug Cl- /L | 543.513 | 537.4581 | 541.3194 | 540.4167 | SDS-TOXb, ug Cl- /L | 287.8099 | 268.4637 | 280.801 | 277.9167
[32 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-18 | 19:00 | 106.5 | 23 | 54 | 52 | 272 | 5.2 | 0.63 |  | 5.83 | 0.20791 | 0.89194 | 45.6552 | 11.8687 | 12.4435 | 418.2778 | 322.1077 | 416.4393 | 0.95251 | 52.0475 | 0.23908 |  |  |  | 320 | 331 |  | 435.6746 |  | 3.7594 | 434.5689 | 26.3638 | 0.03 | 0.202 | 0.896 | 1.6124 | -79.9585 | 85.0746 | 1.5973 | 98.1218 | [8 empty] | SDS-HAA5 | mg/L | 9 | 8.4 | 8.7 | 6.8966 | --- | 214.4143 | --- | 86.8778 | 212.3396 | 95.9028 | SDS-HAA5 | mg/L | 12.6 | --- | 425.6769 | --- | 80.9955 | 421.8718 | 97.0133 | SDS-HAA5 | mg/L | 6.5 | --- | 131.0833 | --- | 90.1961 | 129.9341 | 94.9975 | SDS-HAA5 | mg/L | 5.1 | --- | 93.7957 | --- | 92.3077 | 93.035 | 94.5182 | SDS-CDb, mg/L | 4.6928 | 4.7487 | 4.7589 | 4.766 | SDS-CDb, mg/L | 2.7123 | 2.8908 | 2.9235 | 2.9461
[44 empty] | 1998-12-18 | 19:20 | 106.8333 | 23 | 54 | 52 | 272 | 5.15 | 0.65 |  | 5.8 | 0.20791 | 0.88793 | 45.8966 | 11.7546 | 12.3239 | 417.7781 | 321.7367 | 415.9597 | 0.95132 | 52.0487 | 0.23678 | 7.91 | 8.05 |  | 318 | 329 |  | 447.3846 |  | 4.3609 | 446.1597 | 28.7251 | 0.031 | 0.2 | 0.926 | 1.5479 | -67.1623 | 84.5771 | 1.5336 | 97.9786 | [8 empty] | SDS-HAA6 | mg/L | 13 | 12.1 | 12.55 | 7.1713 | --- | 254.5143 | --- | 84.3711 | 252.074 | 95.0213 | SDS-HAA6 | mg/L | 18.1 | --- | 496.5615 | --- | 77.4595 | 492.1541 | 96.3223 | SDS-HAA6 | mg/L | 9.3 | --- | 157.2167 | --- | 88.4184 | 155.8522 | 94.0328 | SDS-HAA6 | mg/L | 7.1 | --- | 113.187 | --- | 91.1582 | 112.2771 | 93.6764 | TOCb, mg/L | 5.5862 | 5.5933 | 5.5673 | 5.5341 | TOCb, mg/L | 3.0315 | 3.0542 | 2.9712 | 2.865
[44 empty] | 1998-12-19 | 11:00 | 122.5 | 23 | 54 | 52 | 272 | 4.85 | 0.9 |  | 5.75 | 0.20791 | 0.84348 | 46.3043 | 11.0699 | 11.606 | 412.396 | 317.6739 | 410.7071 | 0.93878 | 52.0612 | 0.22293 | 7.89 | 8.02 |  | 316 | 330 |  | 421.4167 |  | 4.9624 | 420.4768 | 24.8472 | 0.044 | 0.205 | 2.16 | 1.0471 | 51.5252 | 78.1095 | 1.0381 | 95.7615 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.16416 | 0.16298 | 0.16254 | 0.16281 | UV254 b, cm-1 | 0.083305 | 0.079514 | 0.078105 | 0.07899
[44 empty] | 1998-12-19 | 12:00 | 123.5 | 23 | 54 | 52 | 272 | 4.9 | 0.8 |  | 5.7 | 0.20791 | 0.85965 | 46.7193 | 11.184 | 11.7256 | 414.3193 | 319.1417 | 412.6047 | 0.9432 | 52.0568 | 0.22525 | 7.91 | 8.08 |  | 316 | 332 |  | 433.5625 |  | 4.9624 | 432.5036 | 26.937 | 0.046 | 0.206 | 2.164 | 1.1504 | 46.8403 | 77.1144 | 1.1404 | 95.9664 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 195.3385 | 190 | 187.9431 | 187.9902 | Bromideb, ug/L | 207.0573 | 190 | 183.4281 | 183.5784
[44 empty] | 1998-12-19 | 13:00 | 124.5 | 23 | 54 | 52 | 272 | 5 | 0.74 |  | 5.74 | 0.20791 | 0.87108 | 46.3868 | 11.4122 | 11.9649 | 415.7095 | 320.185 | 413.9535 | 0.94646 | 52.0535 | 0.22986 | 7.96 | 8.12 |  | 315 | 331 |  | 450.7432 |  | 5.2632 | 449.4956 | 29.9215 | 0.048 | 0.204 | 2.144 | 1.2348 | 42.4075 | 76.1194 | 1.2239 | 96.078 | [47 empty] | Alkb, mg/L CaCO3 | 426.1302 | 440.4804 | 420.9916 | 417.8775 | Alkb, mg/L CaCO3 | 389.099 | 434.9497 | 372.6806 | 362.7304
[44 empty] | 1998-12-19 | 14:00 | 125.5 | 23 | 54 | 52 | 272 | 4.95 | 3.65 |  | 8.6 | 0.20791 | 0.57558 | 30.6279 | 11.2981 | 11.8453 | 383.1713 | 295.1363 | 381.5692 | 0.87234 | 52.1277 | 0.22724 | 7.98 | 8.04 | 8.15 | 308 | 330 | 391 | 365.726 | 6.4639 | 7.3684 | 365.2008 | 15.6628 | 0.043 | 0.209 | 1.462 | 0.41527 | 71.5955 | 78.607 | 0.41189 | 89.5602 | [47 empty] | T-Hdb, mg/L CaCO3 | 275.1094 | 285.0838 | 271.1906 | 271.5294 | T-Hdb, mg/L CaCO3 | 251.2031 | 283.0726 | 238.6823 | 239.7647
[44 empty] | 1998-12-19 | 14:30 | 126 | 23 | 54 | 52 | 272 | 4.96 | 3.92 |  | 8.88 | 0.20791 | 0.55856 | 29.6306 | 11.3209 | 11.8692 | 381.4537 | 293.8108 | 379.8555 | 0.86844 | 52.1316 | 0.22768 | 8.03 | 8.1 | 8.21 | 311 | 331 | 433 | 359.7041 | 16.9275 | 6.4662 | 359.26 | 13.4332 | 0.034 | 0.213 | 1.034 | 0.41231 | 60.1251 | 83.0846 | 0.40886 | 91.6841 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 252.9531 | 258.6257 | 249.7157 | 248.3431 | Ca-Hdb, mg/L CaCO3 | 237.4844 | 255.6089 | 227.1405 | 222.7549
[44 empty] | 1998-12-19 | 15:00 | 126.5 | 23 | 54 | 52 | 272 | 5 | 4.05 |  | 9.05 | 0.20791 | 0.55249 | 29.0552 | 11.4122 | 11.9649 | 380.8505 | 293.3361 | 379.2417 | 0.8671 | 52.1329 | 0.22951 | 8.08 | 8.18 | 8.3 | 308 | 331 | 374 | 362.7469 | 3.0088 | 7.3684 | 362.2437 | 14.9744 | 0.031 | 0.211 | 0.811 | 0.41088 | 49.337 | 84.5771 | 0.40739 | 92.3905 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-12-19 | 15:30 | 127 | 23 | 54 | 52 | 272 | 5 | 4.88 |  | 9.88 | 0.20791 | 0.50607 | 26.5304 | 11.4122 | 11.9649 | 376.2541 | 289.796 | 374.6648 | 0.85664 | 52.1434 | 0.22946 | 8.2 | 8.25 | 8.23 | 306 | 331 | 363 | 359.6516 | 0.92241 | 7.9699 | 359.1585 | 14.8009 | 0.031 | 0.21 | 0.648 | 0.37518 | 42.1018 | 84.5771 | 0.37202 | 91.667 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-12-19 | 16:00 | 127.5 | 23 | 54 | 52 | 272 | 5 | 4.9 |  | 9.9 | 0.20791 | 0.50505 | 26.4747 | 11.4122 | 11.9649 | 376.1541 | 289.7189 | 374.5653 | 0.85641 | 52.1436 | 0.22946 | 8.21 | 8.29 | 8.35 | 304 | 330 | 357 | 361.5816 | -1.2834 | 8.5714 | 361.0524 | 15.8017 | 0.031 | 0.21 | 0.536 | 0.37447 | 30.1363 | 84.5771 | 0.37131 | 91.6512 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-12-20 | 11:30 | 147 | 23 | 54 | 52 | 272 | 4.9 | 4.85 |  | 9.75 | 0.20791 | 0.50256 | 26.8974 | 11.184 | 11.7256 | 375.897 | 289.5458 | 374.3414 | 0.85573 | 52.1443 | 0.22487 | [66 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-12-20 | 12:00 | 147.5 | 23 | 54 | 52 | 272 | 4.8 | 12.2 |  | 17 | 0.20791 | 0.28235 | 15 | 10.9557 | 11.4863 | 355.5555 | 273.9007 | 354.1145 | 0.80934 | 52.1907 | 0.22008 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-12-20 | 13:00 | 148.5 | 23 | 52 | 50 | 272 | 4.85 | 12.1 |  | 16.95 | 0.20791 | 0.28614 | 15.0472 | 11.0699 | 11.606 | 355.8897 | 274.1464 | 354.4321 | 0.81015 | 50.1899 | 0.23124 | 7.78 | 7.81 | 8.02 | 299 | 332 | 343 | 345.9277 | -0.85355 | 10.0752 | 345.5093 | 13.4611 | BMRL | 0.197 | 0.282 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-12-20 | 13:30 | 149 | 23 | 52 | 50 | 272 | 4.8 | 11.8 |  | 16.6 | 0.20791 | 0.28916 | 15.3855 | 10.9557 | 11.4863 | 356.1505 | 274.3591 | 354.7072 | 0.8107 | 50.1893 | 0.22886 | 7.85 | 8.02 | 8.13 | 295 | 331 | 340 | 347.7542 | -2.2807 | 11.2782 | 347.2888 | 15.0563 | 0.009 | 0.2 | 0.276 | 0.2791 | -1.1238 | 95.5224 | 0.27672 | 96.7476 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-12-20 | 14:00 | 149.5 | 23 | 52 | 50 | 272 | 4.8 | 11.7 |  | 16.5 | 0.20791 | 0.29091 | 15.4848 | 10.9557 | 11.4863 | 356.3041 | 274.4774 | 354.8601 | 0.81105 | 50.189 | 0.22886 | 7.82 | 8.05 | 8.21 | 280 | 330 | 339 | 354.0385 | -4.4361 | 15.7895 | 353.3852 | 20.7663 | BMRL | 0.201 | 0.276 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-12-20 | 14:30 | 150 | 23 | 52 | 50 | 272 | 4.8 | 11.5 |  | 16.3 | 0.20791 | 0.29448 | 15.6871 | 10.9557 | 11.4863 | 356.6174 | 274.7187 | 355.1721 | 0.81176 | 50.1882 | 0.22887 | 7.9 | 8.07 | 8.24 | 281 | 331 | 340 | 353.9957 | -4.1164 | 15.4887 | 353.3516 | 20.4758 | 0.01 | 0.2 | 0.28 | 0.28072 | -0.25776 | 95.0249 | 0.27833 | 96.4072 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-12-20 | 15:00 | 150.5 | 23 | 52 | 50 | 272 | 4.84 | 11.4 |  | 16.24 | 0.20791 | 0.29803 | 15.7488 | 11.047 | 11.5821 | 356.9326 | 274.9521 | 355.4738 | 0.81251 | 50.1875 | 0.23078 | 8.01 | 8.2 | 8.29 | 281 | 330 | 341 | 354.3649 | -3.9193 | 15.4887 | 353.7122 | 20.5569 | 0.011 | 0.202 | 0.284 | 0.28167 | 0.8216 | 94.5274 | 0.27926 | 96.061 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-12-20 | 15:30 | 151 | 23 | 52 | 50 | 272 | 4.85 | 11.3 |  | 16.15 | 0.20791 | 0.30031 | 15.8421 | 11.0699 | 11.606 | 357.1341 | 275.105 | 355.6715 | 0.81298 | 50.187 | 0.23125 | 8.14 | 8.2 | 8.35 | 280 | 331 | 339 | 355.0332 | -4.7296 | 15.7895 | 354.3642 | 20.9853 | 0.011 | 0.201 | 0.283 | 0.28255 | 0.15948 | 94.5274 | 0.28013 | 96.0732 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-12-21 | 8:30 | 168 | 23 | 52 | 50 | 272 | 4.65 | 10.4 |  | 15.05 | 0.20791 | 0.30897 | 17.0731 | 10.6134 | 11.1274 | 357.8831 | 275.7293 | 356.4786 | 0.81452 | 50.1855 | 0.22173 | 7.48 | 7.41 | 7.33 | 283 | 329 | 342 | 354.6322 | -3.6936 | 14.8872 | 354.0199 | 20.061 | 0.012 | 0.203 | 0.286 | 0.2855 | 0.17314 | 94.0299 | 0.28317 | 95.7622 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-12-21 | 9:15 | 168.75 | 23 | 52 | 50 | 272 | 4.65 | 10.4 |  | 15.05 | 0.20791 | 0.30897 | 17.0731 | 10.6134 | 11.1274 | 357.8831 | 275.7293 | 356.4786 | 0.81452 | 50.1855 | 0.22173 | 7.42 | 7.38 | 7.36 | 283 | 331 | 343 | 354.6322 | -3.3913 | 14.8872 | 354.0199 | 20.061 | 0.012 | 0.204 | 0.289 | 0.2855 | 1.2094 | 94.0299 | 0.28317 | 95.7622
[44 empty] | 1998-12-21 | 9:30 | 169 | 23 | 52 | 50 | 272 | 4.65 | 10.4 | X | 15.05 | 0.20791 | 0.30897 | 17.0731 | 10.6134 | 11.1274 | 357.8831 | 275.7293 | 356.4786 | 0.81452 | 50.1855 | 0.22173
[44 empty] | 1998-12-21 | 16:45 |  | 23 | 56 | 55 | 272 | 4.8 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 10.9557 | 11.4863 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-21 | 17:00 |  | 23 | 64 | 62 | 272 | 5.55 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 12.6676 | 13.2811 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-21 | 17:15 |  | 23 | 44 | 4 | 272 | 3.64 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 8.3081 | 8.7105 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-21 | 17:30 |  | 23 | 35 | 32 | 272 | 2.9 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 6.6191 | 6.9397 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-22 | 14:00 |  | 23 | 55 | 53 | 272 | 6 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 13.6947 | 14.3579 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-22 | 14:15 |  | 23 | 64 | 62 | 272 | 7.1 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 16.2054 | 16.9902 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-22 | 14:30 |  | 23 | 44 | 42 | 272 | 4.5 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 10.271 | 10.7684 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-22 | 14:45 |  | 23 | 34 | 28 | 272 | 3.6 | NA |  | #VALUE! | 0.20791 | #VALUE! | #VALUE! | 8.2168 | 8.6147 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on U3: C. Rice: Cartridge filtration was the only membrane pretreatment employed.
Note on CY25: C. Rice: Bromide concentrations verified by consultant.

## 7450. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Hydranautics Corp., San Diego, CA | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.21363 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.87 | [7 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | NTR7450 | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1999-03-23 | 1999-03-31 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 9.65 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.51 | [7 empty] | Feed flow rate during sample collection (mL/min) | 12.32 | [7 empty] | Feed flow rate during sample collection (mL/min) | 19.51 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | ~ 1,000 Da | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 0:00 | 0:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 281 | [10 empty] | Influent flow rate during sample collection (mL/min) | 281 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [6 empty] | SDS-THM4F, ug/L | 192.3 | 192.3 | 192.3 | 192.3 | SDS-THM4F, ug/L | 192.3 | 192.3 | 192.3 | 192.3 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Modified Polysulfone | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 61.1 | 71.3 | 48.6 | 41.6 | SDS-THM4p, ug/L | 61.1 | 71.3 | 48.6 | 41.6 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin Film Composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.4 | 7.8 | 8.1 | 7.4074 | 1999-03-31 | 9:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-01 | 10:00 | 0 | 24 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 56.15 | 56.15 | 56.15 | 56.15 | SDS-HAA5F, ug/L | 56.15 | 56.15 | 56.15 | 56.15 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | Hydrophobic | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.31624 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1999-03-31 | 10:00 | 1 | 24 | 60 | 58 | 281 | 5.9 | 2.97 | 8.87 | 0.21479 | 0.66516 | 30.6798 | 13.4664 | 13.7074 | 0 | 0 | 0 | 0 | 59 | 0.23233 | 1999-04-01 | 11:00 | 1 | 24 | 63 | 61 | 281 | 7.37 | 3.17 |  | 10.54 | 0.21479 | 0.69924 | 25.6603 | 16.8216 | 17.1226 | 359.3034 | 280.9279 | 357.2478 | 0.77348 | 61.2265 | 0.27966 |  |  |  | 242 | 304 | 276 | 449.8076 | -62.9738 | 20.5255 | 447.0824 | 45.8713 | 0.021 | 0.165 | 0.202 | 0.4682 | -131.7831 | 86.4952 | 0.46234 | 95.4579 | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 9.35 | 11.5 | 8.2 | 5.4 | SDS-HAA5p, ug/L | 9.35 | 11.5 | 8.2 | 5.4 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 216 | 218 | 217 | 0.92166 | 1999-03-31 | 11:00 | 2 | 24 | 64 | 62 | 281 | 6.8 | 2.52 | 9.32 | 0.21479 | 0.72961 | 29.1502 | 15.5206 | 15.7984 | 0 | 0 | 0 | 0 | 63 | 0.25077 | 1999-04-01 | 12:00 | 2 | 24 | 63 | 61 | 281 | 7.33 | 3.16 |  | 10.49 | 0.21479 | 0.69876 | 25.7874 | 16.7303 | 17.0297 | 359.2516 | 280.8963 | 357.2076 | 0.77333 | 61.2267 | 0.27814 |  |  |  | 279 | 305 | 315 | 363.6503 | -15.4445 | 8.3744 | 362.5462 | 23.0443 | 0.03 | 0.166 | 0.316 | 0.44661 | -41.333 | 80.7074 | 0.44118 | 93.2 | [8 empty] | Sampling date | MM/DD/YY | 1999-04-02 | 1999-04-03 | --- | --- | 1999-04-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-04 | 1999-04-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-05 | 1999-04-05 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-04-06 | 1999-04-06 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 505 | 505 | 505 | 505 | SDS-TOXF, ug Cl- /L | 505 | 505 | 505 | 505 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 304 | 305 | 304.5 | 0.32841 | 1999-03-31 | 12:00 | 3 | 24 | 64 | 62 | 281 | 6.93 | 2.97 | 9.9 | 0.21479 | 0.7 | 27.3838 | 15.8174 | 16.1004 | 0 | 0 | 0 | 0 | 63 | 0.25556 | 1999-04-01 | 13:00 | 3 | 24 | 63 | 61 | 281 | 7.23 | 3.14 |  | 10.37 | 0.21479 | 0.6972 | 26.0974 | 16.5021 | 16.7974 | 359.0893 | 280.7918 | 357.0747 | 0.7729 | 61.2271 | 0.27435 |  |  |  | 282 | 305 | 325 | 356.3073 | -9.633 | 7.3892 | 355.3514 | 20.6419 | 0.033 | 0.165 | 0.396 | 0.43756 | -10.4955 | 78.7781 | 0.43236 | 92.3674 | [8 empty] | Sampling time | hh:mm | 9:00 | 10:00 | --- | --- | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:00 | 19:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 90.5 | 95 | 70 | 64 | SDS-TOXp, ug Cl- /L | 90.5 | 95 | 70 | 64 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 250 | 254 | 252 | 1.5873 | 1999-03-31 | 13:00 | 4 | 24 | 63 | 61 | 281 | 7.2 | 2.69 | 9.89 | 0.21479 | 0.72801 | 27.4125 | 16.4336 | 16.7277 | 0 | 0 | 0 | 0 | 62 | 0.2698 | 1999-04-01 | 14:00 | 4 | 24 | 63 | 61 | 281 | 7.14 | 3.13 |  | 10.27 | 0.21479 | 0.69523 | 26.3612 | 16.2967 | 16.5883 | 358.8906 | 280.6565 | 356.9027 | 0.7724 | 61.2276 | 0.27093 |  |  |  | 298 | 304 | 328 | 319.3275 | 2.6441 | 2.1346 | 319.0565 | 6.5996 | 0.033 | 0.166 | 0.414 | 0.43494 | -5.0582 | 78.7781 | 0.42983 | 92.3226 | [8 empty] | Operation time | hh.hh | 23 | 48 | --- | --- | 23 | --- | --- | --- | --- | --- | Operation time | hh.hh | 81 | 81 | --- | --- | --- | --- | --- | Operation time | hh.hh | 98 | 98 | --- | --- | --- | --- | --- | Cumulative time | hr | 127 | 127 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 5.625 | 5.625 | 5.625 | 5.625 | SDS-CDF, mg/L | 5.625 | 5.625 | 5.625 | 5.625 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 45 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 236 | 238 | 237 | 0.84388 | 1999-03-31 | 14:00 | 5 | 24 | 63 | 61 | 281 | 7.2 | 3.2 | 10.4 | 0.21479 | 0.69231 | 26.0192 | 16.4336 | 16.7277 | 0 | 0 | 0 | 0 | 62 | 0.2698 | 1999-04-01 | 15:00 | 5 | 24 | 63 | 61 | 281 | 7.17 | 3.09 |  | 10.26 | 0.21479 | 0.69883 | 26.3879 | 16.3651 | 16.658 | 359.2285 | 280.9141 | 357.2302 | 0.77315 | 61.2268 | 0.27207 |  |  |  | 287 | 305 | 327 | 345.1068 | -5.5372 | 5.7471 | 344.3655 | 16.6583 | 0.034 | 0.166 | 0.427 | 0.43743 | -2.442 | 78.135 | 0.43228 | 92.1347 | [8 empty] | pH | --- | 8.2 | 8.2 | 8.2 | 0 | 8.3 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8.3 | --- | --- | --- | --- | --- | pH | --- | 7.9 | 8.2 | --- | --- | --- | --- | --- | pH | --- | 8.1 | 8.2 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.5 | 1.6 | 1.29 | 1.11 | SDS-CDp, mg/L | 1.5 | 1.6 | 1.29 | 1.11 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 140 | 1 | 0.7 | 15 | 15.1667 | 62.5992 | 485.129 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.165 | 0.138 | 0.1515 | 17.8218 | 1999-03-31 | 15:00 | 6 | 24 | 63 | 61 | 281 | 7.27 | 3.14 | 10.41 | 0.21479 | 0.69837 | 25.9933 | 16.5934 | 16.8903 | 0 | 0 | 0 | 0 | 62 | 0.27242 | 1999-04-01 | 16:00 | 6 | 24 | 63 | 61 | 281 | 7.08 | 3.06 |  | 10.14 | 0.21479 | 0.69822 | 26.712 | 16.1597 | 16.4489 | 359.156 | 280.8775 | 357.1837 | 0.77292 | 61.2271 | 0.26865 |  |  |  | 286 | 304 | 326 | 347.3039 | -6.5349 | 6.0755 | 346.5316 | 17.4678 | 0.034 | 0.165 | 0.431 | 0.43662 | -1.3034 | 78.135 | 0.43155 | 92.1213 | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 5.9 | 5.9 | 5.9 | 5.9 | TOCF, mg/L | 5.9 | 5.9 | 5.9 | 5.9 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.32 | 2 | 0.9 | 15 | 38.5 | 85.9325 | 485.129 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-03-31 | 16:00 | 7 | 24 | 63 | 61 | 281 | 7.33 | 2.83 | 10.16 | 0.21479 | 0.72146 | 26.6575 | 16.7303 | 17.0297 | 0 | 0 | 0 | 0 | 62 | 0.27467 | 1999-04-01 | 17:00 | 7 | 24 | 63 | 61 | 281 | 7.03 | 2.99 |  | 10.02 | 0.21479 | 0.7016 | 27.0439 | 16.0456 | 16.3327 | 359.4583 | 281.1251 | 357.4986 | 0.77353 | 61.2265 | 0.26676 |  |  |  | 284 | 304 | 326 | 352.699 | -8.1899 | 6.7323 | 351.8396 | 19.2814 | 0.034 | 0.15 | 0.443 | 0.44117 | 0.41372 | 78.135 | 0.43607 | 92.2032 | [8 empty] | Alkalinity | mg/L as CaCO3 | 204 | 198 | 201 | 2.9851 | 252 | 252.6129 | -0.24322 | 7.3733 | 252.0014 | 20.2385 | Alkalinity | mg/L as CaCO3 | 208 | 246 | 277.2308 | -12.6954 | 4.1475 | 276.4259 | 24.7538 | Alkalinity | mg/L as CaCO3 | 206 | 238 | 227.5686 | 4.3829 | 5.0691 | 227.3369 | 9.3856 | Alkalinity | mg/L as CaCO3 | 196 | 230 | 226 | 1.7391 | 9.6774 | 225.6876 | 13.1543 | TOCp, mg/L | 1.45 | 1.7 | 0.9 | 0.8 | TOCp, mg/L | 1.45 | 1.7 | 0.9 | 0.8 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 57.9325 | 485.129 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 5.5 | 6.3 | 5.9 | 13.5593 | 1999-03-31 | 17:00 | 8 | 24 | 63 | 61 | 281 | 7.27 | 4.22 | 11.49 | 0.21479 | 0.63272 | 23.456 | 16.5934 | 16.8903 | 0 | 0 | 0 | 0 | 62 | 0.27242 | 1999-04-02 | 9:00 | 23 | 24 | 63 | 61 | 281 | 6.65 | 2.56 |  | 9.21 | 0.21479 | 0.72204 | 29.5103 | 15.1783 | 15.4499 | 361.2858 | 282.6396 | 359.4246 | 0.77716 | 61.2228 | 0.25235 |  |  |  | 293 | 304 | 330 | 334.373 | -1.3252 | 3.7767 | 333.8835 | 12.2448 | 0.03 | 0.168 | 0.505 | 0.48151 | 4.6523 | 80.7074 | 0.47616 | 93.6996 | [8 empty] | Total dissolved solids | mg/L | 279 | 280 | 279.5 | 0.35778 | 326 | 360.1452 | -10.474 | 8.2102 | 359.1897 | 22.186 | Total dissolved solids | mg/L | 293 | 338 | 381.4615 | -12.8584 | 3.7767 | 380.4331 | 22.9825 | Total dissolved solids | mg/L | 278 | 321 | 329.9608 | -2.7915 | 8.7028 | 329.4026 | 15.6048 | Total dissolved solids | mg/L | 268 | 311 | 320.1429 | -2.9398 | 11.9869 | 319.5998 | 16.1451 | UV254 F, cm-1 | 0.1555 | 0.1555 | 0.1555 | 0.1555 | UV254 F, cm-1 | 0.1555 | 0.1555 | 0.1555 | 0.1555 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 365 | 4 | 0.3 | 15 | 8.5 | 55.9325 | 485.129 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.155 | 0.156 | 0.1555 | 0.64309 | 1999-04-01 | 9:00 | 24 | 24 | 63 | 61 | 281 | 7.27 | 2.71 | 9.98 | 0.21479 | 0.72846 | 27.1563 | 16.5934 | 16.8903 | 0 | 0 | 0 | 0 | 62 | 0.27242 | 1999-04-02 | 10:00 | 24 | 24 | 63 | 61 | 281 | 6.69 | 3.77 |  | 10.46 | 0.21479 | 0.63958 | 25.8642 | 15.2696 | 15.5428 | 353.758 | 276.7418 | 351.9244 | 0.76099 | 61.239 | 0.25381 |  |  |  | 280 | 304 | 327 | 347.9761 | -6.4147 | 8.046 | 347.1669 | 19.3472 | 0.029 | 0.167 | 0.466 | 0.37998 | 18.4595 | 81.3505 | 0.3758 | 92.2831 | [8 empty] | Total hardness | mg/L as CaCO3 | 224 | 226 | 225 | 0.88889 | 289 | 312.0968 | -7.992 | 10.7143 | 311.0649 | 27.6678 | Total hardness | mg/L as CaCO3 | 246 | 318 | 292.1538 | 8.1277 | 2.381 | 291.6173 | 15.6429 | Total hardness | mg/L as CaCO3 | 228 | 274 | 275.0588 | -0.38643 | 9.5238 | 274.5533 | 16.956 | Total hardness | mg/L as CaCO3 | 220 | 270 | 265.7143 | 1.5873 | 12.6984 | 265.2382 | 17.0557 | UV254 p, cm-1 | 0.028 | 0.031 | 0.015 | 0.01 | UV254 p, cm-1 | 0.028 | 0.031 | 0.015 | 0.01 | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | 800 | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.8182 | 2.4762 | 2.6472 | 12.9191 | 1999-04-01 | 9:15 | 24.25 | 24 | 71 | 70 | 281 | 8.33 | 2.89 | 11.22 | 0.21479 | 0.74242 | 24.0446 | 19.0128 | 19.353 | 0 | 0 | 0 | 0 | 70.5 | 0.27451 | 1999-04-02 | 11:00 | 25 | 24 | 63 | 61 | 281 | 6.69 | 3.68 |  | 10.37 | 0.21479 | 0.64513 | 26.0974 | 15.2696 | 15.5428 | 354.2554 | 277.1308 | 352.4192 | 0.76206 | 61.2379 | 0.25381 |  |  |  | 282 | 304 | 324 | 345.4035 | -6.606 | 7.3892 | 344.6488 | 18.1776 | 0.028 | 0.166 | 0.417 | 0.38729 | 7.1255 | 81.9936 | 0.38301 | 92.6895 | [8 empty] | Calcium hardness | mg/L as CaCO3 | 220 | 222 | 221 | 0.90498 | 279 | 272.6129 | 2.2893 | 6.7511 | 272.0014 | 18.7504 | Calcium hardness | mg/L as CaCO3 | 238 | 304 | 230.3077 | 24.2409 | -0.42194 | 230.3971 | -3.2999 | Calcium hardness | mg/L as CaCO3 | 222 | 268 | 251.4118 | 6.1896 | 6.3291 | 251.0958 | 11.5875 | Calcium hardness | mg/L as CaCO3 | 210 | 260 | 248.5714 | 4.3956 | 11.3924 | 248.1697 | 15.3805 | BromideF, ug/L | 170 | 170 | 170 | 170 | BromideF, ug/L | 170 | 170 | 170 | 170 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 75 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 170 | 170 | 170 | 0 | 1999-04-01 | 9:40 | 24.6667 | 24 | 50 | 48 | 281 | 5.8 | 2.43 | 8.23 | 0.21479 | 0.70474 | 33.1434 | 13.2382 | 13.4751 | 0 | 0 | 0 | 0 | 49 | 0.275 | 1999-04-02 | 12:00 | 26 | 24 | 63 | 61 | 281 | 6.69 | 3.77 |  | 10.46 | 0.21479 | 0.63958 | 25.8642 | 15.2696 | 15.5428 | 353.758 | 276.7418 | 351.9244 | 0.76099 | 61.239 | 0.25381 |  |  |  | 280 | 304 | 326 | 347.9761 | -6.7411 | 8.046 | 347.1669 | 19.3472 | 0.027 | 0.166 | 0.403 | 0.38353 | 4.8318 | 82.6367 | 0.37928 | 92.8813 | [8 empty] | Turbidity | ntu | 0.069 | 0.079 | 0.074 | 13.5135 | 0.17 | 0.324 | -90.5882 | 51.1551 | 0.32104 | 76.9498 | Turbidity | ntu | 0.054 | 0.202 | 0.804 | -298.0198 | 64.3564 | 0.79528 | 93.2099 | Turbidity | ntu | 0.051 | 0.15 | 0.24806 | -65.3725 | 66.3366 | 0.24594 | 79.2634 | Turbidity | ntu | 0.051 | 0.166 | 0.19457 | -17.2117 | 66.3366 | 0.19308 | 73.5856 | Bromidep, ug/L | 160 | 160 | 150 | 150 | Bromidep, ug/L | 160 | 160 | 150 | 150 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 25 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 6.5 | 6.5 | 6.5 | 0 | 1999-04-01 | 10:00 | 25 | 24 | 64 | 62 | 281 | 7.45 | 2.76 | 10.21 | 0.21479 | 0.72968 | 26.522 | 17.0042 | 17.3085 | 0 | 0 | 0 | 0 | 63 | 0.27474 | 1999-04-02 | 13:00 | 27 | 24 | 63 | 61 | 281 | 6.74 | 3.58 |  | 10.32 | 0.21479 | 0.6531 | 26.2287 | 15.3837 | 15.659 | 354.9804 | 277.687 | 353.1264 | 0.76366 | 61.2363 | 0.25571 |  |  |  | 283 | 304 | 321 | 344.9777 | -7.4697 | 7.0608 | 344.2344 | 17.7886 | 0.028 | 0.166 | 0.41 | 0.39554 | 3.5264 | 81.9936 | 0.39113 | 92.8413 | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217 | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 64.3739 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.91 | 0.84 | 0.875 | 8 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-02 | 14:00 | 28 | 24 | 63 | 61 | 281 | 6.73 | 3.36 |  | 10.09 | 0.21479 | 0.667 | 26.8494 | 15.3609 | 15.6357 | 356.2352 | 278.6708 | 354.3775 | 0.76636 | 61.2336 | 0.25535 |  |  |  | 282 | 304 | 325 | 349.567 | -7.5591 | 7.3892 | 348.7578 | 19.1416 | 0.028 | 0.168 | 0.414 | 0.41088 | 0.75375 | 81.9936 | 0.40629 | 93.1084 | [8 empty] | Total organic carbon | mg/L | 1.4 | 1.5 | 1.45 | 6.8966 | 12.5 | 15.8048 | -26.4387 | 75.4237 | 15.6348 | 90.7258 | Total organic carbon | mg/L | 1.7 | 25.3 | 34.0077 | -34.4178 | 71.1864 | 33.6321 | 94.9453 | Total organic carbon | mg/L | 0.9 | 9.1 | 10.7039 | -17.6255 | 84.7458 | 10.5986 | 91.5083 | Total organic carbon | mg/L | 0.8 | 6.9 | 8.0857 | -17.1843 | 86.4407 | 8.0098 | 90.0123 | Alkp, mg/L CaCO3 | 201 | 208 | 206 | 196 | Alkp, mg/L CaCO3 | 201 | 208 | 206 | 196
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0023333 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 5.59 | 5.66 | 5.625 | 1.2444 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-02 | 16:00 | 30 | 24 | 63 | 61 | 281 | 6.68 | 2.98 |  | 9.66 | 0.21479 | 0.69151 | 28.089 | 15.2467 | 15.5196 | 358.4647 | 280.4259 | 356.6095 | 0.77111 | 61.2289 | 0.25347 |  |  |  | 282 | 304 | 325 | 354.9362 | -9.2112 | 7.3892 | 354.0693 | 20.3546 | 0.027 | 0.166 | 0.428 | 0.44355 | -3.6325 | 82.6367 | 0.4386 | 93.844 | [8 empty] | UV254 | cm-1 | 0.03 | 0.026 | 0.028 | 14.2857 | 0.47 | 0.43929 | 6.534 | 81.9936 | 0.43442 | 93.5546 | UV254 | cm-1 | 0.031 | 0.874 | 0.98869 | -13.1227 | 80.0643 | 0.97756 | 96.8288 | UV254 | cm-1 | 0.015 | 0.311 | 0.29049 | 6.5948 | 90.3537 | 0.28753 | 94.7832 | UV254 | cm-1 | 0.01 | 0.228 | 0.21786 | 4.4486 | 93.5691 | 0.21569 | 95.3638 | T-HdF, mg/L CaCO3 | 252 | 252 | 252 | 252 | T-HdF, mg/L CaCO3 | 252 | 252 | 252 | 252
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-02 | 17:00 | 31 | 24 | 63 | 61 | 281 | 6.74 | 2.94 |  | 9.68 | 0.21479 | 0.69628 | 28.0289 | 15.3837 | 15.659 | 358.9143 | 280.7644 | 357.0399 | 0.77213 | 61.2279 | 0.25575 |  |  |  | 273 | 304 | 322 | 376.7143 | -16.992 | 10.3448 | 375.4705 | 27.2912 | 0.026 | 0.165 | 0.443 | 0.45238 | -2.1176 | 83.2797 | 0.44727 | 94.1869 | [8 empty] | SUVA | L/(mg*m) | 2.1429 | 1.7333 | 1.9381 | 21.1302 | 3.76 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.8235 | 3.4545 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.6667 | 3.4176 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.25 | 3.3043 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 225 | 246 | 228 | 220 | T-Hdp, mg/L CaCO3 | 225 | 246 | 228 | 220
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 10:00 | 48 | 24 | 63 | 61 | 281 | 6.45 | 1.56 |  | 8.01 | 0.21479 | 0.80524 | 34.0811 | 14.7218 | 14.9852 | 369.1754 | 288.8576 | 367.3318 | 0.79396 | 61.206 | 0.24483 |  |  |  | 280 | 304 | 327 | 405.7981 | -24.0973 | 8.046 | 404.3543 | 30.7538 | 0.03 | 0.165 | 0.64 | 0.67439 | -5.3741 | 80.7074 | 0.667 | 95.5022 | [8 empty] | Bromide | mg/L | 160 | 160 | 160 | 0 | --- | 192.2581 | --- | 5.8824 | 191.8759 | 16.6128 | Bromide | mg/L | 160 | --- | 236.9231 | --- | 5.8824 | 236.0288 | 32.2117 | Bromide | mg/L | 150 | --- | 189.2157 | --- | 11.7647 | 188.7944 | 20.5485 | Bromide | mg/L | 150 | --- | 178.5714 | --- | 11.7647 | 178.2739 | 15.8598 | Ca-HdF, mg/L CaCO3 | 237 | 237 | 237 | 237 | Ca-HdF, mg/L CaCO3 | 237 | 237 | 237 | 237
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | NA | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 11:00 | 49 | 24 | 63 | 61 | 281 | 6.45 | 2.94 |  | 9.39 | 0.21479 | 0.6869 | 28.9255 | 14.7218 | 14.9852 | 358.0003 | 280.1138 | 356.2125 | 0.76993 | 61.2301 | 0.24474 |  |  |  | 278 | 303 | 329 | 362.6378 | -10.2242 | 8.7028 | 361.6664 | 23.1336 | 0.029 | 0.165 | 0.618 | 0.43303 | 29.9311 | 81.3505 | 0.42839 | 93.2304 | [8 empty] | SDS-Cl2 dose | mg/L | 2.5 | 2.5 | 2.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 221 | 238 | 222 | 210 | Ca-Hdp, mg/L CaCO3 | 221 | 238 | 222 | 210
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | NA | [13 empty] | SDS-TOX | mg Cl- /L | 535 | 475 | 505 | 11.8812 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 12:00 | 50 | 24 | 63 | 61 | 281 | 6.57 | 2.74 |  | 9.31 | 0.21479 | 0.70569 | 29.1826 | 14.9957 | 15.264 | 359.7518 | 281.4574 | 357.9212 | 0.77379 | 61.2262 | 0.2493 |  |  |  | 280 | 304 | 330 | 363.2464 | -10.0747 | 8.046 | 362.2732 | 22.7103 | 0.026 | 0.165 | 0.55 | 0.46602 | 15.2697 | 83.2797 | 0.46087 | 94.3585 | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.05 | 0.95 | 1 | 10 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.9 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.21 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.39 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 25 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 140 | 110 | 125 | 24 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 13:00 | 51 | 24 | 63 | 61 | 281 | 6.51 | 2.87 |  | 9.38 | 0.21479 | 0.69403 | 28.9574 | 14.8587 | 15.1246 | 358.6652 | 280.6207 | 356.8572 | 0.7714 | 61.2286 | 0.24702 |  |  |  | 281 | 304 | 330 | 357.8049 | -8.4257 | 7.7176 | 356.9152 | 21.2698 | 0.026 | 0.165 | 0.495 | 0.44924 | 9.2437 | 83.2797 | 0.44434 | 94.1486 | [8 empty] | SDS-Cl2 demand | mg/L | 1.45 | 1.55 | 1.5 | 6.6667 | --- | 14.8065 | --- | 73.3333 | 14.6488 | 89.7603 | SDS-Cl2 demand | mg/L | 1.6 | --- | 32.5615 | --- | 71.5556 | 32.2016 | 95.0313 | SDS-Cl2 demand | mg/L | 1.29 | --- | 9.79 | --- | 77.0667 | 9.6987 | 86.6992 | SDS-Cl2 demand | mg/L | 1.11 | --- | 7.56 | --- | 80.2667 | 7.4928 | 85.1858 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 49 | 48 | 48.5 | 2.0619 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 14:00 | 52 | 24 | 63 | 61 | 281 | 6.51 | 2.81 |  | 9.32 | 0.21479 | 0.6985 | 29.1502 | 14.8587 | 15.1246 | 359.0764 | 280.9424 | 357.2663 | 0.77229 | 61.2277 | 0.24702 |  |  |  | 281 | 304 | 329 | 358.9431 | -9.1012 | 7.7176 | 358.0402 | 21.5172 | 0.027 | 0.166 | 0.496 | 0.4532 | 8.6292 | 82.6367 | 0.44826 | 93.9767 | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 91.6921 | 99.4215 | 83.7161 | 79.8275 | Qp/QT (THM4), % | 119.1311 | 129.1736 | 108.7683 | 103.716
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 50% rejection of 2,000 ppm | [13 empty] | SDS-DBCM | mg/L | 18 | 18 | 18 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 15:00 | 53 | 24 | 63 | 61 | 281 | 6.51 | 2.6 |  | 9.11 | 0.21479 | 0.7146 | 29.8452 | 14.8587 | 15.1246 | 360.5662 | 282.108 | 358.7485 | 0.77549 | 61.2245 | 0.24704 |  |  |  | 283 | 304 | 331 | 358.3327 | -8.2576 | 7.0608 | 357.4601 | 20.8303 | 0.026 | 0.165 | 0.49 | 0.47975 | 2.0922 | 83.2797 | 0.47449 | 94.5205 | [8 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | NA | NA | NA | NA
|  | (e.g., solute type and concentration) | NaCl solution | [13 empty] | SDS-CHBr3 | mg/L | 0.8 | 0.8 | 0.8 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 16:00 | 54 | 24 | 63 | 61 | 281 | 6.55 | 3.17 |  | 9.72 | 0.21479 | 0.67387 | 27.9095 | 14.95 | 15.2175 | 356.8284 | 279.1747 | 355.0183 | 0.76749 | 61.2325 | 0.24852 |  |  |  | 281 | 304 | 330 | 353.0568 | -6.9869 | 7.7176 | 352.217 | 20.2196 | 0.024 | 0.165 | 0.472 | 0.42721 | 9.4891 | 84.5659 | 0.42251 | 94.3197 | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 13.2381 | 11.7583 | 16.0081 | 15.6376 | SDS-HAA5b, ug/L | NA | NA | NA | NA
|  | Variability of rejection of reference solute (%) | 15 | [13 empty] | SDS-THM4 | mg/L | 207.8 | 176.8 | 192.3 | 16.1206 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 17:00 | 55 | 24 | 63 | 61 | 281 | 6.63 | 2.93 |  | 9.56 | 0.21479 | 0.69351 | 28.3933 | 15.1326 | 15.4034 | 358.6397 | 280.574 | 356.7978 | 0.77145 | 61.2286 | 0.25157 |  |  |  | 280 | 303 | 332 | 359.9386 | -8.4152 | 8.046 | 358.9955 | 22.0046 | 0.023 | 0.168 | 0.47 | 0.45532 | 3.1232 | 85.209 | 0.45022 | 94.8914 | [8 empty] | SDS-TOX | mg Cl- /L | 99 | 82 | 90.5 | 18.7845 | --- | 1427.5968 | --- | 82.0792 | 1411.755 | 93.5895 | SDS-TOX | mg Cl- /L | 95 | --- | 3248.8462 | --- | 81.1881 | 3212.1802 | 97.0425 | SDS-TOX | mg Cl- /L | 70 | --- | 922.9412 | --- | 86.1386 | 913.7792 | 92.3395 | SDS-TOX | mg Cl- /L | 64 | --- | 694 | --- | 87.3267 | 687.4388 | 90.6901 | SDS-TOXb, ug Cl- /L | 124.9364 | 97.3719 | 140.8351 | 152.9608 | SDS-TOXb, ug Cl- /L | NA | NA | NA | NA
|  | Standard testing recovery (%) | 20 | [13 empty] | SDS-MCAA* | mg/L | BMRL | 3.1 | 3.1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-03 | 18:00 | 56 | 24 | 63 | 61 | 281 | 6.69 | 2.86 |  | 9.55 | 0.21479 | 0.70052 | 28.4241 | 15.2696 | 15.5428 | 359.2964 | 281.0744 | 357.4341 | 0.77291 | 61.2271 | 0.25385 |  |  |  | 279 | 303 | 330 | 364.1486 | -10.3481 | 8.3744 | 363.135 | 23.1691 | [16 empty] | SDS-CHCl3 | mg/L | 7.4 | 5.8 | 6.6 | 24.2424 | --- | 388.5355 | --- | 94.72 | 384.0104 | 98.2813 | SDS-CHCl3 | mg/L | 9.3 | --- | 899.3 | --- | 92.56 | 888.953 | 98.9538 | SDS-CHCl3 | mg/L | 3.9 | --- | 241.351 | --- | 96.88 | 238.8004 | 98.3668 | SDS-CHCl3 | mg/L | 3 | --- | 177.2857 | --- | 97.6 | 175.4706 | 98.2903 | SDS-CDb, mg/L | 1.8427 | 1.6233 | 1.9959 | 2.0208 | SDS-CDb, mg/L | NA | NA | NA | NA
|  | Standard testing pH | 7 | [13 empty] | SDS-DCAA* | mg/L | 29 | 31 | 30 | 6.6667 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 10:00 | 72 | 24 | 62 | 60 | 281 | 6.26 | 4.72 |  | 10.98 | 0.21479 | 0.57013 | 24.592 | 14.2881 | 14.5438 | 347.5907 | 272.0099 | 345.907 | 0.74739 | 60.2526 | 0.24138 |  |  |  | 283 | 303 | 328 | 333.0148 | -1.5289 | 7.0608 | 332.4577 | 14.8764 | 0.02 | 0.166 | 0.38 | 0.33521 | 11.7869 | 87.1383 | 0.3317 | 93.9704 | [8 empty] | SDS-BDCM | mg/L | 16 | 14 | 15 | 13.3333 | --- | 123.0645 | --- | 69.0722 | 121.7842 | 87.6831 | SDS-BDCM | mg/L | 18 | --- | 252.6154 | --- | 62.8866 | 249.8878 | 92.7968 | SDS-BDCM | mg/L | 9.7 | --- | 85.7784 | --- | 80 | 84.9612 | 88.583 | SDS-BDCM | mg/L | 7.6 | --- | 66.0286 | --- | 84.3299 | 65.4201 | 88.3828 | TOCb, mg/L | 1.8197 | 1.7243 | 1.7142 | 1.8288 | TOCb, mg/L | NA | NA | NA | NA
|  | Acceptable range of operating pressures | 100 - 200 | [13 empty] | SDS-TCAA* | mg/L | 16 | 27 | 21.5 | 51.1628 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 11:00 | 73 | 24 | 62 | 60 | 281 | 5.72 | 2.28 |  | 8 | 0.21479 | 0.715 | 34.125 | 13.0556 | 13.2892 | 360.4542 | 282.1966 | 358.8612 | 0.77461 | 60.2254 | 0.22066 |  |  |  | 276 | 303 | 328 | 376 | -14.6341 | 9.3596 | 374.9822 | 26.3965 | 0.02 | 0.168 | 0.4 | 0.49544 | -23.8596 | 87.1383 | 0.4906 | 95.9234 | [8 empty] | SDS-DBCM | mg/L | 26 | 25 | 25.5 | 3.9216 | --- | 1.3065 | --- | -41.6667 | 1.5931 | -1500.6593 | SDS-DBCM | mg/L | 29 | --- | -55.6154 | --- | -61.1111 | -54.6317 | 153.0828 | SDS-DBCM | mg/L | 20 | --- | 16.0784 | --- | -11.1111 | 16.1206 | -24.0652 | SDS-DBCM | mg/L | 17 | --- | 18.4286 | --- | 5.5556 | 18.4137 | 7.6774 | UV254 b, cm-1 | 0.038593 | 0.03172 | 0.037879 | 0.039351 | UV254 b, cm-1 | NA | NA | NA | NA
|  | Acceptable range of operating pH values | 2-11 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 12:00 | 74 | 24 | 62 | 60 | 281 | 6.52 | 2.53 |  | 9.05 | 0.21479 | 0.72044 | 30.0497 | 14.8816 | 15.1478 | 361.1117 | 282.5326 | 359.2884 | 0.77667 | 60.2233 | 0.25153 |  |  |  | 278 | 303 | 330 | 372.7925 | -12.9674 | 8.7028 | 371.6928 | 25.207 | 0.022 | 0.168 | 0.464 | 0.49954 | -7.6594 | 85.8521 | 0.494 | 95.5466 | [8 empty] | SDS-CHBr3 | mg/L | 13 | 15 | 14 | 14.2857 | --- | -28.5806 | --- | -1650 | -28.0762 | 149.8644 | SDS-CHBr3 | mg/L | 15 | --- | -94.2308 | --- | -1775 | -92.9609 | 116.1358 | SDS-CHBr3 | mg/L | 15 | --- | -12.8431 | --- | -1775 | -12.5441 | 219.5785 | SDS-CHBr3 | mg/L | 14 | --- | -4.8571 | --- | -1650 | -4.6608 | 400.3806 | Bromideb, ug/L | 160.8308 | 160.0579 | 153.2568 | 154.0345 | Bromideb, ug/L | NA | NA | NA | NA
|  | Typical pressure drop across a single element (psi) | 5 | [13 empty] | SDS-DBAA* | mg/L | 3.1 | 3.1 | 3.1 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 13:00 | 75 | 24 | 62 | 60 | 281 | 6.54 | 2.8 |  | 9.34 | 0.21479 | 0.70021 | 29.0857 | 14.9272 | 15.1943 | 359.2402 | 281.0638 | 357.4207 | 0.77267 | 60.2273 | 0.25228 |  |  |  | 271 | 304 | 332 | 382.7464 | -15.2851 | 11.0016 | 381.446 | 28.9546 | 0.022 | 0.168 | 0.465 | 0.46732 | -0.49846 | 85.8521 | 0.46214 | 95.2395 | [8 empty] | SDS-THM4 | mg/L | 62.4 | 59.8 | 61.1 | 4.2553 | --- | 484.3258 | --- | 68.2267 | 479.3115 | 87.2525 | SDS-THM4 | mg/L | 71.3 | --- | 1002.0692 | --- | 62.9225 | 991.2483 | 92.807 | SDS-THM4 | mg/L | 48.6 | --- | 330.3647 | --- | 74.727 | 327.3381 | 85.153 | SDS-THM4 | mg/L | 41.6 | --- | 256.8857 | --- | 78.3671 | 254.6436 | 83.6634 | Alkb, mg/L CaCO3 | 202.3293 | 208.0521 | 207.7912 | 200.2362 | Alkb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible SDI | 4 | [13 empty] | SDS-BCAA* | mg/L | 11 | 11 | 11 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 14:00 | 76 | 24 | 62 | 60 | 281 | 6.46 | 2.86 |  | 9.32 | 0.21479 | 0.69313 | 29.1502 | 14.7446 | 15.0084 | 358.5737 | 280.5602 | 356.7803 | 0.77117 | 60.2288 | 0.24919 |  |  |  | 280 | 303 | 330 | 359.8392 | -9.0422 | 8.046 | 358.9214 | 21.9885 | 0.025 | 0.166 | 0.469 | 0.45027 | 3.9945 | 83.9228 | 0.44538 | 94.3868 | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 227.2431 | 246.0347 | 231.9081 | 226.4552 | T-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Maximum permissible turbidity (ntu) | 1 | [13 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 15:00 | 77 | 24 | 62 | 60 | 281 | 6.49 | 2.79 |  | 9.28 | 0.21479 | 0.69935 | 29.2802 | 14.8131 | 15.0781 | 359.1516 | 281.0057 | 357.3467 | 0.77243 | 60.2276 | 0.25035 |  |  |  | 279 | 303 | 331 | 363.8172 | -9.9146 | 8.3744 | 362.8377 | 23.1061 | 0.024 | 0.168 | 0.477 | 0.46139 | 3.2724 | 84.5659 | 0.45634 | 94.7408 | [8 empty] | SDS-DCAA* | mg/L | 2.4 | 2 | 2.2 | 18.1818 | --- | 91.8774 | --- | 92.6667 | 90.8149 | 97.5775 | SDS-DCAA* | mg/L | 3 | --- | 210.6923 | --- | 90 | 208.2777 | 98.5596 | SDS-DCAA* | mg/L | 2.4 | --- | 56.5176 | --- | 92 | 55.9363 | 95.7094 | SDS-DCAA* | mg/L | 1.1 | --- | 42.3857 | --- | 96.3333 | 41.9557 | 97.3782 | Ca-Hdb, mg/L CaCO3 | 222.3293 | 237.9942 | 224.4426 | 215.4466 | Ca-Hdb, mg/L CaCO3 | NA | NA | NA | NA
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | 100 | [13 empty] | SDS-CDBAA | mg/L | 2.4 | 3 | 2.7 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 16:00 | 78 | 24 | 62 | 60 | 281 | 6.56 | 2.64 |  | 9.2 | 0.21479 | 0.71304 | 29.5435 | 14.9728 | 15.2408 | 360.4311 | 281.9911 | 358.5999 | 0.77524 | 60.2248 | 0.25306 |  |  |  | 281 | 303 | 332 | 362.8939 | -9.3054 | 7.7176 | 361.938 | 22.3624 | 0.024 | 0.168 | 0.482 | 0.48226 | -0.053439 | 84.5659 | 0.47691 | 94.9676 | [8 empty] | SDS-TCAA* | mg/L | 1.4 | 1.2 | 1.3 | 15.3846 | --- | 66.4613 | --- | 93.9535 | 65.6893 | 98.021 | SDS-TCAA* | mg/L | 1.7 | --- | 154.0077 | --- | 92.093 | 152.237 | 98.8833 | SDS-TCAA* | mg/L | 1 | --- | 41.1961 | --- | 95.3488 | 40.7643 | 97.5469 | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 6.6 | 11 | 8.8 | 50 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 17:00 | 79 | 24 | 62 | 60 | 281 | 6.6 | 1.44 |  | 8.04 | 0.21479 | 0.8209 | 33.9502 | 15.0641 | 15.3337 | 370.7403 | 290.0476 | 368.845 | 0.79745 | 60.2025 | 0.2547 |  |  |  | 284 | 302 | 337 | 398.4583 | -18.2369 | 6.7323 | 397.1142 | 28.484 | [16 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 48.1 | 64.2 | 56.15 | 28.6732 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 18:00 | 80 | 24 | 62 | 60 | 281 | 6.57 | 1.08 |  | 7.65 | 0.21479 | 0.85882 | 35.732 | 14.9957 | 15.264 | 374.4971 | 292.9936 | 372.5915 | 0.80551 | 60.1945 | 0.25358 |  |  |  | 286 | 303 | 338 | 417.0417 | -23.3851 | 6.0755 | 415.5097 | 31.1689 | [16 empty] | SDS-DBAA* | mg/L | 6 | 5.7 | 5.85 | 5.1282 | --- | -3.021 | --- | -88.7097 | -2.9159 | 300.6265 | SDS-DBAA* | mg/L | 6.8 | --- | -21.6615 | --- | -119.3548 | -21.3307 | 131.879 | SDS-DBAA* | mg/L | 4.8 | --- | 1.4667 | --- | -54.8387 | 1.5025 | -219.4735 | SDS-DBAA* | mg/L | 4.3 | --- | 2.5857 | --- | -38.7097 | 2.6036 | -65.158 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 59.1 | 75.2 | 67.15 | 23.9762 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 19:00 | 81 | 24 | 62 | 60 | 281 | 6.57 | 1.03 |  | 7.6 | 0.21479 | 0.86447 | 35.9737 | 14.9957 | 15.264 | 375.0643 | 293.4374 | 373.1558 | 0.80673 | 60.1933 | 0.25358 |  |  |  | 284 | 303 | 337 | 435.2621 | -29.1579 | 6.7323 | 433.4938 | 34.4858 | 0.03 | 0.165 | 0.717 | 0.95602 | -33.336 | 80.7074 | 0.94519 | 96.826 | [8 empty] | SDS-BCAA* | mg/L | 4.1 | 3.8 | 3.95 | 7.5949 | --- | 26.6919 | --- | 64.0909 | 26.4225 | 85.0506 | SDS-BCAA* | mg/L | 4.9 | --- | 51.8231 | --- | 55.4545 | 51.2776 | 90.4442 | SDS-BCAA* | mg/L | 2.9 | --- | 18.7824 | --- | 73.6364 | 18.6118 | 84.4184 | SDS-BCAA* | mg/L | 2.3 | --- | 14.7286 | --- | 79.0909 | 14.5991 | 84.2456 | Qp/QT (HAA5), % | 4.594 | 4.8152 | 4.4838 | 4.2365 | Qp/QT (HAA5), % | 62.2863 | 65.2856 | 60.7925 | 57.4384
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 20:00 | 82 | 24 | 62 | 60 | 281 | 6.59 | 0.93 |  | 7.52 | 0.21479 | 0.87633 | 36.367 | 15.0413 | 15.3105 | 376.2652 | 294.3723 | 374.3446 | 0.80933 | 60.1907 | 0.25437 |  |  |  | 286 | 303 | 340 | 435.5914 | -28.1151 | 6.0755 | 433.8373 | 34.0767 | 0.02 | 0.15 | 0.725 | 1.1157 | -53.8836 | 87.1383 | 1.1028 | 98.1864 | [8 empty] | SDS-TBAA | mg/L | 4.4 | 4.3 | 4.35 | 2.2989 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | 4.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 186.2726 | 186.4736 | 185.8567 | 185.9157 | SDS-THM4b, ug/L | 110.5803 | 113.3045 | 104.9412 | 105.7403
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 21:00 | 83 | 24 | 62 | 60 | 281 | 6.63 | 0.91 |  | 7.54 | 0.21479 | 0.87931 | 36.2679 | 15.1326 | 15.4034 | 376.5772 | 294.607 | 374.6432 | 0.81003 | 60.19 | 0.25591 |  |  |  | 289 | 303 | 340 | 417.4286 | -22.7731 | 5.0903 | 415.9135 | 30.5144 | 0.033 |  |  | 1.048 |  | 78.7781 | 1.036 | 96.8148 | [8 empty] | SDS-CDBAA | mg/L | 4 | 3.8 | 3.9 | 5.1282 | --- | 0.029032 | --- | -44.4444 | 0.074895 | -5107.293 | SDS-CDBAA | mg/L | 4.2 | --- | -7.3385 | --- | -55.5556 | -7.2043 | 158.2984 | SDS-CDBAA | mg/L | 3.3 | --- | 2.1235 | --- | -22.2222 | 2.1362 | -54.4823 | SDS-CDBAA | mg/L | 3 | --- | 2.5714 | --- | -11.1111 | 2.5759 | -16.4645 | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-04-04 | 22:00 | 84 | 24 | 62 | 60 | 281 | 6.51 | 0.88 |  | 7.39 | 0.21479 | 0.88092 | 37.0244 | 14.8587 | 15.1246 | 376.7099 | 294.7389 | 374.8109 | 0.81021 | 60.1898 | 0.25128 |  |  |  | 289 | 302 | 340 | 419.1648 | -23.2838 | 5.0903 | 417.657 | 30.8045 | 0.031 | 0.168 | 0.864 | 1.0765 | -24.5969 | 80.0643 | 1.0644 | 97.0876 | [8 empty] | SDS-DCBAA | mg/L | 3 | 2.7 | 2.85 | 10.5263 | --- | 22.0435 | --- | 67.6136 | 21.8161 | 86.9363 | SDS-DCBAA | mg/L | 3.2 | --- | 46.2769 | --- | 63.6364 | 45.7761 | 93.0095 | SDS-DCBAA | mg/L | 2 | --- | 15.3333 | --- | 77.2727 | 15.1901 | 86.8335 | SDS-DCBAA | mg/L | 1.8 | --- | 11.8 | --- | 79.5455 | 11.6959 | 84.6099 | SDS-TOXb, ug Cl- /L | 485.9578 | 485.2576 | 485.4953 | 486.3172 | SDS-TOXb, ug Cl- /L | 246.8232 | 237.3292 | 240.5527 | 251.6966
[44 empty] | 1999-04-05 | 9:30 | 95.5 | 24 | 62 | 60 | 281 | 6.25 | 1.26 |  | 7.51 | 0.21479 | 0.83222 | 36.4168 | 14.2653 | 14.5205 | 371.7746 | 290.9374 | 369.9766 | 0.79938 | 60.2006 | 0.2412 |  |  |  | 297 | 304 | 331 | 341.7024 | -3.2333 | 2.4631 | 341.2052 | 12.9556 | 0.024 | 0.167 | 0.867 | 0.80778 | 6.8302 | 84.5659 | 0.79907 | 96.9965 | [8 empty] | SDS-HAA5 | mg/L | 9.8 | 8.9 | 9.35 | 9.6257 | --- | 160.3177 | --- | 83.3482 | 158.5291 | 94.102 | SDS-HAA5 | mg/L | 11.5 | --- | 354.9615 | --- | 79.5191 | 350.9685 | 96.7234 | SDS-HAA5 | mg/L | 8.2 | --- | 102.2196 | --- | 85.3963 | 101.2097 | 91.898 | SDS-HAA5 | mg/L | 5.4 | --- | 77.9 | --- | 90.3829 | 77.1449 | 93.0002 | SDS-CDb, mg/L | 5.4355 | 5.4312 | 5.4306 | 5.4337 | SDS-CDb, mg/L | 3.0557 | 2.9973 | 2.9896 | 3.0317
[44 empty] | 1999-04-05 | 10:00 | 96 | 24 | 63 | 61 | 281 | 6.13 | 6.02 |  | 12.15 | 0.21479 | 0.50453 | 22.1276 | 13.9914 | 14.2418 | 342.006 | 267.667 | 340.3843 | 0.73528 | 61.2647 | 0.23246 |  |  |  | 289 | 302 | 332 | 320.2832 | 3.5291 | 5.0903 | 319.942 | 9.6711 | 0.02 | 0.168 | 0.553 | 0.29348 | 46.9302 | 87.1383 | 0.29049 | 93.1152 | [8 empty] | SDS-HAA6 | mg/L | 13.9 | 12.7 | 13.3 | 9.0226 | --- | 187.0097 | --- | 80.1936 | 184.9516 | 92.8089 | SDS-HAA6 | mg/L | 16.4 | --- | 406.7846 | --- | 75.5771 | 402.2461 | 95.9229 | SDS-HAA6 | mg/L | 11.1 | --- | 121.002 | --- | 83.4698 | 119.8214 | 90.7362 | SDS-HAA6 | mg/L | 7.7 | --- | 92.6286 | --- | 88.5331 | 91.7441 | 91.6071 | TOCb, mg/L | 5.6956 | 5.6978 | 5.6758 | 5.6839 | TOCb, mg/L | 3.1283 | 3.158 | 2.8604 | 2.9706
[44 empty] | 1999-04-05 | 10:30 | 96.5 | 24 | 62 | 60 | 281 | 6.34 | 6.1 |  | 12.44 | 0.21479 | 0.50965 | 21.5884 | 14.4707 | 14.7296 | 342.4595 | 267.9774 | 340.7791 | 0.73642 | 60.2636 | 0.24442 |  |  |  | 288 | 301 | 328 | 321.6492 | 1.9362 | 5.4187 | 321.2696 | 10.3557 | 0.017 | 0.168 | 0.489 | 0.29945 | 38.7629 | 89.0675 | 0.29626 | 94.2619 | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | 0.14964 | 0.14951 | 0.1492 | 0.14934 | UV254 b, cm-1 | 0.076085 | 0.074219 | 0.070087 | 0.071927
[44 empty] | 1999-04-05 | 11:00 | 97 | 24 | 62 | 60 | 281 | 6.19 | 5.87 |  | 12.06 | 0.21479 | 0.51327 | 22.3002 | 14.1283 | 14.3811 | 342.7447 | 268.2324 | 341.1033 | 0.73692 | 60.2631 | 0.23864 |  |  |  | 263 | 302 | 326 | 348.2624 | -6.8289 | 13.6289 | 347.3233 | 24.278 | 0.014 | 0.168 | 0.39 | 0.30471 | 21.8683 | 90.9968 | 0.30151 | 95.3567 | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 169.5406 | 169.5185 | 169.1032 | 169.1527 | Bromideb, ug/L | 163.7714 | 163.4714 | 157.8415 | 158.5123
[44 empty] | 1999-04-05 | 11:30 | 97.5 | 24 | 62 | 60 | 281 | 5.97 | 5.55 |  | 11.52 | 0.21479 | 0.51823 | 23.3924 | 13.6262 | 13.87 | 343.1341 | 268.5839 | 341.5503 | 0.73758 | 60.2624 | 0.23016 |  |  |  | 272 | 303 | 323 | 339.4595 | -5.0958 | 10.6732 | 338.7429 | 19.7031 | 0.013 | 0.167 | 0.56 | 0.30878 | 44.86 | 91.6399 | 0.30564 | 95.7467 | [47 empty] | Alkb, mg/L CaCO3 | 216.265 | 216.5666 | 216.5068 | 216.1103 | Alkb, mg/L CaCO3 | 207.0342 | 211.1243 | 210.3128 | 204.9379
[44 empty] | 1999-04-05 | 12:00 | 98 | 24 | 62 | 60 | 281 | 5.97 | 9.19 |  | 15.16 | 0.21479 | 0.3938 | 17.5356 | 13.6262 | 13.87 | 332.9899 | 260.6436 | 331.4529 | 0.71578 | 60.2842 | 0.23008 |  |  |  | 269 | 303 | 322 | 327.5615 | -1.7272 | 11.6585 | 326.9394 | 17.7218 | 0.013 | 0.168 | 0.331 | 0.24807 | 25.0542 | 91.6399 | 0.24557 | 94.7063 | [47 empty] | T-Hdb, mg/L CaCO3 | 250.7596 | 251.7111 | 250.9239 | 250.6443 | T-Hdb, mg/L CaCO3 | 235.1827 | 248.0829 | 237.4098 | 233.6197
[44 empty] | 1999-04-05 | 13:00 | 99 | 24 | 62 | 60 | 281 | 5.97 | 6.03 |  | 12 | 0.21479 | 0.4975 | 22.4167 | 13.6262 | 13.87 | 341.4015 | 267.2277 | 339.8256 | 0.73386 | 60.2661 | 0.23015 |  |  |  | 268 | 302 | 321 | 340.6368 | -6.1174 | 11.9869 | 339.8652 | 21.1452 | 0.012 | 0.168 | 0.31 | 0.29757 | 4.009 | 92.283 | 0.29454 | 95.9258 | [47 empty] | Ca-Hdb, mg/L CaCO3 | 236.265 | 237.0482 | 236.3274 | 235.8562 | Ca-Hdb, mg/L CaCO3 | 227.0342 | 237.6529 | 227.8811 | 221.4916
[44 empty] | 1999-04-05 | 14:00 | 100 | 24 | 62 | 60 | 281 | 5.95 | 6.05 |  | 12 | 0.21479 | 0.49583 | 22.4167 | 13.5806 | 13.8236 | 341.2606 | 267.1216 | 339.6907 | 0.73354 | 60.2665 | 0.22937 |  |  |  | 269 | 302 | 322 | 339.4132 | -5.4078 | 11.6585 | 338.6677 | 20.5711 | 0.011 | 0.168 | 0.318 | 0.29761 | 6.4115 | 92.926 | 0.29458 | 96.2658 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-04-05 | 15:00 | 101 | 24 | 62 | 60 | 281 | 5.95 | 5.95 |  | 11.9 | 0.21479 | 0.5 | 22.6134 | 13.5806 | 13.8236 | 341.6071 | 267.3929 | 340.0357 | 0.73429 | 60.2657 | 0.22938 |  |  |  | 271 | 303 | 322 | 338 | -4.9689 | 11.0016 | 337.2907 | 19.6539 | 0.011 | 0.168 | 0.31 | 0.3 | 3.2258 | 92.926 | 0.29694 | 96.2956 | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-04-05 | 16:00 | 102 | 24 | 62 | 60 | 281 | 6 | 6 |  | 12 | 0.21479 | 0.5 | 22.4167 | 13.6947 | 13.9397 | 341.6131 | 267.3869 | 340.0282 | 0.73434 | 60.2657 | 0.2313 |  |  |  | 270 | 302 | 322 | 339 | -5.2795 | 11.33 | 338.2633 | 20.1805 | 0.013 | 0.167 | 0.327 | 0.298 | 8.8685 | 91.6399 | 0.29496 | 95.5926 | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-04-05 | 17:00 | 103 | 24 | 62 | 60 | 281 | 6 | 5.65 |  | 11.65 | 0.21479 | 0.51502 | 23.1202 | 13.6947 | 13.9397 | 342.8685 | 268.3696 | 341.2778 | 0.73704 | 60.263 | 0.23131 |  |  |  | 270 | 303 | 324 | 341.1372 | -5.2892 | 11.33 | 340.3777 | 20.6764 | 0.014 | 0.165 | 0.32 | 0.30577 | 4.4483 | 90.9968 | 0.30265 | 95.3742 | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-04-05 | 18:00 | 104 | 24 | 62 | 60 | 281 | 6 | 6.1 |  | 12.1 | 0.21479 | 0.49587 | 22.2231 | 13.6947 | 13.9397 | 341.2693 | 267.1179 | 339.686 | 0.7336 | 60.2664 | 0.2313 |  |  |  | 267 | 303 | 321 | 341.3852 | -6.3505 | 12.3153 | 340.5911 | 21.6069 | 0.014 | 0.165 | 0.301 | 0.29468 | 2.0996 | 90.9968 | 0.29168 | 95.2003 | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-04-06 | 9:00 | 119 | 24 | 63 | 61 | 281 | 5.93 | 5.83 |  | 11.76 | 0.21479 | 0.50425 | 22.8946 | 13.5349 | 13.7771 | 341.9591 | 267.6726 | 340.3914 | 0.73503 | 61.265 | 0.22488 |  |  |  | 278 | 302 | 320 | 331.4545 | -3.5795 | 8.7028 | 330.8905 | 15.9843 | 0.015 | 0.165 | 0.316 | 0.29841 | 5.5665 | 90.3537 | 0.29542 | 94.9225 | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-04-06 | 10:00 | 120 | 24 | 61 | 59 | 281 | 5.75 | 15.45 |  | 21.2 | 0.21479 | 0.27123 | 12.2547 | 13.1241 | 13.3589 | 323.5543 | 253.302 | 322.1167 | 0.69534 | 59.3047 | 0.22526 |  |  |  | 260 | 302 | 310 | 321.0615 | -3.5682 | 14.6141 | 320.4367 | 18.8607 | 0.014 | 0.165 | 0.242 | 0.20816 | 13.9827 | 90.9968 | 0.20618 | 93.2097 | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-04-06 | 10:30 | 120.5 | 24 | 61 | 59 | 281 | 5.7 | 14.801 |  | 20.501 | 0.21479 | 0.27804 | 12.7066 | 13.0099 | 13.2427 | 324.0604 | 253.7082 | 322.6333 | 0.69639 | 59.3036 | 0.2233 |  |  |  | 261 | 302 | 309 | 321.2522 | -3.9651 | 14.2857 | 320.6411 | 18.6006 | 0.009 | 0.166 | 0.238 | 0.21192 | 10.9586 | 94.2122 | 0.20986 | 95.7114 | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-04-06 | 11:00 | 121 | 24 | 61 | 59 | 281 | 5.75 | 14.91 |  | 20.66 | 0.21479 | 0.27832 | 12.6012 | 13.1241 | 13.3589 | 324.0843 | 253.7169 | 322.6444 | 0.69647 | 59.3035 | 0.22526 |  |  |  | 257 | 302 | 310 | 322.8182 | -4.1349 | 15.5993 | 322.1448 | 20.2222 | 0.011 | 0.166 | 0.221 | 0.21123 | 4.4226 | 92.926 | 0.20918 | 94.7413 | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-04-06 | 11:30 | 121.5 | 24 | 61 | 59 | 281 | 5.74 | 15.07 |  | 20.81 | 0.21479 | 0.27583 | 12.5031 | 13.1012 | 13.3357 | 323.8976 | 253.5728 | 322.4611 | 0.69607 | 59.3039 | 0.22487 |  |  |  | 260 | 302 | 309 | 321.4496 | -4.029 | 14.6141 | 320.822 | 18.9582 | 0.011 | 0.165 | 0.221 | 0.21054 | 4.7337 | 92.926 | 0.2085 | 94.7242 | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-04-06 | 12:00 | 122 | 24 | 61 | 59 | 281 | 5.78 | 14.27 |  | 20.05 | 0.21479 | 0.28828 | 13.015 | 13.1925 | 13.4286 | 324.8341 | 254.2979 | 323.3832 | 0.69811 | 59.3019 | 0.22644 |  |  |  | 258 | 302 | 310 | 323.3346 | -4.3015 | 15.2709 | 322.6627 | 20.0403 | 0.011 | 0.165 | 0.232 | 0.21403 | 7.7461 | 92.926 | 0.21194 | 94.8099 | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-04-06 | 13:00 | 123 | 24 | 61 | 59 | 281 | 5.75 | 14.2 |  | 19.95 | 0.21479 | 0.28822 | 13.0852 | 13.1241 | 13.3589 | 324.8279 | 254.299 | 323.3847 | 0.69807 | 59.3019 | 0.22527 |  |  |  | 261 | 302 | 310 | 322.1144 | -3.9079 | 14.2857 | 321.4892 | 18.8153 | 0.012 | 0.166 | 0.23 | 0.21361 | 7.1272 | 92.283 | 0.21154 | 94.3274 | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-04-06 | 14:00 | 124 | 24 | 61 | 59 | 281 | 6 | 14.29 |  | 20.29 | 0.21479 | 0.29571 | 12.8492 | 13.6947 | 13.9397 | 325.4084 | 254.7032 | 323.8987 | 0.6995 | 59.3005 | 0.23507 |  |  |  | 261 | 302 | 310 | 322.7645 | -4.1176 | 14.2857 | 322.1051 | 18.9706 | 0.013 | 0.167 | 0.226 | 0.21533 | 4.7203 | 91.6399 | 0.21317 | 93.9016
[44 empty] | 1999-04-06 | 15:00 | 125 | 24 | 61 | 59 | 281 | 5.85 | 13.67 |  | 19.52 | 0.21479 | 0.29969 | 13.3955 | 13.3523 | 13.5912 | 325.6997 | 254.9615 | 324.2271 | 0.70002 | 59.3 | 0.22919 |  |  |  | 262 | 303 | 310 | 322.6876 | -4.0928 | 13.9573 | 322.0559 | 18.6477 | 0.012 | 0.165 | 0.254 | 0.21691 | 14.6024 | 92.283 | 0.21478 | 94.4128
[44 empty] | 1999-04-06 | 16:00 | 126 | 24 | 61 | 59 | 281 | 5.83 | 13.37 |  | 19.2 | 0.21479 | 0.30365 | 13.6354 | 13.3067 | 13.5448 | 325.9978 | 255.1988 | 324.5289 | 0.70065 | 59.2994 | 0.22841 |  |  |  | 261 | 302 | 310 | 323.4682 | -4.3446 | 14.2857 | 322.8202 | 19.15 | 0.012 | 0.165 | 0.237 | 0.21807 | 7.986 | 92.283 | 0.21594 | 94.4428
[44 empty] | 1999-04-06 | 17:00 | 127 | 24 | 61 | 59 | 281 | 5.93 | 13.25 |  | 19.18 | 0.21479 | 0.30918 | 13.6507 | 13.5349 | 13.7771 | 326.4242 | 255.5125 | 324.9278 | 0.70164 | 59.2984 | 0.23234 |  |  |  | 262 | 301 | 313 | 323.5208 | -3.3613 | 13.9573 | 322.8716 | 18.8532 | 0.013 | 0.165 | 0.245 | 0.21928 | 10.4998 | 91.6399 | 0.2171 | 94.0119
[44 empty] | 1999-04-07 | 0:00 | 134 | 24 | 61 | 59 | 281 | 6 | 12.35 | X | 18.35 | 0.21479 | 0.32698 | 14.3134 | 13.6947 | 13.9397 | 327.7879 | 256.5657 | 326.2671 | 0.70462 | 59.2954 | 0.23509 |  |  |  | 269 | 300 | 313 | 321.747 | -2.7946 | 11.6585 | 321.1838 | 16.2473 | 0.014 | 0.163 | 0.231 | 0.22424 | 2.9243 | 90.9968 | 0.222 | 93.6937
[44 empty] | 1999-04-07 | 12:30 |  | 24 | 64 | 63 | 281 | 5.93 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 13.5349 | 13.7771 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 12:45 |  | 24 | 72 | 70 | 281 | 6.57 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 14.9957 | 15.264 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 13:00 |  | 24 | 51 | 49 | 281 | 4.5 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 10.271 | 10.4548 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 13:15 |  | 24 | 63 | 62 | 281 | 5.73 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 13.0784 | 13.3124 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 16:30 |  | 24 | 63 | 61 | 281 | 3.94 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 8.9928 | 9.1538 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 16:45 |  | 24 | 73 | 71 | 281 | 4.69 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 10.7047 | 10.8962 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 17:00 |  | 24 | 50 | 48 | 281 | 3.25 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 7.418 | 7.5507 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-04-07 | 17:20 |  | 24 | 64 | 62 | 281 | 4.23 | NA |  | #VALUE! | 0.21479 | #VALUE! | #VALUE! | 9.6547 | 9.8275 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on U3: C. Rice: Cartridge filtration was the only membrane pretreatment employed.
Note on X17: C. Rice: TOC values verified by consultant.
Note on X35: C. Rice: TCAA values verified by consultant.
Note on BX7: C. Rice 7/12/99: Consultant stated that the pH meter malfunctioned during these experiments and therefore no pH measurements were taken.
Note on CY22: C. Rice: All TOC values were verified by consultant due to the consistently high mass balance closure errors.
Note on DL22: C. Rice: All TOC values were verified by consultant due to the consistently high mass balance closure errors.
Note on DV22: C. Rice: All TOC values were verified by consultant due to the consistently high mass balance closure errors.
Note on EF22: C. Rice: All TOC values were verified by consultant due to the consistently high mass balance closure errors.

## SR40. 1st Quarter
FIELD-SET 1: 1st QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Manufacturer Reported Membrane Characteristics1 |  | Field 1-3: RBSMT Design Parameters | [8 empty] | Field 1-4: Foulants And Fouling Indices1 | Field 1-5: Pretreatment Used Prior To Membranes1 |  |  | Field 1-6: Feed Water Quality After Pretreatment | [5 empty] | Field 1-7: Membrane Setting Data | [20 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 1-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 1-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 1-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 1-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 1-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 1-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 1-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 1-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.43424 | [45 empty] | Recovery during sample collection (decimal) | 0.72 | [10 empty] | Recovery during sample collection (decimal) | 0.9 | [7 empty] | Recovery during sample collection (decimal) | 0.5 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-05-19 | 1998-05-27 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 6.64 | [10 empty] | Feed flow rate during sample collection (mL/min) | 5.16 | [7 empty] | Feed flow rate during sample collection (mL/min) | 10.13 | [7 empty] | Feed flow rate during sample collection (mL/min) | 17.51 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 7:30 | 12:45 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 200.15 | [10 empty] | Influent flow rate during sample collection (mL/min) | 180.43 | [7 empty] | Influent flow rate during sample collection (mL/min) | 177 | [7 empty] | Influent flow rate during sample collection (mL/min) | 177 | [6 empty] | SDS-THM4F, ug/L | 190.6 | 190.6 | 190.6 | 190.6 | SDS-THM4F, ug/L | 190.6 | 190.6 | 190.6 | 190.6 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 10.45 | 17.4 | 7.2 | 9 | SDS-THM4p, ug/L | 10.45 | 17.4 | 7.2 | 9 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.54 | 8.42 | 8.48 | 1.4151 | 1998-05-18 | 7:30 | 0 | 24.9 | 60 | 60 | 263 | 4.75 | 2.4 | 7.15 | 0.18158 | 0.66434 | 35.7832 | 10.8416 | 10.7459 | 0 | 0 | 0 | 0 | 60 | 0.1791 | 1998-05-19 | 7:30 | 0 | 25 | 68 | 68 | 202 | 5.17 | 1.97 |  | 7.14 | 0.13946 | 0.72409 | 27.2913 | 11.8002 | 11.6615 | 395.7679 | 221.3863 | 391.3047 | 1.7215 | 66.2785 | 0.17595 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 90.85 | 90.85 | 90.85 | 90.85 | SDS-HAA5F, ug/L | 90.85 | 90.85 | 90.85 | 90.85 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24.5 | 24.25 | 2.0619 | 1998-05-18 | 8:00 | 0.5 | 24.9 | 71 | 71 | 263 | 5.1 | 2.1 | 7.2 | 0.18158 | 0.70833 | 35.5278 | 11.6405 | 11.5377 | 0 | 0 | 0 | 0 | 71 | 0.1625 | 1998-05-19 | 8:00 | 0.5 | 25 | 71 | 71 | 202 | 5.13 | 1.92 |  | 7.05 | 0.13946 | 0.72766 | 27.6525 | 11.709 | 11.5713 | 396.6629 | 221.9069 | 392.2248 | 1.7254 | 69.2746 | 0.16704 |  | 6.44 |  |  | 272 | [7 empty] | 0.192 | [14 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0.6 | 1.5 | 0 | 1 | SDS-HAA5p, ug/L | 0.6 | 1.5 | 0 | 1 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 222 | 236 | 229 | 6.1135 | 1998-05-18 | 9:00 | 1.5 | 24.9 | 69 | 69 | 263 | 5.1 | 1.73 | 6.83 | 0.18158 | 0.74671 | 37.5066 | 11.6405 | 11.5377 | 0 | 0 | 0 | 0 | 69 | 0.16721 | 1998-05-19 | 9:00 | 1.5 | 25 | 70 | 70 | 202 | 5 | 1.81 |  | 6.81 | 0.13946 | 0.73421 | 28.6623 | 11.4122 | 11.2781 | 398.2858 | 222.8795 | 393.944 | 1.7324 | 68.2676 | 0.1652 |  | 7.29 |  |  | 272 | [7 empty] | 0.188 | [14 empty] | Sampling date | MM/DD/YY | 1998-05-19 | 1998-05-20 | --- | --- | 1998-05-19 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-22 | 1998-05-22 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-23 | 1998-05-23 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-05-24 | 1998-05-24 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 537.5 | 537.5 | 537.5 | 537.5 | SDS-TOXF, ug Cl- /L | 537.5 | 537.5 | 537.5 | 537.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 271 | 268 | 269.5 | 1.1132 | 1998-05-18 | 10:30 | 3 | 24.9 | 69 | 69 | 263 | 5 | 1.73 | 6.73 | 0.18158 | 0.74294 | 38.0788 | 11.4122 | 11.3115 | 0 | 0 | 0 | 0 | 69 | 0.16393 | 1998-05-19 | 10:00 | 2.5 | 25 | 70 | 70 | 202 | 4.92 | 1.75 |  | 6.67 | 0.13946 | 0.73763 | 29.2849 | 11.2296 | 11.0976 | 399.1298 | 223.3918 | 394.8495 | 1.736 | 68.264 | 0.16257 | 7.29 | 7.47 | 7.46 | 195 | 272 | 371 | 478.9514 | -29.0974 | 27.6438 | 475.4934 | 58.99 | BMRL | 0.192 | 0.443 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 10:00 | 11:00 | --- | --- | 10:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:00 | 14:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 47.5 | 44 | 29 | 40 | SDS-TOXp, ug Cl- /L | 47.5 | 44 | 29 | 40 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 252 | 330 | 291 | 26.8041 | 1998-05-18 | 11:20 | 3.8333 | 24.9 | 69 | 69 | 263 | 5.1 | 3.1 | 8.2 | 0.18158 | 0.62195 | 31.0732 | 11.6405 | 11.5377 | 0 | 0 | 0 | 0 | 69 | 0.16721 | 1998-05-19 | 11:00 | 3.5 | 25 | 70 | 70 | 202 | 4.89 | 1.72 |  | 6.61 | 0.13946 | 0.73979 | 29.5598 | 11.1612 | 11.03 | 399.6756 | 223.7123 | 395.4159 | 1.7383 | 68.2617 | 0.16158 | 7.41 | 7.42 | 7.58 | 210 | 272 | 403 | 438.6599 | -8.8486 | 22.0779 | 435.8922 | 51.823 | BMRL | 0.19 | 0.536 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 2.5 | 27.5 | --- | --- | 2.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 105 | 105 | --- | --- | --- | --- | --- | Operation time | hh.hh | 126.75 | 126.75 | --- | --- | --- | --- | --- | Cumulative time | hr | 150.5 | 150.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 5.345 | 5.345 | 5.345 | 5.345 | SDS-CDF, mg/L | 5.345 | 5.345 | 5.345 | 5.345 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 236 | 260 | 248 | 9.6774 | 1998-05-18 | 13:15 | 5.75 | 24.9 | 69 | 69 | 263 | 5.2 | 2.16 | 7.36 | 0.18158 | 0.70652 | 34.7337 | 11.8687 | 11.7639 | 0 | 0 | 0 | 0 | 69 | 0.17049 | 1998-05-19 | 14:00 | 6.5 | 25 | 70 | 70 | 202 | 4.5 | 1.58 |  | 6.08 | 0.13946 | 0.74013 | 32.2237 | 10.271 | 10.1503 | 399.5516 | 223.8374 | 395.6371 | 1.7376 | 68.2624 | 0.1487 | 7.38 | 7.4 | 7.68 | 222 | 273 | 420 | 404.7848 | 3.6227 | 17.6252 | 402.7488 | 44.8788 | BMRL | 0.194 | 0.697 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.91 | 8.02 | 7.965 | 1.381 | 8.32 | --- | --- | --- | --- | --- | pH | --- | 8.07 | 8.43 | --- | --- | --- | --- | --- | pH | --- | 8.25 | 8.43 | --- | --- | --- | --- | --- | pH | --- | 8.4 | 8.43 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.26 | 1.53 | 1.07 | 1.01 | SDS-CDp, mg/L | 1.26 | 1.53 | 1.07 | 1.01 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 15.1667 | 78.41 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.112 | 0.142 | 0.127 | 23.622 | 1998-05-18 | 14:30 | 7 | 24.9 | 70 | 70 | 263 | 5.2 | 5.8 | 11 | 0.18158 | 0.47273 | 22.9091 | 11.8687 | 11.7639 | 0 | 0 | 0 | 0 | 70 | 0.16806 | 1998-05-19 | 14:30 | 7 | 25 | 70 | 70 | 202 | 4.48 | 1.58 |  | 6.06 | 0.13946 | 0.73927 | 32.3333 | 10.2254 | 10.1052 | 399.3174 | 223.7162 | 395.4228 | 1.7365 | 68.2635 | 0.14803 | [27 empty] | Temperature | oC | 25 | 25 | 25 | 0 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 25 | 25 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.1 | 6.1 | 6.1 | 6.1 | TOCF, mg/L | 6.1 | 6.1 | 6.1 | 6.1 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 38.5 | 101.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | 0.05 | 0.05 | #VALUE! | 1998-05-18 | 15:30 | 8 | 24.9 | 70 | 70 | 263 | 5.2 | 3.9 | 9.1 | 0.18158 | 0.57143 | 27.9011 | 11.8687 | 11.7639 | 0 | 0 | 0 | 0 | 70 | 0.16806 | 1998-05-19 | 15:00 | 7.5 | 25 | 70 | 70 | 202 | 4.71 | 1.52 |  | 6.23 | 0.13946 | 0.75602 | 31.4238 | 10.7503 | 10.624 | 403.8537 | 226.1417 | 399.71 | 1.7564 | 68.2436 | 0.15568 | 7.85 | 7.65 | 7.64 | 220 | 273 | 423 | 422.8849 | 0.027218 | 18.3673 | 420.5196 | 47.6838 | BMRL | 0.189 | 0.712 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 166 | 164 | 165 | 1.2121 | 275 | 393.5714 | -43.1169 | 27.9476 | 390.8416 | 57.7834 | Alkalinity | mg/L as CaCO3 | 198 | 314 | 508 | -61.7834 | 13.5371 | 504.0105 | 60.7151 | Alkalinity | mg/L as CaCO3 | 168 | 274 | 290 | -5.8394 | 26.6376 | 288.2544 | 41.7182 | Alkalinity | mg/L as CaCO3 | 152 | 244 | 260.4507 | -6.7421 | 33.6245 | 258.895 | 41.289 | TOCp, mg/L | 0.5 | 0.6 | BMRL | BMRL | TOCp, mg/L | 0.5 | 0.6 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 73.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6 | 6.2 | 6.1 | 3.2787 | 1998-05-18 | 16:30 | 9 | 24.9 | 66 | 66 | 202 | 5.1 | 2.4 | 7.5 | 0.13946 | 0.68 | 25.9333 | 11.6405 | 11.5377 | 0 | 0 | 0 | 0 | 66 | 0.17481 | 1998-05-19 | 16:00 | 8.5 | 25 | 70 | 70 | 202 | 4.71 | 1.5 |  | 6.21 | 0.13946 | 0.75845 | 31.5282 | 10.7503 | 10.624 | 404.5031 | 226.5054 | 400.3528 | 1.7592 | 68.2408 | 0.15568 | 7.84 | 7.71 | 7.59 | 219 | 273 | 420 | 428.07 | -1.9214 | 18.7384 | 425.6326 | 48.5472 | BMRL | 0.19 | 0.741 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 188 | 191 | 189.5 | 1.5831 | 354 | 475.2143 | -34.2413 | 29.6846 | 471.802 | 59.8348 | Total dissolved solids | mg/L | 220 | 442 | 715 | -61.7647 | 18.3673 | 708.6297 | 68.9542 | Total dissolved solids | mg/L | 200 | 416 | 339 | 18.5096 | 25.7885 | 337.0112 | 40.6548 | Total dissolved solids | mg/L | 212 | 321 | 292.9859 | 8.7271 | 21.3358 | 291.8242 | 27.3535 | UV254 F, cm-1 | 0.185 | 0.185 | 0.185 | 0.185 | UV254 F, cm-1 | 0.185 | 0.185 | 0.185 | 0.185 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 8.5 | 71.7434 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.185 | 0.185 | 0.185 | 0 | 1998-05-18 | 17:00 | 9.5 | 24.9 | 66 | 66 | 202 | 5 | 2.3 | 7.3 | 0.13946 | 0.68493 | 26.6712 | 11.4122 | 11.3115 | 0 | 0 | 0 | 0 | 66 | 0.17139 | 1998-05-19 | 16:30 | 9 | 25 | 69 | 69 | 202 | 4.79 | 2.36 |  | 7.15 | 0.13946 | 0.66993 | 27.2517 | 10.9329 | 10.8044 | 382.1954 | 213.9758 | 378.2064 | 1.6623 | 67.3377 | 0.16045 | 7.79 | 7.62 | 7.64 | 219 | 273 | 400 | 371.9979 | 7.0005 | 18.7384 | 370.1839 | 40.8402 | BMRL | 0.19 | 0.719 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 166 | 168 | 167 | 1.1976 | 378 | 609.8571 | -61.3379 | 42.6117 | 604.5681 | 72.377 | Total hardness | mg/L as CaCO3 | 210 | 504 | 1020 | -102.381 | 27.8351 | 1009.5759 | 79.1992 | Total hardness | mg/L as CaCO3 | 180 | 342 | 402 | -17.5439 | 38.1443 | 398.8236 | 54.8673 | Total hardness | mg/L as CaCO3 | 156 | 282 | 346.1408 | -22.745 | 46.3918 | 343.4134 | 54.5737 | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.0833 | 2.9839 | 3.0336 | 3.2787 | 1998-05-18 | 17:30 | 10 | 24.9 | 66 | 66 | 202 | 5.3 | 2.3 | 7.6 | 0.13946 | 0.69737 | 25.5789 | 12.097 | 11.9902 | 0 | 0 | 0 | 0 | 66 | 0.18167 | 1998-05-19 | 17:00 | 9.5 | 25 | 69 | 69 | 202 | 4.79 | 2.01 |  | 6.8 | 0.13946 | 0.70441 | 28.7059 | 10.9329 | 10.8044 | 390.6024 | 218.6825 | 386.5257 | 1.6988 | 67.3012 | 0.16054 | 7.7 | 7.57 | 7.58 | 217 | 273 | 415 | 394.6119 | 4.9128 | 19.4805 | 392.5061 | 44.7142 | BMRL | 0.193 | 0.718 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 152 | 162 | 157 | 6.3694 | 372 | 482 | -29.5699 | 36.6935 | 478.1185 | 67.163 | Calcium hardness | mg/L as CaCO3 | 198 | 496 | 698 | -40.7258 | 20.1613 | 691.5654 | 71.3693 | Calcium hardness | mg/L as CaCO3 | 162 | 336 | 334 | 0.59524 | 34.6774 | 331.539 | 51.137 | Calcium hardness | mg/L as CaCO3 | 148 | 276 | 288.8451 | -4.654 | 40.3226 | 286.8247 | 48.4005 | BromideF, ug/L | 62 | 62 | 62 | 62 | BromideF, ug/L | 62 | 62 | 62 | 62 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 63 | 61 | 62 | 3.2258 | 1998-05-18 | 18:00 | 10.5 | 24.9 | 66 | 66 | 202 | 4.72 | 2.4 | 7.12 | 0.13946 | 0.66292 | 27.3708 | 10.7731 | 10.678 | 0 | 0 | 0 | 0 | 66 | 0.16179 | 1998-05-20 | 7:00 | 23.5 | 25 | 68 | 68 | 202 | 4.79 | 1.23 |  | 6.02 | 0.13946 | 0.79568 | 32.5548 | 10.9329 | 10.8044 | 414.7503 | 232.2019 | 410.4215 | 1.8038 | 66.1962 | 0.16322 | [27 empty] | Turbidity | ntu | 0.061 | 0.06 | 0.0605 | 1.6529 | 0.173 | 0.298 | -72.2543 | 52.3622 | 0.29516 | 79.5029 | Turbidity | ntu | 0.056 | 0.381 | 0.766 | -101.0499 | 55.9055 | 0.75686 | 92.601 | Turbidity | ntu | 0.055 | 0.276 | 0.199 | 27.8986 | 56.6929 | 0.19694 | 72.0727 | Turbidity | ntu | 0.054 | 0.215 | 0.15682 | 27.0619 | 57.4803 | 0.15534 | 65.238 | Bromidep, ug/L | 63 | 65 | 59 | 57 | Bromidep, ug/L | 63 | 65 | 59 | 57 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 8 | 7 | 7.5 | 13.3333 | 1998-05-18 | 18:30 | 11 | 24.9 | 66 | 66 | 202 | 5.06 | 2.06 | 7.12 | 0.13946 | 0.71067 | 27.3708 | 11.5492 | 11.4472 | 0 | 0 | 0 | 0 | 66 | 0.17344 | 1998-05-20 | 7:30 | 24 | 25 | 68 | 68 | 202 | 4.85 | 2.28 |  | 7.13 | 0.13946 | 0.68022 | 27.331 | 11.0699 | 10.9398 | 384.6951 | 215.3464 | 380.6291 | 1.6732 | 66.3268 | 0.16494 | [27 empty] | Ammonia | mg NH3-N / L | 0.07 | BMRL | 0.07 | #VALUE! | NA | -0.0014286 | #VALUE! | -40 | -0.0005755 | 12263.4007 | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 229 | 229 | 229 | 229 | AlkF, mg/L CaCO3 | 229 | 229 | 229 | 229
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.71 | 2.6 | 2.155 | 41.2993 | 1998-05-19 | 7:30 | 24 | 25 | 68 | 68 | 202 | 5.17 | 1.97 | 7.14 | 0.13946 | 0.72409 | 27.2913 | 11.8002 | 11.6615 | 0 | 0 | 0 | 0 | 68 | 0.17149 | 1998-05-20 | 8:00 | 24.5 | 25 | 68 | 68 | 194 | 4.85 | 2.28 |  | 7.13 | 0.13394 | 0.68022 | 26.209 | 11.0699 | 10.9398 | 384.7886 | 215.3025 | 380.5514 | 1.6737 | 66.3263 | 0.16494 | [27 empty] | Total organic carbon | mg/L | 0.5 | BMRL | 0.5 | #VALUE! | 19.6 | 20.5 | -4.5918 | 91.8033 | 20.2611 | 97.5322 | Total organic carbon | mg/L | 0.6 | 49.4 | 55.6 | -12.5506 | 90.1639 | 54.8922 | 98.9069 | Total organic carbon | mg/L | BMRL | 12.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 8.6 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 165 | 198 | 168 | 152 | Alkp, mg/L CaCO3 | 165 | 198 | 168 | 152
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 6.29 | 4.4 | 5.345 | 35.3601 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 9:00 | 25.5 | 25 | 68 | 68 | 194 | 4.87 | 2.33 |  | 7.2 | 0.13394 | 0.67639 | 25.9444 | 11.1155 | 10.9849 | 383.8723 | 214.7798 | 379.6275 | 1.6697 | 66.3303 | 0.16561 | 6.91 | 7.18 | 7.96 | 204 | 271 | 399 | 406.4034 | -1.8555 | 24.3043 | 403.863 | 49.4878 | BMRL | 0.191 | 0.443 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.6 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | BMRL | 1.489 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.399 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.263 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 291 | 291 | 291 | 291 | T-HdF, mg/L CaCO3 | 291 | 291 | 291 | 291
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 10:00 | 26.5 | 25 | 68 | 68 | 194 | 4.8 | 2.22 |  | 7.02 | 0.13394 | 0.68376 | 26.6353 | 10.9557 | 10.827 | 385.6217 | 215.7937 | 381.4197 | 1.6773 | 66.3227 | 0.16325 | 7.89 | 7.82 | 7.79 | 218 | 272 | 391 | 380.8514 | 2.5956 | 19.1095 | 378.8367 | 42.4554 | BMRL | 0.191 | 0.536 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.0612 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.0142 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.1417 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.0581 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 167 | 210 | 180 | 156 | T-Hdp, mg/L CaCO3 | 167 | 210 | 180 | 156
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.48 | 8.58 | 8.53 | 1.1723 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 11:00 | 27.5 | 25 | 68 | 68 | 194 | 4.8 | 2.16 |  | 6.96 | 0.13394 | 0.68966 | 26.8736 | 10.9557 | 10.827 | 387.0594 | 216.5983 | 382.8418 | 1.6835 | 66.3165 | 0.16326 | 7.37 | 7.41 | 7.61 | 216 | 273 | 389 | 388.3889 | 0.1571 | 19.8516 | 386.2562 | 44.0786 | BMRL | 0.191 | 0.697 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 63 | 63 | 63 | 0 | --- | 59.4286 | --- | -1.6129 | 59.4712 | -5.9336 | Bromide | mg/L | 65 | --- | 35 | --- | -4.8387 | 35.3861 | -83.6881 | Bromide | mg/L | 59 | --- | 65 | --- | 4.8387 | 64.9142 | 9.1107 | Bromide | mg/L | 57 | --- | 64.0423 | --- | 8.0645 | 63.9412 | 10.8557 | Ca-HdF, mg/L CaCO3 | 248 | 248 | 248 | 248 | Ca-HdF, mg/L CaCO3 | 248 | 248 | 248 | 248
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 25 | 24 | 24.5 | 4.0816 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 12:00 | 28.5 | 25 | 68 | 68 | 194 | 4.8 | 2.15 |  | 6.95 | 0.13394 | 0.69065 | 26.9137 | 10.9557 | 10.827 | 387.3025 | 216.7343 | 383.0822 | 1.6846 | 66.3154 | 0.16326 | [27 empty] | SDS-Cl2 dose | mg/L | 2 | 2 | 2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 157 | 198 | 162 | 148 | Ca-Hdp, mg/L CaCO3 | 157 | 198 | 162 | 148
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 575 | 500 | 537.5 | 13.9535 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 13:00 | 29.5 | 25 | 68 | 68 | 194 | 4.67 | 2.02 |  | 6.69 | 0.13394 | 0.69806 | 27.9985 | 10.659 | 10.5337 | 389.0609 | 217.7842 | 384.9379 | 1.6922 | 66.3078 | 0.15886 | 7.33 | 7.33 | 7.64 | 217 | 273 | 382 | 390.8738 | -2.323 | 19.4805 | 388.781 | 44.1845 | BMRL | 0.192 | 0.712 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.66 | 0.82 | 0.74 | 21.6216 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.47 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.93 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 0.99 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 170 | 160 | 165 | 6.0606 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 14:00 | 30.5 | 25 | 68 | 68 | 194 | 4.84 | 2 |  | 6.84 | 0.13394 | 0.7076 | 27.3626 | 11.047 | 10.9172 | 391.5246 | 219.0766 | 387.2223 | 1.703 | 66.297 | 0.16467 | 7.33 | 7.39 | 7.62 | 214 | 272 | 395 | 403.81 | -2.2304 | 20.5937 | 401.4423 | 46.6922 | BMRL | 0.193 | 0.741 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 1.34 | 1.18 | 1.26 | 12.6984 | --- | 15.8493 | --- | 76.4266 | 15.675 | 91.9617 | SDS-Cl2 demand | mg/L | 1.53 | --- | 39.68 | --- | 71.3751 | 39.189 | 96.0958 | SDS-Cl2 demand | mg/L | 1.07 | --- | 9.62 | --- | 79.9813 | 9.4977 | 88.7341 | SDS-Cl2 demand | mg/L | 1.01 | --- | 7.1156 | --- | 81.1038 | 7.0281 | 85.629 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 24 | 20 | 22 | 18.1818 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 15:00 | 31.5 | 25 | 68 | 68 | 194 | 4.72 | 1.97 |  | 6.69 | 0.13394 | 0.70553 | 27.9985 | 10.7731 | 10.6465 | 390.9437 | 218.8127 | 386.7558 | 1.7004 | 66.2996 | 0.16058 | 7.31 | 7.38 | 7.61 | 225 | 272 | 394 | 376.1193 | 4.5383 | 16.5121 | 374.2809 | 39.8847 | BMRL | 0.191 | 0.719 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 65.834 | 68.4758 | 64.6674 | 65.3084 | Qp/QT (THM4), % | 85.8174 | 89.261 | 84.2966 | 85.1322
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 3.4 | 3.8 | 3.6 | 11.1111 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 16:00 | 32.5 | 25 | 68 | 68 | 194 | 4.85 | 1.95 |  | 6.8 | 0.13394 | 0.71324 | 27.5294 | 11.0699 | 10.9398 | 392.9462 | 219.867 | 388.6193 | 1.7092 | 66.2908 | 0.16503 | 7.84 | 7.82 | 7.68 | 218 | 272 | 395 | 397.5897 | -0.65563 | 19.1095 | 395.3449 | 44.8583 | BMRL | 0.192 | 0.718 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 8.55 | 8.45 | 8.5 | 1.1765 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.42 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.38 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.63 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 16:30 | 33 | 25 | 68 | 68 | 194 | 5 | 2.45 |  | 7.45 | 0.13394 | 0.67114 | 25.0403 | 11.4122 | 11.2781 | 382.6742 | 214.0446 | 378.3281 | 1.6646 | 66.3354 | 0.17002 | [27 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 31.4348 | 29.6669 | 32.0997 | 32.1704 | SDS-HAA5b, ug/L | 13.3998 | 11.0953 | 14.2665 | 14.3588
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 197.4 | 183.8 | 190.6 | 7.1354 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-20 | 17:00 | 33.5 | 25 | 68 | 68 | 194 | 4.75 | 2.32 |  | 7.07 | 0.13394 | 0.67185 | 26.4399 | 10.8416 | 10.7142 | 382.7258 | 214.1981 | 378.5995 | 1.6646 | 66.3354 | 0.16152 | [27 empty] | SDS-TOX | mg Cl- /L | 58 | 37 | 47.5 | 44.2105 | --- | 1797.5 | --- | 91.1628 | 1776.5997 | 97.3264 | SDS-TOX | mg Cl- /L | 44 | --- | 4979 | --- | 91.814 | 4915.4902 | 99.1049 | SDS-TOX | mg Cl- /L | 29 | --- | 1046 | --- | 94.6047 | 1031.4489 | 97.1884 | SDS-TOX | mg Cl- /L | 40 | --- | 740.7042 | --- | 92.5581 | 730.6531 | 94.5254 | SDS-TOXb, ug Cl- /L | 214.9133 | 199.5722 | 208.6663 | 212.5909 | SDS-TOXb, ug Cl- /L | 116.9949 | 96.9971 | 108.8517 | 113.9675
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 6.2 | 4.5 | 5.35 | 31.7757 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 6:00 | 46.5 | 25 | 68 | 68 | 194 | 4.89 | 1.99 |  | 6.88 | 0.13394 | 0.71076 | 27.1977 | 11.1612 | 11.03 | 392.3427 | 219.5088 | 387.9862 | 1.7066 | 66.2934 | 0.16638 | [27 empty] | SDS-CHCl3 | mg/L | 1.3 | BMRL | 1.3 | #VALUE! | --- | 585.9429 | --- | 99.2121 | 578.9604 | 99.7755 | SDS-CHCl3 | mg/L | 2.1 | --- | 1631.1 | --- | 98.7273 | 1610.136 | 99.8696 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CHCl3 | mg/L | 1.2 | --- | 231.9042 | --- | 99.2727 | 228.5949 | 99.4751 | SDS-CDb, mg/L | 2.6557 | 2.7327 | 2.5805 | 2.5139 | SDS-CDb, mg/L | 1.8394 | 1.9397 | 1.7413 | 1.6545
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 51 | 44 | 47.5 | 14.7368 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 8:00 | 48.5 | 25 | 68 | 68 | 211 | 4.86 | 1.88 |  | 6.74 | 0.14568 | 0.72107 | 30.3056 | 11.0927 | 10.9623 | 394.7258 | 221.0587 | 390.7257 | 1.7167 | 66.2833 | 0.16539 | 7.22 | 7.33 | 7.56 | 213 | 271 | 396 | 415.5585 | -4.939 | 20.9647 | 413.2257 | 48.4543 | [16 empty] | SDS-BDCM | mg/L | 2 | 1.3 | 1.65 | 42.4242 | --- | 74.3286 | --- | 92.5 | 73.4606 | 97.7539 | SDS-BDCM | mg/L | 3.8 | --- | 185.8 | --- | 82.7273 | 183.4578 | 97.9287 | SDS-BDCM | mg/L | 1.4 | --- | 42.6 | --- | 93.6364 | 42.0105 | 96.6675 | SDS-BDCM | mg/L | 1.5 | --- | 30.3732 | --- | 93.1818 | 29.9591 | 94.9932 | TOCb, mg/L | 2.4133 | 2.3338 | #VALUE! | #VALUE! | TOCb, mg/L | 1.2942 | 1.1906 | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 40 | 35 | 37.5 | 13.3333 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 9:00 | 49.5 | 25 | 68 | 68 | 194 | 4.77 | 1.8 |  | 6.57 | 0.13394 | 0.72603 | 28.5282 | 10.8873 | 10.7593 | 396.1571 | 221.7049 | 391.8678 | 1.7231 | 66.2769 | 0.16234 | 7.32 | 7.69 | 7.68 | 220 | 222 | 388 | 400.675 | -3.2668 | 18.3673 | 398.4538 | 44.7866 | BMRL | 0.196 | 0.663 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 4.3 | 3.6 | 3.95 | 17.7215 | --- | 2.7 | --- | -9.7222 | 2.7149 | -45.4918 | SDS-DBCM | mg/L | 6.7 | --- | -24.3 | --- | -86.1111 | -23.9011 | 128.0322 | SDS-DBCM | mg/L | 3.2 | --- | 4 | --- | 11.1111 | 3.9886 | 19.7704 | SDS-DBCM | mg/L | 3.3 | --- | 3.7225 | --- | 8.3333 | 3.7165 | 11.2062 | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 10:00 | 50.5 | 25 | 68 | 68 | 194 | 4.8 | 1.75 |  | 6.55 | 0.13394 | 0.73282 | 28.6183 | 10.9557 | 10.827 | 397.9247 | 222.6785 | 393.5887 | 1.7308 | 66.2692 | 0.16338 | 7.37 | 7.48 | 7.6 | 260 | 272 | 397 | 295.5571 | 25.5524 | 3.525 | 295.1173 | 11.8994 | BMRL | 0.189 | 0.669 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 4.5 | 3.9 | 4.2 | 14.2857 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 2.6 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 3 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 62.6583 | 64.0543 | 60.06 | 58.7346 | Bromideb, ug/L | 62.8582 | 64.6778 | 59.4711 | 57.7434
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 1 | BMRL | 1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 11:00 | 51.5 | 25 | 68 | 68 | 194 | 4.73 | 2.19 |  | 6.92 | 0.13394 | 0.68353 | 27.0347 | 10.796 | 10.6691 | 385.5303 | 215.7777 | 381.3915 | 1.6768 | 66.3232 | 0.16087 | 7.21 | 7.45 | 7.96 | 214 | 272 | 388 | 389.3699 | -0.35306 | 20.5937 | 387.232 | 44.736 | BMRL | 0.183 | 0.655 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 12.1 | 8.8 | 10.45 | 31.5789 | --- | 653.8429 | --- | 94.5173 | 646.1588 | 98.3828 | SDS-THM4 | mg/L | 17.4 | --- | 1749.4 | --- | 90.8709 | 1727.1104 | 98.9925 | SDS-THM4 | mg/L | 7.2 | --- | 374 | --- | 96.2225 | 368.7519 | 98.0475 | SDS-THM4 | mg/L | 9 | --- | 264.7746 | --- | 95.2781 | 261.1057 | 96.5531 | Alkb, mg/L CaCO3 | 186.8662 | 207.7725 | 189.5529 | 178.7126 | Alkb, mg/L CaCO3 | 174.0769 | 201.3291 | 177.5791 | 163.4482
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 8.1 | 7.3 | 7.7 | 10.3896 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 12:00 | 52.5 | 25 | 68 | 68 | 194 | 4.88 | 2.16 |  | 7.04 | 0.13394 | 0.69318 | 26.5568 | 11.1383 | 11.0074 | 387.965 | 217.0647 | 383.6661 | 1.6875 | 66.3125 | 0.16599 | [27 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 209.3658 | 235.5346 | 219.2192 | 202.8337 | T-Hdb, mg/L CaCO3 | 184.5865 | 218.6986 | 197.4308 | 176.0716
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 13:00 | 53.5 | 25 | 68 | 68 | 194 | 4.73 | 2 |  | 6.73 | 0.13394 | 0.70282 | 27.8262 | 10.796 | 10.6691 | 390.274 | 218.4328 | 386.0843 | 1.6975 | 66.3025 | 0.16092 | 7.5 | 7.54 | 7.89 | 210 | 272 | 381 | 410.2175 | -7.6686 | 22.0779 | 407.7767 | 48.5012 | BMRL | 0.178 | 0.617 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | 1 | --- | 66.493 | --- | 97.8947 | 65.5535 | 98.4745 | Ca-Hdb, mg/L CaCO3 | 188.091 | 213.7621 | 192.386 | 182.6916 | Ca-Hdb, mg/L CaCO3 | 169.9062 | 203.3695 | 175.5049 | 162.8678
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 14:00 | 54.5 | 25 | 68 | 68 | 194 | 4.71 | 2.04 |  | 6.75 | 0.13394 | 0.69778 | 27.7407 | 10.7503 | 10.624 | 389.0123 | 217.7367 | 384.854 | 1.692 | 66.308 | 0.16022 | 7.93 | 7.79 | 7.86 | 214 | 272 | 376 | 397.6397 | -5.7552 | 20.5937 | 395.4105 | 45.879 | BMRL | 0.191 | 0.618 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 7.3 | 7.6 | 7.45 | 4.0268 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 15:00 | 55.5 | 25 | 68 | 68 | 185 | 4.56 | 2 |  | 6.56 | 0.12773 | 0.69512 | 27.2012 | 10.408 | 10.2856 | 388.3932 | 217.3539 | 384.1773 | 1.6893 | 66.3107 | 0.15511 | 7.38 | 7.37 | 7.63 | 216 | 272 | 380 | 391.48 | -3.0211 | 19.8516 | 389.3173 | 44.5183 | BMRL | 0.19 | 0.615 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 98.2 | 83.5 | 90.85 | 16.1805 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 16:00 | 56.5 | 25 | 68 | 68 | 194 | 4.7 | 1.96 |  | 6.66 | 0.13394 | 0.70571 | 28.1291 | 10.7275 | 10.6014 | 390.977 | 218.8415 | 386.8067 | 1.7005 | 66.2995 | 0.1599 | 7.52 | 7.51 | 7.79 | 223 | 272 | 389 | 381.0051 | 2.0552 | 17.2542 | 379.0911 | 41.1751 | 0.009 | 0.186 | 0.603 | 0.60704 | -0.67012 | 95.1351 | 0.5998 | 98.4995 | [8 empty] | SDS-DBAA* | mg/L | 1.2 | BMRL | 1.2 | #VALUE! | --- | 0.48571 | --- | -20 | 0.49425 | -142.7946 | SDS-DBAA* | mg/L | 1.5 | --- | -3.5 | --- | -50 | -3.4357 | 143.6598 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 106.3 | 90.8 | 98.55 | 15.7281 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 16:30 | 57 | 25 | 68 | 68 | 194 | 4.75 | 2.5 |  | 7.25 | 0.13394 | 0.65517 | 25.7586 | 10.8416 | 10.7142 | 378.7748 | 211.9869 | 374.6911 | 1.6475 | 66.3525 | 0.16147 | 7.71 | 7.75 | 7.78 | 216 | 272 | 381 | 371.15 | 2.5853 | 19.8516 | 369.2506 | 41.5031 | BMRL | 0.188 | 0.614 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1 | --- | 68 | --- | 87.013 | 67.1378 | 98.5105 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 40.831 | 41.2423 | 40.5614 | 41.0128 | Qp/QT (HAA5), % | 70.7479 | 71.4605 | 70.2807 | 71.0629
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 17:00 | 57.5 | 25 | 68 | 68 | 194 | 4.74 | 2.54 |  | 7.28 | 0.13394 | 0.6511 | 25.6484 | 10.8188 | 10.6916 | 377.8179 | 211.4563 | 373.7531 | 1.6433 | 66.3567 | 0.16112 | [27 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 117.0429 | 119.1683 | 116.2105 | 116.1208 | SDS-THM4b, ug/L | 63.1476 | 66.8303 | 61.7052 | 61.5498
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-21 | 17:15 | 57.75 | 25 | 68 | 68 | 194 | 4.67 | 2.13 |  | 6.8 | 0.13394 | 0.68676 | 27.5294 | 10.659 | 10.5337 | 386.2886 | 216.2324 | 382.195 | 1.6801 | 66.3199 | 0.15883 | [27 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-05-22 | 8:00 | 72.5 | 25 | 68 | 68 | 194 | 4.73 | 1.81 |  | 6.54 | 0.13394 | 0.72324 | 28.6636 | 10.796 | 10.6691 | 395.4222 | 221.3141 | 391.1772 | 1.7199 | 66.2801 | 0.16097 | 7.66 | 7.11 | 7.44 | 208 | 272 | 387 | 430.2155 | -11.1668 | 22.82 | 427.5065 | 51.3458 | BMRL | 0.186 | 0.69 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 337.428 | 333.9692 | 331.2455 | 333.4613 | SDS-TOXb, ug Cl- /L | 190.8352 | 184.8422 | 180.1227 | 183.9622
[44 empty] | 1998-05-22 | 9:00 | 73.5 | 25 | 68 | 68 | 185 | 4.67 | 1.72 |  | 6.39 | 0.12773 | 0.73083 | 27.9515 | 10.659 | 10.5337 | 397.4634 | 222.37 | 393.0434 | 1.7288 | 66.2712 | 0.15895 | 7.42 | 7.59 | 7.82 | 218 | 272 | 388 | 409.3285 | -5.497 | 19.1095 | 406.9136 | 46.426 | BMRL | 0.186 | 0.69 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 1.2 | 0 | 0.6 | 200 | --- | 322.9214 | --- | 99.3396 | 319.0719 | 99.812 | SDS-HAA5 | mg/L | 1.5 | --- | 895 | --- | 98.3489 | 883.5013 | 99.8302 | SDS-HAA5 | mg/L | 0 | --- | 181.7 | --- | 100 | 179.1003 | 100 | SDS-HAA5 | mg/L | 1 | --- | 127.5493 | --- | 98.8993 | 125.734 | 99.2047 | SDS-CDb, mg/L | 3.6771 | 3.7716 | 3.611 | 3.5671 | SDS-CDb, mg/L | 2.4549 | 2.6188 | 2.3405 | 2.2644
[44 empty] | 1998-05-22 | 10:00 | 74.5 | 25 | 68 | 69 | 185 | 4.5 | 1.71 |  | 6.21 | 0.12773 | 0.72464 | 28.7907 | 10.271 | 10.1503 | 395.773 | 221.5162 | 391.5344 | 1.7214 | 66.7786 | 0.152 | 7.47 | 7.54 | 7.65 | 220 | 272 | 387 | 399.7632 | -3.298 | 18.3673 | 397.5768 | 44.6648 | BMRL | 0.189 | 0.692 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 1.2 | 0 | 0.6 | 200 | --- | 350.4214 | --- | 99.3912 | 346.2435 | 99.8267 | SDS-HAA6 | mg/L | 2.5 | --- | 963 | --- | 97.4632 | 950.6391 | 99.737 | SDS-HAA6 | mg/L | 0 | --- | 197.1 | --- | 100 | 194.2799 | 100 | SDS-HAA6 | mg/L | 1 | --- | 138.3944 | --- | 98.9853 | 136.4235 | 99.267 | TOCb, mg/L | 3.8135 | 3.8317 | #VALUE! | #VALUE! | TOCb, mg/L | 2.1381 | 2.1697 | #VALUE! | #VALUE!
[44 empty] | 1998-05-22 | 11:00 | 75.5 | 25 | 68 | 69 | 185 | 4.72 | 1.69 |  | 6.41 | 0.12773 | 0.73635 | 27.8612 | 10.7731 | 10.6465 | 398.9237 | 223.1598 | 394.4393 | 1.7352 | 66.7648 | 0.15946 | 7.46 | 7.67 | 7.84 | 218 | 272 | 393 | 413.3343 | -5.1741 | 19.1095 | 410.8425 | 46.9383 | BMRL | 0.198 | 0.707 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-22 | 12:00 | 76.5 | 25 | 68 | 69 | 185 | 4.62 | 1.67 |  | 6.29 | 0.12773 | 0.7345 | 28.4118 | 10.5449 | 10.421 | 398.3837 | 222.9122 | 394.0017 | 1.7328 | 66.7672 | 0.15608 | 7.5 | 7.51 | 7.82 | 221 | 272 | 395 | 403.6737 | -2.1959 | 17.9963 | 401.3927 | 44.9417 | BMRL | 0.194 | 0.709 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 62.4083 | 63.2373 | 60.7832 | 59.9494 | Bromideb, ug/L | 62.7075 | 64.1438 | 59.8916 | 58.4469
[44 empty] | 1998-05-22 | 13:00 | 77.5 | 25 | 68 | 69 | 177 | 4.67 | 1.63 |  | 6.3 | 0.1222 | 0.74127 | 27.0952 | 10.659 | 10.5337 | 400.305 | 223.8443 | 395.6492 | 1.7413 | 66.7587 | 0.15779 | 8.03 | 7.42 | 7.88 | 221 | 271 | 395 | 408.454 | -3.4061 | 17.9963 | 405.9811 | 45.564 | BMRL | 0.184 | 0.709 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 202.8681 | 216.2149 | 204.2576 | 197.4201 | Alkb, mg/L CaCO3 | 183.7213 | 206.8472 | 186.1288 | 174.2816
[44 empty] | 1998-05-22 | 14:00 | 102.5 | 25 | 68 | 69 | 185 | 4.67 | 1.04 |  | 5.71 | 0.12773 | 0.81786 | 31.3993 | 10.659 | 10.5337 | 421.2852 | 235.6977 | 416.6004 | 1.8325 | 66.6675 | 0.158 | 7.41 | 7.44 |  | 228 | 272 |  | 455.851 |  | 15.3989 | 452.9751 | 49.6661 | 0.018 | 0.183 | 0.713 | 0.93489 | -31.1212 | 90.2703 | 0.92332 | 98.0505 | [47 empty] | T-Hdb, mg/L CaCO3 | 240.3695 | 257.5937 | 245.9769 | 235.6327 | T-Hdb, mg/L CaCO3 | 203.2726 | 233.117 | 212.9884 | 195.0651
[44 empty] | 1998-05-22 | 14:30 | 103 | 25 | 68 | 69 | 185 | 4.82 | 0.92 |  | 5.74 | 0.12773 | 0.83972 | 31.23 | 11.0014 | 10.8721 | 427.8403 | 239.2774 | 422.9275 | 1.8611 | 66.6389 | 0.16315 | 7.38 | 7.44 |  | 225 | 272 |  | 502.6413 |  | 16.5121 | 499.0245 | 54.912 | BMRL | 0.188 | 0.754 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 210.8438 | 227.3788 | 213.1172 | 206.9872 | Ca-Hdb, mg/L CaCO3 | 183.6194 | 212.2697 | 187.5586 | 176.9371
[44 empty] | 1998-05-22 | 15:00 | 103.5 | 25 | 68 | 70 | 185 | 4.58 | 0.86 |  | 5.44 | 0.12773 | 0.84191 | 33.0074 | 10.4536 | 10.3307 | 428.309 | 239.68 | 423.6391 | 1.8629 | 67.1371 | 0.15388 | 7.57 | 7.66 |  | 226 | 272 |  | 501.1628 |  | 16.141 | 497.7567 | 54.5963 | BMRL | 0.21 | 0.796 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-05-22 | 15:30 | 104 | 25 | 68 | 69 | 185 | 4.62 | 0.85 |  | 5.47 | 0.12773 | 0.84461 | 32.8208 | 10.5449 | 10.421 | 429.15 | 240.1272 | 424.4295 | 1.8666 | 66.6334 | 0.15639 | 7.76 | 7.74 |  | 230 | 272 |  | 484.1941 |  | 14.6568 | 481.0201 | 52.185 | BMRL | 0.217 | 0.819 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-05-22 | 15:45 | 104.25 | 25 | 68 | 69 | 185 | 4.67 | 0.84 |  | 5.51 | 0.12773 | 0.84755 | 32.5753 | 10.659 | 10.5337 | 430.0774 | 240.6167 | 425.2948 | 1.8707 | 66.6293 | 0.15809 | [66 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-05-22 | 16:00 | 104.5 | 25 | 68 | 70 | 185 | 4.6 | 0.82 |  | 5.42 | 0.12773 | 0.84871 | 33.1328 | 10.4993 | 10.3758 | 430.3722 | 240.8228 | 425.6591 | 1.8719 | 67.1281 | 0.15457 | 7.94 | 7.79 |  | 227 | 271 |  | 507.9146 |  | 15.7699 | 504.4222 | 54.998 | BMRL | 0.199 | 0.916 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-05-22 | 16:15 | 104.75 | 25 | 68 | 70 | 185 | 4.7 | 0.64 |  | 5.34 | 0.12773 | 0.88015 | 33.6442 | 10.7275 | 10.6014 | 440.1911 | 246.257 | 435.2641 | 1.9147 | 67.0853 | 0.15803 | [66 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-05-22 | 16:30 | 105 | 25 | 68 | 70 | 185 | 4.67 | 0.61 |  | 5.28 | 0.12773 | 0.88447 | 34.0379 | 10.659 | 10.5337 | 441.5375 | 247.0283 | 436.6274 | 1.9205 | 67.0795 | 0.15703 | [66 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-05-22 | 17:00 | 105.5 | 25 | 68 | 70 | 185 | 4.69 | 0.58 |  | 5.27 | 0.12773 | 0.88994 | 34.1044 | 10.7047 | 10.5789 | 443.3064 | 248.0058 | 438.3552 | 1.9282 | 67.0718 | 0.15772 | 7.85 | 7.8 | 7.58 | 235 | 272 | 446 | 548.4741 | -22.9763 | 12.8015 | 544.5006 | 56.8412 | BMRL | 0.191 | 0.965 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-05-22 | 17:40 | 106.1667 | 25 | 68 | 70 | 185 | 4.6 | 0.56 |  | 5.16 | 0.12773 | 0.89147 | 34.8527 | 10.4993 | 10.3758 | 443.7182 | 248.2908 | 438.859 | 1.93 | 67.07 | 0.1547 | 7.86 | 7.8 | 7.64 | 235 | 271 | 454 | 552.8929 | -21.7826 | 12.8015 | 548.9407 | 57.1903 | BMRL | 0.185 | 1.031 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-05-22 | 18:15 | 106.75 | 25 | 68 | 70 | 185 | 4.6 | 0.55 |  | 5.15 | 0.12773 | 0.8932 | 34.9223 | 10.4993 | 10.3758 | 444.2759 | 248.6029 | 439.4105 | 1.9324 | 67.0676 | 0.15471 | 7.82 | 7.78 | 7.52 | 235 | 272 | 455 | 558.0455 | -22.6474 | 12.8015 | 554.0292 | 57.5835 | BMRL | 0.186 | 1.09 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-05-22 | 19:05 | 107.5833 | 25 | 69 | 70 | 177 | 4.75 | 0.57 |  | 5.32 | 0.1222 | 0.89286 | 32.2707 | 10.8416 | 10.7142 | 444.4903 | 248.5012 | 439.2307 | 1.9336 | 67.5664 | 0.15857 | 7.84 | 7.71 | 7.59 | 248 | 272 | 457 | 448.6667 | 1.8235 | 7.9777 | 445.9741 | 44.3914 | BMRL | 0.184 | 1.158 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-05-23 | 11:00 | 123.5 | 25 | 69 | 70 | 177 | 4.55 | 0.46 |  | 5.01 | 0.1222 | 0.90818 | 34.3293 | 10.3851 | 10.2631 | 449.3058 | 251.3218 | 444.2163 | 1.9544 | 67.5456 | 0.15194 | 7.57 | 7.53 | 7.7 | 236 | 271 | 538 | 600.8587 | -11.6838 | 12.4304 | 596.1691 | 60.4139 | BMRL | 0.189 | 1.812 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-05-23 | 12:00 | 124.5 | 25 | 69 | 70 | 177 | 4.73 | 0.42 |  | 5.15 | 0.1222 | 0.91845 | 33.3689 | 10.796 | 10.6691 | 452.8989 | 253.2151 | 447.5627 | 1.9702 | 67.5298 | 0.15799 | 8.04 | 7.96 | 7.98 | 239 | 272 | 490 | 612.9881 | -25.0996 | 11.3173 | 607.991 | 60.6902 | BMRL | 0.187 | 1.824 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-05-23 | 12:30 | 125 | 25 | 69 | 70 | 177 | 4.63 | 0.43 |  | 5.06 | 0.1222 | 0.91502 | 33.9802 | 10.5677 | 10.4435 | 451.6528 | 252.583 | 446.4455 | 1.9647 | 67.5353 | 0.15464 | 8.03 |  |  | 242 |  |  | 565.6047 |  | 10.2041 | 561.3722 | 56.8913 | BMRL |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 12:40 | 125.1667 | 25 | 68 | 68 | 177 | 5.1 | 8.43 |  | 13.53 | 0.1222 | 0.37694 | 12.082 | 11.6405 | 11.5037 | 323.2939 | 180.5818 | 319.1819 | 1.4066 | 66.5934 | 0.17274
[44 empty] | 1998-05-23 | 13:00 | 125.5 | 25 | 68 | 69 | 177 | 4.93 | 3.13 |  | 8.06 | 0.1222 | 0.61166 | 20.9603 | 11.2525 | 11.1202 | 369.1063 | 206.2611 | 364.5706 | 1.6058 | 66.8942 | 0.16624 | 7.92 | 7.73 | 7.86 | 217 | 272 | 388 | 352.1917 | 9.2289 | 19.4805 | 350.3089 | 38.0547 | BMRL | 0.182 | 0.848 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 13:15 | 125.75 | 25 | 68 | 69 | 177 | 4.78 | 4.1 |  | 8.88 | 0.1222 | 0.53829 | 18.9324 | 10.9101 | 10.7819 | 353.3827 | 197.5504 | 349.1743 | 1.5373 | 66.9627 | 0.16101 | 7.87 | 7.78 | 7.66 | 253 | 272 | 389 | 288.7366 | 25.7747 | 6.1224 | 288.254 | 12.2302 | BMRL | 0.188 | 0.706 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 13:45 | 126.25 | 25 | 68 | 69 | 177 | 4.73 | 4.4 |  | 9.13 | 0.1222 | 0.51807 | 18.3866 | 10.796 | 10.6691 | 349.2828 | 195.2835 | 345.1674 | 1.5194 | 66.9806 | 0.15929 | 7.68 | 7.85 | 7.78 | 202 | 271 | 367 | 342.0625 | 6.795 | 25.0464 | 340.191 | 40.6216 | BMRL | 0.185 | 0.582 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 14:00 | 126.5 | 25 | 68 | 69 | 177 | 4.8 | 5.5 |  | 10.3 | 0.1222 | 0.46602 | 16.1845 | 10.9557 | 10.827 | 339.2136 | 189.6198 | 335.1568 | 1.4757 | 67.0243 | 0.16154
[44 empty] | 1998-05-23 | 14:15 | 126.75 | 25 | 68 | 69 | 177 | 4.76 | 4.78 |  | 9.54 | 0.1222 | 0.49895 | 17.5535 | 10.8644 | 10.7367 | 345.5173 | 193.1633 | 341.4201 | 1.5031 | 66.9969 | 0.16026 | 7.8 | 7.66 | 7.64 | 209 | 271 | 362 | 329.7469 | 8.9097 | 22.449 | 328.1233 | 36.3044 | BMRL | 0.191 | 0.532 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 14:25 | 126.9167 | 25 | 68 | 69 | 177 | 4.87 | 4.73 |  | 9.6 | 0.1222 | 0.50729 | 17.4375 | 11.1155 | 10.9849 | 347.1897 | 194.0437 | 342.976 | 1.5104 | 66.9896 | 0.16398 | 7.72 | 7.73 | 7.62 | 211 | 271 | 359 | 329.7315 | 8.1528 | 21.7069 | 328.0981 | 35.69 | BMRL | 0.182 | 0.472 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 14:40 | 127.1667 | 25 | 68 | 69 | 177 | 4.84 | 5.26 |  | 10.1 | 0.1222 | 0.47921 | 16.5248 | 11.047 | 10.9172 | 341.7271 | 191.0053 | 337.6056 | 1.4866 | 67.0134 | 0.16291 | 7.77 | 7.73 | 7.6 | 212 | 271 | 393 | 322.4087 | 17.9622 | 21.3358 | 320.8992 | 33.9356 | BMRL | 0.188 | 0.434 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 15:15 | 127.75 | 25 | 68 | 69 | 177 | 4.89 | 5.27 |  | 10.16 | 0.1222 | 0.4813 | 16.4213 | 11.1612 | 11.03 | 342.1422 | 191.2128 | 337.9724 | 1.4884 | 67.0116 | 0.1646 | 7.78 | 7.68 | 7.64 | 206 | 272 | 353 | 328.4213 | 6.9628 | 23.5622 | 326.7302 | 36.951 | BMRL | 0.187 | 0.411 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-23 | 15:45 | 128.25 | 25 | 68 | 69 | 177 | 4.9 | 5.15 |  | 10.05 | 0.1222 | 0.48756 | 16.6119 | 11.184 | 11.0525 | 343.3495 | 191.8826 | 339.1564 | 1.4937 | 67.0063 | 0.16495 | 7.77 | 7.6 | 7.63 | 215 | 271 | 366 | 321.3544 | 12.1983 | 20.2226 | 319.8822 | 32.7878 | BMRL | 0.189 | 0.391 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 10:00 | 146.5 | 25 | 68 | 69 | 177 | 5.2 | 3.67 |  | 8.87 | 0.1222 | 0.58625 | 18.9549 | 11.8687 | 11.7292 | 363.6347 | 203.0627 | 358.9173 | 1.5821 | 66.9179 | 0.17528 | 7.52 | 7.87 | 7.85 |  | 269 | 344 |  | #VALUE! |  |  |  | BMRL | 0.186 | 0.402 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 10:15 | 146.75 | 25 | 68 | 69 | 177 | 5.2 | 5.91 |  | 11.11 | 0.1222 | 0.46805 | 14.9316 | 11.8687 | 11.7292 | 339.7107 | 189.7029 | 335.3036 | 1.478 | 67.022 | 0.17501 | 7.6 | 7.78 | 7.67 | 206 | 269 | 331 | 325.3714 | 1.7005 | 23.5622 | 323.6179 | 36.3447 | BMRL | 0.186 | 0.435 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 10:30 | 147 | 25 | 68 | 69 | 177 | 5.33 | 5.55 |  | 10.88 | 0.1222 | 0.48989 | 15.2684 | 12.1654 | 12.0224 | 343.9318 | 191.9959 | 339.3566 | 1.4965 | 67.0035 | 0.17943 | 7.9 | 7.95 | 7.89 | 205 | 269 | 333 | 331.4432 | 0.46749 | 23.9332 | 329.5395 | 37.792 | BMRL | 0.185 | 0.401 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 10:45 | 147.25 | 25 | 68 | 69 | 177 | 5.27 | 5.6 |  | 10.87 | 0.1222 | 0.48482 | 15.2833 | 12.0285 | 11.8871 | 342.9335 | 191.4682 | 338.4238 | 1.4921 | 67.0079 | 0.1774 | 8.03 | 7.86 | 7.85 | 204 | 269 | 328 | 331.1402 | -0.95737 | 24.3043 | 329.2474 | 38.0405 | BMRL | 0.187 | 0.392 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 11:00 | 147.5 | 25 | 68 | 68 | 177 | 5.18 | 13.33 |  | 18.51 | 0.1222 | 0.27985 | 8.5624 | 11.8231 | 11.6841 | 307.4961 | 171.7223 | 303.5226 | 1.3379 | 66.6621 | 0.17527 | 7.82 | 7.62 | 7.89 | 194 | 269 | 308 | 298.8391 | 2.9743 | 28.0148 | 297.305 | 34.7471 | BMRL | 0.198 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 11:15 | 147.75 | 25 | 68 | 68 | 177 | 5.44 | 13.87 |  | 19.31 | 0.1222 | 0.28172 | 8.1662 | 12.4165 | 12.2706 | 307.8232 | 171.79 | 303.6423 | 1.3394 | 66.6606 | 0.18408
[44 empty] | 1998-05-24 | 11:30 | 148 | 25 | 68 | 68 | 177 | 5.24 | 13.2 |  | 18.44 | 0.1222 | 0.28416 | 8.5987 | 11.96 | 11.8194 | 308.1748 | 172.0748 | 304.1457 | 1.3409 | 66.6591 | 0.17731 | 7.52 | 7.58 | 7.63 | 195 | 268 | 297 | 299.0742 | -0.6984 | 27.6438 | 297.5337 | 34.4612 | BMRL | 0.187 | 0.277 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 11:45 | 148.25 | 25 | 68 | 68 | 177 | 5.24 | 13.12 |  | 18.36 | 0.1222 | 0.2854 | 8.6405 | 11.96 | 11.8194 | 308.3677 | 172.1825 | 304.336 | 1.3417 | 66.6583 | 0.17731
[44 empty] | 1998-05-24 | 12:00 | 148.5 | 25 | 68 | 68 | 177 | 5.26 | 13.25 |  | 18.51 | 0.1222 | 0.28417 | 8.5624 | 12.0057 | 11.8646 | 308.1786 | 172.0681 | 304.1338 | 1.3409 | 66.6591 | 0.17799 | 7.73 | 7.79 | 7.78 | 188 | 269 | 299 | 301.854 | -0.9545 | 30.2412 | 300.1622 | 37.3672 | BMRL | 0.188 | 0.271 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 12:15 | 148.75 | 25 | 68 | 68 | 177 | 5.37 | 13.1 |  | 18.47 | 0.1222 | 0.29074 | 8.5831 | 12.2567 | 12.1127 | 309.2211 | 172.6013 | 305.0762 | 1.3455 | 66.6545 | 0.18172
[44 empty] | 1998-05-24 | 12:30 | 149 | 25 | 68 | 70 | 177 | 5.18 | 12 |  | 17.18 | 0.1222 | 0.30151 | 9.3027 | 11.8231 | 11.6841 | 310.8894 | 173.6173 | 306.872 | 1.3526 | 67.6474 | 0.17272 | 7.71 | 7.68 | 7.88 | 188 | 269 | 300 | 304.6808 | -1.5603 | 30.2412 | 302.9735 | 37.9484 | BMRL | 0.192 | 0.272 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 12:45 | 149.25 | 25 | 70 | 70 | 177 | 5.3 | 12.08 |  | 17.38 | 0.1222 | 0.30495 | 9.1841 | 12.097 | 11.9548 | 311.4531 | 173.8785 | 307.3337 | 1.3551 | 68.6449 | 0.17415
[44 empty] | 1998-05-24 | 13:00 | 149.5 | 25 | 68 | 66 | 177 | 5.16 | 10.2 |  | 15.36 | 0.1222 | 0.33594 | 10.5234 | 11.7774 | 11.639 | 316.4343 | 176.723 | 312.3613 | 1.3767 | 65.6233 | 0.17736 | 7.86 | 7.95 | 7.94 | 198 | 269 | 306 | 305.6706 | 0.10765 | 26.5306 | 304.1012 | 34.8901 | BMRL | 0.198 | 0.293 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 13:15 | 149.75 | 25 | 68 | 70 | 177 | 5.18 | 10.46 |  | 15.64 | 0.1222 | 0.3312 | 10.3171 | 11.8231 | 11.6841 | 315.6629 | 176.2831 | 311.5838 | 1.3734 | 67.6266 | 0.17277
[44 empty] | 1998-05-24 | 13:30 | 150 | 25 | 68 | 70 | 177 | 5.2 | 12 |  | 17.2 | 0.1222 | 0.30233 | 9.2907 | 11.8687 | 11.7292 | 311.0211 | 173.682 | 306.9863 | 1.3532 | 67.6468 | 0.17339 | 7.86 | 7.8 | 7.89 | 191 | 269 | 304 | 303.5167 | 0.15899 | 29.128 | 301.8639 | 36.7264 | BMRL | 0.191 | 0.283 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 13:45 | 150.25 | 25 | 68 | 70 | 177 | 5.24 | 12.27 |  | 17.51 | 0.1222 | 0.29926 | 9.1085 | 11.96 | 11.8194 | 310.5418 | 173.3964 | 306.4817 | 1.3512 | 67.6488 | 0.17472
[44 empty] | 1998-05-24 | 14:00 | 150.5 | 25 | 68 | 69 | 177 | 5.08 | 12.6 |  | 17.68 | 0.1222 | 0.28733 | 9.0113 | 11.5948 | 11.4585 | 308.645 | 172.4082 | 304.7349 | 1.3428 | 67.1572 | 0.17062 | 7.93 | 7.86 | 7.82 | 189 | 269 | 294 | 301.9556 | -2.706 | 29.8701 | 300.3346 | 37.0702 | BMRL | 0.188 | 0.273 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 14:30 | 151 | 25 | 70 | 70 | 177 | 5.22 | 12.29 |  | 17.51 | 0.1222 | 0.29812 | 9.1085 | 11.9144 | 11.7743 | 310.3583 | 173.3029 | 306.3163 | 1.3503 | 68.6497 | 0.17151 | 7.86 | 7.66 | 7.74 | 191 | 270 | 294 | 302.8417 | -3.0074 | 29.128 | 301.1925 | 36.5854 | BMRL | 0.189 | 0.273 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 15:00 | 151.5 | 25 | 68 | 68 | 177 | 5 | 12.25 |  | 17.25 | 0.1222 | 0.28986 | 9.2609 | 11.4122 | 11.2781 | 309.0276 | 172.6574 | 305.1753 | 1.3444 | 66.6556 | 0.1692 | 7.85 | 7.86 | 7.95 | 189 | 269 | 295 | 302.3571 | -2.4939 | 29.8701 | 300.7561 | 37.1584 | BMRL | 0.186 | 0.271 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 15:30 | 152 | 25 | 68 | 68 | 177 | 5.07 | 12.2 |  | 17.27 | 0.1222 | 0.29357 | 9.249 | 11.572 | 11.436 | 309.6205 | 172.9576 | 305.7059 | 1.3471 | 66.6529 | 0.17158 | 7.95 | 7.86 | 7.97 | 190 | 269 | 300 | 302.5381 | -0.84604 | 29.4991 | 300.9263 | 36.8616 | BMRL | 0.191 | 0.274 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 16:00 | 152.5 | 25 | 68 | 68 | 177 | 5.02 | 11.18 |  | 16.2 | 0.1222 | 0.30988 | 9.9259 | 11.4579 | 11.3232 | 312.1937 | 174.4173 | 308.2861 | 1.3582 | 66.6418 | 0.16991 | 7.92 | 7.65 | 7.99 | 190 | 269 | 294 | 305.1968 | -3.8084 | 29.4991 | 303.5632 | 37.4101 | BMRL | 0.192 | 0.276 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 17:00 | 153.5 | 25 | 68 | 68 | 177 | 4.93 | 13 |  | 17.93 | 0.1222 | 0.27496 | 8.8717 | 11.2525 | 11.1202 | 306.706 | 171.391 | 302.937 | 1.3343 | 66.6657 | 0.16681 | 8.02 | 7.83 | 7.95 | 185 | 269 | 295 | 301.545 | -2.2186 | 31.3544 | 299.9219 | 38.3173 | BMRL | 0.195 | 0.271 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-24 | 17:30 | 154 | 25 | 68 | 69 | 177 | 5.15 | 13.6 |  | 18.75 | 0.1222 | 0.27467 | 8.44 | 11.7546 | 11.6164 | 306.6913 | 171.2861 | 302.7515 | 1.3344 | 67.1656 | 0.17295
[44 empty] | 1998-05-24 | 18:00 | 154.5 | 25 | 68 | 69 | 177 | 5.27 | 13.27 |  | 18.54 | 0.1222 | 0.28425 | 8.5469 | 12.0285 | 11.8871 | 308.1925 | 172.0714 | 304.1396 | 1.3409 | 67.1591 | 0.177
[44 empty] | 1998-05-25 | 7:00 | 167.5 | 25 | 68 | 70 | 177 | 5.12 | 8.5 |  | 13.62 | 0.1222 | 0.37592 | 11.9956 | 11.6861 | 11.5488 | 323.1232 | 180.4771 | 318.9969 | 1.4058 | 67.5942 | 0.17085
[44 empty] | 1998-05-25 | 7:30 | 168 | 25 | 68 | 69 | 177 | 5.11 | 10 |  | 15.11 | 0.1222 | 0.33819 | 10.7141 | 11.6633 | 11.5262 | 316.7946 | 176.9469 | 312.7572 | 1.3783 | 67.1217 | 0.17172 | 7.83 | 7.83 | 7.75 | 195 | 269 | 300 | [5 empty] | BMRL | 0.192 | 0.277 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-25 | 8:00 | 168.5 | 25 | 68 | 69 | 177 | 5.02 | 12.6 |  | 17.62 | 0.1222 | 0.2849 | 9.0454 | 11.4579 | 11.3232 | 308.2581 | 172.2186 | 304.3998 | 1.3411 | 67.1589 | 0.1686 | 8.02 | 7.84 | 7.99 | 191 | 269 | 300 | [5 empty] | BMRL | 0.192 | 0.272 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-25 | 8:30 | 169 | 25 | 68 | 69 | 177 | 5.07 | 12.27 |  | 17.34 | 0.1222 | 0.29239 | 9.2076 | 11.572 | 11.436 | 309.4345 | 172.8537 | 305.5223 | 1.3462 | 67.1538 | 0.1703 | 8.01 | 7.81 | 7.96 | 184 | 269 | 291 | [5 empty] | BMRL | 0.193 | 0.27 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-25 | 9:00 | 169.5 | 25 | 68 | 69 | 177 | 5.04 | 12.2 | X | 17.24 | 0.1222 | 0.29234 | 9.2668 | 11.5035 | 11.3683 | 309.4232 | 172.8606 | 305.5346 | 1.3462 | 67.1538 | 0.16929 | 8.04 | 7.81 | 7.95 | 188 | 269 | 289 | [5 empty] | BMRL | 0.191 | 0.269 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-25 | 9:30 |  | 25 | 68 | 69 | 177 | 5.07 | 12.25 |  | 17.32 | 0.1222 | 0.29273 | 9.2194 | 11.572 | 11.436 | 309.4875 | 172.8833 | 305.5746 | 1.3465 | 67.1535 | 0.1703 | 8.05 | 7.86 | 7.84 | 187 | 269 | 290 | [5 empty] | BMRL | 0.193 | 0.269 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-05-26 | 11:05 |  | 25 | 57 | 58 | 211 | 5.07 | 12.25 |  | 17.32 | 0.14568 | 0.29273 | 11.1824 | 11.572 | 11.436 | 309.366 | 173.1769 | 306.0936 | 1.3455 | 56.1545 | 0.20365
[44 empty] | 1998-05-26 | 11:20 |  | 25 | 68 | 69 | 211 | 5.07 | 12.25 |  | 17.32 | 0.14568 | 0.29273 | 11.1824 | 11.572 | 11.436 | 309.366 | 173.1769 | 306.0936 | 1.3455 | 67.1545 | 0.17029
[44 empty] | 1998-05-26 | 11:35 |  | 25 | 68 | 69 | 211 | 5.07 | 12.25 |  | 17.32 | 0.14568 | 0.29273 | 11.1824 | 11.572 | 11.436 | 309.366 | 173.1769 | 306.0936 | 1.3455 | 67.1545 | 0.17029
[44 empty] | 1998-05-26 | 11:50 |  | 25 | 68 | 69 | 211 | 5.07 | 12.25 |  | 17.32 | 0.14568 | 0.29273 | 11.1824 | 11.572 | 11.436 | 309.366 | 173.1769 | 306.0936 | 1.3455 | 67.1545 | 0.17029
[44 empty] | 1998-05-26 | 12:00 |  | 25 | 68 | 69 | 211 | 5.07 | 12.25 |  | 17.32 | 0.14568 | 0.29273 | 11.1824 | 11.572 | 11.436 | 309.366 | 173.1769 | 306.0936 | 1.3455 | 67.1545 | 0.17029
[44 empty] | 1998-05-26 | 13:30 |  | 25 | 68 | 69 | 211 | 5.07 | 12.25 |  | 17.32 | 0.14568 | 0.29273 | 11.1824 | 11.572 | 11.436 | 309.366 | 173.1769 | 306.0936 | 1.3455 | 67.1545 | 0.17029
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X11: C. Rice: Alkalinity values verified by consultant.
Note on X12: C. Rice: TDS values verified by consultant.
Note on X13: C. Rice: Total hardness values verified by consultant.
Note on X14: C. Rice: Calcium hardness values verified by consultant.
Note on X20: C. Rice: Consultant verified feed bromide concentrations but provided no explanantion as to why these values are low relative the other quarters.
Note on X42: C. Rice: Consultant verified feed HAA concentrations but provided no explanation as to why these values are high relative to the other quarters.
Note on X43: C. Rice: Consultant verified feed HAA concentrations but provided no explanation as to why these values are high relative to the other quarters.
Note on BV7: C. Rice 7/12/99: Consultant verified MTCw values but gave no explanation as to why these values are low relative to the other quarters.
Note on CY16: C. Rice: Alkalinity values verified by consultant due to consistently high mass balance closure errors.
Note on CY17: C. Rice: TDS values verified by consultant. No explanation given for the dip in permeate TDS as a function of recovery. TDS values verified due to the consistently high mass balance closure errors.
Note on CY18: C. Rice: Total and calcium hardness values verified by consultant due to consistently high mass balance closure errors.
Note on CY19: C. Rice: Total and calcium hardness values verified by consultant due to consistently high mass balance closure errors.
Note on DN17: C. Rice 7/12/99: Consultant verified all TDS concentrations.
Note on DQ10: C. Rice 7/12/99: Consultant verified all TDS, alkalinity, total hardness and calcium hardness values.
Note on DX17: C. Rice 7/12/99: Consultant verified all TDS concentrations.
Note on EA10: C. Rice 7/12/99: Consultant verified all TDS, alkalinity, total hardness and calcium hardness values.
Note on EH17: C. Rice 7/12/99: Consultant verified all TDS concentrations.
Note on EK10: C. Rice 7/12/99: Consultant verified all TDS, alkalinity, total hardness and calcium hardness values.

## SR40. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Manufacturer Reported Membrane Characteristics1 |  | Field 2-3: RBSMT Design Parameters | [8 empty] | Field 2-4: Foulants And Fouling Indices1 | Field 2-5: Pretreatment Used Prior To Membranes1 |  |  | Field 2-6: Feed Water Quality After Pretreatment | [5 empty] | Field 2-7: Membrane Setting Data | [20 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 2-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 2-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 2-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 2-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 2-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 2-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 2-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 2-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.49221 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.89 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.3 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-07-24 | 1998-07-16 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 10.07 | [10 empty] | Feed flow rate during sample collection (mL/min) | 7.32 | [7 empty] | Feed flow rate during sample collection (mL/min) | 13.34 | [7 empty] | Feed flow rate during sample collection (mL/min) | 21.87 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 9:30 | 9:30 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 284 | [10 empty] | Influent flow rate during sample collection (mL/min) | 284 | [7 empty] | Influent flow rate during sample collection (mL/min) | 284 | [7 empty] | Influent flow rate during sample collection (mL/min) | 284 | [6 empty] | SDS-THM4F, ug/L | 202.15 | 202.15 | 202.15 | 202.15 | SDS-THM4F, ug/L | 202.15 | 202.15 | 202.15 | 202.15 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 15.15 | 27.9 | 14.8 | 12.1 | SDS-THM4p, ug/L | 15.15 | 27.9 | 14.8 | 12.1 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.71 | 8 | 7.855 | 3.6919 | 1998-07-23 | 9:00 | 0 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-24 | 9:30 | 0 | 24 | 44 | 45 | 284 | 7.3 | 8.53 |  | 15.83 | 0.19608 | 0.46115 | 16.9406 | 16.6619 | 16.96 | 371.42 | 186.1873 | 366.6587 | 1.8285 | 42.6715 | 0.39746 | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | SDS-HAA5F, ug/L | 58.05 | 58.05 | 58.05 | 58.05 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1998-07-23 | 10:30 | 1.5 | 24 | 63 | 65 | 340 | 9.87 | 1.38 | 11.25 | 0.23474 | 0.87733 | 29.2222 | 22.5277 | 22.9308 | 0 | 0 | 0 | 0 | 64 | 0.35829 | 1998-07-24 | 10:30 | 1 | 24 | 44 | 45 | 284 | 7.3 | 8.53 |  | 15.83 | 0.19608 | 0.46115 | 16.9406 | 16.6619 | 16.96 | 371.42 | 186.1873 | 366.6587 | 1.8285 | 42.6715 | 0.39746 | [27 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 2.55 | 3.4 | 1.3 | 0 | SDS-HAA5p, ug/L | 2.55 | 3.4 | 1.3 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 334 | 326 | 330 | 2.4242 | 1998-07-23 | 11:00 | 2 | 24 | 63 | 64 | 340 | 10.17 | 6.37 | 16.54 | 0.23474 | 0.61487 | 19.5562 | 23.2125 | 23.6278 | 0 | 0 | 0 | 0 | 63.5 | 0.37209 | 1998-07-24 | 11:00 | 1.5 | 24 | 44 | 45 | 284 | 7.5 | 6.4 |  | 13.9 | 0.19608 | 0.53957 | 19.4317 | 17.1183 | 17.4247 | 391.3457 | 196.105 | 386.1897 | 1.9266 | 42.5734 | 0.40929 | 8.25 | 8.1 | 8.24 | 180 | 283 | 352 | 410.2188 | -16.5394 | 37.0629 | 407.1789 | 55.7934 | BMRL | 0.207 | 0.384 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-07-25 | 1998-07-26 | --- | --- | 1998-07-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-27 | 1998-07-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-28 | 1998-07-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-07-29 | 1998-07-29 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 472.5 | 472.5 | 472.5 | 472.5 | SDS-TOXF, ug Cl- /L | 472.5 | 472.5 | 472.5 | 472.5 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 288 | 284 | 286 | 1.3986 | 1998-07-23 | 11:30 | 2.5 | 24 | 63 | 65 | 340 | 10.25 | 4.05 | 14.3 | 0.23474 | 0.71678 | 22.7762 | 23.3951 | 23.8137 | 0 | 0 | 0 | 0 | 64 | 0.37209 | 1998-07-24 | 11:15 | 1.75 | 24 | 45 | 45 | 284 | 7.27 | 5.6 |  | 12.87 | 0.19608 | 0.56488 | 21.0668 | 16.5934 | 16.8903 | 398.1615 | 199.6032 | 393.0787 | 1.9602 | 43.0398 | 0.39243 | [27 empty] | Sampling time | hh:mm | 9:00 | 15:00 | --- | --- | 9:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 17:00 | 17:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 14:45 | 14:45 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 29 | 38 | BMRL | BMRL | SDS-TOXp, ug Cl- /L | 29 | 38 | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 322 | 278 | 300 | 14.6667 | 1998-07-23 | 12:00 | 3 | 24 | 63 | 65 | 340 | 10.4 | 4.24 | 14.64 | 0.23474 | 0.71038 | 22.224 | 23.7374 | 24.1622 | 0 | 0 | 0 | 0 | 64 | 0.37753 | 1998-07-24 | 11:30 | 2 | 24 | 45 | 45 | 284 | 7.29 | 4.06 |  | 11.35 | 0.19608 | 0.64229 | 24.022 | 16.639 | 16.9368 | 420.7827 | 210.9359 | 415.3961 | 2.0715 | 42.9285 | 0.39453 | 8.21 | 8.09 | 8.4 | 200 | 282 | 376 | 440.4187 | -17.1326 | 30.0699 | 437.3331 | 54.2683 | BMRL | 0.208 | 0.463 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 23.5 | 53.5 | --- | --- | 23.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 79.5 | 79.5 | --- | --- | --- | --- | --- | Operation time | hh.hh | 101.25 | 101.25 | --- | --- | --- | --- | --- | Cumulative time | hr | 122.5 | 122.5 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 4.575 | 4.575 | 4.575 | 4.575 | SDS-CDF, mg/L | 4.575 | 4.575 | 4.575 | 4.575 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 272 | 264 | 268 | 2.9851 | 1998-07-23 | 12:30 | 3.5 | 24 | 64 | 64 | 340 | 10.5 | 4.6 | 15.1 | 0.23474 | 0.69536 | 21.5166 | 23.9657 | 24.3945 | 0 | 0 | 0 | 0 | 64 | 0.38116 | 1998-07-24 | 12:00 | 2.5 | 24 | 45 | 45 | 284 | 7.24 | 3.76 |  | 11 | 0.19608 | 0.65818 | 24.8182 | 16.5249 | 16.8206 | 425.7279 | 213.4341 | 420.3159 | 2.0959 | 42.9041 | 0.39205 | 8.42 | 8.38 | 8.31 | 201 | 282 | 391 | 449.6702 | -15.0052 | 29.7203 | 446.5005 | 54.9833 | BMRL | 0.202 | 0.485 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.84 | 7.65 | 7.745 | 2.4532 | 7.85 | --- | --- | --- | --- | --- | pH | --- | 7.61 | 8.17 | --- | --- | --- | --- | --- | pH | --- | 7.84 | 7.85 | --- | --- | --- | --- | --- | pH | --- | 7.94 | 7.98 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 0.865 | 0.4 | 0.43 | 0.83 | SDS-CDp, mg/L | 0.865 | 0.4 | 0.43 | 0.83 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 15.1667 | 78.41 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.195 | 0.195 | 0.195 | 0 | 1998-07-23 | 13:30 | 4.5 | 24 | 64 | 64 | 340 | 10.38 | 4.3 | 14.68 | 0.23474 | 0.70708 | 22.1608 | 23.6918 | 24.1157 | 0 | 0 | 0 | 0 | 64 | 0.37681 | 1998-07-24 | 13:00 | 3.5 | 24 | 45 | 45 | 284 | 7.05 | 3.47 |  | 10.52 | 0.19608 | 0.67015 | 25.9962 | 16.0912 | 16.3792 | 429.4704 | 215.3841 | 424.1559 | 2.1143 | 42.8857 | 0.38193 | 8.25 | 8.16 | 8.43 | 203 | 282 | 393 | 454.6311 | -15.6822 | 29.021 | 451.5079 | 55.0395 | BMRL | 0.205 | 0.545 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.65 | 6.65 | 6.65 | 6.65 | TOCF, mg/L | 6.65 | 6.65 | 6.65 | 6.65 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 38.5 | 101.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | 0.07 | 0.07 | #VALUE! | 1998-07-23 | 14:15 | 5.25 | 24 | 50 | 51 | 340 | 8.33 | 3.4 | 11.73 | 0.23474 | 0.71014 | 27.9855 | 19.0128 | 19.353 | 0 | 0 | 0 | 0 | 50.5 | 0.38323 | 1998-07-24 | 14:00 | 4.5 | 24 | 45 | 45 | 284 | 7.17 | 3.3 |  | 10.47 | 0.19608 | 0.68481 | 26.1251 | 16.3651 | 16.658 | 434.2851 | 217.7516 | 428.8184 | 2.138 | 42.862 | 0.38864 | 8.26 | 8.2 | 8.19 | 206 | 282 | 384 | 459.8182 | -19.7443 | 27.972 | 456.6142 | 54.8853 | BMRL | 0.201 | 0.576 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 232 | 230 | 231 | 0.8658 | 372 | 550.3548 | -47.9448 | 30 | 546.4482 | 57.727 | Alkalinity | mg/L as CaCO3 | 316 | 442 | 443.2727 | -0.28795 | 4.2424 | 441.8129 | 28.4765 | Alkalinity | mg/L as CaCO3 | 188 | 292 | 477.7959 | -63.6287 | 43.0303 | 474.3248 | 60.3647 | Alkalinity | mg/L as CaCO3 | 162 | 288 | 402 | -39.5833 | 50.9091 | 399.2277 | 59.4217 | TOCp, mg/L | 0.5 | 0.7 | BMRL | 0.6 | TOCp, mg/L | 0.5 | 0.7 | BMRL | 0.6 | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 73.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6.5 | 6.8 | 6.65 | 4.5113 | 1998-07-23 | 14:30 | 5.5 | 24 | 50 | 51 | 340 | 8.3 | 3.6 | 11.9 | 0.23474 | 0.69748 | 27.5714 | 18.9443 | 19.2833 | 0 | 0 | 0 | 0 | 50.5 | 0.38185 | 1998-07-24 | 15:00 | 5.5 | 24 | 45 | 45 | 284 | 7.13 | 3.02 |  | 10.15 | 0.19608 | 0.70246 | 26.9803 | 16.2738 | 16.565 | 440.1496 | 220.708 | 434.6404 | 2.1669 | 42.8331 | 0.38673 | 8.22 | 8.21 | 8.31 | 211 | 283 | 410 | 463.0695 | -12.9438 | 26.2238 | 459.9054 | 54.121 | BMRL | 0.203 | 0.608 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 213 | 219 | 216 | 2.7778 | 385 | 441.8065 | -14.7549 | 24.4755 | 439.0442 | 50.8022 | Total dissolved solids | mg/L | 256 | 458 | 528.7273 | -15.4426 | 10.4895 | 525.5992 | 51.2937 | Total dissolved solids | mg/L | 212 | 357 | 363.0204 | -1.6864 | 25.8741 | 361.2115 | 41.3086 | Total dissolved solids | mg/L | 197 | 324 | 324.1429 | -0.044092 | 31.1189 | 322.6742 | 38.9477 | UV254 F, cm-1 | 0.2035 | 0.2035 | 0.2035 | 0.2035 | UV254 F, cm-1 | 0.2035 | 0.2035 | 0.2035 | 0.2035 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 8.5 | 71.7434 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.192 | 0.215 | 0.2035 | 11.3022 | 1998-07-23 | 15:00 | 6 | 24 | 45 | 45 | 340 | 7.45 | 2.9 | 10.35 | 0.23474 | 0.71981 | 31.8502 | 17.0042 | 17.3085 | 0 | 0 | 0 | 0 | 45 | 0.38463 | 1998-07-24 | 16:00 | 6.5 | 24 | 45 | 45 | 284 | 7.24 | 2.95 |  | 10.19 | 0.19608 | 0.7105 | 26.8705 | 16.5249 | 16.8206 | 442.9293 | 222.0578 | 437.2986 | 2.1806 | 42.8194 | 0.39283 | 8.25 | 8.24 | 8.27 | 206 | 280 | 419 | 482.339 | -15.1167 | 27.972 | 478.8166 | 56.9773 | BMRL | 0.202 | 0.619 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 168 | 226 | 197 | 29.4416 | 438 | 529.2581 | -20.8352 | 34.3333 | 525.1936 | 62.49 | Total hardness | mg/L as CaCO3 | 290 | 698 | 380.9091 | 45.4285 | 3.3333 | 379.8664 | 23.6574 | Total hardness | mg/L as CaCO3 | 162 | 384 | 443.6327 | -15.5293 | 46 | 440.2593 | 63.2035 | Total hardness | mg/L as CaCO3 | 162 | 352 | 359.1429 | -2.0292 | 46 | 356.8656 | 54.6048 | UV254 p, cm-1 | #DIV/0! | 0.009 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.009 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.9538 | 3.1618 | 3.0578 | 6.7996 | 1998-07-23 | 15:45 | 6.75 | 24 | 45 | 45 | 340 | 7.33 | 3.17 | 10.5 | 0.23474 | 0.6981 | 31.381 | 16.7303 | 17.0297 | 0 | 0 | 0 | 0 | 45 | 0.37844 | 1998-07-24 | 17:00 | 7.5 | 23.9 | 45 | 45 | 284 | 7.16 | 3.01 |  | 10.17 | 0.19608 | 0.70403 | 26.9253 | 16.3423 | 16.684 | 440.6929 | 220.9685 | 435.1534 | 2.1695 | 42.8305 | 0.38954 | 8.26 | 8.22 | 8.25 | 213 | 281 | 414 | 459.6478 | -11.026 | 25.5245 | 456.5387 | 53.3446 | BMRL | 0.204 | 0.642 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 156 | 172 | 164 | 9.7561 | 357 | 499.4839 | -39.9114 | 38.806 | 495.3799 | 66.8941 | Calcium hardness | mg/L as CaCO3 | 268 | 618 | 268 | 56.6343 | 0 | 268 | 0 | Calcium hardness | mg/L as CaCO3 | 134 | 340 | 407.4694 | -19.8439 | 50 | 404.1938 | 66.8476 | Calcium hardness | mg/L as CaCO3 | 148 | 314 | 319.4286 | -1.7288 | 44.7761 | 317.4484 | 53.3782 | BromideF, ug/L | 84.5 | 84.5 | 84.5 | 84.5 | BromideF, ug/L | 84.5 | 84.5 | 84.5 | 84.5 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 86 | 83 | 84.5 | 3.5503 | 1998-07-23 | 16:15 | 7.25 | 24 | 37 | 37 | 340 | 6 | 2.32 | 8.32 | 0.23474 | 0.72115 | 39.8654 | 13.6947 | 13.9397 | 0 | 0 | 0 | 0 | 37 | 0.37675 | 1998-07-25 | 9:00 | 23.5 | 24 | 45 | 45 | 284 | 7.2 | 3.13 |  | 10.33 | 0.19608 | 0.697 | 26.4927 | 16.4336 | 16.7277 | 438.3416 | 219.7737 | 432.8005 | 2.158 | 42.842 | 0.39045 | [27 empty] | Turbidity | ntu | 0.065 | 0.066 | 0.0655 | 1.5267 | 0.245 | 0.48324 | -97.2416 | 66.4103 | 0.47813 | 86.3008 | Turbidity | ntu | 0.064 | 0.427 | 1.2549 | -193.8897 | 67.1795 | 1.2412 | 94.8439 | Turbidity | ntu | 0.069 | 0.261 | 0.32614 | -24.9589 | 64.6154 | 0.32306 | 78.6419 | Turbidity | ntu | 0.054 | 0.176 | 0.25543 | -45.1299 | 72.3077 | 0.2531 | 78.6647 | Bromidep, ug/L | 77 | 83 | 74 | 73 | Bromidep, ug/L | 77 | 83 | 74 | 73 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 5 | 6 | 5.5 | 18.1818 | 1998-07-23 | 16:45 | 7.75 | 24 | 46 | 47 | 340 | 7.6 | 3.04 | 10.64 | 0.23474 | 0.71429 | 30.9549 | 17.3466 | 17.657 | 0 | 0 | 0 | 0 | 46.5 | 0.37972 | 1998-07-25 | 10:00 | 24.5 | 24 | 45 | 45 | 284 | 7.17 | 3.1 |  | 10.27 | 0.19608 | 0.69815 | 26.6534 | 16.3651 | 16.658 | 438.7148 | 219.9727 | 433.1923 | 2.1598 | 42.8402 | 0.38884 | 8.27 | 8.15 | 8.43 | 212 | 282 | 417 | 457.1548 | -9.6295 | 25.8741 | 454.0602 | 53.3102 | BMRL | 0.204 | 0.638 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | AlkF, mg/L CaCO3 | 330 | 330 | 330 | 330 | AlkF, mg/L CaCO3 | 330 | 330 | 330 | 330
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 1.15 | 0.7 | 0.925 | 48.6486 | 1998-07-23 | 17:00 | 8 | 24 | 46 | 47 | 340 | 7.86 | 3.66 | 11.52 | 0.23474 | 0.68229 | 28.5139 | 17.94 | 18.261 | 0 | 0 | 0 | 0 | 46.5 | 0.39271 | 1998-07-25 | 11:00 | 25.5 | 24 | 45 | 45 | 284 | 7.09 | 3.12 |  | 10.21 | 0.19608 | 0.69442 | 26.8159 | 16.1825 | 16.4721 | 437.4323 | 219.3612 | 431.9882 | 2.1535 | 42.8465 | 0.38444 | 8.43 | 8.36 | 8.4 | 213 | 282 | 406 | 451.8878 | -11.3024 | 25.5245 | 448.9059 | 52.5513 | BMRL | 0.202 | 0.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | 0.5 | BMRL | 0.5 | #VALUE! | 19.8 | 20.3387 | -2.7208 | 92.4812 | 20.096 | 97.5119 | Total organic carbon | mg/L | 0.7 | 52 | 54.7909 | -5.3671 | 89.4737 | 54.1705 | 98.7078 | Total organic carbon | mg/L | BMRL | 12 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | 0.6 | 8.2 | 9.2429 | -12.7178 | 90.9774 | 9.143 | 93.4376 | Alkp, mg/L CaCO3 | 231 | 316 | 188 | 162 | Alkp, mg/L CaCO3 | 231 | 316 | 188 | 162
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 3.85 | 5.3 | 4.575 | 31.694 | 1998-07-24 | 9:15 | 24.25 | 24 | 43 | 43 | 340 | 7.62 | 1.98 | 9.6 | 0.23474 | 0.79375 | 34.4167 | 17.3922 | 17.7035 | 0 | 0 | 0 | 0 | 43 | 0.41171 | 1998-07-25 | 12:00 | 26.5 | 24 | 45 | 45 | 284 | 7.13 | 3.07 |  | 10.2 | 0.19608 | 0.69902 | 26.8431 | 16.2738 | 16.565 | 438.9898 | 220.1264 | 433.4951 | 2.1612 | 42.8388 | 0.38668 | 8.26 | 8.2 | 8.46 | 221 | 279 | 412 | 436.9609 | -6.0585 | 22.7273 | 434.25 | 49.1077 | BMRL | 0.206 | 0.641 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.628 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.009 | 1.593 | 1.7772 | -11.5619 | 95.5774 | 1.7569 | 99.4877 | UV254 | cm-1 | BMRL | 0.395 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.28 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 300 | 300 | 300 | 300 | T-HdF, mg/L CaCO3 | 300 | 300 | 300 | 300
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | 1998-07-24 | 9:30 | 24.5 | 24 | 44 | 45 | 340 | 7.96 | 3.2 | 11.16 | 0.23474 | 0.71326 | 29.4659 | 18.1683 | 18.4934 | 0 | 0 | 0 | 0 | 44.5 | 0.41558 | 1998-07-25 | 13:00 | 27.5 | 24 | 45 | 45 | 284 | 6.91 | 3.06 |  | 9.97 | 0.19608 | 0.69308 | 27.4855 | 15.7717 | 16.0539 | 436.9113 | 219.171 | 431.6135 | 2.1509 | 42.8491 | 0.37466 | 8.45 | 8.38 | 8.27 | 224 | 279 | 410 | 426.0065 | -3.904 | 21.6783 | 423.549 | 47.1136 | BMRL | 0.204 | 0.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.1717 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | 1.2857 | 3.0635 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.2917 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.4146 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 197 | 290 | 162 | 162 | T-Hdp, mg/L CaCO3 | 197 | 290 | 162 | 162
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 9 | 8.78 | 8.89 | 2.4747 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 14:00 | 28.5 | 23.9 | 45 | 45 | 284 | 6.97 | 2.97 |  | 9.94 | 0.19608 | 0.70121 | 27.5714 | 15.9087 | 16.2412 | 439.6575 | 220.5247 | 434.2795 | 2.1644 | 42.8356 | 0.37915 | 8.25 | 8.23 | 8.35 | 223 | 280 | 417 | 433.8485 | -4.0404 | 22.028 | 431.2611 | 48.2912 | BMRL | 0.202 | 0.641 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 76 | 78 | 77 | 2.5974 | --- | 101.1935 | --- | 8.8757 | 100.8976 | 23.685 | Bromide | mg/L | 83 | --- | 96.6364 | --- | 1.7751 | 96.48 | 13.9718 | Bromide | mg/L | 74 | --- | 95.4286 | --- | 12.426 | 95.1719 | 22.246 | Bromide | mg/L | 73 | --- | 89.4286 | --- | 13.6095 | 89.2388 | 18.197 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268 | Ca-HdF, mg/L CaCO3 | 268 | 268 | 268 | 268
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 15:00 | 29.5 | 24 | 45 | 45 | 284 | 6.91 | 2.92 |  | 9.83 | 0.19608 | 0.70295 | 27.8911 | 15.7717 | 16.0539 | 440.2196 | 220.8305 | 434.8816 | 2.1672 | 42.8328 | 0.3748 | 8.47 | 8.52 | 8.35 | 222 | 283 | 418 | 437.4521 | -4.6536 | 22.3776 | 434.831 | 48.9457 | BMRL | 0.2 | 0.652 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 2 | 2.5 | 2.25 | 22.2222 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 2.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 164 | 268 | 134 | 148 | Ca-Hdp, mg/L CaCO3 | 164 | 268 | 134 | 148
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 415 | 530 | 472.5 | 24.3386 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 16:00 | 30.5 | 23.9 | 45 | 45 | 284 | 6.97 | 2.9 |  | 9.87 | 0.19608 | 0.70618 | 27.7741 | 15.9087 | 16.2412 | 441.3391 | 221.3682 | 435.9406 | 2.1727 | 42.8273 | 0.37923 | 8.27 | 8.23 | 8.43 | 228 | 290 | 416 | 425.4 | -2.2596 | 20.2797 | 422.9777 | 46.0964 | BMRL | 0.204 | 0.653 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.55 | 1.22 | 1.385 | 23.8267 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.6 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.57 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.67 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 150 | 200 | 175 | 28.5714 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-25 | 17:00 | 31.5 | 24 | 45 | 45 | 284 | 7 | 3.76 |  | 10.76 | 0.19608 | 0.65056 | 25.3941 | 15.9771 | 16.263 | 423.2438 | 212.2805 | 418.044 | 2.0836 | 42.9164 | 0.37895 | 8.36 | 8.59 | 8.3 | 223 | 288 | 403 | 403.2872 | -0.071274 | 22.028 | 401.0654 | 44.3981 | BMRL | 0.205 | 0.619 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 0.45 | 1.28 | 0.865 | 95.9538 | --- | 12.8327 | --- | 81.0929 | 12.6863 | 93.1816 | SDS-Cl2 demand | mg/L | 0.4 | --- | 38.3545 | --- | 91.2568 | 37.9192 | 98.9451 | SDS-Cl2 demand | mg/L | 0.43 | --- | 8.8892 | --- | 90.6011 | 8.7879 | 95.1069 | SDS-Cl2 demand | mg/L | 0.83 | --- | 6.18 | --- | 81.8579 | 6.1182 | 86.4339 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 19 | 27 | 23 | 34.7826 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 14:00 | 52.5 | 24 | 45 | 46 | 284 | 6.25 | 3.08 |  | 9.33 | 0.19608 | 0.66988 | 29.4394 | 14.2653 | 14.5205 | 429.0725 | 215.4939 | 424.3722 | 2.1123 | 43.3877 | 0.33467 | [27 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 69.5989 | 74.6915 | 69.4689 | 68.482 | Qp/QT (THM4), % | 88.8503 | 95.3515 | 88.6843 | 87.4244
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 3.8 | 4.5 | 4.15 | 16.8675 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 15:00 | 53.5 | 23.4 | 45 | 46 | 284 | 6.82 | 3.18 |  | 10 | 0.19608 | 0.682 | 27.4 | 15.5663 | 16.1283 | 433.2205 | 217.3547 | 428.0367 | 2.1327 | 43.3673 | 0.3719 | 7.52 | 7.44 | 7.69 | 196 | 275 | 392 | 479.0189 | -22.1987 | 31.4685 | 475.6206 | 58.7907 | BMRL | 0.202 | 0.62 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 15:45 | 54.25 | 24 | 45 | 46 | 284 | 6.8 | 3 |  | 9.8 | 0.19608 | 0.69388 | 27.9796 | 15.5206 | 15.7984 | 437.131 | 219.3245 | 431.9159 | 2.152 | 43.348 | 0.36445 | 7.33 | 7.3 | 7.45 | 223 | 285 | 405 | 428.8 | -5.8765 | 22.028 | 426.3362 | 47.6939 | BMRL | 0.201 | 0.633 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 19.4226 | 17.2311 | 18.6264 | 18.2962 | SDS-HAA5b, ug/L | 8.7381 | 5.9404 | 7.7217 | 7.3002
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 172.8 | 231.5 | 202.15 | 29.0378 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 16:15 | 54.75 | 24 | 45 | 46 | 284 | 6.3 | 2.96 |  | 9.26 | 0.19608 | 0.68035 | 29.6695 | 14.3794 | 14.6367 | 432.4716 | 217.1816 | 427.6958 | 2.129 | 43.371 | 0.33748 | 8.02 | 7.83 | 7.79 | 224 | 284 | 402 | 417.9595 | -3.97 | 21.6783 | 415.8081 | 46.129 | BMRL | 0.201 | 0.633 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | 29 | 29 | #VALUE! | --- | 1459.6452 | --- | 93.8624 | 1442.1442 | 97.9891 | SDS-TOX | mg Cl- /L | 38 | --- | 3988 | --- | 91.9577 | 3942.6946 | 99.0362 | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 163.8287 | 147.9653 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 78.4491 | 58.1977 | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 3.5 | 3.3 | 3.4 | 5.8824 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 17:00 | 55.5 | 23.1 | 45 | 46 | 284 | 6.83 | 2.97 |  | 9.8 | 0.19608 | 0.69694 | 27.9796 | 15.5891 | 16.2959 | 438.1652 | 219.8316 | 432.9144 | 2.1571 | 43.3429 | 0.37598 | 7.59 | 7.48 | 7.53 | 217 | 275 | 397 | 444.6768 | -12.0093 | 24.1259 | 441.939 | 50.8982 | BMRL | 0.204 | 0.637 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 6.8 | 7.6 | 7.2 | 11.1111 | --- | 548.4903 | --- | 95.8857 | 541.8688 | 98.6713 | SDS-CHCl3 | mg/L | 7.2 | --- | 1532.6545 | --- | 95.8857 | 1515.158 | 99.5248 | SDS-CHCl3 | mg/L | 6.5 | --- | 350.3776 | --- | 96.2857 | 346.2586 | 98.1228 | SDS-CHCl3 | mg/L | 5.7 | --- | 247.5571 | --- | 96.7429 | 244.7634 | 97.6712 | SDS-CDb, mg/L | 1.9929 | 1.4566 | 1.6955 | 2.0103 | SDS-CDb, mg/L | 1.2787 | 0.59407 | 0.89904 | 1.301
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 34 | 45 | 39.5 | 27.8481 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 18:00 | 56.5 | 24 | 45 | 46 | 284 | 6.79 | 3.08 |  | 9.87 | 0.19608 | 0.68794 | 27.7741 | 15.4978 | 15.7751 | 435.1603 | 218.3397 | 429.9764 | 2.1423 | 43.3577 | 0.36384 | 7.62 | 7.53 | 7.58 | 225 | 291 | 412 | 420.4773 | -2.0576 | 21.3287 | 418.1405 | 46.1903 | BMRL | 0.201 | 0.645 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 4.1 | 2.5 | 3.3 | 48.4848 | --- | 66.8484 | --- | 85.6522 | 66.071 | 95.0054 | SDS-BDCM | mg/L | 7.6 | --- | 147.6 | --- | 66.9565 | 145.9942 | 94.7943 | SDS-BDCM | mg/L | 3.8 | --- | 42.9837 | --- | 83.4783 | 42.5143 | 91.0618 | SDS-BDCM | mg/L | 3.1 | --- | 31.5286 | --- | 86.5217 | 31.2002 | 90.0642 | TOCb, mg/L | 2.3697 | 2.2059 | #VALUE! | 2.5068 | TOCb, mg/L | 1.1857 | 0.97659 | #VALUE! | 1.3608
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 8.3 | 22 | 15.15 | 90.429 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 19:00 | 57.5 | 23.7 | 45 | 46 | 284 | 6.8 | 2.92 |  | 9.72 | 0.19608 | 0.69959 | 28.2181 | 15.5206 | 15.9391 | 439.0405 | 220.2826 | 433.8026 | 2.1614 | 43.3386 | 0.36778 | 8.05 | 7.9 |  | 225 | 284 |  | 428.0548 |  | 21.3287 | 425.6239 | 47.1364 | BMRL | 0.201 | 0.644 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 3.5 | 2.5 | 3 | 33.3333 | --- | 6.7097 | --- | 27.7108 | 6.6643 | 54.984 | SDS-DBCM | mg/L | 8.3 | --- | -29.4273 | --- | -100 | -28.9946 | 128.6261 | SDS-DBCM | mg/L | 3 | --- | 5.3469 | --- | 27.7108 | 5.3188 | 43.5966 | SDS-DBCM | mg/L | 2.2 | --- | 4.9857 | --- | 46.988 | 4.9535 | 55.5873 | UV254 b, cm-1 | #DIV/0! | 0.058225 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.018041 | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 20:00 | 58.5 | 24 | 45 | 46 | 284 | 6.8 | 2.96 |  | 9.76 | 0.19608 | 0.69672 | 28.0984 | 15.5206 | 15.7984 | 438.0798 | 219.8006 | 432.8534 | 2.1567 | 43.3433 | 0.36449 | 7.71 | 7.58 | 7.84 | 228 | 287 | 412 | 419.2432 | -1.7581 | 20.2797 | 416.9537 | 45.3177 | BMRL | 0.203 | 0.64 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 1.8 | 1.5 | 1.65 | 18.1818 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 4.8 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.5 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHBr3 | mg/L | 1.1 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Bromideb, ug/L | 79.2801 | 83.3796 | 77.2058 | 76.6246 | Bromideb, ug/L | 77.8362 | 83.0697 | 75.1882 | 74.4462
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 21:00 | 59.5 | 24.1 | 45 | 46 | 284 | 6.81 | 2.93 |  | 9.74 | 0.19608 | 0.69918 | 28.1581 | 15.5435 | 15.7749 | 438.9072 | 220.2117 | 433.6631 | 2.1607 | 43.3393 | 0.36399 | 7.85 | 7.68 | 7.82 | 215 | 275 | 396 | 451.0205 | -13.8941 | 24.8252 | 448.1907 | 52.0294 | BMRL | 0.203 | 0.647 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 16.2 | 14.1 | 15.15 | 13.8614 | --- | 618.3758 | --- | 92.5056 | 610.9966 | 97.5204 | SDS-THM4 | mg/L | 27.9 | --- | 1611.9909 | --- | 86.1984 | 1593.8218 | 98.2495 | SDS-THM4 | mg/L | 14.8 | --- | 397.1469 | --- | 92.6787 | 392.5673 | 96.2299 | SDS-THM4 | mg/L | 12.1 | --- | 283.6 | --- | 94.0143 | 280.4639 | 95.6857 | Alkb, mg/L CaCO3 | 261.0971 | 319.5432 | 231.3541 | 214.9503 | Alkb, mg/L CaCO3 | 242.0382 | 316.6508 | 204.0683 | 183.1271
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 5 | 6.7 | 5.85 | 29.0598 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-26 | 22:00 | 60.5 | 24 | 45 | 46 | 284 | 6.81 | 2.92 |  | 9.73 | 0.19608 | 0.6999 | 28.1881 | 15.5435 | 15.8216 | 439.1485 | 220.3328 | 433.9015 | 2.1619 | 43.3381 | 0.36507 | 7.98 | 7.81 |  | 219 | 272 | 405 | 442.2568 | -9.1992 | 23.4266 | 439.5801 | 50.1797 | BMRL | 0.2 | 0.652 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 228.3131 | 292.5308 | 204.1329 | 205.4949 | T-Hdb, mg/L CaCO3 | 208.4842 | 290.4648 | 177.6157 | 179.3544
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 9:30 | 72 | 22.7 | 45 | 45 | 284 | 6.86 | 3.49 |  | 10.35 | 0.19608 | 0.6628 | 26.4396 | 15.6576 | 16.5621 | 427.0479 | 214.2424 | 421.9076 | 2.1024 | 42.8976 | 0.38608 | [27 empty] | SDS-DCAA* | mg/L | 1.3 | 2.8 | 2.05 | 73.1707 | --- | 122.8565 | --- | 94.8101 | 121.3786 | 98.3111 | SDS-DCAA* | mg/L | 1.4 | --- | 347.7636 | --- | 96.4557 | 343.7909 | 99.5928 | SDS-DCAA* | mg/L | 1.3 | --- | 79.2592 | --- | 96.7089 | 78.3254 | 98.3403 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 195.6171 | 268 | 174.9117 | 185.8216 | Ca-Hdb, mg/L CaCO3 | 175.5957 | 268 | 149.1631 | 163.0908
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 10:15 | 72.75 | 24 | 45 | 45 | 284 | 6.71 | 2.95 |  | 9.66 | 0.19608 | 0.69462 | 28.3996 | 15.3152 | 15.5893 | 437.3396 | 219.4647 | 432.1919 | 2.153 | 42.847 | 0.36384 | 7.76 | 7.63 | 7.69 | 195 | 276 | 397 | 492.9864 | -24.1779 | 31.8182 | 489.4662 | 60.1607 | BMRL | 0.2 | 0.655 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 1.2 | 3.9 | 2.55 | 105.8824 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 11:00 | 73.5 | 24 | 45 | 45 | 284 | 6.63 | 2.83 |  | 9.46 | 0.19608 | 0.70085 | 29.0211 | 15.1326 | 15.4034 | 439.3906 | 220.5256 | 434.2812 | 2.1631 | 42.8369 | 0.35958 | 8.11 | 7.92 | 7.85 | 225 | 283 | 405 | 428.9081 | -5.9032 | 21.3287 | 426.528 | 47.2485 | BMRL | 0.201 | 0.662 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 45.8 | 70.3 | 58.05 | 42.205 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 11:45 | 74.25 | 22.9 | 45 | 45 | 284 | 6.71 | 2.91 |  | 9.62 | 0.19608 | 0.69751 | 28.5218 | 15.3152 | 16.1045 | 438.304 | 219.9486 | 433.145 | 2.1578 | 42.8422 | 0.3759 | 8.03 | 7.89 | 7.83 | 221 | 285 | 405 | 435.8797 | -7.6246 | 22.7273 | 433.3413 | 49.0009 | BMRL | 0.201 | 0.659 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | 1 | BMRL | 1 | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 2 | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 50.8 | 77 | 63.9 | 41.0016 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 14:30 | 77 | 24 | 45 | 45 | 284 | 6.67 | 2.9 |  | 9.57 | 0.19608 | 0.69697 | 28.6761 | 15.2239 | 15.4963 | 438.108 | 219.8661 | 432.9824 | 2.1568 | 42.8432 | 0.3617 | 8.02 | 7.89 | 7.88 | 217 | 274 | 396 | 444.7 | -12.298 | 24.1259 | 442.0261 | 50.9079 | BMRL | 0.2 | 0.668 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.4 | --- | 41.8545 | --- | 76.0684 | 41.3905 | 96.6176 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 7.2973 | 7.4108 | 7.1366 | 6.9767 | Qp/QT (HAA5), % | 55.9459 | 56.8161 | 54.7137 | 53.4884
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 15:30 | 78 | 24 | 45 | 45 | 284 | 6.67 | 2.79 |  | 9.46 | 0.19608 | 0.70507 | 29.0211 | 15.2239 | 15.4963 | 440.8342 | 221.2343 | 435.6767 | 2.1702 | 42.8298 | 0.36181 | [27 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 188.5041 | 189.2367 | 188.7796 | 188.8907 | SDS-THM4b, ug/L | 97.5311 | 103.1479 | 99.644 | 100.4953
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 15:45 | 78.25 | 24 | 45 | 46 | 284 | 6.75 | 2.08 |  | 8.83 | 0.19608 | 0.76444 | 31.1631 | 15.4065 | 15.6822 | 461.9295 | 231.7877 | 456.4596 | 2.2741 | 43.2259 | 0.3628 | [27 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-07-27 | 16:15 | 78.75 | 24 | 45 | 46 | 284 | 6.71 | 1.49 |  | 8.2 | 0.19608 | 0.81829 | 33.6341 | 15.3152 | 15.5893 | 482.83 | 242.2926 | 477.1469 | 2.377 | 43.123 | 0.36151 | [27 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 440.1365 | 440.3001 | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 224.3797 | 225.634 | #VALUE! | #VALUE!
[44 empty] | 1998-07-27 | 16:40 | 79.1667 | 24 | 45 | 46 | 284 | 6.6 | 1.2 |  | 7.8 | 0.19608 | 0.84615 | 35.4103 | 15.0641 | 15.3337 | 494.3436 | 248.1193 | 488.6215 | 2.4336 | 43.0664 | 0.35605 | [27 empty] | SDS-HAA5 | mg/L | 2.3 | 2.8 | 2.55 | 19.6078 | --- | 181.5823 | --- | 95.6072 | 179.3922 | 98.5785 | SDS-HAA5 | mg/L | 3.4 | --- | 500.2182 | --- | 94.143 | 494.5198 | 99.3125 | SDS-HAA5 | mg/L | 1.3 | --- | 117.1163 | --- | 97.7606 | 115.7291 | 98.8767 | SDS-HAA5 | mg/L | 0 | --- | 82.9286 | --- | 100 | 81.9707 | 100 | SDS-CDb, mg/L | 4.3043 | 4.2656 | 4.2792 | 4.3137 | SDS-CDb, mg/L | 2.4994 | 2.2029 | 2.3071 | 2.5719
[44 empty] | 1998-07-27 | 17:00 | 79.5 | 24 | 45 | 46 | 284 | 6.6 | 0.93 |  | 7.53 | 0.19608 | 0.87649 | 36.7158 | 15.0641 | 15.3337 | 507.6025 | 254.7742 | 501.7269 | 2.4989 | 43.0011 | 0.35659 | 8.07 | 7.94 | 7.89 | 235 | 274 | 431 | 647.9355 | -50.3331 | 17.8322 | 643.1373 | 63.4604 | BMRL | 0.198 | 0.854 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 2.3 | 2.8 | 2.55 | 19.6078 | --- | 200.4532 | --- | 96.0094 | 198.0323 | 98.7123 | SDS-HAA6 | mg/L | 4.8 | --- | 542.0727 | --- | 92.4883 | 535.9104 | 99.1043 | SDS-HAA6 | mg/L | 1.3 | --- | 129.0551 | --- | 97.9656 | 127.5249 | 98.9806 | SDS-HAA6 | mg/L | 0 | --- | 91.2857 | --- | 100 | 90.2313 | 100 | TOCb, mg/L | 6.2012 | 6.2091 | #VALUE! | 6.2279 | TOCb, mg/L | 3.2093 | 3.2694 | #VALUE! | 3.414
[44 empty] | 1998-07-27 | 17:40 | 80.1667 | 24 | 45 | 45 | 284 | 6.5 | 0.94 |  | 7.44 | 0.19608 | 0.87366 | 37.172 | 14.8359 | 15.1014 | 506.2616 | 254.1468 | 500.4914 | 2.4923 | 42.5077 | 0.35526 | 8.09 | 7.96 | 7.86 | 239 | 274 | 446 | 611 | -36.9955 | 16.4336 | 606.743 | 60.6093 | BMRL | 0.199 | 0.944 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.18909 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.092993 | #VALUE! | #VALUE!
[44 empty] | 1998-07-27 | 18:00 | 80.5 | 24 | 45 | 46 | 284 | 6.56 | 0.91 |  | 7.47 | 0.19608 | 0.87818 | 37.0187 | 14.9728 | 15.2408 | 508.3313 | 255.1583 | 502.4834 | 2.5025 | 42.9975 | 0.35446 | 8.05 | 7.92 | 7.78 | 237 | 274 | 453 | 639.2308 | -41.1105 | 17.1329 | 634.5853 | 62.6528 | BMRL | 0.201 | 1.015 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 83.9527 | 84.3888 | 83.7507 | 83.6977 | Bromideb, ug/L | 80.3041 | 83.6478 | 78.7551 | 78.3488
[44 empty] | 1998-07-27 | 18:30 | 81 | 24 | 45 | 46 | 284 | 6.57 | 0.91 |  | 7.48 | 0.19608 | 0.87834 | 36.9679 | 14.9957 | 15.264 | 508.4118 | 255.1941 | 502.5539 | 2.5029 | 42.9971 | 0.355 | 8.04 | 7.91 | 7.84 | 249 | 288 | 479 | 553.1319 | -15.4764 | 12.9371 | 549.614 | 54.6955 | BMRL | 0.2 | 1.063 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 322.7757 | 328.9625 | 319.8661 | 318.2791 | Alkb, mg/L CaCO3 | 274.6135 | 322.0457 | 252.3066 | 240.1395
[44 empty] | 1998-07-27 | 19:00 | 81.5 | 24 | 45 | 46 | 284 | 6.63 | 0.89 |  | 7.52 | 0.19608 | 0.88165 | 36.766 | 15.1326 | 15.4034 | 509.9479 | 255.9376 | 504.0181 | 2.5105 | 42.9895 | 0.35831 | 8.09 | 7.87 | 7.86 | 259 | 288 | 479 | 487.1348 | -1.6983 | 9.4406 | 484.4719 | 46.5397 | BMRL | 0.199 | 1.116 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 292.4838 | 299.2589 | 290.1515 | 290.3721 | T-Hdb, mg/L CaCO3 | 242.3757 | 294.3184 | 224.4952 | 226.186
[44 empty] | 1998-07-28 | 9:45 | 96.25 | 24 | 45 | 45 | 284 | 6.27 | 0.43 |  | 6.7 | 0.19608 | 0.93582 | 41.3881 | 14.3109 | 14.567 | 535.4187 | 268.8947 | 529.5345 | 2.6358 | 42.3642 | 0.34385 | [66 empty] | Ca-Hdb, mg/L CaCO3 | 260.4108 | 268 | 258.437 | 259.6279 | Ca-Hdb, mg/L CaCO3 | 209.8162 | 268 | 194.6837 | 203.814
[44 empty] | 1998-07-28 | 10:45 | 97.25 | 24 | 45 | 45 | 284 | 6.3 | 0.8 |  | 7.1 | 0.19608 | 0.88732 | 39 | 14.3794 | 14.6367 | 512.2891 | 257.2649 | 506.6319 | 2.522 | 42.478 | 0.34457 | 7.67 | 7.78 | 7.73 | 241 | 278 | 521 | 640.375 | -22.9127 | 15.7343 | 635.9453 | 62.1037 | 0.01 | 0.201 | 2.024 | 1.7273 | 14.6585 | 95.086 | 1.7083 | 99.4146 | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-07-28 | 11:20 | 97.8333 | 24 | 44 | 45 | 284 | 6.6 | 7.6 |  | 14.2 | 0.19608 | 0.46479 | 19 | 15.0641 | 15.3337 | 372.1552 | 186.7909 | 367.8475 | 1.8321 | 42.6679 | 0.35937 | [66 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-07-28 | 11:50 | 98.3333 | 22.3 | 44 | 45 | 284 | 6.67 | 7.27 |  | 13.94 | 0.19608 | 0.47848 | 19.373 | 15.2239 | 16.2949 | 375.5019 | 188.447 | 371.1087 | 1.8486 | 42.6514 | 0.38205 | 7.82 | 7.71 | 7.67 | 195 | 274 | 362 | 369.4897 | -2.069 | 31.8182 | 367.4407 | 46.9302 | BMRL | 0.201 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-07-28 | 13:30 | 100 | 24 | 44 | 45 | 284 | 6.67 | 7.07 |  | 13.74 | 0.19608 | 0.48544 | 19.6696 | 15.2239 | 15.4963 | 377.2202 | 189.3093 | 372.8069 | 1.857 | 42.643 | 0.3634 | 7.63 | 7.57 | 7.66 | 198 | 272 | 338 | 369.0212 | -9.1779 | 30.7692 | 367.0129 | 46.0509 | BMRL | 0.198 | 0.397 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-07-28 | 14:00 | 100.5 | 22.6 | 44 | 45 | 284 | 6.77 | 7.02 |  | 13.79 | 0.19608 | 0.49094 | 19.5946 | 15.4522 | 16.3932 | 378.6084 | 189.9718 | 374.1116 | 1.8639 | 42.6361 | 0.38449 | 7.95 | 7.8 | 7.84 | 209 | 285 | 352 | 360.2578 | -2.346 | 26.9231 | 358.455 | 41.6942 | BMRL | 0.2 | 0.393 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-07-28 | 14:45 | 101.25 | 24 | 44 | 45 | 284 | 6.71 | 6.86 |  | 13.57 | 0.19608 | 0.49447 | 19.9285 | 15.3152 | 15.5893 | 379.4804 | 190.4299 | 375.0137 | 1.8682 | 42.6318 | 0.36567 | 8.05 | 7.86 | 7.81 | 198 | 271 | 344 | 372.0758 | -8.1616 | 30.7692 | 370.0194 | 46.4893 | BMRL | 0.198 | 0.39 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-07-28 | 15:30 | 102 | 24 | 44 | 45 | 284 | 6.67 | 6.48 |  | 13.15 | 0.19608 | 0.50722 | 20.597 | 15.2239 | 15.4963 | 382.6967 | 192.0577 | 378.2194 | 1.884 | 42.616 | 0.36363 | 7.66 | 7.51 | 7.55 | 207 | 280 | 354 | 367.3164 | -3.7617 | 27.6224 | 365.4338 | 43.355 | BMRL | 0.199 | 0.399 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-07-28 | 16:15 | 102.75 | 23.5 | 44 | 45 | 284 | 6.75 | 6.53 |  | 13.28 | 0.19608 | 0.50828 | 20.3855 | 15.4065 | 15.9157 | 382.9858 | 192.1752 | 378.4507 | 1.8854 | 42.6146 | 0.37348 | 7.63 | 7.49 | 7.88 | 199 | 272 | 345 | 375.9311 | -8.9655 | 30.4196 | 373.8285 | 46.767 | BMRL | 0.199 | 0.402 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-07-28 | 17:00 | 103.5 | 24 | 44 | 45 | 284 | 6.75 | 6.6 |  | 13.35 | 0.19608 | 0.50562 | 20.2734 | 15.4065 | 15.6822 | 382.306 | 191.8341 | 377.779 | 1.8821 | 42.6179 | 0.36797 | [66 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-07-29 | 8:20 | 118.8333 | 24 | 44 | 45 | 284 | 6.88 | 6.5 |  | 13.38 | 0.19608 | 0.5142 | 20.2257 | 15.7032 | 15.9842 | 384.5349 | 192.9074 | 379.8927 | 1.8931 | 42.6069 | 0.37516 | 7.57 | 7.52 | 7.58 | 213 | 281 | 350 | 363.2677 | -3.7908 | 25.5245 | 361.4475 | 41.0703 | BMRL | 0.196 | 0.412 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-07-29 | 9:00 | 119.5 | 24 | 44 | 45 | 284 | 6.88 | 6.44 |  | 13.32 | 0.19608 | 0.51652 | 20.3213 | 15.7032 | 15.9842 | 385.1326 | 193.2073 | 380.4832 | 1.896 | 42.604 | 0.37518 | 7.66 | 7.54 | 7.56 | 214 | 286 | 356 | 362.9193 | -1.9436 | 25.1748 | 361.1154 | 40.7392 | BMRL | 0.199 | 0.412 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-07-29 | 9:45 | 120.25 | 24 | 43 | 44 | 284 | 6.67 | 15.6 |  | 22.27 | 0.19608 | 0.29951 | 11.7526 | 15.2239 | 15.4963 | 336.1534 | 168.6998 | 332.2206 | 1.6549 | 41.8451 | 0.37033 | [66 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-07-29 | 10:00 | 120.5 | 24 | 43 | 44 | 284 | 6.78 | 14.93 |  | 21.71 | 0.19608 | 0.3123 | 12.0815 | 15.475 | 15.7519 | 338.7026 | 169.9455 | 334.6738 | 1.6674 | 41.8326 | 0.37655 | 8.16 | 7.95 | 7.91 | 195 | 279 | 315 | 327.3248 | -3.9127 | 31.8182 | 325.7453 | 40.1373 | BMRL | 0.198 | 0.298 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 10:30 | 121 | 24 | 43 | 44 | 284 | 6.75 | 15.2 |  | 21.95 | 0.19608 | 0.30752 | 11.9385 | 15.4065 | 15.6822 | 337.7464 | 169.4749 | 333.7469 | 1.6627 | 41.8373 | 0.37484 | 7.86 | 7.73 | 7.75 | 184 | 272 | 313 | 331.2961 | -5.8454 | 35.6643 | 329.5456 | 44.1655 | BMRL | 0.202 | 0.292 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 11:10 | 121.6667 | 24 | 43 | 44 | 284 | 6.77 | 15.73 |  | 22.5 | 0.19608 | 0.30089 | 11.6222 | 15.4522 | 15.7287 | 336.4365 | 168.8115 | 332.4406 | 1.6563 | 41.8437 | 0.37589 | 8.1 | 7.9 | 7.87 | 191 | 281 | 318 | 326.8868 | -2.7946 | 33.2168 | 325.2672 | 41.279 | BMRL | 0.203 | 0.287 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 12:00 | 122.5 | 24 | 43 | 44 | 284 | 6.67 | 15.6 |  | 22.27 | 0.19608 | 0.29951 | 11.7526 | 15.2239 | 15.4963 | 336.1534 | 168.6998 | 332.2206 | 1.6549 | 41.8451 | 0.37033 | 7.64 | 7.5 | 7.61 | 184 | 270 | 308 | 329.6115 | -7.0167 | 35.6643 | 327.9016 | 43.8856 | BMRL | 0.2 | 0.289 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 13:30 | 124 | 24 | 43 | 44 | 284 | 6.75 | 15.47 |  | 22.22 | 0.19608 | 0.30378 | 11.7813 | 15.4065 | 15.6822 | 337.0054 | 169.1031 | 333.0148 | 1.6591 | 41.8409 | 0.37481 | 7.64 | 7.52 | 7.64 | 195 | 279 | 320 | 325.7059 | -1.7831 | 31.8182 | 324.1526 | 39.8431 | BMRL | 0.2 | 0.292 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 14:30 | 125 | 24 | 43 | 44 | 284 | 6.59 | 15.33 |  | 21.92 | 0.19608 | 0.30064 | 11.9562 | 15.0413 | 15.3105 | 336.3679 | 168.8317 | 332.4803 | 1.6559 | 41.8441 | 0.36589 | 7.77 | 7.69 | 7.77 | 200 | 284 | 320 | 322.9693 | -0.92792 | 30.0699 | 321.5426 | 37.7999 | BMRL | 0.198 | 0.289 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 15:15 | 125.75 | 24 | 43 | 44 | 284 | 6.2 | 15.07 |  | 21.27 | 0.19608 | 0.29149 | 12.3521 | 14.1512 | 14.4044 | 334.5348 | 168.0291 | 330.8998 | 1.6469 | 41.8531 | 0.34417 | 7.79 | 7.69 | 7.8 | 201 | 278 | 319 | 320.9701 | -0.6176 | 29.7203 | 319.6606 | 37.1208 | BMRL | 0.199 | 0.289 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 16:15 | 126.75 | 24 | 43 | 44 | 284 | 6.77 | 15.13 |  | 21.9 | 0.19608 | 0.30913 | 11.968 | 15.4522 | 15.7287 | 338.0699 | 169.6311 | 334.0546 | 1.6643 | 41.8357 | 0.37596 | 7.65 | 7.56 | 7.79 | 190 | 272 | 313 | 328.9557 | -5.0977 | 33.5664 | 327.2995 | 41.9492 | BMRL | 0.199 | 0.292 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-07-29 | 17:00 | 127.5 | 24 | 43 | 44 | 284 | 6.73 | 14.88 |  | 21.61 | 0.19608 | 0.31143 | 12.1421 | 15.3609 | 15.6357 | 338.5234 | 169.8709 | 334.5269 | 1.6665 | 41.8335 | 0.37376
[44 empty] | 1998-07-30 | 8:00 | 142.5 | 24 | 43 | 44 | 284 | 6.73 | 14.88 | X | 21.61 | 0.19608 | 0.31143 | 12.1421 | 15.3609 | 15.6357 | 338.5234 | 169.8709 | 334.5269 | 1.6665 | 41.8335 | 0.37376
[44 empty] | 1998-07-30 | 13:30 |  | 24 | 36 | 36 | 284 | 7.04 | 3.88 |  | 10.92 | 0.19608 | 0.64469 | 25.0073 | 16.0684 | 16.3559 | 421.4339 | 211.3575 | 416.2264 | 2.0747 | 33.9253 | 0.48212
[44 empty] | 1998-07-30 | 14:00 |  | 24 | 64 | 66 | 284 | 12.32 | 8.36 |  | 20.68 | 0.19608 | 0.59574 | 12.7331 | 28.1197 | 28.6229 | 408.4743 | 202.8924 | 399.5561 | 2.0112 | 62.9888 | 0.45441
[44 empty] | 1998-07-30 | 14:20 |  | 24 | 50 | 51 | 284 | 9.93 | 6.27 |  | 16.2 | 0.19608 | 0.61296 | 16.5309 | 22.6647 | 23.0702 | 412.7921 | 205.9409 | 405.5596 | 2.0323 | 48.4677 | 0.47599
[44 empty] | 1998-07-30 | 14:45 |  | 24 | 45 | 46 | 284 | 8.36 | 5.2 |  | 13.56 | 0.19608 | 0.61652 | 19.944 | 19.0813 | 19.4227 | 413.33 | 206.7995 | 407.2504 | 2.0349 | 43.4651 | 0.44686
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X11: C. Rice: Alkalinity values verified by consultant.
Note on X13: C. Rice: Total hardness values verified by consultant.
Note on X14: C. Rice: Calcium hardness values verified by consultant.
Note on X27: C. Rice: Feed TOX concentrations verified by consultant.
Note on X32: C. Rice: Feed THM values verified by consultant.
Note on X42: C. Rice: Feed HAA values verified by consultant.
Note on X43: C. Rice: Feed HAA values verified by consultant.
Note on CY16: C. Rice: Alkalinity values verified by consultant due to consistently high mass balance closure errors.
Note on CY18: C. Rice: Total hardness values verified by consultant due to consistently high mass balance closure errors.
Note on CY19: C. Rice: Calcium hardness values verified by consultant due to consistently high mass balance closure errors.
Note on DQ10: C. Rice 7/12/99: Consultant verified all TDS, alkalinity, total hardness and calcium hardness values due to consistently high mass balance errors.
Note on EA10: C. Rice 7/12/99: Consultant verified all TDS, alkalinity, total hardness and calcium hardness values due to consistently high mass balance errors.
Note on EK10: C. Rice 7/12/99: Consultant verified all TDS, alkalinity, total hardness and calcium hardness values due to consistently high mass balance errors.

## SR40. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Manufacturer Reported Membrane Characteristics1 |  | Field 3-3: RBSMT Design Parameters | [8 empty] | Field 3-4: Foulants And Fouling Indices1 | Field 3-5: Pretreatment Used Prior To Membranes1 |  |  | Field 3-6: Feed Water Quality After Pretreatment | [5 empty] | Field 3-7: Membrane Setting Data | [20 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 3-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 3-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 3-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 3-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 3-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 3-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 3-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 3-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.48998 | [45 empty] | Recovery during sample collection (decimal) | 0.67 | [10 empty] | Recovery during sample collection (decimal) | 0.85 | [7 empty] | Recovery during sample collection (decimal) | 0.51 | [7 empty] | Recovery during sample collection (decimal) | 0.32 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1998-12-05 | 1998-12-19 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 7.04 | [10 empty] | Feed flow rate during sample collection (mL/min) | 4.88 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.53 | [7 empty] | Feed flow rate during sample collection (mL/min) | 16.27 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 12:00 | 13:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 272 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [7 empty] | Influent flow rate during sample collection (mL/min) | 272 | [6 empty] | SDS-THM4F, ug/L | 235.75 | 235.75 | 235.75 | 235.75 | SDS-THM4F, ug/L | 235.75 | 235.75 | 235.75 | 235.75 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 17.7 | 33 | 22.6 | 12.9 | SDS-THM4p, ug/L | 17.7 | 33 | 22.6 | 12.9 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 7.23 | 7.91 | 7.57 | 8.9828 | 1998-11-30 | 8:45 | 0 | 23 | 83 | 83 | 263 | 11.7 | NA | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 26.7046 | 27.9979 | #VALUE! | #VALUE! | #VALUE! | 0 | 83 | 0.33732 | 1998-12-01 | 9:10 | 0 | 23 | 36 | 34 | 272 | 5.2 | 2.49 |  | 7.69 | 0.18779 | 0.6762 | 34.3706 | 11.8687 | 12.4435 | 499.6931 | 252.4402 | 494.9662 | 2.4489 | 32.5511 | 0.38228 | 8.31 | 7.36 | 7.97 | 21 | 332 | 65 | 983.0221 | -1412.3417 | 93.6842 | 973.8263 | 97.8436 | BMRL | 0.204 | 0.039 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 66.3 | 66.3 | 66.3 | 66.3 | SDS-HAA5F, ug/L | 66.3 | 66.3 | 66.3 | 66.3 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 23 | 23 | 23 | 0 | 1998-11-30 | 9:45 | 1 | 23 | 62 | 60 | 272 | 9.2 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 20.9985 | 22.0155 | #VALUE! | #VALUE! | #VALUE! | 0 | 61 | 0.36091 | 1998-12-01 | 10:10 | 1 | 23 | 36 | 34 | 272 | 4.89 | 2.35 |  | 7.24 | 0.18779 | 0.67541 | 36.5691 | 11.1612 | 11.7017 | 499.2532 | 252.363 | 494.8146 | 2.4467 | 32.5533 | 0.35946 | 7.72 | 7.41 | 7.5 | 183 | 336 | 352 | 643.5872 | -82.8373 | 44.9624 | 639.447 | 71.3815 | BMRL | 0.193 | 0.26 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 1.85 | 4.3 | 1.8 | 1.2 | SDS-HAA5p, ug/L | 1.85 | 4.3 | 1.8 | 1.2 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 448 | 438 | 443 | 2.2573 | 1998-11-30 | 10:00 | 1.25 | 23 | 48 | 46 | 272 | 6.9 | 12.5 | 19.4 | 0.18779 | 0.35567 | 13.0206 | 15.7489 | 16.5116 | 0 | 0 | 0 | 0 | 47 | 0.35131 | 1998-12-01 | 11:10 | 2 | 23 | 36 | 34 | 272 | 4.8 | 2.4 |  | 7.2 | 0.18779 | 0.66667 | 36.7778 | 10.9557 | 11.4863 | 495.9898 | 250.7551 | 491.6621 | 2.4307 | 32.5693 | 0.35267 | 7.65 | 7.43 | 7.57 | 229 | 338 | 438 | 539.5 | -23.1735 | 31.1278 | 536.7603 | 57.3366 | BMRL | 0.202 | 0.398 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1998-12-02 | 1998-12-03 | --- | --- | 1998-12-02 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-04 | 1998-12-04 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-06 | 1998-12-06 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1998-12-07 | 1998-12-07 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 660 | 660 | 660 | 660 | SDS-TOXF, ug Cl- /L | 660 | 660 | 660 | 660 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 331 | 334 | 332.5 | 0.90226 | 1998-11-30 | 10:30 | 1.75 | 23 | 44 | 42 | 272 | 6.6 | 11.8 | 18.4 | 0.18779 | 0.3587 | 13.7826 | 15.0641 | 15.7937 | 0 | 0 | 0 | 0 | 43 | 0.3673 | 1998-12-01 | 12:10 | 3 | 23 | 36 | 34 | 272 | 4.95 | 2.67 |  | 7.62 | 0.18779 | 0.64961 | 34.6955 | 11.2981 | 11.8453 | 489.8922 | 247.6036 | 485.4829 | 2.4008 | 32.5992 | 0.36336 | 7.76 | 7.43 | 7.59 | 243 | 335 | 458 | 498.427 | -8.8268 | 26.9173 | 496.1028 | 51.0182 | BMRL | 0.203 | 0.506 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 9:15 | 9:15 | --- | --- | 9:15 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 18:00 | 18:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 13:00 | 13:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 12:00 | 12:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | 26 | 37 | 32 | 26 | SDS-TOXp, ug Cl- /L | 26 | 37 | 32 | 26 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 272 | 300 | 286 | 9.7902 | 1998-11-30 | 11:40 | 2.9167 | 23 | 44 | 42 | 272 | 6.5 | 11.6 | 18.1 | 0.18779 | 0.35912 | 14.0276 | 14.8359 | 15.5544 | 0 | 0 | 0 | 0 | 43 | 0.36173 | 1998-12-01 | 13:10 | 4 | 23 | 36 | 34 | 272 | 4.71 | 2.42 |  | 7.13 | 0.18779 | 0.66059 | 37.1487 | 10.7503 | 11.271 | 493.7356 | 249.6571 | 489.5091 | 2.4197 | 32.5803 | 0.34594 | 7.62 | 7.42 | 7.48 | 244 | 335 | 462 | 504.7459 | -9.2524 | 26.6165 | 502.4883 | 51.4417 | BMRL | 0.192 | 0.533 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 24.08 | 48.08 | --- | --- | 24.08 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80.83 | 80.83 | --- | --- | --- | --- | --- | Operation time | hh.hh | 123.83 | 123.83 | --- | --- | --- | --- | --- | Cumulative time | hr | 146.83 | 146.83 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 5.595 | 5.595 | 5.595 | 5.595 | SDS-CDF, mg/L | 5.595 | 5.595 | 5.595 | 5.595 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 260 | 260 | 260 | 0 | 1998-11-30 | 12:30 | 3.75 | 23 | 46 | 44 | 272 | 6.8 | 2.7 | 9.5 | 0.18779 | 0.71579 | 27.6316 | 15.5206 | 16.2723 | 0 | 0 | 0 | 0 | 45 | 0.36161 | 1998-12-01 | 14:10 | 5 | 23 | 36 | 34 | 272 | 4.67 | 2.38 |  | 7.05 | 0.18779 | 0.66241 | 37.5816 | 10.659 | 11.1752 | 494.3788 | 250.0008 | 490.183 | 2.4228 | 32.5772 | 0.34304 | 7.58 | 7.46 | 7.53 | 244 | 336 | 468 | 506.1534 | -8.1524 | 26.6165 | 503.9029 | 51.578 | BMRL | 0.204 | 0.556 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 7.62 | 8.1 | 7.86 | 6.1069 | 7.76 | --- | --- | --- | --- | --- | pH | --- | 7.92 | 7.92 | --- | --- | --- | --- | --- | pH | --- | 7.81 | 7.92 | --- | --- | --- | --- | --- | pH | --- | 7.78 | 7.78 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 1.235 | 0.62 | 0.52 | 0.31 | SDS-CDp, mg/L | 1.235 | 0.62 | 0.52 | 0.31 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 15.1667 | 78.41 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.3 | 0.25 | 0.275 | 18.1818 | 1998-11-30 | 13:40 | 4.9167 | 23 | 46 | 44 | 272 | 6.5 | 2.5 | 9 | 0.18779 | 0.72222 | 29.2222 | 14.8359 | 15.5544 | 0 | 0 | 0 | 0 | 45 | 0.34565 | 1998-12-01 | 15:10 | 6 | 23 | 36 | 34 | 272 | 4.64 | 2.33 |  | 6.97 | 0.18779 | 0.66571 | 38.0244 | 10.5906 | 11.1035 | 495.5665 | 250.6153 | 491.3879 | 2.4286 | 32.5714 | 0.3409 | 7.73 | 7.55 | 7.61 | 246 | 327 | 469 | 504.7575 | -7.6242 | 26.015 | 502.5505 | 51.0497 | BMRL | 0.187 | 0.521 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 23 | 23 | 23 | 0 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | Temperature | oC | 23 | 23 | --- | --- | --- | --- | --- | TOCF, mg/L | 6.75 | 6.75 | 6.75 | 6.75 | TOCF, mg/L | 6.75 | 6.75 | 6.75 | 6.75 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 38.5 | 101.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1998-11-30 | 14:40 | 5.9167 | 23 | 46 | 44 | 272 | 6.8 | 2.45 | 9.25 | 0.18779 | 0.73514 | 28.4054 | 15.5206 | 16.2723 | 0 | 0 | 0 | 0 | 45 | 0.36161 | 1998-12-01 | 16:10 | 7 | 23 | 36 | 34 | 272 | 4.6 | 2.36 |  | 6.96 | 0.18779 | 0.66092 | 38.0805 | 10.4993 | 11.0077 | 493.8056 | 249.7432 | 489.678 | 2.42 | 32.58 | 0.33787 | 7.71 | 7.54 | 7.6 | 247 | 336 | 464 | 499.1525 | -7.576 | 25.7143 | 497.0204 | 50.3038 | BMRL | 0.202 | 0.554 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 182 | 196 | 189 | 7.4074 | 610 | 958.697 | -57.1634 | 57.3363 | 952.0232 | 80.1475 | Alkalinity | mg/L as CaCO3 | 242 | 696 | 1582 | -127.2989 | 45.3725 | 1571.7825 | 84.6035 | Alkalinity | mg/L as CaCO3 | 180 | 562 | 716.7347 | -27.5329 | 59.3679 | 712.0929 | 74.7224 | Alkalinity | mg/L as CaCO3 | 168 | 530 | 572.4118 | -8.0022 | 62.0767 | 568.5413 | 70.4507 | TOCp, mg/L | #DIV/0! | 0.5 | BMRL | BMRL | TOCp, mg/L | #DIV/0! | 0.5 | BMRL | BMRL | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 73.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 6.4 | 7.1 | 6.75 | 10.3704 | 1998-11-30 | 15:40 | 6.9167 | 23 | 46 | 44 | 272 | 6.8 | 2.4 | 9.2 | 0.18779 | 0.73913 | 28.5652 | 15.5206 | 16.2723 | 0 | 0 | 0 | 0 | 45 | 0.36161 | 1998-12-01 | 16:30 | 7.3333 | 23 | 36 | 34 | 272 | 4.56 | 2.36 |  | 6.92 | 0.18779 | 0.65896 | 38.3064 | 10.408 | 10.912 | 493.0781 | 249.3938 | 488.9928 | 2.4164 | 32.5836 | 0.33489 | 7.77 | 7.55 | 7.56 | 245 | 335 | 464 | 501.5678 | -8.0965 | 26.3158 | 499.4172 | 50.9428 | BMRL | 0.202 | 0.57 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 250 | 248 | 249 | 0.80321 | 476 | 502.0303 | -5.4686 | 25.1128 | 499.8364 | 50.1837 | Total dissolved solids | mg/L | 299 | 665 | 522.3333 | 21.4536 | 10.0752 | 520.6304 | 42.5696 | Total dissolved solids | mg/L | 260 | 380 | 407.9592 | -7.3577 | 21.8045 | 406.6796 | 36.0676 | Total dissolved solids | mg/L | 229 | 370 | 381.2059 | -3.0286 | 31.1278 | 379.7492 | 39.697 | UV254 F, cm-1 | 0.201 | 0.201 | 0.201 | 0.201 | UV254 F, cm-1 | 0.201 | 0.201 | 0.201 | 0.201 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 8.5 | 71.7434 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.201 | 0.201 | 0.201 | 0 | 1998-11-30 | 16:05 | 7.3333 | 23 | 56 | 54 | 272 | 8.8 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 20.0855 | 21.0583 | #VALUE! | #VALUE! | #VALUE! | 0 | 55 | 0.38288 | 1998-12-02 | 9:15 | 24.0833 | 22 | 36 | 34 | 272 | 4.76 | 2.4 |  | 7.16 | 0.18779 | 0.6648 | 36.9888 | 10.8644 | 11.7323 | 495.2911 | 250.4204 | 491.0059 | 2.4273 | 32.5727 | 0.36019 | 6.94 | 7.04 | 7.1 | 244 | 334 | 462 | 508.025 | -9.9621 | 26.6165 | 505.7148 | 51.7515 | BMRL | 0.198 | 0.563 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 198 | 152 | 175 | 26.2857 | 363 | 511.3636 | -40.8715 | 38.8112 | 508.4472 | 65.5815 | Total hardness | mg/L as CaCO3 | 230 | 524 | 603.3333 | -15.1399 | 19.5804 | 600.4867 | 61.6977 | Total hardness | mg/L as CaCO3 | 160 | 380 | 417.1429 | -9.7744 | 44.0559 | 414.919 | 61.4383 | Total hardness | mg/L as CaCO3 | 162 | 336 | 344.3529 | -2.486 | 43.3566 | 342.6077 | 52.7156 | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | BMRL | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 3.1406 | 2.831 | 2.9858 | 10.3704 | 1998-11-30 | 16:30 | 7.75 | 23 | 66 | 66 | 272 | 10.6 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 24.1939 | 25.3657 | #VALUE! | #VALUE! | #VALUE! | 0 | 66 | 0.38433 | 1998-12-02 | 10:30 | 25.3333 | 23 | 36 | 34 | 272 | 4.68 | 2.38 |  | 7.06 | 0.18779 | 0.66289 | 37.5269 | 10.6818 | 11.1992 | 494.5571 | 250.0863 | 490.3508 | 2.4237 | 32.5763 | 0.34378 | 7.46 | 7.35 | 7.55 | 250 | 337 | 470 | 494.7269 | -5.261 | 24.812 | 492.6215 | 49.2511 | BMRL | 0.204 | 0.572 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 175 | 74 | 124.5 | 81.1245 | 404 | 535.1061 | -32.452 | 52.1154 | 531.5459 | 76.5778 | Calcium hardness | mg/L as CaCO3 | 220 | 500 | 486.6667 | 2.6667 | 15.3846 | 484.6333 | 54.6049 | Calcium hardness | mg/L as CaCO3 | 154 | 342 | 370.3265 | -8.2826 | 40.7692 | 368.4557 | 58.2039 | Calcium hardness | mg/L as CaCO3 | 140 | 302 | 316.4706 | -4.7916 | 46.1538 | 314.7817 | 55.5247 | BromideF, ug/L | 190 | 190 | 190 | 190 | BromideF, ug/L | 190 | 190 | 190 | 190 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 190 | 190 | 190 | 0 | 1998-11-30 | 16:55 | 8.1667 | 23 | 34 | 32 | 254 | 5.2 | NA | #VALUE! | 0.17537 | #VALUE! | #VALUE! | 11.8687 | 12.4435 | #VALUE! | #VALUE! | #VALUE! | 0 | 33 | 0.37708 | 1998-12-02 | 11:30 | 26.3333 | 23 | 36 | 34 | 272 | 4.68 | 2.37 |  | 7.05 | 0.18779 | 0.66383 | 37.5816 | 10.6818 | 11.1992 | 494.8993 | 250.2593 | 490.69 | 2.4254 | 32.5746 | 0.3438 | 7.51 | 7.49 |  | 249 | 337 | 469 | 497.3861 | -6.0525 | 25.1128 | 495.2492 | 49.7223 | BMRL | 0.198 | 0.582 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.2 | 0.21 | 0.205 | 4.878 | 0.359 | 0.41712 | -16.1898 | 25.4545 | 0.41528 | 50.636 | Turbidity | ntu | 0.261 | 0.674 | 0.35433 | 47.4283 | 5.0909 | 0.35362 | 26.1923 | Turbidity | ntu | 0.227 | 0.29 | 0.32496 | -12.0549 | 17.4545 | 0.32411 | 29.9625 | Turbidity | ntu | 0.17 | 0.24 | 0.32441 | -35.1716 | 38.1818 | 0.32293 | 47.3577 | Bromidep, ug/L | 170 | 190 | 170 | 160 | Bromidep, ug/L | 170 | 190 | 170 | 160 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 6.5 | 6.5 | 6.5 | 0 | 1998-11-30 | 17:20 | 8.5833 | 23 | 51 | 50 | 263 | 8.08 | NA | #VALUE! | 0.18158 | #VALUE! | #VALUE! | 18.4422 | 19.3353 | #VALUE! | #VALUE! | #VALUE! | 0 | 50.5 | 0.38288 | 1998-12-02 | 12:30 | 27.3333 | 23 | 36 | 34 | 272 | 4.68 | 2.36 |  | 7.04 | 0.18779 | 0.66477 | 37.6364 | 10.6818 | 11.1992 | 495.2429 | 250.4331 | 491.0307 | 2.427 | 32.573 | 0.34382 | 7.54 | 7.41 | 7.53 | 250 | 338 | 473 | 496.1017 | -4.8841 | 24.812 | 493.9845 | 49.3911 | BMRL | 0.202 | 0.59 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | BMRL | NA | #VALUE! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 443 | 443 | 443 | 443 | AlkF, mg/L CaCO3 | 443 | 443 | 443 | 443
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.75 | 1.06 | 0.905 | 34.2541 | 1998-11-30 | 17:40 | 8.9167 | 23 | 35 | 33 | 263 | 5.3 | 1.27 | 6.57 | 0.18158 | 0.8067 | 39.0304 | 12.097 | 12.6828 | 0 | 0 | 0 | 0 | 34 | 0.37302 | 1998-12-02 | 13:30 | 28.3333 | 23 | 36 | 34 | 272 | 4.67 | 2.36 |  | 7.03 | 0.18779 | 0.6643 | 37.6913 | 10.659 | 11.1752 | 495.0645 | 250.3475 | 490.8629 | 2.4262 | 32.5738 | 0.34307 | 7.57 | 7.45 | 7.73 | 251 | 337 | 475 | 493.7733 | -3.9523 | 24.5113 | 491.6892 | 48.9515 | BMRL | 0.2 | 0.589 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 16.6 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | 0.5 | 65 | 42.1667 | 35.1282 | 92.5926 | 41.849 | 98.8052 | Total organic carbon | mg/L | BMRL | 11.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 8.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 189 | 242 | 180 | 168 | Alkp, mg/L CaCO3 | 189 | 242 | 180 | 168
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 5.75 | 5.44 | 5.595 | 5.5407 | 1998-12-01 | 9:10 | 24.4167 | 23 | 36 | 34 | 272 | 5.2 | 2.49 | 7.69 | 0.18779 | 0.6762 | 34.3706 | 11.8687 | 12.4435 | 0 | 0 | 0 | 0 | 35 | 0.35553 | 1998-12-02 | 14:30 | 29.3333 | 23 | 36 | 34 | 272 | 4.68 | 2.34 |  | 7.02 | 0.18779 | 0.66667 | 37.7464 | 10.6818 | 11.1992 | 495.9344 | 250.7828 | 491.7164 | 2.4304 | 32.5696 | 0.34385 | 7.57 | 7.5 | 7.65 | 250 | 337 | 471 | 497.5 | -5.6263 | 24.812 | 495.3708 | 49.5328 | BMRL | 0.202 | 0.594 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.595 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | BMRL | 2.108 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.411 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.3 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 286 | 286 | 286 | 286 | T-HdF, mg/L CaCO3 | 286 | 286 | 286 | 286
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 15:30 | 30.3333 | 23 | 36 | 33 | 272 | 4.68 | 2.3 |  | 6.98 | 0.18779 | 0.67049 | 37.9685 | 10.6818 | 11.1992 | 497.3353 | 251.4912 | 493.1053 | 2.4373 | 32.0627 | 0.34929 | 7.6 | 7.46 | 7.5 | 225 | 337 | 469 | 551.2391 | -17.535 | 32.3308 | 548.4325 | 58.974 | BMRL | 0.207 | 0.596 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.5843 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.2431 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.5128 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.6145 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 175 | 230 | 160 | 162 | T-Hdp, mg/L CaCO3 | 175 | 230 | 160 | 162
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 8.74 | 8.58 | 8.66 | 1.8476 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 16:30 | 31.3333 | 23 | 36 | 33 | 272 | 4.68 | 2.33 |  | 7.01 | 0.18779 | 0.66762 | 37.8017 | 10.6818 | 11.1992 | 496.2824 | 250.9588 | 492.0614 | 2.4321 | 32.0679 | 0.34923 |  |  |  | 251 | 337 | 467 | 496.1996 | -6.2526 | 24.5113 | 494.0901 | 49.1996 | BMRL |  | 0.577 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 170 | 170 | 170 | 0 | --- | 230.6061 | --- | 10.5263 | 230.0806 | 26.1128 | Bromide | mg/L | 190 | --- | 190 | --- | 0 | 190 | 0 | Bromide | mg/L | 170 | --- | 210.8163 | --- | 10.5263 | 210.4633 | 19.2258 | Bromide | mg/L | 160 | --- | 204.1176 | --- | 15.7895 | 203.6954 | 21.4513 | Ca-HdF, mg/L CaCO3 | 260 | 260 | 260 | 260 | Ca-HdF, mg/L CaCO3 | 260 | 260 | 260 | 260
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 17:30 | 32.3333 | 23 | 36 | 33 | 272 | 4.68 | 2.33 |  | 7.01 | 0.18779 | 0.66762 | 37.8017 | 10.6818 | 11.1992 | 496.2824 | 250.9588 | 492.0614 | 2.4321 | 32.0679 | 0.34923 |  |  |  | 249 | 337 | 465 | 500.2167 | -7.5735 | 25.1128 | 498.0555 | 50.0056 | BMRL | 0.201 | 0.599 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 2 | 2 | 2 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.75 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 1.75 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 124.5 | 220 | 154 | 140 | Ca-Hdp, mg/L CaCO3 | 124.5 | 220 | 154 | 140
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 700 | 620 | 660 | 12.1212 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-02 | 18:30 | 33.3333 | 23 | 36 | 33 | 272 | 4.7 | 2.34 |  | 7.04 | 0.18779 | 0.66761 | 37.6364 | 10.7275 | 11.247 | 496.2902 | 250.9534 | 492.0509 | 2.4322 | 32.0678 | 0.35073 | 7.8 | 7.66 | 7.62 | 270 | 337 | 470 | 458.0342 | 2.5459 | 18.797 | 456.4096 | 40.8426 | BMRL | 0.192 | 0.599 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 0.68 | 0.85 | 0.765 | 22.2222 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.13 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.23 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.44 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 160 | 130 | 145 | 20.6897 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 8:45 | 47.5833 | 23 | 36 | 33 | 272 | 4.72 | 2.31 |  | 7.03 | 0.18779 | 0.67141 | 37.6913 | 10.7731 | 11.2949 | 497.693 | 251.6534 | 493.4235 | 2.439 | 32.061 | 0.35229 | 7.11 | 7.24 | 7.25 | 249 | 334 | 446 | 503.1147 | -12.806 | 25.1128 | 500.9099 | 50.2905 | BMRL | 0.206 | 0.572 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 1.32 | 1.15 | 1.235 | 13.7652 | --- | 14.4471 | --- | 77.9267 | 14.3326 | 91.3833 | SDS-Cl2 demand | mg/L | 0.62 | --- | 33.7867 | --- | 88.9187 | 33.5338 | 98.1511 | SDS-Cl2 demand | mg/L | 0.52 | --- | 10.8771 | --- | 90.706 | 10.7876 | 95.1796 | SDS-Cl2 demand | mg/L | 0.31 | --- | 8.0821 | --- | 94.4593 | 8.0077 | 96.1287 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 67 | 64 | 65.5 | 4.5802 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 9:50 | 48.6667 | 23 | 36 | 34 | 272 | 4.76 | 2.31 |  | 7.07 | 0.18779 | 0.67327 | 37.4724 | 10.8644 | 11.3906 | 498.3974 | 251.991 | 494.0853 | 2.4425 | 32.5575 | 0.34986 | 7.37 | 7.39 | 7.58 | 249 | 335 | 456 | 504.5606 | -10.6493 | 25.1128 | 502.3245 | 50.4304 | BMRL | 0.209 | 0.597 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 25 | 25 | 25 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 25 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 75.0975 | 80.7645 | 76.8238 | 73.4799 | Qp/QT (THM4), % | 91.6074 | 98.5203 | 93.7133 | 89.6343
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 24 | 23 | 23.5 | 4.2553 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 10:45 | 49.5833 | 23 | 36 | 34 | 272 | 4.72 | 2.322 |  | 7.042 | 0.18779 | 0.67026 | 37.6254 | 10.7731 | 11.2949 | 497.272 | 251.4406 | 493.0061 | 2.437 | 32.563 | 0.34686 | 7.24 | 7.23 | 7.42 | 253 | 335 | 463 | 494.1021 | -6.7175 | 23.9098 | 492.0102 | 48.5783 | BMRL | 0.195 | 0.604 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 8.56 | 8.51 | 8.535 | 0.58582 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.6 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9.3 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 8.95 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | 1.8 | 1.7 | 1.75 | 5.7143 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 11:45 | 50.5833 | 23 | 36 | 33 | 272 | 4.76 | 2.33 |  | 7.09 | 0.18779 | 0.67137 | 37.3639 | 10.8644 | 11.3906 | 497.6969 | 251.6368 | 493.3908 | 2.4391 | 32.0609 | 0.35528 | 7.22 | 7.29 | 7.39 | 253 | 333 | 460 | 494.912 | -7.5896 | 23.9098 | 492.7953 | 48.6602 | BMRL | 0.199 | 0.592 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 17.8997 | 16.226 | 16.7486 | 18.4646 | SDS-HAA5b, ug/L | 7.259 | 5.2174 | 5.8549 | 7.9481
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 252.8 | 218.7 | 235.75 | 14.4645 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 13:45 | 52.5833 | 23 | 36 | 33 | 272 | 4.76 | 2.28 |  | 7.04 | 0.18779 | 0.67614 | 37.6364 | 10.8644 | 11.3906 | 499.4593 | 252.5279 | 495.138 | 2.4477 | 32.0523 | 0.35538 | 7.24 | 7.25 | 7.64 | 253 | 334 | 466 | 498.4737 | -6.9686 | 23.9098 | 496.3258 | 49.0254 | BMRL | 0.198 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | 25 | 27 | 26 | 7.6923 | --- | 1947.2121 | --- | 96.0606 | 1930.5541 | 98.6532 | SDS-TOX | mg Cl- /L | 37 | --- | 4190.3333 | --- | 94.3939 | 4158.6642 | 99.1103 | SDS-TOX | mg Cl- /L | 32 | --- | 1313.6327 | --- | 95.1515 | 1302.5488 | 97.5433 | SDS-TOX | mg Cl- /L | 26 | --- | 958.3529 | --- | 96.0606 | 949.4298 | 97.2615 | SDS-TOXb, ug Cl- /L | 183.8821 | 156.8372 | 177.5463 | 194.1373 | SDS-TOXb, ug Cl- /L | 79.2089 | 46.2182 | 71.4802 | 91.7186
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | 3.6 | 4 | 3.8 | 10.5263 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 14:45 | 53.5833 | 23 | 36 | 33 | 272 | 4.76 | 2.27 |  | 7.03 | 0.18779 | 0.6771 | 37.6913 | 10.8644 | 11.3906 | 499.8163 | 252.7084 | 495.4919 | 2.4495 | 32.0505 | 0.3554 | 7.27 | 7.25 | 7.44 | 250 | 332 | 465 | 505.4956 | -8.7087 | 24.812 | 503.26 | 50.3239 | BMRL | 0.193 | 0.615 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CHCl3 | mg/L | 1.5 | --- | 958.1667 | --- | 98.9655 | 950.8721 | 99.8423 | SDS-CHCl3 | mg/L | 1.2 | --- | 294.6694 | --- | 99.1724 | 292.1314 | 99.5892 | SDS-CHCl3 | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDb, mg/L | 2.3208 | 1.577 | 1.6962 | 1.7116 | SDS-CDb, mg/L | 1.6009 | 0.69361 | 0.83905 | 0.85783
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 33 | 33 | 33 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 15:45 | 54.5833 | 24 | 36 | 33 | 272 | 4.68 | 2.27 |  | 6.95 | 0.18779 | 0.67338 | 38.1367 | 10.6818 | 10.873 | 498.4018 | 252.0305 | 494.1628 | 2.4425 | 32.0575 | 0.33917 | 7.35 | 7.3 | 7.39 | 257 | 336 | 477 | 488.1564 | -2.3389 | 22.7068 | 486.1678 | 47.1376 | BMRL | 0.189 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 1.5 | 1.8 | 1.65 | 18.1818 | --- | 195.1348 | --- | 97.4809 | 193.4572 | 99.1471 | SDS-BDCM | mg/L | 3.5 | --- | 416.8333 | --- | 94.6565 | 413.6817 | 99.1539 | SDS-BDCM | mg/L | 2.4 | --- | 131.1755 | --- | 96.3359 | 130.0618 | 98.1547 | SDS-BDCM | mg/L | 1.6 | --- | 95.5706 | --- | 97.5573 | 94.6712 | 98.3099 | TOCb, mg/L | #DIV/0! | 1.7022 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 0.59248 | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 21 | 29 | 25 | 32 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-03 | 16:45 | 55.5833 | 24 | 36 | 33 | 272 | 4.68 | 2.27 |  | 6.95 | 0.18779 | 0.67338 | 38.1367 | 10.6818 | 10.873 | 498.4018 | 252.0305 | 494.1628 | 2.4425 | 32.0575 | 0.33917 | 7.35 | 7.29 | 7.4 | 254 | 335 | 464 | 494.3414 | -6.5391 | 23.609 | 492.2738 | 48.4027 | BMRL | 0.208 | 0.612 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 5.2 | 5.9 | 5.55 | 12.6126 | --- | 59.9439 | --- | 76.383 | 59.4723 | 90.6679 | SDS-DBCM | mg/L | 10 | --- | 100 | --- | 57.4468 | 99.3137 | 89.9309 | SDS-DBCM | mg/L | 7 | --- | 40.6735 | --- | 70.2128 | 40.3823 | 82.6657 | SDS-DBCM | mg/L | 4.5 | --- | 32.4412 | --- | 80.8511 | 32.1738 | 86.0134 | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 8:45 | 71.5833 | 23 | 36 | 33 | 272 | 4.72 | 2.18 |  | 6.9 | 0.18779 | 0.68406 | 38.4203 | 10.7731 | 11.2949 | 502.3956 | 254.0313 | 498.0857 | 2.4621 | 32.0379 | 0.35255 | 7.64 | 7.49 | 7.49 | 251 | 335 | 467 | 508.9587 | -8.9847 | 24.5113 | 506.7205 | 50.4658 | BMRL | 0.21 | 0.623 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 11 | 10 | 10.5 | 9.5238 | --- | -16.0152 | --- | -500 | -15.7852 | 166.5178 | SDS-CHBr3 | mg/L | 18 | --- | -90.3333 | --- | -928.5714 | -89.5073 | 120.1101 | SDS-CHBr3 | mg/L | 12 | --- | -8.9184 | --- | -585.7143 | -8.7375 | 237.3397 | SDS-CHBr3 | mg/L | 6.8 | --- | -0.62647 | --- | -288.5714 | -0.55539 | 1324.3541 | Bromideb, ug/L | 174.9805 | 190 | 174.6352 | 167.956 | Bromideb, ug/L | 171.6785 | 190 | 171.2573 | 163.1097
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 4.6 | 4.4 | 4.5 | 4.4444 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 10:15 | 73.0833 | 23 | 36 | 33 | 272 | 4.68 | 2.18 |  | 6.86 | 0.18779 | 0.68222 | 38.6501 | 10.6818 | 11.1992 | 501.6859 | 253.6912 | 497.4189 | 2.4586 | 32.0414 | 0.34952 | 7.17 | 7.11 | 7.28 | 257 | 336 | 472 | 494.5826 | -4.7844 | 22.7068 | 492.5387 | 47.8214 | BMRL | 0.209 | 0.66 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 17.7 | 17.7 | 17.7 | 0 | --- | 678.4576 | --- | 92.492 | 672.7284 | 97.3689 | SDS-THM4 | mg/L | 33 | --- | 1384.6667 | --- | 86.0021 | 1374.3602 | 97.5989 | SDS-THM4 | mg/L | 22.6 | --- | 457.6 | --- | 90.4136 | 453.838 | 95.0202 | SDS-THM4 | mg/L | 12.9 | --- | 340.6206 | --- | 94.5281 | 337.4841 | 96.1776 | Alkb, mg/L CaCO3 | 252.2525 | 280.6634 | 240.9533 | 240.9302 | Alkb, mg/L CaCO3 | 210.3171 | 244.9741 | 196.5339 | 196.5057
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 14 | 14 | 14 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 11:15 | 74.0833 | 23 | 36 | 33 | 272 | 4.68 | 2.18 |  | 6.86 | 0.18779 | 0.68222 | 38.6501 | 10.6818 | 11.1992 | 501.6859 | 253.6912 | 497.4189 | 2.4586 | 32.0414 | 0.34952 | 7.03 | 7.11 | 7.64 | 254 | 337 | 502 | 501.0229 | 0.19463 | 23.609 | 498.8978 | 49.0878 | BMRL | 0.2 | 0.627 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 202.6418 | 240.7719 | 189.202 | 194.8849 | T-Hdb, mg/L CaCO3 | 184.3158 | 230.8286 | 167.9212 | 174.8535
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 13:30 | 76.3333 | 23 | 36 | 32 | 272 | 4.64 | 2.18 |  | 6.82 | 0.18779 | 0.68035 | 38.8827 | 10.5906 | 11.1035 | 500.9702 | 253.348 | 496.7461 | 2.4551 | 31.5449 | 0.35199 | 7.2 | 7.27 | 7.72 | 266 | 334 | 467 | 474.0413 | -1.5078 | 20 | 472.2668 | 43.6759 | BMRL | 0.203 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | 1 | --- | 214.3333 | --- | 96.9697 | 212.7067 | 99.5299 | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 158.2429 | 227.6942 | 178.5667 | 171.8241 | Ca-Hdb, mg/L CaCO3 | 135.8719 | 220.5919 | 160.6639 | 152.4389
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | < 0.1 mg/L (dechlorination prefered) | [13 empty] | SDS-CDBAA | mg/L | 3.2 | 3.5 | 3.35 | 8.9552 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 14:30 | 77.3333 | 23 | 36 | 32 | 272 | 4.68 | 2.2 |  | 6.88 | 0.18779 | 0.68023 | 38.5349 | 10.6818 | 11.1992 | 500.9449 | 253.3165 | 496.6842 | 2.455 | 31.545 | 0.35502 | 7.85 | 7.67 | 7.61 | 268 | 335 | 477 | 469.7091 | 1.5285 | 19.3985 | 467.9738 | 42.7318 | BMRL | 0.202 | 0.636 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 9 | 11 | 10 | 20 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 15:15 | 78.0833 | 23 | 38 | 33 | 272 | 4.76 | 0.78 |  | 5.54 | 0.18779 | 0.85921 | 48.0975 | 10.8644 | 11.3906 | 578.0489 | 292.263 | 573.0477 | 2.8329 | 32.6671 | 0.34869 |  |  |  | 263 | 333 |  | 756.6282 |  | 20.9023 | 752.309 | 65.041 | 0.02 | 0.202 | 0.603 | 1.3056 | -116.5115 | 90.0498 | 1.2943 | 98.4548 | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 62.2 | 70.4 | 66.3 | 12.368 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 17:00 | 79.8333 | 23 | 36 | 33 | 272 | 4.6 | 0.68 |  | 5.28 | 0.18779 | 0.87121 | 50.5152 | 10.4993 | 11.0077 | 583.9426 | 295.3302 | 579.0617 | 2.8617 | 31.6383 | 0.34792 |  |  |  | 278 | 334 |  | 701.1765 |  | 16.391 | 697.5981 | 60.149 | 0.024 | 0.214 | 0.776 | 1.3984 | -80.2001 | 88.0597 | 1.3867 | 98.2693 | [8 empty] | SDS-DBAA* | mg/L | 1.9 | 1.8 | 1.85 | 5.4054 | --- | 9.8803 | --- | 58.8889 | 9.8107 | 81.143 | SDS-DBAA* | mg/L | 3.3 | --- | 11.3 | --- | 26.6667 | 11.239 | 70.638 | SDS-DBAA* | mg/L | 1.8 | --- | 7.3102 | --- | 60 | 7.2626 | 75.2153 | SDS-DBAA* | mg/L | 1.2 | --- | 6.0529 | --- | 73.3333 | 6.0065 | 80.0216 | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 76.2 | 84.4 | 80.3 | 10.2117 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 17:20 | 80.1667 | 23 | 36 | 33 | 272 | 4.6 | 0.68 |  | 5.28 | 0.18779 | 0.87121 | 50.5152 | 10.4993 | 11.0077 | 583.9426 | 295.3302 | 579.0617 | 2.8617 | 31.6383 | 0.34792 |  |  |  | 279 | 329 |  | 694.4118 |  | 16.0902 | 690.8991 | 59.6178 | 0.019 | 0.214 | 0.849 | 1.4322 | -68.6898 | 90.5473 | 1.4202 | 98.6622 | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | 1.1 | --- | 87.1 | --- | 92.1429 | 86.4442 | 98.7275 | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 19.0846 | 19.8387 | 19.0698 | 18.894 | Qp/QT (HAA5), % | 60.9775 | 63.3871 | 60.9302 | 60.3687
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 17:40 | 80.5 | 23 | 36 | 33 | 272 | 4.6 | 0.68 |  | 5.28 | 0.18779 | 0.87121 | 50.5152 | 10.4993 | 11.0077 | 583.9426 | 295.3302 | 579.0617 | 2.8617 | 31.6383 | 0.34792 |  |  |  | 277 | 328 |  | 707.9412 |  | 16.6917 | 704.2972 | 60.67 | 0.021 | 0.214 | 0.868 | 1.4186 | -63.4386 | 89.5522 | 1.4068 | 98.5073 | [8 empty] | SDS-TBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 194.1361 | 195.527 | 195.1028 | 193.6447 | SDS-THM4b, ug/L | 102.7886 | 107.2327 | 105.8772 | 101.2184
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-04 | 18:00 | 80.8333 | 23 | 36 | 33 | 272 | 4.64 | 0.68 |  | 5.32 | 0.18779 | 0.87218 | 50.1278 | 10.5906 | 11.1035 | 584.4673 | 295.5738 | 579.5392 | 2.8643 | 31.6357 | 0.35098 |  |  |  | 279 | 329 |  | 697.5588 |  | 16.0902 | 693.9888 | 59.7976 | 0.022 | 0.22 | 0.899 | 1.4224 | -58.2216 | 89.0547 | 1.4105 | 98.4402 | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1998-12-05 | 10:00 | 96.8333 | 23 | 36 | 32 | 272 | 3.63 | 0.8 |  | 4.43 | 0.18779 | 0.81941 | 60.3995 | 8.2853 | 8.6865 | 558.1214 | 282.7763 | 554.4468 | 2.7351 | 31.2649 | 0.27784 |  |  |  | 303 | 322 |  | 466.3562 |  | 8.8722 | 465.2662 | 34.876 | 0.007 | 0.192 | >2.6 | 1.0813 | #VALUE! | 96.5174 | 1.0741 | 99.3483 | [8 empty] | SDS-DCBAA | mg/L | BMRL | 1.2 | 1.2 | #VALUE! | --- | 27.8667 | --- | 88 | 27.6355 | 95.6578 | SDS-DCBAA | mg/L | 1.3 | --- | 59.3 | --- | 87 | 58.8578 | 97.7913 | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | 539.0039 | 536.4048 | 540.2419 | 540.212 | SDS-TOXb, ug Cl- /L | 273.4026 | 265.0984 | 277.3581 | 277.2627
[44 empty] | 1998-12-05 | 11:00 | 97.8333 | 23 | 36 | 32 | 272 | 4.29 | 0.85 |  | 5.14 | 0.18779 | 0.83463 | 51.9183 | 9.7917 | 10.2659 | 565.7384 | 286.2873 | 561.3309 | 2.7725 | 31.2275 | 0.32875 |  |  |  | 292 | 330 |  | 536.9059 |  | 12.1805 | 534.9745 | 45.418 | 0.013 | 0.195 | 2.744 | 1.1498 | 58.096 | 93.5323 | 1.1409 | 98.8605 | [8 empty] | SDS-HAA5 | mg/L | 1.9 | 1.8 | 1.85 | 5.4054 | --- | 197.153 | --- | 97.2097 | 195.4596 | 99.0535 | SDS-HAA5 | mg/L | 4.3 | --- | 417.6333 | --- | 93.5143 | 414.4817 | 98.9626 | SDS-HAA5 | mg/L | 1.8 | --- | 133.4327 | --- | 97.2851 | 132.2943 | 98.6394 | SDS-HAA5 | mg/L | 1.2 | --- | 96.9353 | --- | 98.19 | 96.0191 | 98.7502 | SDS-CDb, mg/L | 4.7629 | 4.608 | 4.6272 | 4.5965 | SDS-CDb, mg/L | 2.9364 | 2.4415 | 2.5028 | 2.4045
[44 empty] | 1998-12-05 | 12:00 | 98.8333 | 23 | 36 | 32 | 272 | 4.32 | 0.7 |  | 5.02 | 0.18779 | 0.86056 | 53.1833 | 9.8602 | 10.3377 | 578.3652 | 292.6607 | 573.8275 | 2.8344 | 31.1656 | 0.3317 |  |  |  | 298 | 328 |  | 545.4143 |  | 10.3759 | 543.4495 | 45.1651 | 0.013 | 0.194 | 2.552 | 1.3612 | 46.6603 | 93.5323 | 1.3505 | 99.0374 | [8 empty] | SDS-HAA6 | mg/L | 1.9 | 1.8 | 1.85 | 5.4054 | --- | 239.5773 | --- | 97.6961 | 237.516 | 99.2211 | SDS-HAA6 | mg/L | 5.4 | --- | 504.7333 | --- | 93.2752 | 500.9259 | 98.922 | SDS-HAA6 | mg/L | 1.8 | --- | 162.0041 | --- | 97.7584 | 160.6186 | 98.8793 | SDS-HAA6 | mg/L | 1.2 | --- | 117.5235 | --- | 98.5056 | 116.4102 | 98.9692 | TOCb, mg/L | #DIV/0! | 5.5101 | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | 2.7883 | #VALUE! | #VALUE!
[44 empty] | 1998-12-05 | 13:00 | 99.8333 | 23 | 36 | 32 | 272 | 4.36 | 0.64 |  | 5 | 0.18779 | 0.872 | 53.4 | 9.9515 | 10.4334 | 584.1415 | 295.5618 | 579.5157 | 2.8627 | 31.1373 | 0.33508 |  |  | 7.81 | 286 | 330 | 700 | 649.2812 | 7.2455 | 13.985 | 646.3697 | 55.7529 | BMRL | 0.179 | 2.385 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-05 | 14:00 | 100.8333 | 23 | 35 | 32 | 272 | 4.44 | 0.54 |  | 4.98 | 0.18779 | 0.89157 | 53.6185 | 10.1341 | 10.6249 | 594.3033 | 300.6591 | 589.51 | 2.9125 | 30.5875 | 0.34736 | 7.79 | 7.63 |  | 281 | 333 |  | 755.9444 |  | 15.4887 | 752.0681 | 62.6364 | BMRL | 0.213 | 2.371 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 186.1831 | 190 | 186.186 | 184.3318 | Bromideb, ug/L | 177.8045 | 190 | 177.814 | 171.8894
[44 empty] | 1998-12-05 | 14:20 | 101.1667 | 23 | 36 | 32 | 272 | 4.4 | 0.52 |  | 4.92 | 0.18779 | 0.89431 | 54.2846 | 10.0428 | 10.5291 | 595.7107 | 301.3933 | 590.9497 | 2.9194 | 31.0806 | 0.33877 | 7.8 | 7.78 | [64 empty] | Alkb, mg/L CaCO3 | 394.5252 | 403.1242 | 392.8465 | 391.0415 | Alkb, mg/L CaCO3 | 288.1171 | 315.5919 | 282.7535 | 276.9862
[44 empty] | 1998-12-05 | 14:35 | 101.4167 | 23 | 36 | 32 | 272 | 4.6 | 0.48 |  | 5.08 | 0.18779 | 0.90551 | 52.5433 | 10.4993 | 11.0077 | 601.8614 | 304.3927 | 596.8307 | 2.9495 | 31.0505 | 0.35451 | 7.47 | 7.36 | [64 empty] | T-Hdb, mg/L CaCO3 | 264.8161 | 274.8903 | 261.9721 | 262.5714 | T-Hdb, mg/L CaCO3 | 218.315 | 250.5032 | 209.2279 | 211.1429
[44 empty] | 1998-12-05 | 23:20 | 110.1667 | 23 | 35.5 | 32.5 | 272 | 4.49 | 0.49 |  | 4.98 | 0.18779 | 0.90161 | 53.6185 | 10.2482 | 10.7445 | 599.6656 | 303.3438 | 594.7742 | 2.9388 | 31.0612 | 0.34591 | [66 empty] | Ca-Hdb, mg/L CaCO3 | 234.1404 | 252.0645 | 239.786 | 237.3272 | Ca-Hdb, mg/L CaCO3 | 177.3755 | 234.6452 | 195.414 | 187.5576
[44 empty] | 1998-12-06 | 10:00 | 120.8333 | 23 | 35 | 32 | 281 | 4.56 | 0.38 |  | 4.94 | 0.19401 | 0.92308 | 55.8826 | 10.408 | 10.912 | 611.29 | 309.2675 | 606.3888 | 2.9957 | 30.5043 | 0.35772 | [66 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1998-12-06 | 10:50 | 121.6667 | 23 | 34.5 | 32 | 272 | 4.68 | 4.12 |  | 8.8 | 0.18779 | 0.53182 | 29.9091 | 10.6818 | 11.1992 | 451.0859 | 228.1039 | 447.2493 | 2.2106 | 31.0394 | 0.36081 | 7.58 | 7.42 |  | 270 | 333 |  | 403.4951 |  | 18.797 | 402.3467 | 32.8937 | BMRL | 0.204 | 1.588 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1998-12-06 | 11:15 | 122.0833 | 23 | 34 | 32 | 281 | 4.8 | 4.72 |  | 9.52 | 0.19401 | 0.5042 | 28.5168 | 10.9557 | 11.4863 | 442.8742 | 223.9654 | 439.1348 | 2.1704 | 30.8296 | 0.37257 | 7.66 | 7.71 | 7.64 | 253 | 334 | 480 | 413.3475 | 13.8859 | 23.9098 | 411.9779 | 38.5889 | BMRL | 0.201 | 1.032 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1998-12-06 | 11:40 | 122.5 | 23 | 34.5 | 32 | 281 | 4.8 | 4.64 |  | 9.44 | 0.19401 | 0.50847 | 28.7669 | 10.9557 | 11.4863 | 444.1236 | 224.5972 | 440.3736 | 2.1765 | 31.0735 | 0.36965 | 7.74 | 7.6 | 7.55 | 247 | 337 | 468 | 420.9483 | 10.0538 | 25.7143 | 419.4626 | 41.1151 | BMRL | 0.199 | 0.838 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1998-12-06 | 12:00 | 122.8333 | 23 | 34.5 | 32 | 281 | 4.92 | 4.6 |  | 9.52 | 0.19401 | 0.51681 | 28.5168 | 11.2296 | 11.7735 | 446.6139 | 225.8081 | 442.7479 | 2.1887 | 31.0613 | 0.37904 | 7.44 | 7.45 | 7.62 | 248 | 337 | 449 | 422.8783 | 5.8178 | 25.4135 | 421.3473 | 41.1412 | BMRL | 0.2 | 0.694 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1998-12-06 | 12:20 | 123.1667 | 23 | 34.5 | 32 | 281 | 4.9 | 5 |  | 9.9 | 0.19401 | 0.49495 | 27.3838 | 11.184 | 11.7256 | 440.2189 | 222.5828 | 436.4238 | 2.1574 | 31.0926 | 0.37712 | 7.33 | 7.65 | 7.49 | 250 | 337 | 429 | 413.35 | 3.648 | 24.812 | 411.9258 | 39.3095 | BMRL | 0.199 | 0.609 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1998-12-06 | 12:40 | 123.5 | 23 | 34.5 | 32 | 281 | 4.98 | 4.98 |  | 9.96 | 0.19401 | 0.5 | 27.2129 | 11.3666 | 11.9171 | 441.7002 | 223.2998 | 437.8297 | 2.1647 | 31.0853 | 0.38337 | 7.51 | 7.43 | 7.45 | 247 | 337 | 422 | 418 | 0.94787 | 25.7143 | 416.4847 | 40.6941 | BMRL | 0.201 | 0.525 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1998-12-06 | 13:00 | 123.8333 | 23 | 34 | 32 | 281 | 5 | 4.93 |  | 9.93 | 0.19401 | 0.50352 | 27.2981 | 11.4122 | 11.9649 | 442.7306 | 223.8126 | 438.8353 | 2.1697 | 30.8303 | 0.38809 | [66 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1998-12-07 | 8:30 | 143.3333 | 23 | 36 | 34 | 281 | 4.76 | 4.36 |  | 9.12 | 0.19401 | 0.52193 | 29.8114 | 10.8644 | 11.3906 | 448.0929 | 226.6208 | 444.3413 | 2.196 | 32.804 | 0.34723 | 7.3 | 7.19 | 7.35 | 248 | 337 | 420 | 424.7523 | -1.1315 | 25.4135 | 423.2552 | 41.4065 | BMRL | 0.212 | 0.429 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1998-12-07 | 9:35 | 144.4167 | 23 | 36 | 34 | 272 | 4.92 | 12.71 |  | 17.63 | 0.18779 | 0.27907 | 14.4282 | 11.2296 | 11.7735 | 385.7367 | 194.9717 | 382.2861 | 1.8904 | 33.1096 | 0.35559 | 7.59 | 7.4 | 7.36 | 225 | 333 |  | 374.1129 |  | 32.3308 | 372.7643 | 39.6401 |  | 0.206 | 0.304 |  | #VALUE! | [50 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1998-12-07 | 10:05 | 144.9167 | 23 | 36 | 34 | 272 | 5.11 | 12.81 |  | 17.92 | 0.18779 | 0.28516 | 14.1786 | 11.6633 | 12.2282 | 387.1113 | 195.5976 | 383.5134 | 1.8971 | 33.1029 | 0.3694 | 7.03 | 7.38 | 7.47 | 241 | 334 |  | 369 |  | 27.5188 | 367.7976 | 34.4748 |  | 0.213 | 0.294 |  | #VALUE! | [50 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1998-12-07 | 10:45 | 145.5833 | 23 | 37 | 34 | 272 | 5.29 | 11.7 |  | 16.99 | 0.18779 | 0.31136 | 15.0094 | 12.0741 | 12.6589 | 393.0678 | 198.541 | 389.2845 | 1.9264 | 33.5736 | 0.37705 | 7.21 | 7.22 | 7.41 | 219 | 337 |  | 383.8175 |  | 34.1353 | 382.2148 | 42.7024 |  | 0.209 | 0.308 |  | #VALUE! | [50 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1998-12-07 | 11:15 | 146.0833 | 23 | 37 | 34 | 272 | 5.18 | 11.4 |  | 16.58 | 0.18779 | 0.31242 | 15.4053 | 11.8231 | 12.3957 | 393.2979 | 198.6978 | 389.5919 | 1.9275 | 33.5725 | 0.36922 | 7.18 | 7.32 | 7.5 | 230 | 335 | 372 | 379.0746 | -1.9018 | 30.8271 | 377.6551 | 39.0979 | BMRL | 0.215 | 0.299 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-07 | 11:45 | 146.5833 | 23 | 38 | 34 | 272 | 5.2 | 11.4 |  | 16.6 | 0.18779 | 0.31325 | 15.3855 | 11.8687 | 12.4435 | 393.4914 | 198.7882 | 389.7691 | 1.9284 | 34.0716 | 0.36522 | 7.25 | 7.35 | 7.59 | 227 | 335 | 370 | 380.6228 | -2.871 | 31.7293 | 379.1544 | 40.1299 | BMRL | 0.202 | 0.292 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-07 | 12:20 | 147.1667 | 23 | 37 | 34 | 272 | 5.29 | 11.4 |  | 16.69 | 0.18779 | 0.31696 | 15.2972 | 12.0741 | 12.6589 | 394.359 | 199.1932 | 390.5633 | 1.9327 | 33.5673 | 0.37712 | 7.35 | 7.27 | 7.46 | 227 | 330 | 371 | 381.4557 | -2.8182 | 31.7293 | 379.9537 | 40.2559 | BMRL | 0.203 | 0.295 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-07 | 13:45 | 148.5833 | 23 | 37 | 34 | 272 | 5.2 | 11.4 |  | 16.6 | 0.18779 | 0.31325 | 15.3855 | 11.8687 | 12.4435 | 393.4914 | 198.7882 | 389.7691 | 1.9284 | 33.5716 | 0.37066 | 7.17 | 7.29 | 7.56 | 224 | 335 | 371 | 381.9912 | -2.9626 | 32.6316 | 380.481 | 41.1272 | BMRL | 0.2 | 0.302 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-07 | 14:30 | 149.3333 | 23 | 37 | 34 | 272 | 5.18 | 11.3 |  | 16.48 | 0.18779 | 0.31432 | 15.5049 | 11.8231 | 12.3957 | 393.7347 | 198.9185 | 390.0246 | 1.9296 | 33.5704 | 0.36924 | 7.27 | 7.34 | 7.48 | 224 | 334 | 371 | 382.2372 | -3.0289 | 32.6316 | 380.7304 | 41.1657 | BMRL | 0.2 | 0.297 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-08 | 8:45 | 167.5833 | 23 | 37 | 34 | 272 | 5.4 | 9.9 | X | 15.3 | 0.18779 | 0.35294 | 16.7778 | 12.3252 | 12.9221 | 402.8861 | 203.4588 | 398.9269 | 1.9745 | 33.5255 | 0.38544 | 7.47 | 7.51 | 7.63 | 226 | 337 | 366 | 390.5909 | -6.7188 | 32.0301 | 388.9571 | 41.8959 | BMRL | 0.198 | 0.307 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1998-12-09 | 9:15 |  | 23 | 40 | 38 | 272 | 6.06 | 30.1 |  | 36.16 | 0.18779 | 0.16759 | 6.5221 | 13.8316 | 14.5015 | 362.619 | 182.8991 | 358.6149 | 1.7772 | 37.2228 | 0.38959
[44 empty] | 1998-12-09 | 9:45 |  | 23 | 60 | 58 | 272 | 9.5 | 19.5 |  | 29 | 0.18779 | 0.32759 | 8.3793 | 21.6832 | 22.7334 | 397.4531 | 199.1752 | 390.528 | 1.9482 | 57.0518 | 0.39847
[44 empty] | 1998-12-09 | 10:15 |  | 23 | 30 | 27 | 272 | 4.4 | 10.1 |  | 14.5 | 0.18779 | 0.30345 | 17.7586 | 10.0428 | 10.5291 | 391.1406 | 197.8933 | 388.0145 | 1.9168 | 26.5832 | 0.39608
[44 empty] | 1998-12-09 | 10:30 |  | 23 | 50 | 48 | 272 | 7.87 | 16.8 |  | 24.67 | 0.18779 | 0.31901 | 10.0255 | 17.9629 | 18.8328 | 395.199 | 198.6572 | 389.5123 | 1.937 | 47.063 | 0.40016
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X27: C. Rice: Feed TOX concentrations verified by consultant.
Note on X32: C. Rice: Feed THM values verified by consultant.
Note on X42: C. Rice: Feed HAA values verified by consultant.
Note on X43: C. Rice: Feed HAA values verified by consultant.
Note on CY37: C. Rice: THM concentrations at the 70% recovery run were verified by the consultant; however, there was no explanation provided for the slight dip in these concentrations.
Note on DG10: C. Rice 7/12/99: Consultant verified all water quality parameters for the 70% recovery run due to high mass balance closure errors (which may suggest membrane system was not operating at steady-state)
Note on DQ10: C. Rice 7/12/99: Consultant verified all water quality parameters for the 90% recovery run due to high mass balance closure errors (which may suggest membrane system was not operating at steady-state).

## SR40. 4th Quarter
FIELD-SET 4: 4th QUARTER RBSMT RESULTS (FILE: rbsmt-1.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Manufacturer Reported Membrane Characteristics1 |  | Field 4-3: RBSMT Design Parameters | [8 empty] | Field 4-4: Foulants And Fouling Indices1 | Field 4-5: Pretreatment Used Prior To Membranes1 |  |  | Field 4-6: Feed Water Quality After Pretreatment | [5 empty] | Field 4-7: Membrane Setting Data | [20 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water | [16 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [19 empty] | Field 4-8: Membrane Performance Data During Operation With The Test Water (continued) | [11 empty] | Field 4-9: Permeate And Concentrate Water Quality For Run 1 | [11 empty] | Field 4-10: Permeate And Concentrate Water Quality For Run 2 | [8 empty] | Field 4-11: Permeate And Concentrate Water Quality For Run 3 | [8 empty] | Field 4-12: Permeate And Concentrate Water Quality For Run 4 | [8 empty] | Field 4-13: Blending Calculations For Stage 1 D-DBP MCLs |  |  |  |  | Field 4-14: Blending Calculations For Proposed Stage 2 D-DBP MCLs |  |  |  |  | Field 4-15: Membrane Cost Parameters
|  | General Information |  | Input Design Parameters | [8 empty] | Parameters Evaluated Prior to Pretreatment | [79 empty] | Operating Parameters During Sample Collection | [11 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Operating Parameters During Sample Collection | [8 empty] | Feed and Permeate Water Quality Parameters |  |  |  |  | Feed and Permeate Water Quality Parameters |  |  |  |  | General Cost Parameters
PWS Name | Broward County Office of Environmental Services- 2A WTP | Membrane manufacturer | Fluid Systems | [5 empty] | Active membrane area in bench-scale cell, Acell (ft2) | 0.16667 |  |  | Alkalinity (mg/L as CaCO3) | Process | Description | Scale | Parameter | Units | CF-1 | CF-2 | Average | RPD |  |  |  | Average TDS rejection (decimal fraction) | [6 empty] | TDS concentration of setting solution (mg/L) | [13 empty] | Average bulk TDS rejection (decimal fraction) | 0.725 | [45 empty] | Recovery during sample collection (decimal) | 0.69 | [10 empty] | Recovery during sample collection (decimal) | 0.87 | [7 empty] | Recovery during sample collection (decimal) | 0.49 | [7 empty] | Recovery during sample collection (decimal) | 0.29 | [8 empty] | RUN ID # |  |  |  |  | RUN ID # |  |  | Cost Parameter | Parameter value
Public Water System Identification Number | 4060163 | Membrane trade name | TFC-SR | [5 empty] | Active width of membrane in the bench-scale cell, wcell (ft) | 0.33 |  |  | Calcium Hardness (mg/L as CaCO3) | Cartridge filtration | 5 micron filter | bench | Sampling date | MM/DD/YY | 1999-03-23 | 1999-03-31 | --- | --- | [71 empty] | Feed flow rate during sample collection (mL/min) | 8.4 | [10 empty] | Feed flow rate during sample collection (mL/min) | 4.99 | [7 empty] | Feed flow rate during sample collection (mL/min) | 5.37 | [7 empty] | Feed flow rate during sample collection (mL/min) | 9.21 | [6 empty] | Parameter | 1 | 2 | 3 | 4 | Parameter | 1 | 2 | 3 | 4 | Capital Recovery Interest Rate (%) | 6
Water Industry Data Base Number (optional) |  | Molecular weight cutoff (Daltons) | 300 | [5 empty] | Average yearly temperature of feed water, TavgoC (oC) | 24.6 |  |  | LSI |  |  |  | Sampling time | hh:mm | 0:00 | 0:00 | --- | --- | Date | Time | Setting time | Influent | PI | PC | QI | Qp | QW | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) | Date | Time | Operation time | Influent | PI | PC | QI | Qp | QW | Cleaning Event | QF | vc | Recovery | Recycle | FW (ToC) | FW (TavgoC) | TDSW | TDSp | TDSI | Dp | NDP | MTCW (TavgoC) |  | pH | [5 empty] | TDS (mg/L) | [7 empty] | UV254 (cm-1) | [7 empty] | TOC (mg/L), Optional |  |  |  |  | Influent flow rate during sample collection (mL/min) | 276 | [10 empty] | Influent flow rate during sample collection (mL/min) | 272 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [7 empty] | Influent flow rate during sample collection (mL/min) | 281 | [6 empty] | SDS-THM4F, ug/L | 192.3 | 192.3 | 192.3 | 192.3 | SDS-THM4F, ug/L | 192.3 | 192.3 | 192.3 | 192.3 | Capital Recovery Period (years) | 20
|  | Membrane material (e.g., PVD, polyamide, etc.) | Polyamide | [5 empty] | Approximate feed water TDS, TDSF (mg/L) | 700 |  |  | Dissolved iron (mg/L) |  |  |  | Operation time | hh.hh | 0 | 0 | --- | --- | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | MM/DD/YY | hh:mm | hh.hh | Temp. (oC) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | Indicate with "X" | (mL/min) | (fps) | (decimal) | ratio | (gfd) | (gfd) | (mg/L) | (mg/L) | (mg/L) | (psi) | (psi) | (gfd/psi) | pHp | pHF | pHC | TDSp | TDSF | TDSC | TDSC(calc) | ErrorMB (%) | RF (%) | TDSB | RB (%) | UVp | UVF | UVC | UVC(calc) | ErrorMB (%) | RF (%) | UVB | RB (%) | TOCp | TOCF | TOCC | TOCC(calc) | ErrorMB (%) | RF (%) | TOCB | RB (%) | [39 empty] | SDS-THM4p, ug/L | 8.45 | 13.6 | 8.8 | 8.1 | SDS-THM4p, ug/L | 8.45 | 13.6 | 8.8 | 8.1 | Overhead & Profit Factor (% of construction costs) | 15
Official ICR Contact Person |  | Membrane construction (e.g., thin-film composite) | Thin film composite | [5 empty] | Manufacturer reported TDS rejection, RejTDS (decimal fraction) | 0.5 |  |  | Total iron (mg/L) |  |  |  | pH | --- | 8.4 | 7.8 | 8.1 | 7.4074 | 1999-03-23 | 13:30 | 0 | 24 | [5 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-24 | 11:00 | 0 | 24 | [6 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [27 empty] | Permeate and Concentrate Water Quality | [11 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | Permeate and Concentrate Water Quality | [8 empty] | SDS-HAA5F, ug/L | 56.15 | 56.15 | 56.15 | 56.15 | SDS-HAA5F, ug/L | 56.15 | 56.15 | 56.15 | 56.15 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Membrane hydrophobicity | N.A | [5 empty] | Temperature normalized MTCW (gfd/psi) | 0.23718 |  |  | Dissolved aluminum (mg/L) |  |  |  | Temperature | oC | 24 | 24 | 24 | 0 | 1999-03-23 | 14:00 | 0.5 | 24 | 61 | 60 | 272 | 5.77 | 1.34 | 7.11 | 0.18779 | 0.81153 | 37.256 | 13.1697 | 13.4054 | 0 | 0 | 0 | 0 | 60.5 | 0.22158 | 1999-03-24 | 11:15 | 0.25 | 24 | 58 | 57 | 272 | 6.77 | 3.05 |  | 9.82 | 0.18779 | 0.68941 | 26.6986 | 15.4522 | 15.7287 | 613.0088 | 165.5115 | 601.8708 | 4.4193 | 53.0807 | 0.29632 | 8 | 7.2 | 8.1 | 31 | 305 | 80 | 911.5803 | -1039.4754 | 89.8194 | 900.6216 | 96.5579 | BMRL | 0.173 | 0.007 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Parameter | Units | Cp-1 | Cp-1 (dup) | Average | RPD | CC-1 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-2 | CC-2 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-3 | CC-3 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | Parameter | Units | Cp-4 | CC-4 | CC(calc) | ErrorMB (%) | RF (%) | CB | RB (%) | SDS-HAA5p, ug/L | 0 | 1.2 | 0 | 0 | SDS-HAA5p, ug/L | 0 | 1.2 | 0 | 0 | Construction Contingencies (% of construction costs) | 10
|  | Membrane charge (e.g., negative, highly negative, neutral, etc.) | Slightly negative | [9 empty] | Total aluminum (mg/L) |  |  |  | Alkalinity | mg/L as CaCO3 | 216 | 218 | 217 | 0.92166 | 1999-03-23 | 14:30 | 1 | 24 | 60 | 59 | 272 | 6.6 | 1.43 | 8.03 | 0.18779 | 0.82192 | 32.873 | 15.0641 | 15.3337 | 0 | 0 | 0 | 0 | 59.5 | 0.25771 | 1999-03-24 | 11:30 | 0.5 | 24 | 59 | 58 | 272 | 6.67 | 3.2 |  | 9.87 | 0.18779 | 0.67579 | 26.5583 | 15.2239 | 15.4963 | 600.9164 | 162.2912 | 590.1604 | 4.3325 | 54.1675 | 0.28608 | 7.5 | 7.3 | 7.4 | 50 | 306 | 120 | 834.9734 | -595.8112 | 83.5796 | 825.3489 | 93.942 | BMRL | 0.173 | 0.056 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling date | MM/DD/YY | 1999-03-25 | 1999-03-26 | --- | --- | 1999-03-25 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-27 | 1999-03-27 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-28 | 1999-03-28 | --- | --- | --- | --- | --- | Sampling date | MM/DD/YY | 1999-03-29 | 1999-03-29 | --- | --- | --- | --- | --- | SDS-TOXF, ug Cl- /L | 505 | 505 | 505 | 505 | SDS-TOXF, ug Cl- /L | 505 | 505 | 505 | 505 | Engineering Fee Factor (% of construction costs) | 15
Phone Number |  |  |  | Experimental Design1,2 | [8 empty] | Fluoride (mg/L) |  |  |  | Total dissolved solids | mg/L | 304 | 305 | 304.5 | 0.32841 | 1999-03-23 | 15:00 | 1.5 | 24 | 60 | 59 | 281 | 6.67 | 2.53 | 9.2 | 0.19401 | 0.725 | 29.5435 | 15.2239 | 15.4963 | 0 | 0 | 0 | 0 | 59.5 | 0.26044 | 1999-03-24 | 11:45 | 0.75 | 24 | 59 | 58 | 272 | 6.46 | 3.09 |  | 9.55 | 0.18779 | 0.67644 | 27.4817 | 14.7446 | 15.0084 | 601.3582 | 162.5044 | 590.9354 | 4.3364 | 54.1636 | 0.27709 | 7.2 | 7.2 | 7.4 | 106 | 306 | 317 | 719.4871 | -126.9675 | 65.1888 | 712.2019 | 85.1166 | BMRL | 0.178 | 0.166 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Sampling time | hh:mm | 11:00 | 9:15 | --- | --- | 11:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 19:00 | 19:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 20:00 | 20:00 | --- | --- | --- | --- | --- | Sampling time | hh:mm | 18:00 | 432:00 | --- | --- | --- | --- | --- | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | SDS-TOXp, ug Cl- /L | #DIV/0! | BMRL | BMRL | BMRL | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number |  | Design Parameters |  | ID# | Recovery | FW-design | Dp | PI | QI-cell | Qp | QF | QW | Phosphate (mg/L) |  |  |  | Total hardness | mg/L as CaCO3 | 250 | 254 | 252 | 1.5873 | 1999-03-23 | 16:00 | 2.5 | 24 | 60 | 59 | 281 | 6.67 | 1.41 | 8.08 | 0.19401 | 0.8255 | 33.7772 | 15.2239 | 15.4963 | 0 | 0 | 0 | 0 | 59.5 | 0.26044 | 1999-03-24 | 12:00 | 1 | 24 | 60 | 58 | 272 | 6.47 | 3.09 |  | 9.56 | 0.18779 | 0.67678 | 27.4519 | 14.7674 | 15.0317 | 601.6576 | 162.5808 | 591.2134 | 4.3385 | 54.6615 | 0.275 | 7.2 | 7.2 | 7.3 | 108 | 305 | 374 | 715.9417 | -91.4283 | 64.532 | 708.7113 | 84.7611 | BMRL | 0.174 | 0.194 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Operation time | hh.hh | 24 | 46.25 | --- | --- | 24 | --- | --- | --- | --- | --- | Operation time | hh.hh | 80 | 80 | --- | --- | --- | --- | --- | Operation time | hh.hh | 105 | 105 | --- | --- | --- | --- | --- | Cumulative time | hr | 127 | 127 | --- | --- | --- | --- | --- | SDS-CDF, mg/L | 5.625 | 5.625 | 5.625 | 5.625 | SDS-CDF, mg/L | 5.625 | 5.625 | 5.625 | 5.625 | 1998 Producers Price Index (PPI base year 1967 = 100) | 366.8
E-Mail Address (optional) |  | Design flux, FW (gfd) | 24 |  | (decimal) | (gfd) | (psi) | (psi) | (mL/min) | (mL/min) | (mL/min) | (mL/min) | Sulfate (mg/L) |  |  |  | Calcium hardness | mg/L as CaCO3 | 236 | 238 | 237 | 0.84388 | 1999-03-23 | 16:30 | 3 | 24 | 60 | 59 | 272 | 6.8 | 4.17 | 10.97 | 0.18779 | 0.61987 | 23.7949 | 15.5206 | 15.7984 | 0 | 0 | 0 | 0 | 59.5 | 0.26552 | 1999-03-24 | 13:00 | 2 | 24 | 60 | 58 | 272 | 6.2 | 2.81 |  | 9.01 | 0.18779 | 0.68812 | 29.1887 | 14.1512 | 14.4044 | 611.4954 | 165.3618 | 601.3262 | 4.4105 | 54.5895 | 0.26387 | 7.2 | 7.2 | 7.3 | 114 | 306 | 532 | 724.8203 | -36.2444 | 62.5616 | 717.8587 | 84.1194 | BMRL | 0.173 | 0.361 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | pH | --- | 8.6 | 8.6 | 8.6 | 0 | 8 | --- | --- | --- | --- | --- | pH | --- | 8.8 | 8.5 | --- | --- | --- | --- | --- | pH | --- | 8.8 | 8.4 | --- | --- | --- | --- | --- | pH | --- | 8.8 | 8.5 | --- | --- | --- | --- | --- | SDS-CDp, mg/L | 2.45 | 2.05 | 2.02 | 1.9 | SDS-CDp, mg/L | 2.45 | 2.05 | 2.02 | 1.9 | Labor Rate + Fringe ($/work-hour) | 30
|  | Net driving pressure at the design flux, NDP (psi) | 100 | 1 | 0.7 | 15 | 15.1667 | 78.41 | 429.2657 | 6.5712 | 9.3874 | 2.8162 | Calcium (mg/L) |  |  |  | Turbidity | ntu | 0.165 | 0.138 | 0.1515 | 17.8218 | 1999-03-23 | 17:00 | 3.5 | 24 | 59 | 58 | 272 | 6.52 | 2.56 | 9.08 | 0.18779 | 0.71806 | 28.9559 | 14.8816 | 15.1478 | 0 | 0 | 0 | 0 | 58.5 | 0.25894 | 1999-03-24 | 14:00 | 3 | 24 | 60 | 58 | 272 | 6.2 | 2.79 |  | 8.99 | 0.18779 | 0.68966 | 29.2558 | 14.1512 | 14.4044 | 612.87 | 165.7335 | 602.6779 | 4.4204 | 54.5796 | 0.26392 | 7.2 | 7.2 | 7.3 | 151 | 305 | 591 | 645.6111 | -9.2405 | 50.4105 | 639.974 | 76.4053 | BMRL | 0.174 | 0.412 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Temperature | oC | 24 | 24 | 24 | 0 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | Temperature | oC | 24 | 24 | --- | --- | --- | --- | --- | TOCF, mg/L | 5.9 | 5.9 | 5.9 | 5.9 | TOCF, mg/L | 5.9 | 5.9 | 5.9 | 5.9 | Labor Overhead Factor (% of labor) | 40
Technical ICR Contact Person |  | Water mass transfer coefficient, MTCW (gfd/psi) | 0.24 | 2 | 0.9 | 15 | 38.5 | 101.7434 | 429.2657 | 6.5712 | 7.3013 | 0.73013 | Barium (mg/L) |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! | 1999-03-24 | 8:45 | 19.25 | 24 | 60 | 60 | 272 | 6.88 | 2.7 | 9.58 | 0.18779 | 0.71816 | 27.3925 | 15.7032 | 15.9842 | 0 | 0 | 0 | 0 | 60 | 0.2664 | 1999-03-24 | 15:00 | 4 | 24 | 60 | 58 | 272 | 6.08 | 2.81 |  | 8.89 | 0.18779 | 0.68391 | 29.5962 | 13.8773 | 14.1256 | 607.673 | 164.3822 | 597.7641 | 4.3834 | 54.6166 | 0.25863 | 7.2 | 7.2 | 7.3 | 134 | 307 | 564 | 673.411 | -19.3991 | 55.9934 | 667.3823 | 79.9216 | BMRL | 0.169 | 0.451 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Alkalinity | mg/L as CaCO3 | 102 | 96 | 99 | 6.0606 | 413 | 479.6452 | -16.1368 | 54.3779 | 475.6484 | 79.1863 | Alkalinity | mg/L as CaCO3 | 118 | 266 | 879.5385 | -230.6536 | 45.6221 | 873.4611 | 86.4905 | Alkalinity | mg/L as CaCO3 | 100 | 338 | 329.4118 | 2.5409 | 53.9171 | 328.3377 | 69.5435 | Alkalinity | mg/L as CaCO3 | 90 | 266 | 268.8732 | -1.0802 | 58.5253 | 268.0231 | 66.4208 | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | TOCp, mg/L | #DIV/0! | BMRL | BMRL | BMRL | Electric Rate ($/kW-h) | 0.055
Mailing Address |  | Temperature at which the MTCW was determined, ToC (oC) | 25 | 3 | 0.5 | 15 | 10.5 | 73.7434 | 429.2657 | 6.5712 | 13.1424 | 6.5712 | Strontium (mg/L) |  |  |  | Total organic carbon | mg/L | 5.5 | 6.3 | 5.9 | 13.5593 | 1999-03-24 | 9:00 | 19.5 | 24 | 60 | 60 | 272 | 6.87 | 3.5 | 10.37 | 0.18779 | 0.66249 | 25.2295 | 15.6804 | 15.961 | 0 | 0 | 0 | 0 | 60 | 0.26602 | 1999-03-24 | 16:00 | 5 | 24 | 60 | 58 | 272 | 6.2 | 2.77 |  | 8.97 | 0.18779 | 0.69119 | 29.3233 | 14.1512 | 14.4044 | 614.257 | 166.1086 | 604.0418 | 4.4304 | 54.5696 | 0.26396 | 7.2 | 7.2 | 7.3 | 143 | 306 | 575 | 665.9801 | -15.8226 | 53.0378 | 660.0197 | 78.334 | BMRL | 0.169 | 0.465 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total dissolved solids | mg/L | 128 | 130 | 129 | 1.5504 | 595 | 695.129 | -16.8284 | 57.6355 | 689.1847 | 81.2822 | Total dissolved solids | mg/L | 159 | 656 | 1278.2308 | -94.8523 | 47.7833 | 1269.2989 | 87.4734 | Total dissolved solids | mg/L | 131 | 455 | 471.1961 | -3.5596 | 56.9787 | 469.6033 | 72.1041 | Total dissolved solids | mg/L | 121 | 368 | 379.4507 | -3.1116 | 60.2627 | 378.2224 | 68.0082 | UV254 F, cm-1 | 0.1555 | 0.1555 | 0.1555 | 0.1555 | UV254 F, cm-1 | 0.1555 | 0.1555 | 0.1555 | 0.1555 | Fuel Oil Rate ($/gal) | NA
|  | Active membrane area of an equivalent 8" x 40" element (ft2) | 330 | 4 | 0.3 | 15 | 8.5 | 71.7434 | 429.2657 | 6.5712 | 21.9039 | 15.3328 | Reactive silica (mg/L as SiO2) |  |  |  | UV254 | cm-1 | 0.155 | 0.156 | 0.1555 | 0.64309 | 1999-03-24 | 9:15 | 19.75 | 24 | 70 | 70 | 272 | 8.48 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 19.3551 | 19.7015 | #VALUE! | #VALUE! | #VALUE! | 0 | 70 | 0.28145 | 1999-03-24 | 17:00 | 6 | 24 | 60 | 58 | 272 | 6.15 | 2.76 |  | 8.91 | 0.18779 | 0.69024 | 29.5275 | 14.037 | 14.2882 | 613.3612 | 165.8891 | 603.2438 | 4.4241 | 54.5759 | 0.2618 | 7.2 | 7.2 | 7.3 | 155 | 306 | 538 | 637.625 | -18.5177 | 49.0969 | 632.1689 | 75.4812 | BMRL | 0.169 | 0.467 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total hardness | mg/L as CaCO3 | 70 | 64 | 67 | 8.9552 | 623 | 663.7742 | -6.5448 | 73.4127 | 657.5081 | 89.81 | Total hardness | mg/L as CaCO3 | 104 | 696 | 1242.4615 | -78.5146 | 58.7302 | 1233.3762 | 91.5679 | Total hardness | mg/L as CaCO3 | 66 | 454 | 430.7059 | 5.1309 | 73.8095 | 428.9983 | 84.6153 | Total hardness | mg/L as CaCO3 | 60 | 356 | 330.4225 | 7.1847 | 76.1905 | 329.1374 | 81.7705 | UV254 p, cm-1 | #DIV/0! | 0.009 | BMRL | BMRL | UV254 p, cm-1 | #DIV/0! | 0.009 | BMRL | BMRL | Natural Gas Rate ($/ft3) | NA
Phone Number |  | Purchase price for an equivalent 8" x 40 " element ($) | N.A. | 1: For experimental matrix see Table 4-2 in Part 3 of the ICR Treatment Studies Manual. | [8 empty] | Turbidity (ntu) |  |  |  | SUVA | L/(mg*m) | 2.8182 | 2.4762 | 2.6472 | 12.9191 | 1999-03-24 | 9:30 | 20 | 24 | 50 | 49 | 272 | 5.8 | NA | #VALUE! | 0.18779 | #VALUE! | #VALUE! | 13.2382 | 13.4751 | #VALUE! | #VALUE! | #VALUE! | 0 | 49.5 | 0.27222 | 1999-03-24 | 17:45 | 6.75 | 24 | 60 | 58 | 272 | 6.2 | 2.72 |  | 8.92 | 0.18779 | 0.69507 | 29.4933 | 14.1512 | 14.4044 | 617.7797 | 167.0612 | 607.5059 | 4.4558 | 54.5442 | 0.26409 | 7.2 | 7.2 | 7.3 | 159 | 305 | 549 | 636.1544 | -15.8751 | 47.7833 | 630.7163 | 74.7906 | BMRL | 0.169 | 0.471 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Calcium hardness | mg/L as CaCO3 | 58 | 58 | 58 | 0 | 581 | 635.4194 | -9.3665 | 75.5274 | 629.3565 | 90.7842 | Calcium hardness | mg/L as CaCO3 | 96 | 604 | 1180.6154 | -95.4661 | 59.4937 | 1171.9598 | 91.8086 | Calcium hardness | mg/L as CaCO3 | 60 | 414 | 407.0588 | 1.6766 | 74.6835 | 405.4339 | 85.201 | Calcium hardness | mg/L as CaCO3 | 52 | 324 | 312.5634 | 3.5298 | 78.0591 | 311.3251 | 83.2972 | BromideF, ug/L | 170 | 170 | 170 | 170 | BromideF, ug/L | 170 | 170 | 170 | 170 | Current Process Water Rate ($/1000 gal) | 1.54
FAX Number |  | Maximum flow rate to the 8" x 40" element, QI, max (gpm) | 80 | 2: Flow rates and pressures may need to be adjusted in order to obtain the desired operating conditions. | [8 empty] | SDI |  |  |  | Bromide | mg/L | 170 | 170 | 170 | 0 | 1999-03-24 | 10:00 | 20.5 | 24 | 60 | 61 | 272 | 6.93 | 3.49 | 10.42 | 0.18779 | 0.66507 | 25.1036 | 15.8174 | 16.1004 | 0 | 0 | 0 | 0 | 60.5 | 0.26612 | 1999-03-25 | 11:00 | 24 | 24 | 60 | 58 | 272 | 5.87 | 2.53 |  | 8.4 | 0.18779 | 0.69881 | 31.381 | 13.398 | 13.6377 | 621.004 | 168.0852 | 611.2296 | 4.4803 | 54.5197 | 0.25014 | 7.2 | 7.2 | 7.4 | 125 | 306 | 620 | 720.9684 | -16.2852 | 58.9491 | 714.5376 | 82.5062 | BMRL | 0.17 | 0.517 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Turbidity | ntu | 0.077 | 0.08 | 0.0785 | 3.8217 | 0.15 | 0.31398 | -109.3226 | 48.1848 | 0.31151 | 74.8003 | Turbidity | ntu | 0.06 | 0.199 | 0.76385 | -283.8423 | 60.396 | 0.75823 | 92.0868 | Turbidity | ntu | 0.06 | 0.186 | 0.23941 | -28.716 | 60.396 | 0.23857 | 74.8503 | Turbidity | ntu | 0.07 | 0.172 | 0.18479 | -7.4353 | 53.7954 | 0.18424 | 62.0067 | Bromidep, ug/L | 77.5 | 100 | 81 | 78 | Bromidep, ug/L | 77.5 | 100 | 81 | 78 | Modifications to Existing Plant (% of construction costs) | 20
E-Mail Address (optional) |  | Minimum flow rate to the 8" x 40" element, QI, min (gpm) | 20 | [9 empty] | MFI |  |  |  | SDS-Cl2 dose | mg/L | 6.5 | 6.5 | 6.5 | 0 | 1999-03-24 | 10:30 | 21 | 24 | 59 | 58 | 272 | 6.87 | 3.25 | 10.12 | 0.18779 | 0.67885 | 25.8775 | 15.6804 | 15.961 | 0 | 0 | 0 | 0 | 58.5 | 0.27284 | 1999-03-25 | 12:00 | 25 | 24 | 60 | 58 | 272 | 5.87 | 2.46 |  | 8.33 | 0.18779 | 0.70468 | 31.6531 | 13.398 | 13.6377 | 626.476 | 169.5663 | 616.6155 | 4.5198 | 54.4802 | 0.25032 | 7.2 | 7.2 | 7.4 | 146 | 306 | 592 | 682.7093 | -15.3225 | 52.0525 | 676.918 | 78.4317 | BMRL | 0.169 | 0.534 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Ammonia | mg NH3-N / L | 0.21 | 0.24 | 0.225 | 13.3333 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.15 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.18 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | Ammonia | mg NH3-N / L | 0.12 | NA | #DIV/0! | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217 | AlkF, mg/L CaCO3 | 217 | 217 | 217 | 217
|  | Total width of all membrane envelopes in the 8" x 40" element, w (ft) | 58.2011 | [9 empty] | MPFI | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | SDS-Free Cl2 residual | mg/L | 0.91 | 0.84 | 0.875 | 8 | 1999-03-24 | 11:00 | 21.5 | 24 | 59 | 58 | 272 | 6.87 | 3.25 | 10.12 | 0.18779 | 0.67885 | 25.8775 | 15.6804 | 15.961 | 0 | 0 | 0 | 0 | 58.5 | 0.27284 | 1999-03-25 | 13:00 | 26 | 24 | 60 | 58 | 272 | 5.86 | 2.45 |  | 8.31 | 0.18779 | 0.70517 | 31.7316 | 13.3751 | 13.6145 | 626.9327 | 169.6945 | 617.0819 | 4.5231 | 54.4769 | 0.24991 | 7.2 | 7.2 | 7.3 | 140 | 306 | 508 | 697.9571 | -37.3931 | 54.023 | 691.9468 | 79.7672 | BMRL | 0.171 | 0.544 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Total organic carbon | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | 14.5 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Total organic carbon | mg/L | BMRL | 31 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 9.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Total organic carbon | mg/L | BMRL | 6.7 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | Alkp, mg/L CaCO3 | 99 | 118 | 100 | 90 | Alkp, mg/L CaCO3 | 99 | 118 | 100 | 90
Plant Name | Broward County District 2A Water Treatment Plant | Feed spacer thickness in the 8" x 40" element, T (ft) | 0.0025833 | [10 empty] | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | SDS-Cl2 demand | mg/L | 5.59 | 5.66 | 5.625 | 1.2444 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-25 | 14:30 | 27.5 | 24 | 60 | 58 | 272 | 5.87 | 2.46 |  | 8.33 | 0.18779 | 0.70468 | 31.6531 | 13.398 | 13.6377 | 626.476 | 169.5663 | 616.6155 | 4.5198 | 54.4802 | 0.25032 | 7.2 | 7.3 | 7.3 | 133 | 306 | 454 | 713.7297 | -57.2092 | 56.3218 | 707.4633 | 81.2004 | BMRL | 0.172 | 0.541 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | UV254 | cm-1 | BMRL | BMRL | #DIV/0! | #VALUE! | 0.469 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | UV254 | cm-1 | 0.009 | 0.954 | 1.1359 | -19.0695 | 94.2122 | 1.1269 | 99.2014 | UV254 | cm-1 | BMRL | 0.316 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | UV254 | cm-1 | BMRL | 0.237 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | T-HdF, mg/L CaCO3 | 252 | 252 | 252 | 252 | T-HdF, mg/L CaCO3 | 252 | 252 | 252 | 252
Treatment Plant Category | Conventional Filtration | [12 empty] | is to list the pretreatment processes used in this particular RBSMT run. |  |  | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-25 | 15:30 | 28.5 | 24 | 60 | 58 | 272 | 5.93 | 2.43 |  | 8.36 | 0.18779 | 0.70933 | 31.5359 | 13.5349 | 13.7771 | 630.9176 | 170.7404 | 620.885 | 4.5516 | 54.4484 | 0.25303 | 7.2 | 7.3 | 7.3 | 131 | 305 | 490 | 727.8971 | -48.5504 | 56.9787 | 721.3905 | 81.8406 | BMRL | 0.173 | 0.542 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SUVA | L/(mg*m) | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 3.2345 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.0774 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.3617 | --- | --- | --- | --- | --- | SUVA | L/(mg*m) | #VALUE! | 3.5373 | --- | --- | --- | --- | --- | T-Hdp, mg/L CaCO3 | 67 | 104 | 66 | 60 | T-Hdp, mg/L CaCO3 | 67 | 104 | 66 | 60
Process Train Name | Lime softening and conventional filtration | Additional Information | [14 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-25 | 16:30 | 29.5 | 24 | 60 | 58 | 272 | 5.93 | 2.43 |  | 8.36 | 0.18779 | 0.70933 | 31.5359 | 13.5349 | 13.7771 | 630.9176 | 170.7404 | 620.885 | 4.5516 | 54.4484 | 0.25303 | 7.2 | 7.2 | 7.3 | 135 | 306 | 495 | 718.1358 | -45.0779 | 55.665 | 711.7792 | 81.0334 | BMRL | 0.172 | 0.543 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | Bromide | mg/L | 78 | 77 | 77.5 | 1.2903 | --- | 375.8871 | --- | 54.4118 | 372.754 | 79.2088 | Bromide | mg/L | 100 | --- | 638.4615 | --- | 41.1765 | 634.1644 | 84.2312 | Bromide | mg/L | 81 | --- | 255.5098 | --- | 52.3529 | 254.6927 | 68.197 | Bromide | mg/L | 78 | --- | 207.5775 | --- | 54.1176 | 206.9616 | 62.3119 | Ca-HdF, mg/L CaCO3 | 237 | 237 | 237 | 237 | Ca-HdF, mg/L CaCO3 | 237 | 237 | 237 | 237
ICR Treatment Plant Identification Number | 293 | Design cross-flow velocity (fps) | 1 | [13 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-25 | 17:30 | 30.5 | 24 | 60 | 58 | 272 | 5.82 | 2.4 |  | 8.22 | 0.18779 | 0.70803 | 32.09 | 13.2838 | 13.5215 | 629.6043 | 170.4364 | 619.7795 | 4.5426 | 54.4574 | 0.2483 | 7.2 | 7.2 | 7.3 | 154 | 306 | 529 | 669.4625 | -26.5525 | 49.4253 | 663.9478 | 76.8054 | BMRL | 0.169 | 0.548 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 dose | mg/L | 3.5 | 3.5 | 3.5 | 0 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | SDS-Cl2 dose | mg/L | 3.5 | --- | --- | --- | --- | --- | --- | Ca-Hdp, mg/L CaCO3 | 58 | 96 | 60 | 52 | Ca-Hdp, mg/L CaCO3 | 58 | 96 | 60 | 52
PWSID Number of Plant (if assigned) |  | Required influent flow to permeate flow rate ratio, QI:Qp | 6:1 minimum | [13 empty] | SDS-TOX | mg Cl- /L | 535 | 475 | 505 | 11.8812 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-25 | 18:30 | 31.5 | 24 | 60 | 58 | 272 | 5.97 | 2.46 |  | 8.43 | 0.18779 | 0.70819 | 31.2657 | 13.6262 | 13.87 | 629.855 | 170.4341 | 619.7714 | 4.5438 | 54.4562 | 0.2547 | 7.2 | 7.2 | 7.3 | 157 | 306 | 535 | 662.4573 | -23.8238 | 48.4401 | 656.9103 | 76.1002 | BMRL | 0.169 | 0.549 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Free Cl2 residual | mg/L | 1.05 | 1.05 | 1.05 | 0 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.45 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.48 | --- | --- | --- | --- | --- | --- | SDS-Free Cl2 residual | mg/L | 1.6 | --- | --- | --- | --- | --- | ---
Historical Minimum Water Temperature (oC) | 24.5 | Maximum element recovery (%) | 17 | [9 empty] | 1: Only those foulants and fouling indices relevant to the water being tested need to |  |  |  | SDS-CHCl3 | mg/L | 140 | 110 | 125 | 24 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 8:30 | 45.5 | 24 | 60 | 58 | 272 | 5.73 | 2.07 |  | 7.8 | 0.18779 | 0.73462 | 33.8718 | 13.0784 | 13.3124 | 655.8304 | 177.5796 | 645.7554 | 4.7321 | 54.2679 | 0.24531 | 7.3 | 7.2 | 7.4 | 118 | 307 | 449 | 820.7536 | -82.7959 | 61.2479 | 813.3515 | 85.4921 | BMRL | 0.17 | 0.576 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Cl2 demand | mg/L | 2.45 | 2.45 | 2.45 | 0 | --- | 12.6919 | --- | 56.4444 | 12.5844 | 80.5314 | SDS-Cl2 demand | mg/L | 2.05 | --- | 29.55 | --- | 63.5556 | 29.3305 | 93.0107 | SDS-Cl2 demand | mg/L | 2.02 | --- | 9.0886 | --- | 64.0889 | 9.0555 | 77.6932 | SDS-Cl2 demand | mg/L | 1.9 | --- | 7.1465 | --- | 66.2222 | 7.1215 | 73.3204 | Blended Water Quality if THM4 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if THM4 Controls the Blend Ratio
Historical Average Water Temperature (oC) | 26 | Variability of design flux (%) | 15 | [9 empty] | be evaluated. Additional foulants and indices can be listed in the blank rows. |  |  |  | SDS-BDCM | mg/L | 49 | 48 | 48.5 | 2.0619 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 9:15 | 46.25 | 24 | 60 | 58 | 272 | 5.72 | 3.1 |  | 8.82 | 0.18779 | 0.64853 | 29.839 | 13.0556 | 13.2892 | 577.7106 | 156.4313 | 568.8513 | 4.1685 | 54.8315 | 0.24236 | 7.3 | 7.2 | 7.4 | 134 | 307 | 368 | 619.1 | -68.2337 | 55.9934 | 613.9993 | 78.1759 | BMRL | 0.172 | 0.554 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination temp. | oC | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | SDS-Chlorination temp. | oC | 24 | --- | --- | --- | --- | --- | --- | Qp/QT (THM4), % | 65.4338 | 67.3195 | 65.5586 | 65.3094 | Qp/QT (THM4), % | 85.015 | 87.465 | 85.1771 | 84.8534
State Approved Plant Capacity (MGD) | 30 | Rejection of reference solute and conditions of test | 1,000 mg/L MgSO4 100 psi | [13 empty] | SDS-DBCM | mg/L | 18 | 18 | 18 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 10:00 | 47 | 24 | 60 | 58 | 272 | 5.67 | 2.71 |  | 8.38 | 0.18779 | 0.67661 | 31.4582 | 12.9415 | 13.173 | 601.0357 | 162.7696 | 591.8997 | 4.337 | 54.663 | 0.24099 | 7.3 | 7.2 | 7.4 | 142 | 306 | 457 | 644.4908 | -41.0264 | 53.3662 | 639.2534 | 77.7866 | BMRL | 0.173 | 0.532 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Chlorination pH | --- | 9 | 9 | 9 | 0 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-Chlorination pH | --- | 9 | --- | --- | --- | --- | --- | --- | SDS-THM4b, ug/L | 72 | 72 | 72 | 72 | SDS-THM4b, ug/L | 36 | 36 | 36 | 36
|  | (e.g., solute type and concentration) | 25 C, pH=7.5 | [13 empty] | SDS-CHBr3 | mg/L | 0.8 | 0.8 | 0.8 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 10:45 | 47.75 | 24 | 60 | 58 | 281 | 5.68 | 2.71 |  | 8.39 | 0.19401 | 0.677 | 32.4923 | 12.9643 | 13.1963 | 601.2668 | 162.9088 | 592.4061 | 4.3393 | 54.6607 | 0.24142 | 7.4 | 7.3 | 7.3 | 133 | 305 | 598 | 663.9539 | -11.0291 | 56.3218 | 658.5877 | 79.8053 | BMRL | 0.172 | 0.521 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-Incubation time | hours | 24 | 24 | 24 | 0 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-Incubation time | hours | 24 | --- | --- | --- | --- | --- | --- | SDS-HAA5b, ug/L | 19.4089 | 19.1579 | 19.3389 | 19.4787 | SDS-HAA5b, ug/L | 8.4141 | 8.088 | 8.3231 | 8.5048
|  | Variability of rejection of reference solute (%) | 95% rejection minimum | [13 empty] | SDS-THM4 | mg/L | 207.8 | 176.8 | 192.3 | 16.1206 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 11:15 | 48.25 | 24 | 60 | 58 | 281 | 5.87 | 2.67 |  | 8.54 | 0.19401 | 0.68735 | 31.904 | 13.398 | 13.6377 | 610.4822 | 165.3224 | 601.183 | 4.4051 | 54.5949 | 0.2498 | 7.3 | 7.3 | 7.3 | 145 | 306 | 521 | 655.161 | -25.7507 | 52.381 | 649.8325 | 77.6866 | BMRL | 0.173 | 0.534 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TOX | mg Cl- /L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOX | mg Cl- /L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Standard testing recovery (%) | 10 | [13 empty] | SDS-MCAA* | mg/L | BMRL | 3.1 | 3.1 | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 14:00 | 51 | 24 | 60 | 58 | 281 | 5.6 | 2.43 |  | 8.03 | 0.19401 | 0.69738 | 33.9938 | 12.7817 | 13.0104 | 619.3979 | 167.8568 | 610.3992 | 4.4704 | 54.5296 | 0.23859 | 7.4 | 7.4 | 7.7 | 128 | 306 | 610 | 711.249 | -16.5982 | 57.9639 | 705.4372 | 81.8552 | BMRL | 0.172 | 0.527 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHCl3 | mg/L | 1.7 | 1.3 | 1.5 | 26.6667 | --- | 399.8871 | --- | 98.8 | 395.704 | 99.6209 | SDS-CHCl3 | mg/L | 1.6 | --- | 950.8308 | --- | 98.72 | 943.2556 | 99.8304 | SDS-CHCl3 | mg/L | 1.3 | --- | 243.849 | --- | 98.96 | 242.7134 | 99.4644 | SDS-CHCl3 | mg/L | 1.3 | --- | 175.5254 | --- | 98.96 | 174.6973 | 99.2559 | SDS-CDb, mg/L | 3.5475 | 3.2183 | 3.2616 | 3.1922 | SDS-CDb, mg/L | 2.9258 | 2.4981 | 2.5544 | 2.4642
|  | Standard testing pH | 7.5 | [13 empty] | SDS-DCAA* | mg/L | 29 | 31 | 30 | 6.6667 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 15:00 | 52 | 24 | 60 | 58 | 281 | 5.6 | 4.35 |  | 9.95 | 0.19401 | 0.56281 | 27.2412 | 12.7817 | 13.0104 | 516.3568 | 139.9327 | 508.8551 | 3.7267 | 55.2733 | 0.23538 | 7.5 | 7.7 | 7.8 | 131 | 305 | 634 | 527.8563 | 16.7419 | 56.9787 | 523.9019 | 74.9953 | BMRL | 0.172 | 0.524 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BDCM | mg/L | 1.9 | 1.8 | 1.85 | 5.4054 | --- | 152.3339 | --- | 96.1856 | 150.7538 | 98.7728 | SDS-BDCM | mg/L | 2.4 | --- | 357.0154 | --- | 95.0515 | 354.1854 | 99.3224 | SDS-BDCM | mg/L | 1.8 | --- | 93.3686 | --- | 96.2887 | 92.9399 | 98.0633 | SDS-BDCM | mg/L | 1.9 | --- | 67.5338 | --- | 96.0825 | 67.2219 | 97.1735 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
|  | Acceptable range of operating pressures | 600 maximum (< 300 prefered) | [13 empty] | SDS-TCAA* | mg/L | 16 | 27 | 21.5 | 51.1628 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-26 | 16:30 | 53.5 | 24 | 60 | 58 | 281 | 5.6 | 2.42 |  | 8.02 | 0.19401 | 0.69825 | 34.0374 | 12.7817 | 13.0104 | 620.1976 | 168.0735 | 611.1873 | 4.4762 | 54.5238 | 0.23862 | 7.5 | 7.7 | 7.9 | 135 | 305 | 621 | 696.7314 | -12.1951 | 55.665 | 691.1341 | 80.4669 | BMRL | 0.173 | 0.541 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBCM | mg/L | 3.1 | 3.1 | 3.1 | 0 | --- | 51.1645 | --- | 82.7778 | 50.6598 | 93.8808 | SDS-DBCM | mg/L | 5.2 | --- | 103.6615 | --- | 71.1111 | 102.8758 | 94.9454 | SDS-DBCM | mg/L | 3.4 | --- | 32.0275 | --- | 81.1111 | 31.8934 | 89.3395 | SDS-DBCM | mg/L | 3.1 | --- | 24.0859 | --- | 82.7778 | 23.9862 | 87.0759 | UV254 b, cm-1 | #DIV/0! | 0.056877 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.027364 | #VALUE! | #VALUE!
|  | Acceptable range of operating pH values | 2.5 - 11.0 | [13 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 9:00 | 70 | 24 | 60 | 58 | 281 | 5.66 | 2.4 |  | 8.06 | 0.19401 | 0.70223 | 33.8635 | 12.9186 | 13.1498 | 623.9221 | 169.056 | 614.76 | 4.5029 | 54.4971 | 0.24129 | 7.5 | 7.7 | 7.8 | 143 | 306 | 553 | 685.3708 | -23.9369 | 53.0378 | 679.9085 | 78.9678 | BMRL | 0.17 | 0.539 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CHBr3 | mg/L | 2 | 2 | 2 | 0 | --- | -1.871 | --- | -150 | -1.8303 | 209.2704 | SDS-CHBr3 | mg/L | 4.4 | --- | -23.2923 | --- | -450 | -23.0713 | 119.0713 | SDS-CHBr3 | mg/L | 2.3 | --- | -0.64118 | --- | -187.5 | -0.62741 | 466.5889 | SDS-CHBr3 | mg/L | 1.8 | --- | 0.39155 | --- | -125 | 0.39824 | -351.9854 | Bromideb, ug/L | 109.4738 | 122.8763 | 111.6529 | 109.9153 | Bromideb, ug/L | 91.3612 | 108.7745 | 94.1924 | 91.9349
|  | Typical pressure drop across a single element (psi) | < 5 (10 maximum) | [13 empty] | SDS-DBAA* | mg/L | 3.1 | 3.1 | 3.1 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 10:00 | 71 | 24 | 60 | 58 | 281 | 5.66 | 2.38 |  | 8.04 | 0.19401 | 0.70398 | 33.9502 | 12.9186 | 13.1498 | 625.5544 | 169.4983 | 616.3684 | 4.5146 | 54.4854 | 0.24135 | 7.5 | 7.6 | 7.7 | 145 | 306 | 543 | 683.8151 | -25.9328 | 52.381 | 678.3886 | 78.6258 | BMRL | 0.171 | 0.532 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-THM4 | mg/L | 8.7 | 8.2 | 8.45 | 5.9172 | --- | 601.5145 | --- | 95.6058 | 595.2873 | 98.5805 | SDS-THM4 | mg/L | 13.6 | --- | 1388.2154 | --- | 92.9277 | 1377.2455 | 99.0125 | SDS-THM4 | mg/L | 8.8 | --- | 368.6039 | --- | 95.4238 | 366.9193 | 97.6017 | SDS-THM4 | mg/L | 8.1 | --- | 267.5366 | --- | 95.7878 | 266.3036 | 96.9584 | Alkb, mg/L CaCO3 | 139.7881 | 150.3537 | 140.2965 | 134.057 | Alkb, mg/L CaCO3 | 116.6823 | 130.4096 | 117.3428 | 109.2362
|  | Maximum permissible SDI | 5 (< 3 prefered) | [13 empty] | SDS-BCAA* | mg/L | 11 | 11 | 11 | 0 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 11:00 | 72 | 24 | 60 | 58 | 281 | 5.66 | 2.4 |  | 8.06 | 0.19401 | 0.70223 | 33.8635 | 12.9186 | 13.1498 | 623.9221 | 169.056 | 614.76 | 4.5029 | 54.4971 | 0.24129 | 7.5 | 7.6 | 7.7 | 168 | 306 | 521 | 626.4125 | -20.2327 | 44.8276 | 621.7957 | 72.9815 | BMRL | 0.17 | 0.542 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-MCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | T-Hdb, mg/L CaCO3 | 130.9475 | 152.3671 | 130.061 | 126.6059 | T-Hdb, mg/L CaCO3 | 94.7223 | 122.5518 | 93.5706 | 89.0814
|  | Maximum permissible turbidity (ntu) | 1 (0.2 prefered) | [13 empty] | SDS-TBAA | mg/L | NR | BMRL | #DIV/0! | #VALUE! | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 12:00 | 73 | 24 | 60 | 58 | 281 | 5.66 | 2.38 |  | 8.04 | 0.19401 | 0.70398 | 33.9502 | 12.9186 | 13.1498 | 625.5544 | 169.4983 | 616.3684 | 4.5146 | 54.4854 | 0.24135 | 7.5 | 7.6 | 7.7 | 158 | 306 | 512 | 652.8992 | -27.5194 | 48.1117 | 647.9149 | 75.6141 | BMRL | 0.171 | 0.542 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Ca-Hdb, mg/L CaCO3 | 119.8735 | 142.0795 | 120.9613 | 116.1775 | Ca-Hdb, mg/L CaCO3 | 84.8232 | 113.6743 | 86.2365 | 80.0212
|  | Chlorine/oxidant tolerance (e.g., < 0.1 mg/L for extended use, etc.) | [14 empty] | SDS-CDBAA | mg/L | 2.4 | 3 | 2.7 | 22.2222 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 13:00 | 74 | 24 | 60 | 58 | 281 | 5.71 | 2.46 |  | 8.17 | 0.19401 | 0.6989 | 33.3941 | 13.0328 | 13.266 | 620.8611 | 168.2043 | 611.663 | 4.4806 | 54.5194 | 0.24333 | 7.5 | 7.6 | 7.7 | 151 | 306 | 509 | 660.7947 | -29.8221 | 50.4105 | 655.6151 | 76.9682 | BMRL | 0.17 | 0.538 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE!
|  | 1: All of the information requested in this field may not be available, but values for all Design | [14 empty] | SDS-DCBAA | mg/L | 6.6 | 11 | 8.8 | 50 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 14:00 | 75 | 24 | 60 | 58 | 281 | 5.66 | 2.4 |  | 8.06 | 0.19401 | 0.70223 | 33.8635 | 12.9186 | 13.1498 | 623.9221 | 169.056 | 614.76 | 4.5029 | 54.4971 | 0.24129 | 7.5 | 7.5 | 7.6 | 133 | 306 | 484 | 708.9542 | -46.4781 | 56.3218 | 703.1536 | 81.0852 | BMRL | 0.171 | 0.543 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-MBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-MBAA* | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0!
|  | Parameters must be entered in cells E14:E23, since these parameters are used in calculations. | [14 empty] | SDS-HAA5 | mg/L | 48.1 | 64.2 | 56.15 | 28.6732 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 15:00 | 76 | 24 | 60 | 58 | 281 | 5.66 | 2.46 |  | 8.12 | 0.19401 | 0.69704 | 33.6059 | 12.9186 | 13.1498 | 619.1231 | 167.7557 | 610.0315 | 4.4682 | 54.5318 | 0.24114 | 7.5 | 7.6 | 7.7 | 130 | 306 | 479 | 705.9919 | -47.3887 | 57.3071 | 700.191 | 81.4336 | BMRL | 0.17 | 0.542 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DBAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DBAA* | mg/L | 1.2 | --- | 15.8154 | --- | 61.2903 | 15.6987 | 92.3561 | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DBAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Blended Water Quality if HAA5 Controls the Blend Ratio |  |  |  |  | Blended Water Quality if HAA5 Controls the Blend Ratio
[17 empty] | SDS-HAA6 | mg/L | 59.1 | 75.2 | 67.15 | 23.9762 | [9 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 16:00 | 77 | 24 | 60 | 58 | 281 | 5.73 | 2.36 |  | 8.09 | 0.19401 | 0.70828 | 33.7342 | 13.0784 | 13.3124 | 629.6572 | 170.5784 | 620.2959 | 4.544 | 54.456 | 0.24446 | 7.6 | 7.5 | 7.8 | 135 | 307 | 509 | 716.0403 | -40.6759 | 55.665 | 710.1161 | 80.989 | BMRL | 0.171 | 0.542 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-BCAA* | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-BCAA* | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | Qp/QT (HAA5), % | 3.829 | 3.9126 | 3.829 | 3.829 | Qp/QT (HAA5), % | 51.9145 | 53.0482 | 51.9145 | 51.9145
[17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 16:45 | 77.75 | 24 | 60 | 58 | 272 | 5.5 | 0.65 |  | 6.15 | 0.18779 | 0.89431 | 43.2276 | 12.5535 | 12.7781 | 875.0096 | 237.0761 | 862.1103 | 6.3148 | 52.6852 | 0.24254 | 7.7 | 7.6 | 7.8 | 161 | 301 | 579 | 1518.7308 | -162.3024 | 47.1264 | 1505.0037 | 89.3024 | BMRL | 0.171 | 0.541 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-TBAA | mg/L | NR | NR | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | BMRL | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NR | --- | #VALUE! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-THM4b, ug/L | 185.2603 | 185.3081 | 185.2737 | 185.2469 | SDS-THM4b, ug/L | 96.8552 | 97.5028 | 97.0369 | 96.6735
[17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 17:45 | 78.75 | 24 | 60 | 58 | 272 | 5.6 | 0.68 |  | 6.28 | 0.18779 | 0.89172 | 42.3121 | 12.7817 | 13.0104 | 870.4533 | 235.7771 | 857.3864 | 6.2814 | 52.7186 | 0.24679 | 7.7 | 7.6 | 7.8 | 199 | 306 | 649 | 1173.3235 | -80.7894 | 34.647 | 1163.2937 | 82.8934 | BMRL | 0.17 | 0.546 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-CDBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-CDBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-HAA5b, ug/L | 54 | 54 | 54 | 54 | SDS-HAA5b, ug/L | 27 | 27 | 27 | 27
[17 empty] | should be reported if measured. | [14 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 1999-03-27 | 18:30 | 79.5 | 24 | 60 | 58 | 272 | 5.35 | 0.57 |  | 5.92 | 0.18779 | 0.90372 | 44.9459 | 12.2111 | 12.4296 | 892.3386 | 241.8705 | 879.5445 | 6.4407 | 52.5593 | 0.23649 | 7.7 | 7.6 | 7.8 | 189 | 306 | 654 | 1388.5789 | -112.3209 | 37.931 | 1376.7816 | 86.2723 | BMRL | 0.17 | 0.674 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-DCBAA | mg/L | BMRL | BMRL | #DIV/0! | #VALUE! | --- | #DIV/0! | --- | #DIV/0! | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-DCBAA | mg/L | BMRL | --- | #VALUE! | --- | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | SDS-TOXb, ug Cl- /L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-27 | 19:00 | 80 | 24 | 60 | 58 | 272 | 5.2 | 0.68 |  | 5.88 | 0.18779 | 0.88435 | 45.2585 | 11.8687 | 12.0811 | 856.6589 | 232.2946 | 844.7226 | 6.184 | 52.816 | 0.22874 | 7.7 | 7.6 | 7.7 | 200 | 305 | 675 | 1103.6176 | -63.4989 | 34.3186 | 1094.9801 | 81.7348 | BMRL | 0.171 | 0.764 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA5 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 181.129 | --- | 100 | 179.2272 | 100 | SDS-HAA5 | mg/L | 1.2 | --- | 423.8923 | --- | 97.8629 | 420.5191 | 99.7146 | SDS-HAA5 | mg/L | 0 | --- | 110.098 | --- | 100 | 109.5826 | 100 | SDS-HAA5 | mg/L | 0 | --- | 79.0845 | --- | 100 | 78.7087 | 100 | SDS-CDb, mg/L | 5.5034 | 5.4851 | 5.487 | 5.4824 | SDS-CDb, mg/L | 3.9767 | 3.7285 | 3.7535 | 3.6912
[44 empty] | 1999-03-27 | 19:30 | 80.5 | 24 | 60 | 58 | 272 | 5.05 | 0.62 |  | 5.67 | 0.18779 | 0.89065 | 46.9718 | 11.5264 | 11.7326 | 867.6232 | 235.3641 | 855.8845 | 6.2639 | 52.7361 | 0.22248 | 7.7 | 7.6 | 7.8 | 251 | 306 | 812 | 740.2661 | 8.8342 | 17.5698 | 735.7242 | 65.884 | BMRL | 0.172 | 0.903 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | SDS-HAA6 | mg/L | 0 | 0 | 0 | #DIV/0! | --- | 216.6129 | --- | 100 | 214.3385 | 100 | SDS-HAA6 | mg/L | 1.2 | --- | 508.5077 | --- | 98.213 | 504.4592 | 99.7621 | SDS-HAA6 | mg/L | 0 | --- | 131.6667 | --- | 100 | 131.0502 | 100 | SDS-HAA6 | mg/L | 0 | --- | 94.5775 | --- | 100 | 94.128 | 100 | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE! | TOCb, mg/L | #DIV/0! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-27 | 20:00 | 81 | 24 | 60 | 58 | 272 | 5.11 | 0.58 |  | 5.69 | 0.18779 | 0.89807 | 46.8032 | 11.6633 | 11.872 | 881.2906 | 239.0326 | 869.2247 | 6.3623 | 52.6377 | 0.22554 | 7.7 | 7.6 | 7.8 | 224 | 306 | 787 | 1013.7328 | -28.8098 | 26.4368 | 1006.3145 | 77.7406 | BMRL | 0.172 | 0.943 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [8 empty] | UV254 b, cm-1 | #DIV/0! | 0.14977 | #VALUE! | #VALUE! | UV254 b, cm-1 | #DIV/0! | 0.077784 | #VALUE! | #VALUE!
[44 empty] | 1999-03-27 | 20:30 | 81.5 | 24 | 60 | 58 | 272 | 5.07 | 0.7 |  | 5.77 | 0.18779 | 0.87868 | 46.1404 | 11.572 | 11.7791 | 846.6131 | 229.652 | 835.1131 | 6.1121 | 52.8879 | 0.22272 | 7.6 | 7.6 | 7.8 | 218 | 305 | 875 | 931.0071 | -6.4008 | 28.4072 | 924.362 | 76.4162 | BMRL | 0.171 | 0.998 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [8 empty] | Bromideb, ug/L | 166.4581 | 167.2611 | 166.5922 | 166.4773 | Bromideb, ug/L | 121.9791 | 132.8662 | 123.7961 | 122.2386
[44 empty] | 1999-03-27 | 21:00 | 82 | 24 | 60 | 58 | 272 | 5.07 | 0.66 |  | 5.73 | 0.18779 | 0.88482 | 46.4695 | 11.572 | 11.7791 | 857.2673 | 232.5421 | 845.6227 | 6.189 | 52.811 | 0.22304 | 7.7 | 7.6 | 7.8 | 231 | 306 | 846 | 869.1136 | -2.7321 | 24.1379 | 863.1665 | 73.2381 | BMRL | 0.17 | 1.037 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Alkb, mg/L CaCO3 | 212.4817 | 213.1265 | 212.52 | 212.1371 | Alkb, mg/L CaCO3 | 155.7409 | 164.4823 | 156.26 | 151.0686
[44 empty] | 1999-03-28 | 11:00 | 96 | 24 | 60 | 58 | 272 | 2.55 | 0.44 |  | 2.99 | 0.18779 | 0.85284 | 89.9699 | 5.8202 | 5.9244 | 801.1331 | 218.8064 | 795.6738 | 5.796 | 53.204 | 0.11135 | 7.7 | 7.6 | 7.8 | 309 | 305 | 699 | 278.4205 | 60.1687 | -1.4778 | 278.5638 | -10.9261 | BMRL | 0.171 | 1.024 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | T-Hdb, mg/L CaCO3 | 244.9163 | 246.2093 | 244.878 | 244.6483 | T-Hdb, mg/L CaCO3 | 155.9581 | 173.4886 | 155.439 | 152.3241
[44 empty] | 1999-03-28 | 11:30 | 96.5 | 24 | 60 | 58 | 272 | 2.6 | 0.6 |  | 3.2 | 0.18779 | 0.8125 | 84 | 5.9344 | 6.0405 | 743.8058 | 203.1217 | 738.6375 | 5.381 | 53.619 | 0.11266 | 7.7 | 7.6 | 7.8 | 308 | 305 | 689 | 289.3333 | 58.0068 | -1.1494 | 289.4225 | -6.4188 | BMRL | 0.171 | 1.003 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Ca-Hdb, mg/L CaCO3 | 230.146 | 231.4832 | 230.2226 | 229.9163 | Ca-Hdb, mg/L CaCO3 | 144.073 | 162.202 | 145.1113 | 140.9581
[44 empty] | 1999-03-28 | 12:30 | 97.5 | 24 | 60 | 58 | 272 | 2.53 | 2.87 |  | 5.4 | 0.18779 | 0.46852 | 49.3704 | 5.7746 | 5.8779 | 461.7479 | 126.1199 | 458.6261 | 3.3407 | 55.6593 | 0.10561 | 7.7 | 7.6 | 7.7 | 208 | 306 | 598 | 389.5679 | 34.8549 | 31.6913 | 388.7235 | 46.4915 | BMRL | 0.171 | 0.93 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Notes: |  |  |  |  | Notes:
[44 empty] | 1999-03-28 | 13:00 | 98 | 24 | 60 | 58 | 272 | 2.63 | 2.43 |  | 5.06 | 0.18779 | 0.51976 | 52.7549 | 6.0028 | 6.1102 | 489.4202 | 133.6422 | 485.9801 | 3.5406 | 55.4594 | 0.11018 | 7.6 | 7.6 | 7.7 | 213 | 306 | 545 | 403.5309 | 25.9576 | 30.0493 | 402.6097 | 47.0952 | BMRL | 0.17 | 0.764 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to |  |  |  |  | This spreadsheet uses the feed and permeate water quality parameters copied to the first block to
[44 empty] | 1999-03-28 | 13:30 | 98.5 | 24 | 60 | 58 | 272 | 2.61 | 2.49 |  | 5.1 | 0.18779 | 0.51176 | 52.3333 | 5.9572 | 6.0638 | 484.8831 | 132.4104 | 481.5009 | 3.5078 | 55.4922 | 0.10927 | 7.6 | 7.5 | 7.7 | 223 | 306 | 514 | 389.9277 | 24.1386 | 26.7652 | 389.1268 | 42.6922 | BMRL | 0.17 | 0.628 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | determine the percentage of total flow that must be treated by the membrane process to meet the |  |  |  |  | determine the percentage of total flow that must be treated by the membrane process to meet the
[44 empty] | 1999-03-28 | 14:00 | 99 | 24 | 60 | 58 | 272 | 2.67 | 2.8 |  | 5.47 | 0.18779 | 0.48812 | 48.7258 | 6.0941 | 6.2032 | 471.9797 | 128.8659 | 468.6116 | 3.4143 | 55.5857 | 0.1116 | 7.6 | 7.5 | 7.7 | 216 | 306 | 468 | 388.8911 | 16.9036 | 29.064 | 388.0425 | 44.336 | BMRL | 0.171 | 0.561 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Stage 1 DBP MCLs. |  |  |  |  | Stage 2 DBP MCLs.
[44 empty] | 1999-03-28 | 19:00 | 104 | 24 | 60 | 60 | 272 | 2.6 | 2.14 |  | 4.74 | 0.18779 | 0.54852 | 56.384 | 5.9344 | 6.0405 | 506.4281 | 138.2976 | 502.9093 | 3.6637 | 56.3363 | 0.10722 | 7.7 | 7.5 | 7.7 | 138 | 305 | 476 | 506.7897 | -6.4684 | 54.6798 | 505.0271 | 72.6747 | BMRL | 0.171 | 0.353 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | A 10% factor of safety has been applied all the MCLs. i.e., 72 / 54 mg/L for THM4 and HAA5. |  |  |  |  | A 10% factor of safety has been applied all the MCLs. i.e., 36 / 27 mg/L for THM4 and HAA5.
[44 empty] | 1999-03-28 | 19:30 | 104.5 | 24 | 61 | 59 | 281 | 2.63 | 3.16 |  | 5.79 | 0.19401 | 0.45423 | 47.532 | 6.0028 | 6.1102 | 454.5928 | 124.1603 | 451.5002 | 3.2889 | 56.7111 | 0.10774 | 7.7 | 7.6 | 7.8 | 136 | 305 | 469 | 444.7389 | 5.1729 | 55.3366 | 443.2941 | 69.3206 | BMRL | 0.171 | 0.35 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for |  |  |  |  | Since either THM4 or HAA5 can control the allowable blend ratio, the blend ratio is calculated for
[44 empty] | 1999-03-28 | 20:00 | 105 | 24 | 61 | 59 | 281 | 2.65 | 3.13 |  | 5.78 | 0.19401 | 0.45848 | 47.6159 | 6.0485 | 6.1567 | 456.7016 | 124.7298 | 453.5709 | 3.3041 | 56.6959 | 0.10859 | 7.7 | 7.6 | 7.8 | 135 | 305 | 457 | 448.0064 | 1.968 | 55.665 | 446.5305 | 69.7669 | BMRL | 0.171 | 0.344 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | both parameters and the maximum (Qp/QT) ratio controls the design. |  |  |  |  | both parameters and the maximum (Qp/QT) ratio controls the design.
[44 empty] | 1999-03-28 | 21:00 | 106 | 24 | 61 | 59 | 281 | 2.68 | 2.98 |  | 5.66 | 0.19401 | 0.4735 | 48.6466 | 6.117 | 6.2264 | 464.3122 | 126.7984 | 461.0932 | 3.359 | 56.641 | 0.10993 | 7.7 | 7.5 | 7.8 | 131 | 306 | 440 | 460.5336 | -4.6667 | 56.9787 | 458.9621 | 71.4573 | BMRL | 0.17 | 0.329 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio. |  |  |  |  | Qp/QT (THM4) is the permeate to total flow ratio for the case where THM4 controls the blend ratio.
[44 empty] | 1999-03-28 | 22:00 | 107 | 24 | 61 | 59 | 281 | 2.7 | 2.9 |  | 5.6 | 0.19401 | 0.48214 | 49.1786 | 6.1626 | 6.2729 | 468.8092 | 128.0198 | 465.5347 | 3.3915 | 56.6085 | 0.11081 | 7.8 | 7.6 | 7.9 | 134 | 306 | 432 | 463.2414 | -7.2318 | 55.9934 | 461.6596 | 70.9743 | BMRL | 0.171 | 0.335 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio. |  |  |  |  | Qp/QT (HAA5) is the permeate to total flow ratio for the case where HAA5 controls the blend ratio.
[44 empty] | 1999-03-28 | 23:00 | 108 | 24 | 61 | 59 | 281 | 2.68 | 2.85 |  | 5.53 | 0.19401 | 0.48463 | 49.8137 | 6.117 | 6.2264 | 470.1124 | 128.3824 | 466.8532 | 3.401 | 56.599 | 0.11001 | 7.7 | 7.5 | 7.8 | 129 | 305 | 436 | 469.5316 | -7.6907 | 57.6355 | 467.9077 | 72.4305 | BMRL | 0.17 | 0.321 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | The subscript "b" refers to the blended water quality for a given blend ratio. |  |  |  |  | The subscript "b" refers to the blended water quality for a given blend ratio.
[44 empty] | 1999-03-29 | 9:00 | 118 | 24 | 61 | 60 | 281 | 2.56 | 2.38 |  | 4.94 | 0.19401 | 0.51822 | 55.8826 | 5.8431 | 5.9476 | 488.4933 | 133.4438 | 485.2586 | 3.5343 | 56.9657 | 0.10441 | 7.7 | 7.5 | 7.8 | 132 | 304 | 457 | 490.0462 | -7.2311 | 56.6502 | 488.4153 | 72.9738 | BMRL | 0.166 | 0.355 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL. |  |  |  |  | If the permeate quality does not meet the MCL, then the calculations are meaningless for that MCL.
[44 empty] | 1999-03-29 | 10:00 | 119 | 24 | 61 | 60 | 281 | 2.61 | 2.75 |  | 5.36 | 0.19401 | 0.48694 | 51.4254 | 5.9572 | 6.0638 | 471.3171 | 128.7349 | 468.1351 | 3.4099 | 57.0901 | 0.10621 | 7.7 | 7.5 | 7.8 | 128 | 304 | 450 | 472.0145 | -4.8921 | 57.9639 | 470.4169 | 72.7901 | BMRL | 0.164 | 0.331 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [47 empty] | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL. |  |  |  |  | If the feed water quality meets the MCL, then a negative ratio will be calculated for that MCL.
[44 empty] | 1999-03-29 | 11:00 | 120 | 24 | 61 | 60 | 281 | 2.66 | 2.7 |  | 5.36 | 0.19401 | 0.49627 | 51.4254 | 6.0713 | 6.1799 | 476.3292 | 130.0869 | 473.0516 | 3.446 | 57.054 | 0.10832 | 7.7 | 7.6 | 7.8 | 131 | 304 | 443 | 475.4296 | -7.3205 | 56.9787 | 473.7994 | 72.3512 | BMRL | 0.166 | 0.348 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 12:00 | 121 | 24 | 61 | 60 | 281 | 2.63 | 2.58 |  | 5.21 | 0.19401 | 0.5048 | 52.9347 | 6.0028 | 6.1102 | 480.9862 | 131.369 | 477.714 | 3.4798 | 57.0202 | 0.10716 | 7.7 | 7.5 | 7.9 | 127 | 304 | 441 | 485.4399 | -10.0771 | 58.2923 | 483.7625 | 73.7474 | BMRL | 0.166 | 0.33 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 14:00 | 123 | 24 | 61 | 60 | 281 | 2.63 | 2.49 |  | 5.12 | 0.19401 | 0.51367 | 53.8828 | 6.0028 | 6.1102 | 485.937 | 132.7212 | 482.6311 | 3.5156 | 56.9844 | 0.10723 | 7.8 | 7.5 | 7.8 | 128 | 304 | 457 | 490.9237 | -7.4231 | 57.9639 | 489.2253 | 73.8362 | BMRL | 0.164 | 0.351 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 15:30 | 124.5 | 24 | 61 | 60 | 281 | 2.7 | 2.48 |  | 5.18 | 0.19401 | 0.52124 | 53.2471 | 6.1626 | 6.2729 | 490.2588 | 133.8771 | 486.8345 | 3.5467 | 56.9533 | 0.11014 | 7.7 | 7.5 | 7.8 | 130 | 304 | 450 | 494.4798 | -9.8844 | 57.3071 | 492.7288 | 73.6163 | BMRL | 0.166 | 0.344 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 16:00 | 125 | 24 | 61 | 60 | 281 | 2.65 | 5.95 |  | 8.6 | 0.19401 | 0.30814 | 31.6744 | 6.0485 | 6.1567 | 392.3886 | 107.1653 | 389.6988 | 2.8388 | 57.6612 | 0.10677 | 7.6 | 7.7 | 7.7 | 126 | 304 | 412 | 384 | 6.7961 | 58.6207 | 382.7835 | 67.0832 | BMRL | 0.167 | 0.294 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 16:30 | 125.5 | 24 | 61 | 60 | 281 | 2.66 | 6.05 |  | 8.71 | 0.19401 | 0.3054 | 31.2618 | 6.0713 | 6.1799 | 391.3839 | 106.8881 | 388.6908 | 2.8315 | 57.6685 | 0.10716 | 7.6 | 7.7 | 7.8 | 122 | 304 | 389 | 384.7397 | 1.0952 | 59.9343 | 383.4961 | 68.1874 | BMRL | 0.166 | 0.253 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 17:00 | 126 | 24 | 61 | 60 | 281 | 2.68 | 6.67 |  | 9.35 | 0.19401 | 0.28663 | 29.0535 | 6.117 | 6.2264 | 384.6423 | 105.0414 | 381.9756 | 2.7827 | 57.7173 | 0.10788 | 7.7 | 7.7 | 7.8 | 117 | 304 | 374 | 379.8373 | -1.5608 | 61.5764 | 378.5839 | 69.0954 | BMRL | 0.167 | 0.244 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 17:30 | 126.5 | 24 | 61 | 60 | 281 | 2.69 | 6.66 |  | 9.35 | 0.19401 | 0.2877 | 29.0535 | 6.1398 | 6.2496 | 385.0214 | 105.1422 | 382.3421 | 2.7854 | 57.7146 | 0.10829 | 7.8 | 7.7 | 7.7 | 117 | 305 | 368 | 380.232 | -3.3239 | 61.5764 | 378.972 | 69.127 | BMRL | 0.167 | 0.236 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 18:00 | 127 | 24 | 61 | 60 | 281 | 2.7 | 6.6 |  | 9.3 | 0.19401 | 0.29032 | 29.2151 | 6.1626 | 6.2729 | 385.9526 | 105.3938 | 383.2568 | 2.7921 | 57.7079 | 0.1087 | 7.7 | 7.7 | 7.8 | 118 | 304 | 365 | 380.7955 | -4.3275 | 61.2479 | 379.5329 | 68.9092 | BMRL | 0.166 | 0.233 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 18:30 | 127.5 | 24 | 61 | 60 | 281 | 2.71 | 6.49 |  | 9.2 | 0.19401 | 0.29457 | 29.5435 | 6.1854 | 6.2961 | 387.4682 | 105.8049 | 384.7518 | 2.8031 | 57.6969 | 0.10912 | 7.7 | 7.7 | 7.8 | 115 | 305 | 361 | 383.6287 | -6.2683 | 62.2332 | 382.3333 | 69.9215 | BMRL | 0.167 | 0.231 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-29 | 19:00 | 128 | 24 | 61 | 60 | 281 | 2.73 | 6.4 |  | 9.13 | 0.19401 | 0.29901 | 29.7777 | 6.2311 | 6.3426 | 389.0715 | 106.2371 | 386.3237 | 2.8146 | 57.6854 | 0.10995 | 7.6 | 7.5 | 7.7 | 116 | 303 | 364 | 384.907 | -5.7437 | 61.9048 | 383.6008 | 69.7602 | BMRL | 0.166 | 0.235 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 8:30 | 141.5 | 24 | 61 | 60 | 281 | 2.66 | 5.81 |  | 8.47 | 0.19401 | 0.31405 | 32.1759 | 6.0713 | 6.1799 | 394.574 | 107.7593 | 391.859 | 2.8546 | 57.6454 | 0.10721 | 7.7 | 7.5 | 7.7 | 121 | 304 | 376 | 388.512 | -3.3277 | 60.2627 | 387.2459 | 68.7537 | BMRL | 0.168 | 0.244 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 10:00 | 143 | 24 | 61 | 60 | 281 | 2.64 | 7 |  | 9.64 | 0.19401 | 0.27386 | 28.1494 | 6.0257 | 6.1335 | 380.1799 | 103.8337 | 377.5836 | 2.7505 | 57.7495 | 0.10621 | 7.7 | 7.6 | 7.8 | 120 | 304 | 360 | 374.0829 | -3.9119 | 60.5911 | 372.8893 | 67.8189 | BMRL | 0.167 | 0.269 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 11:45 | 144.75 | 24 | 61 | 60 | 281 | 2.68 | 6.76 |  | 9.44 | 0.19401 | 0.2839 | 28.7669 | 6.117 | 6.2264 | 383.6795 | 104.7785 | 381.0195 | 2.7757 | 57.7243 | 0.10786 | 7.7 | 7.7 | 7.8 | 120 | 304 | 361 | 377.645 | -4.6108 | 60.5911 | 376.4163 | 68.1204 | BMRL | 0.167 | 0.242 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 14:00 | 147 | 24 | 61 | 60 | 281 | 2.69 | 6.57 | X | 9.26 | 0.19401 | 0.2905 | 29.3456 | 6.1398 | 6.2496 | 386.0135 | 105.4131 | 383.3273 | 2.7926 | 57.7074 | 0.1083 | 7.7 | 7.5 | 7.7 | 121 | 305 | 368 | 379.6317 | -3.1608 | 60.2627 | 378.3937 | 68.0227 | BMRL | 0.165 | 0.234 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 15:30 |  | 24 | 60 | 60 | 281 | 3.03 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 6.9158 | 7.0396 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 15:45 |  | 24 | 70 | 70 | 281 | 3.64 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 8.3081 | 8.4568 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 16:00 |  | 24 | 50 | 48 | 281 | 2.5 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 5.7061 | 5.8082 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 16:15 |  | 24 | 60 | 60 | 281 | 3.08 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 7.0299 | 7.1557 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 17:45 |  | 24 | 59 | 57 | 281 | 6.37 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 14.5392 | 14.7993 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 18:00 |  | 24 | 71 | 70 | 281 | 7.8 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 17.8031 | 18.1216 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 18:15 |  | 24 | 51 | 50 | 281 | 5.45 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 12.4393 | 12.6619 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[44 empty] | 1999-03-30 | 18:30 |  | 24 | 60 | 58 | 281 | 6.56 | NA |  | #VALUE! | 0.19401 | #VALUE! | #VALUE! | 14.9728 | 15.2408 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
[54 empty] | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Note on A1: C. Rice 7/12/99: All inorganic rejections were significantly higher this quarter, compared to the previous quarters. Consultant suggested that it is possible that the major fouling that occurred during this quarter resulted in changes in rejection characteristics (compared to the previous three quarters). However, the fouling did not occur until Run 2 - yet higher rejections were observed during all four runs!?!
Note on Q3: C. Rice 7/12/99: Consultant stated that no water quality parameters (including potential foulants) were measured prior to pretreatment because they were not required by the ICR.
Note on V6: Alison Gusses: Consultant verified that cartridge filtration was the only membrane pretreatment employed.
Note on X35: C. Rice: Feed TCAA concentrations verified by consultant.
Note on BV7: C. Rice 7/12/99: Consultant suggested that the major drop in MTCw around day 3 was probably caused by membrane fouling. All operational data were verified and found to be correct so no changes were made.
Note on BV52: C. Rice 7/12/99: Consultant suggested that the major drop in MTCw was probably caused by membrane fouling. All operational data were verified and found to be correct so no changes were made.
Note on CE8: C. Rice 7/12/99: Consultant verified all TDS values and stated that fouling could have resulted in changes in TDS rejection making these values significantly higher (relative to the previous three quarters).
Note on DB3: C. Rice 7/12/99: Consultant suggested that it is possible that the major fouling that occurred during this quarter resulted in changes in rejection characteristics (compared to the previous three quarters).
Note on DP3: C. Rice 7/12/99: Consultant suggested that it is possible that the major fouling that occurred during this quarter resulted in changes in rejection characteristics (compared to the previous three quarters).
Note on DQ10: C. Rice 7/12/99: Consultant verified all water quality parameters for the 90% recovery run due to high mass balance closure errors.
Note on DZ3: C. Rice 7/12/99: Consultant suggested that it is possible that the major fouling that occurred during this quarter resulted in changes in rejection characteristics (compared to the previous three quarters).
Note on EJ3: C. Rice 7/12/99: Consultant suggested that it is possible that the major fouling that occurred during this quarter resulted in changes in rejection characteristics (compared to the previous three quarters).