## Sheet1. 1st Quarter
FIELD-SET 1: 1st QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 1-1: PWS And Treatment Plant Data |  | Field 1-2: Full-Scale GAC Characteristics1 |  | Field 1-3: RSSCT Design Parameters |  |  |  | Field 1-4: Pretreatment Used Prior To GAC1 |  |  | Field 1-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 1-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 1-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 1-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 1-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Abilene | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-04-06 | [5 empty] | 20-min. EBCT Start Date | 1998-04-06 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2210001 | Carbon trade name | F-300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 15 mg/L alum, 4 mg/L cationic polymer | Bench | 10-min. EBCT Start Time | 16:15 | [5 empty] | 20-min. EBCT Start Time | 16:15 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminus coal | Minimum RSSCT Reynolds number, ReSC, min | 0.488 | 4 | 4.75 | Floculation | 2 min. rapid mix,30 min. slow mix | Bench | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 19 | 6 | 3.35 | Sedimentation | settling for at least 90 min. | Bench | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-04-06 | 17:15 | 1 | 78.9333 | 8.27 | 21.9 | BMRL | BMRL | #VALUE! | 1.15 | 1.18 | -0.03 | 20 | 8.5 | 24 | BMRL | NR | NR | NR | NR | NR | NR | 36.3 | 33.2 | 29.6 | NR | 11.9 | NA | NA | NA | NR | NR | C1-20 | N | 1998-04-06 | 17:15 | 1 | 39.4667 | 8.5 | 22 | BMRL | BMRL | #VALUE! | 1.15 | 1.2 | -0.05 | 20 | 8.5 | 24 | BMRL | NR | NR | NR | NR | NR | NR | 23.8 | 25.1 | 21.8 | NR | 2.96 | NA | NA | NA | NR | NR | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 5 um exclusion size | Bench | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-04-06 | 23:22 | 7.1167 | 561.7422 | 8.21 | 21 | BMRL | BMRL | #VALUE! | 1.15 | 1.24 | -0.09 | 20 | 8.5 | 24 | BMRL | NR | NR | NR | NR | NR | NR | 27.1 | 23.7 | 21.1 | NR | 2.83 | NA | NA | NA | NR | NR | C2-20 | N | 1998-04-07 | 7:22 | 15.1167 | 596.6044 | 8.11 | 19.7 | BMRL | BMRL | #VALUE! | 1.15 | 1.08 | 0.07 | 20 | 8.5 | 24 | BMRL | NR | NR | NR | NR | NR | 8.15 | BMRL | 5.5 | NR | BMRL | BMRL | NA | NA | NA | NR | NR | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.455 | 10 | 2 | Cartridge filtration | 1 um exclusion size | Bench | Sampling date | MM/DD/YY | 1998-04-06 | 1998-04-08 | --- | --- |  | Sampling date | MM/DD/YY | 1998-04-06 | 1998-04-10 | --- | --- |  | C3-10 | N | 1998-04-07 | 7:22 | 15.1167 | 1193.2089 | 8.22 | 19.5 | BMRL | BMRL | #VALUE! | 1.15 | 0.94 | 0.21 | 20 | 8.5 | 24 | 31 | NR | NR | NR | NR | NR | NR | 30.6 | 29.5 | 27.3 | NR | 8.44 | NA | NA | NA | NR | NR | C3-20 | N | 1998-04-07 | 23:22 | 31.1167 | 1228.0711 | 8.33 | 21.2 | BMRL | BMRL | #VALUE! | 1.15 | 0.9 | 0.25 | 20 | 8.4 | 24 | BMRL | NR | NR | NR | NR | NR | 32.3 | 2.59 | 9.36 | NR | 1.85 | BMRL | NA | NA | NA | NR | NR | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 16:15 | 16:53 | --- | --- |  | Sampling time | hh:mm | 16:15 | 15:18 | --- | --- |  | AVG C4-10 | Y | 1998-04-07 | 15:22 | 23.1167 | 1824.6756 | 8.27 | 20.85 | 0.991 | 0.0107 | 1.0797 | 1.47 | 1 | 0.47 | 20 | 8.4 | 24 | 47 | NR | NR | NR | NR | NR | 43.75 | 18.75 | 11.95 | NR | 11.51 | BMRL | NA | NA | NA | NR | NR | AVG C4-20 | Y | 1998-04-08 | 15:22 | 47.1167 | 1859.5378 | 8.37 | 20.5 | 0.58 | 0.0085 | 1.4655 | 1.15 | 0.87 | 0.28 | 20 | 8.5 | 23 | 46.5 | 22 | 28.1 | 5.75 | 87.3 | 143.15 | 20.05 | 22.1 | NR | 20.7 | 8.91 | 1.03 | NA | NA | NA | NR | NR | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 48.6333 | --- | --- |  | Operation time | hh.hh | 0 | 95.05 | --- | --- |  | C5-10 | N | 1998-04-07 | 23:22 | 31.1167 | 2456.1422 | 8.3 | 20.8 | 1.141 | 0.0164 | 1.4373 | 1.52 | 0.92 | 0.6 | 20 | 8.4 | 23.2 | 57 | NR | NR | NR | NR | NR | 25 | 12.7 | 5.39 | NR | 8.76 | BMRL | NA | NA | NA | NR | NR | C5-20 | N | 1998-04-09 | 7:22 | 63.1167 | 2491.0044 | 8.23 | 19.8 | 1.023 | BMRL | #VALUE! | 1.5 | 0.94 | 0.56 | 20 | 8.5 | 23 | 63 | BMRL | 26.3 | 4.6 | 26.3 | 57.2 | 31.7 | 13.7 | NR | 33.3 | 10.4 | BMRL | NA | NA | NA | NR | NR | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 3838.7911 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 3751.3067 | --- | --- |  | C6-10 | N | 1998-04-08 | 7:22 | 39.1167 | 3087.6089 | 8.18 | 20 | 1.601 | 0.0212 | 1.3242 | 1.76 | 1.14 | 0.62 | 20 | 8.4 | 23.2 | 87 | NR | NR | NR | NR | NR | 58.3 | 9.91 | 9.71 | NR | 9.35 | 3.21 | NA | NA | NA | NR | NR | C6-20 | N | 1998-04-09 | 23:22 | 79.1167 | 3122.4711 | 8.21 | 21.5 | 1.485 | 0.0124 | 0.83502 | 1.7 | 0.9 | 0.8 | 20 | 8.5 | 23.6 | 78 | 4.61 | 5.16 | 23.27 | 55.74 | 88.78 | NR | 46.9 | 10.2 | 12.7 | 11.4 | NR | NA | NA | NA | NR | NR | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 160 | 160 | 160 | 0 |  | Alkalinity | mg/L as CaCO3 | 160 | 147 | 153.5 | 8.4691 |  | AVG C7-10 | Y | 1998-04-08 | 15:22 | 47.1167 | 3719.0756 | 8.345 | 20.15 | 1.911 | 0.0238 | 1.2454 | 1.925 | 0.89 | 1.035 | 20 | 8.45 | 23 | 122.5 | NR | BMRL | NR | NR | NR | 44.95 | 21.25 | 16.35 | 9.63 | 13.115 | 8.22 | NA | NA | NA | 105.295 | 113.515 | AVG C7-20 | Y | 1998-04-10 | 15:22 | 95.1167 | 3753.9378 | 8.33 | 21.1 | 1.7845 | 0.01965 | 1.1011 | 1.855 | 0.78 | 1.075 | 20 | 8.6 | 23.55 | 89 | 2.55 | BMRL | 20.6 | 58.6 | 81.75 | NR | 23.85 | 16.7 | 22.7 | 20.245 | NR | NA | NA | NA | NR | NR | Labor Rate + Fringe ($/work-hour) | 15
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3071.0258 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 243 | 241 | 242 | 0.82645 |  | Total hardness | mg/L as CaCO3 | 241 | 251 | 246 | 4.065 |  | C8-10 | N | 1998-04-08 | 23:22 | 55.1167 | 4350.5422 | 8.15 | 20.6 | 2.139 | 0.0276 | 1.2903 | 2.04 | 0.86 | 1.18 | 20 | 8.4 | 23 | 130 | 18.3 | 4.71 | 31 | 51.3 | 105.31 | 59.3 | BMRL | NR | 8.38 | 20.9 | 8.18 | NA | NA | NA | NR | NR | C8-20 | N | 1998-04-11 | 7:22 | 111.1167 | 4385.4044 | 8.31 | 21.6 | 1.922 | 0.0212 | 1.103 | 1.93 | 0.88 | 1.05 | 20 | 8.6 | 23.5 | 100 | BMRL | BMRL | 30.8 | 63 | 93.8 | NR | 18.6 | 6.9 | 14.8 | 18.2 | NR | NA | NA | NA | NR | NR | Labor Overhead Factor (% of labor) | 15
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 6142.0516 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 133 | 132 | 132.5 | 0.75472 |  | Calcium hardness | mg/L as CaCO3 | 131 | 138 | 134.5 | 5.2045 |  | C9-10 | N | 1998-04-09 | 11:22 | 67.1167 | 5297.7422 | 8.22 | 20 | 2.872 | 0.0334 | 1.163 | 2.53 | 1 | 1.53 | 20 | 8.4 | 23 | 140 | 2.65 | BMRL | 18.2 | 44.9 | 65.75 | 56.7 | 3.2 | NR | 4.3 | 22.2 | 12 | NA | NA | NA | NR | NR | C9-20 | N | 1998-04-12 | 19:22 | 147.1167 | 5806.2044 | 8.27 | 21.9 | 2.494 | 0.0231 | 0.92622 | 2.3 | 0.9 | 1.4 | 20 | 8.5 | 24.7 | 105 | BMRL | 1.74 | 28.2 | 54 | 83.94 | NR | 9.95 | 8.15 | 6.23 | 21.2 | NR | NA | NA | NA | NR | NR | Electric Rate ($/kW-h) | 0.056
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7984.6671 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.31 | BMRL | 0.31 | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-04-09 | 23:22 | 79.1167 | 6244.9422 | 8.2 | 21 | 2.789 | 0.0369 | 1.3231 | 2.39 | 0.8 | 1.59 | 20 | 8.6 | 23.1 | 145 | 0.505 | 12.7 | 37.3 | 56.7 | 107.205 | 47.6 | 17.6 | NR | 10.1 | 25.5 | 10.2 | NA | NA | NA | NR | NR | C10-20 | N | 1998-04-14 | 7:22 | 183.1167 | 7227.0044 | 8.27 | 21.6 | 2.731 | 0.0268 | 0.98133 | 2.3 | 0.9 | 1.4 | 20 | 8.5 | 24.6 | 125 | BMRL | 1.83 | 28.8 | 51.1 | 81.73 | NR | 10.4 | 8.85 | 27.4 | 21.3 | NR | NA | NA | NA | NR | NR | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 430 | 440 | 435 | 2.2989 |  | Bromide | mg/L | 440 | 440 | 440 | 0 |  | AVG C11-10 | Y | 1998-04-10 | 11:22 | 91.1167 | 7192.1422 | 8.35 | 20.5 | 3.055 | 0.0408 | 1.3355 | 2.535 | 0.83 | 1.705 | 20 | 8.6 | 23.35 | 165 | 1.0617 | 13.65 | 40.85 | 44.95 | 100.5117 | 44.7 | 16.2 | 9.49 | 11.045 | 21.85 | 14.6 | NA | NA | NA | 103.285 | 117.885 | AVG C11-20 | Y | 1998-04-15 | 18:44 | 218.4833 | 8622.8089 | 8.29 | 21 | 3.015 | 0.04435 | 1.471 | 2.53 | 0.9 | 1.63 | 20 | 8.5 | 24.65 | 156 | BMRL | 13.45 | 38.85 | 59.55 | 111.85 | NR | 21.55 | 7.235 | 15.7 | 19.7 | NR | NA | NA | NA | NR | NR | Natural Gas Rate ($/ft3) | 0.003
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-04-10 | 23:22 | 103.1167 | 8139.3422 | 8.28 | 20.9 | 3.139 | 0.0456 | 1.4527 | 2.58 | 0.94 | 1.64 | 20 | 8.6 | 23.3 | 170 | BMRL | 15.9 | 40.2 | 56.4 | 112.5 | 59.7 | 1.46 | NR | 5.94 | 24.3 | 12.6 | NA | NA | NA | NR | NR | C12-20 | N | 1998-04-17 | 7:22 | 255.1167 | 10068.6044 | 8.36 | 21.8 | 3.341 | 0.034 | 1.0177 | 2.76 | 1 | 1.76 | 20 | 8.6 | 24.1 | 160 | BMRL | BMRL | 45.2 | 64.1 | 109.3 | NR | 23 | 9.63 | 21.2 | 24.1 | NR | NA | NA | NA | NR | NR | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.0521e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [6 empty] | C13-10 | N | 1998-04-11 | 13:22 | 117.1167 | 9244.4089 | 8.34 | 21.6 | 3.307 | 0.0495 | 1.4968 | 2.66 | 0.84 | 1.82 | 20 | 8.6 | 23.4 | 180 | BMRL | 10.3 | 36.4 | 53.1 | 99.8 | NR | 15.2 | 8.99 | 17.2 | 4.92 | NR | NA | NA | NA | NR | NR |  |  |  |  | -861400.25 | -33996596.5333 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0 | Modifications to Existing Plant (% of construction costs) | 15
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD | [38 empty] | -861400.25 | -33996596.5333 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-04-06 | 1998-04-08 | 1998-04-10 | --- | --- | Sampling date | MM/DD/YY | 1998-04-06 | 1998-04-10 | 1998-04-17 | --- | --- | [38 empty] | -861400.25 | -33996596.5333 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Plant Name | Grimes Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3934 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:15 | 16:53 | 23:22 | --- | --- | Sampling time | hh:mm | 16:15 | 15:18 | 8:15 | --- | --- | [38 empty] | -861400.25 | -33996596.5333 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Treatment Plant Category | Conventional |  |  | RSSCT flow rate, QSC (mL/min) | 21.7752 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 48.6333 | 103.1167 | --- | --- | Operation time | hh.hh | 0 | 95.05 | 256 | --- | --- | [38 empty] | -861400.25 | -33996596.5333 |  |  |  |  | #DIV/0! |  |  | 0 | [8 empty] | 0 | [9 empty] | 0 | 0
Process Train Name | Conv |  |  | Estimated total influent volume required, VSCT (L) | 396.4897 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 3838.7911 | 8139.3422 | --- | --- | Bed volumes | (20 minute) | 0 | 3751.3067 | 10103.4667 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 652 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.9 | 8.16 | 8.1 | 8.0533 | 1.6904 | pH | --- | 8 | 8.22 | 8.34 | 8.1867 | 2.1063 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | NA |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.13 | 0.12 | 0.09 | 0.11333 | 18.3676 | Turbidity | ntu | 0.14 | 0.07 | 0.09 | 0.1 | 36.0555 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 20.3 | 20.1 | 20 | 20.1333 | 0.7587 | Temperature | oC | 20.2 | 21 | 20.3 | 20.5 | 2.1263
Historical Average Water Temperature (oC) | 19.5 |  |  | Estimated full-scale run time, tLCT (days) | 55.4491 | [5 empty] | Total organic carbon | mg/L | 4.643 | 4.587 | 4.483 | 4.571 | 1.7762 | Total organic carbon | mg/L | 4.673 | 4.758 | 4.601 | 4.6773 | 1.6802 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 25 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.0788 | 0.0776 | 0.0773 | 0.0779 | 1.0189 | UV254 | cm-1 | 0.078 | 0.0746 | 0.0865 | 0.0797 | 7.6906 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 4.2149 | [5 empty] | SUVA | L/(mg*m) | 1.6972 | 1.6917 | 1.7243 | 1.7044 | 1.0231 | SUVA | L/(mg*m) | 1.6692 | 1.5679 | 1.88 | 1.7057 | 9.336 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 9.3666 | [5 empty] | SDS-Cl2 dose | mg/L | 3.45 | 3.45 | 3.29 | 3.3967 | 2.7196 | SDS-Cl2 dose | mg/L | 3.45 | 3.45 | 3.45 | 3.45 | 0 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 132.1632 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.92 | 0.8 | 0.88 | 0.86667 | 7.0501 | SDS-Free Cl2 residual | mg/L | 0.9 | 0.8 | 0.88 | 0.86 | 6.1529 | C4-10 | Primary | 1998-04-07 | 15:22 | 23.1167 | 1824.6756 | 8.27 | 20.2 | 1.21 | 0.0114 | 0.94215 | 1.61 | 1 | 0.61 | 20 | 8.4 | 24 | 49 | NR | NR | NR | NR | NR | 39.1 | 19.9 | 10.9 | NR | 14.6 | BMRL | NA | NA | NA | NR | NR | C4-20 | Primary | 1998-04-08 | 15:22 | 47.1167 | 1859.5378 | 8.37 | 20.5 | 0.586 | 0.0092 | 1.57 | 1.15 | 0.84 | 0.31 | 20 | 8.5 | 23 | 42 | NR | 28.1 | NR | NR | NR | 12.1 | 19 | NR | 20.3 | 7.99 | 1.03 | NA | NA | NA | NR | NR
|  |  |  | Mass GAC required, mSC (g) | 7.5312 | [5 empty] | SDS-Cl2 demand | mg/L | 2.53 | 2.65 | 2.41 | 2.53 | 4.7431 | SDS-Cl2 demand | mg/L | 2.55 | 2.65 | 2.57 | 2.59 | 2.0431 | D1-10 | Duplicate | 1998-04-07 | 15:22 | 23.1167 | 1824.6756 | 8.27 | 21.5 | 0.772 | 0.01 | 1.2953 | 1.33 | 1 | 0.33 | 20 | 8.4 | 24 | 45 | NR | NR | NR | NR | NR | 48.4 | 17.6 | 13 | NR | 8.42 | BMRL | NA | NA | NA | NR | NR | D1-20 | Duplicate | 1998-04-08 | 15:22 | 47.1167 | 1859.5378 | 8.37 | 20.5 | 0.574 | 0.0078 | 1.3589 | 1.15 | 0.9 | 0.25 | 20 | 8.5 | 23 | 51 | NR | NR | NR | NR | NR | 28 | 25.2 | NR | 21.1 | 9.83 | BMRL | NA | NA | NA | NR | NR
[11 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 | AVG C4-10 | Average | --- | --- | --- | --- | 8.27 | 20.85 | 0.991 | 0.0107 | 1.1187 | 1.47 | 1 | 0.47 | 20 | 8.4 | 24 | 47 | NR | NR | NR | NR | NR | 43.75 | 18.75 | 11.95 | NR | 11.51 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR | AVG C4-20 | Average | --- | --- | --- | --- | 8.37 | 20.5 | 0.58 | 0.0085 | 1.4644 | 1.15 | 0.87 | 0.28 | 20 | 8.5 | 23 | 46.5 | NR | NR | NR | NR | NR | 20.05 | 22.1 | NR | 20.7 | 8.91 | 1.03 | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.3 | 8.4 | 8.5 | 8.4 | 1.1905 | SDS-Chlorination pH | --- | 8.4 | 8.5 | 8.6 | 8.5 | 1.1765 |  | RPD | --- | --- | --- | --- | 0 | 6.235 | 44.1978 | 13.0841 | 31.5701 | 19.0476 | 0 | 59.5745 | 0 | 0 | 0 | 8.5106 | NR | NR | NR | NR | NR | 21.2571 | 12.2667 | 17.5732 | NR | 53.6924 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NR | NR |  | RPD | --- | --- | --- | --- | 0 | 0 | 2.069 | 16.4706 | 14.4139 | 0 | 6.8966 | 21.4286 | 0 | 0 | 0 | 19.3548 | NR | NR | NR | NR | NR | 79.3017 | 28.0543 | NR | 3.8647 | 20.651 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NR | NR
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 24 | 23 | 23.5 | 23.5 | 2.1277 | SDS-Incubation time | hours | 24 | 23.5 | 24.2 | 23.9 | 1.5086 | C7-10 | Primary | 1998-04-08 | 15:22 | 47.1167 | 3719.0756 | 8.36 | 20.1 | 1.87 | 0.0236 | 1.262 | 1.9 | 0.88 | 1.02 | 20 | 8.4 | 23 | 120 | NR | NR | NR | NR | NR | 53.8 | 18.6 | 15.1 | NR | 16.4 | BMRL | NA | NA | NA | NR | NR | C7-20 | Primary | 1998-04-10 | 15:22 | 95.1167 | 3753.9378 | 8.29 | 21 | 1.812 | 0.0185 | 1.021 | 1.87 | 0.86 | 1.01 | 20 | 8.6 | 23.6 | 88 | 2.55 | BMRL | 17.3 | 60 | 79.85 | NR | 23.4 | 16.7 | 25.9 | 17.69 | NR | NA | NA | NA | NR | NR
|  |  |  | Estimated full-scale run time, tLCT (days) | 110.8982 | [5 empty] | SDS-TOX | mg Cl- /L | 260 | 275 | 240 | 258.3333 | 6.7972 | SDS-TOX | mg Cl- /L | 240 | 260 | 230 | 243.3333 | 6.2775 | D2-10 | Duplicate | 1998-04-08 | 15:22 | 47.1167 | 3719.0756 | 8.33 | 20.2 | 1.952 | 0.024 | 1.2295 | 1.95 | 0.9 | 1.05 | 20 | 8.5 | 23 | 125 | NR | NR | NR | NR | NR | 36.1 | 23.9 | 17.6 | 9.63 | 9.83 | 8.22 | NA | NA | NA | 105.3 | 113.5 | D2-20 | Duplicate | 1998-04-10 | 15:22 | 95.1167 | 3753.9378 | 8.37 | 21.2 | 1.757 | 0.0208 | 1.1838 | 1.84 | 0.7 | 1.14 | 20 | 8.6 | 23.5 | 90 | BMRL | BMRL | 23.9 | 57.2 | 81.1 | NR | 24.3 | NR | 19.5 | 22.8 | NR | NA | NA | NA | NR | NR
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | NR | NR | 12.4 | NR | #DIV/0! | SDS-CHCl3 | mg/L | NR | BMRL | BMRL | NR | #DIV/0! | AVG C7-10 | Average | --- | --- | --- | --- | 8.345 | 20.15 | 1.911 | 0.0238 | 1.2458 | 1.925 | 0.89 | 1.035 | 20 | 8.45 | 23 | 122.5 | NR | NR | NR | NR | NR | 44.95 | 21.25 | 16.35 | NR | 13.115 | 8.22 | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR | AVG C7-20 | Average | --- | --- | --- | --- | 8.33 | 21.1 | 1.7845 | 0.01965 | 1.1024 | 1.855 | 0.78 | 1.075 | 20 | 8.6 | 23.55 | 89 | 2.55 | #DIV/0! | 20.6 | 58.6 | 80.475 | #DIV/0! | 23.85 | NR | 22.7 | 20.245 | NR | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.4298 | [5 empty] | SDS-BDCM | mg/L | NR | 242 | 20.5 | NR | #VALUE! | SDS-BDCM | mg/L | NR | 16.1 | 42.3 | NR | #VALUE! |  | RPD | --- | --- | --- | --- | 0.3595 | 0.49628 | 4.2909 | 1.6807 | 2.6107 | 2.5974 | 2.2472 | 2.8986 | 0 | 1.1834 | 0 | 4.0816 | NR | NR | NR | NR | NR | 39.3771 | 24.9412 | 15.2905 | NR | 50.0953 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | NR | NR |  | RPD | --- | --- | --- | --- | 0.96038 | 0.94787 | 3.0821 | 11.7048 | 14.7736 | 1.6173 | 20.5128 | 12.093 | 0 | 0 | 0.42463 | 2.2472 | #VALUE! | #VALUE! | 32.0388 | 4.7782 | 1.5533 | #VALUE! | 3.7736 | NR | 28.1938 | 25.2408 | NR | #VALUE! | #VALUE! | #VALUE! | NR | NR
|  |  |  | RSSCT bed length, lSC (cm) | 18.7332 | [5 empty] | SDS-DBCM | mg/L | NR | NR | 71.6 | NR | #DIV/0! | SDS-DBCM | mg/L | NR | 78.2 | 70 | NR | #VALUE! | C11-10 | Primary | 1998-04-10 | 11:22 | 91.1167 | 7192.1422 | 8.34 | 20.5 | 3.031 | 0.0415 | 1.3692 | 2.53 | 0.8 | 1.73 | 20 | 8.6 | 23.2 | 165 | 1.6094 | 14.4 | 40.6 | 27.3 | 83.9094 | 44.7 | 12 | NR | 6.09 | 24.8 | 14.6 | NA | NA | NA | NR | NR | C11-20 | Primary | 1998-04-15 | 18:44 | 218.4833 | 8622.8089 | 8.29 | 21 | 3.042 | 0.0461 | 1.5155 | 2.53 | 0.8 | 1.73 | 20 | 8.5 | 24.7 | 157 | BMRL | 14.1 | 39.3 | 60.5 | 113.9 | NR | 23.7 | 5.46 | 18.7 | 21.4 | NR | NA | NA | NA | NR | NR
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 264.3265 | [5 empty] | SDS-CHBr3 | mg/L | NR | NR | 64 | NR | #DIV/0! | SDS-CHBr3 | mg/L | NR | 71.6 | 77.3 | NR | #VALUE! | D3-10 | Duplicate | 1998-04-10 | 11:22 | 91.1167 | 7192.1422 | 8.36 | 20.5 | 3.079 | 0.0401 | 1.3024 | 2.54 | 0.86 | 1.68 | 20 | 8.6 | 23.5 | 165 | 0.514 | 12.9 | 41.1 | 26.06 | 80.574 | NR | 20.4 | 9.49 | 16 | 18.9 | NR | NA | NA | NA | NR | NR | D3-20 | Duplicate | 1998-04-15 | 18:44 | 218.4833 | 8622.8089 | 8.29 | 21 | 2.988 | 0.0426 | 1.4257 | 2.53 | 1 | 1.53 | 20 | 8.5 | 24.6 | 155 | BMRL | 12.8 | 38.4 | 58.6 | 109.8 | NR | 19.4 | 9.01 | 12.7 | 18 | NR | NA | NA | NA | NR | NR
|  |  |  | Mass GAC required, mSC (g) | 15.0624 | [5 empty] | SDS-THM4 | mg/L | NR | NR | 168.5 | NR | #DIV/0! | SDS-THM4 | mg/L | NR | 165.9 | 189.6 | NR | #VALUE! | AVG C11-10 | Average | --- | --- | --- | --- | 8.35 | 20.5 | 3.055 | 0.0408 | 1.3358 | 2.535 | 0.83 | 1.705 | 20 | 8.6 | 23.35 | 165 | 1.0617 | 13.65 | 40.85 | 26.68 | 82.2417 | NR | 16.2 | NR | 11.045 | 21.85 | NR | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR | AVG C11-20 | Average | --- | --- | --- | --- | 8.29 | 21 | 3.015 | 0.04435 | 1.4706 | 2.53 | 0.9 | 1.63 | 20 | 8.5 | 24.65 | 156 | #DIV/0! | 13.45 | 38.85 | 59.55 | 111.85 | NR | 21.55 | 7.235 | 15.7 | 19.7 | NR | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR
[11 empty] | SDS-MCAA* | mg/L | NR | 71.7 | NR | NR | #DIV/0! | SDS-MCAA* | mg/L | NR | NR | NR | NR | #DIV/0! |  | RPD | --- | --- | --- | --- | 0.23952 | 0 | 1.5712 | 3.4314 | 5.0019 | 0.39448 | 7.2289 | 2.9326 | 0 | 0 | 1.2848 | 0 | 103.1742 | 10.989 | 1.224 | 4.6477 | 4.0556 | NR | 51.8519 | NR | 89.7239 | 27.0023 | NR | #VALUE! | #VALUE! | #VALUE! | NR | NR |  | RPD | --- | --- | --- | --- | 0 | 0 | 1.791 | 7.8918 | 6.1029 | 0 | 22.2222 | 12.2699 | 0 | 0 | 0.40568 | 1.2821 | #VALUE! | 9.6654 | 2.3166 | 3.1906 | 3.6656 | NR | 19.9536 | 49.067 | 38.2166 | 17.2589 | NR | #VALUE! | #VALUE! | #VALUE! | NR | NR
[11 empty] | SDS-DCAA* | mg/L | 27.5 | 34 | 8.7 | 23.4 | 56.149 | SDS-DCAA* | mg/L | 23.6 | 23.3 | 27.5 | 24.8 | 9.4479 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 8.59 | 7.11 | 9.31 | 8.3367 | 13.4546 | SDS-TCAA* | mg/L | BMRL | 11.7 | 4.03 | 7.865 | 68.9575 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 11.1 | NR | 22.4 | NR | #VALUE! | SDS-MBAA* | mg/L | 8.44 | 24.2 | 20.1 | 17.58 | 46.511
[11 empty] | SDS-DBAA* | mg/L | NR | 21.3 | 24.5 | NR | #VALUE! | SDS-DBAA* | mg/L | NR | 25.4 | 25.1 | NR | #VALUE!
[11 empty] | SDS-BCAA* | mg/L | 22.7 | 14.8 | NR | NR | #VALUE! | SDS-BCAA* | mg/L | 17 | NR | NR | NR | #DIV/0!
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | NR | NR | NR | NR | #DIV/0! | SDS-HAA5 | mg/L | NR | NR | NR | NR | #DIV/0!
[11 empty] | SDS-HAA6 | mg/L | NR | NR | NR | NR | #DIV/0! | SDS-HAA6 | mg/L | NR | NR | NR | NR | #DIV/0!
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (11/8/99): Reviewer adjusted Reynolds number based on revised full-scale temperature supplied by utility.
Note on H8: Reviewer D.S. (10/12/99): Full-scale temperature is 19C, column design based on 20C.
Note on Q43: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on Q53: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on Q54: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on S11: M.H. (08/12/99): Changed time from 15:22.
Note on S23: M.H. (08/12/99): Changed time from 15:22.
Note on Y43: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on Y53: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on Y54: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on AA11: M.H. (08/12/99): Changed time from 15:23.
Note on AA23: M.H. (08/12/99): Changed time from 15:23.
Note on AJ5: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on AJ30: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on AO35: Reviewer D.S. (10/12/99): Per Consultant: "TOC results are correct."
Note on AY43: Reviewer D.S. (10/12/99): Per Consultant: "Bromoform for D3-10 was entered wrong. Chloroform result is correct."
Note on BC5: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on BC30: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on BM5: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on BM30: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on BN5: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on BN30: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on BS5: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on BS30: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on CL5: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on CL30: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on CV5: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on CV30: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on CW5: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on CW30: Reviewer D.S. (10/12/99): Per Consultant on THM and HAA NRs: "The rejected THM samples were spiked with the standard instead of with the surrogate. The rejected HAA samples, the spikes for MCAA, DBAA, and BCAA were not recovered. Sample B1-10 the surrogate recovery was low and was rejected."
Note on CZ13: Reviewer M.H. (11/8/99): Per utility, "I could not locate a 98 PPI that made sense on a base year of 1967."
Note on CZ17: Reviewer M.H. (11/8/99): Per utility, "we do not use fuel oil in this region for any purpose."

## Sheet2. 2nd Quarter
FIELD-SET 2: 2nd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 2-1: PWS And Treatment Plant Data |  | Field 2-2: Full-Scale GAC Characteristics1 |  | Field 2-3: RSSCT Design Parameters |  |  |  | Field 2-4: Pretreatment Used Prior To GAC1 |  |  | Field 2-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 2-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 2-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 2-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 2-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Abilene | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-06-12 | [5 empty] | 20-min. EBCT Start Date | 1998-06-12 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2210001 | Carbon trade name | F-300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 15 mg/L alum, 4 mg/L cationic polymer | Bench | 10-min. EBCT Start Time | 16:15 | [5 empty] | 20-min. EBCT Start Time | 16:15 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminus coal | Minimum RSSCT Reynolds number, ReSC, min | 0.577 | 4 | 4.75 | Floculation | 2 min. rapid mix,30 min. slow mix | Bench | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 26 | 6 | 3.35 | Sedimentation | settling for at least 90 min. | Bench | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-06-12 | 17:14 | 0.98333 | 77.6178 | 8.1 | 23.4 | BMRL | BMRL | #VALUE! | 1.4 | 1.2 | 0.2 | 20 | 8.4 | 23.67 | BMRL | 2.72 | 2.49 | BMRL | 9.86 | 15.07 | 49 | 28.5 | 20.7 | 18.4 | 7.76 | 14.6 | NA | NA | NA | 124.36 | 138.96 | C1-20 | N | 1998-06-12 | 17:14 | 0.98333 | 38.8089 | 8.3 | 23.1 | BMRL | BMRL | #VALUE! | 1.12 | 0.64 | 0.48 | 20 | 8.4 | 23.73 | BMRL | BMRL | BMRL | BMRL | 7.47 | 7.47 | 53.8 | 32.9 | 20.4 | 17.6 | 8.25 | 10.4 | NA | NA | NA | 132.95 | 143.35 | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 5 um exclusion size | Bench | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-06-12 | 23:22 | 7.1167 | 561.7422 | 8.04 | 22.4 | BMRL | BMRL | #VALUE! | 1.14 | 0.64 | 0.5 | 20 | 8.4 | 23.75 | 27 | BMRL | BMRL | BMRL | 20.1 | 20.1 | 50.6 | 28.1 | 20.8 | 22.9 | 6.72 | 12.3 | NA | NA | NA | 129.12 | 141.42 | C2-20 | N | 1998-06-13 | 7:22 | 15.1167 | 596.6044 | 8.01 | 22 | BMRL | BMRL | #VALUE! | 1.12 | 0.6 | 0.52 | 20 | 8.4 | 24.83 | BMRL | BMRL | BMRL | 0.733 | 13.6 | 14.333 | 51.7 | 30.7 | 22.5 | 16.6 | 12.6 | 10.3 | NA | NA | NA | 134.1 | 144.4 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.455 | 10 | 2 | Cartridge filtration | 1 um exclusion size | Bench | Sampling date | MM/DD/YY | 1998-06-12 | 1998-06-14 | --- | --- |  | Sampling date | MM/DD/YY | 1998-06-12 | 1998-06-16 | --- | --- |  | C3-10 | N | 1998-06-13 | 7:22 | 15.1167 | 1193.2089 | 7.97 | 22.4 | 0.624 | BMRL | #VALUE! | 1.38 | 0.6 | 0.78 | 20 | 8.4 | 23.17 | 28 | BMRL | BMRL | 4.59 | NR | NR | 50.7 | 29.7 | 19.5 | 12.7 | 10.3 | 8.44 | NA | NA | NA | 122.9 | 131.34 | C3-20 | N | 1998-06-13 | 23:22 | 31.1167 | 1228.0711 | 8.1 | 22.4 | BMRL | BMRL | #VALUE! | 1.17 | 0.86 | 0.31 | 20 | 8.4 | 24.86 | 33 | BMRL | BMRL | BMRL | 30.2 | 30.2 | 45.3 | 25.7 | 21.9 | 19.1 | 6.61 | 5.11 | NA | NA | NA | 118.61 | 123.72 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 16:15 | 16:48 | --- | --- |  | Sampling time | hh:mm | 16:15 | 15:15 | --- | --- |  | AVG C4-10 | Y | 1998-06-13 | 15:22 | 23.1167 | 1824.6756 | 8.05 | 22.5 | 0.874 | BMRL | #VALUE! | 1.535 | 0.63 | 0.905 | 20 | 8.4 | 23.885 | 55.5 | BMRL | BMRL | 6.74 | 15.7 | 22.44 | 50.35 | 16.7 | 16.7 | 21.7 | 8.075 | 6.3 | NA | NA | NA | 113.525 | 119.825 | AVG C4-20 | Y | 1998-06-14 | 15:22 | 47.1167 | 1859.5378 | 8.16 | 21.5 | 0.752 | BMRL | #VALUE! | 1.355 | 0.56 | 0.795 | 20 | 8.3 | 24.26 | 46.5 | BMRL | BMRL | 5.745 | 21.05 | 26.795 | 52 | 29.1 | 19.3 | 22.9 | 12.29 | 8.23 | NA | NA | NA | 135.59 | 143.82 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0 | 48.55 | --- | --- |  | Operation time | hh.hh | 0 | 95 | --- | --- |  | C5-10 | N | 1998-06-13 | 23:22 | 31.1167 | 2456.1422 | 8.08 | 22.3 | 1.34 | 0.0152 | 1.1343 | 1.79 | 0.6 | 1.19 | 20 | 8.4 | 23.78 | 79 | 1.81 | BMRL | 11.8 | 38.4 | 52.01 | 55.2 | 18.1 | 15 | 21.1 | 18 | 6.76 | NA | NA | NA | 127.4 | 134.16 | C5-20 | N | 1998-06-15 | 7:22 | 63.1167 | 2491.0044 | 8.2 | 20.8 | 1.06 | 0.0128 | 1.2075 | 1.62 | 0.5 | 1.12 | 20 | 8.3 | 24.27 | 76 | BMRL | BMRL | 8.63 | 44.1 | 52.73 | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 0 | 3832.2133 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 3749.3333 | --- | --- |  | C6-10 | N | 1998-06-14 | 7:22 | 39.1167 | 3087.6089 | 7.95 | 22.1 | 1.64 | 0.0176 | 1.0732 | 1.96 | 0.6 | 1.36 | 20 | 8.4 | 24.92 | 100 | BMRL | BMRL | 16.9 | 61.9 | 78.8 | 40.7 | 23.4 | 5.77 | 0.98 | 25.3 | 6.59 | NA | NA | NA | 96.15 | 102.74 | C6-20 | N | 1998-06-15 | 23:22 | 79.1167 | 3122.4711 | 8.06 | 21.3 | 1.4 | 0.0174 | 1.2429 | 1.99 | 0.6 | 1.39 | 20 | 8.4 | 24.07 | 81 | BMRL | BMRL | 15.8 | 62.3 | 78.1 | 48.1 | 29.4 | 14.8 | NR | 15 | 3.81 | NA | NA | NA | NR | NR | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 165 | 166 | 165.5 | 0.60423 |  | Alkalinity | mg/L as CaCO3 | 166 | 166 | 166 | 0 |  | AVG C7-10 | Y | 1998-06-14 | 15:22 | 47.1167 | 3719.0756 | 8.11 | 21.6 | 1.915 | 0.0228 | 1.1906 | 2.12 | 0.56 | 1.56 | 20 | 8.3 | 24.235 | 115 | BMRL | BMRL | 24.9 | 76.3 | 101.2 | 37.75 | 23.7 | 8.585 | 19.8 | 22.65 | 14.9 | NA | NA | NA | 112.485 | 127.385 | AVG C7-20 | Y | 1998-06-16 | 15:22 | 95.1167 | 3753.9378 | 8.17 | 22.15 | 1.84 | 0.0224 | 1.2174 | 2.27 | 0.4 | 1.87 | 20 | 8.4 | 24.35 | 105 | BMRL | BMRL | 22 | 76.2 | 98.2 | 52.45 | 30.6 | 13.85 | 21.85 | 17.95 | 13.6 | NA | NA | NA | 136.7 | 150.3 | Labor Rate + Fringe ($/work-hour) | 15
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3071.0258 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 255 | 255 | 255 | 0 |  | Total hardness | mg/L as CaCO3 | 259 | 259 | 259 | 0 |  | C8-10 | N | 1998-06-14 | 23:22 | 55.1167 | 4350.5422 | 8.2 | 21.1 | 2.07 | 0.0296 | 1.43 | 2.21 | 0.58 | 1.63 | 20 | 8.3 | 24.2 | 120 | BMRL | BMRL | 21.2 | 67.6 | 88.8 | NR | 10.8 | 17 | 10.4 | 12.8 | 3.81 | NA | NA | NA | 51 | 54.81 | C8-20 | N | 1998-06-17 | 7:22 | 111.1167 | 4385.4044 | 8.28 | 21.1 | 1.94 | 0.0264 | 1.3608 | 2.33 | 0.2 | 2.13 | 20 | 8.4 | 24.27 | 125 | BMRL | BMRL | 26.5 | 74.3 | 100.8 | 33.8 | 31.2 | 13.8 | 21.4 | 18.7 | 12.9 | NA | NA | NA | 118.9 | 131.8 | Labor Overhead Factor (% of labor) | 15
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 6142.0516 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 137 | 137 | 137 | 0 |  | Calcium hardness | mg/L as CaCO3 | 139 | 142 | 140.5 | 2.1352 |  | C9-10 | N | 1998-06-15 | 11:22 | 67.1167 | 5297.7422 | 7.99 | 21.8 | 2.41 | 0.0337 | 1.3983 | 2.41 | 0.56 | 1.85 | 20 | 8.3 | 24.25 | 135 | 6.28 | 0.983 | 24 | 65 | 96.263 | 30.9 | 16.7 | 17.8 | 30.7 | 25.9 | 9.55 | NA | NA | NA | 122 | 131.55 | C9-20 | N | 1998-06-18 | 19:22 | 147.1167 | 5806.2044 | 8.11 | 23.6 | 2.38 | 0.0281 | 1.1807 | 3.25 | 0.62 | 2.63 | 20 | 8.4 | 23.88 | 110 | BMRL | BMRL | 22.3 | 92.4 | 114.7 | 69.8 | 31.6 | 18.7 | NR | 21.7 | 21.5 | NA | NA | NA | NR | NR | Electric Rate ($/kW-h) | 0.056
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7984.6671 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | C10-10 | N | 1998-06-15 | 23:22 | 79.1167 | 6244.9422 | 8.08 | 21.6 | 2.749 | 0.0354 | 1.2877 | 2.84 | 0.4 | 2.44 | 20 | 8.4 | 24 | 155 | BMRL | BMRL | 28.7 | 81.4 | 110.1 | 59 | 15.1 | 17.1 | 2.61 | 17.8 | 1.02 | NA | NA | NA | 111.61 | 112.63 | C10-20 | N | 1998-06-20 | 7:22 | 183.1167 | 7227.0044 | 8.16 | 22.2 | 2.63 | 0.0311 | 1.1825 | 3.45 | 0.62 | 2.83 | 20 | 8.4 | 23.97 | 140 | BMRL | BMRL | 39.9 | 94.9 | 134.8 | 51.7 | 31.7 | 14.1 | 21.5 | 18.5 | 13.5 | NA | NA | NA | 137.5 | 151 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 440 | 450 | 445 | 2.2472 |  | Bromide | mg/L | 460 | 460 | 460 | 0 |  | AVG C11-10 | Y | 1998-06-16 | 11:22 | 91.1167 | 7192.1422 | 8.125 | 22 | 3.2 | 0.04285 | 1.3391 | 3.12 | 0.25 | 2.87 | 20 | 8.4 | 24.31 | 162.5 | BMRL | 5.91 | 36.65 | 76.8 | 119.36 | 60.1 | 25.35 | 16.5 | 12.57 | 21.5 | 12.2 | NA | NA | NA | 136.02 | 148.22 | AVG C11-20 | Y | 1998-06-21 | 19:22 | 219.1167 | 8647.8044 | 8.165 | 21.8 | 2.815 | 0.0373 | 1.325 | 3.605 | 0.55 | 3.055 | 20 | 8.4 | 24.05 | 157.5 | BMRL | BMRL | 47.43 | NR | NR | 56 | 33.45 | 20.2 | NR | 21.85 | 16.95 | NA | NA | NA | NR | NR | Natural Gas Rate ($/ft3) | 0.003
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-06-16 | 23:22 | 103.1167 | 8139.3422 | 8.18 | 22.3 | 3.25 | 0.0478 | 1.4708 | 3.16 | 0.2 | 2.96 | 20 | 8.4 | 24.22 | 175 | BMRL | 8.51 | 37.2 | 83.5 | 129.21 | 64.9 | 16 | 19.1 | 1.02 | 24.3 | 10.8 | NA | NA | NA | 125.32 | 136.12 | C12-20 | N | 1998-06-23 | 7:22 | 255.1167 | 10068.6044 | 8.13 | 21.8 | 2.99 | 0.0407 | 1.3612 | 3.73 | 0.84 | 2.89 | 20 | 8.4 | 24.07 | 195 | BMRL | NR | 62.9 | 81.4 | NR | 36.1 | 31.1 | 19.1 | NR | 21.1 | 22 | NA | NA | NA | NR | NR | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 8.8923e-07 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [40 empty] | C13-20 | N | 1998-06-25 | 10:04 | 305.8167 | 12069.5644 | 8.23 | 21.9 | 3.24 | 0.0481 | 1.4846 | 3.94 | 0.8 | 3.14 | 20 | 8.4 | 24.1 | 225 | BMRL | NR | 71.4 | 84.9 | NR | 37.3 | 31.7 | 16.5 | NR | 20 | 22.4 | NA | NA | NA | NR | NR | Modifications to Existing Plant (% of construction costs) | 15
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-06-12 | 1998-06-14 | 1998-06-16 | --- | --- | Sampling date | MM/DD/YY | 1998-06-12 | 1998-06-16 | 1998-06-25 | --- | ---
Plant Name | Grimes Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3884 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 16:15 | 16:48 | 23:30 | --- | --- | Sampling time | hh:mm | 16:15 | 15:15 | 11:45 | --- | ---
Treatment Plant Category | Conventional |  |  | RSSCT flow rate, QSC (mL/min) | 21.7606 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0 | 48.55 | 103.25 | --- | --- | Operation time | hh.hh | 0 | 95 | 307.5 | --- | ---
Process Train Name | Conv |  |  | Estimated total influent volume required, VSCT (L) | 396.2235 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 0 | 3832.2133 | 8149.8667 | --- | --- | Bed volumes | (20 minute) | 0 | 3749.3333 | 12136 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [11 empty] | 0.56833 |  |  |  | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 652 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.94 | 7.89 | 8.07 | 7.9667 | 1.1663 | pH | --- | 7.96 | 8.05 | 8.23 | 8.08 | 1.7015 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2210001 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.13 | 0.14 | 0.16 | 0.14333 | 10.6572 | Turbidity | ntu | 0.17 | 0.11 | 0.11 | 0.13 | 26.6469 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 22 | 21.5 | 21.4 | 21.6333 | 1.4859 | Temperature | oC | 21.9 | 21.2 | 21.9 | 21.6667 | 1.8653
Historical Average Water Temperature (oC) | 19.5 |  |  | Estimated full-scale run time, tLCT (days) | 55.4491 | [5 empty] | Total organic carbon | mg/L | 4.43 | 4.58 | 4.97 | 4.66 | 5.9817 | Total organic carbon | mg/L | 4.43 | 4.73 | 4.24 | 4.4667 | 5.531 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 25 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.0793 | 0.0776 | 0.0852 | 0.0807 | 4.9427 | UV254 | cm-1 | 0.0845 | 0.0808 | 0.081 | 0.0821 | 2.5345 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 4.2149 | [5 empty] | SUVA | L/(mg*m) | 1.7901 | 1.6943 | 1.7143 | 1.7329 | 2.9149 | SUVA | L/(mg*m) | 1.9074 | 1.7082 | 1.9104 | 1.842 | 6.2901 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 9.3603 | [5 empty] | SDS-Cl2 dose | mg/L | 3.59 | 6.48 | 5.31 | 5.1267 | 28.3556 | SDS-Cl2 dose | mg/L | 6.48 | 5.11 | 4.72 | 5.4367 | 17.0022 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 132.0745 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.2 | 1.44 | 0.7 | 0.78 | 79.9819 | SDS-Free Cl2 residual | mg/L | 1.4 | 0.7 | 0.64 | 0.91333 | 46.2626 | C4-10 | Primary | 1998-06-13 | 15:22 | 23.1167 | 1824.6756 | 8.05 | 22.5 | 0.888 | BMRL | #VALUE! | 1.56 | 0.62 | 0.94 | 20 | 8.4 | 23.85 | 61 | BMRL | BMRL | 7.11 | 11.7 | 18.81 | 53.9 | 18.5 | 15.2 | 16.1 | 14 | 5.03 | NA | NA | NA | 117.7 | 122.73 | C4-20 | Primary | 1998-06-14 | 15:22 | 47.1167 | 1859.5378 | 8.16 | 21.5 | 0.698 | BMRL | #VALUE! | 1.24 | 0.56 | 0.68 | 20 | 8.3 | 24.22 | 37 | BMRL | BMRL | 3.81 | 19.7 | 23.51 | 51.5 | 29.1 | 18.3 | 26.7 | 8.08 | 8.59 | NA | NA | NA | 133.68 | 142.27
|  |  |  | Mass GAC required, mSC (g) | 7.5262 | [5 empty] | SDS-Cl2 demand | mg/L | 3.39 | 5.04 | 4.61 | 4.3467 | 19.6919 | SDS-Cl2 demand | mg/L | 5.08 | 4.41 | 4.08 | 4.5233 | 11.2648 | D1-10 | Duplicate | 1998-06-13 | 15:22 | 23.1167 | 1824.6756 | 8.05 | 22.5 | 0.86 | BMRL | #VALUE! | 1.51 | 0.64 | 0.87 | 20 | 8.4 | 23.92 | 50 | BMRL | BMRL | 6.37 | 19.7 | 26.07 | 46.8 | 14.9 | 18.2 | 27.3 | 2.15 | 7.56 | NA | NA | NA | 109.35 | 116.91 | D1-20 | Duplicate | 1998-06-14 | 15:22 | 47.1167 | 1859.5378 | 8.16 | 21.5 | 0.806 | BMRL | #VALUE! | 1.47 | 0.56 | 0.91 | 20 | 8.3 | 24.3 | 56 | BMRL | BMRL | 7.68 | 22.4 | 30.08 | 52.5 | 29.1 | 20.3 | 19.1 | 16.5 | 7.87 | NA | NA | NA | 137.5 | 145.37
[11 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 | AVG C4-10 | Average | --- | --- | --- | --- | 8.05 | 22.5 | 0.874 | #DIV/0! | #VALUE! | 1.535 | 0.63 | 0.905 | 20 | 8.4 | 23.885 | 55.5 | #DIV/0! | #DIV/0! | 6.74 | 15.7 | 22.44 | 50.35 | 16.7 | 16.7 | 21.7 | 8.075 | 6.295 | #DIV/0! | #DIV/0! | #DIV/0! | 113.525 | 119.82 | AVG C4-20 | Average | --- | --- | --- | --- | 8.16 | 21.5 | 0.752 | #DIV/0! | #VALUE! | 1.355 | 0.56 | 0.795 | 20 | 8.3 | 24.26 | 46.5 | #DIV/0! | #DIV/0! | 5.745 | 21.05 | 26.795 | 52 | 29.1 | 19.3 | 22.9 | 12.29 | 8.23 | #DIV/0! | #DIV/0! | #DIV/0! | 135.59 | 143.82
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.3 | 8.4 | 8.4 | 8.3667 | 0.69006 | SDS-Chlorination pH | --- | 8.4 | 8.4 | 8.4 | 8.4 | 0 |  | RPD | --- | --- | --- | --- | 0 | 0 | 3.2037 | #VALUE! | #VALUE! | 3.2573 | 3.1746 | 7.7348 | 0 | 0 | 0.29307 | 19.8198 | #VALUE! | #VALUE! | 10.9792 | 50.9554 | 32.3529 | 14.1013 | 21.5569 | 17.9641 | 51.6129 | 146.7492 | 40.1906 | #VALUE! | #VALUE! | #VALUE! | 7.3552 | 4.8573 |  | RPD | --- | --- | --- | --- | 0 | 0 | 14.3617 | #VALUE! | #VALUE! | 16.9742 | 0 | 28.9308 | 0 | 0 | 0.32976 | 40.8602 | #VALUE! | #VALUE! | 67.3629 | 12.8266 | 24.5195 | 1.9231 | 0 | 10.3627 | 33.1878 | 68.511 | 8.7485 | #VALUE! | #VALUE! | #VALUE! | 2.8173 | 2.1555
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 24 | 23.63 | 24.35 | 23.9933 | 1.5006 | SDS-Incubation time | hours | 23.47 | 24.2 | 24.13 | 23.9333 | 1.6829 | C7-10 | Primary | 1998-06-14 | 15:22 | 47.1167 | 3719.0756 | 8.11 | 21.6 | 1.93 | 0.0232 | 1.2021 | 2.13 | 0.64 | 1.49 | 20 | 8.3 | 24.15 | 120 | BMRL | BMRL | 25.5 | 70.2 | 95.7 | 22.62 | 16.33 | 5.87 | 15.8 | 26 | 15.4 | NA | NA | NA | 86.62 | 102.02 | C7-20 | Primary | 1998-06-16 | 15:22 | 95.1167 | 3753.9378 | 8.16 | 22.2 | 1.82 | 0.0224 | 1.2308 | 2.26 | 0.5 | 1.76 | 20 | 8.4 | 24.37 | 105 | BMRL | BMRL | 20.9 | 73.1 | 94 | 54 | 31.2 | 14.5 | 22.4 | 18.6 | 14 | NA | NA | NA | 140.7 | 154.7
|  |  |  | Estimated full-scale run time, tLCT (days) | 110.8982 | [5 empty] | SDS-TOX | mg Cl- /L | 320 | 280 | 260 | 286.6667 | 10.6572 | SDS-TOX | mg Cl- /L | 300 | 250 | 300 | 283.3333 | 10.1885 | D2-10 | Duplicate | 1998-06-14 | 15:22 | 47.1167 | 3719.0756 | 8.11 | 21.6 | 1.9 | 0.0224 | 1.1789 | 2.11 | 0.48 | 1.63 | 20 | 8.3 | 24.32 | 110 | BMRL | BMRL | 24.3 | 82.4 | 106.7 | 52.9 | 31.1 | 11.3 | 23.8 | 19.3 | 14.4 | NA | NA | NA | 138.4 | 152.8 | D2-20 | Duplicate | 1998-06-16 | 15:22 | 95.1167 | 3753.9378 | 8.18 | 22.1 | 1.86 | 0.0224 | 1.2043 | 2.28 | 0.3 | 1.98 | 20 | 8.4 | 24.33 | 105 | BMRL | BMRL | 23.1 | 79.3 | 102.4 | 50.9 | 30 | 13.2 | 21.3 | 17.3 | 13.2 | NA | NA | NA | 132.7 | 145.9
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | 11.8 | 26.5 | BMRL | 19.15 | 54.2792 | SDS-CHCl3 | mg/L | 14.1 | 11.4 | 45.3 | 23.6 | 79.8355 | AVG C7-10 | Average | --- | --- | --- | --- | 8.11 | 21.6 | 1.915 | 0.0228 | 1.1905 | 2.12 | 0.56 | 1.56 | 20 | 8.3 | 24.235 | 115 | #DIV/0! | #DIV/0! | 24.9 | 76.3 | 101.2 | 37.76 | 23.715 | 8.585 | 19.8 | 22.65 | 14.9 | #DIV/0! | #DIV/0! | #DIV/0! | 112.51 | 127.41 | AVG C7-20 | Average | --- | --- | --- | --- | 8.17 | 22.15 | 1.84 | 0.0224 | 1.2175 | 2.27 | 0.4 | 1.87 | 20 | 8.4 | 24.35 | 105 | #DIV/0! | #DIV/0! | 22 | 76.2 | 98.2 | 52.45 | 30.6 | 13.85 | 21.85 | 17.95 | 13.6 | #DIV/0! | #DIV/0! | #DIV/0! | 136.7 | 150.3
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.4298 | [5 empty] | SDS-BDCM | mg/L | 61.5 | 77 | 52.3 | 63.6 | 19.6277 | SDS-BDCM | mg/L | 66.4 | 40.8 | 96.9 | 68.0333 | 41.2822 |  | RPD | --- | --- | --- | --- | 0 | 0 | 1.5666 | 3.5088 | 1.9425 | 0.9434 | 28.5714 | 8.9744 | 0 | 0 | 0.70146 | 8.6957 | #VALUE! | #VALUE! | 4.8193 | 15.9895 | 10.8696 | 80.1907 | 62.2813 | 63.2499 | 40.404 | 29.5806 | 6.7114 | #VALUE! | #VALUE! | #VALUE! | 46.0226 | 39.8556 |  | RPD | --- | --- | --- | --- | 0.2448 | 0.45147 | 2.1739 | 0 | 2.1739 | 0.88106 | 50 | 11.7647 | 0 | 0 | 0.16427 | 0 | #VALUE! | #VALUE! | 10 | 8.1365 | 8.554 | 5.9104 | 3.9216 | 9.3863 | 5.0343 | 7.2423 | 5.8824 | #VALUE! | #VALUE! | #VALUE! | 5.8522 | 5.855
|  |  |  | RSSCT bed length, lSC (cm) | 18.7206 | [5 empty] | SDS-DBCM | mg/L | 73.8 | 86.3 | 75.8 | 78.6333 | 8.5389 | SDS-DBCM | mg/L | 72.8 | 70.2 | 85.8 | 76.2667 | 10.9587 | C11-10 | Primary | 1998-06-16 | 11:22 | 91.1167 | 7192.1422 | 8.12 | 22 | 3.22 | 0.0424 | 1.3168 | 3.13 | 0.4 | 2.73 | 20 | 8.4 | 24.3 | 160 | BMRL | 7.09 | 30.1 | 65.3 | 102.49 | 68.5 | 19.2 | 19.9 | 3.74 | 21.7 | 10.3 | NA | NA | NA | 133.04 | 143.34 | C11-20 | Primary | 1998-06-21 | 19:22 | 219.1167 | 8647.8044 | 8.13 | 21.8 | 2.84 | 0.037 | 1.3028 | 3.63 | 0.58 | 3.05 | 20 | 8.4 | 24.02 | 145 | BMRL | BMRL | 46.04 | 20.09 | 66.13 | 54.2 | 35.4 | 21.5 | NR | 22.9 | 20.4 | NA | NA | NA | NR | NR
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 264.149 | [5 empty] | SDS-CHBr3 | mg/L | 100 | 107 | 98.7 | 101.9 | 4.3811 | SDS-CHBr3 | mg/L | 106 | 87.7 | 86.1 | 93.2667 | 11.8546 | D3-10 | Duplicate | 1998-06-16 | 11:22 | 91.1167 | 7192.1422 | 8.13 | 22 | 3.18 | 0.0433 | 1.3616 | 3.11 | 0.1 | 3.01 | 20 | 8.4 | 24.32 | 165 | BMRL | 4.73 | 43.2 | 88.3 | 136.23 | 51.7 | 31.5 | 13.1 | 21.4 | 21.3 | 14.1 | NA | NA | NA | 139 | 153.1 | D3-20 | Duplicate | 1998-06-21 | 19:22 | 219.1167 | 8647.8044 | 8.2 | 21.8 | 2.79 | 0.0376 | 1.3477 | 3.58 | 0.52 | 3.06 | 20 | 8.4 | 24.08 | 170 | BMRL | BMRL | 48.82 | NR | NR | 57.8 | 31.5 | 18.9 | NR | 20.8 | 13.5 | NA | NA | NA | NR | NR
|  |  |  | Mass GAC required, mSC (g) | 15.0523 | [5 empty] | SDS-THM4 | mg/L | 247.1 | 296.8 | 226.8 | 256.9 | 14.0188 | SDS-THM4 | mg/L | 259.3 | 210.1 | 314.1 | 261.1667 | 19.9203 | AVG C11-10 | Average | --- | --- | --- | --- | 8.125 | 22 | 3.2 | 0.04285 | 1.3392 | 3.12 | 0.25 | 2.87 | 20 | 8.4 | 24.31 | 162.5 | #DIV/0! | 5.91 | 36.65 | 76.8 | 119.36 | 60.1 | 25.35 | 16.5 | 12.57 | 21.5 | 12.2 | #DIV/0! | #DIV/0! | #DIV/0! | 136.02 | 148.22 | AVG C11-20 | Average | --- | --- | --- | --- | 8.165 | 21.8 | 2.815 | 0.0373 | 1.3252 | 3.605 | 0.55 | 3.055 | 20 | 8.4 | 24.05 | 157.5 | #DIV/0! | #DIV/0! | 47.43 | 20.09 | 66.13 | 56 | 33.45 | 20.2 | NR | 21.85 | 16.95 | #DIV/0! | #DIV/0! | #DIV/0! | NR | NR
[11 empty] | SDS-MCAA* | mg/L | 62.8 | 59.5 | 61 | 61.1 | 2.7042 | SDS-MCAA* | mg/L | 56.6 | 58 | 53.6 | 56.0667 | 4.0094 |  | RPD | --- | --- | --- | --- | 0.12308 | 0 | 1.25 | 2.1004 | 3.3501 | 0.64103 | 120 | 9.7561 | 0 | 0 | 0.082271 | 3.0769 | #VALUE! | 39.9323 | 35.7435 | 29.9479 | 28.2674 | 27.9534 | 48.5207 | 41.2121 | 140.4932 | 1.8605 | 31.1475 | #VALUE! | #VALUE! | #VALUE! | 4.3817 | 6.5848 |  | RPD | --- | --- | --- | --- | 0.85732 | 0 | 1.7762 | 1.6086 | 3.3845 | 1.387 | 10.9091 | 0.32733 | 0 | 0 | 0.24948 | 15.873 | #VALUE! | #VALUE! | 5.8613 | #VALUE! | #VALUE! | 6.4286 | 11.6592 | 12.8713 | NR | 9.611 | 40.708 | #VALUE! | #VALUE! | #VALUE! | NR | NR
[11 empty] | SDS-DCAA* | mg/L | 24.9 | 30.7 | 33.9 | 29.8333 | 15.2922 | SDS-DCAA* | mg/L | 28.3 | 34.2 | 31.5 | 31.3333 | 9.4262 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 14.8 | 13 | 14.6 | 14.1333 | 6.9805 | SDS-TCAA* | mg/L | 10 | 15.7 | 17 | 14.2333 | 26.1594 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 2.53 | 19.4 | 22.4 | 14.7767 | 72.4891 | SDS-MBAA* | mg/L | BMRL | 23.1 | NR | NR | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 30.1 | 21.3 | 21 | 24.1333 | 21.4204 | SDS-DBAA* | mg/L | 30.7 | 22.6 | 12.1 | 21.8 | 42.7788
[11 empty] | SDS-BCAA* | mg/L | 24.1 | 16.1 | 15.4 | 18.5333 | 26.0804 | SDS-BCAA* | mg/L | 24.7 | 16.5 | 18.4 | 19.8667 | 21.6052
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 135.13 | 143.9 | 152.9 | 143.9767 | 6.1713 | SDS-HAA5 | mg/L | 125.6 | 153.6 | NR | NR | #VALUE!
[11 empty] | SDS-HAA6 | mg/L | 159.23 | 160 | 168.3 | 162.51 | 3.0946 | SDS-HAA6 | mg/L | 150.3 | 170.1 | NR | NR | #VALUE!
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (11/8/99): Reviewer adjusted Reynolds number based on revised full-scale temperature supplied by utility.
Note on H8: Reviewer D.S. (10/12/99): Full-scale temperature is 26C, column design based on 20C.
Note on Q35: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on Q53: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Q54: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on S11: M.H. (08/12/99): Changed time from 15:20.
Note on Y35: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on Y53: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Y54: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on AA11: M.H. (08/12/99): Changed time from 15:20.
Note on AA23: M.H. (08/12/99): Changed time from 15:20.
Note on AC39: Reviewer D.S. (10/12/99): Per Consultant: "CHCl3 result for sample B3-20 is correct."
Note on AJ5: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on AJ30: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on AU5: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on AU30: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on BB35: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BD39: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BD43: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BE39: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BE43: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BF39: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BF43: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BG35: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BG39: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BG43: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BH35: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BH39: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BH43: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BI39: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BI43: Reviewer D.S. (10/12/99): Per Consultant: "Results are verified."
Note on BM5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BM30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BN5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BN30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BS5: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on BS30: Reviewer D.S. (10/12/99): Per Consultant: "It is highly unusual tha all the samples were collected at the same time. However, we set up our sampling schedule to do just that. Each sampler was instructed to sample at precise times. Actually, the sampling time is the average time of the sampling range. The same sampling schedule was used for both the first and second quarter."
Note on CD5: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on CD30: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on CJ35: Reviewer D.S. (10/12/99): Per Consultant: "results are verified."
Note on CP35: Reviewer D.S. (10/12/99): Per Consultant: "results are verified."
Note on CQ35: Reviewer D.S. (10/12/99): Per Consultant: "results are verified."
Note on CV5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CV30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CW5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CW30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CZ13: Reviewer M.H. (11/8/99): Per utility, "I could not locate a 98 PPI that made sense on a base year of 1967."
Note on CZ17: Reviewer M.H. (11/8/99): Per utility, "we do not use fuel oil in this region for any purpose."

## Sheet3. 3rd Quarter
FIELD-SET 3: 3rd QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 3-1: PWS And Treatment Plant Data |  | Field 3-2: Full-Scale GAC Characteristics1 |  | Field 3-3: RSSCT Design Parameters |  |  |  | Field 3-4: Pretreatment Used Prior To GAC1 |  |  | Field 3-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 3-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 3-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 3-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 3-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Abilene | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1998-11-09 | [5 empty] | 20-min. EBCT Start Date | 1998-10-29 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2210001 | Carbon trade name | F-300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 15 mg/L alum, 4 mg/L cationic polymer | Bench | 10-min. EBCT Start Time | 6:00 | [5 empty] | 20-min. EBCT Start Time | 16:12 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminus coal | Minimum RSSCT Reynolds number, ReSC, min | 0.453 | 4 | 4.75 | Floculation | 2 min. rapid mix,30 min. slow mix | Bench | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 16 | 6 | 3.35 | Sedimentation | settling for at least 90 min. | Bench | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1998-11-09 | 7:00 | 1 | 78.9333 | 8.17 | 20.8 | BMRL | BMRL | #VALUE! | 1.11 | 1.2 | -0.09 | 20 | 8.5 | 23.08 | 28 | BMRL | 0.11 | 1.52 | 3.47 | 5.1 | 14.48 | BMRL | 5.94 | 11.26 | BMRL | 1.36 | NA | NA | NA | 31.68 | 33.04 | C1-20 | N | 1998-10-29 | 17:11 | 0.99167 | 39.1378 | 8.12 | 22.5 | BMRL | BMRL | #VALUE! | 1.11 | 1.3 | -0.19 | 20 | 8.4 | 23.78 | NR | BMRL | BMRL | BMRL | 3.42 | NR | 23.76 | BMRL | 8.93 | NR | 4.93 | 2.91 | NA | NA | NA | NR | NR | Overhead & Profit Factor (% of construction costs) | 10
Official ICR Contact Person |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 5 um exclusion size | Bench | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1998-11-09 | 10:59 | 4.9833 | 393.3511 | 8.18 | 21.5 | 0.539 | BMRL | #VALUE! | 1.11 | 1.2 | -0.09 | 20 | 8.5 | 23.08 | 32 | 3.38 | 0.92 | 3.49 | 7.37 | 15.16 | 22.41 | BMRL | 7.48 | 9.32 | 7.2 | 1.59 | NA | NA | NA | 46.41 | 48 | C2-20 | N | 1998-10-30 | 9:02 | 16.825 | 664.0267 | 8.17 | 21.5 | 0.659 | 0.0103 | 1.563 | 1.11 | 0.6 | 0.51 | 20 | 8.4 | 24.42 | 25 | BMRL | BMRL | BMRL | 12.26 | 12.26 | 14.25 | BMRL | 7.42 | NR | 9.24 | 1.43 | NA | NA | NA | NR | NR | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.455 | 10 | 2 | Cartridge filtration | 1 um exclusion size | Bench | Sampling date | MM/DD/YY | 1998-11-09 | 1998-11-10 | --- | --- |  | Sampling date | MM/DD/YY | 1998-10-29 | 1998-11-02 | --- | --- |  | AVG C3-10 | Y | 1998-11-09 | 16:59 | 10.9917 | 867.6089 | 8.22 | 21.7 | 0.86 | 0.0066 | 0.76744 | 1.35 | 1.2 | 0.15 | 20 | 8.5 | 23.08 | NR | 1.605 | 1.435 | 2.12 | 14.48 | 19.64 | 20.9 | BMRL | 7.01 | 9.545 | 14.73 | 3.435 | NA | NA | NA | 52.185 | 55.62 | C3-20 | N | 1998-10-30 | 11:20 | 19.125 | 754.8 | 8.2 | 21.8 | 1.006 | 0.0128 | 1.2724 | 1.17 | 1.2 | -0.03 | 20 | 8.4 | 24.42 | 58 | BMRL | BMRL | 2.15 | 6.84 | 8.99 | 21.49 | BMRL | 6.96 | NR | 15.07 | 1.26 | NA | NA | NA | NR | NR | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 8:18 | 11:00 | --- | --- |  | Sampling time | hh:mm | 16:12 | 13:37 | --- | --- |  | C4-10 | N | 1998-11-09 | 22:59 | 16.9917 | 1341.2089 | 8.17 | 20.4 | 1.38 | 0.0127 | 0.92029 | 1.62 | 1.1 | 0.52 | 20 | 8.5 | 23.08 | 86 | 2.38 | 3.04 | 11.58 | 21.7 | 38.7 | 17.53 | BMRL | 7.11 | 18.94 | 17.18 | 5.53 | NA | NA | NA | 60.76 | 66.29 | AVG C4-20 | Y | 1998-10-31 | 15:20 | 47.125 | 1859.8667 | 8.35 | 21.4 | 1.63 | 0.0148 | 0.90798 | 1.79 | 1.6 | 0.19 | 20 | 8.4 | 24.25 | 107.5 | 0.27145 | 8.855 | 18.93 | 22.08 | 50.1365 | 19.945 | BMRL | 7.64 | NR | 19.46 | 7.28 | NA | NA | NA | NR | NR | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 2.3 | 29 | --- | --- |  | Operation time | hh.hh | 0 | 93.4167 | --- | --- |  | C5-10 | N | 1998-11-10 | 4:59 | 22.9917 | 1814.8089 | 8.2 | 19.4 | 1.91 | 0.0202 | 1.0576 | 1.92 | 1 | 0.92 | 20 | 8.5 | 23.08 | 115 | BMRL | 2.395 | 10.805 | 19.28 | 32.48 | 25.68 | BMRL | 7.56 | BMRL | 19.35 | 7.07 | NA | NA | NA | 52.59 | 59.66 | C5-20 | N | 1998-11-01 | 7:19 | 63.125 | 2491.3333 | 7.97 | 19.7 | 1.745 | NR | #VALUE! | NA | NA | #VALUE! | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 181.5467 | 2289.0667 | --- | --- |  | Bed volumes | (20 minutes) | 0 | 3686.8444 | --- | --- |  | C6-10 | N | 1998-11-10 | 10:59 | 28.9833 | 2287.7511 | 8.21 | 20 | 2.44 | 0.0239 | 0.97951 | 2.22 | 1 | 1.22 | 20 | 8.5 | 23.08 | 160 | BMRL | 3.94 | 13.7 | 20.72 | 38.36 | 28.22 | 2.4 | 8.17 | 25.99 | 21.44 | 8.51 | NA | NA | NA | 86.22 | 94.73 | C6-20 | N | 1998-11-01 | 23:19 | 79.1167 | 3122.4711 | 8.14 | 19.9 | 2.07 | NR | #VALUE! | 2.02 | 1.6 | 0.42 | 20 | 8.4 | 24.25 | 120 | BMRL | 1.18 | 17.16 | 31.9 | 50.24 | 22.58 | BMRL | 4.27 | 22.46 | 19.83 | 9.91 | NA | NA | NA | 69.14 | 79.05 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 170 | 170 | 170 | 0 |  | Alkalinity | mg/L as CaCO3 | 176 | 170 | 173 | 3.4682 |  | AVG C7-10 | Y | 1998-11-10 | 16:00 | 33.9917 | 2683.0756 | 8.24 | 20.6 | 2.93 | 0.029 | 0.98976 | 2.49 | 1.43 | 1.06 | 20 | 8.5 | 23.08 | NR | 3.805 | 0.56 | 22.295 | 30.56 | 57.22 | 12.3 | 2.345 | 8.345 | 13.335 | 4.75 | 9.505 | NA | NA | NA | 41.075 | 50.58 | AVG C7-20 | Y | 1998-11-02 | 15:20 | 95.125 | 3754.2667 | 8.17 | 20.4 | 2.54 | 0.0281 | 1.1063 | 2.25 | 2 | 0.25 | 20 | 8.4 | 24.25 | 150 | 7.665 | 8.23 | 25.575 | 35.59 | 77.06 | 31.66 | BMRL | 3.56 | 10.54 | 15.145 | 4.95 | NA | NA | NA | 60.905 | 65.855 | Labor Rate + Fringe ($/work-hour) | 15
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3071.0258 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 233 | 260 | 246.5 | 10.9533 |  | Total hardness | mg/L as CaCO3 | 246 | 241 | 243.5 | 2.0534 |  | C8-10 | N | 1998-11-10 | 21:00 | 38.9917 | 3077.7422 | 8.21 | 20.5 | 3.01 | 0.0311 | 1.0332 | 2.54 | 1.4 | 1.14 | 20 | 8.5 | 23.08 | NR | BMRL | 1.11 | 23.37 | 37.38 | 61.86 | 16.62 | 2.54 | 8.03 | 20.15 | 23.83 | 11.45 | NA | NA | NA | 71.17 | 82.62 | C8-20 | N | 1998-11-03 | 7:19 | 111.125 | 4385.7333 | 8.12 | 20.1 | 2.64 | 0.0327 | 1.2386 | 2.31 | 2 | 0.31 | 20 | 8.4 | 24.25 | 170 | BMRL | BMRL | 25.25 | 37.37 | 62.62 | 26.27 | BMRL | 7.86 | 22.21 | 16.87 | 10.31 | NA | NA | NA | 73.21 | 83.52 | Labor Overhead Factor (% of labor) | 15
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 6142.0516 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 109 | 133 | 121 | 19.8347 |  | Calcium hardness | mg/L as CaCO3 | 112 | 110 | 111 | 1.8018 |  | C9-10 | N | 1998-11-11 | 6:00 | 47.9917 | 3788.1422 | 8.18 | 20.5 | 3.36 | 0.0355 | 1.0565 | 2.74 | 1.5 | 1.24 | 20 | 8.5 | 23.08 | NR | BMRL | 7.75 | 35.13 | 50.14 | 93.02 | 24.81 | 3.98 | 7.1 | 24.67 | 6.37 | 12.71 | NA | NA | NA | 66.93 | 79.64 | C9-20 | N | 1998-11-04 | 9:23 | 137.1833 | 5414.1689 | 8.07 | 20.1 | 2.94 | 0.0358 | 1.2177 | 2.6 | 2 | 0.6 | 20 | 8.4 | 24.25 | 150 | BMRL | BMRL | 27.35 | 37.38 | 64.73 | 24.49 | BMRL | 7.89 | 22.35 | 18.81 | 12.37 | NA | NA | NA | 73.54 | 85.91 | Electric Rate ($/kW-h) | 0.056
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7984.6671 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | 0.1 | 0.09 | 0.095 | 10.5263 |  | Ammonia | mg NH3-N / L | 0.14 | 0.12 | 0.13 | 15.3846 |  | AVG C10-10 | Y | 1998-11-11 | 13:59 | 55.9917 | 4419.6089 | 8.31 | 20.7 | 3.49 | 0.0397 | 1.1375 | 2.835 | 1.35 | 1.485 | 20 | 8.5 | 23.08 | 205 | 15.265 | 4.955 | 39.23 | 52.36 | 111.81 | 37.74 | 2.75 | 11.575 | 19.94 | 16.82 | 9.76 | NA | NA | NA | 88.825 | 98.585 | AVG C10-20 | Y | 1998-11-05 | 11:58 | 163.775 | 6463.6533 | 8.19 | 20.5 | 3.39 | 0.0416 | 1.2271 | 2.76 | 1.05 | 1.71 | 20 | 8.35 | 23.42 | 200 | BMRL | 6.56 | 33.34 | 44.66 | 84.56 | 18.235 | 1.96 | 7.035 | 21.83 | 22.32 | 12.14 | NA | NA | NA | 71.38 | 83.52 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 620 | 640 | 630 | 3.1746 |  | Bromide | mg/L | 630 | 620 | 625 | 1.6 |  | C11-10 | N | 1998-11-11 | 22:00 | 63.9917 | 5051.0756 | 8.26 | 20.3 | 3.7 | 0.043 | 1.1622 | 2.93 | 1.34 | 1.59 | 20 | 8.5 | 23.08 | 200 | BMRL | 4.15 | 38.49 | 53.53 | 96.17 | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | C11-20 | N | 1998-11-06 | 11:30 | 187.3 | 7392.1067 | 8.2 | 20.2 | 3.66 | 0.0454 | 1.2404 | 2.93 | 1 | 1.93 | 20 | 8.4 | 23.42 | 200 | BMRL | BMRL | 29.8 | 43.52 | 73.32 | 26.55 | 0.62 | 7.42 | 19.66 | 18.98 | 11.3 | NA | NA | NA | 73.23 | 84.53 | Natural Gas Rate ($/ft3) | 0.003
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1998-11-12 | 4:59 | 70.9917 | 5603.6089 | 8.22 | 20.1 | 3.8 | 0.0463 | 1.2184 | 2.99 | 1.35 | 1.64 | 20 | 8.5 | 23.08 | 305 | BMRL | 5.16 | 38.48 | 44.7 | 88.34 | 17.58 | BMRL | 11.71 | 22.9 | 25.74 | 13.98 | NA | NA | NA | 77.93 | 91.91 | C12-20 | N | 1998-11-07 | 11:30 | 211.3 | 8339.3067 | 8.3 | 20 | 3.89 | 0.0464 | 1.1928 | 3.05 | 0.95 | 2.1 | 20 | 8.4 | 23.42 | 225 | BMRL | BMRL | 29.86 | 42.32 | 72.18 | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.1336e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [40 empty] | C13-20 | N | 1998-11-08 | 11:30 | 235.3 | 9286.5067 | NR | NR | 4.02 | 0.0505 | 1.2562 | 3.1 | 1 | 2.1 | 20 | 8.35 | 23.42 | 205 | 3.5 | 4.53 | 28.8 | 33.2 | 70.03 | NR | NR | NR | NR | NR | NR | NA | NA | NA | NR | NR | Modifications to Existing Plant (% of construction costs) | 15
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD | [34 empty] | C14-20 | N | 1998-11-09 | 11:30 | 259.3 | 10233.7067 | 8.18 | 21.1 | 4.14 | 0.0549 | 1.3261 | 3.16 | 0.9 | 2.26 | 20 | 8.35 | 23.42 | 210 | 4.38 | 5.16 | 30.19 | 33.52 | 73.25 | 42.7 | 4.32 | 4.96 | 15.36 | 17.68 | 11.14 | NA | NA | NA | 85.02 | 96.16
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1998-11-09 | 1998-11-10 | 1998-11-12 | --- | --- | Sampling date | MM/DD/YY | 1998-10-29 | 1998-11-02 | 1998-11-09 | --- | ---
Plant Name | Grimes Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3945 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 8:18 | 11:00 | 5:45 | --- | --- | Sampling time | hh:mm | 16:12 | 13:37 | 12:20 | --- | ---
Treatment Plant Category | Conventional |  |  | RSSCT flow rate, QSC (mL/min) | 21.7786 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 2.3 | 29 | 71.75 | --- | --- | Operation time | hh.hh | 0 | 93.4167 | 260.1333 | --- | ---
Process Train Name | Conv |  |  | Estimated total influent volume required, VSCT (L) | 396.5511 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 181.5467 | 2289.0667 | 5663.4667 | --- | --- | Bed volumes | (20 minute) | 0 | 3686.8444 | 10266.5956 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 652 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 8.13 | 8.17 | 8.22 | 8.1733 | 0.5517 | pH | --- | 8.01 | 8.09 | 8.17 | 8.09 | 0.98888 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2210001 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.14 | 0.18 | 0.16 | 0.16 | 12.5 | Turbidity | ntu | 0.17 | 0.22 | 0.19 | 0.19333 | 13.017 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 20.3 | 19.5 | 20.1 | 19.9667 | 2.0851 | Temperature | oC | 22 | 19.7 | 19.9 | 20.5333 | 6.205
Historical Average Water Temperature (oC) | 19.5 |  |  | Estimated full-scale run time, tLCT (days) | 55.4491 | [5 empty] | Total organic carbon | mg/L | 5.2 | 5.06 | 5.11 | 5.1233 | 1.3848 | Total organic carbon | mg/L | 4.989 | 5.096 | 5.2 | 5.095 | 2.0707 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 25 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.0828 | 0.0796 | 0.0814 | 0.081267 | 1.9739 | UV254 | cm-1 | 0.0874 | 0.0826 | 0.0861 | 0.085367 | 2.9082 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 4.2149 | [5 empty] | SUVA | L/(mg*m) | 1.5923 | 1.5731 | 1.593 | 1.5861 | 0.71041 | SUVA | L/(mg*m) | 1.7519 | 1.6209 | 1.6558 | 1.6762 | 4.0466 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 9.368 | [5 empty] | SDS-Cl2 dose | mg/L | 3.79 | 3.7 | 3.73 | 3.74 | 1.2253 | SDS-Cl2 dose | mg/L | 3.45 | 3.73 | 3.79 | 3.6567 | 4.9629 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 132.1837 | [5 empty] | SDS-Free Cl2 residual | mg/L | 1.2 | 1.4 | 1.2 | 1.2667 | 9.1161 | SDS-Free Cl2 residual | mg/L | 2.4 | 0.17 | 1 | 1.19 | 94.7123 | C3-10 | Primary | 1998-11-09 | 16:59 | 10.9917 | 867.6089 | 8.22 | 21.7 | 0.82 | 0.006 | 0.73171 | 1.34 | 1.1 | 0.24 | 20 | 8.5 | 23.08 | 86 | 3.21 | 2.87 | 4.24 | 3.47 | 13.79 | 20.9 | BMRL | 6.24 | 15.91 | 12.41 | 2.03 | NA | NA | NA | 55.46 | 57.49 | C4-20 | Primary | 1998-10-31 | 15:20 | 47.125 | 1859.8667 | 8.35 | 21.4 | 1.713 | 0.0164 | 0.95738 | 1.79 | 1.6 | 0.19 | 20 | 8.4 | 24.25 | 90 | BMRL | BMRL | 10.59 | 25.52 | 36.11 | 19.67 | BMRL | 8.31 | NR | 20.37 | 7.38 | NA | NA | NA | NR | NR
|  |  |  | Mass GAC required, mSC (g) | 7.5324 | [5 empty] | SDS-Cl2 demand | mg/L | 2.59 | 2.3 | 2.53 | 2.4733 | 6.1892 | SDS-Cl2 demand | mg/L | 1.05 | 3.56 | 2.79 | 2.4667 | 52.1294 | D1-10 | Duplicate | 1998-11-09 | 16:59 | 10.9917 | 867.6089 | 8.22 | 21.7 | 0.89 | 0.0072 | 0.80899 | 1.36 | 1.3 | 0.06 | 20 | 8.5 | 23.08 | NR | BMRL | BMRL | BMRL | 2.37 | 23.87 | NR | BMRL | 7.78 | 16.5 | 17.05 | 4.84 | NA | NA | NA | NR | NR | D1-20 | Duplicate | 1998-10-31 | 15:20 | 47.125 | 1859.8667 | 8.35 | 21.4 | 1.546 | 0.0131 | 0.84735 | 1.79 | 1.6 | 0.19 | 20 | 8.4 | 24.25 | 125 | 0.5429 | 17.71 | 27.27 | 18.64 | 64.1629 | 20.22 | BMRL | 6.97 | NR | 18.55 | 7.18 | NA | NA | NA | NR | NR
[11 empty] | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 | SDS-Chlorination temp. | oC | 20 | 20 | 20 | 20 | 0 |  | Average | --- | --- | --- | --- | 8.22 | 21.7 | 0.855 | 0.0066 | 0.77035 | 1.35 | 1.2 | 0.15 | 20 | 8.5 | 23.08 | 86 | 3.21 | 2.87 | 4.24 | 2.92 | 18.83 | 20.9 | #DIV/0! | 7.01 | 16.205 | 14.73 | 3.435 | #DIV/0! | #DIV/0! | #DIV/0! | 55.46 | 57.49 |  | Average | --- | --- | --- | --- | 8.35 | 21.4 | 1.6295 | 0.01475 | 0.90237 | 1.79 | 1.6 | 0.19 | 20 | 8.4 | 24.25 | 107.5 | 0.5429 | 17.71 | 18.93 | 22.08 | 50.1365 | 19.945 | #DIV/0! | 7.64 | #DIV/0! | 19.46 | 7.28 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.5 | 8.5 | 8.5 | 8.5 | 0 | SDS-Chlorination pH | --- | 8.4 | 8.5 | 8.5 | 8.4667 | 0.68191 |  | RPD | --- | --- | --- | --- | 0 | 0 | 8.1871 | 18.1818 | 10.032 | 1.4815 | 16.6667 | 120 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 37.6712 | 53.5316 | #VALUE! | #VALUE! | 21.9686 | 3.6409 | 31.5003 | 81.8049 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 10.2485 | 22.3729 | 12.1942 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5581 | #VALUE! | #VALUE! | 88.1141 | 31.1594 | 55.9531 | 2.7576 | #VALUE! | 17.5393 | #VALUE! | 9.3525 | 2.7473 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 23.08 | 23.08 | 23.08 | 23.08 | 0 | SDS-Incubation time | hours | 23.78 | 22.83 | 24.67 | 23.76 | 3.8727 | C7-10 | Primary | 1998-11-10 | 16:00 | 33.9917 | 2683.0756 | 8.24 | 20.6 | 2.94 | 0.0295 | 1.0034 | 2.5 | 1.5 | 1 | 20 | 8.5 | 23.08 | NR | BMRL | 1.12 | 21.36 | 30.81 | 53.29 | 12.3 | 3.25 | 6.44 | 15.03 | 5.22 | 10.84 | NA | NA | NA | 42.24 | 53.08 | C7-20 | Primary | 1998-11-02 | 15:20 | 95.125 | 3754.2667 | 8.17 | 20.4 | 2.55 | 0.0279 | 1.0941 | 2.25 | 2 | 0.25 | 20 | 8.4 | 24.25 | 150 | BMRL | BMRL | 17.76 | 33.66 | 51.42 | 30.64 | BMRL | 2.51 | 10.54 | 8.81 | 0.76 | NA | NA | NA | 52.5 | 53.26
|  |  |  | Estimated full-scale run time, tLCT (days) | 110.8982 | [5 empty] | SDS-TOX | mg Cl- /L | 345 | 300 | 340 | 328.3333 | 7.512 | SDS-TOX | mg Cl- /L | 300 | NR | NR | 300 | #DIV/0! | D2-10 | Duplicate | 1998-11-10 | 16:00 | 33.9917 | 2683.0756 | 8.24 | 20.6 | 2.91 | 0.0284 | 0.97595 | 2.48 | 1.35 | 1.13 | 20 | 8.5 | 23.08 | NR | 7.61 | BMRL | 23.23 | 30.31 | 61.15 | NR | 1.44 | 10.25 | 11.64 | 4.28 | 8.17 | NA | NA | NA | NR | NR | D2-20 | Duplicate | 1998-11-02 | 15:20 | 95.125 | 3754.2667 | 8.17 | 20.4 | 2.52 | 0.0283 | 1.123 | 2.25 | 2 | 0.25 | 20 | 8.4 | 24.25 | 150 | 15.33 | 16.46 | 33.39 | 37.52 | 102.7 | 32.68 | BMRL | 4.61 | NR | 21.48 | 9.14 | NA | NA | NA | NR | NR
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | 29.57 | 6.89 | 17.48 | 17.98 | 63.116 | SDS-CHCl3 | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! |  | Average | --- | --- | --- | --- | 8.24 | 20.6 | 2.925 | 0.02895 | 0.98967 | 2.49 | 1.425 | 1.065 | 20 | 8.5 | 23.08 | #DIV/0! | 7.61 | 1.12 | 22.295 | 30.56 | 57.22 | 12.3 | 2.345 | 8.345 | 13.335 | 4.75 | 9.505 | #DIV/0! | #DIV/0! | #DIV/0! | 42.24 | 53.08 |  | Average | --- | --- | --- | --- | 8.17 | 20.4 | 2.535 | 0.0281 | 1.1086 | 2.25 | 2 | 0.25 | 20 | 8.4 | 24.25 | 150 | 15.33 | 16.46 | 25.575 | 35.59 | 77.06 | 31.66 | #DIV/0! | 3.56 | 10.54 | 15.145 | 4.95 | #DIV/0! | #DIV/0! | #DIV/0! | 52.5 | 53.26
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.4298 | [5 empty] | SDS-BDCM | mg/L | 31.81 | 22.25 | 28.33 | 27.4633 | 17.6183 | SDS-BDCM | mg/L | BMRL | BMRL | BMRL | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | 0 | 0 | 1.0256 | 3.7997 | 2.7743 | 0.80321 | 10.5263 | 12.2066 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 8.3875 | 1.6361 | 13.7365 | #VALUE! | 77.1855 | 45.6561 | 25.4218 | 19.7895 | 28.0905 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 1.1834 | 1.4235 | 2.6068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 61.1144 | 10.8457 | 66.5455 | 6.4435 | #VALUE! | 58.9888 | #VALUE! | 83.658 | 169.2929 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | RSSCT bed length, lSC (cm) | 18.7361 | [5 empty] | SDS-DBCM | mg/L | 54.25 | 46.87 | 52.49 | 51.2033 | 7.528 | SDS-DBCM | mg/L | BMRL | 17.66 | 21.71 | 19.685 | 14.548 | C10-10 | Primary | 1998-11-11 | 13:59 | 55.9917 | 4419.6089 | 8.31 | 20.7 | 3.5 | 0.0396 | 1.1314 | 2.82 | 1.4 | 1.42 | 20 | 8.5 | 23.08 | 205 | BMRL | 6.85 | 40.89 | 54.33 | 102.07 | 37.74 | 2.23 | 10.88 | 19.76 | 26.92 | 13.24 | NA | NA | NA | 97.53 | 110.77 | C10-20 | Primary | 1998-11-05 | 11:58 | 163.775 | 6463.6533 | 8.19 | 20.5 | 3.31 | 0.0415 | 1.2538 | 2.7 | 1 | 1.7 | 20 | 8.3 | 23.42 | 210 | BMRL | BMRL | 29.86 | 45.96 | 75.82 | 21.31 | 1.96 | 7.63 | 21.83 | 19.68 | 12.39 | NA | NA | NA | 72.41 | 84.8
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 264.3674 | [5 empty] | SDS-CHBr3 | mg/L | 49.05 | 46.2 | 49.7 | 48.3167 | 3.8531 | SDS-CHBr3 | mg/L | 30.88 | 32.99 | 38 | 33.9567 | 10.7699 | D3-10 | Duplicate | 1998-11-11 | 13:59 | 55.9917 | 4419.6089 | 8.31 | 20.7 | 3.48 | 0.0398 | 1.1437 | 2.85 | 1.3 | 1.55 | 20 | 8.5 | 23.08 | NR | 30.53 | 3.06 | 37.57 | 50.39 | 121.5 | NR | 3.27 | 12.27 | 20.12 | 6.72 | 6.28 | NA | NA | NA | NR | NR | D3-20 | Duplicate | 1998-11-05 | 11:58 | 163.775 | 6463.6533 | 8.19 | 20.5 | 3.47 | 0.0417 | 1.2017 | 2.82 | 1.1 | 1.72 | 20 | 8.4 | 23.42 | 190 | BMRL | 13.12 | 36.82 | 43.36 | 93.3 | 15.16 | BMRL | 6.44 | NR | 24.96 | 11.89 | NA | NA | NA | NR | NR
|  |  |  | Mass GAC required, mSC (g) | 15.0648 | [5 empty] | SDS-THM4 | mg/L | 164.68 | 122.21 | 148 | 144.9633 | 14.7604 | SDS-THM4 | mg/L | 30.88 | 50.65 | 59.71 | 47.08 | 31.3144 |  | Average | --- | --- | --- | --- | 8.31 | 20.7 | 3.49 | 0.0397 | 1.1376 | 2.835 | 1.35 | 1.485 | 20 | 8.5 | 23.08 | 205 | 30.53 | 4.955 | 39.23 | 52.36 | 111.785 | 37.74 | 2.75 | 11.575 | 19.94 | 16.82 | 9.76 | #DIV/0! | #DIV/0! | #DIV/0! | 97.53 | 110.77 |  | Average | --- | --- | --- | --- | 8.19 | 20.5 | 3.39 | 0.0416 | 1.2278 | 2.76 | 1.05 | 1.71 | 20 | 8.35 | 23.42 | 200 | #DIV/0! | 13.12 | 33.34 | 44.66 | 84.56 | 18.235 | 1.96 | 7.035 | 21.83 | 22.32 | 12.14 | #DIV/0! | #DIV/0! | #DIV/0! | 72.41 | 84.8
[11 empty] | SDS-MCAA* | mg/L | NR | NR | NR | #DIV/0! | #DIV/0! | SDS-MCAA* | mg/L | 12.52 | 21.94 | 23.13 | 19.1967 | 30.2797 |  | RPD | --- | --- | --- | --- | 0 | 0 | 0.57307 | 0.50378 | 1.0768 | 1.0582 | 7.4074 | 8.7542 | 0 | 0 | 0 | #VALUE! | #VALUE! | 76.4884 | 8.4629 | 7.5248 | 17.3816 | #VALUE! | 37.8182 | 12.0086 | 1.8054 | 120.0951 | 71.3115 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | RPD | --- | --- | --- | --- | 0 | 0 | 4.7198 | 0.48077 | 4.2392 | 4.3478 | 9.5238 | 1.1696 | 0 | 1.1976 | 0 | 10 | #VALUE! | #VALUE! | 20.8758 | 5.8218 | 20.6717 | 33.7264 | #VALUE! | 16.9154 | #VALUE! | 23.6559 | 4.1186 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | SDS-DCAA* | mg/L | 8.79 | 7.44 | 6.71 | 7.6467 | 13.8006 | SDS-DCAA* | mg/L | 7.25 | 5.66 | 5.79 | 6.2333 | 14.1635 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 12.21 | 10.41 | 6.78 | 9.8 | 28.2236 | SDS-TCAA* | mg/L | 6.52 | 7.41 | 4.61 | 6.18 | 23.1493 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 24.06 | 21.64 | 23.32 | 23.0067 | 5.39 | SDS-MBAA* | mg/L | NR | NR | NR | #DIV/0! | #DIV/0!
[11 empty] | SDS-DBAA* | mg/L | 26.46 | 26.37 | 26.57 | 26.4667 | 0.37846 | SDS-DBAA* | mg/L | 25.07 | 26.87 | 24 | 25.3133 | 5.7298
[11 empty] | SDS-BCAA* | mg/L | 16.94 | 16.21 | 16.33 | 16.4933 | 2.3734 | SDS-BCAA* | mg/L | 12.87 | 14.41 | 15.08 | 14.12 | 8.0254
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | NR | NR | NR | #DIV/0! | #DIV/0! | SDS-HAA5 | mg/L | NR | NR | NR | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA6 | mg/L | NR | NR | NR | #DIV/0! | #DIV/0! | SDS-HAA6 | mg/L | NR | NR | NR | #DIV/0! | #DIV/0!
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H7: Reviewer M.H. (11/8/99): Reviewer adjusted Reynolds number based on revised full-scale temperature supplied by utility.
Note on H8: Reviewer D.S. (10/12/99): Full-scale temperature is 16C, column design based on 20C.
Note on Q35: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on Q53: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Q54: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Y35: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on Y43: Reviewer D.S. (10/12/99): Per Consultant: "The THM influent curve has been verified to be below the effluent breakthrough curve."
Note on Y53: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Y54: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on AA11: M.H. (08/12/99): Changed time from 15:12.
Note on AA23: M.H. (08/12/99): Changed time from 15:12.
Note on AJ5: Reviewer D.S. (10/12/99): Per Consultant: "XX:59 sampling time have been verified."
Note on AU5: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on AU30: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on AX19: Reviewer D.S. (10/12/99): Per Consultant: "TOX result in cell AX19 is correct."
Note on AZ43: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BH43: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BI43: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BM5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BM30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BN5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BN30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BP12: Reviewer D.S. (10/12/99): Per Consultant on sample C5-20: "Sample C5-20 was spilled."
Note on CD5: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on CD30: Reviewer D.S. (10/12/99): Per Consultant on SDS temperature: "The reported results are the measured results."
Note on CJ35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on CJ39: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on CJ43: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on CK35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on CV5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CV19: Reviewer D.S. (10/12/99): Per Consultant: "Samples C12-20 and C13-20 internal standard failed."
Note on CV20: Reviewer D.S. (10/12/99): Per Consultant: "Samples C12-20 and C13-20 internal standard failed."
Note on CV30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CW5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CW19: Reviewer D.S. (10/12/99): Per Consultant: "Samples C12-20 and C13-20 internal standard failed."
Note on CW20: Reviewer D.S. (10/12/99): Per Consultant: "Samples C12-20 and C13-20 internal standard failed."
Note on CW30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CZ13: Reviewer M.H. (11/8/99): Per utility, "I could not locate a 98 PPI that made sense on a base year of 1967."
Note on CZ17: Reviewer M.H. (11/8/99): Per utility, "we do not use fuel oil in this region for any purpose."

## Sheet4. 4th Quarter
FIELD-SET 4: 4th QUARTER RSSCT RESULTS (FILE: gacrssct.xls)
Field 4-1: PWS And Treatment Plant Data |  | Field 4-2: Full-Scale GAC Characteristics1 |  | Field 4-3: RSSCT Design Parameters |  |  |  | Field 4-4: Pretreatment Used Prior To GAC1 |  |  | Field 4-5: GAC Influent Water Quality For The 10-Minute EBCT Run | [6 empty] | Field 4-6: GAC Influent Water Quality For The 20-Minute EBCT Run1 | [6 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run1 | [15 empty] | Field 4-7: GAC Effluent Water Quality For The 10-Minute EBCT Run (continued) | [17 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run1 | [14 empty] | Field 4-8: GAC Effluent Water Quality For The 20-Minute EBCT Run (continued) | [18 empty] | Field 4-9: GAC Cost Parameters
|  |  |  | Input Design Parameters |  | US Standard Mesh Sizes | [18 empty] | Group C, 12 effluent samples per run | [33 empty] | Group C, 12 effluent samples per run
PWS Name | City of Abilene | Carbon manufacturer | Calgon | RSSCT influent TOC (mg/L) | 4.5 | US standard | Opening | Process | Description | Scale | 10-min. EBCT Start Date | 1999-01-19 | [5 empty] | 20-min. EBCT Start Date | 1999-01-19 | [5 empty] | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Was sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Cost Parameter | Parameter value
Public Water System Identification Number | TX2210001 | Carbon trade name | F-300 | Inner diameter of the RSSCT column, DSC (mm) | 15 | mesh size | (mm) | Coagulation | 15 mg/L alum, 4 mg/L cationic polymer | Bench | 10-min. EBCT Start Time | 5:45 | [5 empty] | 20-min. EBCT Start Time | 15:45 | [5 empty] | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | duplicated? | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | Capital Recovery Interest Rate (%) | 10
Water Industry Data Base Number (optional) | NA | Carbon type | Bituminus coal | Minimum RSSCT Reynolds number, ReSC, min | 0.388 | 4 | 4.75 | Floculation | 2 min. rapid mix,30 min. slow mix | Bench | [15 empty] | Y/N | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  | Y/N | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | Capital Recovery Period (years) | 20
|  | Original GAC mesh size, upper (US standard mesh) | 8 | Full-scale operating temperature, ToC (oC) | 10 | 6 | 3.35 | Sedimentation | settling for at least 90 min. | Bench | Group A, 2 samples per batch | [6 empty] | Group A, 2 samples per batch | [6 empty] | C1-10 | N | 1999-01-19 | 6:46 | 1.0167 | 80.2489 | 8.04 | 21 | BMRL | BMRL | #VALUE! | 1.11 | 1 | 0.11 | 20.5 | 8.5 | 23.2 | BMRL | 4.24 | 2.1 | 2.35 | 6.3 | 14.99 | 31.2 | 14.6 | 27.6 | 20.56 | 4.45 | 10.34 | NA | NA | NA | 98.41 | 108.75 | C1-20 | N | 1999-01-19 | 16:46 | 1.0167 | 40.1244 | 7.95 | 21.3 | BMRL | BMRL | #VALUE! | 0.83 | 0.8 | 0.03 | 20.5 | 8.4 | 23 | BMRL | BMRL | BMRL | 1.82 | 4.53 | 6.35 | BMRL | 11.25 | 22.92 | 12.36 | BMRL | 7.44 | NA | NA | NA | 46.53 | 53.97 | Overhead & Profit Factor (% of construction costs) | 10
0 |  | Original GAC mesh size, lower (US standard mesh) | 30 | Full-scale bed porosity, eLC | 0.45 | 8 | 2.36 | Cartridge filtration | 5 um exclusion size | Bench | Parameter | Units | Sample A1-10 | Sample A2-10 | Average | RPD |  | Parameter | Units | Sample A1-20 | Sample A2-20 | Average | RPD |  | C2-10 | N | 1999-01-19 | 11:00 | 5.25 | 414.4 | 8.02 | 21.3 | BMRL | BMRL | #VALUE! | 1.11 | 1 | 0.11 | 20.5 | 8.5 | 23.2 | 25 | BMRL | BMRL | 2.71 | 8.52 | 11.23 | BMRL | 12.42 | 22.03 | 17.39 | 5.1 | 8.76 | NA | NA | NA | 56.94 | 65.7 | C2-20 | N | 1999-01-20 | 7:00 | 15.25 | 601.8667 | 7.99 | 21.4 | BMRL | BMRL | #VALUE! | 0.88 | 1 | -0.12 | 20.5 | 8.4 | 23 | BMRL | 3.31 | BMRL | 3.07 | 8.18 | 14.56 | BMRL | 11.88 | BMRL | 14.76 | 1.84 | 8.19 | NA | NA | NA | 28.48 | 36.67 | Special Sitework Factor (% of construction costs) | 10
Mailing Address |  | Original carbon particle diameter, dLC (mm) | 1.48 | Measured RSSCT dry bed density, rSC (g/cm3) | 0.455 | 10 | 2 | Cartridge filtration | 1 um exclusion size | Bench | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-20 | --- | --- |  | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-23 | --- | --- |  | AVG C3-10 | Y | 1999-01-19 | 17:00 | 11.25 | 888 | 8.01 | 21.6 | BMRL | BMRL | #VALUE! | 1.11 | 0.9 | 0.21 | 20.5 | 8.5 | 23.2 | 40 | 6.92 | 4.94 | 9.185 | 24.5275 | 45.5725 | 14.695 | 12.38 | 25.395 | 16.79 | 8.875 | 9.66 | NA | NA | NA | 78.135 | 87.795 | C3-20 | N | 1999-01-20 | 23:00 | 31.25 | 1233.3333 | 8.13 | 21.5 | BMRL | BMRL | #VALUE! | 0.98 | 1 | -0.02 | 20.5 | 8.5 | 23 | 38 | 4.12 | BMRL | 6.17 | 15.86 | 26.15 | BMRL | 12.16 | 23.84 | 15.34 | 10.54 | 8.18 | NA | NA | NA | 61.88 | 70.06 | Construction Contingencies (% of construction costs) | 10
|  | 1: These are the characteristics before the carbon is ground for RSSCT experiments. |  | RSSCT GAC mesh size, upper (US standard mesh) | 100 | 12 | 1.68 |  |  |  | Sampling time | hh:mm | 6:02 | 10:15 | --- | --- |  | Sampling time | hh:mm | 16:00 | 16:30 | --- | --- |  | C4-10 | N | 1999-01-19 | 23:00 | 17.25 | 1361.6 | 7.96 | 21.8 | 0.601 | 0.009 | 1.4975 | 1.17 | 1 | 0.17 | 20.5 | 8.5 | 23.2 | 58 | 3.4 | BMRL | 8.39 | 17.73 | 29.52 | 29.84 | 14.97 | 28.49 | 22.03 | 15.75 | 4.12 | NA | NA | NA | 111.08 | 115.2 | AVG C4-20 | Y | 1999-01-21 | 15:15 | 47.5 | 1874.6667 | 8.06 | 20.7 | 0.516 | BMRL | #VALUE! | 1.115 | 0.9 | 0.215 | 20.5 | 8.5 | 23.4 | 65 | BMRL | BMRL | 11.265 | 30.005 | 41.27 | 1.08 | 24.31 | 25.82 | 25.19 | 19.59 | 11.89 | NA | NA | NA | 95.99 | 107.88 | Engineering Fee Factor (% of construction costs) | 10
Phone Number |  |  |  | RSSCT GAC mesh size, lower (US standard mesh) | 200 | 16 | 1.18 |  |  |  | Operation time | hh.hh | 0.28333 | 28.5 | --- | --- |  | Operation time | hh.hh | 0.25 | 96.75 | --- | --- |  | C5-10 | N | 1999-01-20 | 5:00 | 23.25 | 1835.2 | 7.99 | 22 | 0.829 | 0.0131 | 1.5802 | 1.3 | 1 | 0.3 | 20.5 | 8.5 | 23.2 | 89 | BMRL | BMRL | 15.21 | 34.26 | 49.47 | BMRL | 12.7 | 26.83 | 17.67 | 16.66 | 3.69 | NA | NA | NA | 73.86 | 77.55 | C5-20 | N | 1999-01-22 | 7:00 | 63.25 | 2496.2667 | 8.02 | 20.8 | 0.749 | 0.0062 | 0.82777 | 1.25 | 1 | 0.25 | 20.5 | 8.3 | 23.4 | 87 | BMRL | BMRL | 16.06 | 41.95 | 58.01 | 50.7 | 16.1 | 16.9 | 18.47 | 18.22 | 4.97 | NA | NA | NA | 120.39 | 125.36 | 1998 ENR Construction Cost Index (CCI base year 1913) | 5920
FAX Number | [5 empty] | 20 | 0.85 |  |  |  | Bed volumes | (10 minutes) | 22.3644 | 2249.6 | --- | --- |  | Bed volumes | (20 minutes) | 9.8667 | 3818.4 | --- | --- |  | C6-10 | N | 1999-01-20 | 11:00 | 29.25 | 2308.8 | 7.99 | 21.8 | 0.913 | 0.016 | 1.7525 | 1.4 | 0.8 | 0.6 | 20.5 | 8.4 | 22.7 | 97 | BMRL | BMRL | 10.63 | 37.16 | 47.79 | BMRL | 13.59 | 28.6 | 18.72 | 21.18 | 6.27 | NA | NA | NA | 82.09 | 88.36 | C6-20 | N | 1999-01-22 | 21:00 | 77.25 | 3048.8 | 8.12 | 20.4 | 1.265 | 0.0181 | 1.4308 | 1.57 | 0.9 | 0.67 | 20.5 | 8.3 | 23.4 | 97 | BMRL | BMRL | 20.06 | 44.29 | 64.35 | 47.51 | 10.87 | 28.37 | 28.83 | 30.44 | 6.5 | NA | NA | NA | 146.02 | 152.52 | 1998 Producers Price Index (PPI base year 1967 = 100) | NA
E-Mail Address (optional) |  |  |  | Estimated Run Length |  | 30 | 0.6 |  |  |  | Alkalinity | mg/L as CaCO3 | 178 | 174 | 176 | 2.2727 |  | Alkalinity | mg/L as CaCO3 | 178 | 180 | 179 | 1.1173 |  | AVG C7-10 | Y | 1999-01-20 | 17:32 | 35.7833 | 2824.4978 | 8.06 | 21.6 | 1.01 | 0.0226 | 2.2376 | 1.415 | 0.85 | 0.565 | 20.5 | 8.45 | 22.97 | 105 | 3.43 | BMRL | 7.68 | 35.185 | 46.295 | 49.5 | 17.35 | 35 | 24.005 | 28.07 | 8.77 | NA | NA | NA | 153.925 | 162.695 | AVG C7-20 | Y | 1999-01-23 | 15:00 | 95.25 | 3759.2 | 8.22 | 20.4 | 1.4725 | 0.02025 | 1.3752 | 1.69 | 1 | 0.69 | 20.5 | 8.35 | 23.4 | 118 | BMRL | BMRL | 17.625 | 38.34 | 55.965 | 54.645 | 23.86 | 34.88 | 35.215 | 33.135 | 7.715 | NA | NA | NA | 181.735 | 189.45 | Labor Rate + Fringe ($/work-hour) | 15
|  |  |  | Bed volumes to 50% TOC breakthrough, BV50 | 3071.0258 | 40 | 0.425 |  |  |  | Total hardness | mg/L as CaCO3 | 242 | 244 | 243 | 0.82305 |  | Total hardness | mg/L as CaCO3 | 240 | 270 | 255 | 11.7647 |  | C8-10 | N | 1999-01-20 | 23:00 | 41.25 | 3256 | 8.07 | 21.5 | 1.22 | 0.0178 | 1.459 | 1.56 | 0.8 | 0.76 | 20.5 | 8.4 | 22.7 | 125 | BMRL | 1.77 | 21.64 | 41.21 | 64.62 | 52.06 | 11.91 | 25.43 | BMRL | 18.12 | 6.52 | NA | NA | NA | 107.52 | 114.04 | C8-20 | N | 1999-01-24 | 7:00 | 111.25 | 4390.6667 | 8.03 | 20.4 | 1.578 | 0.0205 | 1.2991 | 1.75 | 1 | 0.75 | 20.5 | 8.3 | 23.4 | 125 | 1.12 | BMRL | 28.29 | 51.34 | 80.75 | NR | 24.77 | 54.22 | 50.96 | 36.95 | 8.88 | NA | NA | NA | NR | NR | Labor Overhead Factor (% of labor) | 15
Technical ICR Contact Person |  |  |  | Estimated run length, BVT ( = 2 x BV50) | 6142.0516 | 50 | 0.3 |  |  |  | Calcium hardness | mg/L as CaCO3 | 115 | 115 | 115 | 0 |  | Calcium hardness | mg/L as CaCO3 | 114 | 77.2 | 95.6 | 38.4937 |  | C9-10 | N | 1999-01-21 | 8:15 | 50.5 | 3986.1333 | 8.02 | 21.5 | 1.264 | 0.0216 | 1.7089 | 1.54 | 0.8 | 0.74 | 20.5 | 8.3 | 23.4 | 135 | BMRL | 2.96 | 17.92 | 33.07 | 53.95 | NR | 24.66 | 29.9 | 29.34 | 36.37 | 11.89 | NA | NA | NA | NR | NR | C9-20 | N | 1999-01-25 | 7:00 | 135.25 | 5337.8667 | 7.97 | 20.3 | 1.788 | 0.0224 | 1.2528 | 1.87 | 0.8 | 1.07 | 20.5 | 8.3 | 23.4 | 135 | BMRL | 7.65 | 37.95 | 61.45 | 107.05 | NR | 20.4 | 26.37 | 22.96 | 30.39 | 6.94 | NA | NA | NA | NR | NR | Electric Rate ($/kW-h) | 0.056
Mailing Address |  |  |  | BVT + 30% safety factor, BVT+30% ( = 2.6 x BV50) | 7984.6671 | 60 | 0.25 |  |  |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | Ammonia | mg NH3-N / L | BMRL | BMRL | #DIV/0! | #VALUE! |  | AVG C10-10 | Y | 1999-01-21 | 17:30 | 59.75 | 4716.2667 | 8 | 21.3 | 1.546 | 0.0256 | 1.6559 | 1.74 | 0.8 | 0.94 | 20.5 | 8.35 | 23.4 | 155 | BMRL | 6.125 | 32.85 | 51.515 | 90.49 | 52.105 | 24.66 | 28.755 | 28.99 | 37.28 | 13.645 | NA | NA | NA | 171.79 | 185.435 | C10-20 | N | 1999-01-26 | 7:00 | 159.25 | 6285.0667 | 8.05 | 21 | 1.95 | 0.0286 | 1.4667 | 1.93 | 0.75 | 1.18 | 20.5 | 8.4 | 23.83 | NR | BMRL | 4.29 | 31.69 | 52.45 | 88.43 | 36.09 | 25.47 | 40.06 | 34.74 | 37.03 | 12.77 | NA | NA | NA | 173.39 | 186.16 | Fuel Oil Rate ($/gal) | NA
[6 empty] | 70 | 0.21 |  |  |  | Bromide | mg/L | 660 | 630 | 645 | 4.6512 |  | Bromide | mg/L | 660 | 670 | 665 | 1.5038 |  | C11-10 | N | 1999-01-22 | 2:00 | 68.25 | 5387.2 | 7.97 | 20.9 | 1.69 | 0.0291 | 1.7219 | 1.8 | 0.7 | 1.1 | 20.5 | 8.3 | 23.4 | 155 | BMRL | 9.04 | 36.44 | 55.58 | 101.06 | NR | 14.39 | 21.23 | 22.44 | 36.64 | 12.06 | NA | NA | NA | NR | NR | AVG C11-20 | Y | 1999-01-27 | 7:00 | 183.25 | 7232.2667 | 8.11 | 20.6 | 1.958 | 0.033 | 1.6854 | 1.94 | 0.75 | 1.19 | 20.5 | 8.4 | 23.83 | 175 | 5.35 | 8.955 | 33.845 | 53.47 | 101.62 | 50.24 | 23.23 | 25.61 | 27.1 | 35.67 | 12.09 | NA | NA | NA | 161.85 | 173.94 | Natural Gas Rate ($/ft3) | 0.003
Phone Number |  |  |  | General RSSCT Design Parameters |  | 80 | 0.18 | [17 empty] | C12-10 | N | 1999-01-23 | 15:45 | 106 | 8366.9333 | 8.19 | 21 | 2.566 | 0.0449 | 1.7498 | 2.34 | 0.9 | 1.44 | 20.5 | 8.3 | 23.4 | 195 | BMRL | 14.12 | 46.35 | 50.58 | 111.05 | NR | 22.11 | 13.92 | 30.36 | 18.11 | 4.14 | NA | NA | NA | NR | NR | C12-20 | N | 1999-01-28 | 9:00 | 209.25 | 8258.4 | 8.01 | 21 | 2.182 | 0.0349 | 1.5995 | 2.07 | 0.7 | 1.37 | 20.5 | 8.4 | 23.83 | 185 | 3.31 | 11.94 | 37.09 | 54.86 | 107.2 | NR | 25.78 | 33 | 32.97 | 38.72 | 15.53 | NA | NA | NA | NR | NR | Current Process Water Rate ($/1000 gal) | 0.38
FAX Number |  |  |  | Kinematic viscosity at ToC, nLC (m2/s) | 1.3222e-06 | 100 | 0.15 |  |  |  | Group B, 3 samples per batch | [6 empty] | Group B, 3 samples per batch | [74 empty] | Modifications to Existing Plant (% of construction costs) | 15
E-Mail Address (optional) |  |  |  | RSSCT carbon particle diameter, dSC (mm) | 0.1125 | 120 | 0.125 |  |  |  | Parameter | Units | Sample B1-10 | Sample B2-10 | Sample B3-10 | Average | %SD | Parameter | Units | Sample B1-20 | Sample B2-20 | Sample B3-20 | Average | %SD
|  |  |  | Scaling factor, SF | 13.1556 | 140 | 0.106 | 1: Design information, similar to that shown in Tables 6c and 6d of the ICR rule, must be included in |  |  | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-20 | 1999-01-23 | --- | --- | Sampling date | MM/DD/YY | 1999-01-19 | 1999-01-23 | 1999-01-28 | --- | ---
Plant Name | Grimes Treatment Plant |  |  | RSSCT hydraulic loading rate, vSC (m/hr) | 7.3872 | 170 | 0.088 | the hard-copy Treatment Study Summary Report (see Section 10.0). The purpose of this table |  |  | Sampling time | hh:mm | 6:02 | 10:15 | 16:30 | --- | --- | Sampling time | hh:mm | 16:00 | 16:30 | 8:40 | --- | ---
Treatment Plant Category | Conventional |  |  | RSSCT flow rate, QSC (mL/min) | 21.7571 | 200 | 0.075 | is to list the pretreatment processes used in this particular RSSCT run. |  |  | Operation time | hh.hh | 0.28333 | 28.5 | 106.75 | --- | --- | Operation time | hh.hh | 0.25 | 96.75 | 208.9167 | --- | ---
Process Train Name | Conv |  |  | Estimated total influent volume required, VSCT (L) | 396.1589 | 230 | 0.062 |  |  |  | Bed volumes | (10 minute) | 22.3644 | 2249.6 | 8426.1333 | --- | --- | Bed volumes | (20 minute) | 9.8667 | 3818.4 | 8245.2444 | --- | --- | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
ICR Treatment Plant Identification Number | 652 |  |  |  |  | 270 | 0.053 |  |  |  | pH | --- | 7.66 | 7.84 | 8.05 | 7.85 | 2.4865 | pH | --- | 7.85 | 7.97 | 7.93 | 7.9167 | 0.7718 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
PWSID Number of Plant (if assigned) | TX2210001 |  |  | 10-Minute EBCT Run |  | 325 | 0.044 |  |  |  | Turbidity | ntu | 0.32 | 0.26 | 0.26 | 0.28 | 12.3718 | Turbidity | ntu | 0.27 | 0.24 | 0.24 | 0.25 | 6.9282 | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below. | [33 empty] | 1: Do not enter the results from duplicate samples into the table above, instead enter the average value for the primary and duplicate analyses in the above table, and enter the results for the primary and duplicate analyses below.
Historical Minimum Water Temperature (oC) | 8 |  |  | Full-scale empty bed contact time, EBCTLC (min) | 10 | 400 | 0.037 |  |  |  | Temperature | oC | 20.7 | 21.6 | 20.8 | 21.0333 | 2.3453 | Temperature | oC | 20.5 | 20.1 | 20.4 | 20.3333 | 1.0238
Historical Average Water Temperature (oC) | 19.5 |  |  | Estimated full-scale run time, tLCT (days) | 55.4491 | [5 empty] | Total organic carbon | mg/L | 2.994 | 2.617 | 3.514 | 3.0417 | 14.8075 | Total organic carbon | mg/L | 2.692 | 3.278 | 3.207 | 3.059 | 10.4547 | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses) | [33 empty] | Group D, 3 duplicate effluent samples per run (results from primary and duplicate analyses)
State Approved Plant Capacity (MGD) | 25 |  |  | RSSCT empty bed contact time, EBCTSC (min) | 0.76014 | [5 empty] | UV254 | cm-1 | 0.0828 | 0.0855 | 0.0815 | 0.083267 | 2.4505 | UV254 | cm-1 | 0.0867 | 0.0807 | 0.0773 | 0.081567 | 5.8352 | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | Sample | Sample | Sampling | Sampling | Operation | Bed | pH | Temp. | TOC | UV254 | SUVA | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS | SDS
|  |  |  | Estimated RSSCT run time, tSCT (days) | 4.2149 | [5 empty] | SUVA | L/(mg*m) | 2.7655 | 3.2671 | 2.3193 | 2.784 | 17.0322 | SUVA | L/(mg*m) | 3.2207 | 2.4619 | 2.4104 | 2.6976 | 16.8181 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6 | ID | Type | date | time | time | volumes | [5 empty] | Cl2 dose | Free Cl2 residual | Cl2 demand | Chlorination temp. | Chlorination pH | Incubation time | TOX | CHCl3 | BDCM | DBCM | CHBr3 | THM4 | MCAA* | DCAA* | TCAA* | MBAA* | DBAA* | BCAA* | TBAA | CDBAA | DCBAA | HAA5 | HAA6
|  |  |  | RSSCT bed length, lSC (cm) | 9.3588 | [5 empty] | SDS-Cl2 dose | mg/L | 2.61 | 2.31 | 3.01 | 2.6433 | 13.2858 | SDS-Cl2 dose | mg/L | 2.36 | 2.8 | 2.65 | 2.6033 | 8.5921 |  |  | MM/DD/YY | hh:mm | hh.hh | (10 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L |  |  | MM/DD/YY | hh:mm | hh.hh | (20 minute) | --- | oC | mg/L | cm-1 | L/(mg*m) | mg/L | mg/L | mg/L | oC | --- | hours | mg Cl- /L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L | mg/L
|  |  |  | Estimated volume required for 10-minute EBCT, VSC (L) | 132.053 | [5 empty] | SDS-Free Cl2 residual | mg/L | 0.8 | 0.8 | 0.9 | 0.83333 | 6.9282 | SDS-Free Cl2 residual | mg/L | 0.7 | 0.9 | 0.9 | 0.83333 | 13.8564 | C3-10 | Primary | 1999-01-19 | 17:00 | 11.25 | 888 | 8.01 | 21.6 | BMRL | BMRL | #VALUE! | 1.11 | 1 | 0.11 | 20.5 | 8.5 | 23.2 | 36 | 6.92 | 4.94 | 7.38 | 21.54 | 40.78 | 17.8 | 11.84 | 25.13 | 16.16 | 7.46 | BMRL | NA | NA | NA | 78.39 | 78.39 | C4-20 | Primary | 1999-01-20 | 15:15 | 23.5 | 927.4667 | 8.06 | 20.8 | 0.492 | BMRL | #VALUE! | 1.1 | 1 | 0.1 | 20.5 | 8.5 | 23.4 | 65 | BMRL | BMRL | 11.48 | 30.22 | 41.7 | 1.08 | 24.31 | 25.82 | 25.19 | 19.59 | 11.89 | NA | NA | NA | 95.99 | 107.88
|  |  |  | Mass GAC required, mSC (g) | 7.5249 | [5 empty] | SDS-Cl2 demand | mg/L | 1.81 | 1.51 | 2.11 | 1.81 | 16.5746 | SDS-Cl2 demand | mg/L | 1.66 | 1.9 | 1.75 | 1.77 | 6.8499 | D1-10 | Duplicate | 1999-01-19 | 17:00 | 11.25 | 888 | 8.01 | 21.6 | BMRL | BMRL | #VALUE! | 1.11 | 0.8 | 0.31 | 20.5 | 8.5 | 23.2 | 44 | BMRL | BMRL | 10.99 | 27.5149 | 38.5049 | 11.59 | 12.92 | 25.66 | 17.42 | 10.29 | 9.66 | NA | NA | NA | 77.88 | 87.54 | D1-20 | Duplicate | 1999-01-20 | 15:15 | 23.5 | 927.4667 | 8.06 | 20.8 | 0.541 | BMRL | #VALUE! | 1.13 | 0.8 | 0.33 | 20.5 | 8.5 | 23.4 | 65 | BMRL | BMRL | 11.05 | 29.79 | 40.84 | NR | 24.24 | 20 | 30.3 | 21.12 | 2.44 | NA | NA | NA | NR | NR
[11 empty] | SDS-Chlorination temp. | oC | 20.5 | 20.5 | 20.5 | 20.5 | 0 | SDS-Chlorination temp. | oC | 20.5 | 20.5 | 20.5 | 20.5 | 0 |  | Average | --- | --- | --- | --- | 8.01 | 21.6 | #DIV/0! | #DIV/0! | #VALUE! | 1.11 | 0.9 | 0.21 | 20.5 | 8.5 | 23.2 | 40 | 6.92 | 4.94 | 9.185 | 24.5275 | 39.6424 | 14.695 | 12.38 | 25.395 | 16.79 | 8.875 | 9.66 | #DIV/0! | #DIV/0! | #DIV/0! | 78.135 | 82.965 |  | Average | --- | --- | --- | --- | 8.06 | 20.8 | 0.5165 | #DIV/0! | #VALUE! | 1.115 | 0.9 | 0.215 | 20.5 | 8.5 | 23.4 | 65 | #DIV/0! | #DIV/0! | 11.265 | 30.005 | 41.27 | 1.08 | 24.275 | 22.91 | 27.745 | 20.355 | 7.165 | #DIV/0! | #DIV/0! | #DIV/0! | 95.99 | 83.85
|  |  |  | 20-Minute EBCT Run | [6 empty] | SDS-Chlorination pH | --- | 8.4 | 8.4 | 8.4 | 8.4 | 0 | SDS-Chlorination pH | --- | 8.4 | 8.4 | 8.3 | 8.3667 | 0.69006 |  | RPD | --- | --- | --- | --- | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | 0 | 22.2222 | 95.2381 | 0 | 0 | 0 | 20 | #VALUE! | #VALUE! | 39.3032 | 24.3601 | 5.739 | 42.2593 | 8.7237 | 2.087 | 7.5045 | 31.8873 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.65272 | 11.0287 |  | RPD | --- | --- | --- | --- | 0 | 0 | 9.4869 | #VALUE! | #VALUE! | 2.6906 | 22.2222 | 106.9767 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | 3.8171 | 1.4331 | 2.0838 | #VALUE! | 0.28836 | 25.4038 | 18.4177 | 7.5166 | 131.8911 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
|  |  |  | Full-scale empty bed contact time, EBCTLC (min) | 20 | [5 empty] | SDS-Incubation time | hours | 23.17 | 23 | 23.4 | 23.19 | 0.86567 | SDS-Incubation time | hours | 23 | 23.4 | 23.83 | 23.41 | 1.7731 | C7-10 | Primary | 1999-01-20 | 17:32 | 35.7833 | 2824.4978 | 8.06 | 21.6 | 1.035 | 0.0225 | 2.1739 | 1.44 | 0.8 | 0.64 | 20.5 | 8.4 | 23.2 | 105 | BMRL | BMRL | BMRL | 36.89 | 36.89 | BMRL | 14.02 | 20.33 | 16.81 | 20.1 | 8.01 | NA | NA | NA | 71.26 | 79.27 | C7-20 | Primary | 1999-01-23 | 15:00 | 95.25 | 3759.2 | 8.22 | 20.4 | 1.485 | 0.0202 | 1.3603 | 1.7 | 1 | 0.7 | 20.5 | 8.3 | 23.4 | 110 | BMRL | BMRL | 18.72 | 43.39 | 62.11 | 45.15 | 23.86 | 36.16 | 36.01 | 33.07 | 8.52 | NA | NA | NA | 174.25 | 182.77
|  |  |  | Estimated full-scale run time, tLCT (days) | 110.8982 | [5 empty] | SDS-TOX | mg Cl- /L | 315 | 275 | 295 | 295 | 6.7797 | SDS-TOX | mg Cl- /L | NR | 270 | NR | 270 | #DIV/0! | D2-10 | Duplicate | 1999-01-20 | 17:32 | 35.7833 | 2824.4978 | 8.06 | 21.6 | 0.985 | 0.0226 | 2.2944 | 1.39 | 0.9 | 0.49 | 20.5 | 8.5 | 22.74 | 105 | 3.43 | BMRL | 7.68 | 33.48 | 44.59 | 49.5 | 20.68 | 49.67 | 31.2 | 36.04 | 9.53 | NA | NA | NA | 187.09 | 196.62 | D2-20 | Duplicate | 1999-01-23 | 15:00 | 95.25 | 3759.2 | 8.22 | 20.4 | 1.46 | 0.0203 | 1.3904 | 1.68 | 1 | 0.68 | 20.5 | 8.4 | 23.4 | 125 | BMRL | BMRL | 16.53 | 33.29 | 49.82 | 64.14 | 23.86 | 33.6 | 34.42 | 33.2 | 6.91 | NA | NA | NA | 189.22 | 196.13
|  |  |  | RSSCT empty bed contact time, EBCTSC (min) | 1.5203 | [5 empty] | SDS-CHCl3 | mg/L | BMRL | 12.73 | 9.87 | 11.3 | 17.8967 | SDS-CHCl3 | mg/L | 16.9 | 8.21 | 12.06 | 12.39 | 35.1444 |  | Average | --- | --- | --- | --- | 8.06 | 21.6 | 1.01 | 0.02255 | 2.2342 | 1.415 | 0.85 | 0.565 | 20.5 | 8.45 | 22.97 | 105 | 3.43 | #DIV/0! | 7.68 | 35.185 | 40.74 | 49.5 | 17.35 | 35 | 24.005 | 28.07 | 8.77 | #DIV/0! | #DIV/0! | #DIV/0! | 129.175 | 137.945 |  | Average | --- | --- | --- | --- | 8.22 | 20.4 | 1.4725 | 0.02025 | 1.3753 | 1.69 | 1 | 0.69 | 20.5 | 8.35 | 23.4 | 117.5 | #DIV/0! | #DIV/0! | 17.625 | 38.34 | 55.965 | 54.645 | 23.86 | 34.88 | 35.215 | 33.135 | 7.715 | #DIV/0! | #DIV/0! | #DIV/0! | 181.735 | 189.45
|  |  |  | Estimated RSSCT run time, tSCT (days) | 8.4298 | [5 empty] | SDS-BDCM | mg/L | 33.84 | 27.93 | 31.7 | 31.1567 | 9.6038 | SDS-BDCM | mg/L | 26.31 | 28.5 | 30.71 | 28.5067 | 7.7175 |  | RPD | --- | --- | --- | --- | 0 | 0 | 4.9505 | 0.44346 | 5.3937 | 3.5336 | 11.7647 | 26.5487 | 0 | 1.1834 | 2.0026 | 0 | #VALUE! | #VALUE! | #VALUE! | 9.6916 | 18.9003 | #VALUE! | 38.3862 | 83.8286 | 59.9458 | 56.7866 | 17.3318 | #VALUE! | #VALUE! | #VALUE! | 89.6691 | 85.0701 |  | RPD | --- | --- | --- | --- | 0 | 0 | 1.6978 | 0.49383 | 2.1916 | 1.1834 | 0 | 2.8986 | 0 | 1.1976 | 0 | 12.766 | #VALUE! | #VALUE! | 12.4255 | 26.3432 | 21.9602 | 34.7516 | 0 | 7.3394 | 4.5151 | 0.39233 | 20.8684 | #VALUE! | #VALUE! | #VALUE! | 8.2373 | 7.052
|  |  |  | RSSCT bed length, lSC (cm) | 18.7175 | [5 empty] | SDS-DBCM | mg/L | 51.06 | 45.49 | 56.92 | 51.1567 | 11.1728 | SDS-DBCM | mg/L | 43.12 | 44.36 | 45.07 | 44.1833 | 2.2337 | C10-10 | Primary | 1999-01-21 | 17:30 | 59.75 | 4716.2667 | 7.97 | 20.9 | 1.716 | 0.0259 | 1.5093 | 1.7 | 0.8 | 0.9 | 20.5 | 8.3 | 23.4 | 155 | BMRL | 5.96 | 30 | 51.95 | 87.91 | 50.99 | 24.17 | 26.03 | 26.36 | 37.98 | 14.55 | NA | NA | NA | 165.53 | 180.08 | C11-20 | Primary | 1999-01-27 | 7:00 | 183.25 | 7232.2667 | 8.11 | 20.6 | 2.009 | 0.032 | 1.5928 | 1.97 | 0.7 | 1.27 | 20.5 | 8.4 | 23.83 | 175 | 5.35 | 9.88 | 35.01 | 54.04 | 104.28 | NR | 23.75 | 29.31 | BMRL | 29.16 | 14.34 | NA | NA | NA | NR | NR
|  |  |  | Estimated volume required for 20-minute EBCT, VSC (L) | 264.1059 | [5 empty] | SDS-CHBr3 | mg/L | 53.86 | 50.89 | 50.89 | 51.88 | 3.3052 | SDS-CHBr3 | mg/L | 48.75 | 48 | 46.19 | 47.6467 | 2.7621 | D3-10 | Duplicate | 1999-01-21 | 17:30 | 59.75 | 4716.2667 | 7.97 | 20.9 | 1.671 | 0.0253 | 1.5141 | 1.78 | 0.8 | 0.98 | 20.5 | 8.4 | 23.4 | 155 | BMRL | 6.29 | 35.7 | 51.08 | 93.07 | 53.22 | 25.15 | 31.48 | 31.62 | 36.58 | 12.74 | NA | NA | NA | 178.05 | 190.79 | D3-20 | Duplicate | 1999-01-27 | 7:00 | 183.25 | 7232.2667 | 8.11 | 20.6 | 1.908 | 0.033 | 1.7296 | 1.91 | 0.8 | 1.11 | 20.5 | 8.4 | 23.83 | NR | BMRL | 8.03 | 32.68 | 52.9 | NR | 50.24 | 23.23 | 25.61 | 27.1 | 35.67 | 12.09 | NA | NA | NA | 161.85 | 173.94
|  |  |  | Mass GAC required, mSC (g) | 15.0499 | [5 empty] | SDS-THM4 | mg/L | 138.76 | 137.04 | 149.38 | 141.7267 | 4.7158 | SDS-THM4 | mg/L | 135.08 | 129.07 | 134.03 | 132.7267 | 2.4185 |  | Average | --- | --- | --- | --- | 7.97 | 20.9 | 1.6935 | 0.0256 | 1.5117 | 1.74 | 0.8 | 0.94 | 20.5 | 8.35 | 23.4 | 155 | #DIV/0! | 6.125 | 32.85 | 51.515 | 90.49 | 52.105 | 24.66 | 28.755 | 28.99 | 37.28 | 13.645 | #DIV/0! | #DIV/0! | #DIV/0! | 171.79 | 185.435 |  | Average | --- | --- | --- | --- | 8.11 | 20.6 | 1.9585 | 0.0325 | 1.6612 | 1.94 | 0.75 | 1.19 | 20.5 | 8.4 | 23.83 | 175 | 5.35 | 8.955 | 33.845 | 53.47 | 104.28 | 50.24 | 23.49 | 27.46 | 27.1 | 32.415 | 13.215 | #DIV/0! | #DIV/0! | #DIV/0! | 161.85 | 173.94
[11 empty] | SDS-MCAA* | mg/L | 10.1 | 55.91 | 62.65 | 42.8867 | 66.6719 | SDS-MCAA* | mg/L | BMRL | NR | NR | #DIV/0! | #DIV/0! |  | RPD | --- | --- | --- | --- | 0 | 0 | 2.6572 | 2.3438 | 0.31352 | 4.5977 | 0 | 8.5106 | 0 | 1.1976 | 0 | 0 | #VALUE! | 5.3878 | 17.3516 | 1.6888 | 5.7023 | 4.2798 | 3.974 | 18.9532 | 18.1442 | 3.7554 | 13.2649 | #VALUE! | #VALUE! | #VALUE! | 7.288 | 5.7756 |  | RPD | --- | --- | --- | --- | 0 | 0 | 5.157 | 3.0769 | 8.2307 | 3.0928 | 13.3333 | 13.4454 | 0 | 0 | 0 | #VALUE! | #VALUE! | 20.6588 | 6.8843 | 2.132 | #VALUE! | #VALUE! | 2.2137 | 13.4741 | #VALUE! | 20.0833 | 17.0261 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[11 empty] | SDS-DCAA* | mg/L | BMRL | 12.12 | 19.7 | 15.91 | 33.6887 | SDS-DCAA* | mg/L | 6.97 | 23.23 | 24.35 | 18.1833 | 53.4949 | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [15 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [17 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [14 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | SDS-TCAA* | mg/L | 20.58 | 26.92 | 11.88 | 19.7933 | 38.1482 | SDS-TCAA* | mg/L | 18.2 | 28.12 | 27.22 | 24.5133 | 22.3796 | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [15 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [17 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [14 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
[11 empty] | SDS-MBAA* | mg/L | 12.34 | 21.01 | 23.28 | 18.8767 | 30.5858 | SDS-MBAA* | mg/L | 7.56 | 31.3 | 26.77 | 21.8767 | 57.6129
[11 empty] | SDS-DBAA* | mg/L | 16.95 | 22.7 | 18.6 | 19.4167 | 15.2483 | SDS-DBAA* | mg/L | 17.96 | 8.04 | 42.44 | 22.8133 | 77.613
[11 empty] | SDS-BCAA* | mg/L | 9.4 | 13.67 | 3.02 | 8.6967 | 61.6296 | SDS-BCAA* | mg/L | 8.36 | 25.08 | 24.85 | 19.43 | 49.3443
[11 empty] | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-TBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-CDBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0! | SDS-DCBAA | mg/L | NA | NA | NA | #DIV/0! | #DIV/0!
[11 empty] | SDS-HAA5 | mg/L | 59.97 | 138.66 | 136.11 | 111.58 | 40.0733 | SDS-HAA5 | mg/L | 50.69 | NR | NR | 50.69 | #DIV/0!
[11 empty] | SDS-HAA6 | mg/L | 69.37 | 152.33 | 139.13 | 120.2767 | 37.0627 | SDS-HAA6 | mg/L | 59.05 | NR | NR | 59.05 | #DIV/0!
[11 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported | [6 empty] | BMRL = Below Minimum Reporting Level; NA = Not Analyzed; NR = Not Reported
[11 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured. | [6 empty] | *: These six species make up HAA6, but the other three HAA species, TBAA, CDBAA and DCBAA, should be reported if measured.
Note on H5: Reviewer D.S. (10/12/99): Per Consultant on design TOC higher than the measured TOC: "This is due to technician error."
Note on H7: Reviewer M.H. (11/8/99): Reviewer adjusted Reynolds number based on revised full-scale temperature supplied by utility.
Note on H8: Reviewer D.S. (10/12/99): Full-scale temperature is 10C, column design based on 20C.
Note on Q53: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Q54: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Y53: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on Y54: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BA35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BB35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BD35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BD39: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BE39: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BF39: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BG39: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BH35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BH39: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on BM5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BM6: Reviewer D.S. (10/12/99): Per Consultant on abnormal HAA effluent curves: "Results have been verified."
Note on BM30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BN5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on BN6: Reviewer D.S. (10/12/99): Per Consultant on abnormal HAA effluent curves: "Results have been verified."
Note on BN30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CO35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on CR35: Reviewer D.S. (10/12/99): Per Consultant on high DBP RPDs: "Results are verified."
Note on CV5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CV6: Reviewer D.S. (10/12/99): Per Consultant on abnormal HAA effluent curves: "Results have been verified."
Note on CV30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CW5: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CW6: Reviewer D.S. (10/12/99): Per Consultant on abnormal HAA effluent curves: "Results have been verified."
Note on CW30: Reviewer D.S. (10/12/99): Per Consultant on HAA data: "There are two possible causes for this phenomen. The first, and most unlikely, is the presence of precursors in the water source. The most probable cause is laboratory contamination. We have experienced this before on HAAs."
Note on CZ13: Reviewer M.H. (11/8/99): Per utility, "I could not locate a 98 PPI that made sense on a base year of 1967."
Note on CZ17: Reviewer M.H. (11/8/99): Per utility, "we do not use fuel oil in this region for any purpose."